## Sheet2
EventNotificationNumber | RetractIndicator | SiteName | UnitInd1 | UnitInd2 | UnitInd3 | RxType | EventDate | NotificationDate | DateUpdated | Text | CurrPower1 | CurrPower2 | CurrPower3 | InitPower1 | InitPower2 | InitPower3 | CriticalIndicator1 | CriticalIndicator2 | CriticalIndicator3 | ScramType1 | ScramType2 | ScramType3 | EventDescription | CfrDescription1 | CfrDescription2 | CfrDescription3 | CfrDescription4 | IMode1 | IMode2 | IMode3 | FMode1 | FMode2 | FMode3 | EmergencyClass | RegionNumber | StateCode | DocumentTypeCode | SubType | CfrCode1 | CfrCode2 | CfrCode3 | CfrCode4 | Security | ReleaseDate
54951 | 0 | San Onofre |  |  |  | Isfsi | 2020-10-15 16:26 | 2020-10-15 20:08 | 2020-10-15 | SAFEGUARDS REPORT - DISCOVERY OF A VULNERABILITY IN A SAFEGUARD SYSTEM Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the region. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | Safeguards Reports | [9 empty] | Non Emergency | 4 | CA | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2020-10-15
54950 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2020-10-12 13:15 | 2020-10-15 17:17 | 2020-10-15 | AGREEMENT STATE REPORT - UNPLANNED FIRE AND DOSE TO THE PUBLIC The following was received from the state of Tennessee via email: "Energy Solutions experienced a fire in the gas furnace 'Drum Drying Operation' of the Liquid Volume Reduction Facility (LVRF) building, which is a sub building off of the Incinerator building located at the 1560 Bear Creek Road, [Oak Ridge, TN] facility. The drums being processed contained Energy Solutions secondary waste with the following listed source term associated with the containers: C-14 (0.5 mCi), Co-60 (2.2 mCi), Cs-137 (0.96 mCi), Fe-55 (2 mCi), H-3 (4 Ci), and Tc-99 (98 mCi). "Estimated 0.03 mrem dose to the public as a result of the event." TN event number: TN-20-155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-10-23
54949 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2020-10-14 15:00 | 2020-10-15 17:29 | 2020-10-15 | AGREEMENT STATE REPORT - LOST GAUGES The following was received from the state of Tennessee via email: "General licensee, Blues City Brewery, reported the loss of 3 gauges after contractor work that involved the movement of the gauges. Blues City reported the loss. It is possible that the gauges could have made it into the local scrap metal stream. From the scrap metal facility, the load that might have included the gauges went to a shredding facility in Alabama. The State of Alabama Radiation Control has been notified in case gauges are discovered at the shredding facility. The gauge is below: "Manufacturer Model SN Isotope Activity "Industrial Dynamics CI-2GV/3 44 Am-241 300 mCi "Industrial Dynamics CI-2GV/3 46 Am-241 300 mCi "Industrial Dynamics FT-100 33 Am-241 100 mCi" TN event number: TN-20-152 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-10-23
54948 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-10-14 10:00 | 2020-10-15 14:31 | 2020-10-15 | AGREEMENT STATE REPORT - MISSING DENSITY GAUGE The following was received from the Colorado Department of Public Health and Environment (CDPHE) via email: "[A Troxler 3440 (SN 23106) containing not more than 333 MBq (9 mCi) of cesium-137 and 1.63 GBq (44 mCi) of americium-241:beryllium; or 2.44 MBq (66 microCi) of californium-252] was reported missing after a licensee was unable to account for it during a routine inventory check. The material was noticed missing at approximately 1000 MDT on Wednesday, October 14, 2020. The event was reported to the CDPHE at approximately 1700 on October 14, 2020. "No signs of a burglary at the facility are present. The last entry for the gauge in the utilization log is August 19, 2020. The licensee suspects that a former employee stole the gauge, the employee to last check-out the gauge was terminated on bad terms. "The licensee is in the process of reporting the theft to the local police." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-10-23
54947 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-10-09 08:30 | 2020-10-14 14:28 | 2020-10-14 | AGREEMENT STATE REPORT - TC-99M EXTERNAL CONTAMINATION The following was received from Illinois Emergency Management Agency (the Agency) via email: "During the afternoon of October 13, 2020, the Agency received a call from the RSO [(Radiation Safety Officer)] at Rush Oak Park Hospital, Inc. (IL-01676-01) to notify the Agency of a potential 24-hr notification requirement from an event which occurred at 0830 CDT, Friday, October 9, 2020. According to the RSO, a Nuclear Medicine Technologist (NMT) was administering a 27 mCi dose of Tc-99m to a patient when the vein "collapsed" which created pressure and sprayed a small quantity of Tc-99m back into the technicians face and eyes. The technician soon thereafter went to the E.R. [(emergency room)] and had her eyes rinsed out. At 1000 the same morning, the RSO met the NMT in the E.R. and took a near contact measurement of her face utilizing a Ludlum model 26 which identified a maximum 6,050 cpm on her forehead. The RSO stated that he could not identify any contamination elsewhere or within the wash water at the E.R. Having no other information, the RSO calculated that in consideration of an approximately 0.23 percent efficiency of the instrument, approximately 1.2 microCi of Tc-99m was on the skin of the NMT. The RSO also stated that he did a few worst case scenario calculations but didn't come close to reportable levels. The Agency concurs with the licensee's determinations. Furthermore, the patient was given most of the dose and still had a normal scan. No contamination was identified on the patient. The used syringe measured 1 mCi remaining following treatment and the accident. The RSO explained that he didn't think it was reportable but following a closer look at 32 IAC 340.1220(c)(3) thought he had better complete his due diligence and give us a call. Inspection and Enforcement supervisor to follow up with the licensee. "The incident will be entered into NMED [(Nuclear Material Events Database)] and reported to the Headquarters Operations Officer within 24 hours of notification, as required. "The licensee will be advised of the requirement to submit a written report within 30 days in accordance with 32 IAC 340.1230." Item Number: IL200019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-10-22
54946 | 0 | IU Health Methodist Hospital |  |  |  |  | 2020-10-13 10:00 | 2020-10-13 14:49 | 2020-10-13 | NON-AGREEMENT STATE REPORT - Y-90 MICROSPHERE UNDERDOSE The following is a summary from a phone call with the licensee: A patient at the Indiana University Health Methodist Hospital was prescribed 46.7 mCi of Y-90 Theraspheres to segments 5 and 8 of the liver, but received 54 percent (25.2 mCi) of the prescribed dose. The remaining 46 percent (21.5 mCi) was trapped in the catheter or the line. The patient and the physician were notified and a follow-up treatment has been scheduled for next week. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Dose <> Prescribed Dosage | [9 empty] | Non Emergency | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2020-10-21
54945 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-10-10 | 2020-10-12 12:41 | 2020-10-13 | <br><br>EN Revision Imported Date : 10/14/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The following was received from the Texas Department of State Health Services (the Agency) via email: "On October 12, 2020, the licensee notified the Agency that on October 10, 2020, one of its technicians completed a job at a temporary job site in Dallas, Texas, and drove to another temporary job site in Venus, Texas. Upon arriving, the technician found he did not have the Humboldt 5001 EZ moisture/density gauge in his truck. The gauge contained an 8 milliCurie cesium-137 and a 40 milliCurie americium-241/beryllium source. The technician believed he left the gauge at the Dallas site so he drove back to that site. The gauge was not there. The technician called his supervisor but never made contact. The technician called the company office and left a voicemail about the incident which was retrieved this morning. The licensee is notifying local law enforcement, contacting area pawn shops, and conducting its investigation. More information will be provided as it is obtained in accordance with SA-300." Texas Incident Number: 9806 * * * UPDATE ON 10/13/2020 AT 1414 EDT FROM KAREN BLANCHARD TO OSSY FONT * * * The following update was received from the Agency via email: "The location where the event occurred is a temporary job site in the 7400 block of Hillcrest Road in Frisco, Texas. The gauge, a Humboldt 5001 EZ, contains 10 milliCuries of cesium-137 (not 8) and 40 milliCuries of americium-241/beryllium. The insertion rod was locked. The licensee has made a report to the Frisco police department. The licensee has thoroughly searched the construction site a second time and will be checking businesses around the site for possible video surveillance that may provide information. The Agency has informed the Frisco fire department/emergency management coordinator. Further information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Azua) and NMSS Events Notification, ILTAB, and CNSNS (Mexico) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-10-20
54944 | 0 | Cook |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-10-12 00:26 | 2020-10-12 03:46 | 2020-10-12 | AUTOMATIC REACTOR TRIP "At 0026 [EDT] on October 12, 2020, D.C. Cook Unit 2 tripped automatically on low-low level of #24 steam generator which occurred after a lowering of main condenser vacuum. "The reason for the lowering main condenser vacuum and the reason for the low steam generator #24 level is under investigation. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation as a four (4) hour report. Notification is also being made as an eight (8) hour report under 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). "The D.C. Cook Resident NRC Inspector has been notified. "Unit 2 is being supplied by offsite power. All control rods fully inserted. Auxiliary Feedwater Pumps started as required and are operating properly. Decay heat is being removed via steam generator power operated relief valves (PORVs) due to condenser steam dump unavailability from low main condenser vacuum. All four Reactor Coolant Pumps remain running. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. D.C. Cook Unit 2 remains stable in Mode 3. No radioactive release is in progress as a result of this event." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode2: Power Operation; FMode2: Hot Standby | Non Emergency | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-10-12
54943 | 0 | Catawba | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-10-11 03:15 | 2020-10-11 10:25 | 2020-10-11 | LONG TERM HABITABILITY OF THE TECHNICAL SUPPORT CENTER UNDER ACCIDENT DOSE ANALYSIS EXCEEDS THE CALCULATED ALLOWABLE VALUES "At 0315 [EDT] on October 11, 2020, Unit 2 ECCS [Emergency Core Cooling System] leakage outside containment was determined to exceed the long term habitability dose analysis for the Catawba Nuclear Station Technical Support Center (TSC) under bounding conditions. At the current leakage (approximately 3.2 gpm), the dose analysis indicates dose to TSC inhabitants would exceed the 30 days REM TEDE [Total Effective Dose Equivalent] limit should leakage continue for the entire duration. Repairs are currently in-progress to arrest the leakage and restore functionality of the TSC. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to the alternate facility. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the discovered condition of the TSC affects the functionality of an emergency response facility, "There is no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-10-11
54942 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-10-08 | 2020-10-09 19:34 | 2020-10-09 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA STUCK HAND-CRANK ASSEMBLY The following information was received via E-mail: "ND Testing Inc. made a 24-hour report to the Radiologic Health Branch that on October 8, 2020, at 1256 PDT a hand-crank assembly became stuck/seized and would not allow the source to travel forward or backwards at a temporary job site. The team of two experienced radiographers contacted their Radiation Safety Officer (RSO) for assistance and secured the area around their QSA Global 880 exposure device. "The RSO arrived onsite at 1445 EDT with extra lead shielding and survey meters. He and the radiographers were able to place lead blankets and some solid lead blocks over the guidetube containing the Ir-192 source, open the crank assembly to remove some metal shavings and close the assembly. This allowed them to secure the Ir-192 source after approximately 2 hours at 1645 EDT. The highest individual dose received was 195 mrem by one of the radiographers. "The Ir-192 source was a QSA Global model A424-9, with an activity of 67.1 Ci of Ir-192." California 5010 Number: 100920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-10-19
54941 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2020-04-14 | 2020-10-09 13:42 | 2020-10-09 | AGREEMENT STATE REPORT - MISSING IODINE-125 SEED The following information was received via facsimile: "On April 29, 2020, the Department [New York State Department of Health, Bureau of Environmental Radiation Protection] was notified of a missing I-125 localization seed (Best Medical International, Inc., Model 2301, Activity: 220 microCuries) at Roswell Park Cancer Institute in Buffalo, New York. "In this incident, two seeds were placed into a patient on 4/10/2020 and removed on 4/14/2020. One of the two seeds was lost by the attending surgeon. An extensive survey of the patient was performed to verify that the seed was not in the patient and the Nuclear Medicine Department was notified. A survey of the operating room (OR) suite was conducted and the seed was not recovered. The Radiation Safety Office was notified, another survey of the OR was performed, again the seed was not recovered. The patient also had a lymphoscintigraphy with Tc-99m so the surgical trash that was still in the room was sequestered. After three days, the trash was surveyed and examined but the seed was not recovered. "Searches and surveys were performed in surgery, pathology, radiation safety and environmental service areas. Trash and regulated medical waste were also surveyed and inspected. "Ultimate disposition of the source is unknown and it is possible that the source may still be recovered." New York State Event Report ID No.: NYDOH - 20-05 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2020-10-19
54940 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2020-10-08 | 2020-10-09 13:42 | 2020-10-09 | AGREEMENT STATE REPORT - LOST THEN FOUND MOISTURE / DENSITY GAUGE The following is a synopsis of information received via phone and facsimile: The Department (Nebraska Department of Health and Human Services, Office of Radiological Health) was notified around 0815 CDT on October 9, 2020, by the Nebraska State Patrol, of a lost, and subsequently recovered, nuclear gauge. The gauge was a Troxler 3400 series moisture density gauge containing a 9 mCi Cs-137 source and a 44 mCi Am-241/Be source. During the afternoon of October 8, 2020, the gauge was on the tailgate of a pickup truck. The gauge user entered the vehicle before securing the gauge package. The user was distracted and began driving away. The gauge fell out of the back of the vehicle. An employee from the Nebraska Department of Transportation (NDOT) found the lost gauge near Norfolk, NE. The NDOT employee notified the Nebraska State Patrol and the gauge manufacturer, Troxler. Using the serial number of the gauge, Troxler was able to determine the gauge belonged to Olsson Associates. Olsson Associates was notified of the recovered gauge, and the gauge user retrieved the gauge. The estimated time between the loss of control and recovery is estimated to be one hour. During the evening of October 8, 2020, the corporate Radiation Safety Officer (RSO) for Olsson Associates was notified of the incident. He did not report the event to the Department. A representative of the Department spoke with him at 1030 CDT on October 9, 2020. The RSO then provided a brief account of the incident to the Department representative. The RSO noted that the gauge package appeared to be undamaged. The gauge itself did not appear damaged. The gauge was surveyed to confirm the presence of the source, and a leak test will be performed immediately. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-10-19
54939 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-10-08 | 2020-10-09 07:58 | 2020-10-09 | AGREEMENT STATE REPORT - A NON-LICENSED INDIVIDUAL PARTICIPATED IN MEDICAL TREATMENT The following event was received from the Florida Bureau of Radiation Control (BRC, ERCM) via email: "The incident was reported by [the medical physicist (MP)], who is standing in for local physics administrator who is on vacation. A 50 year old female was being treated with Ir-192 High Dose Rate (HDR). The Authorized Radiation Therapist and Physician were in the room along with [an acting MP with a] temporary license TMP-1. The supervising MP was remote. The supervising MP told the facility that the acting MP was on the license as an AMP [(Authorized MP)], which is why the AMP was in the room. The AMP was actually not on the license. After treatment was complete, the error about the AMP not being on the license was discovered, and the report to the Florida BRC was made. The treatment plan was confirmed before treatment by the AMP. Treatment was delivered as prescribed. Per ERCM: The AMP's license is null and void and TMP-1 is expired." Florida Incident Number: FL20-116. THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-10-19
54938 | 0 | Monticello | 1 |  |  | [1] GE-3 | 2020-10-08 11:25 | 2020-10-08 13:14 | 2020-10-08 | NOTIFICATION OF AN UNUSUAL EVENT At 1125 CDT on 10/8/20 Monticello Nuclear Generating Plant declared a Notification of an Unusual Event (NOUE) due to a Security Condition that did not involve a hostile action, due to a helicopter that hovered over the site for approximately 10 minutes. The unit remained at 100 percent power during the event. The licensee notified the NRC Resident Inspector, the Minnesota State Duty Officer and the Wright County and Sherburne County Sherriff departments of the event. Notified DHS SWO, FEMA Operations Center, CISA Central, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 10/8/2020 AT 2013 EDT FROM JEFF OLSON TO JEFFREY WHITED * * * "At 1715 CDT Monticello Nuclear Generating Plant terminated the Notice of Unusual Event (HU1.1), upon confirmation through federal law enforcement and conversation with the aircraft owner that the aircraft in question was performing power line inspections for a different utility and was not a threat to the plant. Monticello determined that this condition did not meet the 1-hour reporting requirements of 10 CFR 73.71." Notified R3DO (Orlikowski), NRR EO (Miller), and IRD MOC (Gott). Additionally, notified DHS SWO, FEMA Operations Center, CISA Central, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Emergency Declared | Offsite Notification | Safeguards Reports |  | IMode1: Power Operation; FMode1: Power Operation | Unusual Event | 3 | MN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) | 73.71(b)(1) |  | 0 | 2020-10-08
54937 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-10-08 | 2020-10-08 12:44 | 2020-10-08 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following information was received from the Texas Department of State Health Services (the Agency) via email: "On October 8, 2020, the Agency was contacted by the licensee and notified that while being used at a job site, a Troxler 3440 nuclear gauge was damaged by a road grader. The gauge contains a 40 milliCurie americium-241 source and an 8 milliCurie cesium-137 source. The licensee's technician had started a measurement and walked back to their truck when the grader came around a dirt pile and struck the gauge before the technician could respond. The cesium source operating rod was extended about 6 inches into the soil. The licensee performed a survey at the gauge and the reading at 3 feet was 1.2 millirem per hour. The licensee established a boundary at 15 feet from the gauge. The radiation safety officer (RSO) responded to the location. The RSO inspected the gauge and thought they could retract the cesium source back to the shielded position. The RSO's attempt to retract the source was successful. The RSO took a radiation reading 3 feet from the source and it was 0.14 millirem per hour. The gauge was placed in the transport case and will be taken to the licensee's storage area. The RSO stated they would contact the manufacturer to dispose of the gauge. No individual received an exposure due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I - 9805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-10-16
54936 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-09-28 | 2020-10-07 13:19 | 2020-10-07 | AGREEMENT STATE REPORT - RECOVERED MISCELLANEOUS RADIOACTIVE ITEMS The following was received from the Pennsylvania Bureau of Radiation Protection (BRP; the Department) via email: "On Sunday afternoon, September 28, 2020, the Department was notified of radioactive material found in a private residence being cleaned-out for an auction sale. BRP staff responded and found several sealed radium-226 sources and small quantities of uranium ore. The initial investigation revealed an additional nearby property also had radioactive material present. Staff inspected that property as well and discovered several more items. Owners of the houses were related and have passed away. HazMat responder's shoes and gloves were surveyed on September 28, with no removable contamination noted. Ambient dose rates were in the microrem to few millirem per hour range around the sources. The houses were secured that evening and further investigation continued through the week. As of October 7, 45 items have been collected. Note, some items contain multiple exempt sources, pieces of rock, or bottles of circa 1920 quack medical tablets with radium-226. These items include: old quack radium consumer products, exempt check sources, vacuum tubes, a military compass, luminous tubes and deck markers, cans of thorium oxide, and various other items containing radium-226, thorium-232, strontium-90, carbon-14, and natural uranium in quantities ranging from less than a microCurie to a few milliCuries (in the case of two radium-226 sources). An empty 5 gallon pail with 'US Radium, Bloomsburg PA' stenciled on the side was found. It is believed this old manufacturer of radium products, and now an EPA Superfund site, is where these items originated from. No exposure to members of the public above the public dose limit of 100 mrem per year are believed to have occurred during discovery and recovery, as the higher activity sources were within lead containers when found. BRP will update this event if more information becomes available. A complete inventory and activity calculations are underway for proper disposal." Event Report ID No: PA200020 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-10-15
54935 | 0 | Grand Gulf | 1 |  |  | [1] GE-6 | 2020-10-06 13:07 | 2020-10-07 10:25 | 2020-10-07 | FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee informed the NRC Resident Inspector. | 83 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2020-10-07
54934 | 0 | Harris | 1 |  |  | [1] W-3-LP | 2020-10-06 10:06 | 2020-10-06 20:16 | 2020-10-06 | FITNESS FOR DUTY REPORT A non-licensed employee supervisor had a confirmed positive during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2020-10-06
54933 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2020-10-05 | 2020-10-06 15:30 | 2020-10-06 | AGREEMENT STATE REPORT - REPORT OF LOST STATIC ELIMINATOR The following is a summary of an email from the state of Minnesota: During a lab reorganization, the licensee determined that a static eliminator (Po-210; 6 mCi; Model NRD P-2063; S/N A2LU743) was lost. The licensee presumes it was mistakenly disposed of as electronic waste and sent to a recycling facility some time in August of 2020. The licensee is examining their program to identify process improvements that would prevent future loss of material. The licensee has notified the recycling facility. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2020-10-14
54932 | 0 | Browns Ferry |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-08-06 17:49 | 2020-10-05 14:25 | 2020-10-05 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF AN INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On August 6, 2020, at approximately 1749 CDT, Browns Ferry Nuclear Plant (BFN), Unit 2 experienced a loss of Reactor Protection System (RPS) Bus 2A. Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolated in response to this event. The PCIS isolations caused the initiation of Standby Gas Treatment (SBGT) trains A, B, and C, and Control Room Emergency Ventilation (CREV) subsystem A. Unit 2 declared RCS leakage detection instrumentation inoperable and entered TS LCO 3.4.5 condition A, B, and D with required action D.1 to enter LCO 3.0.3 immediately. Unit 2 entered TS LCO 3.0.3 with required actions to be in Mode 2 within 10 hours, Mode 3 within 13 hours, and Mode 4 within 37 hours. Upon investigation, it was discovered that an age-related overheating condition resulted in the failure of the 2A RPS Motor Generator (MG) set, causing the feeder beaker from the 2A 480v Remote Motor-Operated Valve distribution board to trip. On August 6, 2020, at approximately 1808 CDT, Operations personnel commenced restoration of Unit 2 to normal after transferring 2A RPS to its alternate power supply. The 2A RPS MG Set drive motor was replaced on August 24, 2020. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel (RV) Low Water Level or Drywell High Pressure. Plant conditions which initiate PCIS Group 3 actuations are RV Low Water Level or Reactor Water Cleanup Area High Temperature. Plant conditions which initiate PCIS Group 6 actuations are RV Low Water Level, High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation. Plant conditions which initiate PCIS Group 8 actuations are Reactor Vessel (RV) Low Water Level or Drywell High Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "All affected safety systems responded as expected. There were no safety consequences or impact to the health and safety of the public as a result of this event. This event was entered into the Corrective Action Program as Condition Report 1628707. The NRC Resident Inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-10-05
54931 | 0 | Browns Ferry |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-08-06 01:28 | 2020-10-05 13:51 | 2020-10-05 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF AN INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of an emergency service water system component that does not normally run and which provides an ultimate heat sink. "On August 6, 2020, at approximately 0128 CDT, the A3 Emergency Equipment Cooling Water (EECW) pump received an auto-start signal while performing Post-Maintenance Testing (PMT) on the 3C Core Spray pump. Normally, the involved EECW pump would be started prior to testing to prevent an auto-start; however, in this case the pump was not running prior to the test. When the 3C Core Spray pump breaker was closed while in the test position, an unanticipated actuation of the A3 EECW pump occurred. Work was stopped and the workers reported to the Control Room to evaluate the condition. Based on a review of this event, individuals involved were coached on understanding system response prior to performing work. "The A3 EECW pump responded in accordance with the plant design. No other plant equipment was affected during this event. There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for evaluation and resolution. Reference corrective action document CR 1628479. The NRC Resident Inspector has been notified of this event." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode3: Power Operation; FMode3: Power Operation | Non Emergency | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-10-05
54930 | 0 | Point Beach | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2020-10-03 09:13 | 2020-10-03 15:07 | 2020-10-03 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE "During a scheduled refueling outage, a walkdown inside containment to investigate leakage revealed a pressure boundary leak upstream of 1RC-526B, HX-1B Steam Generator Channel Head Drain. This location would be considered part of the reactor coolant system as defined under 10 CFR 50.2. As such, this event is being reported pursuant to 10 CFR 50.72 (b)(3)(ii)(A). Unit 1 is currently in mode 4. Repairs for the condition are being determined. "The NRC Resident Inspector has been notified." The leak rate was determined to be 0.138 gpm. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Degraded Condition |  |  |  | IMode1: Hot Standby; FMode1: Hot Shutdown | Non Emergency | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2020-10-03
54929 | 0 | Comanche Peak |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-09-30 08:15 | 2020-10-03 11:48 | 2020-10-03 | RADIATION MONITORS REQUIRED FOR EVENT ASSESSMENT OUT OF SERVICE FOR PLANNED MAINTENANCE "At time 0815 (CDT) on 09/30/20, Main Steamline Radiation Monitor 2-RUK-2325/2327 (Main Steam Line 2-01/2-03 Radiation Monitor) was removed from service for planned maintenance. "Compensatory measures were in place prior to removing the monitor from service to assure adequate monitoring capability available to implement the CPNPP [Comanche Peak Nuclear Power Plant] emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 radiation monitor serves as a backup with alarm function and Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL 2-01 and MSL 2-03. "With this radiation monitor non-functional, compensatory measures in place and the monitor not restored to service within 72 hours, the condition is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant (CPNPP) has assurance of steam generator integrity and fuel cladding integrity and there is negligible safety significance to the current condition with respect to the public health and safety perspective. "Corrective actions are being pursued to complete maintenance and restore 2-RUK-2325/2327 to functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-10-03
54928 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-10-02 08:30 | 2020-10-02 16:41 | 2020-10-02 | AGREEMENT STATE REPORT - PACKAGE RECEIVED BY LICENSEE EXCEEDS SURFACE RADIATION DOSE LIMITS The following information was received from the Commonwealth of Massachusetts via email: "A shipment of radioactive material in the form of 5 packages, each containing 555 GBq of Americium/Beryllium, was delivered to QSA Global, Inc. at 0830 [EDT] on October 2, 2020, each of which exceeded regulatory package dose rate limits. All 5 packages exceeded the surface dose rate limit of 200 mrem/hour, the highest of which was 295 mrem/hour and the lowest 220 mrem/hour. Each package was labeled as Yellow III; TI 7. The transport index was also exceeded with a range of 13 mrem/hr at 1 meter for the lowest and 15 mrem/hr at 1 meter for the highest. "It was reported that the final delivery carrier, [a common carrier], was notified of the event at 1430 [EDT] on October 2, 2020. The shipper, Weatherford International, LLC, at 7504 Benbrook Parkway, Benbrook, Texas, 76126, was also notified. "The cause of the event is under investigation by the licensee. Further information from the Massachusetts Radiation Control Program will be forthcoming." The Commonwealth will be notifying NMED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-10-12
54927 | 0 | Millstone |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2020-10-02 09:45 | 2020-10-02 12:35 | 2020-10-02 | SECONDARY CONTAINMENT INOPERABLE "At 0945 hours [EDT] on 10/02/2020, with Millstone Unit 3 in Mode 4, Operations discovered a door in the Secondary Containment boundary blocked open. Investigation determined the door was blocked open at 1842 [EDT] on 10/01/2020, rendering Secondary Containment inoperable. The door was closed at 1002 [(EDT) on 10/02/2020], restoring Secondary Containment to operable status. "Since Secondary Containment was rendered inoperable, Dominion Energy is reporting this as a condition that could have prevented the fulfillment of the safety function to control the release of radioactive material and mitigate the consequences of an accident. This condition is being reported as an eight hour report pursuant to 10 CFR 50.72 (b)(3)(v)(C) and (D). There was no release of radioactivity to the public. "The NRC Senior Resident Inspector has been notified." With the door blocked open, the plant was in a 24-hour shutdown action statement. The state of Connecticut and local towns were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Pot Uncntrl Rad Rel | Accident Mitigation |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | Non Emergency | 1 | CT | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2020-10-02
54926 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-09-04 | 2020-10-01 12:03 | 2020-10-01 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The Florida Bureau of Radiation Control reported the following via email: "The RSO [Radiation Safety Officer] notified the BRC [Bureau of Radiation Control] by mail that a leak test performed on this source [217.6 microCurie Cs-137 e-vial] resulted in greater than 0.005 microCi of the acceptable removable contamination. After determination, the source was sealed within the shielded e-vial container using silicone. The outer shielded container had no removable contamination. The sealed container was then wrapped in plastic. The outer plastic also had no removable contamination. The area was evaluated for signs of removable contamination with no results above background. The licensee intends to dispose of this source through a licensed radioactive waste disposal company." Florida Event Number: FL20-113 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-10-09
54925 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-10-01 | 2020-10-01 12:10 | 2020-10-01 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following was received from the state of Texas (the Agency) by email: "On October 1, 2020, the Agency was notified by the licensee's radiation safety officer (RSO) that a Troxler model 3430 moisture\density gauge containing a 40 milliCurie americium-241 source and an 8 milliCurie cesium-137 source was stolen from an employee's truck. The truck was parked at the employee's residence and when they came out to go to the job site they found both chains securing the gauge in the truck were cut and the gauge was missing. The RSO stated they had notified local law enforcement and the fire department. "The RSO stated their management group was searching social media looking for the gauge. The RSO stated they currently have people in the field looking for the gauge. The RSO stated the gauge operating arm was locked. The gauge would not create an exposure risk to any individual unless the lock was cut off the operating arm and the cesium source exposed. Additional information will be provided as it is received in accordance with SA-300." TX Incident # 9803. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-10-09
54924 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2020-09-30 15:00 | 2020-09-30 16:54 | 2020-10-01 | <br><br>EN Revision Imported Date : 10/2/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - VEHICLE RAN OVER PORTABLE MOISTURE GAUGE This is a summary of a call from the state of Mississippi Division of Radiological Health via phone: A portable moisture density gauge, containing 9 mCi Cs-137 and 44 mCi Am-241/Be sealed sources, was run over by a vehicle at a construction site in Clinton, MS. No visible damage of the gauge was identified. The licensee's survey results were normal for a retracted source. The gauge was returned to a local office and the state will also perform a survey once they are on site. There was no exposure to personnel. * * * UPDATE ON 10/01/2020 AT 1957 EDT FROM ART ROBERT SIMS TO BRIAN P. SMITH * * * The updated report was sent from the state of Mississippi Division of Radiological Health via email: "Off Norrell Road, off MS. 1-20 Clinton Mississippi Continental Tire Construction site off-ramp, the gauge user was on a noisy construction site with heavy equipment and ear protection requirements. The gauge user was taking a measurement and the high elevated Rubber Tire Roller used to pack asphalt did not see the gauge user. The gauge user yelled at him trying to get him to stop, but due to the noise and the driver not seeing him, the rubber tire roller ran over edge of Humboldt Moisture Density Gauge model 5001 Ser. No. 9624, only damaging the outer housing. The RSO was contacted, used a survey meter Troxalert Model 01754 calibrated 01/10/2020, and received readings of 6 mR/hr which are consistent with previous readings that indicate the source was in the shielded position. The gauge is at the RSO's office and is being sent to Humboldt for electronics and housing repair and a wipe test. The incident was an accident. No violations could be issued to the licensee due to gauge user being present taking moisture readings and the driver of the rubber tire packer just did not see him." Mississippi Event Number MS-200003 Notified R4DO (Silva), NMSS Events Notification (e-mail) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2020-10-08
54923 | 0 | Quad Cities |  | 2 |  | [1] GE-3,[2] GE-3 | 2020-07-22 10:30 | 2020-09-29 21:19 | 2020-09-29 | OPRM COUNT SETPOINT DISCREPANCY "On July 22, 2020, at 1030 CDT, it was discovered that the as-found Unit 2 Oscillation Power Range Monitor (OPRM) Maximum Confirmation Count Setpoint did not match the values in the Quad Cities Unit 2 [Core Operating Limits Report] (COLR) per TS SR 3.3.1.3.3. All Unit 2 OPRMs were declared inoperable. Due to this inoperability, the OPRM system was in a condition that could have prevented the fulfillment of a safety function; therefore, this condition is being reported per 10 CFR 50.72(b)(3)(v)(D). There were no other Technical Specification or safety systems inoperable at the time of this event. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." Quad Cities Unit 2 returned their OPRMs to operable on July 23, 2020, at 1210 CDT, following a setpoint adjustment. In addition, during a more recent meeting between station personnel and the NRC resident inspectors, feedback was provided that brought to the station management's attention that they needed to make the required 50.72 notification as a result to this past inoperability. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-09-29
54922 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-09-29 07:30 | 2020-09-29 11:33 | 2020-09-29 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The Ohio Department of Health reported the following via email: "On September 29, 2020, at 0948 EDT, the licensee reported the theft of a moisture-density gauge from their location, Cincinnati, Ohio. Due to heavy rain the evening of September 28, a technician left the gauge locked in a company truck outside the secure facility instead of moving the gauge inside the secure facility as required. At approximately 0730 on September 29, the locked box containing the gauge was discovered broken into and the gauge and storage container missing. "The gauge is a Troxler model 3411-B with a 8 mCi Cs-137 and a 40 mCi Am-241/Be sources. "A report was filed with the Cincinnati police." Ohio Item Number: OH200009 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-10-07
54921 | 0 | North Anna | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2020-09-28 16:00 | 2020-09-29 10:21 | 2020-09-29 | FITNESS FOR DUTY REPORT A non-licensed Dominion Energy supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | Non Emergency | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2020-09-29
54920 | 0 | Callaway | 1 |  |  | [1] W-4-LP | 2020-09-29 | 2020-09-29 05:23 | 2020-09-29 | SAFEGUARDS REPORT Due to an equipment failure a vulnerability occurred. Licensee Security has implemented compensatory measures. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Safeguards Reports |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | Non Emergency | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2020-09-29
54919 | 0 | Millstone |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2020-09-28 15:45 | 2020-09-28 16:30 | 2020-09-28 | SAFEGUARDS REPORT - PHYSICAL SECURITY "An event involving plant access authorization is being reported. Specific details are not for public disclosure. Appropriate action has been taken." The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | Safeguards Reports |  |  |  | IMode3: Power Operation; FMode3: Power Operation | Non Emergency | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2020-09-28
54918 | 0 | Sequoyah | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-09-28 11:43 | 2020-09-28 14:39 | 2020-09-28 | OFFSITE NOTIFICATION - OIL SPILL "On 9/28/20 at 1143 EDT, a notification to the National Response Center was made after discovery of a visible oil sheen on the waters of the U.S. (Sequoyah's side of the intake forebay skimmer wall at the Essential Raw Cooling Water (ERCW) building). The source was an oil bucket that overflowed with rain at the ERCW pumping station. Efforts are in progress to eliminate all other potential sources of oil at the station that could be released to the environment. Estimate of volume spilled is less than one quart. "The following agencies have also been notified: - EPA Region 4 - Tennessee Emergency Management Agency (TEMA) - Tennessee Department of Environment and Conservation (TDEC). "Cleanup is in progress. Measures to prevent recurrence are being taken. "This is a four-hour notification, non-emergency for a notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-09-28
54917 | 0 | Peach Bottom | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2020-09-28 05:00 | 2020-09-28 05:02 | 2020-10-09 | <br><br>EN Revision Imported Date : 10/12/2020<br><br>EN Revision Text: LOSS OF TECHNICAL SUPPORT CENTER VENTILATION SYSTEM DUE TO PLANNED MAINTENANCE: "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the planned maintenance affects the functionality of an emergency response facility. Planned maintenance activities are being performed on 09/28/20 to the Peach Bottom Atomic Power Station (PBAPS) Technical Support Center (TSC) HVAC. The work includes replacement of supply fan and roof-top unit. Work is scheduled to complete on 10/11/20. "If an emergency is declared requiring PBAPS TSC activation during this period, the PBAPS TSC will be staffed and activated using existing Emergency Preparedness (EP) procedures. If the PBAPS TS becomes uninhabitable due to radiological, or other conditions, the TSC Station Emergency Director will relocate the TSC staff to an alternate location in accordance with EP procedures. The Emergency Response Organization team has been notified of the maintenance and the possible need to relocate during an emergency." The NRC Resident Inspector will be notified by the licensee. * * * UPDATE ON 10/9/20 AT 1234 EDT FROM BRIAN BAILEY TO ANDREW WAUGH * * * "An eight-hour, non-emergency notification for a loss of Emergency Assessment Capability was made on 9/28/20 under Event Notification 54917 for planned maintenance activities to the Peach Bottom Atomic Power Station (PBAPS) Technical Support Center (TSC) ventilation system. This event was reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the planned maintenance affected the functionality of an emergency response facility. "This update to EN 54917 is to notify applicable stakeholders that, following satisfactory completion of the planned supply fan and roof-top unit replacement work, the PBAPS TSC ventilation system has been returned to service with no remaining work or outstanding deficiencies related to this work." The licensee has notified the NRC Resident Inspector. Notified R1DO (Lally). | 84 | 100 | 0 | 84 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-09-28
54916 | 0 | Callaway | 1 |  |  | [1] W-4-LP | 2020-09-27 02:03 | 2020-09-27 05:08 | 2020-09-27 | AUTOMATIC REACTOR TRIP "At 0203 [CDT] on September 27, 2020 the plant was in Mode 1 at 98 percent power when a turbine trip/reactor trip [from a generator trip signal] occurred. All systems responded as expected. A Feedwater Isolation signal was received due to the reactor trip with RCS average temperature less than 564 degrees Fahrenheit. The Auxiliary Feedwater system started on a valid actuation signal to restore and maintain steam generator levels. The plant is being maintained stable in Mode 3 with no complications. The NRC Resident Inspector has been notified of the reactor trip." All control rods fully inserted from the reactor trip signal, and decay heat is being removed via the Auxiliary Feedwater and Steam Dump Systems. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-09-27
54915 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-09-26 | 2020-09-26 11:13 | 2020-09-26 | AGREEMENT STATE REPORT - VEHICLE CARRYING RADIO-PHARMACEUTICALS INVOLVED IN ACCIDENT The following was received from the state of Florida via email: "A transport vehicle carrying radio-pharmaceuticals was rear-ended at the intersection of County road 39 and State road 62 in Parrish Florida. Duette Fire rescue is on scene with a representative from the pharmaceutical company. The shipping papers indicate 227 mCi of Tc-99m but the driver had already made several stops and may have additional radioactive waste materials not on manifest. Cardinal Health Sarasota has taken custody of all packages." Florida Incident Number: FL20-110. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-10-05
54914 | 0 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2020-09-25 | 2020-09-25 19:59 | 2020-09-25 | PART 21 REPORT - CONTINUOUSLY ENERGIZED EATON D26 RELAYS The following is a summary of the report provided by the notifier: "Pursuant to 10 CFR 21.21(d)(3)(ii), Nutherm International, Inc. is providing written notification of the identification of a potential defect found in Eaton D26 relays. "On July 23, 2019, Eaton Corporation released a letter, 'Update on Reports of Size 1 & 2 AC Contactors that Failed to Open When Deenergized'. This letter described a condition observed on AC contactors after being energized for a long period of time without being 'cycled'. Eaton also stated that this would occur in only a few isolated cases in continuously energized applications. "The cause of the problem is the coating on each of the steel laminations in the cores of these devices. This steel is coated with an organic insulating varnish classified as C3. This coating, when heated for a long time period, can migrate from the lamination surfaces to the edges at the area between the separate core pieces (referred to as armatures and magnets). This substance is sticky and can potentially hold the core pieces together with enough strength to overcome the forces of the device's return springs." Potentially impacted components may include: Freedom contactors NEMA Size 00 through 5 A200 contactors NEMA Size 00 through 4 D15 Relays D26Relays AR Relays (AC Only) BF Relays (AC Only and including NBF relays) Vacuum contactors NEMA Size 4 Nutherm identified that they had supplied the Eaton relays to the following facilities: Dresden Nuclear Station Quad Cities Nuclear Station Palisades Nuclear Power Plant HB Robinson Steam Electric Plant Point Beach Nuclear Plant If you have any questions please contact Adrienne Smith at 618-244-6000, extension 3034, email adrienne.smith@nutherm.com or Kyle Mitchell at 618-244-6000, extension 3097 email kyle.mitchell@nutherm.com. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-09-25
54913 | 0 | FitzPatrick | 1 |  |  | [1] GE-4 | 2020-09-25 12:38 | 2020-09-25 15:28 | 2020-09-25 | FITNESS FOR DUTY REPORT A non-licensed contract supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Refueling; FMode1: Refueling | Non Emergency | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2020-09-25
54912 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-09-16 | 2020-09-25 13:59 | 2020-09-25 | AGREEMENT STATE REPORT - LEAKING SOURCE The following is a summary of the email received from the State of Ohio: The licensee discovered that one of their Electron Capture Detectors (Model: G2397A; S/N: U23974; Source: Ni-63 0.015 Ci) was leaking during a routine leak test. The source has been transferred for disposal. Item Number: OH200008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-10-05
54911 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-08-24 | 2020-09-25 12:20 | 2020-09-25 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received from the Pennsylvania Bureau of Radiation Protection via email: "On August 24, 2020, the licensee identified a failure of the shutter assembly and indicator on one of its Valmet Multi-Filler Module, Serial Number 0022 containing 20 mCi of lron-55. The shutter had failed closed. The gauge was immediately removed from service. The manufacturer was contacted, and the broken shutter mechanism was removed and replaced on August 26, 2020. The shutter mechanism was then tested and confirmed as operating properly. No exposures were resulted from this event." Event Report ID No.: PA200018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-10-05
54910 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2019-07-31 10:28 | 2020-09-24 12:57 | 2020-09-24 | AGREEMENT STATE REPORT - CAMERA SOURCE UNABLE TO RETRACT The following was reported by the Virginia Office of Radiological Health, via email: "On August 26, 2019, the Virginia Office of Radiological Health (ORH) received an incident report from the licensee, MISTRAS GROUP, Inc. The source, 66 curies of Ir-192, could not be retracted to its shielded position during radiographic work. The radiographic work involved inspecting a water tank located in an open space. The incident occurred on July 31, 2019, at about 1028 EDT at a temporary jobsite located in White Post, Virginia. The incident occurred because a magnetic stand that was utilized to support the source tube fell during an exposure, creating a kink in the source tube and preventing full retraction back to the shielded position. The radiography crew immediately established a new boundary, notified the Radiation Safety Officer (RSO) and customer, and relocated all workers outside the boundary area. A radiation survey was performed immediately at the new boundary and the measurement did not exceed 2 mR in any one hour. The site was supervised by the radiography crew until the RSO arrived at the scene and repositioned the source back to its shielding position safely. The pocket dosimeters indicated that the RSO, the radiographer, and assistant radiographer received 28 mrem, 20 mrem, and 10 mrem, respectively. In addition, the whole body dosimeters were sent to Landauer for analysis and no significant radiation exposures were reported to the RSO, Radiographer, and Assistant Radiographer. "On August 28, 2019, the ORH inspector conducted a reactive inspection and it was found that the root causes of the incident were identified properly by the licensee and corrective actions, including training on procedures, on radiographic techniques, and on set up for that particular type of radiography work were discussed with the radiographer. The ORH determined that this incident is closed." The report from Virginia also stated: "This incident was reported to the NRC through NMED on August 29, 2019 as if it was a 30-day notification requirement. However, the 2020 Virginia IMPEP review team discovered that it should have been classified as a 24-hour notification requirement. Accordingly, this report is being sent to correct the error." Event Report ID No: VA-19004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2020-10-02
54909 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-09-24 09:30 | 2020-09-24 12:41 | 2020-09-24 | AGREEMENT STATE REPORT - LOST/STOLEN TROXLER GAUGE The following is a summary of information reported by the Florida Department of Health via email: Terracon Consultants reported a Troxler 2440 gauge was stolen from a truck while the truck was parked at a residence in Brandenton, Florida. The gauge was stolen around 0930 EDT on 9/24/2020. The gauge was secured with two chains and two locks by the driver of the truck. The local police department has been notified. The gauge contained a 8 mCi Cs-137 source (S/N: 75-1841) and a 40 mCi Am241:Be source (S/N: 47-15958). Florida Incident Number: FL20-109 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-10-02
54908 | 0 | Grand Gulf | 1 |  |  | [1] GE-6 | 2020-09-24 02:58 | 2020-09-24 06:31 | 2020-09-24 | EMERGENCY SIREN INADVERTENTLY ACTUATED "On September 24, 2020, at 0258 CDT, Grand Gulf Nuclear Station (GGNS) was notified that one Emergency Notification Siren located on US Hwy 61 had actuated. Claiborne County was informed that no emergency exists at GGNS. The alarming siren has since been secured. Notification is being provided to the NRC in regards to the potential for media inquiry. "The licensee informed the NRC Resident Inspector." | 83 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-09-24
54907 | 0 | Fort Calhoun | 1 |  |  | (1) CE | 2020-09-23 15:28 | 2020-09-23 18:56 | 2020-09-23 | OFFSITE NOTIFICATION - PRESS RELEASE FOR A FIRE IN CONTAINMENT "At 1528 CDT, a fire was reported in containment. Fire was extinguished using a portable fire extinguisher by dedicated fire watch. Offsite fire departments responded at 1541 CDT and the fire was confirmed extinguished at 1601 CDT. There were no injuries reported. The state Fire Marshal of Nebraska has been notified. There was no release of radioactivity or hazardous materials. "The following statement is planned to be released to the media: "A small industrial fire broke out this afternoon at OPPD's Fort Calhoun Station, the decommissioning nuclear plant just south of Blair, Nebraska. It had been put out by fire extinguishers before firefighters arrived. No release of radioactivity occurred. All employees and contractors are accounted for and safe. "Based on our preliminary investigation, the fire appears to have been caused by a torch used for cutting. Firefighters are using a thermal gun to identify any potential remaining hot spots. "The plant is undergoing decommissioning and all spent nuclear fuel is fully secured in industry-standard dry cask storage, located away from the site of today's fire. The public remains safe and the facility remains secure. All work at the site is on a temporary hold. Safety remains our highest priority. "OPPD will provide additional information as it becomes available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode1: Defueled; FMode1: Defueled | Non Emergency | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-09-23
54906 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-09-22 | 2020-09-23 14:58 | 2020-09-23 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received via email from the Illinois Emergency Management Agency (The Agency): "The Agency was notified on 9/23/20 that a high dose rate afterloader (HDR) administration resulted in a medical event on 9/22/20 at the Western Illinois Cancer Treatment Center in Galesburg, IL. The licensee states no untoward effects are expected of the patient. Agency staff will respond and evaluate on 9/24/20. The Agency was contacted by an authorized medical physicist and radiation safety officer for Western Illinois Cancer Treatment Center in Galesburg (RML IL-01902-01), to report a medical event that occurred the previous day on September 22, 2020. Reportedly, a patient was prescribed a 30 Gy therapeutic dose to the vaginal cuff, to be delivered over a series of (5) fractionated 6 Gy administrations. Two of the 6 Gy administrations had already been performed on 9/15/20 and 9/18/20 without issue. The patient arrived for the third fractionated dose of 6 Gy on 9/22/20. An unnamed nurse was present as well. It is unclear if an authorized medical physicist was physically present at time of administration. Rather than delivering the dose through the vaginal cavity, the HDR applicator was inserted into the rectal cavity. This was not noticed until after the treatment was delivered. Based on the information currently available, the written directive specified a 6 Gy fraction to be delivered to the vaginal treatment area. The dose delivered was 1.46 Gy. This meets the reportable criteria in 32 Ill. Adm. Code 335.1080(a)(1) for an underdose. Additionally, had the administration gone as prescribed; the rectum would have only received (for 50% of the volume) 1.53 Gy per fraction. In this administration, the dose to the rectum (50% of volume) was 3.94 Gy. This also meets the reportable criteria for an overexposure. The format of this report provides data in the context of an overexposure. The language in the written directive will be reviewed, as well as procedures, personnel present, treatment plan and post-plan calculations on September 24, 2020. Reporting timeliness appears appropriate at this time. A written report will be required to the Agency by October 7, 2020. The referring physician has been notified. The patient is being advised today, which at this time appears to be in accordance with applicable regulations. This report will be updated as additional information becomes available." Illinois Item Number: IL200017. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-10-01
54905 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-09-14 | 2020-09-21 14:29 | 2020-09-21 | AGREEMENT STATE REPORT - LOSS OF YELLOW II PACKAGE CONTAINING APPROXIMATELY 61 mCi OF LIQUID Tl-201 The following is a synopsis of the report received via email from the Illinois Emergency Management Agency (Agency): The Agency was contacted the morning of 9/14/20 by the licensee to report a Yellow-II package containing approximately 61 mCi of Tl-201 had not arrived at its final destination. There is no reason to suspect intentional diversion or criminal activity. The 12 inch x 6 inch x 6 inch package was labeled Radioactive Yellow-II with a transport index of 0.4 and was shipped via a commercial carrier. The package contained six shielded vials of diagnostic radiopharmaceutical liquid thallium-201. It was shipped from the licensee address on Tuesday, 9/8/20 with an assay activity of 225 mCi. The package was expected to arrive at the final destination, but as of 1600 CDT on Friday, 9/11/20, the package had not reported any movement after reaching the commercial carrier hub at Memphis, TN. As a result, the licensee contacted the recipient, as well as the radiation safety officer of the commercial carrier. The licensee contacted the Agency to report the package as lost. The last known location remains as the commercial carrier hub. No updates were available as of 9/21/20. The Tl-201 was shipped in a shielded container and does not represent a significant exposure hazard. The remaining activity as of 9/21/20 is 12 mCi. Unshielded, this dose would give rise to about 1.1 mR/hour at one foot. This quantity of material is over the NRC reporting requirement and is being reported within the required 30 day timeline. Illinois Item Number: IL200015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-09-29
54904 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-09-16 | 2020-09-16 18:48 | 2020-09-16 | AGREEMENT STATE REPORT - CONSTRUCTION GAUGE RUN OVER BY CONSTRUCTION VAN The following was received from the Arizona Department of Health Services (The Department) via email: "The Department received notification from the licensee that a construction vehicle ran over a portable gauge. The gauge is a Troxler 3430, Serial Number 21871, containing approximately 8 milliCuries of Cesium-137 and 40 milliCuries of Americium-241:Beryllium. The Department has requested additional information and continues to investigate the event." Arizona Event No. 20-018. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-09-24
54903 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2020-09-16 13:00 | 2020-09-16 18:00 | 2020-09-16 | AGREEMENT STATE REPORT - INCORRECT RADIONUCLIDE ADMINISTERED TO A PATIENT The following was received from the state of Utah, Division of Waste Management and Radiation Control, via email: "At approximately 1300 (MDT), on September 16, 2020, a Nuclear Medicine Technician injected 9.5 mCi of Tc-99 Sestamibi into the wrong patient. The prescribed radiopharmaceutical to be administered was Tc-99m MAA. The dose of Tc-99 Sestamibi was intended for a patient scheduled earlier in the day that did not show up for their appointment. The Nuclear Medicine Technician failed to swap out the Tc-99 Sestamibi for Tc-99m MAA for the 1300 MDT patient." State Event Report No.: Will be provided in a follow up report. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2020-09-24
54902 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2020-08-11 | 2020-09-16 17:16 | 2020-09-16 | AGREEMENT STATE REPORT - LOST I-125 SEED The following information was obtained from the state of New York via facsimile: "On September 9, 2020, the Department [New York State Department of Health] was notified of a missing I-125 localization seed (Best Medical International, Inc., Model 2301, Activity: 251 microCuries) at Roswell Park Cancer Institute in Buffalo, New York. "In this incident two seeds were placed into a patient on 8/10/2020 and removed on 8/11/2020. Removal of the seeds from the patient was confirmed by x-ray in the operating suite. The seeds were then sent to the Frozen Section Room for margin check then sent to the Grossing Room in Pathology. After slicing in the Grossing Room, the specimen was x-rayed again and only one seed was visualized. Pathology believed that the seed was in the Frozen Section Room and immediately searched and surveyed both the Frozen Section Room and the Grossing Room, then notified the RSO [radiation safety officer] when the seed was not found. The RSO and an assistant surveyed the OR suite, Frozen Section Room and Grossing Room. Trash from all three locations was surveyed and after three days radioactive waste was surveyed and examined but the seed was still not recovered. "In the time between the incident and reporting to the Department, searches and surveys were performed in Surgery, Pathology, Radiation Safety and Environmental Service areas. In addition, trash, regulated medical waste, and radioactive waste were surveyed and inspected. The seed has not been recovered. "Ultimate disposition of the source is unknown and it is possible that the source may still be recovered." New York Event Report ID No.: NYDOH-20-04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2020-09-24
54901 | 0 | Westinghouse Electric Corporation |  |  |  | Uranium Fuel Fabrication | 2020-09-15 09:00 | 2020-09-16 08:50 | 2020-09-16 | UNPLANNED MEDICAL TREATMENT "On September 15, 2020, at approximately 0900 EDT, a Westinghouse employee performing routine work in the Conversion Decontamination Area was exposed to nitric acid on the bottom of the right foot due to an issue with his protective footwear. The nitric acid came in contact with the employee's footwear impacting the bottom of the right foot. Appropriate treatment for exposure to nitric acid was provided by onsite medical response staff, and per procedure the employee's foot was wrapped in plastic, and the employee was transported to an offsite medical facility accompanied by plant health physics personnel for evaluation. "Contamination was detected on the exposed area of the employee's skin during [Health Physics] surveys. Direct survey results for the bottom of the right foot were 1700 dpm/100 cm2 [disintegrations per minute per 100 square centimeters] alpha. Surveys for direct contamination were also performed at the hospital before and after cleaning the exposed area and the contamination level remained the same at 1700 dpm/100 cm2 alpha. All smear results of the exposed area were below clean area limits (less than 200 dpm/100 cm2). Contamination surveys were performed on the ambulance and at the hospital and all results were below clean area limits indicating no spread of contamination during care for the employee. All potentially contaminated materials associated with the issue were collected and returned to [Commercial Fuel Fabrication Facility] (CFFF) for disposal. The operator was provided with over the counter medication and released to go home. "A leaking valve was identified as the source of the nitric acid, which was promptly isolated and left in a safe state. There was no release to the environment and the liquid accumulation of nitric acid on the floor has been removed and the floor cleaned. "The Columbia plant is a licensed Part 70 facility subject to 10CFR70 Subpart H, and this event does not challenge the performance requirements of 10 CFR 70.61 as analyzed in the Integrated Safety Analysis." The isotope involved was U-235. The hospital that performed medical treatment was Prisma Health. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Med Treat Involving Contam | [9 empty] | Non Emergency | 2 | SC | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2020-09-16
54900 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-09-14 | 2020-09-16 07:40 | 2020-10-08 | <br><br>EN Revision Imported Date : 10/9/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - LOST AND FOUND DEVICE The following information was submitted by the Texas Department of Health Services (the Agency) via email: "On September 15, 2020, at 1700 CDT, the Agency was notified by the licensee's radiation safety officer (RSO) that one of their technicians had left a Troxler model 4640B density gauges at a job site overnight. The technician had completed their work on September 14, 2020, and left the job site after completing their paperwork, but failed to store the device into their truck. The RSO stated the gauge handle was locked and did not believe any individual would receive an exposure. The RSO stated the device contains two cesium-137 sources, but did not know the activities. The manufacturer's website states the activity to be 8 (+ or - 1) milliCuries. The licensee's license states a device source cannot exceed 9 milliCuries. The RSO stated they had technicians out searching for the gauge. At 1736 CDT, on September 15, 2020, the RSO contacted the Agency and reported the gauge had been recovered. He could not provide any additional information. Additional information has been requested. If during the investigation of this event it is determined that an individual could have been exposed, the Agency will submit an update to this report. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: 9797 * * * UPDATE ON 10/08/2020 AT 0749 EDT FROM ART TUCKER TO OSSY FONT * * * The following update was received from the Agency via email: "On October 7, 2020, the Agency was notified by the licensee that the gauge only had one source and not two as first reported. The licensee stated it thought it had two sources because of the way it calculates the density of the top two inches. The licensee stated it has only one source, but two detectors so it can calculate thin lift density. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Josey) and NMSS Events Notification and ILTAB via email. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-24
54899 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-09-01 | 2020-09-15 12:08 | 2020-09-15 | AGREEMENT STATE REPORT - UNDERDOSE DURING MEDICAL TREATMENT The following information was received via e-mail from the Texas Department of State Health Services (the Agency): "On September 14, 2020, the Agency was notified by the licensee's radiation safety officer (RSO) that they had discovered a medical event [occurred September 1, 2020] involving a Varian high dose rate remote afterloader (HDR) unit had occurred. The RSO reported that a patient was to receive two boost treatments using the HDR unit. While setting up for the second treatment, the licensee noted the length of source catheter tube used in the first treatment was incorrect, therefore only part of the intended target was treated. The RSO stated the patient and physician were both notified of the event and that the current plan is to perform an additional treatment to the area that was under exposed in the first treatment. The RSO stated they did not expect any adverse effects to the patient. The Agency has requested additional information on the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9796 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-23
54898 | 0 | Catawba | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-09-12 17:48 | 2020-09-12 21:12 | 2020-09-12 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At 1748 EDT on September 12, 2020, Unit 2 emergency core cooling system (ECCS) leakage outside containment was determined to exceed the long-term habitability dose analysis for the Catawba Nuclear Station Technical Support Center (TSC) under bounding conditions. Repair options to arrest the leakage and restore functionality of the TSC are currently being evaluated. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to the alternate facility. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable In accordance with 10 CFR 50.72(b)(3)(xiii) because the discovered condition of the TSC affects the functionality of an emergency response facility. "There is no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." This same condition was reported under EN #54887. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-09-12
54897 | 0 | Palisades | 1 |  |  | [1] CE | 2020-09-11 19:30 | 2020-09-11 22:54 | 2020-09-11 | DEGRADED CONDITION "At 1930 EDT, on September 11, 2020, Palisades Nuclear Plant was conducting ultrasonic data analysis from reactor vessel closure head in-service inspections. During this analysis, signals that display characteristics consistent with primary water stress corrosion cracking were identified in head penetration 34. No leak path signal was identified during ultrasonic testing. "The plant was in cold shutdown at 0% power and in Mode 6 for a refueling outage at the time of discovery. Repair actions will be completed prior to plant startup from the outage. "This condition has no impact to the health and safety of the public. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A) for degradation of a principal safety barrier. This is the only indication that is currently present, however, if additional indications are found, they will also be repaired prior to the plant startup. "The licensee notified the NRC Senior Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Degraded Condition |  |  |  | IMode1: Refueling; FMode1: Refueling | Non Emergency | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2020-09-11
54896 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2020-09-09 16:29 | 2020-09-11 13:56 | 2020-09-11 | AGREEMENT STATE REPORT - WATER LOSS FROM SOURCE STORAGE POOL The following is a synopsis of the report received from the State of Nebraska Division of Radioactive Materials via phone: The licensee reported that while they were responding to a product jam alarm they discovered some water on the floor by the source storage pool. In reviewing the control system operation log, the operators found the system had responded to a low water level by opening the make-up water valve. This is a normal system occurrence due to evaporation from the pool. The make-up valve did not close upon reaching the normal water level, so level in the pool continued to rise. Level reached the high water alarm point which is at the top of the pool. The drain valve opened at the high water alarm point causing level to drop, but some water had already overflowed from the pool onto the surrounding floor. Level continued to lower and upon reaching the low level setpoint the system correctly responded by closing the drain valve and reopening the make-up valve. The level control system then responded correctly and the make-up valve closed when water level returned to normal. The irradiator facility has replaced the level switches and updated the preventative maintenance frequency for the valves and switches to prevent a repeat of this event. The source was never uncovered. No release or personnel exposure occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-09-21
54895 | 0 | Pilgrim | 1 |  |  | [1] GE-3 | 2020-09-10 | 2020-09-10 16:09 | 2020-09-10 | FITNESS FOR DUTY (FFD) POLICY VIOLATION A contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's rights to access the plant have been suspended. The licensee notified the NRC Region I Decommissioning Lead Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Defueled; FMode1: Defueled | Non Emergency | 1 | MA | POW |  | 26.719 |  |  |  | 0 | 2020-09-10
54894 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2020-09-09 | 2020-09-09 16:29 | 2020-09-09 | AGREEMENT STATE REPORT - MEDICAL EVENT - UNDERDOSE The following was received from the New York State Department of Health via fax: "A medical licensee reported that only 30.3 mCi of a prescribed dose of 45.1 mCi of SIRTEX SIR-Spheres was delivered to a patient. The microspheres apparently became clogged in the applicator. A written report is forthcoming." Event Report ID No.: NYDOH-20-03 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2020-09-17
54893 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2020-09-09 | 2020-09-09 16:28 | 2020-09-09 | AGREEMENT STATE REPORT - LOST AND FOUND MO-99/TC-99M GENERATOR The following was received from the State of Wisconsin Department of Health Services (the Department) via email: "On September 9, 2020, the licensee reported a missing 7.5 Ci Mo-99/Tc-99m generator, which was subsequently found, to the Department. The facility receives a generator every Sunday evening. On September 8, the licensee became aware that this week's generator was missing and initiated search efforts. The licensee confirmed with the generator supplier that a generator was delivered on September 6. The licensee reviewed security footage and determined that the generator was delivered at 2115 CDT on September 6. The licensee reviewed additional camera footage and determined that a different courier service requested access to the nuclear medicine hot lab about an hour later and took the package that had been delivered at 2115 CDT. The licensee contacted the second courier service and determined that the missing generator was found in the courier's warehouse on September 9. The generator has been returned to the licensee. "The licensee is evaluating potential dose to members of the public. The Department will perform a follow-up investigation." Event Report No.: WI200006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2020-09-17
54892 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2020-09-09 | 2020-09-09 12:17 | 2020-09-24 | <br><br>EN Revision Imported Date : 9/25/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - BROKEN SHUTTER MECHANISM ON FIXED GAUGE The following was received from Iowa Department of Public Health via email: "The licensee reported today that during a routine shutter check it was discovered that a shutter on a fixed gauging device had come off of its hinge. The device is located on coal silo 106 outlet at the 163 foot elevation. Due to the location of the device, no personnel can be exposed to the beam. The licensee has contacted a vendor to repair the shutter. This event will be updated once the Agency (Iowa Department of Public Health) receives the written report." The gauge was a Kay-Ray Sensall model 7700-C containing 50 milliCuries of Cs-137. Iowa NMED Number: IA200003 * * * UPDATE ON 9/24/20 AT 1119 EDT FROM RANDAL DAHLIN TO SOLOMON SAHLE* * * The following information was received from the State of Iowa Department of Public Health via email: "The outside vendor arrived on-site September 16, 2020 and found that the right end mounting bracket for the shaft was bent and the shaft was no longer in the mounting bracket. The vendor removed the device and repaired the shutter. The apparent cause of the shutter failure was the source was swung out to where it completely cleared the calibration blocks and then swung back into place. The state considers this event be closed." Notified R3DO (Cameron) and NMSS Events Notifications (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2020-09-17
54891 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-09-08 | 2020-09-09 11:26 | 2020-09-09 | AGREEMENT STATE REPORT - LOST AND RECOVERED CAMERA The following was received from Texas Department of Health Services (the agency) via email: "On September 9, 2020, the Agency was notified by the licensee's radiation safety officer (RSO) that on September 8, 2020, one of his crews lost a QSA 880D exposure device containing a 38.1 Curie iridium-192 source. The radiography crew had placed the exposure device on the tailgate of their truck at the licensee's location. The crew drove away from the site with the exposure device still on the tailgate. The device fell off the truck a short distance from the licensee's location. A second crew left the licensee's location a short time (10 minutes) later and found the device on the pavement. The second crew performed a radiation survey of the device and found the radiation levels to be normal and the source was still fully shielded. The second crew returned the device to the licensee's location. The device was inspected and did not appear to be damaged. The licensee has sent the device to the manufacturer for inspection. Additional information has been requested from the licensee. Additional information will be provided as it is received in accordance with SA-300. " Texas Incident Number: I-9798 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-17
54890 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-09-08 10:15 | 2020-09-09 09:09 | 2020-09-09 | REPORT OF OFFSITE NOTIFICATION DUE TO IMPAIRMENT OF FIRE SUPPRESSION SYSTEM "At approximately 1015 (EDT) on September 8th, 2020, the New Hanover County Deputy Fire Marshal was notified per State code requirements that the fire suppression system encompassing a part of the Fuel Manufacturing Operation (FMO) was impaired due to planned piping replacement. Additional compensatory measures were enacted. The system was restored at approximately 1750 (EDT) yesterday (9/8/2020) and the Deputy Fire Marshal informed of restoration. Because the New Hanover County Deputy Fire Marshal was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." NRC Region 2 and the State of North Carolina will be notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-09-09
54889 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-09-07 20:45 | 2020-09-08 14:16 | 2020-09-08 | REPORT OF OFFSITE NOTIFICATION DUE TO IMPAIRMENT OF FIRE SUPPRESSION SYSTEM "At approximately 2045 EDT on September 7th, 2020, the New Hanover County Deputy Fire Marshal was notified per State code requirements that the fire suppression system encompassing a part of the Fuel Manufacturing Operation (FMO) was impaired due the discovery of a water leak in the sprinkler system. Additional compensatory measures were enacted. The system was restored at approximately 0930 today (9/8/2020) and the Deputy Fire Marshal informed of restoration. Because the New Hanover County Deputy Fire Marshal was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The NRC Region 2 and the State of North Carolina Radiation Protection Office will be notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-09-08
54888 | 0 | Catawba | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-09-08 09:25 | 2020-09-08 13:13 | 2020-09-08 | AUTOMATIC REACTOR TRIP ON OVER POWER DELTA TEMPERATURE "At 0925 EDT, on September 8, 2020, with Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped on Overpower Delta Temperature. Unit 1 Channel 1 Overpower Delta Temperature was tripped as a planned evolution when an inadvertent Unit 1 Channel 2 Overpower Delta Temperature signal was received. This resulted in an automatic reactor trip. The trip was not complex, with all systems responding normally. Because of the reactor trip, the Auxiliary Feedwater (AFW) System actuated as expected due to on ATWS Mitigation System Actuation Circuitry (AMSAC) signal. Unit 2 is not affected. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the main condenser using the condenser steam dump valves. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a 4-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-09-08
54887 | 0 | Catawba | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-09-06 03:45 | 2020-09-06 11:39 | 2020-09-06 | LONG TERM HABITABILITY OF TECHNICAL SUPPORT CENTER UNDER ACCIDENT DOSE ANALYSIS EXCEEDS CALCULATED ALLOWABLE VALUES "At 034S [EDT] on September 6, 2020, Unit 2 ECCS leakage outside containment was determined to exceed the long term habitability dose analysis for the Catawba Nuclear Station Technical Support Center (TSC) under bounding conditions. Repairs are currently in-progress to arrest the leakage and restore functionality of the TSC. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC: becomes uninhabitable. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to the alternate facility. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the discovered condition of the TSC affects the functionality of an emergency response facility. "There is no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-09-06
54886 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-09-05 | 2020-09-05 14:35 | 2020-09-05 | AGREEMENT STATE REPORT - GAUGE DAMAGED WHEN STRUCK BY VEHICLE The following was received from the Texas Department of State Health Services (the Agency) via email: "On September 5, 2020, The Agency was notified by the licensee's site radiation safety officer (SRSO) that a Humboldt EZ 5001 moisture/density gauge was damaged at a temporary job site when a bulldozer struck the gauge. The gauge contains a 40 milliCurie americium-241 source and a 10 milliCurie cesium-137 source. The cesium source was in the shielded position when the event occurred. The operating rod was bent, and the SRSO stated he did not believe the cesium source rod would move. The SRSO stated they performed radiation surveys around the gauge and the highest reading they obtained was 1.3 millirem per hour, which is a normal reading. The SRSO stated they were taking the gauge back to their storage location and would perform a leak test of the gauge. The event did not present an exposure risk to any individual. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-14
54885 | 0 | Cook |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-09-04 22:42 | 2020-09-05 02:27 | 2020-09-05 | MANUAL REACTOR TRIP AND AUTOMATIC SAFETY INJECTION "On September 4, 2020, DC Cook Unit 2 experienced a lowering Reactor Coolant System (RCS) pressure caused by a failed open Reactor Coolant Pressurizer Spray valve. At approximately 2242 [EDT], a manual Reactor Trip was performed due to the lowering RCS pressure. Following the manual reactor trip, an automatic Safety Injection was actuated due to the lowering RCS pressure. RCS pressure has recovered to normal and is stable. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation, and 10 CFR 50.72(b)(2)(iv)(A), ECCS Discharge to RCS, as a four (4) hour report. Notification is also being made as an 8 hour report under 10 CFR 50.72(b)(3)(iv)(A), Reactor Protection System (RPS), Containment Isolation, Emergency Core Cooling (ECCS), Auxiliary Feedwater System (AFW), and Emergency AC Electrical Power actuations. The DC Cook Resident NRC Inspector has been notified. "Unit 2 is being supplied by offsite power. All control rods fully inserted. Aux Feedwater Pumps started as required and are operating properly. All ECCS components operated as required including Containment Isolation. Decay heat is being removed via the Condenser Steam Dumps and ECCS has been secured. Three of four Reactor Coolant Pumps were secured and RCS pressure has recovered to normal pressure and is stable. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip and Safety Injection. DC Cook Unit 2 remains stable in Mode 3. No radioactive release is in progress as a result of this event." Unit 1 was not affected and remains in Mode 1, 100 % power. | 0 | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | Eccs Injection | RPS Actuation - Critical | Valid Specif Sys Actuation |  | IMode2: Power Operation; FMode2: Hot Standby | Non Emergency | 3 | MI | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2020-09-05
54884 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-09-03 | 2020-09-04 20:51 | 2020-09-04 | AGREEMENT STATE REPORT - POOL WATER CONDUCTIVITY EXCEEDED LIMITS The following was received from the State of California Department of Public Health - Radiologic Health Branch (CDPH/RHB) via email: "The licensee Radiation Safety Officer reported that the pool water conductivity exceeded 100 microSiemens/cm on 9/3/20. The reason was the loss of operability of the demineralizer pump. The pump has been repaired and is currently operable with declining pool water conductivity, but the pool water is still in excess of 100 microSiemens/cm. CDPH/RHB is continuing to investigate the circumstances surrounding this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-09-14
54883 | 0 | Soil and Materials Engineering, Inc |  |  |  |  | 2020-09-04 14:40 | 2020-09-04 16:28 | 2020-09-04 | DAMAGED GAUGE DUE TO VEHICLE INCIDENT The following was received via email from the licensee: "[The Engineering Technician] was performing density tests on an aggregate base with a nuclear density gauge (nuc) [gauge: Troxler 3411 s/n 14468; 8.0 mCi Cs-137; 40.0 mCi Am-241] and the loader operator was also working in the area. The [loader] operator was trying to back-up and grazed [the Engineering Technician] on his left shoulder slightly with the rear bumper end, just after [the Engineering Technician] had brought the source rod into the safe position to record the test results. [The Engineering Technician] rolled out of the way and as the loader came to a stop it had hit the nuc gauge and broke the guide rod. Unsure if the source was intact, [the Engineering Technician] kept the loader in-place and kept people more than 15 feet away until [the Operations Manager and the Senior Project Consultant] could arrive on-site to assess the situation. [The Engineering Technician] informed [the Operations Manager and the Senior Project Consultant] on the phone and once they arrived on-site that he was uninjured, since he was able to easily roll out of the way of the loader. [The licensee] then determined that both sources were still intact and the source tip was in the shielded position within the gauge. [The licensee] took a Geiger Counter reading at the site (0.06 mRem/hr 3 feet from the gauge) and again after loading the gauge into the transport box (less than 0.03 mRem/hr 3 feet from the box). Prior to loading the gauge into the box, [the licensee] performed a leak test on the gauge and shipped the leak test to Instrotek as soon as [the licensee] returned to the office with the damaged gauge." The licensee noted that the gauge is currently locked-out/tagged-out and once they receive the leak test results they will most likely transfer the gauge to Instrotek for disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Safety Equipment Failure | [9 empty] | Non Emergency | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-09-14
54882 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2020-09-02 | 2020-09-04 15:01 | 2020-09-04 | AGREEMENT STATE REPORT - MEDICAL EVENT - UNDERDOSE The following was received from the Georgia Radioactive Materials Program via email: "At the end of the administration of Y-90 SIR Spheres [for the treatment of tumors in the right lobe of the liver], the delivery vial (D-Vial) appeared to overfill as the radiologist was attempting to mix the spheres with a 50/50 solution of contrast and 5 percent dextrose/glucose (D5W). The radiologist noticed some clumping and after attempting to gently disperse the Spheres, he gave a couple hard pushes of the contrast/D5W into the D-Vial. At that time, he noticed the leak. He examined the septum and found it to be dry. As a precaution the radiologist put Durabond on top of the septum. Further examination showed that the material leaked out of the sides of the crimped vial top rather than the septum. The procedure was stopped to prevent further contamination. "The event occurred while using SIRTEX new SIROS delivery system. The SIRTEX representative was present providing guidance to the radiologist as this was the first time he used the new system. "It is estimated that 75 percent of Y-90 SIR-Spheres were administered to the patient [Prescribed Activity: 3.1 GBq (83.7 mCi); Delivered Activity (estimated): 2.87 Gbq (77.7 mCi)]. It is likely that the residual activity was over estimated due to contamination of the SIROS delivery dome. The usual waste from the procedure is contained in a 1-liter Nalgene containers and then placed in a Lucite shield for dose rate measurements to determine the residual activity. The Siros delivery dome could not be measured in the same geometry and likely resulted in an increased dose rate and underestimate of the total dose delivered. "At this time, the prescribing physician indicated he does not expect any adverse effects for the patient and is awaiting the dosimetry evaluation from the patients PET/CT Scan. "Attempts have been made to recreate the event without success. There is speculation regarding the size of the dose and that the number of Spheres may have been a factor (larger than typically administered). Representatives from SIRTEX indicate that this has not been an issue at other sites. "Prior and subsequent studies with the new SIROS delivery system were successful with less activity. "Further evaluation of the equipment to determine why the vial leaked, will be performed following decay and return the manufacturer." Georgia Incident Number: 30 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-09-14
54881 | -1 | Eli Lilly Company Manufacturers |  |  |  |  | 2020-09-04 | 2020-09-04 13:38 | 2020-09-09 | <br><br>EN Revision Imported Date : 9/10/2020<br><br>EN Revision Text: LOST TRITIUM EXIT SIGN The following is the summary of a call with the licensee: During an annual inventory review, the licensee noticed that an exit sign had been removed from the wall. It was supposed to have been repurposed and moved to a different location but the licensee has lost confidence that the exit sign is in its control. The licensee is continuing to look for the exit sign. Exit sign details: purchased from SRBT, s/n C083911, manufacture date 2/2011, original activity: 21.6 Ci, current activity 12.6 Ci. * * * RETRACTION ON 9/9/2020 AT 1455 EDT FROM TRENTON MAYS TO THOMAS HERRITY * * * The following is the summary of a call with the licensee: The licensee is retracting this event. After further searching for the exit sign, the licensee was able to recover the sign and determined that it had continuously been in its possession. The licensee notified R3 (Warren) that the sign had been found. Notified R3DO (Hills) and NMSS Events Notification and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Lost/Stolen Lnm>10x | [9 empty] | Non Emergency | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2020-09-14
54880 | 0 | River Bend | 1 |  |  | [1] GE-6 | 2020-09-03 20:48 | 2020-09-04 01:40 | 2020-09-04 | HIGH PRESSURE CORE SPRAY INOPERABLE "River Bend Station experienced an inadvertent initiation and injection of High Pressure Core Spray (HPCS) at 2048 [CDT] on 9/3/2020 while operating at 92% power. Initial investigation indicates a power supply failure in the Division III trip units which feeds HPCS and Division III Diesel Initiation signals. "The Control Room Operator responded to the event by taking manual control of Feedwater Level Control to maintain Reactor Water Level nominal values. The HPCS injection valve was open for approximately 25 seconds before operators manually closed the valve. "The manual closure of the injection isolation valve caused the system to be incapable of responding to an automatic actuation signal. The manual override of the injection isolation valve was reset approximately 52 minutes after the event. The HPCS system has remained inoperable. The event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that caused loss of function of the HPCS System. "No radiological releases have occurred due to this event. "The Senior NRC Resident Inspector has been notified." These conditions put the unit in a 14-day LCO (3.5.1) for HPCS Inoperability and a 30-day LCO (3.7.1) for one Standby Service Water Pump Inoperable (2C). | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-09-04
54879 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2020-08-27 | 2020-09-03 17:27 | 2020-09-03 | AGREEMENT STATE REPORT - LOSS OF MEDICAL SEED AFTER REMOVAL FROM PATIENT The following is a synopsis of the event received from the Georgia Radioactive Materials Program: On July 31, 2020, a physician did not follow proper procedure while recording the number of seeds administered to a patient. The physician initially planned on administering one seed but decided to administer two. The physician did remove both seeds from the patient on August 3, 2020. The tracking system for the administered seeds was based on writing the number of seeds administered on a colored bracelet or arm band, which the patient wears while the seed(s) are implanted. It is removed and travels with the removed tissue through the remaining processes at the hospital. In this case, the physician did not revise the number on the bracelet, therefore during the subsequent processes, other hospital staff only looked for one seed to recover from the procedure by-products. One seed was not recovered. There was some discussion between departments prior to August 21, 2020 about the seed. Radiation Safety was not contacted. On August 21, 2020, an Assistant RSO discovered the discrepancy while conducting an inventory, preparing the seeds for return to the seed vendor. Subsequent searches that included the involved staff did not recover the missing seed. After a review of the laboratory processes for analyzing the removed tissue, the hospital staff believes the missing seed was retained in the transport bin and disposed of with that bin in the bio-hazard waste stream. But, this can not be proven. It was demonstrated to not be in the frozen sample that the hospital retained. The hospital declared the seed lost on August 27, 2020. The seeds were I-125 encapsulated in titanium. Model IAI-125A. Activity level calculated to be 145.1 microCuries at time of loss/disposal. The radioactivity is small, and the decay rate high such that this poses a low risk to the public. Based on literature, the RSO states the contact dose, assuming the seed was trapped in clothing (contact) for twelve hours to be 2.66 milliSeverts. The hospital has conducted a root cause analysis, and has revised its procedures and re-trained staff to prelude future loss of radioactive seeds. Incident #: 29 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-09-11
54878 | -1 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2012-05-31 | 2020-09-03 16:17 | 2020-10-01 | <br><br>EN Revision Imported Date : 10/2/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS This is information received from the state of Nebraska via email: "In conducting a search for records for NRC Event #54500, it was determined that Home Depot #3210 was remodeled at the same time as Home Depot #3208 in Grand Island, NE and all (16) tritium exit signs were exchanged for LED in May 2012. Disposal records are unavailable due to Staybright Electric, the contractor in charge of replacement and disposal, going out of business. Home Depot was unable to produce disposal records but it is their belief that the signs were disposed of properly as Staybright conducted tritium exit sign removals for other Home Depots in the region prior to their closing for which records of disposal were obtained, demonstrating knowledge of proper procedure. "The State of Nebraska also checked with Tritiumdisposal.com and SRBT in attempt to locate records as the outlets of disposal for Staybright, but no records were found. "Home Depot currently has a plan in place that was submitted to the NRC in July of 2009 for facility management to reiterate tritium exit sign management requirements to existing vendors to ensure signs are managed within NRC requirements. As part of ongoing tritium exit sign servicing it is very reasonable to believe that Staybright transferred and disposed of tritium exit sign inventory properly. Home Depot continues to proactively address and replace (as appropriate) its remaining tritium exit sign inventories through the use of professional, third party vendors and continues to responsibly manage its existing inventories at current stores throughout the United States. "A Home Depot corporate representative will track all purchases and returned signs to ensure accurate inventory and disposal. "All Tritium Exit Signs have been replaced with LED. "Home Depot will no longer install tritium exit signs within newly constructed locations." Nebraska Item Number: NE200006 * * * RETRACTION ON 10/1/2020 AT 1020 EDT FROM DEB WILSON TO ANDREW WAUGH * * * This is information received from the state of Nebraska via email: "While the Home Depots were remodeled at similar times, it was found that the tritium exit signs at Store 3210 in Scottsbluff were kept in service until the end of their useful life. Records were recovered showing all signs being disposed of by Curie Environmental Services in Albuquerque, NM on 9/20/2019." Notified R4DO (Silva), NMSS Events (email), and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-09-11
54877 | 0 | Prairie Island | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2020-09-03 14:21 | 2020-09-03 15:36 | 2020-09-03 | OFFSITE NOTIFICATION DUE TO A HYDRAULIC OIL SPILL "On 9/3/2020, at 1421 (CDT), a notification was made to the National Response Center as a result of a spill of approximately 3 fluid ounces of hydraulic oil into the plant waters of Prairie Island Nuclear Plant intake on 9/2/2020. "This notification is being made as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact to public health and safety. "The NRC resident inspector has been notified." | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-09-03
54876 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-08-27 | 2020-09-03 11:13 | 2020-09-03 | AGREEMENT STATE REPORT - INCORRECT DOSE DELIVERED TO PATIENT The following was received from the Ohio Department of Health: "The licensee tried to perform a split dose procedure on the right lobe anterior and right lobe posterior portion of a patient's liver. "The prescribed dose was 60 mCi Y-90 Theraspheres (approximately 150 Gy) for each site. The posterior was treated first and then the catheter was moved to the anterior position. Post treatment scans of the patient indicated the posterior received 20 mCi (35 Gy) and the anterior received 100 mCi (180 Gy). The physician believes the catheter slipped after initial placement, resulting in an overdose to the anterior and underdose to the posterior. "The licensee will no longer conduct spilt dose procedures." Ohio Item Number: OH200006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-09-11
54875 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-09-02 10:27 | 2020-09-02 16:52 | 2020-09-02 | CONCURRENT REPORT FOR OFFSITE NOTIFICATION "At approximately 1027 EDT on September 2, 2020, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire suppression system encompassing a part of the Fuel Manufacturing Operation (FMO) was impaired due to planned sprinkler head modifications. Additional compensatory measures were enacted. The system was restored at approximately 1300 EDT today (9/2/2020) and the Deputy Fire Marshall informed of restoration. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will notify Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-09-10
54874 | 0 | Nine Mile Point |  | 2 |  | [1] GE-2,[2] GE-5 | 2020-03-06 | 2020-09-01 14:48 | 2020-09-01 | PART 21 REPORT - FAILURE OF MAIN STEAM ISOLATION VALVE AIR PACKS The following is a synopsis of information received from the licensee: On March 6, 2020, while at zero percent power and in Cold Shutdown - Mode 4, Nine Mile Point Unit 2 (NMP2) determined through surveillance testing that three Main Steam Isolation Valves (MSIVs) did not meet their Technical Specification closure time. The cause of the MSIV failures has been determined to be delayed Air Pack response. The delay was caused by a buildup of corrosion product and waxy foreign material believed to be dried pipe thread sealant or O-ring assembly lube that accumulated on the internal surfaces of the Air Pack during refurbishment by the vendor Trillium (previously Hiller). The following is action taken or planned to be taken to prevent recurrence: A note will be added to the procurement requirement evaluation form and purchase order for MSIV Air Pack refurbishments to minimize use of O-ring lubricant and thread sealant to limit likelihood of capturing foreign material on Air Pack valve internals. The Energy Industry Identification System (EIIS) component function identifier and system name of each component or system referred to above is: Component - Main Steam Isolation Valves, Air Pack. IEEE 803 Function Identifier - VOP. IEEE805 System Identification - SB. The licensee notified the NRC Resident Inspector. For further information contact: Todd Tierney Plant Manager Nine Mile Point Nuclear Station Exelon Generation Company, LLC Brandon Shultz Site Regulatory Assurance Manager Nine Mile Point Nuclear Station (315) 349-7012 . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Defects And Noncompliance |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | Non Emergency | 1 | NY | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2020-09-01
54873 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-08-28 | 2020-09-01 13:53 | 2020-09-01 | AGREEMENT STATE REPORT - SHUTTER MECHANISM MALFUNCTION The following was received from the Ohio Dept. of Health via e-mail: "During a routine inspection of a generally licensed device a broken spring on the basis weight shutter was discovered. This spring is a fail-safe that closes the shutter in the event of the loss of air pressure. A temporary repair to the spring was made and the shutter was tested. The shutter is now working properly and a replacement spring is on order with a plan to install the spring as soon as possible after it arrives. "Until the spring is replaced, the scanner will be taken off-line daily and observations made that the shutter closes. "The device contains a 400 mCi, Kr-85 source. No personnel were exposed due to the spring failure." Ohio Item Number: OH200005 Ohio Reference Number: OH2020-037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-09-09
54872 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-31 | 2020-09-01 11:03 | 2020-09-01 | AGREEMENT STATE REPORT- SHUTTER STUCK IN OPEN POSITION The following was received from the Texas Department of State Health Services (the Agency) via e-mail: "On September 1, 2020, the Agency received a report from the licensee's radiation safety officer (RSO) indicating the shutter on an Ohmart Vega model SH-F1B nuclear gauge was stuck in the open position. Open is the normal operating position of this gauge. The gauge contains a 100 milliCurie (original activity) cesium-137 source. The stuck shutter was found during routine inspections. The licensee has contacted a service provider to repair the gauge. The gauge does not create an exposure risk to any individual. Additional information will be provided in accordance with SA-300." Texas Incident Number: 9791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-09
54871 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-08-28 | 2020-08-31 15:06 | 2020-08-31 | AGREEMENT STATE REPORT - RADIOACTIVITY FOUND IN RECYCLED MATERIAL The following was received from the state of Louisiana: "On August 28, 2020, the Louisiana Department of Environmental Quality (LDEQ) / Emergency Response Services Division / Radiation Section was contacted to report radioactive material was discovered being brought into the facility in a roll-off box to Southern Recycling LLC. The roll-off box came from Monsanto Company, Luling, Louisiana 70070. The roll-off box contained scrap metal from a new construction site at Monsanto Company. American Radiation Services (ARS), Port Allen, LA was brought in to survey the box and make determination of the radioactive material. ARS determined that the radioactive material was Se-75. The survey reading was two mR/hr at surface contact. The survey reading was taken from a corrugated paper box with no removable contamination. At this time, no radiation sealed source has been found or indication to make determination of the potential source. "LDEQ is sending an inspector to the facility to make further determination if possible with ARS. The radioactive material is secured on site at Southern Recycling." Louisiana Incident No.: LA20200008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-09-08
54870 | 0 | Watts Bar | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-07-23 09:56 | 2020-08-31 15:30 | 2020-08-31 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR TWO INVALID CONTAINMENT VENTILATION ISOLATION ACTUATIONS "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report two invalid Containment Ventilation Isolation (CVI) actuations at Watts Bar Nuclear Plant (WBN) Unit 1. "On July 23, 2020, at 0956 Eastern Daylight Time (EDT), the Train A CVI actuated due to an invalid high radiation signal from 1-RM-90-130, Containment Purge Air Exhaust Monitor. Upon investigation, the high radiation signal was caused by a failed power supply. Corrective action included replacing the power supply, 1-RM-90-130 detector, and restoring the system to service. "On August 7, 2020, at 2017 EDT, the Train A CVI actuated due to an invalid high radiation signal from 1-RM-90-130, Containment Purge Air Exhaust Monitor. Upon investigation, a small tear was identified in the foil covering the scintillation detector. This defect caused erratic indication and the system actuation. The foil was replaced and the system was restored to service. "Prior to and following the invalid high radiation alarms, all radiation monitors except 1-RM-90-130 were stable at their normal values; therefore, the CVI was invalid. Control room operators performed appropriate checks and confirmed that all required automatic actuations occurred as designed. These events were entered into the corrective action program as CR 1625135 and CR 1628904. "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-08-31
54869 | 0 | Callaway | 1 |  |  | [1] W-4-LP | 2020-08-31 11:11 | 2020-08-31 12:58 | 2020-08-31 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability occurred which could have allowed access to a protected area for which compensatory measures were not employed. Security measures have since been re-established. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Safeguards Reports |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2020-08-31
54868 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2020-08-30 10:15 | 2020-08-31 11:49 | 2020-08-31 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the state of Kentucky via email: "The Radiation Safety Officer (RSO) of the Kentucky Radioactive Materials Licensee Geotechnology Inc. (RML #201-189-51), reported the theft of a single CPN MC-1 Elite Series Moisture Density gauge (Serial No: 31113 with sealed source models HEG137, 10 mCi Cs-137, sealed source serial number Q785, and AM1.NO2, 50 mCi AM-241:Be, sealed source serial Number K039/18) from an authorized users vehicle while parked overnight at the user's residence located in Lexington KY. The gauge was secured by 2 chains within the cab of the vehicle, but was stolen from the vehicle along with several other items. No forced entry into the vehicle was noted, but one of the two chains securing the gauge was cut and the second chain was removed by breaking the top handle of the gauge transportation case. A report was made to the Lexington Police Department which is investigating the theft (Case No. 2020145606). The Kentucky Radiation Health Branch, will follow up with an interview with the RSO and authorized user. "Reporting Criteria In 10 CFR 20.2201(a)(1)(i)" Kentucky Incident No.: 201-189-51 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2020-09-08
54867 | 0 | Palisades | 1 |  |  | [1] CE | 2020-08-30 20:40 | 2020-08-31 08:28 | 2020-08-31 | FITNESS FOR DUTY (FFD) POLICY VIOLATION A contract employee supervisor had a confirmed positive for alcohol during a fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | Non Emergency | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2020-08-31
54866 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-29 09:00 | 2020-08-29 16:14 | 2020-08-29 | AGREEMENT STATE REPORT - STOLEN VEHICLE WITH MOISTURE DENSITY GAUGE The following was received from the Texas Department of State Health Services (the Agency) via email: "The licensee notified the Agency at approximately 1315 CDT that one of its company pickups had been stolen and a Troxler model 3440 moisture/density gauge (SN: 37337) was secured in the bed of the truck. The gauge contains 40 milliCurie americium-241 and 8 milliCurie cesium-137 sources. The technician had a late testing and then went to his residence from the job site due to a serious water leak that was occurring there. After fixing the leak, it was late and he fell asleep and did not return the gauge to the licensee's facility. He last saw the vehicle/gauge at approximately 0100. At approximately 0900, he discovered the vehicle, with the gauge, had been stolen. The set of keys to the locks securing the gauge and the insertion rod were in the cab of the truck. Local police were notified. Police will notify the local pawn shops and the licensee will search local buy/sell/trade internet sites for the gauge and other equipment. More information will be provided as it is obtained in accordance with SA-300." Texas Incident # I-9790 * * * UPDATE ON 08/29/20 AT 2018 EDT FROM KAREN BLANCHARD TO OSSY FONT * * * The following update was received from the Texas Department of State Health Services via email: "The licensee's Radiation Safety Officer notified the Agency at approximately 1847 CDT that he has possession of the gauge and it was back at their facility. He had been called by the San Antonio Fire Department HAZMAT at approximately 1800 that they had been called to a location where the gauge was - the gauge was sitting on the edge of a street next to the curb. The latches on the transport case were unlocked but the gauge and all other equipment were present. The chains and locks that secured the gauge in the bed of the truck were also present. There was no damage to the transport container or the gauge. Technicians put the device through its normal testing procedures and it is fully operational. Any further information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Kellar), and NMSS Events Notification, ILTAB, and CNSNS (Mexico) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-07
54865 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-28 | 2020-08-28 18:58 | 2020-08-31 | <br><br>EN Revision Imported Date : 9/1/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - LOST SHIPMENT OF TRITIUM EXIT SIGNS The following was received from the Texas Department of State Health Services (the Agency) via email: "On August 28, 2020, the Agency was contacted by an individual to notify it that they had shipped seven Forever Lite tritium exit signs to a manufacturer in May of 2020 and they have been informed by the transportation company that they do not know where the signs are. The signs are Forever Lite signs, each containing 7.03 curies (original activity) of tritium, manufactured in May 2011. "The package was last scanned in Fort Worth, Texas, in May of 2020. The shipper stated that they were told on May 19, 2020 it was to be delivered in Canada. The next update when they followed up they were advised the package was lost and they were trying to locate the shipment and opened a claim. The location where the signs were lost is unknown at this time; therefore, the Agency is making this report for your information. "The Agency has requested additional information and clarifications from the shipper. Additional information will be provided as it is received." Texas Incident #: I - 9789 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf * * * UPDATE ON AUGUST 31, 2020 AT 1126 EDT FROM ART TUCKER TO BRIAN LIN * * * The following was received from the Texas Department of State Health Services (the Agency) via email: "After reviewing documents provided by the licensee, the Agency contacted the licensee and confirmed that eight signs were lost and not seven as previously reported. The transportation company's radiation safety officer (RSO) was contacted by the Agency and the RSO stated they do not store the tracking records of shipments in their computer system for very long, therefore they would not be able to review the tracking information for this shipment. The Agency will provide additional information as it is received in accordance with SA-300." Notified R4DO (Deese), NMSS Events Notification, ILTAB, CNSC (Canada), and CNSNS (Mexico) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-07
54864 | 0 | Vogtle | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2020-08-26 09:30 | 2020-08-28 16:38 | 2020-08-28 | DESIGN CHANGE ALTERED BASIS FOR ITAAC "In accordance with 10 CFR 52.99(c)(2), as described in NEI 08-01, 'Industry Guideline for the ITAAC Closure Process Under 10 CFR Part 52,' Vogtle Units 3 and 4 Construction is making this notification to the NRC for determining that Inspections, Tests, Analyses and Acceptance Criteria (ITAAC) 2.5.02.07a (Index No. 534) and ITAAC 2.5.02.07e (Index No. 538) for both units require additional actions to restore their completed status. The ITAAC Closure Notifications for ITAAC 534 were submitted on March 31, 2017 (Unit 3 ML17093A286, Unit 4 ML17093A535). The ITAAC Closure Notifications for ITAAC 538 were submitted on November 30, 2016 (Unit 3 ML16351A350, Unit 4 ML16351A334). "On August 26, 2020, it was determined that a design change, issued for several Protection and Safety Monitoring System (PMS) isolation barrier assemblies (ISBs), materially altered the basis for determining that the ITAAC 534 and ITAAC 538 Acceptance Criteria were met. The modified ISBs will require testing per IEEE 384-1981, Standard Criteria for Independence of Class 1E Equipment and Circuits, to demonstrate that the Acceptance Criteria is met. System function is not required while the plant is under construction. "ITAAC Post Closure Notifications in accordance with 10 CFR 52.99(c)(2) will be submitted following completion of corrective actions. "The 10 CFR 52.99(c)(4) All ITAAC Complete Notification has not been submitted for VEGP [(Vogtle Electric Generating Plant)] 3 and 4. "The resident inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Other Unspec Reqmnt |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | Non Emergency | 2 | GA | POW | [5 empty] | 0 | 2020-08-28
54863 | 0 | Dresden | 2 |  |  | [2] GE-3,[3] GE-3 | 2020-08-27 16:45 | 2020-08-28 10:22 | 2020-08-28 | FITNESS-FOR-DUTY REPORT - LICENSED OPERATOR TESTED POSITIVE "At 1645 CDT on 8/27/2020, it was determined that a licensed operator tested positive in accordance with the FFD testing program. The individual's authorization for site access has been terminated. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2020-08-28
54862 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-26 | 2020-08-27 09:34 | 2020-09-01 | <br><br>EN Revision Imported Date : 9/2/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - UNABLE TO DETERMINE IF SOURCE IN SHIELDED POSITION ON LEVEL INDICATOR The following information was received via E-mail: "On August 26, 2020, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that while making preparations for the coming hurricane, the position of the source rod on a Tracerco, Model T-218-160032 [used for level indication] could not be confirmed. The source rod contains 10 cesium-137 sources of 10 milliCuries each (original activity.) The RSO stated when they return the sources to the shielded position, the control system does indicate the sources are shielded as indicated by a light change on the system console. When the licensee attempted to shield the sources on this day, the light did not change to indicate the sources were shielded. The gauge source rod is operated manually. They tried it a couple of times, but the light still did not change. A survey was performed on the outside of the vessel. The RSO stated there wasn't enough change in dose rate readings with shutter in the open and closed positions to determine whether the sources were shielded based on survey. The RSO stated it may be that the sources are not moving, or it may be that there is an issue within the control system causing the light not to change. They cannot determine at this time which problem is occurring. The RSO is contacting the manufacturer to send someone out after the hurricane. There is no risk of exposure. The RSO stated they will update the Agency once the manufacturer determines the problem. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9787 * * * RETRACTION ON 9/01/2020 AT 1406 EDT FROM ART TUCKER TO THOMAS HERRITY * * * The following information was received via e-mail: "On September 1, 2020, the licensee notified the Agency (Texas DSHS) that on August 31, 2020, a service company came onsite to investigate the shutter problem they had reported, and identified that there was no mechanical issue with the shutter. The problem they had was a failure of the output signal to indicate source position. The source rod was functioning normally. Based on this information, the Agency is retracting this event." Notified R4DO (Deese) and NMSS Events (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-04
54861 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-07-07 | 2020-08-26 23:49 | 2020-08-27 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE RETRACTION FAILURE The following information was received via E-mail: "The Radiation Safety Officer with Mistras Group, Inc. contacted the Radiologic Health Branch regarding an incident with an Ir-192 radiography source that was determined to be locked out of its exposure device. The source was an Industrial Nuclear Model 32 Ir-192 source, Serial Number 550F, with an activity of 63.4 Curies. The device was an Industrial Nuclear Ir-100, Serial Number 4358. The incident occurred during radiography operations at a refinery in El Segundo. "After a routine exposure, the radiographer retracted the source. The radiographer then proceeded with the radiation survey that showed a dose rate of 80 mR/hr approximately 2 feet from the exposure device, indicating that the source was not in the locked and shielded position. The radiographer contacted the RSO who instructed them to readjust the restricted area boundary to maintain 2 mR/hr dose rate. "After the RSO arrived at the site, they placed shielding to reduce the dose rate while performing retrieval and returning the source to the locked and secured position. The device was then red tagged and placed out of service until it could be evaluated by the manufacturer. The highest dose received by Mistras Personnel (RSO) was 20 mrem, as read by a self-reading pocket dosimeter. The licensee's investigation into this event is ongoing and will be reviewed further by the California Department of Public Health." California 5010 Number: 070820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-09-10
54860 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-08-26 08:00 | 2020-08-26 18:03 | 2020-08-26 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF RADIOACTIVE MATERIAL The following information was received from the State of Colorado via email: "A Troxler 3400 Series moisture/density gauge, containing 9 mCi Cs-137 and 44 mCi Am-241:Be or 66 microCi of Cf-252 sealed sources, fell out of the back of a pickup truck during transport by the licensee and was recovered by a member of the public, who turned the gauge into the fire department and the fire department returned the gauge to the licensee." Colorado Event Report ID No.: CO200058 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-09-03
54859 | 0 | Prairie Island | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2020-08-26 13:19 | 2020-08-26 18:10 | 2020-08-26 | AUTOMATIC REACTOR TRIP DUE TO FLUX RATE "At 1319 CDT, on August 26, 2020, with Unit 1 in Mode 1 at 95.2 percent power in coast down for the 1R32 refueling outage, the reactor automatically tripped due to flux rate. All systems responded normally to these conditions with auxiliary feedwater initiating as expected. Operations stabilized the plant without complication. Decay heat is being removed via a main feedwater pump to the steam generators. Unit 2 is not affected and remains at 100 percent power. Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and an eight-hour report per 10 CFR 50.72(b)(3)(iv)(A), specified system actuation. The cause of the scram is under investigation. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 3 | MN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-08-26
54858 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-08-25 | 2020-08-25 20:35 | 2020-08-25 | AGREEMENT STATE REPORT - SOURCE POTENTIALLY DAMAGED BY FIRE The following information was received by the state of California via email: "On 08/25/20, the California Office of Emergency Services contacted the Radiologic Health Branch (RHB) to report potential fire damage to a moisture gauge stored inside a barn located in Napa County, CA. The gauge involved is a CPN International, Inc. Model 503, moisture gauge containing 50 milliCuries of Am-241:Be. "The Radiation Safety Officer (RSO) hasn't been to the incident location, however, he confirmed that the barn where the gauge was stored and the adjacent house have been burned down during the wildfire. The gauge is presumed to have been damaged by the fire; however, due to high temperature resistant construction of the source, the source integrity may not have been affected. According to the RSO, the property is located in a remote area in Napa County, and the entrance to the property is secured by two locked metal gates. Access by the general public is not anticipated. The RSO had already contacted the vendor, Instrotek for disposal of the damaged gauge. The RHB will be coordinating with Instrotek and intends to accompany Isotek if Isotek goes to the site. The United States Environmental Protection Agency has also been informed, and it is possible they may be involved in the gauge recovery." California Incident No.: 082520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-09-02
54857 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-24 | 2020-08-25 16:52 | 2020-08-25 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER STUCK OPEN The following information was received from the Texas Department of State Health Services (the Agency) via email: "On August 25, 2020, the Agency was notified by the licensee's consultant that during routine inspections the shutter on a Vega model SHGL-1 nuclear gauge containing a 2,000 milliCurie (original activity) cesium-137 source was stuck in the open position. Open is the normal position for the shutter. The gauge does not create an exposure hazard to any individual. The licensee's service provider is aware of the failure. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-09-02
54856 | 0 | DIAMOND TECHNICAL SERVICES |  |  |  |  | 2020-07-29 12:40 | 2020-08-25 14:26 | 2020-08-25 | NON-AGREEMENT STATE REPORT: FAILURE OF SOURCE CONNECTION The following summary was received from the licensee via email: On 1240 EDT on 7/29/2020, a Radiographer for Diamond Technical Services discovered that the source for a radiography projector disconnected from the drive cable. The radiation barriers were expanded, additional shielding was laid down, and site personnel were notified to clear the immediate area. No personnel were exposed at the time of the discovery. The source projector is a Sentinel 880D, S/N: 12726 with an Iridium-192 source with an activity of 52.5 Curies. The Operations Manager and Radiation Safety Officer traveled to Alma, WV from their offices in Blairsville, PA with emergency equipment and radiation safety supplies. At 1715 EDT, the source was retrieved and secured in its shielded position. There were no indications of excessive exposures. The preliminary cause of the source disconnection was determined to be fatigue failure. The components will be shipped to QSA for manufacturer evaluation and inspection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Safety Equipment Failure | [9 empty] | Non Emergency | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-08-25
54855 | 0 | Grand Gulf | 1 |  |  | [1] GE-6 | 2020-08-24 23:05 | 2020-08-25 02:26 | 2020-08-25 | REACTOR SCRAM AFTER LOSS OF FEEDWATER - GRAND GULF "On August 24, 2020 at 2305 CT at Grand Gulf Nuclear Station (GGNS) an Automatic Reactor Scram occurred after a trip of the Reactor Feed Pump B and subsequent lowering of reactor water level to 11.4 inches Narrow Range. The scram occurred with Reactor Power at 14% and the main generator offline. "All control rods fully inserted and there were no complications. All systems responded as designed. "Main Steam Isolation Valves were manually closed to control reactor cooldown, Currently GGNS reactor pressure is being maintained at 450-600psig. Reactor water level is being maintained with condensate through startup level control. "No radiological releases have occurred due to this event from the unit. "The NRC Resident has been notified." Decay heat is being removed via the main condenser. Notified R4DO. | 0 | 0 | 0 | 14 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS Actuation - Critical |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | Non Emergency | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-08-25
54854 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2020-08-24 | 2020-08-24 16:36 | 2020-08-24 | AGREEMENT STATE REPORT - TWO LOST SOURCES The following is a summary of information received via email: On August 24, 2020, the licensee notified the New Jersey Department of Environmental Protection of two lost sealed sources. The sources had been sent from the licensee's Austin, Texas facility to their Fair Lawn, New Jersey facility, and are reported as missing by the shipper. The two sources were Ni-63 foil sources with an activity of 10 mCi each (S/N: AO-2484 and AO-5478). Each source was in a Life Technology Holdings, model Trace 1300, electron capture detector (S/N: 719420216 and 719420261). The shipper has been searching for the sources, but at this time considers them missing with little likelihood of recovery. The shipper's tracking system indicates that the sources were delivered to the licensee's Fair Lawn facility, but that location has stated they never received the sources. The address to which the sources were reportedly delivered does not exist and the person who reportedly signed for the package is unknown to the licensee. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2020-09-01
54853 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2020-08-17 | 2020-08-24 10:48 | 2020-08-26 | <br><br>EN Revision Imported Date : 8/27/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - LEAKING CHECK SOURCE The following was received from the State of Washington via email: "Framatome notified the State of Washington of a leaking 5 microCi Cs-137 check source that was identified on 8/17/2020. A set of stack samples showed evidence of Cs-137 contamination, leading the Radiation Safety Officer for the licensee to contact the Radiological Safety Supervisor to investigate into the possibility of a leaking Cs-137 check source. A visibly damaged source was identified and a leak test of the source revealed 0.02 microCi of removable material. The source storage area was surveyed to determine if there was any additional contamination, but none above the licensee's limits for action was identified. The source was contained and placed in storage to be held for disposal." Washington Incident No.: WA-20-017 * * * UPDATE ON AUGUST 26, 2020 AT 1250 EDT FROM ANDREW HALLORAN TO BRIAN LIN * * * The following information was received from the State of Washington via email: "The leak test was performed in accordance with approved procedures using an instrument that was appropriate and in calibration. The source was part of a source jig used for routine instrument checks around the site. According to the Radiation Safety Officer, the source was likely damaged from impact against a hard surface during routine use." Notified R4DO (Kellar) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2020-09-01
54852 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2020-08-21 | 2020-08-22 09:29 | 2020-09-16 | <br><br>EN Revision Imported Date : 9/17/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - BROKEN SHUTTER ON FIXED GAUGE The following was received from the Iowa Department of Public Health via email: "On Friday August 21, 2020 the registrant reported to the Iowa Department of Public Health that they had discovered, on that day, a broken shutter handle on a Berthold Technologies model LB 7440 fixed gauging device. The registrant also indicated that an outside vendor had been contacted to repair the handle. This device is located on a barge used for dredging the Mississippi River. There is no threat to the health and safety of the public. "This event will be updated in NMED once the required 30 day written report has been received." * * * UPDATE ON 09/16/2020 AT 0758 EDT FROM RANDAL DAHLIN TO BETHANY CECERE * * * Iowa Item Number IA200002. "On September 9, 2020, the manufacturer of the device arrived on site and found that the stem that is rotated by the open/close bar on the shield had broken off. The manufacturer's technician replaced the shield, moved the source to the new shield, performed a device shield survey and performed a leak test of the source. The device and the shutter are working properly. The State considers this event closed." Notified R3DO (Feliz-Adorno) and NMSS_Events_Notification (by email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2020-08-31
54851 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-21 08:00 | 2020-08-21 15:08 | 2020-09-11 | <br><br>EN Revision Imported Date : 9/14/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - NUCLEAR GAUGE ENGULFED DURING FIRE The following information was received from the Texas Department of State Health Services (the Agency) via email: "On August 21, 2020, at 1307 CDT the Agency was notified by the licensee consultant (LC) that a fire was burning on one of its dredges off the coast Corpus Christi, Texas. The LC stated the drudge had a 250 milliCurie (original activity) [Cs-137] source in a Berthold model 7440 nuclear gauge installed on a pipe for density measurement. The LC did not have any other information on the location, but knew the dredge was in between 40 and 50 feet of water. The LC stated that the personnel on board were fighting the fire. The LC stated they believed that the gauge would be engulfed by the fire. The LC stated they would supply additional information once the fire is out and they have a chance to inspect the equipment. "At 1553 CDT the LC contacted the Agency and stated the dredge workers were able to take dose rate reading about two feet from the gauge and the reading was 26 millirem per hour. The LC stated that the steel was still too hot to stay very long in the area. The LC stated (when asked) that they believe the fire is out. The LC stated the current priority on the drudge was locating several missing individuals. The LC stated they directed personnel on the drudge to take a contamination survey on the gauge as soon as possible. The LC stated the gauge source serial number was 0025-06. "A search of news sources in Corpus Christi, Texas by the Agency found that a barge had struck an underwater natural gas line at a facility in Corpus Christy, Texas. This information was verified by the licensee's LC. The news reports stated the event occurred at about 0800 CDT. The report stated that the Texas Division of Emergency Management and Texas Department of Public Safety personnel are on the ground to provide support, and the Texas Commission on Environmental Quality is monitoring air quality in the area. The United States Coast Guard is assisting in the fire fighting and search for individuals. The name of the dredge involved was provided in several reports. The Agency contacted the LC verified the ship was owned by the licensee. This information was verified by the Agency by reviewing four different news sources. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9784 * * * UPDATE ON 8/21/20 AT 2337 EDT FROM ARTHUR TUCKER TO ANDREW WAUGH * * * The following information was received from the Texas Department of State Health Services (the Agency) via email: "On August 21, 2020, at 2200 CDT, the Agency was notified by the LC that the dredge has sunk. The dredge is believed to be in 45-50 feet of water on its starboard (stbd) side. The gauge is located on the stbd side of the vessel and the shutter was in the open position. The LC stated that after talking to the radiation safety officer who is at the location the LC stated the dose rate they were able to take earlier today and was reported as 26 mR/hr at 2 feet was 26 mR/hr at 6 feet. A request for the composition of the source material has been made to the manufacturer. The search for four missing persons continues and is the current priority." Notified R4DO (Taylor), NMSS (Jamerson), and NMSS Events Notifications (email). * * * UPDATE ON 8/22/20 AT 0915 EDT FROM ARTHUR TUCKER TO THOMAS KENDZIA * * * The following information was received from the Texas Department of State Health Services (the Agency) via email: "On August 22, 2020 the manufacturer confirmed the source involved in this event is made of ceramic source material and is double encapsulated." Follow-up phone call to the Agency confirmed that the fire is out and the LC and the RSO are working on a recovery plan. First priority remains the search for the four missing persons. Notified R4DO (Taylor), NMSS (Jamerson), and NMSS Events Notifications (email). * * * UPDATE ON 8/23/20 AT 1444 EDT FROM ARTHUR TUCKER TO ANDREW WAUGH * * * The following information was received from the Texas Department of State Health Services (the Agency) via email: "The Agency has contacted the licensee's radiation safety officer (RSO) and received the following information. The RSO stated that before the vessel sank a hazmat crew was able to get eyes on the gauge. The hazmat team stated the gauge did not appear to have been damaged by the fire. The area around the gauge also did not appear to have been damaged by the fire. The RSO stated the current plan is to raise the vessel, survey the gauge, and close the shutter. The RSO stated they would send a written report providing additional information." Notified R4DO (Taylor), NMSS (Jamerson), and NMSS Events Notifications (email). * * * UPDATE ON 8/24/20 AT 2209 EDT FROM ARTHUR TUCKER TO ANDREW WAUGH * * * The following information was received from the Texas Department of State Health Services (the Agency) via email: "The Agency contacted the licensee's consultant (LC) on August 24, 2020, and requested an update on the event. The consultant stated he had received a written report completed by the licensee's RSO for his review. The LC stated he is on vacation but hoped to forward it to the Agency today. As of the writing of this update the report has not been received by the Agency. The LC stated they had a contractor in place to retrieve the vessel. Once raised the plan is to inspect the gauge, perform surveys of the gauge, and close the shutter. The raising of the vessel is not scheduled to take place until next week or the week after that due to difficulties getting the needed equipment in place. In addition, the local weather may hamper recovery activities." Notified R4DO (Kellar) and NMSS Events Notifications (email). * * * UPDATE ON 8/25/20 AT 2046 EDT FROM ARTHUR TUCKER TO BRIAN LIN * * * The following information was received from the Texas Department of State Health Services (the Agency) via email: "On August 25, 2020, the Agency received the following information from the licensee's radiation safety officer: 'We do not have the equipment to do a deep-water survey of the radiation source. T&T our salvage contractor is ordering the equipment to do the survey of the source to insure the safety of their divers because the source has not had an up-close survey since the vessel sunk. We have taken a survey above the water and have not picked up any radioactivity.' The report from the licensee has been delayed while a review is completed. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Kellar) and NMSS Events Notifications (email). * * * UPDATE ON AUGUST 27, 2020 AT 1136 EDT FROM ART TUCKER TO BRIAN LIN * * * The following information was received from the Texas Department of State Health Services via email: "The licensee has confirmed that a member of a hazmat team who was able to inspect the gauge from a small boat next to the vessel prior to it sinking stated the gauge appeared undamaged, the wires leading to and from the gauge appeared to be undamaged, and that painted surfaces in the area of the gauge did not appear to be damaged by heat or the fire. The licensee stated they were unable to locate any pictures of the gauge prior to the vessel sinking. The licensee stated that their salvage contractor is ordering the equipment to do an underwater survey of the source to insure the safety of their divers because the source has not had an up-close survey since the vessel sunk. The licensee stated they have taken a survey in the water above the vessel and have not picked up any radioactivity. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Kellar) and NMSS Events Notifications (email). * * * UPDATE ON 9/11/20 AT 1653 EDT FROM ARTHUR TUCKER TO ANDREW WAUGH * * * The following information was received from the Texas Department of State Health Services (the Agency) via email: "On September 11, 2020, the licensee reported the dredge was raised to the surface and the gauge was recovered on the dredge. The gauge was undamaged, and the licensee was able to shutter the source. Dose rates at the gauge were reported as normal. The shutter has been locked closed and the source will be disposed by a contractor. Additional information will be provided via the Nuclear Materials Events Database." Notified R4DO (Warnick) and NMSS Events Notifications (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-08-31
54850 | 0 | Uniformed Services University |  |  |  |  | 2020-08-18 19:00 | 2020-08-21 13:03 | 2020-08-21 | POTENTIAL OVEREXPOSURE RESULTING IN BURN The following is a summary from a phone call with the Radiation Safety Officer (RSO) at Uniformed Services University of Health Services: At the Uniformed Services University of Health Services, a research individual, authorized to operate the self-shielded CO-60 irradiator, last operated the irradiator on Tuesday, August 18, 2020 at 1900 EDT. On Wednesday, August 19, 2020, she experienced a burn on her left hand and went to the hospital believing it to be from a radiation overexposure. From information she received at the hospital, in order for her to have received that burn from a radiation overexposure the dose equivalent would have to be estimated to be 600R. The RSO does not believe that to be the case since the highest surveyed area both before and after the event where her hand could have come in contact was a thin pipe reading 150mR/hour on contact. The individual has been in contact with her physician, fingernail samples have been sent out for analysis, the Radiation Emergency Assistance Center/Training Site (REAC/TS) has been contacted by both the individual and the RSO, and her TLD has been sent out for analysis. The site has taken the machine out-of-service until more information can be collected. The RSO had been in contact with specialists in Region 1. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Pers Overexposure/Tede >= 5 Rem | [9 empty] | Non Emergency | 1 | MD | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2020-08-31
54849 | 0 | River Bend | 1 |  |  | [1] GE-6 | 2020-08-21 09:18 | 2020-08-21 12:53 | 2020-08-21 | MANUAL REACTOR SCRAM "On August 21, 2020 at 0908 CDT, River Bend Station was operating at 100% reactor power when reactor recirculation pump 'B' tripped. At 0918 CDT, a manual reactor scram was inserted at 67% reactor power after receiving indications of thermal hydraulic instability as indicated by flux oscillations on the period based detection system (PBDS) and average power range monitors (APRMs). All control rods fully inserted and there were no complications. All systems responded as designed. Currently River Bend Station Unit 1 is stable and pressure is being maintained using turbine bypass valves. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical and 10 CFR 50.72 (b)(3)(iv)(A) Specified System Actuation as result of Group 3 isolations. "NRC Resident Inspector has been briefed on this event. "No radiological releases have occurred due to this event from the unit." | 0 | 0 | 0 | 67 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | Non Emergency | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-08-21
54848 | 0 | Perry | 1 |  |  | [1] GE-6 | 2020-08-21 09:53 | 2020-08-21 12:42 | 2020-08-21 | STANDBY LIQUID CONTROL SYSTEM INOPERABLE "At 0953 EDT on 8/21/20, it was discovered that both trains of the standby liquid control system were simultaneously inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). All control rods remained operable during this time period. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." Both trains of the standby liquid control system were declared inoperable due to an inadvertent addition of water to the storage tank which caused the boron concentration in the tank to go low out of specification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Pot Unable To Safe Sd | Accident Mitigation |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2020-08-21
54847 | 0 | Turkey Point | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2020-08-20 23:54 | 2020-08-21 03:12 | 2020-08-21 | MANUAL REACTOR TRIP DUE TO STEAM GENERATOR WATER LEVEL CONTROL "On 08/20/20 at 2354 [EDT], with Unit 3 in Mode 1 at approximately 34% RTP [Rated Thermal Power], the reactor was manually tripped. This was due to Steam Generator Water Level control issues that resulted in the only Steam Generator [S/G] Feed Pump tripping on low suction pressure. Unit 3 reactor was tripped manually upon the loss of the last running feed pump. All other systems operated normally. Auxiliary Feedwater initiated as designed to provide S/G water level control. EOPs have been exited and General Operating Procedures (GOPs) were entered. Unit 3 is stable in Mode 3 at normal operating temperature and pressure. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) "The NRC Resident Inspector bas been notified." Decay heat removal is by the steam dumps to atmosphere. Unit 4 is not affected. The cause of the low suction feed pressure to the steam generator feed pump is under investigation. | 0 | 0 | 0 | 34 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-08-21
54846 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-06-09 | 2020-08-19 18:14 | 2020-08-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received via e-mail: One tritium exit sign, model number SLXTUIGW10, containing 7.09 Ci of H-3 was reported as missing during annual registration. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-08-27
54845 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-06-10 | 2020-08-19 18:08 | 2020-08-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received via e-mail: New owner reported one tritium exit sign lost. Model number SLXTU1RW10 containing 7.09 Ci of H-3. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-08-27
54844 | 0 | Turkey Point | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2020-08-19 13:25 | 2020-08-19 15:57 | 2020-08-19 | AUTOMATIC REACTOR TRIP DURING STARTUP "On 08/19/20 at 1325 EDT, during Unit 3 startup at approximately 0 percent rated thermal power, the reactor automatically tripped. The trip was automatically initiated from the Source Range Nuclear Power Instrumentation. All other systems operated normally. Operations stabilized the plant in Mode 3. Decay heat is being removed by Steam Dumps. Unit 4 is not affected. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B). "The NRC Resident Inspector has been notified." The cause of the Source Range Nuclear Power Instrumentation trip is under investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | RPS Actuation - Critical |  |  |  | IMode1: Startup; FMode1: Hot Standby | Non Emergency | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-08-19
54843 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-08-18 | 2020-08-19 00:19 | 2020-08-19 | AGREEMENT STATE REPORT - MISSING SOURCE ROD SHUTTER The following report from the Arizona Department of Health Services (Department) was received by email: "On August 18, 2020, during a routine inspection, the Department discovered that a licensee was in possession of a portable gauge which appeared to be missing its Cs-137 source rod shutter. The gauge was a Troxler Model 3430, Serial# 38482, containing 8 milliCuries of Cesium-137 and 40 milliCuries of Americium-241/Beryllium. While performing a survey of the gauge, inspectors recorded an exposure rate of 175 mR/hr over the shutter opening while the handle was in its locked position. "The Department has requested additional information and continues to investigate the event." AZ Incident Number: 20-014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-09-02
54842 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2020-08-14 | 2020-08-18 17:36 | 2020-08-18 | AGREEMENT STATE REPORT - LOST SOURCE The following information was received from the Alabama Department of Public Health via email. "On August 14, 2020, the Agency [Alabama Department of Public Health] received e-mail communication from PPG Industries, a general license device registrant in Huntsville, Alabama. The registrant reported that apparently a registered device containing 10 milliCuries of polonium-210 (at assay) was unable to be located for inventory. The registrant reported that the area of use was searched for 3 weeks; the device remains unaccounted for. The device has been reported to the manufacturer (NRD Systems) as lost." Alabama Event No.: 20-19 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2020-08-26
54841 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-08-18 | 2020-08-18 16:47 | 2020-08-18 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The following information was received from the Colorado Department of Health via email. The licensee is unable to locate sixteen tritium exit signs that have an activity of 11.5 Ci each. The signs may have been removed by a contractor. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-08-26
54840 | 0 | OHIO DEPARTMENT OF HEALTH |  |  |  |  | 2020-08-18 | 2020-08-18 13:13 | 2020-08-18 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following report was received from the Ohio Department of Health via email. "On August 14, 2020, the licensee attempted to treat a patient with Y-90 TheraSphere microspheres. Under the guidance of the manufacturer's representative, the AU [Authorized User] performed pre-patient checks on the device, including tubing patency check. After the infusion was started it became apparent the patient was not receiving the dose, and the licensee was unable to clear the blockage in the tubing. The procedure was terminated and the patient and referring physician were notified. Approximately 93% of the activity remained in the device. Static imaging was performed on the patient to determine the dose received. There was no measurable activity in the patient." Ohio Event No.: OH200004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-08-26
54839 | 0 | Turkey Point | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2020-08-17 21:13 | 2020-08-18 00:08 | 2020-08-18 | MANUAL REACTOR TRIP DUE TO RISING STEAM GENERATOR LEVEL "On 08/17/20 at 2113 EDT, with Unit 3 in Mode 1 at approximately 92% [Rated Thermal Power] RTP, the reactor was manually tripped. This was due to a turbine runback caused by CV-3-2011, Low Pressure Feedwater Heater Bypass Control Valve, failing open, followed by rising Steam Generator (S/G) levels. Unit 3 reactor was tripped manually when the 3C S/G Level reached 78% narrow range. Unit 3 Main Steam Isolation Valves were closed manually in accordance with Emergency Operating Procedure (EOP) network due to 38 MSR Main Steam Stop valve position indication lost. All other systems operated normally. Auxiliary Feedwater initiated as designed to provide S/G water level control. EOPs have been exited and General Operating Procedures (GOPs) were entered. Unit 3 is stable in Mode 3 at normal operating temperature and pressure. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." All rods are inserted, decay heat is being removed via S/G through normal secondary systems. The plant is in normal electrical line up. Lightning strike is believed to be the initial cause of the runback. | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-08-18
54838 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-08-05 10:20 | 2020-08-14 17:03 | 2020-08-14 | AGREEMENT STATE REPORT - RAM PACKAGES SWITCHED IN ERROR The following email was received from the Massachusetts Radiation Control Program (the agency) via email: "On August 5, 2020, InviCRO reported receiving in error on same day a White I package of 140 mCi Lu-177. Receipt survey recorded a package surface dose rate of 0.2 mRem/hr. The received package activity exceeded their license radioactive material possession limit of 125 mCi. Package held by licensee in secure storage until activity falls below license limit (Lu-177 half-life is 6.7 days). The intended activity as requested by the licensee was 60 mCi. Package ordered through Radiomedix in Texas who forwarded order to supplier (ITM Medical isotopes GmbH) in Germany. Package sent from Germany arrived in [common carrier] US facility and directly forwarded to customer without going through Texas. Agency contacted [common carrier] and Texas Department of State Health Services. Apparent cause was [common carrier] accidentally switching labels/paperwork on two similar Lu-177 packages. The package originally intended for InviCRO was forwarded to a customer licensed in Indiana. Indiana customer (Endocyte) notified by Radiomedix. All US parties identified above are aware of incident. Radiomedix continuing its internal investigation. Agency left detailed voicemail messages (including circumstances, package receipt date and activity) at Indiana Department of Homeland Security and Indiana Department of Health. Agency determined this to be a 30-day reportable event and considers this event currently still open." MA Event Number: 20-4230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-08-24
54837 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-13 | 2020-08-13 23:28 | 2020-08-14 | <br><br>EN Revision Imported Date : 8/17/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - FIRE INVOLVING OIL WELL LOGGING SOURCE "On August 13, 2020, the Agency [Texas Department of State Health Services] was contacted by the Nuclear Regulatory Agency (NRC) and notified that they had been contacted by a State of Texas licensee. The NRC still had the licensee on their bridge line and tied the Agency into the call with the licensee. The licensee's radiation safety officer (RSO) reported that one of their well service blending trucks was engaged in a fire. The well is located near Mentone, Texas. The truck has a TN model 5190 nuclear gauge containing a 200 milliCurie cesium - 137 source installed on the piping system. The gauge was purchased in December 2019. At the time of the call (2121 CDT) the fire was still burning, and a fire department was on scene. The RSO believed the fire department was aware of the source. The RSO stated all their personnel had been evacuated from the scene of the fire. There is no way to know the status of the gauge shielding or of the source. The RSO agreed to contact the Agency when the fire was put out, and after completing a survey of the gauge. Additional information will be provided as it is received in accordance with SA-300." TX Incident #: I-9783 Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, CISA Central, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * RETRACTION ON 8/14/2020 AT 2051 EDT FROM ART TUCKER TO KERBY SCALES * * * The following retraction was received from the state of Texas via email: "On August 14, 2020, the licensee reported that after the fire was extinguished it found that the fire did not reach the gauge or equipment around it. This included electrical wiring and rubber hoses which showed no damage from the fire. A portion of the equipment the gauge was mounted to did have some fire damage. An Agency radioactive material inspector went to the site and performed a dose rate survey on the gauge. Based on this survey, it does not appear there was any damage to the gauge shielding. There was a second gauge at the site, but it was not anywhere near the area of the fire and was not affected. It was also surveyed and did not appear to have had any damage. The dose rates taken on the gauges were similar. Based on this information this event does not meet the reporting criteria and is therefore retracted. The licensee has performed a leak test of the gauge and if the results are greater than the limit it will be reported in accordance with SA-30." Notified R4DO (Proulx), NMSS EO (Williams), IRD MOC (Gott), and NMSS Event Notifications (email). Additionally notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, CISA Central, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-08-21
54836 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2020-06-25 | 2020-08-13 16:36 | 2020-08-13 | AGREEMENT STATE REORT - MISSING I-125 SEED The following was received via fax from the New York State Department of Health: "On July 7, 2020, the [New York State] Department [of Health] was notified of a missing Iodine-125 localization seed (Best Medical International, Inc., Model 2301, Activity: 142 microCuries) at Roswell Park Cancer Institute in Buffalo, New York. An lodine-125 localization seed was removed from a patient in a procedure that took place on June 25, 2020, and is believed to have been lost in the intraoperative frozen section room in surgery. The RSO [Radiation Safety Officer] was informed of the missing seed on June 29, 2020. The facility conducted searches and surveys of the Surgery, Pathology, Radiation Safety and Environmental Services areas. Trash and regulated medical waste were also surveyed and inspected. It is believed that the seed will be recovered from the facility's regular trash, but more likely in the facility's radioactive waste." New York State Event Report Number: NYDOH 20-02 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2020-08-21
54835 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-08-11 | 2020-08-13 14:47 | 2020-08-13 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE "The [Pennsylvania] Department [of Environmental Protection (DEP)] received notification from a licensee on August 12, 2020, of a medical event involving Yttrium-90 Sir-Spheres. The licensee believes a patient received only 47% of the prescribed dose. The prescribed dose was 1.44 GBq and the delivered dose is believed to be 0.67 GBq. Preliminary cause is believed to be a clotted catheter. The licensee continues to investigate the event. The patient and referring physician were informed following the procedure. The DEP is currently in contact with the licensee and will update this event as soon as more information is provided." PA NMED Event # PA2000016 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-08-21
54834 | 0 | Harris | 1 |  |  | [1] W-3-LP | 2020-08-13 09:38 | 2020-08-13 13:24 | 2020-08-13 | MANUAL REACTOR TRIP DUE TO DROPPED CONTROL ROD "On August 13, 2020, at 0938 EDT, with Harris Nuclear Plant Unit 1 in Mode 1 at 100 percent power, a control rod dropped during control rod testing. This is considered to be an unanalyzed condition and requires a manual reactor trip in accordance with plant procedure. All safety systems functioned as expected. Auxiliary Feedwater started as designed and was secured. Steam generator levels are being maintained by Main Feedwater through the feedwater regulator bypass valves. Decay heat is being removed by using the condenser steam dump flow path. Due to the RPS actuation, this event is being reported as a four hour non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Due to the unanalyzed condition and unplanned Auxiliary Feedwater actuation, this event is also being reported as an eight hour non-emergency notification per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Unanalyzed Condition | Valid Specif Sys Actuation |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2020-08-13
54833 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2020-08-10 | 2020-08-12 14:48 | 2020-08-12 | AGREEMENT STATE REPORT - ABANDONED TRITIUM SIGN The following information was received via a letter from Goodwill Industries to the Oregon Department of Health Radiation Protection: "Goodwill Industries of Lane and South Coast Counties found an abandoned exit sign (Tritium) in their inventory. The exit sign was sent to SRB Technologies, INC. at 2580 Landmark Drive, Winston-Salem, NC 27103 (NC Radioactive Materials License# 034-0534-2) for proper disposal. One sign was sent. The sign had been manufactured by lsolite Safety Light Corp. Bloomberg, PA/ Model Number 2040. Serial Number 0412499. Date of Manufacture 12-84. Life rating/ Curies of 10 years 9.8ci. The device was never registered or installed at any of our sites as it was abandoned here. "The Oregon Department of Health Radiation Protection will attempt to find the original owner based on the serial number. Since the light has been disposed of properly and reporting is now entered per SA300, Oregon is requesting that this event be marked as complete and request closure of this event." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2020-08-20
54832 | 0 | Palo Verde | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2020-08-11 14:32 | 2020-08-12 11:24 | 2020-08-12 | FITNESS-FOR-DUTY - LICENSED OPERATOR VIOLATED THE FFD POLICY On August 11, 2020, at approximately 1432 MST, a licensed operator's test results were confirmed positive for use of a controlled substance following a random Fitness For Duty screening test. The individual's unescorted access has been terminated in accordance with station procedures. The NRC Resident Inspector has been notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Non Emergency | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2020-08-12
54831 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2020-08-11 11:30 | 2020-08-12 10:57 | 2020-08-12 | FIRE INVOLVING A CONTAINER POSSESSING LICENSED MATERIAL The following information was received from the state of Tennessee via email: "An incident took place while processing a liner with water filters and Dry Active Waste (DAW) in it during filter shredding operation in the Filter Shredding area of the Radioactive Material Solutions (RMS) Building on site. The container contained mixed fission and activation products with Co-60 as a primary contaminant. A fire was observed in the steel Final Form Container (FFC) liner through the remote observation. The size of the fire was limited to the container itself. The FFC is a steel liner where the material accumulates and is contained in preparation for sealing for disposal. The filter processing room was accessed via a hatch and a crane was used to seal the FFC. The fire suppression system was activated to cool down the FFC liner. The Oak Ridge Fire Department responded to the site. Since the fire was contained to the FFC liner, the Oak Ridge Fire Department did not enter the building. The area radiation and air effluent stack monitors did not alarm. Samples from air samplers are being analyzed for airborne material. Staff that remained in the building will undergo a bioassay to assess for potential uptake. A follow-up report will be submitted within 30 days." TN Incident No.: TN-20-116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-08-20
54830 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2020-08-10 17:30 | 2020-08-12 07:54 | 2020-08-12 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA DRIVE CABLE FAILURE This was received from the South Carolina Department of Health and Environmental Control via email: "On August 11, 2020, at 1500 (EDT), the Department (SC Department of Health and Environmental Control) was notified by the licensee that a drive cable used to crank out a source on a Spec 150 camera failed to function as designed. The radiographer was performing the initial source crank out of the source to check the 2 mR in any one hour boundary when he realized that the drive cable was not functioning properly and quickly retracted the source to the shielded position. The radiographer then contacted the Radiation Safety Officer (RSO) to provide him with the details. The RSO then cancelled the job for the night until the drive cable could be replaced. The RSO stated that there were no overexposures that occurred as a result of this incident. The RSO was informed by the Department's on-call duty officer that a 30-day written report will be required detailing the incident." The event occurred on Shaw Air Force Base. South Carolina Incident No: 54830 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2020-08-20
54829 | 0 | Peach Bottom | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2020-08-11 13:34 | 2020-08-11 20:22 | 2020-08-11 | LOSS OF TECHNICAL SUPPORT CENTER VENTILATION SYSTEM "At 1334 EDT on Tuesday August 11th, the Peach Bottom Atomic Power Station (PBAPS) Technical Support Center (TSC) Ventilation System lost power due to a trip of the Station Blackout (SBO) electric power supply breaker. The trip was due to a fault at the Conowingo Dam and Conowingo was not able to realign electric power to the SBO within an hour. Power restoration is complete and TSC Ventilation was restored at 1725 EDT. "This report is being submitted pursuant to 10CFR 50.72(b)(3)(xiii) as a Major Loss of Emergency Preparedness Capabilities due to a reduction in the effectiveness of the Onsite Technical Support Center (TSC). "The NRC Resident Inspector has been notified." | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-08-11
54828 | 0 | Diablo Canyon | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-08-10 09:15 | 2020-08-11 11:12 | 2020-08-11 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED SUPERVISOR "At 0915 PDT, on August 10, 2020, Pacific Gas and Electric determined a non-licensed employee supervisor had a confirmed positive during a random fitness-for-duty test. The employee's access to the plant has been terminated. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2020-08-11
54827 | 0 | WATERFORD STEAM ELECTRIC STATION |  |  |  |  | 2020-08-03 16:59 | 2020-08-10 17:05 | 2020-08-10 | PART 21 REPORT - DEFECT OF MASONEILAN 8012N-3C ELECTROPNEUMATIC POSITIONER The following was received from the licensee: "On August 3, 2020, Entergy Operations, Inc. (Entergy) completed an evaluation of a deviation at Waterford 3 which concluded the condition constitutes a defect pursuant to 10 CFR 21. The Waterford 3 Site Vice President was notified of the result of this evaluation on August 10, 2020. "The Masoneilan 8012N-3C electropneumatic positioner installed on Emergency Feedwater Valve EFW-223A locked during as-found diagnostic testing. Failure analysis concluded that the condition was due to an internal failure of the magnet-coil assembly due to the magnet base had poor solder joints. This has been attributed to a manufacturing defect. Entergy concluded that this condition could affect the ability to properly respond to an Emergency Feedwater Actuation Signal / Main Steam Isolation Signal if present on any of the four air operated Emergency Feedwater to Steam Generator flow control valves; therefore, it could have created a substantial safety hazard." Licensees affected: Waterford. The licensee notified the NRC Resident Inspector. Notified R4DO and the Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 4 | LA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-08-10
54826 | 0 | Duane Arnold | 1 |  |  | [1] GE-4 | 2020-08-10 12:58 | 2020-08-10 14:38 | 2020-08-10 | NOTICE OF UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER DUE TO HIGH WINDS At 1258 CDT on August 10, 2020, Duane Arnold Energy Center declared an Unusual Event due to a loss of offsite power due to high winds. The event at the single unit plant resulted in an automatic scram from 82 percent power (Mode-1) to zero percent power (Mode-3). They are headed to Mode-4. There is damage on site, but the Reactor Building is intact. All rods inserted and cooling is being addressed via Reactor Core Isolation Cooling (RCIC) for level control and Safety Relief Valves are removing decay heat to the torus. Both Standby Diesel Generator are running. The licensee notified the NRC Resident Inspector, the Iowa Department of Emergency Management, and the Linn County and Benton County Emergency Management agencies. Notified DHS SWO, FEMA Operations Center, CISA Central, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 08/10/2020 AT 1554 EDT FROM CURTIS HANSEN TO OSSY FONT * * * "This report is being made under CFR 50.72 (b)(2)(iv)(B) for an automatic reactor scram due to loss of offsite power due to high winds. "In addition, this report is being made under CFR 50.72 (b)(3)(iv)(A) and (B) due to PCIS [(Primary Containment Isolation System)] Groups 1, 2, 3, 4 and 5 [activating] due to loss of offsite power. All isolations went to completion. RCIC injecting for level control. "All rods fully inserted during the scram. The plant electrical line up is both SBDGs (Standby Diesel Generators) are running. "Decay heat is being removed via SRVs (Safety Relief Valves) to the torus. "Progress towards shutdown cooling. "NRC Senior Resident [Inspector] notified at 1448." Notified R3DO (Pelke). | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | Emergency Declared | Eccs Injection | RPS Actuation - Critical | Valid Specif Sys Actuation | IMode1: Power Operation; FMode1: Hot Shutdown | Unusual Event | 3 | IA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 0 | 2020-08-10
54825 | 0 | USAF |  |  |  |  | 2020-06-23 11:30 | 2020-08-10 07:10 | 2020-08-10 | LEAKING SOURCE FROM AIRCRAFT RADIUM DIAL The following summary of information was received via email: On June 23, 2020 at approximately 1130 [CDT], the Permit Radiation Safety Officer (PRSO) was working on a J-79 engine and proceeded to survey his work area. During the survey, he found measurements indicating contamination on a nearby table that contained an instrument dial. He did a direct measurement of the Oxygen Pressure Indicator dial, which is approximately 2 inches in diameter and found approximately 7000 Counts Per Minute (CPM) direct reading. The PRSO surveyed the covering over the table on which the dial was on and found approximately 100 CPM with the Ludlum 44-9 pancake style Geiger Muller (GM) probe. The area of the contamination he found was about the size of the probe area. Surveys of the cockpit and surrounding areas were all less than 20 disintegrations per minute (dpm)/100 square centimeter loose and 100 dpm/100 square cm total for Radium-226 in accordance with the Acceptable Surface Contamination Levels. The dial was removed from a restored aircraft in a publicly accessible part of the museum. The aircraft was originally surveyed in 1989 and the presence of the radium dial was not detected. Therefore, no radiological controls were implemented to prevent any possible public exposure. The quantity of Radium-226 was estimated at 2 microCuries for the dial. The dial was turned into the Air Force Radioactive Recycling and Disposal center for disposal. The contaminated portion of the table was cut out and disposed of. The open cockpit was surveyed to verify no presence of Radium-226. Any cleaning equipment for the cockpit and surrounding area of the aircraft were controlled and moved to a radioactive storage area. The licensee contacted Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Safety Equipment Failure | [9 empty] | Non Emergency | 3 | OH | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-08-10
54824 | 0 | Grand Gulf | 1 |  |  | [1] GE-6 | 2020-08-08 01:27 | 2020-08-08 05:34 | 2020-08-08 | REACTOR SCRAM DUE TO A TURBINE HIGH PRESSURE CONTROL VALVE MALFUNCTION On August 8, 2020, at 0127 CDT, Grand Gulf Nuclear Station was manually shut down due to a turbine high pressure control valve malfunction. Reactor pressure is being controlled with bypass control valves to the main condenser. Reactor level is being maintained with condensate and feedwater through startup level control. The plant is stable in MODE 3 and proceeding to cold shutdown. The cause of the 'D' high pressure control valve malfunction is under investigation at this time. All rods fully inserted and there were no complications. All systems responded as designed. This event is being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical. Additionally, at 0159 CDT, with all rods fully inserted and after the 0127 CDT manual reactor Scram, an automatic valid RPS actuation signal was received. This event is also being reported under 10 CFR 50.72(b)(3)(iv)(A), as an event or condition that results in a valid actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). | 0 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | Non Emergency | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-08-08
54823 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2020-08-06 15:30 | 2020-08-07 16:59 | 2020-08-07 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA GUIDE TUBE DENTED The following was received from the Tennessee Division of Radiological Health via email: "On August 6, 2020, World Testing radiographers were radiographing at Matrix Drilling in Lewisburg, Tennessee. They were radiographing pipes and one of the pipes (weighing approximately 1000 pounds) rolled onto the guide tube, denting it. They could not crank the source back in. They called the RSO [(Radiation Safety Officer)]. The guide tube was curled and making it more difficult to get the source back into the camera. They pulled on the crank to straighten out the guide tube and with enough pressure they were able to get the source past the dent and back into the exposure device. They placed lead on the collimator for additional shielding while working with it. The camera was a Sentinel, Model 880D, Serial number D-1120. The [Ir-192] source serial number was 96522G, with an activity of 44Ci. The source was exposed for approximately 4 hours. All personnel involved were wearing dosimetry. There were no overexposures." Tennessee Event Report ID No.: TN-20-114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-08-17
54822 | 0 | Department of Veterans Affairs |  |  |  |  | 2020-08-05 13:00 | 2020-08-06 16:32 | 2020-08-06 | MEDICAL EVENT "A Y-90 microsphere therapy administration was performed on August 5, 2020, [at VA Boston Healthcare System in Boston, Massachusetts]. The prescribed dose was intended for the right lobe of the liver. Post implant imaging on that day indicated that the dosage of microspheres was unintentionally administered to a portion of the left lobe of the liver. "The patient and the referring physician have been notified. "The National Health Physics Program (NHPP) will follow up with a written report in accordance with NRC requirements in 10 CFR 35.3045. "NHPP notified our NRC Region III Project Manager (Parker)." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Dose To Other Site > Specified Limits | [9 empty] | Non Emergency | 4 | AR | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2020-08-14
54821 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2020-08-06 | 2020-08-06 13:46 | 2020-08-06 | AGREEMENT STATE REPORT - STUCK SHUTTER The following is a summary of information received via email: On 8/6/2020, the licensee notified the Kentucky Radiation Health Branch of an event which had occurred on the same day. The shutter control mechanism malfunctioned on a nuclear gauge and the shutter could not be completely closed. The gauge has been taken out of service and no overexposures were reported as a result of this incident. A service provider has been contacted to help repair or replace the damaged gauge. The gauge is a Data Measurement Corporation Model AM-3E containing a 3 Ci Am-241 sealed source. Kentucky Event Report ID No.: KY200003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2020-08-14
54820 | 0 | Peach Bottom |  | 3 |  | [2] GE-4,[3] GE-4 | 2020-06-08 04:24 | 2020-08-06 13:10 | 2020-08-06 | INVALID SPECIFIED SYSTEM ACTUATION "This report is being made as required by 10 CFR 50.73(a)(2)(iv)(A) to describe an automatic actuation of containment isolation valves in more than one system. Because the actuation was invalid, this 60-day telephone notification is being made instead of a written LER [licensee event report], in accordance with 10 CFR 50.73(a)(1). "On 06/08/2020, at approximately 0424 EDT, a trip of the Unit 3 'A' reactor protection system (RPS) MG-Set resulted in a partial activation of the primary containment isolation system and inboard containment isolation valves closed in multiple systems. All affected Group III containment isolation valves were verified to be closed. It was determined that the normal power supply for the Unit 3 'A' RPS had failed. Power was transferred from the normal to the alternate source and the RPS 'A' channel was reset. "Investigation determined that the 3A RPS MG Set motor contactor coil winding had failed due to an internal short circuit. The motor contactor has been replaced. "The containment isolation was not due to actual plant conditions or parameters meeting design criteria for containment isolation. Therefore, this is considered to be an invalid actuation. "The NRC Resident Inspector has been informed of this notification." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-08-06
54819 | 0 | VT OFFICE OF RADIOLOGICAL HEALTH |  |  |  |  | 2020-03-27 | 2020-08-06 10:33 | 2020-08-06 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL REJECTED AT WASTE FACILITY The following is a summary of information received via email: On 3/27/20, the Vermont Department of Health (VDH) was notified that a waste transport truck was rejected at a waste facility in Concord, NH. The truck was rejected because radioactive material was detected in the waste. The truck was redirected to Goodenough Rubbish Removal in Brattleboro, VT, and instructed to isolate the waste. On 3/30/20, VDH Radiation Control responded to the waste center. The radioactive waste was identified as clay cat litter containing I-131 with a maximum dose rate of 8.04 mrem/hr on contact and 0.54 mrem/hr at one meter while background measurements were 10 microR/hr. The waste hauler was instructed to isolate the container in a remote section of the recycling center with the contents covered for 80 days. On 4/3/20, VDH issued Vermont Information Notice IN 20-001 (Release of humans and animals receiving I-131 therapy) to all Vermont radioactive materials licensees who are authorized to use I-131. This Information Notice recommends all affected licensees review their I-131 administration procedures, patient release criteria, and pet owner release instructions. On 6/26/20, a VDH inspector returned to survey the material, and found that the radiation levels of the material were indistinguishable from background. With the decay of the I-131 waste this incident has been closed out by VDH on 8/5/20. Vermont Incident No.: VT-20-002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | VT | OTH | AGR |  |  |  |  | 0 | 2020-08-14
54818 | 0 | VT OFFICE OF RADIOLOGICAL HEALTH |  |  |  |  | 2020-02-27 | 2020-08-05 17:17 | 2020-08-05 | AGREEMENT STATE REPORT RADIOACTIVE MATERIAL REJECTED AT WASTE FACILITY The following is a summary of information received via email: On 2/27/20, the Vermont Department of Health (VDH) was notified that a waste transport truck was rejected at a waste facility in Hudson Falls, NY. The truck was rejected because radioactive material was detected measuring 1.4 mrem/hr while background radiation was 0.01 mrem/hr. The truck was redirected to Tam Recycling in Pownal, VT, and instructed to isolate the waste. On 3/2/20, the Vermont Hazardous Materials Response Team (VHMRT) and a member of VDH Radiation Control responded to the recycling center. The radioactive waste was identified as human bladder control products which contained an estimated 4.6 microCi of I-131. The contents were double bagged and isolated in a remote storage area at the recycling center for to decay. On 4/3/20, VDH issued Vermont Information Notice IN 20-001 (Release of humans and animals receiving I-131 therapy) to all Vermont radioactive materials licensees who are authorized to use I-131. This Information Notice recommends all affected licensees review their I-131 administration procedures, patient release criteria, and pet owner release instructions. On 6/26/20, a VDH inspector returned to survey the material, and found that the radiation levels of the material were indistinguishable from background. With the decay of the I-131 waste this incident has been closed out by VDH on 8/5/20. Vermont Incident No.: VT-20-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | VT | OTH | AGR |  |  |  |  | 0 | 2020-08-13
54817 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2020-07-21 | 2020-08-05 13:19 | 2020-10-15 | <br><br>EN Revision Imported Date : 10/16/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - BROKEN SHUTTER The following is a summary of information received via email: On July 21, 2020, the licensee was conducting a semi-annual leak test and inventory when they discovered a shutter was not working on an in service source device. The source has been barricaded and appropriate warnings have been posted. An offsite technician is being contacted to replace the device. The device is an Ohmart Model A-2102 density gauge with a 100 mCi Cs-137 source. * * * UPDATE ON 8/6/20 AT 1757 EDT FROM SHATAVIA WALKER TO ANDREW WAUGH * * * The following is a summary of information received via email: The broken shutter concerned in this event was stuck in the open position. Notified R1DO (Arner) and NMSS Event Notifications via email. * * * UPDATE ON 10/15/2020 AT 1614 EDT FROM THOMAS GRAFTON TO OSSY FONT * * * The following update was received from the state of Georgia via email: "A qualified technician from BBP installed the new source on September 23, 2020. The old source was sent back to QSA [Global, Inc.] with a confirmation receipt [dated October 2, 2020]." Notified R1DO (Jackson) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-08-13
54816 | -1 | Millstone |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2020-08-04 17:45 | 2020-08-04 22:43 | 2020-08-19 | <br><br>EN Revision Imported Date : 8/20/2020<br><br>EN Revision Text: BOTH SERVICE WATER HEADERS DECLARED INOPERABLE On 8/4/20, at 1745 EDT, Millstone Unit 2 entered technical specification (TS) 3.0.3 due to both service water headers being declared inoperable because strainer differential pressures (D/Ps) were greater than 9 psid. The high service water strainer D/P was the result of heavy debris impingement caused by tropical storm Isaias. To reduce heat loads and service water flow, Unit 2 reduced power to 75 percent. One service water header was restored to operable at 1816 EDT, at which time TS 3.0.3 was exited. At 1843 EDT both service water headers were declared operable. The NRC Resident Inspector has been notified. * * * RETRACTION ON 8/19/2020 AT 1141 EDT FROM ERIC DONCH TO KIRBY SCALES * * * "The purpose of this call is to retract a report made on August 4, 2020, NRC Event Number EN 54816 describes a condition at Millstone Power Station Unit 2 (MPS2) in which both trains of service headers were declared inoperable due to service water strainer differential pressures greater than 9 psid. "The condition was reported to the NRC pursuant to 10 CFR 50.72(b)(3)(v)(A), (B) and (D) via an 8 hour prompt report as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition, remove residual heat and mitigate the consequences of an accident. "Upon further review, MPS2 determined that there was no loss of safety function. An engineering evaluation supports the conclusion that a strainer differential pressure of 16 psid would not challenge the system flow distribution during worst case conditions. The evaluation also demonstrates that flowrates on both headers were observed to be unaffected during the timeframe of the high strainer differential pressure conditions. Therefore, both service water headers would have provided the required flows to perform their safety function. "Therefore, this condition is not reportable and NRC Event Number EN 54816 is being retracted. "The basis for this conclusion has been provided to the NRC Resident Inspector." Notified R1DO (Greives). | 0 | 75 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Pot Unable To Safe Sd | Pot Rhr Inop | Accident Mitigation |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 1 | CT | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2020-08-04
54815 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-03 | 2020-08-04 21:21 | 2020-08-04 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following information was received from the Texas Department of State Health Services (the Agency) via email: "On August 4, 2020, the Agency was notified by the licensee's radiation safety officer (RSO) that an event occurred during the administration of Y-90 TheraSpheres on August 3, 2020. The RSO stated the written directive prescribed dosage was 22.3 mCi. During the administration of the TheraSpheres, the pressure observed by the Authorized User (AU) became significantly less than expected, and activity leaving the dose administration vial into the catheter decreased significantly before the entire dose could be delivered. The RSO stated a TheraSpheres (Boston Scientific) representative was present during the procedure and assisted the authorized user through troubleshooting, and remote consultation with TheraSpheres medical specialists. However, flow from the dose administration vial could not be re-initiated. The AU chose to end the procedure. "Following survey of the dose administration vial in the hot lab, it was determined that approximately 7.1 mCi (31.8 percent) was delivered to the patient. The RSO stated that their initial assessment is that this was the result of a device malfunction. There were no adverse effects to the patient. It is likely that a second procedure will be scheduled to complete the procedure. The RSO stated that the patient and referring physician were notified. "This is the first event involving TheraSpheres reported to the Agency by this licensee. "The RSO stated additional information on the event will be provided within the next 10 days. Additional information will be provided as it is received by the Agency in accordance with SA-300." Texas Incident Number: 9782 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-08-12
54814 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-08-04 11:20 | 2020-08-04 15:38 | 2020-08-04 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA The following is a summary of information that was received from the Louisiana Department of Environmental Quality via email: On August 4, 2020, at 1120 CDT, at a job site in New Iberia, LA, the drive cable on one of the licensee's industrial radiography cameras broke six inches from the drive cable to source cable connector. The radiographers set up a 2mR boundary after being unable to retract the source into a shielded position. One of the licensee's radiation safety officers (RSO) was called to the scene and was able to retrieve the source. During this event the RSO received a dose of 313 mR and the crew received 16 and 11 mR according to their insta-dose badges. The radiography camera is a SPEC 150 (s/n: 2131) with a 56 Ci Ir-192 source (s/n: BF2401). Event Report ID No.: LA20200007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-08-12
54813 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2020-08-03 17:00 | 2020-08-04 13:29 | 2020-08-04 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA The following is a summary of information received from the Alabama Department of Public Health via telephone: On August 3, 2020 at approximately 1700 CDT, the licensee was working at an asphalt plant in Mulga, AL, when one of its radiography cameras was damaged. The source of the radiography camera was being exposed when a magnetic stand, which was attached to the source, fell and crushed part of the guide tube. Multiple efforts to retrieve the source were unsuccessful. The licensee's radiation safety officer (RSO) responded to the scene. The RSO was able to retract the source after cutting part of the guide tube. No un-badged personnel received any dose as part of the event and applicable dosimetry badges have been sent for emergency processing. The camera is being sent to the manufacturer for investigation. Alabama Incident Report No.: 20-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2020-08-12
54812 | 0 | Brunswick | 1 |  |  | [1] GE-4,[2] GE-4 | 2020-08-03 23:12 | 2020-08-03 23:31 | 2020-08-04 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF OFFSITE POWER At 2312 EDT, on August 4, 2020, Brunswick Unit 1 declared an Unusual Event due to a loss of offsite power. The unit was at approximately 20 percent power and was not synced to the grid when the unit automatically scrammed. All control rods fully inserted. Emergency Diesel Generators started and began powering the safety buses. Safety systems actuated as expected. The Unit also experienced a loss of Fuel Pool Cooling and Cleanup System, but one pump was returned to service. Unit 2 remains at 100 percent power and is unaffected. The licensee notified State and local governments, as well as the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE FROM MARK TURKAL TO DONALD NORWOOD AT 0120 EDT ON 8/4/2020 * * * "At approximately 2302 EDT, a loss of offsite power occurred on Unit 1. This resulted in a Reactor Protection System (RPS) actuation. Per design, emergency diesel generators 1 and 2 properly started and loaded to their respective emergency buses. The Reactor Core Isolation Cooling (RCIC) system was manually started and is being used to control reactor water level. The High Pressure Coolant Injection (HPCI) system was manually started and is being used for pressure control. As previously reported, an Unusual Event was declared at 2312 EDT due to the loss of offsite power. At the time of the event, Unit 1 was in the process of shutting down for maintenance associated with a ground on the main generator. "Due to the RPS actuation while critical, this event is being reported as a four-hour, nonemergency notification per 10 CFR 50.72(b)(2)(iv)(B). "As a result of the reactor trip, reactor water level reached low level 1 (LL1). The LL1 signal causes a Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sample isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL1 isolations occurred as designed; the Group 8 valves were closed at the time of the event. Per design, the loss of offsite power also caused a Group 1 (i.e., main steam isolation valve) isolations. "Due to the Emergency Diesel Generator and Primary Containment Isolation System (PCIS) actuations, this event is also being reported as an eight-hour, nonemergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A). "Unit 2 was not affected. There was no impact to the health and safety of the public or plant personnel. The safety significance of the event is minimal. All safety related systems operated as designed. "Investigation of the cause of the loss of offsite power is in progress." The licensee notified the NRC Resident Inspector. Notified R2DO (Inverso). | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | Emergency Declared | RPS Actuation - Critical | Valid Specif Sys Actuation |  | IMode1: Power Operation; FMode1: Hot Shutdown | Unusual Event | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2020-08-03
54811 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-08-03 | 2020-08-03 21:55 | 2020-08-03 | AGREEMENT STATE REPORT - MISSING SHUTTER ON FIXED GAUGE "On August 3, 2020, during a routine inspection, the Department [Arizona Department of Health Services] discovered that the licensee had a shutter go missing from a fixed gauge in November of 2016. The radiation safety officer was attempting to perform a lock-out procedure when he realized that the entire shutter mechanism was missing from the unit. The gauge was a Texas Nuclear Corporation Model 5192, SN: B4192, containing 100 milliCuries of Cs-137. "The Department has requested additional information and continues to investigate the event." Arizona Incident: 20-013. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-08-11
54810 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-08-01 12:00 | 2020-08-01 20:36 | 2020-08-01 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE "At approximately 1749 CDT on August 1, 2020, the licensee notified the agency (Texas Department of State Health Services) that at approximately 1200 CDT, one of the licensee's technicians had completed density testing and placed the Troxler Model 3440 gauge (SN: 25201) in the bed of his pickup with the insertion rod locked. The technician then collected a moisture sample. He failed to secure the gauge in its transportation case and failed to raise the tailgate of the truck as well. The technician had driven approximately 1.5 miles from the site when he realized what had happened and that the gauge was not in the bed of the truck. He reported immediately to his supervisor. The licensee searched by vehicle and on foot the entire route the technician had driven and also checked with some other workers on the site but they had not seen anything. The licensee reported the loss to local police department and then notified the agency. The licensee will pursue other avenues to attempt to locate the gauge (notify pawn shops, check for surveillance cameras at locations along the route, etc.). The gauge contained an 8 milliCurie cesium-137 and 40 milliCurie americium-241 source. More information will be provided as it is obtained in accordance with SA-300." Texas Incident No.: TBD. * * * UPDATE ON 8/1/20 AT 2150 EDT FROM KAREN BLANCHARD TO BETHANY CECERE * * * "The licensee has notified the agency (Texas Department of State Health Services) that a member of the public had posted on Facebook that he had found the gauge. The technician who lost the gauge saw the post and made arrangements to get the gauge from him. At approximately 1945 CDT, the licensee took possession of the gauge. The lock on the insertion rod was still in place, sources were in the fully shielded position, and there is no apparent damage to the gauge. The licensee will have it checked by the manufacturer/service company. Licensee will notify LLEA of the recovery." Notified R4DO (Gepford), NMSS Events Notification, ILTAB, and CNSNS (Mexico). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-08-10
54809 | 0 | Mistras Group |  |  |  |  | 2020-07-31 11:55 | 2020-08-01 09:51 | 2020-08-01 | NON-AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA GUIDE TUBE The following is a summary of information received from the licensee's Radiation Safety Officer (RSO) via phone: While two radiographers where shooting pipe welds in Saint Albans, WV with a 100 Ci Ir-192 radiography camera, a separate pipe rolled off and crimped the guide tube with the source in the collimator. They extended the work area to 1 mR/h and called a retrieval team. The team arrived 1.5 hours later with lead bags, which were placed on the collimator, reducing the dose rate to 1 mR/h at the source. They cut some of the crimped metal in order to retract the source. The camera was returned to the licensee's South Point, Ohio storage unit. The guide tube will be cut and replaced. The dose to the radiographer and radiographer assistant was 30 mrem and 19 mrem, respectively. The dose to the retrieval team RSO and RSO assistant was 30 mrem and 22 mrem, respectively. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Safety Equipment Failure | [9 empty] | Non Emergency | 3 | IL | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-08-10
54808 | 0 | Saint Lucie | 1 | 2 |  | [1] CE,[2] CE | 2020-07-31 17:00 | 2020-07-31 17:40 | 2020-08-02 | NOTICE OF UNUSUAL EVENT DUE TO HURRICANE WARNING POSTED FOR AREA "A Hurricane Warning is in effect for St. Lucie County including the plant site. A Hurricane Warning was confirmed with the State Watch Office at 1700 EDT. As a mater of procedure, St. Lucie Nuclear Power Plant entered an Unusual Event classification for the Hurricane Warning. State and local officials have been notified by the licensee. "The NRC Resident Inspector was notified by the licensee. "This report is submitted in accordance with 10 CFR 50.72(a)(1)(i) due to the Notice of Unusual Event and 10 CFR 50.72(b)(2)(xi) due to the Offsite Notification." Notified DHS SWO, FEMA OC, DHS NICC WO, CISA IOCC (email), DHS SWO (email); FEMA NWC (email), FEMA Ops Center (email), FEMA-NRCC-sasc (email), NRCC THD Desk (email), NuclearSSA (email). * * * UPDATE ON 8/2/20 AT 1456 EDT FROM LOUIS ENGELKE TO BETHANY CECERE * * * "The Hurricane Warning was downgraded to a Tropical Storm Warning by the National Weather Service for St. Lucie County, including the plant site. At time 1445 EDT, on 08/02/20, St. Lucie Nuclear Plant has terminated from the Unusual Event classification. "There are no changes in plant status for either unit. Both units are stable at 100% power. "The NRC Resident Inspector was notified of this by the licensee. The licensee notified State and County officials of the termination." Notified R2DO (M. Miller), IRD MOC (Kennedy), NRR EO (C. Miller), DHS SWO, FEMA OC, DHS NICC WO, CISA IOCC (email), DHS SWO (email); FEMA NWC (email), FEMA Ops Center (email), FEMA-NRCC-sasc (email), NRCC THD Desk (email), NuclearSSA (email) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Emergency Declared | Offsite Notification |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Unusual Event | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2020-07-31
54807 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-07-01 | 2020-07-30 12:35 | 2020-09-02 | <br><br>EN Revision Imported Date : 9/3/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - ABANDONED RADIOACTIVE SCRAP METAL The following information was received via email: "On 7/1/2020, Massachusetts Radiation Control Program was informed by Schnitzer Steel Industries, Inc., that a scrap metal shipment from Town of Littleton Transfer Station in Littleton, MA set off the radiation monitor alarm. The vehicle was redirected back to Littleton Transfer Station for follow-up survey and mitigation in accordance with MA RCP DOT Special Permit 10656 MA-MA-20-01. "On 7/6/20, the material was identified and segregated from the scrap metal load by an independent radiation consultant. The radioactive material discovered was radium-226 Aircraft gauge. Device is intact and not leaking as a wipe test was done by radiation consultant. A Ludlum Model 9DP-1 ion chamber was used for direct measurements on the instrument. The dose rate at 6 inches from the instrument was 1 mR/hr. Dose rate outside of drum is less than 300 microR/hr. The radium-226 activity was estimated to be approximately 31.6 microCuries based on the dose rate measured. "The RAM material is being stored in safe secure storage away from people and labeled as radioactive material held for proper disposal. "This activity meets the 30-day event report requirement for lost or abandoned radioactive material greater than 10 times the quantities specified in 10 CFR 20 Appendix C, or the Massachusetts equivalent, 105 CMR 120.297 Appendix C, which is ten times reportable quantity for radium-226 (1 microCurie). "The Massachusetts Radiation Control Program considers this event to be open until proper disposal of this instrument is confirmed." Event Docket No.: MA 19-4216 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf * * * UPDATE FROM ZARA REJAEE TO DONALD NORWOOD AT 1549 EDT ON 9/2/2020 * * * The following information was received via E-mail and is the Agency's (Massachusetts Radiations Control Program) final update to this report: "1). Event Cause: Device abandoned or discarded by person(s) unknown. "2). Corrective Action: Device transferred for proper disposal at licensed facility. "3). Manufacturer of Source or Device: Not Available / Not Indicated. Device found in scrap metal load. "4). No additional information expected by Agency. "5). Agency considers this event to be closed." Notified R1DO (Ambrosini), NMSS Events Notification E-mail group and ILTAB E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-08-07
54806 | -1 | Callaway | 1 |  |  | [1] W-4-LP | 2020-07-30 08:15 | 2020-07-30 11:59 | 2020-08-17 | <br><br>EN Revision Imported Date : 8/18/2020<br><br>EN Revision Text: EMERGENCY PROCEDURE ERROR POTENTIALLY PREVENTING TIMELY COMPLETION OF EMERGENCY CORE COOLING SYSTEM RECIRCULATION ALIGNMENT "At 0815 CDT on 7/30/2020, it was determined that a procedural error in emergency procedure ES1.3, Transfer to Cold Leg Recirculation, could delay realignment from emergency core cooling system (ECCS) injection phase to recirculation phase under lower plant operational modes. It is noted this scenario is postulated to occur only when the boron dilution mitigation system is operable in lower modes of operation as per Technical Specification 3.3.9 (required operable in Mode 2 [below P-6], 3, 4 and 5). Current plant conditions require this feature nonfunctional so this issue does not impact current plant conditions. This condition is not bounded by existing design and licensing documents; however, it poses no current impact to the health and safety of the public or plant personnel. Therefore, this event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." * * * RETRACTION ON 8/17/2020 AT 1603 EDT FROM JOSH COPELAND TO KERBY SCALES * * * "Event Notification (EN) 54806, made on 7/30/2020, is being retracted because re-evaluation performed subsequent to the notification has demonstrated that the error in Emergency Operating Procedure ES1.3 would not have resulted in a condition outside of the current licensing basis analyses of record for the Callaway Plant. This re-evaluation addressed core effects, containment pressure-temperature and radiological consequences analyses, documented in the plant's corrective action program. "The re-evaluation has led to the conclusion that the procedural error in ES1.3 would not have prevented any system required to be OPERABLE by the Technical Specifications from performing its specified safety functions. With all systems capable of performing their specified safety functions, the current licensing basis analyses of record for Callaway Plant remain valid and bounding. Based on these considerations, it has been determined that the condition reported in EN 54806 did not result in the plant being in an unanalyzed condition that significantly degraded plant safety. Consequently the condition did not meet the criteria for an 8-hour notification per 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition that significantly degrades safety. "The NRC Resident Inspector has been notified of this Event Notification retraction. " Notified R4DO (Taylor) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Unanalyzed Condition |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2020-07-30
54805 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-07-29 | 2020-07-30 08:13 | 2020-07-30 | AGREEMENT STATE REPORT - STUCK SHUTTERS The following information was received via email: "On July 29, 2020, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that during the performance of routine gauge inspections two gauges were found to have shutters that would not function. One was a Ronan model SA-1-F37 gauge containing a 150 mCi cesium-137 source with the shutter stuck in the open position. The second gauge was a Ronan model SA-1-C10 gauge containing a 100 mCi cesium-137 source with the shutter stuck in the closed position. Both source activities reported are the original activities. The gauge shutters are stuck in the normal operating position and do not create any additional exposure risk to any individual. The licensee has contacted a service company to repair the gauges. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-08-07
54804 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-07-28 | 2020-07-29 13:43 | 2020-07-29 | AGREEMENT STATE REPORT- PATIENT UNDERDOSE The following was received from the Illinois Emergency Management Agency (IEMA) via email: "KishHealth System in Dekalb, IL (d/b/a Kishwaukee Community Hospital) contacted the IEMA at approximately 1100 CDT on 7/29/20 to report a patient scheduled to receive Y-90 microsphere therapy for hepatocellular cancer received only 58% of the dose prescribed in the written directive. While investigation is ongoing, the reportable underdose is based on licensee's pre and post-administration measurements of the dose vial and waste container, respectively. "IEMA staff have contacted the licensee and are seeking additional information on post-administration imaging, status of patient/referring AU notification, the nature of the written directive (i.e., was this a fractionated dose), and the members of the treatment team. These factors, among others, will determine regulatory compliance as well as patient impact. Therefore, this report will be updated as information becomes available. IEMA is dispatching staff today (7/29/20) for a reactionary inspection. The reporting requirements for the licensee, as specified in 32 Ill. Adm. Code 335.1080(c) were met, and the licensee is aware of the need for a written report within 15 days." Illinois item number: IL200013 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-08-06
54803 | 0 | Prairie Island | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2020-07-28 19:49 | 2020-07-29 04:28 | 2020-07-29 | FAILED RADIATION DETECTOR "Radiation monitor RE-69, 'Guardhouse Area Radiation Detector' was found failed on operator rounds. RE-69 is a category A1 piece of equipment that provides the sole means of indication for a parameter used to directly assess emergency action level (EAL) RA3.1, 'dose rate greater than 15 mR/hr in either of the following areas: Control Room (R-1), Central Alarm Station (R-69).' A compensatory measure was subsequently established and the ability to assess EAL RA3.1 has been restored." There was no impact on the health and safety of the public or plant personnel. The NRC Senior Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-29
54802 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-07-27 | 2020-07-27 13:05 | 2020-07-27 | AGREMENT STATE REPORT - TROXLER GAUGE ON EBAY The following was received from the Florida Bureau of Radiation Control (BRC) via email: The RSO [Radiation Safety officer] of Laboratory Technical Services, Milton, FL (License number 3734-1) contacted this office [BRC] at 1200 [EDT] to report a model 3450 Troxler Gauge inappropriately advertised on ebay. The Troxler location is advertised in Jacksonville, FL. Acting IRC [Incident Response Coordinator] contacted ebay at 1237 to report the prohibited item. Florida Incident Number: FL20-086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-08-04
54801 | 0 | Westinghouse Electric Corporation |  |  |  | Uranium Fuel Fabrication | 2020-07-25 11:00 | 2020-07-26 08:10 | 2020-07-26 | CONTAMINATED INJURED EMPLOYEE TAKEN TO HOSPITAL The following was received via email from Westinghouse: "On July 25, 2020, at approximately 1100 EDT, a Westinghouse employee performing routine work in the pelleting area passed out due to a personal medical emergency. Site emergency first responders responded per plant procedures and training until Emergency Medical Services (EMS) personnel arrived. The employee was transported to an offsite medical facility accompanied by a plant health physics technician due to the potential for radioactive contamination based on the work location of the employee. "There was no release to the environment and no process or plant equipment involved. Surveys taken at the hospital and of all emergency response equipment and response personnel revealed no contamination. [All removable contamination from the Westinghouse employee was returned to the facility.] The Columbia plant is a licensed Part 70 facility subject to 10CFR70 Subpart H." The licensee has notified state and local county governments. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Med Treat Involving Contam | [9 empty] | Non Emergency | 2 | SC | FUE |  | 70.50(b)(3) |  |  |  | 0 | 2020-08-03
54800 | 0 | Sequoyah |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-07-24 01:05 | 2020-07-24 09:00 | 2020-07-24 | ICE BED INOPERABLE "At 0105 [EDT] on 7/24/20 it was discovered Unit 2 Ice Bed was INOPERABLE. Therefore, since this is a single train system the requirements of 50.72 (b)(3)(v)(C) and (D) have been met. This condition is being reported as an 8-hour non-emergency NRC Notification. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." This condition put the unit in a 48-hour LCO. The old chillers were put into service to bring the temperature of the ICE bed down. At 0833 EDT, the technical specification limit was no longer exceeded and the unit exited the LCO. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Pot Uncntrl Rad Rel | Accident Mitigation |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2020-07-24
54799 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-07-23 | 2020-07-23 12:47 | 2020-07-23 | AGREEMENT STATE REPORT - LOST SHIPMENT OF I-125 SEEDS The following was received from the Florida Bureau of Radiation Control (BRC) via email: "[The licensee] called the BRC at around 0945 EDT to report that a package [containing 53.91 mCi of I-125] of Brachytherapy seeds was lost by [the common carrier]. The package left the manufacturing facility, then the local facility, was picked up by [the common carrier] at 1706 on July 20, 2020, but was lost somewhere before Tampa. IsoAid checked the delivery status on July 21, 2020, but it was not scanned. Route intended to be Tampa to Memphis to New York to South Africa. "There are 100 seeds loaded in 7 magazines, 6 magazines contain 15 seeds each, and a 7th magazine contains 10 seeds. These seven magazines are contained in a white leaded pig. The pig was packaged in a white box, 9" x 7" x 5" weighing about 4lbs. The package was labeled as Radioactive White - I, UN2915." Florida Incident Number: FL20-085 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-07-31
54798 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-07-16 23:30 | 2020-07-22 17:59 | 2020-07-22 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following was received form the California Radiologic Health Branch (RHB) via email: "On 7/17/2020, licensee's RSO [(Radiation Safety Officer)] contacted RHB to report an incident in which a portable nuclear gauge (Humboldt 5001EZ SN: 2919, 11 mCi Cs137, 44 mCi Am241:Be) was damaged by a construction truck at approximately 2330 PDT on 7/16/2020. The RSO secured the gauge after notification by the gauge technician and transported the gauge to the licensee's permanent storage location. The RSO determined and confirmed to RHB that the source rod was able to be retracted into the shielded position after the incident. The RSO performed a radiation survey and reported readings of 0.099 mR/hr at 1 meter. RHB will be following up with this investigation." California 5010 Number: 071720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-07-30
54797 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-07-21 10:30 | 2020-07-22 10:04 | 2020-07-22 | CONCURRENT REPORT FOR FIRE SUPPRESION OUT OF SERVICE The following was received from Global Nuclear Fuels, America: "At 1030 (EDT) on July 21st, 2020, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire suppression system for the Fuel Manufacturing Operation Sandblast Building was impaired. An underground pipe that feeds water to the sprinkler system had developed a leak. The building is normally unoccupied and no other buildings are affected. Compensatory measures were enacted and communicated to the Deputy Fire Marshall. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will notify Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-07-22
54796 | 0 | Robinson | 2 |  |  | [2] W-3-LP | 2020-07-21 08:51 | 2020-07-21 12:42 | 2020-07-21 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "At 0851 EDT on July 21, 2020, a Technical Specification required shutdown was initiated at Robinson Unit 2. Technical Specification LCO 3.0.3 was entered due to LCO 3.1.7 not being met as a result of indication loss on Control Rod positions with more than one position indication inoperable for a group. LCO 3.0.3 was entered at 0752 EDT to initiate action within 1 hour to place the unit in MODE 3 within 7 hours. Since a Technical Specification required shutdown was initiated, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(i). "Technical Specification LCO 3.0.3 was exited at 1003 EDT on July 21, 2020. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." Shutdown was initiated and power was reduced approximately 3 percent. Reactor power was back to 98.5 percent at the time of notification. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Plant S/D Reqd By Ts |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2020-07-21
54795 | 0 | Browns Ferry | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-07-21 04:35 | 2020-07-21 08:58 | 2020-07-21 | BIOFOULING OF INTAKE STRUCTURE LEADS TO MANUAL REACTOR SCRAM OF UNIT 1 The following was received from TVA - Brown's Ferry at 0858, 21 July 20. "On July 21, 2020, at 0435 hours Central Daylight Time, Browns Ferry Unit 1 inserted a manual reactor scram due to degrading main condenser vacuum from marine biofouling at the intake structure. Browns Ferry Unit 2 is in Mode 4 and Browns Ferry Unit 3 is at approximately 76% rated thermal power and stable. "Primary Containment Isolation Systems received an actuation signal for groups 2, 3, 6, 8 on reactor water level below +2". All Primary Containment Isolation System groups that received an actuation signal performed as designed. Additionally, all other systems functioned as designed. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "This event also requires an 8 hour report per 10CFR50.72(b )(3)(iv)(A), Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including: reactor scram or reactor trip, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation and (2) General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs). "The NRC Resident Inspector has been notified." The plant is stable in Mode 3 and will remain shutdown until marine growth clogging the intake structure abates. | 0 | 0 | 0 | 40 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | Non Emergency | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-07-21
54794 | 0 | Browns Ferry | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-07-20 13:25 | 2020-07-20 18:11 | 2020-07-20 | BIOFOULING OF INTAKE STRUCTURE LEADS TO MANUAL REACTOR SCRAM OF UNIT 2 AND DOWNPOWER OF UNITS 1 & 3 "On July 20, 2020, at 1325 hours Central Daylight Time, Brown's Ferry Unit 2 inserted a manual reactor scram due to degrading main condenser vacuum from marine biofouling at the intake structure. Brown's Ferry Unit 1 performed a down power to 43% and Unit 3 down powered to 76%. Conditions are stable on both Unit 1 and 3 following unit down power. "Primary Containment Isolations Systems received an actuation signal for groups 2, 3, 6, and 8 on reactor water level below +2". All Primary Containment Isolations System groups that received an actuation signal performed as designed. Additionally, all other systems functioned as designed. "This event is reportable within 4 hours per 10CFR50.72(b)(2)(iv)(B) - Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. "This event also requires an 8 hour report per 10CFR 50.72(b)(3)(iv)(A), "Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including: reactor scram or reactor trip, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation and (2) General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs). "The NRC Resident Inspector has been notified." All control rods fully inserted and decay heat is being removed via normal feedwater and condenser. | 43 | 0 | 76 | 100 | 100 | 100 | -1 | -1 | -1 | N | M/R | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | Power Operation | Power Operation | Power Operation | Power Operation |  | Power Operation | Non Emergency | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-07-20
54793 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-04-20 | 2020-07-20 17:35 | 2020-07-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Nebraska via email and phone: "Approximately April 2019, a tritium exit sign was thrown away with construction debris while a contractor was cleaning up to remodel from catastrophic flooding in Pender, Nebraska. The sign was discovered missing when inventory was taken 7/17/2020. "Device Name: RADIOLUMINESCENT SIGN Manufacturer: Best Lighting Model Number: SLTURW10 Serial Number: 165713 Radionuclide: H-3 Activity: 7.03 Ci (260.11 GBq)" Nebraska Incident Report No.: NE200005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-07-28
54792 | 0 | Davis Besse | 1 |  |  | [1] B&W-R-LP | 2020-07-19 20:03 | 2020-07-20 16:36 | 2020-07-20 | OFFSITE NOTIFICATION - EMERGENCY SIREN FAILURE "In the evening of 7/19/20, a report was received from Ottawa County Sheriff Dispatch personnel that a single siren had sounded. Review of the siren system computer log determined Siren 202 in Carroll Township had malfunctioned and sounded at approximately 2003 EDT, and sounded a second time at approximately 2045 EDT while the siren was being polled for troubleshooting. Personnel were dispatched to Siren 202 to deenergize both the AC and DC power to prevent additional soundings. The cause of the siren sounding is under review, but it occurred following storms passing through the area. "This notification is being made solely as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-07-20
54791 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2020-07-17 | 2020-07-18 11:17 | 2020-07-20 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The following was received by the state of Maryland via email: "On July 17, 2020 at 2115 EDT the Maryland Radiological Health Program was notified of a lost or stolen portable moisture density gauge. A technician for J. D. Hynes and Associates was at a job site at the University of Maryland Eastern Shore, 30610 College Backbone Road, Princess Anne Maryland. The technician completed the job and was preparing to store the gauge in the transportation case when he was distracted. He then drove the truck approximately 16 miles back to the office at 32185 Beaver Run Drive, Salisbury, MD 21804. The technician discovered the gauge was not in the case. The technician contacted his supervisor and the owner at 1730 EDT and then returned to the job site at approximately 1800 EDT to search for the gauge and discovered the site was locked. The project superintendent was contacted and a key for entry was obtained by the licensee supervisor. Both the licensee supervisor and technician entered the jobsite and searched for the missing gauge and did not locate it there. Then they searched along the travel route independently from each other to try and locate the missing gauge. Both employees searched until approximately 2100 EDT when it got too dark to see. The licensee contacted Wicomico County Police Department and Somerset County Police department and both county fire departments. The gauge was a Troxler 3400 series with 9 mCi Cs-137 and 44 mCi AmBe sources. The serial number is 75791. A reactive inspection will be conducted on Monday July 20, 2020." * * * UPDATE ON 7/2/2020 AT 1724 EDT FROM ATNATIWOS MESHESHA TO THOMAS KENDZIA * * * The following update was received via email: "A portable density gauge was lost from the J.D. Hynes and Associates, Inc. on July 17, 2020 between approximately 14:45 EDT to 15:20 hours EDT. The gauge was identified as Troxler, model 3440P, serial number 75791 with nominal activities of 8 mCi of Cs-137 (on 1/7/2019) and 40 mCi of Am-241:Be (on 2/11/2019). The last leak test was performed on March 6, 2020. The gauge was lost while returning to office from the job-site. "On July 17, 2020, at approximately 10:00 hours EDT, the density gauge was placed in the tailgate of a pick-up truck by the gauge operator after warm up and daily calibration, and waiting for the day's work at a building construction in the University of Maryland Eastern Shore Campus located at 30610 Collage Backbone Road; Princess Anne, Maryland 25813; in Somerset County. Work was suspended at about 14:45 hours EDT due to water leakages in the underground pipes. The gauge operator proceeded to drive back to the licensee's office located at 32185 Beaver Run Drive, Salisbury, MD 21804, in Wicomico County. After driving for about 25 minutes (about 18 miles) and arriving at the office parking lot the gauge operator realized that the gauge was not placed in its transportation case. The gauge was missing from the bed of the open tailgate of the pick-up truck. "The event has been reported to the Maryland State Police, in Salisbury; the Incident Number is: 2020-00322775. "Maryland Department of Environment, Radiological material Division will conduct a reactive investigation. Notified R1DO (Carfang), NMSS Event Notifications (email) and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2020-07-27
54790 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2020-07-16 | 2020-07-17 20:05 | 2020-07-17 | AGREEMENT STATE REPORT - MISADMINSTRATION OF MEDICAL TREATMENT The following was received from the State of Utah, Department of Environmental Quality, Division of Waste Management and Radiation Control: "Misadministration with external beam radiation therapy, the licensee (Utah Cancer Specialists) delivered 300 cGy per site, per day, over two treatments, as follows: Two sites were treated incorrectly at 1000 MDT on July 16, 2020 in the 3rd lumbar area and the right kidney. One site was treated incorrectly at 1530 MDT on July 17, 2020 in the 3rd lumbar area while the right kidney was treated correctly. "It was discovered by way of a cone beam CT in preparation for the kidney treatment where the misalignment was observed. The misalignment was made due to setting up at incorrect tattoos." Utah Event Number will be provided in a later report. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2020-07-27
54789 | 0 | Diablo Canyon |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-07-17 13:46 | 2020-07-17 19:59 | 2020-07-17 | MANUAL REACTOR SCRAM DUE TO INCREASED HYDROGEN USAGE "On July 17, 2020, at 1346 PDT with Diablo Canyon Power Plant Unit 2 operating at 100 percent power, the reactor was manually tripped in accordance with plant procedures due to increasing hydrogen usage in the Unit 2 main generator. The reactor trip was uncomplicated and the Auxiliary Feedwater system started as expected. The plant is stable in Mode 3. "This notification is being made in accordance the requirements of 10 CFR 50.72(b)(2)(iv)(B) as a manual actuation of the reactor protection system and 10 CFR 50.72(b)(3)(iv)(A) as an automatic actuation of a specified safety system. "The cause of the increased hydrogen usage is under investigation. There was no impact to the health and safety of the public or plant personnel. "The Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS Actuation - Critical |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | Non Emergency | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-07-17
54788 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-07-17 | 2020-07-17 17:20 | 2020-07-17 | AGREEMENT STATE REPORT - UNDERDOSE ADMINISTERED TO PATIENT The following was reported by the Florida Bureau of Radiation Control: "On 7/17/2020 during ablative treatment with Y-90 TheraSpheres to the male patient, it was discovered that only a partial treatment was administered to the patient. 511.6 Gy was prescribed, 358.9 Gy was delivered, for a 70% delivery rate. The event was discovered during a routine check of waste activity. The Radiation Safety Officer (RSO) reports that from initial information from the tech, all procedures were followed. No abnormal events were noted during the procedure. The prescribing physician and patient have been notified. Clinical outcome is expected to be ok. The RSO will phone in more details on Monday as he was working remotely on Friday. A fifteen day letter will follow. Licensing and Technology will be tasked to investigate." FL incident number: FL20-082 Notified RI and NMSS Events Notification. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-07-27
54787 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-07-12 | 2020-07-17 10:48 | 2020-07-17 | AGREEMENT STATE REPORT - SOURCE DAMAGED IN SHIPMENT The following was received from the Louisiana Department of Environmental Quality via email: "On July 12, 2020, the Radiation Safety Officer (RSO) contacted the state by voice mail to the Louisiana Department of Environmental Quality/Emergency Response Services Division/Radiation Section to report that a High Dose Rate (HDR) Ir-192 source was damaged in transit with the shipper. The source was being shipped to Providence Regional Cancer Partnership, Rad Oncology Department, 1717 13th Street, Everett, WA 98201. The source serial number is 02-01-2499-001-062320-11518-64. The activity of the Ir-192 source was 11.189 Ci on June 26, 2020 when it was shipped. The source was returned back to Alpha-Omega Services because the HDR drive cable was found damaged and twisted. The transport container had been damaged. The source was found to be one inch high from its designated shielding transportation position. The return survey found the exposure to be 80 mR.hr at surface and 4.0 mR/hr TI. The container had been shipped at a surface reading of 31 mR/hr and a TI of 0.9 mR/hr at one meter." LA Report Number: LA20200006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-07-27
54786 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-07-16 | 2020-07-17 09:49 | 2020-07-17 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following was received from the Florida Bureau of Radiation Control (BRC) via email: "On July 16, 2020, a 54 year old man was mistakenly provided two doses of Tc-99 Sestamibi for heart stress test. Two doses were administered with a total activity of 41.6 mCi, estimated dose of 7.49 R, to the intestinal wall. The RSO [(Radiation Safety Officer]) reports that standard verification process for patient identification prior to dosage was not followed. Patient and patient's cardiologist have both been notified, no effects of the mis-dose are expected. "The RSO will provide additional info in the 15 day letter to BRC. Licensing and Technology will be tasked to investigate." Florida Incident Number FL20-081 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-07-27
54785 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-07-15 | 2020-07-16 13:09 | 2020-07-16 | AGREEMENT STATE REPORT - STUCK FIXED GAUGE SHUTTER The following is a synopsis of information received via E-mail and phone: On July 15, 2020, at 1445 CDT, the Radiation Safety Officer (RSO) for Syngenta Crop Protection, LLC contacted the Louisiana Department of Environmental Quality / Emergency and Radiological Services Division / Radiation Section to report that shutters had failed to close on two fixed density gauges during routine maintenance. The shutters are stuck in the open position and do not affect operation. The gauges are Ronan Engineering Model SAI, s/n's 5832GK and 5835GK, each with a 50 mCi Cs-137 sealed source, at the time of installation. The licensee contacted the contractor, BBP Sales, LLC, to determine whether the gauges should be disposed of or repaired. The decision will be made on July 16, 2020 on how to deal with the stuck shutters. Repair or disposal of the gauges should be accomplished by July 20, 2020. Louisiana Event Report ID No.: LA20200005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-07-24
54784 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-07-14 15:30 | 2020-07-16 10:48 | 2020-07-16 | AGREEMENT STATE REPORT - GAUGE CRUSHED WITH SOURCE ROD EXTENDED The following was received from the Illinois Emergency Management Agency (IEMA; the Agency) via email: "At approximately 1530 CDT on July 14, 2020, the Agency was contacted by the RSO [(Radiation Safety Officer)] /owner of Construction & Geotechnical Material Testing (IL-02179-01) regarding a Troxler 3440 gauge [s/n: 24805; containing 8 mCi of Cs-137 and 40 mCi of Am-241] that was run over and crushed by an operator running a roller on a construction site at 1514 Main Street in Lombard. The RSO reported that operations had stopped and that he needed guidance to get the source rod out. At 1550 CDT, the Agency contacted the licensee for details and to provide guidance. "The gauge user was uninjured but the gauge was run over and destroyed. At the time of the incident it was confirmed that the source rod was extended into the ground and a measurement was in process. The gauge user immediately notified personnel in the area and cordoned off the area. The gauge user then notified his RSO, who then notified Troxler (their emergency contact) and IEMA as per their emergency procedures. The RSO immediately went to the scene. He stated that he verified the security of the scene. He did not believe that the source rod was bent. The RSO stated that he was headed back to his office for a survey meter. "Agency inspectors reviewed concerns regarding exposure from the Cs-137 source and the possibility of a leaking source with the RSO. Procedures were reviewed for surveys of the area once the gauge was removed to ensure the Cs-137 source had not become dislodged and that the source was not leaking. The Agency offered to dispatch inspectors to assist; however, the licensee had the gauge manufacturer engaged and able to respond. "The gauge manufacturer responded to the scene at approximately 1700 CDT and confirmed the source rod was unbent and able to be shielded. Both the Am-241 and the Cs-137 sources were confirmed as present and intact. The gauge was safely repackaged into the Troxler case by Troxler personnel and the TI [Transport Index] confirmed as 0.3. This information was confirmed with pictures sent to the Agency. Troxler personnel performed surveys of the area to confirm the source was removed and that there was no contamination/leakage. Both sources (Cs-137 and Am-241) were placed into the Troxler transport container without incident. Both Troxler and the licensee performed surveys of the site prior to departing and after packaging the damaged source. At 1830, the licensee confirmed background readings at the site and the gauge was transported back to Troxler. The gauge will be leak tested and then shipped to Troxler in North Carolina for disposal. "This matter will remain open pending receipt of leak tests, additional gauge information, documentation of disposal, and required written reports." Illinois Item Number: IL200011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-07-24
54783 | 0 | NASA MICHOUD ASSEMBLY FACILITY |  |  |  |  | 2020-07-06 | 2020-07-15 15:15 | 2020-07-15 | LOSS TRITIUM EXIT SIGN The following information was received via email: "The Michoud Assembly Facility [(MAF)] operates under an NRC general license. The MAF currently has a project being performed by a subcontractor to replace approximately 28 Tritium exit signs. On 7/6/2020, an employee noticed that one Tritium exit sign [source activity of 3.0 Curies] was not in the location of its last inventory. Further investigation into the incident and discussions with the project manager indicated that the exit sign was most likely removed by the subcontractor performing the demolition work on-site. The project manager notified the subcontractor to investigate the incident further, at which time the subcontractor reported the Tritium exit sign had been disposed of at the Construction and Debris (C&D) waste [facility] in the Gentilly Landfill LCC 1 located at 10200 Almonaster Blvd. in New Orleans, LA 70127." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Lost/Stolen Lnm>1000x | [9 empty] | Non Emergency | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2020-07-23
54782 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-07-14 09:15 | 2020-07-15 14:35 | 2020-07-15 | AGREEMENT STATE REPORT - THERASPHERE PROCEDURE UNDERDOSE The following information was received via E-mail: "On 7/15/2020, at 1340 EDT, the licensee reported that yesterday, 7/14/2020, sometime between 0915 and 0930 EDT, a male patient receiving TheraSphere treatment was underdosed by approximately 30 percent due to a leak in the delivery assembly. This was discovered around half-way through the procedure. No exposure to anyone other than the patient occurred. Contamination has been contained and removed. The prescribed activity was 5.7 GBq and dose was 150 Gy. The actual activity delivered is estimated to be 3.99 GBq and dose was 105 Gy. The patient is scheduled to return next week for follow-up treatment." Florida Incident Number: FL20-080 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-07-23
54781 | 0 | Watts Bar | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-07-15 08:35 | 2020-07-15 14:58 | 2020-07-15 | MAIN CONTROL ROOM ENVELOPE INOPERABLE DUE TO MCR DOOR BEING AJAR "At 0835 EDT on July 15, 2020, it was discovered that the main control room (MCR) envelope was inoperable due to a MCR door being found ajar; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). The door was closed, restoring the MCR envelope to operable at 0839 EDT. There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-07-15
54780 | -1 | Billings Clinic |  |  |  |  | 2020-07-14 11:15 | 2020-07-15 12:25 | 2020-07-28 | <br><br>EN Revision Imported Date : 7/29/2020<br><br>EN Revision Text: UNAUTHORIZED USE OF A RESTRICTED RADIATION ROOM AS A TOUCHDOWN SPACE "On July 14, 2020, at approximately 1115 MDT, the Radiation Safety Officer was notified that a restricted radiation room was used intermittently for 30-45 minute periods as a touchdown space for Billings Clinic's Internal Medicine residents. The room had not been decommissioned. "The restricted radiation room being used was the Billings Clinic Hospital I-131 Inpatient Therapy Room (room 3501; general inpatient medical floor). This room was last used for [a 153 mCi I-131 Sodium Iodine] radiation treatment on June 21, 2017. Beginning June 4, 2020, the room began being used as a touchdown space for Internal Medicine residents. Surveys were performed on July 14, 2020 using survey meters. Wipes for removable contamination were performed on a table, two computers, phone, and the floor around the area where staff were working. All items had activity levels indistinguishable from background readings. The items were removed from the room. The room has been secured with a new lock and radiation warning signs have been reposted. The radiation signs had been removed at an unknown time between June 4, 2020 and July 14, 2020. "The licensee is not aware of any radiation exposure as a result of this reported event." The licensee is making this report as a deviation from 10 CFR 35.13(f) as required by reporting requirement 10 CFR 30.50(b)(1)(iii). * * * RETRACTION ON 07/28/2020 AT 1428 EDT FROM CHRIS FITZ TO THOMAS KENDZIA * * * This is a summary of information received from the licensee via telephone: After discussion with NRC RIV personnel the licensee determined that this event is not reportable in accordance with 10 CFR 30.50(b)(1)(iii). Notified R4DO (Gepford) and NMSS Events (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Unplanned Contamination | [9 empty] | Non Emergency | 4 | MT | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2020-07-23
54779 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2020-07-15 09:45 | 2020-07-15 10:22 | 2020-07-15 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGES The following is a summary from the South Carolina Department of Public Health received via phone: At 0945 EDT on 07/15/2020, the licensee's Radiation Safety Officer (RSO) notified the State that two Troxler moisture density gauges (model 3430P, serial #'s 72756 and 75041), each containing 8 mCi of Cs-137 and 40 mCi of Am-241, were stolen from their Ballentine, SC storage facility. The devices had not been used in a few days, so it is unknown when they were stolen. The RSO reports that the job box containing the travel cases were taken, but the locks were not cut. Additionally, the roll up gate was closed but not secured. The RSO believes it could be an inside job. The RSO was in the process of calling the police. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2020-07-23
54778 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-07-13 06:00 | 2020-07-14 23:51 | 2020-07-15 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the California Department of Public Health via email: "A Troxler moisture density gauge (model 3430, serial # 31716) was reported stolen Monday morning at approximately 0600 PDT from the bed of an employee's vehicle while the vehicle was parked for 1-2 hours outside the employee's residence in Moreno Valley, CA. The gauge contains approximately 0.3 GBq (8 mCi) of Cs-137 and 1.50 GBq (40 mCi) of Am-241. The gauge was reportedly picked up earlier that morning at the licensee's office in Rancho Cucamonga, and left appropriately chained/locked in the back of the vehicle at the employee's residence before leaving for a work location. The theft was reported to the Moreno Valley Police Department (police report #MV201950058 taken by Officer Flores). A reward will be advertised for the return of the gauge." California 5010 NUMBER: 071420 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-08-05
54777 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-07-13 10:15 | 2020-07-14 10:13 | 2020-07-14 | CONCURRENT REPORT FOR FIRE SUPPRESSION OUT OF SERVICE "At 1015 EST on July 13, 2020, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire suppression system for various Fuel Manufacturing Operation Shop Areas was taken offline for planned maintenance to conduct a NFPA [(National Fire Protection Association)] required 5-year inspection. These inspections will be ongoing throughout the week. Compensatory measures were enacted and communicated to the Deputy Fire Marshall. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." Licensee will notify Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-07-22
54776 | 0 | Vogtle | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2020-07-13 08:31 | 2020-07-13 17:10 | 2020-07-13 | SUPERVISOR FAILED FITNESS FOR DUTY TEST "On July 13, 2020 at 0831 (EDT), Southern Nuclear Operating Company (SNC) determined an SNC supervisory personnel failed their fitness for duty test. The employee has been removed from the site and their access has been terminated. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | Non Emergency | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2020-07-13
54775 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-07-08 | 2020-07-10 20:18 | 2020-07-10 | AGREEMENT STATE REPORT - MEDICAL EVENT The following report was received from the State of California via email: "On July 10, 2020, the Radiation Safety Officer for the University of California, Los Angeles, notified the Radiologic Health Branch of a Medical Event that occurred with a Varian High Dose Afterloader with an Ir-192 source during an ovarian cancer treatment. The prescribed dose to the intended organ was 24 Gray (2400 rad). Due to an incorrect entry of the catheter length into the treatment delivery system, an unintended dose of 21.8 Gray (2180 rad) was estimated to have been delivered to the large bowel. The dose delivered to the intended organ was initially estimated at 0 Gray (0 rad). The patient and the patient's physician were notified. The licensee's investigation into this medical event is ongoing and will be reviewed further by the California Department of Public Health" California 5010 report no: 071020 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-07-20
54774 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2020-07-09 | 2020-07-10 11:12 | 2020-07-10 | AGREEMENT STATE REPORT - PORTABLE MOISTURE DENSITY GAUGE DAMAGED The following report was received from the Commonwealth of Virginia via email: "On July 9, 2020, a representative of the Virginia Radioactive Materials Program (VRMP) received a report from a licensee through the Virginia Department of Emergency Management that a portable nuclear moisture /density gauge was damaged at a temporary jobsite in Manassas, Virginia. The VRMP contacted the licensee immediately and learned that a Bobcat V519 forklift struck the gauge (CPN MC1 Elite, Serial # 30950, containing 10 milliCuries of Cesium-137 and 50 milliCuries of Americium-241/Beryllium). The incident occurred while the gauge operator was running a gauge standardization count in front of the forklift. The guide tube of the gauge was bent and the case was scratched. However, the sources were in the shielded position and the shielding integrity was not damaged. The licensee performed a survey of the gauge and readings observed were less than 0.4 mR/hr at three (3) feet distance from the gauge. The gauge was put in its transport box and returned to the Manassas office. Wipe test samples were taken and results are pending. The VRMP is working with the licensee to obtain additional information and this report will be updated once the licensee's investigation is complete and the information is received." Virginia report no.: VA-20-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2020-07-20
54773 | 0 | Harris | 1 |  |  | [1] W-3-LP | 2020-07-10 09:00 | 2020-07-10 08:30 | 2020-07-10 | PLANNED COMMON EMERGENCY OPERATIONS FACILITY MAINTENANCE "At 900 EDT on July 10, 2020, Duke Energy will undertake planned maintenance activities on the common Emergency Operations Facility (EOF) for Brunswick, Catawba, Harris, McGuire, Oconee, and Robinson Nuclear Sites. The work includes performance of upgrades to the emergency AC power system and requires the removal of both normal and emergency power to the facility. The work duration is approximately ten (10) days. "If a declared emergency were to occur at Harris Nuclear Plant, the Alternate EOF would be set up in the McGuire Alternate Technical Support Center (TSC) location as described in implementing procedures. The Emergency Response Organization has been notified that the primary EOF will be unavailable during the upgrade project and to report to the alternate location, if activated. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "The Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-10
54772 | 0 | Brunswick | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2020-07-10 09:00 | 2020-07-10 08:28 | 2020-07-10 | PLANNED COMMON EMERGENCY OPERATIONS FACILITY MAINTENANCE "At 0900 EDT hours on 7/10/2020 Duke Energy will undertake planned maintenance activities on the common Emergency Operations Facility (EOF) for Brunswick, Catawba, Harris, McGuire, Oconee, and Robinson nuclear sites. The work includes performance of upgrades to the emergency AC power system and requires the removal of both normal and emergency power to the facility. The work duration is approximately ten (10) days. "If a declared emergency were to occur at Brunswick, the Alternate EOF would be set up in the Catawba Alternate Technical Support Center (TSC) location as described in implementing procedures. The Emergency Response Organization has been notified that the primary EOF will be unavailable during the upgrade project and to report to the alternate location, if activated. "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-10
54771 | 0 | Oconee | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2020-07-10 09:00 | 2020-07-10 08:17 | 2020-07-10 | PLANNED COMMON EMERGENCY OPERATIONS FACILITY MAINTENANCE "At 0900 EDT hours on 7/10/2020 Duke Energy will undertake planned maintenance activities on the common Emergency Operations Facility (EOF) for Brunswick, Catawba, Harris, McGuire, Oconee, and Robinson nuclear sites. The work includes performance of upgrades to the emergency AC power system and requires the removal of both normal and emergency power to the facility. The work duration is approximately ten (10) days. "If a declared emergency were to occur at Oconee, the Alternate EOF would be set up in the Catawba Alternate Technical Support Center (TSC) location as described in implementing procedures. The Emergency Response Organization has been notified that the primary EOF will be unavailable during the upgrade project and to report to the alternate location, if activated. "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-10
54770 | 0 | Catawba | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-07-10 09:00 | 2020-07-10 08:01 | 2020-07-10 | PLANNED COMMON EMERGENCY OPERATIONS FACILITY MAINTENANCE "At 0900 EDT hours on 7/10/2020 Duke Energy will undertake planned maintenance activities on the common Emergency Operations Facility (EOF) for Brunswick, Catawba, Harris, McGuire, Oconee, and Robinson nuclear sites. The work includes performance of upgrades to the emergency AC power system and requires the removal of both normal and emergency power to the facility. The work duration is approximately ten (10) days. "If a declared emergency were to occur at Catawba, the Alternate EOF would be set up in the McGuire Alternate Technical Support Center (TSC) location as described in implementing procedures. The Emergency Response Organization has been notified that the primary EOF will be unavailable during the upgrade project and to report to the alternate location, if activated. "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-10
54769 | 0 | Mcguire | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-07-10 09:00 | 2020-07-10 07:45 | 2020-07-10 | PLANNED COMMON EMERGENCY OPERATIONS FACILITY MAINTENANCE "At 0900 EDT hours on 7/10/2020 Duke Energy will undertake planned maintenance activities on the common Emergency Operations Facility (EOF) for Brunswick, Catawba, Harris, McGuire, Oconee, and Robinson nuclear sites. The work includes performance of upgrades to the emergency AC power system and requires the removal of both normal and emergency power to the facility. The work duration is approximately ten (10) days. "If a declared emergency were to occur at McGuire, the Alternate EOF would be set up in the Catawba Alternate Technical Support Center (TSC) location as described in implementing procedures. The Emergency Response Organization has been notified that the primary EOF will be unavailable during the upgrade project and to report to the alternate location, if activated. "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-10
54768 | 0 | Robinson | 2 |  |  | [2] W-3-LP | 2020-07-10 09:00 | 2020-07-10 07:10 | 2020-07-10 | PLANNED COMMON EMERGENCY OPERATIONS FACILITY MAINTENANCE "At 0900 EDT hours on 7/10/2020 Duke Energy will undertake planned maintenance activities on the common Emergency Operations Facility (EOF) for Brunswick, Catawba, Harris, McGuire, Oconee, and Robinson nuclear sites. The work includes performance of upgrades to the emergency AC power system and requires the removal of both normal and emergency power to the facility. The work duration is approximately ten (10) days. "If a declared emergency were to occur at Robinson, the Alternate EOF would be set up in the Catawba Alternate Technical Support Center (TSC) location as described in implementing procedures. The Emergency Response Organization has been notified that the primary EOF will be unavailable during the upgrade project and to report to the alternate location, if activated. "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-07-10
54767 | 0 | PIEZOTECH, LLC |  |  |  |  | 2020-01-01 | 2020-07-09 16:17 | 2020-07-09 | PART 21 - PARTS MANUFACTURED USING SOURCE MATERIAL WITHOUT A SPECIFIC LICENSE The following is a summary of information received from Piezotech, LLC: Piezotech possessed and used source material, in the form of depleted uranium, without applying for and receiving a specific license in accordance with 10 CFR 40.31. The depleted uranium was used to manufacture piezoelectric ceramics which contained an "Unimportant Quantity" of depleted uranium as defined in 10 CFR 40.13(c)(2)(ii). Piezotech transferred the piezoelectric ceramics to several customers without first applying for and receiving a license for initial transfer of items containing source material in accordance with 10 CFR 40.52 and did not file initial transfer reports as required by 10 CFR 40.53. Piezotech suspects that a formulation to manufacture piezoceramics, named K180, was developed in the 1970s or 1980s. K180 uses depleted uranium as one of the doping materials in the manufacture of piezoceramics. The formulation uses an amount of depleted uranium that is less than 1 percent by weight. In January of 2020, an engineer raised a concern to Piezotech's General Manager and to its Compliance Director that the company may need an NRC license to use depleted uranium in making the K180 piezoceramic. A review of NRC regulations showed that this was the case and at that time all activity regarding K180 was halted. All material used in K180 manufacturing and all existing inventory and intermediate stage materials were segregated from manufacturing and the container of depleted uranium was secured in a locked cabinet where it currently remains. In February 2020, Piezotech commissioned a radiation survey of the facility and sampling occurred in all areas where K180 and its component materials were stored or processed. This survey indicated that all processing areas were at background radiation levels and all areas where the depleted uranium and K180 ceramics had been stored were below the annual exposure levels for untrained personnel. Piezotech has decided to discontinue manufacturing the K180 material. The depleted uranium will remain sealed in the original container and shipping crate, having all the original markings and labels and secured in a locked flameproof cabinet. Piezotech is making arrangements with an appropriately licensed facility for the proper disposal of the remaining depleted uranium and intermediate stage and finished K180 product. If in the future Piezotech decides to resume manufacturing the K180 material or any material using NRC regulated substances, Piezotech will apply for the required licenses and will not initiate any regulated manufacturing or sales activities until all applicable licenses have bee issued. For further information, contact: John Churchill Piezotech Compliance Director Phone: (301) 216-3002 FAX: (301) 330-8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 3 | IN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-07-17
54766 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-07-03 | 2020-07-09 14:27 | 2020-07-09 | AGREEMENT STATE REPORT - STOLEN HYDROPROBE The following was received from the California Radiologic Health Branch (RHB) via email: "On 07/08/20, the licensee's ARSO [(Assistant Radiation Safety Officer)] contacted the RHB to report a stolen hydroprobe, CPN Model 503, S/N H330301362 containing 50 mCi of Am-241. The gauge belonged to Blue Ocean Organics, Inc. and was stolen on 07/03/20, out of a technician's truck parked overnight at a location in Visalia, CA. The ARSO stated that the hydroprobe was removed from the two chain lock in the back of the truck and placed in the cab of the truck overnight when it was stolen along with some other items. On 07/03/20, immediate notification was made to Tulare County Police Department (Deputy G. Canales A344, case # 20-055488). Licensee will be posting a reward for the safe return of the gauge. "RHB will be following up with the investigation. The licensee will be cited for several items including failure to notify RHB per 10 CFR 20.2201(a)." CA 5010 Number: 070820 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-07-17
54765 | 0 | TTL ASSOCIATES, INC |  |  |  |  | 2020-07-07 14:00 | 2020-07-07 14:38 | 2020-07-07 | SOURCE DISLODGED FROM DAMAGED GAUGE The following is a summary of a phone call received from the licensee: A technician was at a job site taking measurements with a Troxler 3430 density gauge (S/N: 23216). The gauge contains an 8 mCi Cs-137 source and a 40 mCi Am-Be source. While the source rod was extended into the ground, the technician, along with others, attempted to get the attention of the driver of a pickup truck backing up into the work area. They were unsuccessful, and the truck backed into the gauge, bending the rod, preventing it from being retracted. The technician attempted to straighten the rod, but was unsuccessful. Then the rod was bent in the other direction and the Cs-137 source became dislodged. It was placed in a plastic container and the area was cordoned off. The Radiation Safety Officer (RSO) was en route, and with guidance from the service company, will place the source in a bucket and fill it with sand, survey the area for any contamination, return the source to the facility for a leak test, and store the gauge. The RSO will determine how to dispose of the source and gauge once the leak test results are received. The technician was wearing dosimetry and it will be sent in for analysis. It is not expected that there was much additional exposure received. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Safety Equipment Failure | [9 empty] | Non Emergency | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-07-15
54764 | -1 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2020-07-02 | 2020-07-06 13:26 | 2020-08-14 | <br><br>EN Revision Imported Date : 8/17/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - MEDICAL EVENT The following was received via email: "On 6/30/20 microspheres were injected in the patient [intended target of Hepatic Segments 4 through 8] at the vessel branch point with the intention of targeting both the right hepatic artery (RHA) and the middle hepatic artery (MHA). However, post-therapy imaging demonstrates that radiotracer was preferentially deposited along the MHA distribution. This is attributed to unforeseeable clumping of microspheres at the origin of the RHA, such that a majority of the microspheres were preferentially injected into MHA. As such, microspheres were predominantly deposited in the extrahepatic lymph node as well as an unexpected pancreaticoduodenal lymph node. Deposition in this second node can be attributed to additional unintended reflux into a third branching vessel upstream from the RHA and MHA, and further supports the assertion flow into the RHA was hindered by the clumping of microsphere particles. Ultimately, SPECT-CT image analysis suggests no more than approximately 40 percent of the therapy dose was deposited within the liver (as detailed below). "It is estimated the following activity distribution from post-treatment imaging: At most, approximately 40 percent of the administered activity appears to be within the liver, with the other 60 percent being in extrahepatic tissue (e.g. lymph nodes). This breakdown should be considered approximate, as these images are not scatter corrected. "From pre-treatment macro aggregated albumin (MAA) imaging, it appears that 84 percent of the administered activity was expected to be delivered to the liver, and 16 percent was expected to shunted to the nodes. Overall, this indicates that approximately 53 percent less activity than what was intended reached the liver. There is uncertainty in this estimate. "The dose to extrahepatic tissue (lymph nodes) differs from what was intended/expected by more than 50 Rem (0.5 Gy)." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 8/14/2020 AT 1131 EDT FROM RANDAL DAHLIN TO KERBY SCALES * * * The following retraction was received from the state of Iowa via email: "On July 6, 2020 Iowa reported a potential medical event at the University of Iowa (License number 0037-1-52-AAB) involving Yttrium-90 (Y-90) microspheres. This potential medical event occurred on June 30, 2020 and was discovered by the licensee on July 1, 2020 during analysis of post therapy SPECT/CT imaging. This event was reported to the state on July 2, 2020 after staff working hours. Iowa Department of Public Health (IDPH) Radioactive Materials Program (RAM) staff became aware of the potential medical event on July 6, 2020 after the holiday weekend. "IDPH staff conducted a reactive inspection at the University of Iowa on July 8, 2020 to interview university staff involved in the procedure and the university radiation safety officer, review the written directive for the Y-90 procedure and review fluoroscopic images of placement of the catheter in the right hepatic artery. IDPH staff determined that the university used due diligence in following their policies and procedures for Y-90 administrations and manufacturer's instructions and no violations were noted. "The university followed up with a written report on July 16, 2020 which determined that the unintended dose to the lymph nodes was due to shunting through a pathway or bypass due to patient vasculature. A review of the NRC licensing guidance for Y-90 microspheres dated March 20, 2020 Revision 10.1 revealed that unintended doses to tissue or organs during a Y-90 procedure due to shunting is not considered a reportable medical event. "IDPH program staff had a meeting with NRC Region III staff on Wednesday, August 12, 2020 to discuss this potential medical event. Region III staff agreed with IDPH that this unintended dose was due to shunting and therefore not a reportable medical event. "Therefore Iowa is retracting event number 54764." Notified R3DO (Pelke) and NMSS Events (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2020-07-14
54763 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-07-01 | 2020-07-06 11:40 | 2020-07-06 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received via email: "A 98 microCurie I-125 breast cancer localization seed (titanium encapsulated) was inadvertently cut in half during its extraction from a patient. All portions of seed presumably removed and lavage performed. A pancake probe was used at tissue surface prior to tissue closure and measured 200 microR/hr. Tissue entry point was closed and re-surveyed at some later time with a measurement of 10 microR/hr. Post recovery, patient was apprised of the event and initiated a 10-day KI treatment plan. [The Radiation Safety Regional Health Director] is in consultation with the dose calibrator manufacturer and seed manufacturer (Team Best) in order to better calculate activity of recovered seed portions and subsequently compare to initial, inserted activity. The difference will yield activity remaining in the patient." Florida Incident Number: FL20-073 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-07-14
54762 | 0 | Turkey Point |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2020-07-05 21:09 | 2020-07-05 23:05 | 2020-07-05 | REACTOR TRIP DUE TO TURBINE TRIP "Reactor trip caused by turbine trip due to voltage regulator issues. Plant is stable. Exited the Emergency Operating Procedure Network." Auxiliary Feedwater automatically actuated and was subsequently restored to standby. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS Actuation - Critical |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | Non Emergency | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-07-05
54761 | 0 | Fermi | 2 |  |  | [2] GE-4 | 2020-07-01 23:05 | 2020-07-02 02:01 | 2020-07-02 | LOSS OF OFFSITE POWER - AUTO INITIATION OF EMERGENCY DIESEL GENERATOR "At 2305 EDT on July 1, 2020, while in Mode 5 for Refueling Outage 20 with no core alterations in progress, Fermi 2 experienced a loss of Division 2 offsite power (345 kV) which resulted in a valid automatic initiation of the Division 2 Emergency Diesel Generators (EDG) 13 and 14. EDG 13 and 14 started as expected to supply their associated busses. Division 1 offsite power remains operable and powering the Division 1 Residual Heat Removal (RHR) system in Shutdown Cooling (SDC) mode of operation. Division 1 EDGs 11 and 12 remain operable and available. "The cause of the loss of Division 2 offsite power is under review and has preliminarily been determined to be caused by Mayfly accumulation in and around the Division 2 (345 kV) switchyard. Actions have been put in place to minimize and deter Mayflies from gathering near plant switchyards. "All systems responded as expected for the loss of Division 2 offsite power and no loss of SDC occurred. There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified. "The event is reportable pursuant to 10 CFR 50.72(b)(3)(iv)(A), as a valid specified system actuation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Valid Specif Sys Actuation |  |  |  | IMode1: Refueling; FMode1: Refueling | Non Emergency | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2020-07-02
54760 | 0 | PARAGON ENERGY SOLUTIONS |  |  |  |  | 2020-06-01 | 2020-06-30 17:41 | 2020-07-21 | PART 21 - FAILURE OF SIZE 1 AND 2 FREEDOM SERIES AUXILIARY CONTACTS The following is a summary of information received from Paragon Energy Solutions: DUKE Harris Nuclear Plant (HNP) has identified instances where Size 1 and 2 Eaton Freedom Series starters have failed to function as expected in assemblies that were originally supplied by NLI. The auxiliary contacts have degraded prematurely and have failed to change state when the starter was energized which has affected indication and other controlling actions within the circuit. The premature degradation of the auxiliary contacts with the old model NLI special coil, part number: 057018-COIL-1/2, has occurred on size 1 and 2 contactors that were continuously energized with significant run time after approximately 3 to 5 years of service time. HNP has provided information to manage the known degradation. The auxiliary contacts should be replaced at an increased frequency until new auxiliary contacts are installed along with the new design NLI special coil, part number: 057018-COIL-1/2-M. The nature of the defect is the pre-mature aging of the component within the auxiliary contact mechanism that is adjacent to the operating coil. The starter coil is potentially being subjected to voltages of a nature that elevates the temperature within the starter adjacent to the auxiliary contacts. It is recommended that the starters and coils be replaced in the applications where the units are being operated in a continuous duty application. It is also recommended that the control transformer be replaced with a true 4:1 ratio transformer. Paragon/NLI has developed a true 4:1 ratio transformer that will provide additional mitigation of this potential over-voltage condition. Replacing the transformer with a true 4:1 ratio reduces the control voltage that is being applied to the control circuit in a manner that will not prevent the unit from providing a sufficient voltage during a degraded voltage condition, and also will not subject the components to a voltage above the ratings when the supply voltage is operated above the nominal 480 VAC bus voltage. Paragon has no other recommendations as the accelerated aging of the components and the expected life based on the additional heat the units have been subjected to is unknown. Affected plants: Sharon Harris Oconee Turkey Point Columbia North Anna Waterford River Bend Beaver Valley Should you have any questions regarding this matter, please contact: Tracy Bolt Chief Nuclear Officer Paragon Energy Solutions 817-284-0077 tbolt@paragones.com * * * UPDATE ON 7/21/20 AT 1241 EDT FROM TRACY BOLT TO ANDREW WAUGH * * * The following is the summary of an email received from Paragon Energy Solutions: The root cause of the degraded component is due to the increased voltage and the overall temperature of the starter coil at the elevated voltage. This elevated voltage and temperature has degraded the mechanism of the auxiliary contact operator to a point to which it has become separated from the parent component. Paragon/NLI has developed a new version of the special coil (part number: 057018-COIL-1/2-M) that operates at a lower temperature than the original special coil that is currently in use at HNP. When the new version of the special coil is subjected to the same voltages, the temperature is lower. The affected plants have been revised to: Sharon Harris Oconee Turkey Point Columbia North Anna Notified R1DO (Carfang), R2DO (Miller), R4DO (Drake), and Part 21 Reactors Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-06-30
54759 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-06-29 | 2020-06-29 16:12 | 2020-08-10 | <br><br>EN Revision Imported Date : 8/11/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - RELOCATION OF RADIOACTIVE MATERIAL DUE TO FLOODING The following was received from the Commonwealth of Massachusetts (via email): "Excessive rain caused flooding in a medical building where licensed radioactive materials are used and stored at Steward Norwood Hospital on the evening of 6/28/2020. A call was received by the Massachusetts Radiation Control Program from licensee's consultant, F. X. Masse Associates, Inc., at approximately 0906 EDT on 6/29/2020. It was reported that the building where licensed material is used and stored was flooded and evacuation was mandatory by 1200 EDT. "The Radiation Control Program (RCP) contacted the Director of Imaging at Steward Norwood Hospital at 0955 EDT and discussed the event. The hospital was requested to evacuate the relevant building by 1200 EDT by local government. The licensed materials to be moved included: one 186.5 microCurie cesium-137 vial source; one 1.970 milliCurie cobalt-57 flood source; one 2.301 milliCurie cobalt-57 flood source; one 0.277 microCurie cesium-137 rod source; one 9.404 microCurie cesium-137 button source; one 1.691 microCurie cobalt-57 button source; one 0.722 microCurie cobalt-57 button source; one 0.284 milliCurie cobalt-57 flood source; and two intact iodine-125 capsules of unknown activities (at this time). There may be other sources moved and it is expected that they will be reported to the RCP. "The licensee was granted an emergency approval to move the sources to a different secure building on the site campus until such time as the relevant building is allowed to be reoccupied. A written report and amendment request are forthcoming from the licensee. "There has been no report of personnel exposure or contamination as a result of the flooding. The hot lab where the licensed materials were initially being used and stored had no reported damage. Additional details will be forthcoming." MA Item Number: 54759 * * * UPDATE ON 7/2/2020 AT 1724 EDT FROM ANTHONY CARPENITO TO BRIAN LIN * * * The following update was received via email: "The subject licensee inventory included Iodine originally reported as Iodine-125. The licensee updated inventory is the same as previously reported except there is no Iodine-125. The correct isotope is Iodine-123 (two intact capsules, each capsule with licensee-reported estimated current activity of 1.2 microCuries). "The agency [Massachusetts Radiation Control Program] considers this event to still be open." Notified R1DO (Werkheiser) and NMSS Event Notifications (email). * * * UPDATE ON 8/10/2020 AT 1724 EDT FROM ANTHONY CARPENITO TO THOMAS HERRITY * * * The following update was received via email: "The licensee has requested, and the Agency approved, a license amendment to include a new radioactive material storage location. No additional information is expected by the Agency. The Agency considers this event to be CLOSED." Notified R1DO (Gray) and NMSS Event Notifications (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-07-07
54758 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2020-05-01 | 2020-06-29 12:04 | 2020-06-29 | PART 21 - ABB/THOMAS & BETTS/CYBEREX PRINTED CIRCUIT BOARD SHORTS TO GROUND WHEN INSTALLED IN HOST BATTERY CHARGER The following is a summary of information received from United Controls International: On May 1, 2020, Peach Bottom Atomic Power Station notified United Controls International (UCI) that a printed circuit board (PCB) in a station battery charger was shorting to ground. UCI has determined that an energized trace was too close to the mounting screw/washer causing the short. The trace was too close because the mounting holes were modified at the time of installation prior to commercial grade dedication. The modification was not documented. However, this modification was made to subsequent Time Delay Oscillator PCBs. UCI has determined that in this application the energized trace is not used and can be removed from the board without affecting the function. The subject boards should be returned to UCI for this additional modification. UCI will remove the trace and inspect to ensure sufficient clearance exists. The component is used in ABB/Thomas & Betts/Cyberex P/N: 93-41-119385. The subject board was supplied to Peach Bottom Generating Station in May, 2009. CONTACT: Wesley Hickle Engineering Manager whickle@unitedcontrols.com 770-496-1406 x 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-06-29
54757 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2020-06-23 | 2020-06-24 16:31 | 2020-07-21 | AGREEMENT STATE REPORT - SUSPECTED DOSE TO WRONG ORGAN The following is a summary of email received from the Oklahoma Department of Environmental Quality (OK DEQ): OK DEQ was just informed that yesterday, June 23, 2020, a medical event may have occurred involving a patient undergoing radiation therapy to the vagina. The treatment plan called for three (3) fractions delivered by a High Dose Rate (HDR) afterloader. After the first fraction was administered, the therapist noted the presence of fecal matter on the applicator. The licensee is assuming that the applicator was placed in the patient's rectum instead of the vagina. The treatment plan estimated a dose of 0.85 Sv to the rectum due to the procedure. The licensee estimates the actual dose delivered, assuming the applicator was in the rectum, to be 1.5 Sv. The licensee is the University of Oklahoma Health Science Center, OK-03176-01. This is a Type A medical broadscope license. OK DEQ will provide more information as it becomes available. * * * UPDATE ON 07/21/2020 AT 1549 EDT FROM LIBBY MCCASKILL TO OSSY FONT * * * The following update was received from the OK DEQ via email: OK DEQ is correcting the licensee name and license number. Initially, they were reported as the University of Oklahoma Health Science Center, OK-03176-01. The correct licensee is OU Medicine, Inc., License No. OK-21035-01. Notified R4DO (Drake) and NMSS Event Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2020-07-02
54756 | 0 | GE HITACHI NUCLEAR ENERGY |  |  |  |  | 2020-04-28 | 2020-06-24 13:00 | 2020-06-24 | PART 21 REPORT - NON-CONSERVATIVE BWR/6 SIDE ENTRY ORIFICE LOSS COEFFICIENTS The following is a summary of information received from GE Hitachi Nuclear Energy: For core monitoring, Global Nuclear Fuel-Americas (GNF) applies different hydraulic loss coefficients to BWR/6 fuel bundles as a function of location. The Side Entry Orifice (SEO) loss coefficient varies in BWR/6 plants, depending on the orientation of the SEO relative to intersecting core support beams. The SEO loss coefficient for some bundle locations are under predicted, which results in a local over prediction of Minimum Critical Power Ratio (MCPR) margin. Specifically, the SEO loss coefficients for fuel bundle locations adjacent to Intermediate and Source Range Monitor (IRM/SRM) locations should be higher than the current "one beam" values that are applied. The MCPR effect on affected bundles under conditions where they are near limits can reduce margin by 0.02 in CPR. The condition is not a substantial safety hazard, but the MCPR effect is above the threshold that GNF applies for reportability. GNF has completed its evaluation and concluded that this issue is a reportable condition under 10 CFR 21.21(d). The basis for reportability is that the change in MCPR associated with this issue could contribute to the exceeding of a safety limit, as defined in the technical specifications of a license for operation issued under 10 CFR Part 50. US BWR Potentially Affected Plants: Grand Gulf, River Bend, Clinton, and Perry. There are currently no US ABWR plants in operation that would potentially be affected by this evaluation. The potential error in the core monitoring system does not affect the NRC certified design of the ABWR or the GEH ABWR design certification renewal application currently under review. The unique core support structure design of the BWR6 and ABWR is not shared by earlier BWR plants or the ESBWR. Affected plants should review the following paragraph and contact their GNF account representative for schedule and delivery dates for updated core monitoring databanks. Updated core monitoring databanks for the affected BWR/6 plants are scheduled to be completed by July 10, 2020. For affected plants that use GNF core monitoring software, the long-term corrective action is to implement an updated core monitoring databank with corrected SEO loss coefficient values. Affected plants should contact their GNF account representative for schedule and delivery dates. If necessary, a short-term corrective action such as an administrative MCPR penalty on IRM/SRM locations, should be applied to the core monitoring system. An effective short-term measure would be to assure that IRM/SRM locations are 0.02 less than the Maximum Fraction of Limiting CPR limit (e.g., MFLCPRlimit = 1.00). This condition is met if the core wide MFLCPR is 0.02 below the limit (e.g., MFLCPR < 0.98), because the IRM/SRM locations will be bounded. Note that this recommended short term or interim measure was developed on a standalone basis and does not supplant any existing MFLCPR limit reductions established for other purposes. For non-affected plants, there are no recommended actions. GNF recognizes that other non-GNF fueled plants, safety analysis methodologies, and core monitoring systems may have different design bases and address SEO losses by other means. For more information, please contact: Michelle Catts GE Hitachi Nuclear Energy Safety Evaluation Program Manager 3901 Castle Hayne Road, Wilmington, NC 28401 Michelle.Catts@GE.com (910) 200-9836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-06-24
54755 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-06-23 09:00 | 2020-06-24 08:00 | 2020-06-30 | AGREEMENT STATE REPORT - HIGH DOSE RATE TANDEM APPLICATOR BROKEN DURING TREATMENT The following was received via E-mail from the State of Texas: "On June 23, 2020, the licensee reported that at approximately 0900 CDT, a Medical Event occurred at its facility. The event involved a patient receiving an High Dose Rate (HDR) cervix treatment with a Nucletron Model microSelectron using a tandem and ring. The device contained a 5.191Curie Iridium-192 source. After the treatment was completed and the device was removed, it was discovered the tandem had broken into two pieces. The licensee stated it is unknown where the source was positioned during the treatment. The licensee reported no warnings or errors from the machine were recorded from either the check source or the treatment cable. The licensee stated the source was in the patient for a total of 564.7 seconds. The source was in the tandem a total of 355.2 seconds of that total time. The licensee stated the physician has been notified, but was not sure if the patient had been notified. The licensee stated they were still investigating what occurred and will provide more specific information as it is discovered. Additional information will be provided as it is received in accordance with SA300." Texas Incident No.: 9774 * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 0902 EDT ON 6/30/2020 * * * "The break in the tandem occurred about four inches from the end of the tandem. A picture provided by the licensee shows the break at the beginning of the bend in the tandem on the insertion end at the start of the ring. The licensee stated using the location of the guide wire, which they could track, it now appears that the source tracked next to the tandem and that the exposure occurred only to the intended tissue. The manufacture is investigating the event with the licensee. Additional information will be provided as it is received in accordance with SA300." Notified R4DO (Silva) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-07-02
54754 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-06-18 | 2020-06-22 15:43 | 2020-06-22 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following was received from the state of California via email: "The Radiologic Health Branch was notified by the facility RSO [Radiation Safety Officer] that he detected radiation levels approximately 20 times background on a small subassembly piece that he had replaced for his Mount Sopris Instrument Co, Model HLP-2375 logging tool. The Mt. Sopris supplied sub-assembly contains an Isotope Products Lab model HEG series Cs-137 sealed source # B2-951 (100 mCi on ref. date 7/1/2003). "On June 19, 2020, a wipe from the subassembly piece was measured using a pancake GM (with 15 percent efficiency for Cs-137), and showed approximately 1 microCi activity." California Event ID Number: 061820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-06-30
54753 | 0 | Watts Bar | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-06-22 13:04 | 2020-06-22 13:45 | 2020-06-22 | OFFSITE NOTIFICATION - GROUNDWATER INITIATIVE "At 1304 EDT on June 22, 2020, Watts Bar Nuclear Plant (WBN) Units 1 and 2 initiated voluntary communication to the State of Tennessee and local officials as part of the Nuclear Energy Institute (NEI) Groundwater Protection Initiative (GPI), after receiving analysis results for one on-site monitoring well that indicated tritium activity above the GPI voluntary communication threshold. WBN identified and corrected the cause. This condition did not exceed any NRC regulations or reporting criteria. This notification is being made solely as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-06-22
54752 | 0 | Catawba | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-06-21 21:00 | 2020-06-22 01:00 | 2020-06-22 | UNPLANNED TECHNICAL SUPPORT CENTER VENTILATION MAINTENANCE "At 2100 on June 21, 2020, a condition was discovered which will require corrective maintenance activities to be performed on the Technical Support Center (TSC) HVAC. The work will include repair of the Condensing Unit system. The estimated duration of repair is unknown at this time. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to the alternate facility. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the discovered condition of the TSC affects the functionality of an emergency response facility. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-06-22
54751 | 0 | Bwx Technologies, Inc. |  |  |  | Uranium Fuel Fabrication | 2020-06-19 10:30 | 2020-06-19 13:02 | 2020-06-19 | ONSITE FATALITY The following was received via email: "At approximately 1030 EDT on Friday, June 19, 2020, a BWXT NOG-L employee lost his life due to a fire incident. There were no eye witnesses, but workers in the area reported hearing a pop and then found the victim on the floor in the Supercompactor Room (an intermediate controlled work area). At this time the investigation has not determined what caused the event. The fire did not continue and was out before the Emergency Team could respond to the incident. There was no release of radioactive material above 1 DAC [Derived-Air-Concentration]. The victim was pronounced dead at the scene by paramedics on the Emergency Team. The Campbell County Sheriff's Department and the VA OSHA [Virginia Occupational Safety and Health Administration] were contacted at 1140. A message was left with the Federal OSHA. At approximately 1415, NOG-L was contacted by John Ratcliffe from Federal OSHA. The local Fire Marshall and Campbell County Sheriff's department are completing their investigation and the body has been removed from the scene of the incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-06-29
54750 | 0 | Monongalia County General Hospital |  |  |  |  | 2020-06-15 | 2020-06-19 09:28 | 2020-06-22 | MISSING BRACHYTHERAPY SEEDS "[The licensed material lost is] Palladium-103, 3.56 mCi in a solid brachytherapy seed form. "Forty-nine Pd-103 seeds were ordered from the local radiopharmacy, Pharmalogic in Bridgeport, WV. The order was for three cartridges of 15 seeds and one cartridge of four seeds. The package containing the seeds was received in Nuclear Medicine on 6/12/20. As per procedure, the package was checked in and surveyed and checked against the manifest. Four cartridges were locked inside the container which matched the manifest. The individual seeds were not counted. To count the individual seeds requires opening the entire package and unscrewing the cartridges from the container and then inspecting each cartridge carefully. That same afternoon, the package was transferred to Sterilization. [The RSO] interviewed the director of Sterilization and [they] confirmed that the container was not opened except to crack it to insert a tag indicating that the package had completed sterilization. The package, now wrapped in sterile cloth, was returned to Nuclear Medicine for storage until Monday, 6/15/20, when it was transferred to the Operating Room (OR) for implantation into the patient. "In the OR on 6/15/20, the Authorized User (AU) unwrapped the sterile cloth around the package and began to prepare the seeds for implantation. The AU immediately noticed that something wasn't right. The cartridge that was supposed to contain 4 seeds was empty. The AU stopped the procedure and a survey of the OR and the container was undertaken. No loose seeds were found. The AU determined that 45 seeds was sufficient to complete the procedure, amended the Written Directive to indicate such and completed the procedure. "Immediately following the procedure, Sterilization, Nuclear Medicine and the trash were surveyed with no seeds found. Pharmalogic was notified and they surveyed their preparation areas, packaging/shipping materials which had, by this time, been returned and the truck that made the delivery on 6/12/20. No seeds were found. "[The licensee doesn't] know what happened to the seeds. After careful evaluation, [they] can find no breakdown in our process that would have allowed an opportunity for the seeds to disappear. [The cartridges] were screwed to the inside of the canister and were not removed until they were in the OR in preparation for implantation. It appears from [the licensee's] end that the four seeds were never in the cartridge that was screwed into the canister. The pharmacy insists that they were. "Given the extremely small size of the seeds, the small number of seeds and their very low external dose rate, even if the seeds were lost on [hospital] premises, it is unlikely to produce any meaningful external exposure to anyone." * * * UPDATE ON 6/22/20 AT 0911 EDT FROM MARK PERNA TO THOMAS KENDZIA * * * The following update was received via telephone: The pharmacy determined that they had not put the four seeds in the canister and that they had possession of the seeds. The seeds were not lost. Notified R1DO (Janda), ILTAB (email) and NMSS Event Notifications (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Lost/Stolen Lnm>10x | [9 empty] | Non Emergency | 1 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2020-06-29
54749 | 0 | Beaver Valley | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2020-06-18 17:25 | 2020-06-18 20:37 | 2020-06-18 | NOTIFICATION OF ENVIRONMENTAL REPORT TO ANOTHER GOVERNMENT AGENCY "On June 18, 2020, Beaver Valley Power Station, Unit 1 determined that leakage from an outside out-of-service liquid waste pipe that is within a radiologically controlled area contains several isotopes. Analysis indicates greater than 2,000 picoCuries per liter of tritium, and isotopes of Mn-54, Co-58, Co-60, and Cs-137 are above the lower limit of detection. At 1725 EDT, in accordance with site procedures and NEI 07-07, 'Industry Ground Water Protection Initiative,' notification to the Commonwealth of Pennsylvania was planned. At 1930 EDT notification to the Commonwealth of Pennsylvania was completed. The leak is currently contained. The leakage did not exceed any NRC regulations or reporting criteria. "This notification is being made solely as a four-hour, non-emergency notification for a planned notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-06-18
54748 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-06-18 11:30 | 2020-06-18 16:35 | 2020-06-18 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY CAMERA The following information was received via email: "On June 18, 2020 at 1130 CDT, an industrial radiography crew was working at DOW Chemical Company located in St. Charles Parish. The crew was working on top of a furnace. The crank-out controls [of a radiography camera] came into contact with a pipe and melted while the source was out. The source retracted some but stopped. The source was secured. Six people worked the boundary to ensure no one got exposed. The Radiation Safety Officer (RSO) disconnected the 35 foot crank-out that had melted and pulled on the cable to finish retracting the source into a shielded condition. The RSO received a 43 mrem exposure and their assistant received a 73 mrem exposure. "The radiography camera was a QSA 880 Delta, s/n D6309. Source s/n was 92997G, with an activity of 23 Ci of Ir-192." Event Report ID No.: LA20200004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-06-26
54747 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-06-15 | 2020-06-17 10:57 | 2020-06-17 | AGREEMENT STATE REPORT - FOUND NUCLEAR GAUGE IN SCRAP YARD The following was received by email from the state of Ohio: "The Bureau received a call on June 15 to report that a company working under reciprocity, Chase Environmental [license number 00004KY2001, Louisville, KY], had discovered a gauging device containing a Cs-137 source at the Cohen Brothers scrap yard in Middletown, Ohio. Chase Environmental packaged the gauge and took possession of the gauge for ultimate disposal. "The shutter on the gauge appeared to be stuck open or non-existent. Dose rates of 407 mR/hr on contact with the area where the shutter should be, and 23.5 mR/hr at 1 foot were measured. No loose contamination was detected. No scrap yard personnel were exposed. The Cs-137 source is estimated at 6 mCi. No identifying information was visible on the gauge. "A representative of the scrap yard said that they were cleaning up a section of the yard and a load of dirt with the gauge alarmed their radiation monitors on the way out. He said that this device could have been there for 10+ years. The origin of the gauge is unknown. "The Bureau performed a survey of the scrap yard on June 16 with no other radioactive material detected." Ohio Item Number: OH200003 Ohio Reference Number: OH 2020-024 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-06-25
54746 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-06-11 | 2020-06-13 20:48 | 2020-06-13 | AGREEMENT STATE REPORT - FOUND RADIOACTIVE MATERIAL The following was received from the Arizona Department of Health and Services (the Department) via email: "On June 11, 2020, the Department received a call from the Mesa Fire Department that they were responding to a residence that possessed a metal ammo can that was believed to contain yellowcake. The Department responded to the residence and surveyed the metal ammo can and obtained a high reading of approximately 8.5 mR/hr on contact. The metal ammo can was transported back to the Department for storage. The Department has no additional information at this time. "The Department continues to investigate the event." Arizona Incident 20-011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-06-22
54745 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-06-12 | 2020-06-13 20:08 | 2020-06-13 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the Arizona Department of Health Services (the Department) via email: "On June 12, 2020, the Department received notification from the licensee of a possible medical event involving an I-125 eye plaque. A patient was implanted with an eye plaque on June 4, with a prescribed dose of 85 Gy. On June 8, the patient had a stroke and was admitted to St. Joseph's Medical Center. Once the patient was able to be transported, they were transported back to the Mayo Clinic Hospital on June 9. It was then determined that the patient was not strong enough to endure the procedure for removing the eye plaque. The eye plaque was finally removed on June 11 and the final dose to the tumor was 123.5 Gy or 145.3 percent of the prescription. "The Department has requested additional information and continues to investigate the event." Arizona Incident 20-010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-06-22
54744 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-06-09 | 2020-06-09 18:03 | 2020-06-09 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received by email from the state of Texas: "On June 9, 2020, the Agency [Texas Department of State Health Services] was contacted by the licensee and informed that the shutter on a Vega SH-F1 gauge was found stuck in the open position during a routine inspection. The gauge contains a 20 milliCurie cesium-137 source. The gauge does not pose an exposure risk to any individual. The licensee has contacted the manufacturer for assistance in repairing the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-06-17
54743 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-06-05 | 2020-06-09 16:55 | 2020-06-09 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received via email from the Florida Bureau of Radiation: "At 1605 [EDT], [on June 9, 2020, the University of Florida] RSO [Radiation Safety Officer] reported a radiation overdose at the Human Use Facility, Jacksonville, FL. The physicists began reviewing the patient's treatments on Friday, June 5, 2020. They were evaluating an Excel spreadsheet used to calculate monitoring units (MUs) for double scatter proton therapy and after 15 fractions caught an error. The intended dose was 80 Gy. At this point in the treatment 30 Gy should have been delivered, but instead the current total is approximately 50 Gy. The treating physician was informed and they informed the patient. It has been concluded that the patient will return to complete treatment and receive in total 59 Gy, which is a commonly used fractionation scheme. The doses to the organs at risk (OARs) are within the tolerance of the treatment goals of the delivered fractionation scheme. They are continuing to review the issue and will send a report as soon as possible." Incident Number: FL20-066 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-06-17
54742 | 0 | Summer | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2020-06-08 13:55 | 2020-06-08 18:52 | 2020-06-08 | OFFSITE NOTIFICATION - TRANSMISSION FLUID SPILL "At 1725 EDT on 6/8/2020, V.C. Summer Nuclear Station reported a transmission fluid spill to the South Carolina Department of Health and Environmental Control. The spill was the result of a hydraulic hose leak during equipment testing. This spill did not violate any NRC regulations or reporting criteria. This notification is being made solely as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified. "The spill resulted in 1 - 2 ounces of transmission fluid being released into the Monticello Reservoir." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-06-08
54741 | 0 | Grand Gulf | 1 |  |  | [1] GE-6 | 2020-06-07 22:38 | 2020-06-08 01:08 | 2020-06-08 | OFFSITE NOTIFICATION - EMERGENCY SIREN FAILURE "On June 7, 2020, at 2238 CDT Grand Gulf Nuclear Station (GGNS) was notified by Claiborne County that one Emergency Notification Siren located on US Hwy 61 South had actuated. Claiborne County was informed that no emergency exists at GGNS. "The alarming siren has since been secured. "Notification is being provided to the NRC in regards to the potential for media inquiry. "The licensee informed the NRC Resident Inspector." | 78 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-06-08
54740 | 0 | Seabrook | 1 |  |  | [1] W-4-LP | 2020-06-06 09:20 | 2020-06-06 12:25 | 2020-06-06 | MANUAL REACTOR TRIP WHEN GROUP ONE, BANK 'B' CONTROL RODS INSERTED INTO THE CORE "At 0920 [EDT], with the unit in Mode 1 and 100 percent power, the reactor was manually tripped due to group 1 of control rod bank 'B' fully inserting into the core. All systems responded normally post trip. Operations has stabilized the plant in mode 3 at NOP/NOT [normal operating pressure and temperature]. Decay heat removal is being accomplished via the steam dumps in the steam pressure mode to the main condenser. "Emergency feedwater actuated due to low low steam generator level as expected. "This event is being reported pursuant to 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A) "The senior NRC Resident Inspector has been notified." The plant response to the trip was uncomplicated. All safe shutdown equipment is available. There were no reliefs or safeties actuated during the transient. The licensee manually tripped eight days ago for the same condition. See EN #54731. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-06-06
54739 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-06-04 | 2020-06-05 14:40 | 2020-06-05 | AGREEMENT STATE REPORT - SOURCE DELIVERED TO THE WRONG FACILITY The following information was received from the state of Ohio via email: "JSW Steel (OH license # 31201420001) located in Mingo-Junction, Ohio reported that they sent a mold to RTI in Titusville, PA with a source still in the mold on June 2, [2020]. The device is a Berthold LB 300 ML series with a 4 mCi Co-60 source. JSW contacted AM Health and Safety to go to RTI and secured the source in a container. AM Health and Safety is planning on shipping the source back to JSW Steel next week once the transportation paperwork is completed." Ohio Event Report No.: OH200002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-06-15
54738 | -1 | Millstone |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2020-06-05 03:20 | 2020-06-05 10:39 | 2020-10-05 | <br><br>EN Revision Imported Date : 10/6/2020<br><br>EN Revision Text: CONTROL ROOM BOUNDARY DOOR FAILURE "On June 5, 2020, at 0320 [EDT] a loss of control room envelope (CRE) was declared inoperable due to failure of door 204-36-007. The door was repaired at 0322 [EDT], restoring the CRE to operable. "The NRC Resident Inspector, state, and local authorities were notified." * * * RETRACTION ON 07/09/2020 AT 1443 EDT FROM GERALD A. BAKER TO OSSY FONT * * * "The purpose of this call is to retract a report made on June 5, 2020, NRC Event Number EN54738. "NRC Event Report number EN54738 describes a condition at Millstone Power Station Unit 2 (MPS2) in which a control room envelope boundary door was discovered to not be able to fully close due to the latching mechanism being stuck in the extended position. "The condition was reported to the NRC pursuant to 10 CFR 50.72(b)(3)(v)(D) via an 8 hour prompt report as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "Upon further review, MPS2 determined that there was no loss of safety function. An engineering evaluation determined that even with the control room boundary door unable to be fully closed due to the latching mechanism being stuck in, the extended position, control room air in-leakage would not have been sufficient to prevent the control room emergency ventilation system from performing its safety function. "Therefore, this condition is not reportable and NRC Event Number EN54738 is being retracted. "The basis for this conclusion has been provided to the NRC Resident Inspector." Notified R1DO (Dimitriadis). * * * UPDATE FROM MICHAEL GAGNON TO BRIAN P. SMITH AT 1444 EDT ON 10/01/2020 * * * "The purpose of this call is to provide an update to the retraction for a report made on June 5, 2020, NRC Event Number EN54738. The retraction being updated was made on 7/9/2020 at 1443 hours. "NRC Event Report number EN54738 describes a condition at Millstone Power Station Unit 2 (MPS2) in which a control room envelope boundary door was discovered to not be able to fully close due to the latching mechanism being stuck in the extended position. The condition was reported to the NRC pursuant to 10 CFR 50.72(b)(3)(v)(D) via an 8 hour prompt report as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident (the Control Room Envelope). "A subsequent engineering evaluation of the conditions that existed at the time, determined that the inability of the control room boundary door to fully close due to the latching mechanism being stuck in the extended position did not have an adverse impact upon the ability of the CRE to perform its safety function. The CRE remained operable throughout this event, and the ventilation system would have performed its safety function. Therefore, this condition is not reportable and NRC Event Number EN54738 is being retracted. "The basis for this conclusion has been provided to the NRC Resident Inspector." Notified R1DO (Lally). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode2: Startup; FMode2: Startup | Non Emergency | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-06-05
54737 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-06-04 01:00 | 2020-06-04 16:57 | 2020-06-04 | AGREEMENT STATE REPORT - LOW LEVEL RADIOACTIVE WASTE RAILCAR FIRE The following was received from the Illinois Emergency Management Agency (IEMA; the Agency) via email: "At approximately 0700 [CDT] on 6/4/2020, the Agency was contacted by the Texas Radiation Control Program to advise that a rail car containing radioactive material had caught fire at the Belt Railway Co. of Chicago (BRC) located 6900 Central Ave., Bedford Park, IL. The Texas program had been contacted by the railway. IEMA staff contacted BRC and was informed that a lidded gondola (car WP-9241) transporting a load of UN2912 LSA-1 was found to be smoldering at approximately 0100 on 6/4/2020. The shipping manifest listed contents as 'solid oxides' with 4.13 mCi of Co-60, Cs-134, Cs-137, U-234, U-235 and U-238. BRC staff agitated the railcar and continued to observe until approximately 0300. At that time, flames had engulfed approximately 10 percent of the car and the Bedford Park Fire/Hazmat team arrived on scene. There is no indication of arson. The fire was monitored and the car separated from an adjacent car also containing LLRW [(Low Level Radioactive Waste)] (WP 9124). At approximately 0630, the fire burned itself out. At 0837, IEMA staff contacted the Response Management Team for the shipper and the General Manager for Alaron/Veolia to get shipping manifests (received 0920). Indications at that time were that the fire was rekindling and soil was added atop the fiberglass lid to help smother. "Agency responders arrived on scene at approximately 1040. Bedford Park Fire/Hazmat was on scene as well as the railway's emergency response team. AreaRays had been deployed by the hazmat team and were reporting background exposure rates. Based on conversations with the shipper, the subject load contained un-irradiated zirconium fuel cladding and other debris enroute from Alaron Nuclear Services in PA to Waste Control Specialists in TX. The cladding at one point contained enriched fuel, so there is approximately 1.3 mCi of uranium present (predominately U-234 at a concentration of 41 pCi/gram and U-235 at 3 pCi/g. Load contains approximately 44g of SNM [Special Nuclear Material]). It is believed that the friction due to transport created pyrophoric zirconium dust which reacted with the surrounding building debris and combustible waste. This debris and combustible waste was also contaminated with radioactive material - approximately 0.8 mCi of Co-60, Cs-134 and Cs-137 each. "At the time Agency staff arrived, the lid had been covered with soil and only a small amount of smoke was escaping. This was air sampled for any volatile radioactive contaminants by on site IEMA staff. Areas impacted by smoke, including adjacent cars, were wiped to check for surface contamination. On site measurements did not indicate any deviations from background and there is no indication that the radioactive material within the suspect load impacted personnel or the environment. Lab analyses will supplement this assessment. Impacted areas on the ground were surveyed and exposure rate measurements (reportedly maximally 400 microR/hour on contact with the railcar) documented for any first responder dose recreations. Modeling efforts are underway to provide bounding numbers on potential environmental impacts - albeit unexpected. Temperature of the car was recorded as approximately 400 degrees F and falling. Local Fire/Hazmat was still on scene and the shipper's radiological expertise was expected to arrive at approximately 1530. "In the initial fire response, approximately 1000 gallons of water was added to the railcar. A hydrant was not accessible. The bulk of this water impacted the fiberglass cover and ran off. This drip line was assessed for contamination and none identified. The car was also moved approximately 2000 feet to distance it from the second car of LLRW. Both sites were evaluated by inspectors and no indications of radioactive contamination identified. Agency staff will continue to monitor the situation, especially if the shipper intends to uncover or repackage the shipment. The incident was reported to the National Response Center under Incident Report 1278842 by the Railway Police Department. Nuclear Regulatory Commission, IEPA and USEPA notified and briefed. This matter is also reportable to the Nuclear Regulatory Commission Ops Center for Emergencies under 32 Ill. Adm. Code 340.1220(c)(4)." Item Number: IL200010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-06-12
54736 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-06-04 09:41 | 2020-06-04 15:24 | 2020-06-04 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the California Department of Public Health Radiologic Health Branch via email: "On 06/04/20 [PDT], California Office of Emergency Services (Cal OES) contacted the Radiologic Health Branch (RHB) to report a stolen moisture density gauge (CPN Model MC2, S/N 07226, containing 10 mCi of Cs-137 and 50 mCi of Am-241). The gauge belonged to Twining Inc. and was stolen out of a technician's truck while parked overnight at a Marriott hotel located at 2970 Lakeside Drive, Santa Clara, CA. The RSO [(Radiation Safety Officer)] was aware of the fact that the technician was working at a jobsite away from the permanent storage location. An immediate notification was made to Santa Clara Police Department (Report # T20001625). The RSO will be posting a reward for the safe return of the gauge. The RHB will be following up on this investigation." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-06-12
54735 | 0 | Mcguire | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-06-03 13:00 | 2020-06-03 17:10 | 2020-06-03 | FAILED FITNESS FOR DUTY TEST A non-licensed employee supervisor had a confirmed positive for drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | NC | POW |  | 26.719 |  |  |  | 0 | 2020-06-03
54734 | 0 | PARAGON ENERGY SOLUTIONS |  |  |  |  | 2020-06-01 | 2020-06-03 11:31 | 2020-06-03 | PART 21 REPORT - FAILURE OF SIZE 1 AND 2 FREEDOM SERIES AUXILIARY CONTACTS The following was received from Paragon Energy Solutions via email: "Pursuant to 10 CFR 21.21(d)(3)(i), Paragon Energy Solutions is providing initial notification of the identification of a defect. "Duke Energy Harris Plant has identified instances where Size 1 and 2 starters have failed to function as expected in assemblies that were originally supplied by NLI. The auxiliary contacts have degraded prematurely and have failed to change state when the starter was energized which has affected indication and other controlling actions within the circuit. "The identified starters have been installed for 3-5 years, operating in a continuous duty application. "Formal notification will be submitted on or before 6/30/2020." For any questions or comments, please contact: Tracy Bolt, Chief Nuclear Officer Paragon Energy Solutions 817-284-0077 tbolt@paragones.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 4 | TX | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-06-03
54733 | 0 | Brunswick | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2020-06-02 19:05 | 2020-06-02 19:41 | 2020-06-02 | OFFSITE NOTIFICATION TO THE DEPARTMENT OF TRANSPORTATION "On June 2, 2020, at 1905 Eastern Daylight Time (EDT), Brunswick Steam Electric Plant (BSEP) made a report to the Department of Transportation (DOT) concerning the identification during receipt inspection of removable contamination in excess of 49 CFR 173.443(a) limits on an empty Type 'A' transportation shipping cask received at BSEP. All smears taken on the cask rain cover, trailer bed, and tires were less than minimum detectable activity for removable contamination. "This notification is being made as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-06-02
54732 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-05-30 07:00 | 2020-06-01 10:09 | 2020-06-01 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was received via E-mail: "At approximately 1420 CDT on Saturday, May 30, 2020, the Radiation Safety Officer (RSO) for Global Brass and Copper, Inc., d/b/a Olin Brass, IL-01069-01 contacted the Agency [Illinois Emergency Management Agency (IEMA)] to advise that a SU-S3 fixed gauge containing 1 Ci of Am-241 was damaged on a process line. The source assembly was somehow separated from the fixed gauge housing and fell onto surrounding equipment in an unshielded position. Workers immediately withdrew and fire/safety and security staff cordoned off the area with Radioactive Material (RAM) signage. Reportedly, this incident happened at approximately 0700 CDT on the morning of May 30, 2020. The licensee was attempting to contact their consultant and the manufacturer for assistance. "Agency staff responded to the facility to assist in securing the source, assess for removable contamination, and to evaluate any potential exposures to workers. IEMA arrived on site at approximately 1600 CDT on May 30, 2020. IEMA evaluated airflow, took surveys, and established a recovery plan with site security/safety and the RSO. Exposure rates were approximately 170 mR/hour at one foot. Exposure rates were approximately background at the RAM signage/cordon. Remote handling tools were used to place the source in a pig owned by the licensee. The source was then secured within the licensee's RAM storage safe. Exposure rates around the properly secured safe were approximately 20 microR/hour. Wipes were taken of the area, the damaged gauge housing, and the process equipment. No removable contamination was identified. Discussions concerning worker proximity and time in place after the source became dislodged indicate no exposures exceeding regulatory limits. "IEMA is awaiting a return phone call on June 1, 2020 for additional source details, results of leak tests and availability of the manufacturer to respond and evaluate." Event Report ID No.: IL200009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-06-09
54731 | 0 | Seabrook | 1 |  |  | [1] W-4-LP | 2020-05-29 14:03 | 2020-05-29 16:41 | 2020-05-29 | MANUAL TRIP DUE TO ROD BANK UNEXPECTEDLY INSERTING "At 1403 EDT, with the unit in Mode 1 and 100 percent power, the reactor was manually tripped due to Group 1 of Control Rod Bank 'B' unexpectedly inserting. All systems responded normally post-trip. Operations stabilized the plant in Mode 3 at 557 degrees Fahrenheit. Decay heat removal is being accomplished via the steam dumps in the steam pressure mode to the main condenser. Emergency feedwater actuated due to low low steam generator level as expected. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR (b)(3)(iv)(A). The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS Actuation - Critical |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-05-29
54730 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-05-28 23:00 | 2020-05-29 06:27 | 2020-06-03 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF RADIOACTIVE MATERIAL The following information was received from the Texas Department of State Health Services (the Agency) via E-mail: "On May 29, 2020, at approximately 0130 [CDT], the licensee notified the Agency that at approximately 2300 [CDT] on May 28, 2020, one of its industrial radiography crews was crossing a river southeast of Fredericksburg, Texas, when their vehicle was washed off the road and into the river. Their SPEC 150 exposure device, containing a 47 curie Iridium-192 source, is secured in the vehicle locked inside a robust overpack container, which is held by locked metal brackets which are bolted to the truck. The two radiographers and two licensee staff who responded, aided by county law enforcement with a helicopter, are looking for the vehicle. The river is flowing full and swift and making their search difficult and the truck appears to be being carried downstream. "The roof of the darkroom was seen by helicopter at approximately 0440 [CDT]. At this time, it is unlikely that an exposure could result to persons in unrestricted areas. More information will be provided as it is obtained in accordance with SA-300." Notified DHS SWO, DOE Operations Center, FEMA Operations Center, HHS Operations Center, USDA Operations Center, EPA Emergency Operations Center, DHS CISA IOCC Watch Officer, FDA Emergency Operations Center (email), Nuclear SSA (email), FEMA National Watch Center (email) and DNDO Joint Analysis Center (email). Texas Incident No.: I-9722 * * * UPDATE ON 5/30/2020 AT 1924 EDT FROM KAREN BLANCHARD TO BRIAN P. SMITH * * * The following updated information was received from the Texas Department of State Health Services (the Agency) via E-mail: "On May 29, 2020, the pickup was found almost totally submerged approximately 1 mile downstream from where it entered the [Pedernales River at Goehmann Lane southeast of Fredericksburg, Texas]. On May 30, 2020, the darkroom, which had separated, intact, from the vehicle, was found approximately 11 miles downstream from where it entered the river. Both were recovered May 30, 2020 by the licensee and will be transported to one of their licensed facilities on May 31, 2020. Neither the exposure device nor the overpack in which it was stored in the darkroom were in the vehicle or darkroom. The licensee has attempted to continue search operations to locate the device, but the river levels and water current are prohibitive at this time. They will continue the search as conditions permit, which will improve as the water recedes. Media and public attention are increasing. The Agency has released and the county will release statements (press releases). Exposure risk is still considered low at this time." In the update email a correction has been made in that the device is an INC IR100 and not a SPEC 150 as previously reported. The source information remains the same. Notified R4DO (Werner), ILTAB (Clark), IRD (Kennedy), INES (Milligan), NMSS (Williams), NMSS Events Notification (email), CNSNS (email) * * * UPDATE ON 5/31/2020 AT 1933 EDT FROM KAREN BLANCHARD TO BRIAN P. SMITH * * * The following updated information was received from the Texas Department of State Health Services (the Agency) via email: "The device has been found on the riverbank and recovered by the licensee approximately 13 miles from where the truck entered the river. It was still secured inside the overpack container. No exposures to any member of the public." Notified R4DO (Werner), ILTAB (Clark), IRD (Kennedy), INES (Milligan), NMSS (Williams), NMSS Events Notification (email), CNSNS (email), DHS SWO, DOE Operations Center, FEMA Operations Center, HHS Operations Center, USDA Operations Center, EPA Emergency Operations Center, DHS CISA IOCC Watch Officer, FDA Emergency Operations Center (email), Nuclear SSA (email), FEMA National Watch Center (email) and DNDO Joint Analysis Center (email). * * * UPDATE ON 6/3/2020 AT 0904 EDT FROM KAREN BLANCHARD TO THOMAS KENDZIA * * * The following updated information was received from the Texas Department of State Health Services (the Agency) via email: "GPS coordinate mapping has provided more accurate information on the locations of the truck, darkroom, and industrial radiography device recovery locations. From the bridge where the truck entered the water: the truck was located within 1 mile, the radiography device was approximately 8.5 miles and the darkroom was approximately 9.9 miles." Notified R4DO (Proulx), ILTAB (Clark), IRD (Gott), INES (Milligan), NMSS (Rivera-Capella), NMSS (Williams), NMSS Events Notification (email), CNSNS (email), DHS SWO, DOE Operations Center, FEMA Operations Center, HHS Operations Center, USDA Operations Center, EPA Emergency Operations Center, DHS CISA IOCC Watch Officer, FDA Emergency Operations Center (email), Nuclear SSA (email), FEMA National Watch Center (email) and DNDO Joint Analysis Center (email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-06-08
54729 | 0 | Cook | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-27 09:12 | 2020-05-27 11:35 | 2020-05-27 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF SIRENS "On 5/27/20 at approximately 0912 EDT, the Operations Shift Manager was made aware that the Berrien County Sheriff's Department (BCSD) inadvertently actuated the emergency sirens during a planned weekly test. BCSD notified Cook Nuclear Plant that an audible test was initiated instead of a silent test. All Emergency Notification sirens remain in service. No press release is planned by the licensee at this time. "This notification is being made under 10 CFR 50.72(b)(2)(xi), Offsite Notification, as a four (4) hour report. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-05-27
54728 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2020-05-26 15:30 | 2020-05-27 08:06 | 2020-05-27 | AGREEMENT STATE REPORT - POSSIBLE ADMINISTRATION AT THE WRONG TREATMENT SITE The following information was received from the state of Alabama via email: "The Alabama Department of Public Health Office of Radiation Control was notified on May 26, 2020, at about 1620 CDT by the Radiation Safety Officer (RSO) of the University of South Alabama Health University Hospital (license 584) of a possible misadministration via HDR [high dose rate] afterloader. The RSO stated that the patient was apparently treated at the wrong treatment site on May 26, 2020 around 1530 CDT; the prescribed dose for the fraction was 700 cGy (treatment course to total 2100 cGy). The licensee is currently working to reconstruct dosimetry at the time of this report, and is unsure of the variance from the prescribed dose. The licensee is authorized to possess an Elekta 136149A02, with a maximum of 12 Ci of Ir-192." Alabama Incident Report No.: 20-09. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2020-06-04
54727 | 0 | Surry | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2020-05-25 19:38 | 2020-05-26 15:55 | 2020-05-26 | FITNESS FOR DUTY (FFD) POSITIVE TEST A contract foreman had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | Non Emergency | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2020-05-26
54726 | 0 | Fermi | 2 |  |  | [2] GE-4 | 2020-05-26 10:04 | 2020-05-26 13:17 | 2020-05-26 | FITNESS FOR DUTY (FFD) POSITIVE TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Defueled; FMode1: Defueled | Non Emergency | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2020-05-26
54725 | 0 | Grand Gulf | 1 |  |  | [1] GE-6 | 2020-05-25 04:33 | 2020-05-25 08:44 | 2020-05-25 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "An [automatic] reactor SCRAM occurred at 0433 CDT, on 05/25/2020, from 66 percent core thermal power. The cause of the SCRAM was due to a Main Turbine Trip. The cause of the Turbine Trip is under investigation. "All systems responded as designed. No loss of offsite power or [Emergency Safety Feature] (ESF) power occurred. No [Emergency Core Cooling System] (ECCS) or Emergency Diesel Generator initiations occurred. Main Steam Isolation valves remained open and no radioactive release occurred due to this event. The plant is stable in mode 3. This event is being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "The NRC Resident Inspector has been notified." Decay heat removal is through the Feedwater and Condensate System. | 0 | 0 | 0 | 66 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS Actuation - Critical |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | Non Emergency | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-05-25
54724 | 0 | Waterford | 3 |  |  | [3] CE | 2020-05-21 10:23 | 2020-05-21 17:38 | 2020-05-21 | FITNESS FOR DUTY (FFD) POLICY VIOLATION A licensed operator had a confirmed positive for alcohol during a pre-access fitness-for-duty test. The individual's unescorted access has been terminated. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2020-05-21
54723 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-05-21 | 2020-05-21 16:39 | 2020-05-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email: "On May 21, 2020, the Agency (Texas Department of State Health Services) was contacted by the licensee's radiation safety officer (RSO) and notified that a Humboldt 5000 EZ moisture/density gauge had been lost by one of its technicians. The gauge contained a 40 milliCuries americium-241 source and a 10 milliCuries cesium-137 source. The RSO stated the technician had completed a job and placed the gauge back in the transport case. After completing their paperwork, they got into the cab of their truck and drove off, leaving the tailgate down and the gauge on the tailgate. The gauge came off at the intersection which was at a farmers' market. The technician drove to the next job site and discovered the gauge was missing. The technician backtracked and started looking for the gauge. The technician found an individual at the farmers' market that saw the gauge fall off the truck and someone pull up, grab the gauge, and drive off. The individual took a picture of the vehicle and captured part of the license plate. The technician contacted the RSO who responded to that location. The licensee contacted local law enforcement. The RSO stated the cesium source rod was locked in the shielded position, but was not sure if the transport case was locked. Additional information will be provided as it is received in accordance with SA-300." Texas event number I-9770 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-05-29
54722 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-05-20 15:52 | 2020-05-20 21:34 | 2020-05-20 | AGREEMENT STATE REPORT - LOST PACKAGE IN TRANSIT The following is taken from the Massachusetts Radiation Control Report abstract: "PerkinElmer reported on May 20, 2020, that one UN2910 package, Transport Index 0.0, shipped from the licensee's Billerica, Massachusetts facility via a common carrier, containing 5.73 mCi I-125, was reported missing by the carrier on May 20, 2020. The last known location of the package was at the Atlanta, Georgia, airport on May 15, 2020 (when the carrier reported to the licensee that the package was still being held in place awaiting transfer). The package, measuring 10x6x6 inches and weighing approximately 2 kg, was one of a 22-package shipment destined for a customer in the Netherlands. The package was left behind in Atlanta on May 6, 2020, due to external package damage and the other twenty-one packages continued to the customer. There was no reported external package radioactive contamination or loss of radioactive material. The licensee continues to work with the carrier to locate package. No significant public health and safety concern exists based on the package radiation measured at background levels. "This situation is an immediately reportable event per regulation. The Agency (Massachusetts Radiation Control Program) currently considers this docket to still be OPEN." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-05-28
54721 | 0 | Diablo Canyon |  |  |  |  | 2020-05-18 11:57 | 2020-05-20 14:07 | 2020-05-20 | PART 21 REPORT - INADEQUATE DEDICATION OF REPLACEMENT THERMOCOUPLES The following is a summary from the Diablo Canyon Part 21 Report submitted: On May 18, 2020, Pacific Gas and Electric (PG&E) completed its evaluation of a deviation concerning commercial-grade thermocouples dedicated at Diablo Canyon Power Plant. The original defect was discovered on April 10, 2020 during bench testing where two separate thermocouples exhibited leakage during static pressure testing. The two thermocouples were tested as part of a spare safety-related pump motor refurbishment. Upon subsequent review, it was identified that a pressure boundary test had not been required as part of the dedication process, but should have for its safety-related application. These components were not installed in the plant and there was no risk to the health and safety of the public. Thermocouples from the same batch have been quarantined to prevent installation, and it has been confirmed that none of the suspect batch of thermocouples have been installed in the plant. The thermocouple replacement part evaluation has been revised to include a pressure boundary test as part of the commercial-grade dedication prior to acceptance. Thermocouple Make and Model: March Bellofram 3060-2-JJ-2-13.00-0-1-000 The NRC Resident Inspectors have been notified. This report only affects Diablo Canyon Power Plant. The person informing the Nuclear Regulatory Commission: Kenneth Cortese Quality Verification Director Diablo Canyon Power Plant Pacific Gas and Electric 805-440-367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-05-20
54720 | 0 | Watts Bar | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-20 05:21 | 2020-05-20 12:07 | 2020-05-20 | AUTOMATIC ACTUATION OF EMERGENCY DIESEL GENERATORS "At 0521 EDT on May 20, 2020, with Unit 2 in Mode 3 at 0 percent power and Unit 1 defueled, an actuation of the Emergency Diesel Generator (EDG) System occurred while transferring the 1B-B 6.9kV Shutdown Board (SDBD) from the maintenance feed to its normal power supply. The reason for the 1B-B 6.9kV SDBD failing to transfer to the normal power supply is under investigation. The EDGs automatically started as designed when a valid actuation signal was received. "The event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the EDGs. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Valid Specif Sys Actuation |  |  |  | Defueled | Hot Standby |  | Defueled | Hot Standby |  | Non Emergency | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2020-05-20
54719 | 0 | Dow Chemical Company |  |  |  | 300 Kw Triga Mark I | 2020-05-19 19:30 | 2020-05-19 20:28 | 2020-05-21 | NOTICE OF UNUSUAL EVENT DUE TO DAM BREAK AND POTENTIAL FLOODING AT SITE At approximately 1930 EDT on May 19, 2020, the Dow Chemical Company TRIGA Reactor received notification of an upstream dam break in Sanford, Michigan and the potential to flood the facility. A Notification of Unusual Event was subsequently declared at 1930 EDT. The reactor was in a shutdown condition at the time of the event and has been due to COVID-19. The licensee is monitoring the flood situation in the area and licensee personnel have responded to the site. The NRC remains in the normal mode of operations. Notified DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 5/21/2020 AT 0850 EDT FROM SIAKA YUSUF TO JEFFREY WHITED * * * At 0850 EDT on May 21, 2020, the Dow Chemical Company TRIGA Reactor Terminated the Notification of Unusual Event. The event was terminated after flood water receded. The flood water receded faster than was expected. As stated, the reactor was in a shutdown condition at the time of the event. There was no effect on the reactor due to the flood water. Notified NPR PM (Wertz and Reed), NRR EO (Miller) IR MOC (Grant), DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | Emergency Declared | [9 empty] | Unusual Event | 0 | MI | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2020-05-19
54718 | 0 | Watts Bar |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-19 13:29 | 2020-05-19 19:57 | 2020-05-19 | CONTROL ROOM ENVELOPE INOPERABLE "At 1329 EDT on May 19, 2020, it was discovered that the main control room (MCR) envelope was inoperable due to a control room envelope (CRE) door being found ajar; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). The CRE door was closed, restoring the MCR envelope to operable at 1331 EDT. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | Non Emergency | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-05-19
54717 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-05-12 | 2020-05-19 07:38 | 2020-05-19 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received via report from the Florida Bureau of Radiation: "On May 15, 2020 at 1530 EDT, the Bureau of Radiation Control (BRC) received a call from the medical physicist at the Lynn Cancer Institute regarding the following narrative which was received this morning, May 18, 2020 at 1000 EDT, from the Chief Medical Physicist. On May 12, 2020, a patient presented for a Vaginal Cylinder treatment utilizing the Elekta Ir-192 high dose rate remote afterloader. The written directive was initially written for 7 Gy [Ir-192] x 3 fractions to a depth of 0.5cm (5mm) and a 20mm diameter cylinder was chosen to treat the patient. Due to the relatively small diameter of the cylinder, the Radiation Oncologist decided to change the written directive to 7 Gy x 3 fractions to the surface of the cylinder. The treatment plan was created and the doses to the normal tissues (bladder, rectum and bowel) were accepted by the Radiation Oncologist and the treatment plan was subsequently approved. The approved treatment plan was then delivered to the patient. "On May 14, 2020 it was discovered that the prescription isodose line did not appear to fall on the surface of the cylinder and on May 15, 2020, it was discovered that the 7 Gy isodose line was at about 4.2mm from the surface of the cylinder, and the dose to the points on the surface of the cylinder was found to be 158.3 percent of the prescription, on average. In the professional opinion of the Radiation Oncologist, the dose delivered did not negatively affect the patient and the doses to the normal tissues were acceptable dose levels for this type of treatment. It should be reiterated that the initial intent was to deliver the 7 Gy per fraction to a depth of 0.5cm (5mm) which would have fallen close to the 4.2mm at which the prescription dose was actually delivered. Additionally, had the plan been normalized to the surface of the cylinder the Radiation Oncologist would more than likely have increased the dose and he stated that the dose would have been too low for the intended treatment." Incident Number: FL20-060 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-05-27
54716 | 0 | Salem |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-15 09:47 | 2020-05-15 13:25 | 2020-05-15 | OFFSITE NOTIFICATION DUE TO A HYDRAULIC OIL SPILL "At 0947 [EDT] on 5/15/20, Salem reported to the New Jersey Department of Environmental Protection a sheen on the Delaware River. This discovery did not violate any NRC [Nuclear Regulatory Commission] regulations or reporting criteria. This notification is being made solely as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The licensee will be notifying the National Response Center and Lower Alloways Creek Township. The substance spilled was less than one pint of hydraulic oil. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | Non Emergency | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-05-15
54715 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2020-05-14 | 2020-05-15 09:38 | 2020-05-15 | AGREEMENT STATE REPORT - BROKEN SHUTTER HANDLE The following information was received via email: "The Alabama Dept. of Public Health Office of Radiation Control was notified on May 14, 2020, by a representative of Indorama Ventures Xylenes and PTA, LLC of a broken shutter handle on a fixed gauge. The licensee identified the device as an Ohmart SHRD-1-35, s/n 0018HB, with a Co-60 source of 3000 mCi, manufactured 10/2000. The licensee stated that there were no exposures to individuals as a result of this shutter failure, apparently no radioactive material was released outside the source housing. The device and source are in storage onsite, waiting for disposal." Alabama Incident Report No.: 20-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2020-05-25
54714 | 0 | South Texas | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-14 16:10 | 2020-05-14 19:28 | 2020-05-14 | OFFSITE NOTIFICATION FOR HYDRAULIC OIL RELEASE "At 1535 CDT, on 5/14/2020, it was determined that approximately 10 gallons of hydraulic oil was spilled during dredging activities into the STP Intake Basin (adjacent to the Colorado River). Cleanup using oil booms is underway and there is no longer a visible sheen. The cause of the hydraulic oil spill is under investigation. "The Texas General Land Office was notified at 1610 CDT. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-05-14
54713 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-05-14 15:04 | 2020-05-14 18:58 | 2020-08-20 | <br><br>EN Revision Imported Date : 8/21/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was received from the Commonwealth of Massachusetts via email: "On 05/14/2020, the Massachusetts Radiation Control Program (hereafter, Agency) received a notification from Thermo Scientific Portable Analytical Instruments, Inc. (hereafter, Licensee ) of two Fe-55 leaking sealed sources. A total of 308 sealed sources (containing either Fe-55, Cd-109, or Am-241) were leak tested but only two exceeded reporting limits of 0.005 microCuries of removable contamination for each source. These sources were removed from customer devices for storage prior to disposal. The information of the two leaking sealed sources is as follows: MAKE MODEL SERIAL INITIAL ACT. CURRENT ACT. DETECTED ACT. QSA Global IEC.A1 OA959 20 milliCuries 0.65 milliCuries 0.0206 microCurie QSA Global IEC.A1 OW788 20 milliCuries 0.72 milliCuries 0.0065 microCurie "The sources have been stored in individual plastic bags, inside a lead container since December 2019. They were leak tested inside each bag and the work area was surveyed after the operation (no contamination of the work area was detected). The two sources will be transferred to a licensed waste broker in June. No radiological risk to workers was identified. "The Agency considers this event to be open." * * * UPDATE ON 8/20/20 AT1831 EDT FORM SZYMON MUDREWICZ TO MICHAEL BLOODGOOD * * * The following was received from the Commonwealth of Massachusetts via email: "On 08/07/2020, the Licensee provided a waste manifest that on 06/08/2020, the leaking sources were accepted by Alaron Nuclear Services for disposal. Also, the Licensee further explained that these leaking sources are open window sources similar to those involved in an event the Licensee reported in 2019 and the windows on the sources can be easily damaged due to age, removal from source housing, even from being leak tested. "The Agency considers this event to be closed." Notified R1DO (Greives) and NMSS Event Notification via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-05-22
54712 | 0 | Catawba | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-14 16:30 | 2020-05-14 18:36 | 2020-05-14 | OFFSITE NOTIFICATION DUE TO CONTRACTOR FATALITY "At approximately 1430 [EDT] on May 14, 2020, Catawba Nuclear Station (CNS) requested offsite transport for treatment of a contractor to an offsite medical facility. Upon arrival of the coroner, the individual was declared deceased at 1630 [EDT] on May 14, 2020. "The fatality was not work-related and the individual was outside of the Radiological Controlled Area. No news release by CNS is planned. Notifications are planned to the South Carolina Division of Occupational Safety and Health. "This is a four-hour notification, non-emergency for a notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Offsite Notification |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | Non Emergency | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-05-14
54711 | 0 | Curium Pharma |  |  |  |  | 2020-05-13 08:00 | 2020-05-14 15:52 | 2020-05-14 | FIRE INVOLVING LOSS OF INTEGRITY OF LICENSED CONTAINER "At approximately 0800 EST on May 13, 2020, a thermal reaction occurred inside a production hot cell during a rubidium dissolution process. The pressure created by the reaction caused the back door of the hot cell to open approximately six inches for a few seconds. Curium employees performing the dissolution process immediately activated the hot cell fire suppression system to put out the fire, closed the hot cell door and placed the production area in a secured state. The open hot cell door released airborne radioactive material to a localized area inside the controlled and posted production area. Six employees that were in the vicinity of the production hot cell presented contamination. Contamination was also found on the floor immediately around the production hot cell. "Curium's RSO isolated the affected area and used the data collected from personal surveys to preliminarily estimate the potential dose to the six employees and the total activity released from the hot cell. The initial dose estimates indicated that the employee with the highest exposure potentially received approximately 6.5 mrem DDE and <1 mrem CEDE. Urinalysis was performed to confirm the internal exposure and intake. At the time of this report, the urinalysis results are still pending. Analysis of air samples taken in the immediate affected area indicated the presence of Sr-82, Sr-85, Rb-83, Rb-84, and Rb-86. After the performance of contamination surveys, decontamination of affected employees and analysis of samples, Curium employees decontaminated the affected area. After decontamination procedures were completed, the affected area was released for normal operations within the same business day without the need for imposing additional radiological controls or restrictions. Radiological surveys confirmed that there was no detectable release of radioactive material to uncontrolled areas adjacent to the hot cell production area. "Curium performed a preliminary root cause analysis on May 13, 2020. After completing a preliminary assessment of the dose and release of radioactive materials, Curium reviewed the notification requirements prescribed in 10 CFR 20.2203, 20.2204 and 30.50 and made a determination that neither the immediate nor 24-hour notification requirements were warranted. Curium performed a formal root cause analysis on May 14, 2020. Despite a belief that notification was not required, Curium communicated the incident in good faith to Mr. Jason Draper (NRC Region III) on May 14, 2020 at 1100 EST. After further discussions with Mr. Draper throughout May 14, 2020 and further review of the incident and conditions, Curium personnel made a decision to self-report the incident to the NRC Operations Center as specified under 10 CFR 30.50(b)(4). "Curium is in the process of finalizing the root cause analysis, finalizing the dose estimates, completing confirmatory actions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Fire/Explosion | [9 empty] | Non Emergency | 3 | IN | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2020-05-22
54710 | 0 | Byron | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-13 10:00 | 2020-05-13 18:01 | 2020-05-13 | LOSS OF EMERGENCY RESPONSE FACILITY "At 1000 CDT on May 13, 2020, the Byron Station Technical Support Center (TSC) emergency ventilation system inlet isolation damper would not open as required to support system operation. This failure affected the ability of the TSC ventilation system to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities of the TSC were unaffected by this condition. If an emergency was declared requiring TSC activation during this period, the TSC would be staffed and activated using existing emergency planning procedures. If the TSC became uninhabitable, the Station Emergency Director would relocate the TSC staff to an alternate TSC location in accordance with applicable procedures. The TSC emergency ventilation system inlet isolation damper has been repaired and is now functional. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the discovered condition affected the functionality of an emergency response facility. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Loss Comm/Asmt/Response |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-05-13
54709 | 0 | Browns Ferry |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-03-16 01:02 | 2020-05-13 13:10 | 2020-05-13 | INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On March 16, 2020, at approximately 0102 CDT, Browns Ferry Nuclear Plant (BFN), Unit 3 received motor trip-out alarms and diagnosed Group 2 and 3 Primary Containment Isolation System (PCIS) Isolations, 3C Residual Heat Removal (RHR) Pump tripping and Reactor Water Cleanup (RWCU) system isolating. All affected safety systems responded as expected. BFN, Unit 3, was nearing the end of the U3R19 refueling outage at the time of the event, and was still dependent on the Shutdown Cooling (SDC) system. Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. At the time of the event, these conditions did not exist: therefore, the PCIS actuation was invalid. "The event was determined to have been caused by clearance restoration activities in an unprotected control panel. A fuse re-installation inadvertently created a fault condition between two different plant 120 VAC power sources when the fuse holder's lower spring clip contacted a different fuse. This was a result of age-related degradation of the fuse holder, its close proximity to other fuses, and the lack of insulating isolation barriers between fuses. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Condition Report 1594925. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode3: Refueling; FMode3: Refueling | Non Emergency | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-05-13
54708 | 0 | Sequoyah | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-05-13 02:08 | 2020-05-13 05:38 | 2020-05-13 | AUTOMATIC REACTOR TRIP "At 0208 EDT on 05/13/2020, Sequoyah Unit 1 was at 100% power when an automatic reactor trip signal was received concurrent with a low steam line pressure safety injection signal. "The low steam line pressure safety injection signal was actuated from the steam pressure rate of decrease feature. Main steam isolation valves (MSIVs) automatically closed as designed and steam generator pressures stabilized following the isolation. All other safety-related equipment operated as designed, with the exception of 1-FCV-61-122 Glycol inboard containment isolation valve which failed to automatically isolate on a Phase A containment isolation signal. The corresponding outboard containment isolation valve, 1-FCV-61-110, automatically isolated as designed which isolated penetration X-114. "Safety injection was terminated at 0221 EDT 5/13/20, and Unit 1 is currently being maintained in Mode 3 at normal operating temperature and pressure with auxiliary feedwater supplying the steam generators and decay heat removal via steam generator atmospheric relief valves. "There is no indication of any primary to secondary leakage. The electrical alignment is normal with shutdown power supplied from off-site power. There is no current operational impact to Unit 2. "There is no impact on public health or safety. Post safety injection actuation investigation is in progress. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | Eccs Injection | RPS Actuation - Critical | Valid Specif Sys Actuation |  | IMode1: Power Operation; FMode1: Hot Standby | Non Emergency | 2 | TN | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2020-05-13
54707 | 0 | Catawba | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-05-12 22:20 | 2020-05-13 01:14 | 2020-05-13 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY DEGRADED "During the performance of reactor vessel closure head (RVCH) inspections, at 2220 EDT on May 12, 2020, it was determined that the Unit 1 RVCH penetration nozzle number 18 did not meet ASME code case N-729-4 requirements. A surface examination (penetrant test) identified a linear indication on nozzle number 18. The indication was not through-wall as determined by ultrasonic testing. The condition of the Unit 1 reactor vessel head penetration nozzle number 18 will be resolved prior to re-installation of the Unit 1 reactor vessel head. This event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Degraded Condition |  |  |  | IMode1: Refueling; FMode1: Refueling | Non Emergency | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2020-05-13
54706 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-05-10 | 2020-05-12 14:02 | 2020-07-01 | AGREEMENT STATE REPORT - NUCLEAR GAUGE BROKEN LOCKING MECHANISM The following was received by the state of Texas via email: "On May 12, 2020, the Agency [Texas Department of State Health Services] was notified by the licensee that the locking mechanism on a Endress Houser nuclear gauge model number FQG61 had broken off the gauge housing preventing them from locking the shutter in the closed position. The gauge contains a 100 milliCurie (original activity) cesium-137 source. The shutter operates normally. The licensee reported the gauge will not present an exposure risk to any individual. The licensee stated it is in the process of trying to schedule repairs to the gauge. Additional information will be provided as it is received in accordance with SA 300." Texas Incident Number: 9766 * * * UPDATE ON 7/1/2020 AT 1312 EDT FROM KAREN BLANCHARD TO BRIAN LIN * * * The following update was received via email: "On June 30, 2020, the licensee reported that there had been another failure with the gauge. The Radiation Safety Officer [RSO] was investigating to determine what had happened and learned that the rotary element and the source tube attached to it had come partially out of the gauge and when employees tried to put it back in it came apart into pieces. The two employees thought the source was still in the gauge housing and they picked up the pieces. They did not realize that one of the pieces they picked up was the source and it had separated from the source tube. One employee picked it up and gave it to the other employee who put it into his shirt pocket. The RSO contacted a licensed service company who put the source into a lead pig and it is now secured at the licensee's facility. The licensee is continuing to investigate, but initial dose calculations as of July 1, 2020 indicate the dose, especially to the one employee, will exceed reporting requirement of greater than 25 rem TEDE [Total Effective Dose Equivalent]. The licensee will conduct a re-enactment to collect better information for dose reconstruction and calculation. They have been given the information for REAC/TS and have indicated they will pursue contacting them for biodosimetry. Current activity for the Cesium-137 source is 95 milliCuries (was 100 milliCi original activity). More information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Silva), NMSS Regional/INES Coordinator (Rivera-Capella) and NMSS Event Notifications (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-05-20
54705 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-05-11 | 2020-05-12 12:00 | 2020-05-12 | AGREEMENT STATE REPORT - RADIATION LEVEL ON PACKAGE EXCEEDS DOT LIMITS The following was received via email: "On May 11, 2020 the licensee received a 10 gallon drum that fell outside of the Department of Transportation (DOT) dose rate level limitations. The package came from Cadman Materials, Inc. in Vancouver WA. The material inside is a gauge with a Cs-137 sealed source inside with an activity of 100 millicuries (3700 MBq). The package was shipped as UN2915, Radioactive Material Type A Package with Yellow-II labeling and a Transport Index of 0.1. Upon survey at receipt, the container exhibited dose rates of 3.4 rem/hr on contact, 240 mrem/hr at 12 inches, and 18 mrem/hr at 3.3 feet. The delivering carrier, and the client, Cadman Materials, have been notified. The Pennsylvania Bureau of Radiation Protection will update this event as soon as more information is provided." The event is reportable per 10 CFR 20.1906(d)(2). PA Event Report ID No: PA200012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-05-20
54704 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-05-11 | 2020-05-12 09:50 | 2020-05-12 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following is a summary of an email received from the state of Florida: A patient underdose occurred during a Y-90 TheraSphere treatment at the licensee on 5/11/20. The patient was prescribed 2.48 GBq of Y-90, but only received 1.86 GBq (75% of the prescribed dose). The underdose was caused by the catheter being displaced during patient movement. Florida Incident Number: FL20-056 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-05-20
54703 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-05-11 20:30 | 2020-05-12 07:41 | 2020-05-12 | AGREEMENT STATE REPORT - LOST GAUGE The following is a summary of an email received from the state of Florida: At approximately 2030 EDT on 5/11/2020, a Troxler density gauge (serial number: 28189) fell off the back of one of the licensee's trucks because the chain securing the gauge's case was not properly attached. The gauge has not been located at this time. The gauge contains an 8 milliCurie Cs-137 source and a 40 milliCurie Am-241 source. Nearby police departments, the US Department of Transportation, and the Florida Department of Environmental Protection have all been notified. Florida Incident Number: FL20-057 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-05-20
54702 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-05-11 | 2020-05-11 21:55 | 2020-05-11 | AGREEMENT STATE REPORT - TROXLER GAUGE DESTROYED BY BULLDOZER The following was received from the Illinois Emergency Management Agency via email: "The Illinois Emergency Management Agency (IEMA) communications center was notified at approximately 1942 [CDT] on 5/11/20 by the radiation safety officer for Testing Service Corp., license number IL-01178-01, to advise that a gauge user operating a Troxler model 3440 was struck by a bulldozer. The gauge user is reportedly fine, but the gauge was destroyed. The density gauge, serial number 72404, contains 8 mCi of Cs-137 and 40 mCi of Am-241/Be. Reportedly the source rod remained intact and both sources were identified and recovered into a lead drum. The licensee does possess a Geiger Muller survey meter and reported an external survey rate of 0.4 mR/hour on the outside of the drum (0.0 mR/hour is the reported background). The incident occurred at the southeast corner of Vollmer and Harlem in Matteson, IL. The sources were transported back to the licensee's facility. Agency inspectors are meeting with the licensee at 0700 [CDT] on 5/12/20 to verify the recovery of both sources, perform gross leak tests, advise on appropriate follow-up actions, and perform a site survey in Matteson. The licensee has already been in contact with the manufacturer for advice and instructions for returning the sources." Illinois Event No.: IL200007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-05-19
54701 | 0 | Palo Verde |  |  | 3 | [1] CE,[2] CE,[3] CE | 2020-03-14 12:44 | 2020-05-11 13:07 | 2020-05-11 | INVALID ACTUATION OF SPRAY POND PUMP SYSTEM - 60 DAY REPORTS "The following event descriptions are based on information currently available. If through subsequent reviews of these events additional information is identified that is pertinent to the events or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "This telephone notification is being made pursuant to the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) and 50.73(a)(1) to describe invalid actuations of both trains of the Palo Verde Nuclear Generating Station (PVNGS) Unit 3 essential spray pond (SP) system, which serves as an emergency service water system that does not normally run and serves as an ultimate heat sink as described in 10 CFR 50.73(a)(2)(iv)(B)(9). "This notification covers two similar, but separate invalid actuations occurring in Unit 3 on March 14, 2020 at 12:44 [MST] and again on April 25, 2020 at 12:10 [MST]. On each day, an invalid actuation of the Unit 3 train "B" Fuel Building Essential Ventilation Actuation Signal (FBEVAS) occurred during performance of the Balance of Plant Engineered Safety Features Actuation System weekly auto test. The auto/manual pushbutton was depressed to initiate the test and the sequencer immediately tripped FBEVAS train "B" with subsequent cross trip of FBEVAS train "A". These actuations resulted in complete and successful actuations of both trains of essential spray pond pumps. "The events were entered into the PVNGS corrective action program and a station evaluation is in progress. There was no adverse impact to public health and safety nor to plant employees. "The NRC resident inspectors have been informed." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode3: Power Operation; FMode3: Power Operation | Non Emergency | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-05-11
54700 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-05-09 12:15 | 2020-05-10 09:47 | 2020-05-10 | OFFSITE NOTIFICATION FOR FIRE IMPAIRMENT "On May 8th, GNF-A [Global Nuclear Fuels - America] underwent an unplanned local power outage due to failed equipment at a substation. The facility shutdown safely. While critical systems are on generators, the fire alarm systems are on batteries which will be depleted before power can be restored. Compensatory measures were enacted. "At approximately 1215 (EDT) on May 9th, 2020, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire alarm systems would not function. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-05-10
54699 | 0 | Global Nuclear Fuel - Americas |  |  |  | Uranium Fuel Fabrication | 2020-05-07 16:25 | 2020-05-08 14:23 | 2020-05-08 | CONCURRENT REPORT FOR A COMMUNICATION LINE OUT OF SERVICE The following was received via email from Global Nuclear Fuel - America: "On May 7, 2020, Global Nuclear Fuel America initiated maintenance activities on fire alarm systems that affect the Waste Treatment facility and the Process Lagoons. Compensatory measures were enacted. Upon system restoration, it was determined that a communication line between the initiating devices of fire alarm systems and the Emergency Control Center (ECC) was not functioning. Per State code requirements, fire alarm systems must report back to a continuously monitored station. Compensatory measures remained in place. "At approximately 1625 (EDT) on May 7, 2020, the New Hanover County Deputy Fire Marshall was notified per State code requirements that communications between the initiating devices of fire alarm systems and the ECC were not functioning. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A (c)." The licensee will notify NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Offsite Notification/News Rel | [9 empty] | Non Emergency | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-05-08
54698 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-05-07 | 2020-05-07 20:41 | 2020-05-11 | AGREEMENT STATE REPORT - DAMAGED NUCLEAR GAUGE The following was received from the state of Texas by email: "On May 7, 2020, the Agency was notified by the licensee that a Humboldt model 5001 EZ was damaged at a temporary job site [in Dallas, TX]. The gauge contains a 40 milliCurie americium-241 source and an 8 milliCurie cesium-137 source. The gauge was struck by the bucket of a Bobcat machine breaking the handle rod. The cesium source was in the fully shielded position. The cesium source could not be operated. The technician set up a barrier and contacted the radiation safety officer (RSO.) The RSO performed a radiation survey and measured the dose rate at two feet from the gauge at 0.15 millirem per hour, which is normal according to the licensee. The gauge was returned to the licensee's facility. No individual received a significant exposure due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9764 * * * UPDATE FROM ART TUCKER TO BRIAN P. SMITH AT 1046 EDT ON 5/11/2020 * * * The following update was received from the state of Texas by email: "On May 8, 2020, the licensee notified the Agency that the activity of the cesium source involved in this event was 10 milliCuries and not 8 milliCuries as previously reported. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (O'Keefe), and via E-mail: NMSS Events Notifications E-mail group | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-05-15
54697 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-03-08 20:21 | 2020-05-06 14:11 | 2020-05-06 | INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. On March 8, 2020, at approximately 2021 CDT, Browns Ferry Nuclear Plant Unit 2 experienced an unexpected loss of the 2A Reactor Protection System (RPS). This resulted in Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations, and the initiation of Standby Gas Treatment Trains A and B, and Control Room Emergency Ventilation System Train A. All affected safety systems responded as expected. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The RPS MG Set trip was believed to have been caused by an intermittent short across a spike suppressor, which led to a loss of generator output signal to a voltage regulator. The affected components have been replaced. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Condition Report 1593265. "The NRC Resident Inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-05-06
54696 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-05-05 | 2020-05-06 12:43 | 2020-05-12 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received via email: "The Department [Pennsylvania Bureau of Radiation Protection] received notification from a licensee on May 5, 2020, of a medical event involving a Varian GammMedplus iX high dose rate remote afterloader (HDR) containing 8.6 Ci of iridium 192. The patient was set to receive 10 fractions (channels) of breast cancer treatment. An error was noted when treatment from the third channel was attempted. The source was retracted back into the safe position upon the error indication. Staff reset the unit and rebooted. The unit functioned normally for the fourth channel. During the fifth channel the machine experienced another fault, but the source did not automatically retract. Staff then attempted two emergency stop procedures; however, both failed. Staff were finally able to manually retract the source after approximately two to four minutes; however, it hasn't been determined if the source was completely retracted into the shielded safe on the HDR due to catheter interference. The patient was quickly disconnected from the catheter, everyone was immediately removed, and the room was secured from entry. No dose is expected outside the HDR room as it is housed within an accelerator vault. The manufacturer has been contacted. The licensee has also requested the log files from the manufacturer for dose reconstruction of those involved. The department is currently in contact with the licensee and will update this event as soon as more information is provided." PA Event Report ID No: PA200011 * * * UPDATE ON 5/7/20 AT 1208 EDT FROM JOHN CHIPPO TO ANDREW WAUGH * * * The following information was received via email: "Manufacturer service technicians removed the wire/source from the afterloader on 5/6/2020. Preliminarily, it appears the source became stuck approximately 4 to 5 inches from the shielded park position (inside the afterloader, but outside the shielded safe). Dosimetry badges have been sent for emergency read, results are expected today, and those results are expected to be minimal." The patient and all personnel involved were surveyed after the incident and readings were at background levels. Notified R1DO (Dentel) and NMSS Event Notifications (email). * * * UPDATE ON 5/12/20 AT 1158 EDT FROM JOHN CHIPPO TO JEFFREY WHITED * * * The following information was received via email: "The preliminary dosimetry report indicates three staff members involved in the event. The technologist received 4 mrem whole body dose, the authorized user received 3 mrem whole body dose and the AMP received 3 mrem whole body dose and a 15 mrem dose on their finger dosimeter. No other dose information was received at this time." Notified R1DO (Lally) and NMSS Event Notifications (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-05-14
54695 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-07-01 | 2020-05-05 17:34 | 2020-05-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via email: The licensee is unable to locate six tritium exit signs that have an activity of 7.5 Ci each. The exit signs may have been lost during a renovation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-05-13
54694 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2020-05-04 | 2020-05-05 13:16 | 2020-05-05 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following was received via email: "On 5/4/20, Piedmont Athens Regional Medical Center (GA 4-1) experienced a misadministration of BTG's TheraSphere Y-90 product. The plan of treatment was for [the treating physician] to deliver 120 Gy to the patient's left hepatic lobe with 1.62 GBq (43.78 milliCuries) of Y-90. The treating physician positioned the microcatheter in the left hepatic artery and verified positioning with a left hepatic arteriogram. With the microcatheter in this position, the treating physician began administering the microspheres. However, only a portion of the dose was delivered as the catheter quickly became occluded. Because of the patient's tortuous hepatic vasculature, the assessment is that a kink in the microcatheter prevented the majority of the dose from being delivered. "The delivered activity was calculated by comparing pre- and post-treatment survey meter measurements of the administration equipment as outlined in TheraSphere's administration procedure. The delivered activity to the patient was 0.28 GBq (7.52 milliCuries). The delivered activity is approximately 83 percent less than the prescribed activity. Post treatment surveys of all gowns, syringes, gloves, drapes, floor coverings, and trash revealed no contamination of the surgical suite. Post treatment planar imaging revealed no extrahepatic deposition of activity. The treating physician explained our inability to deliver the full dose with the patient and a plan was made for the patient to return on 6/5/20 for a second attempt at treating the left hepatic lobe." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-05-13
54693 | -1 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2020-05-04 16:40 | 2020-05-04 23:40 | 2020-05-08 | DIESEL GENERATOR COOLING WATER SYSTEM DECLARED INOPERABLE "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to mitigate the Consequences of an Accident. A through wall leak was found on piping connected to the Division 3 Diesel Generator (DG) Cooling Water Strainer. This condition has been evaluated and the Division 3 DG Cooling Water System has been declared inoperable. The Division 3 DG Cooling Water System is a support system for the Division 3 Emergency DG and the High Pressure Core Spray System (HPCS). "The NRC Resident Inspector has been notified." * * * RETRACTION ON MAY 8, 2020 AT 1709 EDT FROM JOE MESSINA TO BRIAN LIN * * * "This update retracts Event Notification #54693, which reported a condition that could have potentially prevented fulfillment of a safety function needed to mitigate the consequences of an accident. "An evaluation of the flaw on the piping connected to the Unit 2 Division 3 Diesel Generator (DG) Cooling Water strainer concluded that the system would have remained operable. The High Pressure Core Spray system, supported by the operable DG Cooling Water system, remained operable and capable of performing its safety function. "The NRC Resident Inspector has been notified." Notified R3DO (Stone). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-05-04
54692 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2020-05-03 17:50 | 2020-05-03 22:28 | 2020-05-03 | MAIN CONTROL ROOM AIR TREATMENT SYSTEM INOPERABLE "On 5/3/2020 at 1100 EDT, Operations identified a step change in the Main Control Room ambient noise. The cause of the noise was a rise in vibrations on the Number 11 fan motor of the Main Control Room Ventilation Circulating Fan. Another step change in noise occurred and Operations swapped from the Number 11 fan motor to its redundant Number 12 fan motor, but the noise and vibrations did not improve. The two independent motors are connected to the blower shaft with belts on either end of the shaft. This entire fan and motor assembly is contained within the Main Control Room ventilation ducting and is not visible. At 1118 EDT, Operations shut off the Main Control Room Ventilation Circulating Fan due to Number 11 fan motor vibrations, declared the Main Control Room Air Treatment System inoperable, and entered the Technical Specification 3.4.5.e, 7-day action statement. "At 1750 EDT, Maintenance entered the ductwork and informed Operations that the Number 11 fan bearing had catastrophically failed and because of the extent of damage and close physical proximity to the Number 12 fan motor, jeopardized its continued operation. As a result, Operations also declared the Number 12 fan motor inoperable and determined the event was reportable as a loss of safety function per 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-05-03
54691 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2020-05-03 08:21 | 2020-05-03 11:43 | 2020-05-03 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 0821 EDT on May 3, 2020, the Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a trip of the Main Turbine. "The Unit 1 reactor was operating at 76 percent reactor power following a ramp schedule to full power subsequent to a maintenance outage. The Control Room received indication of a Main Turbine trip with both divisions of the Reactor Protection System actuated and all control rods inserted. The Reactor Recirculation Pumps tripped on End of Cycle - Recirculation Pump Trip. Reactor water level lowered to -1 inch causing Level 3 (+13 inches) isolations. No Emergency Core Cooling System or Reactor Core Isolation Cooling actuations occurred. The operations crew subsequently maintained reactor water level at the normal operating band using Reactor Feed Water. No Steam Relief Valves opened. "The reactor is currently stable in Mode 3. Investigation into the trip of the Main Turbine is in progress. "The NRC Resident Inspector was notified. A voluntary notification to the Pennsylvania Emergency Management Agency and press release will occur. "This event requires a 4-hour Emergency Notification System (ENS) notification in accordance with 10 CFR 50.72(b)(2)(iv)(B) and an 8-hour ENS notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(3)(iv)(B)." | 0 | 0 | 0 | 76 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | Non Emergency | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-05-03
54690 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2020-05-01 08:31 | 2020-05-01 15:34 | 2020-05-01 | BOTH SECONDARY CONTAINMENT ACCESS DOORS OPEN SIMULTANEOUSLY "At 0831 CDT, the Main Control Room received a 'Reactor Building 903 ft. Access Both Doors Open' alarm. Investigation found the interlock between the inner and outer doors did not prevent the opening of both doors while personnel were accessing the Reactor Building. The doors were immediately closed. Based on alarm times, both doors were open for less than one second. With both doors open, SR 3.6.4.1.3 was not met and Secondary Containment was declared inoperable. This unplanned Secondary Containment inoperability constitutes a condition reportable under 10 CFR 50.72(b)(3)(v)(c) and (d), 'An event or condition that at the time of discovery could have prevented the fulfillment of the safety function of SSCs that are needed to control the release of radioactive material and mitigate the consequences of an accident.' "Secondary Containment was declared operable at 0836 CDT after independently verifying at least one Secondary Containment access door was closed. "The NRC Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | Pot Uncntrl Rad Rel | Accident Mitigation |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 4 | NE | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2020-05-01
54689 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-04-28 | 2020-05-01 12:22 | 2020-05-04 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the state of California via email: "On 4/30/2020, at approximately 1127 [PDT], the RSO [radiation safety officer] of RMA Group, RML Number 8055-19, contacted RHB [California Radiologic Health Branch] Brea concerning a moisture/density gauge, Troxler, model 3440, serial number 25671 (Cs-137, 0.3 GBq, Am-241, 1.50 GBq) that had been stolen from in front of a private apartment complex while the RMA employee was offloading his vehicle. The Troxler radioactive gauge was left on the sidewalk during offloading of the vehicle. [The RMA employee] forgot about the gauge he had left on the sidewalk as he then drove off to have his vehicle washed. When he returned from the carwash at approximately 1730 to 1800 on 4/28/2020, he realized that he had left the radioactive gauge in front of the apartment complex and that it was no longer there. The [RSA employee] finally reported the theft to the RMA RSO on 4/29/2020 at 1215, prior to reporting the theft to Los Angeles Police Department at the West Los Angeles office on 4/29/2020 at 1245. A copy of the theft report and the [employee's] statement has been sent to RHB Brea as part of this report. [The RMA RSO] will utilize local papers to attempt to retrieve the stolen gauge as well as notifying local servicing vendors of radioactive gauges to be alert of the serial number of the stolen gauge in case it turns up for any of their services. "The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame. This is being reported to the NRC Operations Center as a 24-hour report under 10 CFR 20.220(a)(1)(i) since the radioactive gauge has been stolen with the source handle locked and the Type A transport container locked." California Report Number 5010-043020 * * * UPDATE FROM DONALD OESTERLE TO DONALD NORWOOD AT 1516 EDT ON 5/4/2020 * * * The gauge has been recovered intact. A formal closing report will be submitted later. Notified R4DO (Drake), and via E-mail: NMSS Events Notifications E-mail group, ILTAB, and CNSNA (Mexico). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-05-11
54688 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2020-05-01 12:53 | 2020-05-01 13:16 | 2020-05-01 | NOTIFICATION OF UNUSUAL EVENT DUE TO FIRE IN NON-SAFETY RELATED ELECTRICAL SWITCHGEAR At approximately 1238 EDT on May 1, 2020, an alarm indicated smoke on a non-safety related electrical switchgear bus in the turbine building. Plant personnel were dispatched to investigate. Smoke and heat were found coming from the bus. At 1253 EDT, a Notification of Unusual Event was declared. At 1308 EDT the fire was declared out and fire watches posted. Offsite assistance was requested during the event and the Jenkinsville, SC fire department responded to the site. There were no plant personnel injuries or impact to the health and safety of the public. The cause of this event is unknown at the present time. The electrical bus has been de-energized. The unit is currently in a planned refueling outage. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE FROM GEORGE SHEALY TO DONALD NORWOOD AT 1754 EDT * * * The Notification of Unusual Event was terminated at 1737 EDT on May 1, 2020. The cause of the event is currently being investigated. The licensee will notify the NRC Resident Inspector. Notified R2DO (Miller). NRR EO (Miller), IRD MOC (Grant). Additionally, notified DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Emergency Declared |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | Unusual Event | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2020-05-01
54687 | -1 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-05-01 03:54 | 2020-05-01 11:53 | 2020-05-15 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE "At 1000 EDT on May 1 2020, Operations commenced a shutdown of DC Cook Unit 2 to comply with LCO 3.4.13, Condition B Reactor Coolant System (RCS) pressure boundary leakage. "At 0354 EDT on May 1, 2020, Operations detected an estimated 8 gpm Reactor Coolant System leak. The source of the leak could not be identified and Tech Spec 3.4.13, Condition A was entered for unidentified RCS leakage in excess of the 0.8 gpm limit. "At 0745 EDT on May 1, 2020, Unit 2 entered LCO 3.4.13, Condition B when the 4-hour limit to complete the required actions of Condition A could not be met. "At 0945 EDT on May 1, 2020, Unit 2 entered LCO 3.4.13, Condition B when the 4-hour limit to complete the required actions of Condition A could not be met. "At 0945 EDT on May 1, 2020, inspections inside containment identified the leak as pressure boundary leakage from a pressurizer spray line which also requires entry into LCO 3.4.13, Condition B. "At 1059 EDT on May 1, Unit 2 was tripped from 15 percent power. All systems functioned normally. "This event is reportable under 10 CFR 50.72(b)(2)(i), the initiation of any nuclear plant shutdown required by the plant's Technical Specifications as a 4-hour report and under 10 CFR 50.72 (b)(3)(ii)(A), degraded condition, as an 8-hour report. The NRC Resident Inspector has been notified." * * * PARTIAL RETRACTION ON 5/15/2020 AT 1442 EDT FROM BUD HINCKLEY TO THOMAS HERRITY * * * "The condition identified in EN #54687, pursuant to 10 CFR 50.72 (b)(3)(ii)(a) has been evaluated, and has been determined not to be RCS pressure boundary leakage. As such, the 8-hour report is being retracted, as it is not an event or condition that results in, 'the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The leakage was subsequently determined to be from the tell-tale nipple of a pressurizer spray valve, not from the pressurizer spray line piping as previously reported. The Reactor Coolant Pressure Boundary (RCPB) is formed by the valve body, plug, seat, body to bonnet extension, and bonnet of the pressurizer spray valve. Therefore, the leakage is not RCPB leakage. "There is no change to the 4-hour report made under 10 CFR 50.72(b)(2)(i), the initiation of any nuclear plant shutdown required by the plant's Technical Specifications. "The NRC Resident Inspector was notified of this retraction." Notified R3DO (Stone). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Plant S/D Reqd By Ts | Degraded Condition |  |  | IMode2: Power Operation; FMode2: Hot Standby | Non Emergency | 3 | MI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2020-05-01
54686 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2020-03-20 | 2020-04-30 19:50 | 2020-04-30 | AGREEMENT STATE REPORT - BRACHYTHERAPY UNDERDOSE DUE TO AN ERROR IN THE TREATMENT PLAN The following information is summarized from the report received from the state of Nevada via email: A patient was scheduled to receive 34 Gy to the treatment site via a Nucletron brachytherapy device containing 444 GBq of Ir-192. The dose was to be received via two fractions-a-day for 5 days. All fractions were delivered as scheduled. During the post-treatment review, it was determined that the delivery device was placed 8 mm proximal to the intended treatment site due to a digitization error in the treatment plan. This resulted in the patient receiving 71 percent of the intended dose. At the time of the report, there were no acute ill-effects on the patient. NMED Report No.: NV200006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2020-05-08
54685 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2020-04-29 | 2020-04-30 18:51 | 2020-04-30 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE DURING BRACHYTHERAPY TREATMENT The following information was received from the state of Nevada via email: "The patient was undergoing radiation treatment using Ir-192 and the high dose rate remote afterloader (Varian VS 2000) in three fractions. There were no problems with fractions one and two. During the third fraction, the vaginal cylinder device was inserted into the patient by the doctor. Unknown to the doctor, the device penetrated through the body wall weakened by previous surgery (according to the doctor, [this is] not unknown following robotic hysterectomies). This penetration allowed the source to move about 4 cm past the treatment area. As a result, the treatment area only received 25 percent volume coverage instead of the planned 95 percent volume coverage." The device was a Varian Remote Afterloader, Model VS 2000, which contained 407 GBq of Ir-192. NMED Report No: NV200007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2020-05-08
54684 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-04-20 | 2020-04-30 15:37 | 2020-04-30 | AGREEMENT STATE REPORT - USED BEVERAGE CAN (UBC) BALED ALUMINUM RETURNED TO FLORIDA The following information was received from the state of Florida via email: "The state of Kentucky Radiation Health [Branch] faxed a report of rejection of an UBC [used beverage can) bale from Logan Aluminum of KY, originating from Republic Services of Jacksonville, FL. The radiation measurement was 1200 cps (also reported as 0.7 mR/hr.) midway of the enclosed trailer. Background measured 121 cps. "DOT-SP 10656 KY-FL-20-001 was issued. Per [an employee] of Republic Services, this load was comprised of household curbside waste, and 'people put whatever they want in there.' Only one bale was higher than background. The rest of load successfully resubmitted. "Update: This bale was returned to Florida for investigation, whereupon [the Radiation Safety Officer at Republic Services] reached out to the [Headquarters Operations Officer at the Nuclear Regulatory Commission], who transferred him to the BRC [Florida Bureau of Radiation Control]." Florida BRC will be conducting a follow-up investigation. Florida Incident Number: FL20-051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-05-08
54683 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2020-02-24 | 2020-04-28 14:49 | 2020-04-28 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATORS CONTAINING POLONIUM-210 The following information was obtained from the state of Tennessee via email: "During a recent inventory at two different locations of Service King Collision Repair Centers, two static elimination devices were found to be missing. One location in Chattanooga, TN, lost the device during the transition of closing the repair center. Updated information will be included in a follow-up report. The information for the devices is below: Manufacturer Model Serial# Isotope Activity NRD, LLC P-2021 A2LV457 Po-210 10 mCi NRD, LLC P-2021 A2LU553 Po-210 10 mCi" Tennessee Event Report ID No.: TN-20-076 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-05-06
54682 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2020-04-24 | 2020-04-27 09:50 | 2020-04-27 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER TEST FAILURE The following was received from the Commonwealth of Virginia via email: "On April 24, 2020, a licensee reported that the shutter of a fixed gauge used to measure the level of material inside a process vessel was stuck in the open position. This incident was identified on April 24, 2020, during the biennial leak testing of the source. The gauge is a Ronan Engineering Company, device (Model SA-1, serial number SO-VA-7063), and Source (Model SA1-F37, serial number M7451), containing 40 mCi of Cs-137. The report indicated that the impacted site personnel were notified immediately and barriers were erected to prevent access to the gauge area. Based on the report, there was no public exposure or environmental release from this event. The licensee has contacted the manufacturer (Ronan Engineering Company) for further investigation and to fix the problem. "The Virginia Office of Radiological Health will review the licensee's written report and determine if additional actions are needed to be taken." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2020-05-05
54681 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2020-04-24 05:44 | 2020-04-24 07:10 | 2020-04-24 | SAFEGUARDS REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND Attempted introduction of contraband into a protected area. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Safeguards Reports | [9 empty] | Non Emergency | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2020-05-04
54680 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2020-04-24 01:30 | 2020-04-24 07:00 | 2020-04-24 | REACTOR COOLANT SYSTEM (RCS) PRESSURE BOUNDARY DEGRADED "At 0130 [EDT] on April 24, 2020, during the Beaver Valley Power Station, Unit 2 refueling outage, while performing examinations of the 66 reactor vessel head penetrations, it was determined that one penetration could not be dispositioned as acceptable per ASME Code Section XI. Penetration 37 will require repair prior to returning the vessel head to service. The indication was not through wall and there was no evidence of leakage based on inspections performed on the top of the reactor vessel head. The examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-4 to find potential flaws/indications before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. This event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Degraded Condition |  |  |  | IMode2: Refueling; FMode2: Refueling | Non Emergency | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2020-04-24
54679 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-04-05 | 2020-04-23 10:57 | 2020-04-23 | AGREEMENT STATE REPORT - STUCK SHUTTER ON BERTHOLD RADIOACTIVE GAUGE The following information was received from the Commonwealth of Pennsylvania via email: "On April 5, 2020, a technician reported to the [licensee radiation safety officer] RSO that when a shutter handle on a Berthold LB8010 with 20 mCi Cs-137 was moved to the closed position, the radiation survey indicated reduced radiation, but not the expected level. The shutter was opened and closed again, and radiation levels were lower but not at normal closed position levels. The gauge has been removed from service and is secured onsite in Canton, PA, awaiting a shipping container for return to the manufacturer. The gauge will be returned for repair or replacement. No personnel overexposure has occurred. "The Department [Pennsylvania Department of Environmental Protection] will perform a reactive inspection. More information will be provided upon receipt. Pennsylvania Report ID No.: PA200008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-05-01
54678 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2020-04-22 10:54 | 2020-04-22 18:46 | 2020-04-22 | FITNESS FOR DUTY (FFD) POLICY VIOLATION A licensed operator had a confirmed positive for alcohol during a random fitness-for-duty test. The individual's unescorted access has been terminated. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | Fitness For Duty |  |  |  | Power Operation | Defueled | Power Operation | Power Operation | Defueled | Power Operation | Non Emergency | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2020-04-22
54677 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2020-04-22 10:15 | 2020-04-22 14:52 | 2020-04-22 | HIGH PRESSURE COOLANT INJECTION SYSTEM (HPCI) INOPERABLE "At 1015 [EDT], on 04/22/2020, while Unit 2 was at approximately 0.4 percent power in MODE 2, reactor pressure was increased to 150 psig while HPCI was INOPERABLE due to not having been placed in standby. HPCI does not have a redundant system; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). ADS [Automatic Depressurization System] and low pressure ECCS [Emergency Core Cooling System] systems were OPERABLE during this time. HPCI was returned to OPERABLE status at 1109 hrs. on 04/22/2020. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0.4 | 0 | 0 | 0.4 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | IMode2: Startup; FMode2: Startup | Non Emergency | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-04-22
54676 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2020-04-22 10:42 | 2020-04-22 14:23 | 2020-04-22 | AGREEMENT STATE REPORT - GAUGE SYSTEM SWITCH FAILURE The following was received from the state of Kentucky via fax: "Kentucky Radiation Health Branch was notified on 4/22/20 by a representative from International Paper of a failure of a magnetic reed switch on their Honeywell gauging system. This switch senses when the mass measurement heads are separated and closes the shutter window on the radioactive source. There are two other means of determining whether the heads are out-of-alignment that also trigger the shutter window to close if indicated. Therefore, these additional layers of protection are adequate to protect against a radiation exposure if the heads are separated. International Paper has returned the system to service with the Honeywell recommendation to replace the switch as soon as the replacement part arrives. Per [the representative] of Honeywell, with the understanding that the failed component will be replaced, the customer can continue to keep the scanner under operation with the basis weight sensor." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2020-04-30
54675 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2020-03-05 10:25 | 2020-04-22 10:43 | 2020-04-22 | 60-DAY TELEPHONIC NOTIFICATION OF AN INVALID SPECIFIED SYSTEM ACTUATION "This 60-day optional telephone notification is being made in lieu of an LER [licensee event report] submittal as allowed by 10 CFR 50.73(a)(1). This notification is made pursuant to the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of one of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). "At approximately 1025 Eastern Standard Time (EST) on March 5, 2020, with Unit 1 shutdown in Mode 5 for refueling, an invalid actuation of Group 6 Primary Containment Isolation Valves (PCIVs) (i.e., Containment Atmospheric Control/Monitoring and Post Accident Sampling isolation valves) occurred. The invalid actuation occurred when power was lost as a result of the Inboard Isolation Logic Fuse being removed per a planned clearance hang to support maintenance. "The PCIVs functioned successfully and the actuation was complete. The actuation was not initiated in response to actual plant conditions, it was not an intentional manual initiation, and there were no parameters satisfying the requirements for initiation of the system. Therefore, this event has been determined to be an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | Invalid Specif System Actuation |  |  |  | IMode1: Refueling; FMode1: Power Operation | Non Emergency | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2020-04-22
54674 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2020-04-20 | 2020-04-21 17:18 | 2020-04-21 | PART 21 REPORT - DEFECT IN THERMOCOUPLE LOW LEVEL AMPLIFIER MODULES The following is a summary of information received from Curtiss-Wright, Nuclear Division: Three RTL modules [thermocouple low level amplifiers] have been delivered to clients that may have included faulty resistors that could have remained undetected during functional testing and will eventually malfunction with time in service. MAY/MCY resistors are precision, low temperature coefficient, metal foil technology resistors used in circuits where stability with time and temperature is required. The RTL module uses this style of resistor to achieve its accuracy and variable temperature effects specifications. The symptoms exhibited by faulty resistors were open circuit or changes in value in response to physical or thermal stress. Faulty resistors were sent to the manufacturer for failure analysis. Cracks were discovered in the bond wires that connected the resistor leads to the resistor chip inside the resistor package. The failure rate of resistors manufactured in 2017 and 2018 was significantly greater than resistors manufactured in earlier years. A search of the build records during that time interval resulted in three units. These three modules contain 10 kilo-ohm resistors with date codes from 2017. There are two 10 kilo-ohm resistors in an RTL module, R8 and R17, on the main circuit board assembly. Configured for an RTD input, only R8 is active. R8 sets the 1 milli-ampere excitation current for the RTD element. R17 is used in a voltage offset circuit that is only used in thermocouple and low level amplifier configurations. If the module has been in service for any significant amount of time with no problems, 12 weeks or more, then it is probable that R8, the only suspect resistor in the default configuration, is not affected by this phenomenon. However, if the module has not seen significant service, then the module should be considered suspect. Additionally, if the module has been or could in the future be reconfigured to a low level amplifier or thermocouple application, then the same situation exists with R17, which is not used in the default configuration. Affected Plant - Part Number (Serial Numbers): Beaver Valley - NUS-A135PA-1/3 (s/n: 1800083) Indian Point 3 - NUS-A138PA-3/13/W (s/n: 1800334) Ginna - NUS-A138PA-1/4 (s/n: 1800666) Contact Scientech-I&C-Repair@curtisswright.com to return these modules for further testing and rework, if necessary. Should you have any questions regarding this matter, please contact: Shanen Onken Scientech Business Segment Manager Curtiss-Wright Nuclear Division sonken@curtisswright.com Tel 208-497-3410, Cell 208-821-4054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [10 empty] | 4 | ID | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-04-21
54673 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-04-17 18:00 | 2020-04-18 12:20 | 2020-04-18 | AGREEMENT STATE REPORT - POSSIBLE MEDICAL EVENT The following was received from the state of Arizona via email: "On April 17, 2020, at approximately 1800 [MDT], the Department [Arizona Department of Health Services] received notification from the licensee of a possible medical event involving Yttrium-90 radiolabeled glass microspheres (Therasphere). The dose on the written directive was 150 Gy and the pre-treatment measurement was approximately 4.6 GBq. Following the delivery, the nuclear medicine technologist took readings of the waste containers and got an average of 4.58 mR/hr (highest of 11.8 mR/hr) from the first jar and an average of 1.39 mR/hr (highest of 2.6 mR/hr) from the second jar. The licensee is investigating the irregular waste readings and attempting to calculate the actual dose to the patient. "The Department has requested additional information and continues to investigate the event." Arizona Event No. 20-009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-04-27
54672 | 0 | CHRISTIANA CARE HEALTH SERVICES |  |  |  |  | 2020-04-16 | 2020-04-17 12:37 | 2020-04-17 | UNDERDOSE TO PATIENT The following is a summary of information received via telephone: On April 16, 2020, a patient received 11.5 percent of the prescribed dose of Y-90 TheraSphere therapy to the left liver. It is believed that the delivery device malfunctioned as the technician experienced increased pressure in the line when pushing the TheraSphere into the caster. The therapy was aborted after a few failed attempts. The intended dose was 97.3 milliCuries of Y-90. The patient is aware and will be returning for the remainder of the dose. The licensee contacted the vendor who will discard the malfunctioned device. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Dose <> Prescribed Dosage | [9 empty] | Non Emergency | 1 | DE | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2020-04-27
54671 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-06-14 | 2020-04-16 15:34 | 2020-04-16 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following is a summary of information received from the State of Colorado via e-mail: The licensee is unable to locate two tritium exit signs each with an activity of 10.0 Ci. The two exit signs were not able to be accounted for during annual registration. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-24
54670 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2020-04-16 07:46 | 2020-04-16 09:09 | 2020-04-27 | SECURITY WEAPON LEFT UNATTENDED Discovered a vulnerability and non-compliance with the security plan. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 4/17/20 AT 0856 EDT FROM RANDY SHACKELFORD TO ANDREW WAUGH * * * This event is being retracted because it does not meet the reporting requirements. The licensee notified the NRC Resident Inspector. Notified R2DO (Miller), NMSS Events Notification (email), 73.71 Reports Group (email), Fuels Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | Safeguards Reports | [9 empty] | Non Emergency | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2020-04-24
54669 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2020-04-15 12:56 | 2020-04-15 14:50 | 2020-04-15 | AGREEMENT STATE REPORT - EXPLOSION OF BUILDING CONTAINING NUCLEAR GAUGES The following information was received via e-mail: "The State of Maine Radiation Control Program became aware of a breaking news item, reporting that the Pixelle Androscoggin paper mill in Jay, Maine had suffered an explosion. https://www.wabi.tv/content/news/Explosion-reported-at-Jay-mill-details-limited-569661451.html "The precise location of the explosion is unknown at this time but it may be the boiler or power plant. Later report from MEMA - Maine Emergency Management Agency - says that it was 'the Digester of Pulp Mill A or maybe B.' The Maine Radiation Control Program will confirm the information as it comes in. There were no fatalities or injuries reported. "'A' Pulp Mill contains six gauges, 'B' Pulp Mill contains three gauges, and the Power Plant/Boiler contains five gauges. There could be from three to six gauges involved in the explosion, depending on which building exploded. "The Maine Radiation Control Program has not been notified by the mill. This report is the first written notification to NMED." Maine Event Report ID No.: ME 20-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2020-04-23
54668 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2020-04-14 13:15 | 2020-04-15 10:12 | 2020-04-15 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE EVENT OF Y-90 SIRTEX The following is a summary of an email received from the Kentucky Department of Radiation: At the University of Louisville Hospital on April 14, 2020, a patient received two doses (each dose was 0.4 GBq) of Y-90 Sirtex. The first dose was given at 1130 EDT and the second dose started at 1315 EDT. The second dose was started to be administered when a problem developed. While pushing saline into the dose V-vial, pressure built and vented out the top of the vial rather than pushing the spheres via the tubing to the patent as normal. Liquid, and presumably spheres, vented either from the side of the septum or around the needle at this time which is unknown. The administration box contained the leakage and prevented wider contamination. The second dose was not delivered to the patient so the patient received 0.4 GBq of a planned 0.8 GBq treatment. The manufacturer was contacted and the administration was stopped. Most of the intended dose remained in the plexiglass box that is used for shielding during administration. To prevent any contamination everything was kept and confined to the box. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2020-04-23
54667 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-04-09 | 2020-04-15 09:20 | 2020-04-15 | AGREEMENT STATE REPORT - DOSE NOT DELIVERED TO THE CORRECT LOCATION DURING BRACHYTHERAPY TREATMENT The following was received from the state of Texas via email and by telephone: "On April 10, 2020, the licensee reported to the Agency [Texas Department of State Health Services] that it had an event on April 9, 2020, involving a Novoste device in which the source train had not advanced to the designated treatment site during two attempts to deliver intravascular brachytherapy to a patient. It was unclear if the source train had actually entered the patient and the Agency requested confirmation and more information. On April 14, 2020, the licensee reported back to the Agency confirming that the source train had stopped moving after it had entered the patient. During the first attempt, the source train of 16 Strontium-90 sources in the Novoste device failed to go to the expected treatment position and instead got stuck in the beta-rail catheter proximally to the treatment area for 6 minutes 54 seconds. The device was checked and a second attempt was made during which the source got stuck in the beta-rail catheter proximally to the desired treatment area for 3 minutes 41 seconds. The source train was stuck at different positions in the catheter for the two attempts and each time the physicians worked with the catheter to try and get the source train to move to the treatment site. Doses calculated for each of the locations: first location = 26.2 Gy at 2 mm; second location = 14.2 Gy at 2 mm. The licensee was able to fully retract the source into the device each time. The vendor is expected onsite next week to check the device and investigate the cause. The licensee has suspended this particular treatment program indefinitely pending identification of cause. "Device Information: Novoste device SN: 89670 Source train SN: ZA925 Active source train length: 40 mm Number of Sr-90 sources: 16 Total activity: 2 GBq calibrated on 8/16/2002 "Treatment Information: Vessel description: RCA Vessel diameter: 4 mm Lesion length: 30 mm Radiation dose: 23 Gy Dwell time: 5 minutes and 57 seconds "Dose to staff was negligible since the source train was inside the patient. Effects to the patient, if any, as a result of this event were not reported with this initial information. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident Number: I-9760 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-04-23
54666 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2020-04-14 16:45 | 2020-04-14 23:36 | 2020-04-14 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "On April 14, 2020 at 1645 CDT, the Control Room Emergency Ventilation Air Conditioning (CREV AC) system was declared inoperable when the electrical feed breaker to the Refrigeration Compressor Unit (RCU) was found in a tripped condition. As a result, both units entered Technical Specification 3.7.5 Condition A. Investigation is in progress to determine the cause and corrective actions of the RCU feed breaker trip. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident." | 100 | 15 | 0 | 100 | 15 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | Accident Mitigation |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | Non Emergency | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-04-14
54665 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-04-14 | 2020-04-14 17:29 | 2020-04-14 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via E-mail: 21 tritium exit signs, each containing 9.21 Ci, are unaccounted for. There has been no response for annual general license registrations since 2015. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-22
54664 | 0 | SCHULZ ELECTRIC |  |  |  |  | 2020-03-12 | 2020-04-14 07:55 | 2020-04-14 | PART 21 NOTIFICATION - MOTOR BEARING OIL RESERVOIR RECOATING The following is a summary of information obtained from Schulz Electric via email report: During the time period of January 2014 through November 2015, Schulz Electric performed recoating on several vertical motor endbell bearing oil reservoirs. In November 2015, one of Schulz Electric's nuclear customers identified an issue with the adherence of the coatings. In January 2016, the same customer reported another motor which had indicated coating adherence issues. The lack of adequate adherence root cause was determined to be a contamination that was introduced to the oil reservoir surface through the use of a chemical chelating agent to remove rust from the endbells after cleaning. On March 12, 2020 the same customer contacted Schulz Electric again to identify that two more motors had been pulled from service for standard overhaul and the bearing oil reservoirs for both motors had degraded coatings as well. As such, Schulz Electric performed an extent of condition investigation and determined that there were additional customers for which Schulz Electric provided the bearing oil reservoir recoating. The loss of adhesion and flaking exposes the bearing oil reservoir to oil and allows oil migration into the base metal. Over time the safety related motors could degrade from the foreign material (flaking) concerns. The licensees affected are Hope Creek, North Anna, Hatch, Farley, Vogtle, Grand Gulf, and Columbia. Point of Contact: Charles Eldredge, Quality Assurance Manager at Schulz Electric, 30 Gando Drive, New Haven, CT 06513, Office Number (203) 859-7413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Defects And Noncompliance | [9 empty] | Non Emergency | 1 | CT | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-04-14
54663 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2020-04-13 15:50 | 2020-04-13 19:33 | 2020-04-13 | AUTOMATIC TRIP DUE TO LOW CONDENSER VACUUM "At 1550 EDT on 4/13/2020, with Millstone Power Station Unit 3 operating at approximately 82 percent reactor power, an automatic reactor trip occurred following a turbine trip due to low condenser vacuum caused by the trip of multiple circulating water pumps. Due to the loss of the circulating water pumps, decay heat removal was established by the steam generator atmospheric dump valves. All other systems responded as expected to the trip. "Auxiliary feedwater actuated automatically as expected following the trip due to low-low levels in the steam generators. "There was no risk to the public. There was no impact to Millstone Unit 2. "The Senior Resident Inspector has been informed. "This event is being reported as a four hour report under 10 CFR 50.72(b)(2)(iv)(B) as a condition that resulted in actuation of the reactor protection system while the reactor was critical, and as an eight hour report under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(3)(iv)(B) for actuation of the auxiliary feedwater system." The licensee also notified the state of Connecticut, the Connecticut Department of Energy and Environmental Protection, and the city of Waterford. | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | -1 | N | N | A/R | Power Reactor | Rps Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode3: Power Operation; FMode3: Hot Standby | Non Emergency | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-04-13
54662 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2020-03-31 | 2020-04-13 12:21 | 2020-04-13 | AGREEMENT STATE REPORT - LOSS OF IODINE-125 SEED The following was received from the state of Georgia via email: "An Iodine-125 seed [assayed at 69 microCuries on March 24, 2020 (Best Model 10172-11, Double wall titanium encapsulated, Serial Number: 49802A20)] used for breast lesion localization was shipped within a tissue specimen from Piedmont Fayette Hospital to Piedmont Atlanta and then lost into the ordinary solid waste stream, rather than being recovered and placed in decay-in-storage at Piedmont Fayette, as is the standard procedure. "The seed was implanted in a patient with a breast lesion at Piedmont Fayette on March 24, 2020. The lesion containing the seed was successfully removed in surgery and sent to the pathology lab on March 30, 2020. The presence of the seed in the specimen was verified in pathology by Neoprobe measurement. There was no pathology physician assistant present that day and the pathologist was not notified. A lab staff member arranged for all specimens to be shipped to Piedmont Atlanta. The specimens, including the one containing the seed, were shipped by MedSpeed courier service that same day. At the Atlanta campus, the specimen with the seed was processed by the normal procedure on April 1, 2020. The histotechnologist there removed what he thought was a marker or a clip and discarded it in the regular waste bin. The waste containing the seed was removed from the Atlanta campus [in a bag of solid waste] and transported to the [Pine Ridge Regional Landfill] by the waste disposal company's normal procedure on or around April 2, 2020. "[The Radiation Safety Officer (RSO)] was notified by phone on April 3, 2020 and searches of all relevant areas at Piedmont Atlanta were performed by staff using a GM survey meter with pancake probe as well as with a Sodium Iodide scintillator probe that day. No evidence of radiation or the seed was found in any location. "The proper course of action that should have been taken in order to prevent this situation is as follows: The pathologist at Fayette should have been notified that there was a specimen with a radioactive seed. The pathologist would have removed the seed and the pathology staff would have contacted Nuclear Medicine to retrieve the seed and place it in decay-in-storage. Seeds should not leave the Fayette Campus. "In [the RSO's] estimation, it is unlikely that any occupationally exposed worker or member of the public received any significant exposure or exceeded any dose limit. "All staff in pathology have been educated on the circumstances that led to this incident. The procedure has been updated to clarify what actions should be taken if a specimen with a seed arrives in pathology when no pathology physician assistant is present. Knowledge of this procedure has been added to the competency checklist for pathology employees." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-04-21
54661 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2020-04-10 21:25 | 2020-04-11 01:03 | 2020-04-11 | MANUAL REACTOR TRIP "At 2125 EDT on April 10, 2020, with Unit 3 in Mode 1 at approximately 32 percent power, the reactor was manually tripped due to a tube leak in the 3F1 feedwater heater. The trip occurred during a planned shutdown for a refueling outage. "The trip was not complicated, with all systems responding normally post-trip. Decay heat is being removed by discharging steam to the main condenser using the turbine bypass valves. Units 1 and 2 were not affected. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | Non Emergency | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-04-11
54660 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2020-04-09 14:32 | 2020-04-10 17:30 | 2020-04-10 | ABNORMAL OCCURRENCE "On 4/9/20, at 1432 CDT, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to the failure of the geared rotary limit switch assembly to move with corresponding regulating blade drive mechanism movement. This email is a required notification per MURR Technical Specification (TS) 6.6.c(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1, had occurred. MURR was not in compliance with one (1) Limiting Conditions of Operations (LCO). TS 3.2.f states, 'The reactor shall not be operated unless the following rod run-in functions are operable.' Specifically, the rod run-in function that occurs when regulating blade position is less than or equal to 10 percent withdrawn was not operable as required by TS 3.2.f.8. "The regulating blade drive mechanism was repaired, post-maintenance operability testing was conducted satisfactorily, and permission from the Reactor Facility Director was obtained prior to the reactor returning to operation later on 4/9/20. Currently, MURR is at 10 MW. A detailed event report will follow within 14 days as required by MURR TS 6.6.c(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | Non Emergency | 0 | MO | NPR | [5 empty] | 0 | 2020-04-10
54659 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2020-04-09 | 2020-04-10 15:20 | 2020-04-10 | AGREEMENT STATE REPORT - LOST GAUGE The following is a summary received from the state of California via email: On 04/09/20, the California Office of Emergency Services (OES) contacted the Radiologic Health Branch (RHB) to report a notification made by a California licensee regarding a lost hydro probe. The gauge involved is a CPN Model 503DR, S/N H380104084 hydro probe containing 50 mCi of Am-241. The report stated that the field user placed the probe into its case without securing its latches and locks and drove off to the next field site. It is believed that the probe had fallen out of the truck somewhere on Crows Landing Road between Carpenter Road and Ehrlich Road. The RSO [Radiation Safety Officer] had notified the California Highway Patrol (CHP) and the local Fire Department of the incident. Repeated attempts made by the RSO, his staff and CHP to locate the gauge were unsuccessful. The RSO will be posting a reward on social media for the safe return of the gauge. The RHB will be following up on this investigation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2020-04-20
54658 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2020-04-09 13:42 | 2020-04-10 14:30 | 2020-04-10 | AGREEMENT STATE REPORT - STUCK SHUTTER The following is a summary received from the state of Mississippi via phone: The licensee notified the state that during a routine check of an Ohmart gauge (s/n: 1169GK), the shutter would not close. The gauge contains a 10 mCi Cs-137 source (source holder: SHF-1). It is located over a chemical bin and the normal shutter position is open, so there is no additional exposure to employees. An authorized company is scheduled to remove and replace the gauge with an identical model. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2020-04-20
54657 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2020-04-10 03:00 | 2020-04-10 10:58 | 2020-04-10 | HIGH PRESSURE CORE INJECTION SYSTEM DECLARED INOPERABLE "On April 10, 2020, at 0300 [EDT], an oil leak from 23PCV-12, HPCI [High Pressure Core Injection] Trip System Pressure Control Valve (PCV), resulted in the system being declared inoperable. This condition is being reported as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident per 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-04-10
54656 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-18 | 2020-04-09 16:17 | 2020-04-09 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following is a summary of information received from the State of Colorado via E-mail: The licensee is unable to locate a tritium exit sign with an activity of 7.5 Ci. The exit sign was determined to be missing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-17
54655 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-28 | 2020-04-09 10:50 | 2020-04-09 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received via E-mail: One tritium exit sign containing 7.5 Ci was unaccounted for after the construction of a new clubhouse was completed. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-17
54654 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2020-04-07 | 2020-04-09 09:21 | 2020-04-09 | AGREEMENT STATE REPORT - IRRADIATOR APERTURE FAILED TO CLOSE The following information was received via E-mail: "The aperture electronic opening and closing mechanism malfunctioned on a J.L. Shepard Mark I series irradiator while the aperture was open. There was a smell of burning wires and visible smoke. The analysts cut power to the unit and notified department management. Utilizing portable shielding, and following ALARA principles, the attenuator of the device was able to be closed, which significantly reduced dose rates. Currently, the aperture is stuck partially open and the attenuator is closed. At 1.5 meters from the point of highest dose, the rate is approximately 10 mR/hr. Both analysts were wearing Mirion Instadose dosimeters and the measured dose to both dosimeters was less than the minimum read amount of 1 mrem. "The irradiator is located in a shielded calibration room located in the waste building. There is no dose rate above background in any area, accessible by either non-radiation workers or members of the public, around the building where the calibration room is located. The area has been securely locked, the door alarm is activated, and there are signs placed to remind everyone to not use the device. "Utah Department of Environmental Quality, Division of Waste Management and Radiation Control personnel were notified of the incident via normal work E-mail after the conclusion of the business of the day on April 8, 2020. The notification was not read until the morning of April 9, 2020 when normal business resumed and was then assigned to appropriate staff. "The device manufacturer has been contacted to determine repair options." Utah Event Report ID No.: UT 200004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2020-04-17
54653 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2020-04-08 01:00 | 2020-04-09 09:35 | 2020-04-09 | RESEARCH AND TEST REACTOR FORCED SHUTDOWN DUE TO FAILURE OF REGULATING BLADE DRIVE MECHANISM "On 4/8/20 at 0100 CDT, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to a failure of the regulating blade drive mechanism to move the regulating blade during reactor operation. This email is a required notification per MURR Technical Specification (TS) 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1, had occurred. Specifically, MURR was not in compliance with all Limiting Conditions for Operations (LCOs). MURR was not in compliance with two (2) LCOs: 1. TS 3.2.a states, 'All control blades, including the regulating blade, shall be operable during reactor operation,' and 2. TS 3.2.f states, 'The reactor shall not be operated unless the following rod run-in functions are operable.' Specifically, the rod run-in function that occurs when the regulating blade position is less than or equal to 10 percent withdrawn was not operable as TS 3.2.f.8 requires. "The regulating blade drive mechanism was repaired, post-maintenance operability testing was conducted on the regulating blade, and permission from the Reactor Facility Director was obtained prior to the reactor returning to operation later on 4/8/20. Currently, MURR is at 10 MW. A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | Non Emergency | 0 | MO | NPR | [5 empty] | 0 | 2020-04-09
54652 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2020-04-09 01:00 | 2020-04-09 03:37 | 2020-04-09 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE "On April 9, 2020 at 0100 EDT, while performing a containment walkdown due to a small increased Reactor Coolant System (RCS) unidentified leakage, a leak was identified on the 'A' Reactor Coolant Pump (RCP) seal injection piping. The source of the leakage cannot be isolated and is considered RCS pressure boundary leakage. At that time, Condition B of Technical Specification (TS) LCO 3.4.13, 'RCS Operational Leakage' was entered due to pressure boundary leakage. TS 3.4.4 'RCS Loops - Mode 1 and 2' and Technical Requirement (TR) 3.4.6 'ASME Code Class 1, 2, and 3 Components' are also applicable. Unit 2 is projected to be taken to Mode 5 for repairs. "This event is reportable in accordance with 10 CFR 50.72(b)(2) for 'Initiation of plant shutdown required by Technical Specifications' and 10 CFR 50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principle safety barriers, being seriously degraded.'" The licensee notified the NRC Resident Inspector. There is no effect on Unit 1 | 0 | 35 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | Non Emergency | 2 | VA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2020-04-09
54651 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2020-04-08 09:45 | 2020-04-08 17:23 | 2020-04-08 | LOSS OF TECHNICAL SUPPORT CENTER FUNCTIONALITY "On April 8, 2020 at 0945 EDT, a condition impacting functionality of the Technical Support Center (TSC) Ventilation System was discovered. The issue involved a loss of TSC habitability due to failure of outside air intake fans. These fans were returned to service at 1237 EDT and the TSC is currently functional. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the condition affects the functionality of an emergency response facility. "This condition does not affect the health and safety of the public or plant personnel. The NRC Resident Inspectors have been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | Non Emergency | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-04-08
54650 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2020-04-08 08:42 | 2020-04-08 17:03 | 2020-04-08 | FITNESS-FOR-DUTY REPORT - LICENSED SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | Non Emergency | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2020-04-08
54649 | 0 | TILDEN MINING CO. |  |  |  |  | 2020-04-07 14:09 | 2020-04-08 11:25 | 2020-04-08 | STUCK SHUTTER The following is a summary of the report received from the licensee: On 4/7/2020 a trained technician was in the process of performing the bi-annual inventory/shutter checks when he reported that an Ohmart gauge (Model Number ED-6, Serial Number 65902, 100 mCi, Cs-137) located on 9B DTU (Deslime Thickener U/Flow) in the Deslime basement had a frozen shutter mechanism, rendering the shutter non-operable. The technician notified the Radiation Safety Officer who then instructed the technician to replace the gauge with the stuck shutter with a spare gauge. However, the replacement will not take place until the line it is on goes down for repair (estimated May 1, 2020). If the line goes down prior to this time, the licensee will replace the gauge at that time. The licensee noted that they have had events similar to this in the past and have not had an exposure to any individuals. The licensee additionally noted that in the event of an emergency, the gauge will be removed, placed on a piece of lead and brought into storage. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | Non Emergency | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-04-16
54648 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-31 | 2020-04-07 18:43 | 2020-04-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following summary was received from the State of Colorado via E-mail: The licensee is unable to locate two tritium exit signs with an activity of 10 Ci each. The exit signs were apparently sold, and there was no response from the new owner. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-15
54647 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-01-24 | 2020-04-07 17:55 | 2020-04-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following summary was received from the State of Colorado via E-mail: The licensee is unable to locate two tritium exit signs with an activity of 11.5 Ci each. The site is a rental property. After the occupants moved out the property owner could not account for the exit signs. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-15
54646 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-05-16 | 2020-04-07 14:36 | 2020-04-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following summary was received from the State of Colorado via E-mail: The licensee is unable to locate a tritium exit sign with an activity of 9.21 Ci. The exit sign may have been removed during renovation. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-15
54645 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-09-12 | 2020-04-07 13:46 | 2020-04-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following summary was received from the State of Colorado via E-mail: The licensee is unable to locate two tritium exit signs with an activity of 7.5 Ci each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-15
54644 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-06-09 | 2020-04-07 12:39 | 2020-04-07 | AGREEMENT STATE REPORT - STUCK SHUTTER The following is a summary of information provided by the State of Georgia via E-mail: Licensee personnel were performing three year wipe tests when one gauge was found to have a stuck shutter. The gauge contained a Cesium-137 source (Device: Model D14400S, S/N SE4029, Source; 250 milliCuries; S/N SNC250066). The gauge was not in service at the time of the wipe test. The licensee is planning on selling the gauge and having it removed from the premises. The company buying the gauge is aware of the stuck shutter and will fix the shutter before removing it from the licensee's premises. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-04-15
54643 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-04-06 | 2020-04-06 15:52 | 2020-04-23 | AGREEMENT STATE REPORT - LOST MATERIAL IN TRANSIT The following is summarized from an e-mail received from the Commonwealth of Massachusetts: The licensee reported on 4/6/20 that three UN2915 White I label packages, shipped from Germany via common carrier, each containing 21.14 Ci Sulfur-35, did not arrive on 3/29/20 as expected. Upon inquiry on 3/31/20, the common carrier informed the licensee that the packages arrived at JFK Airport, NY, and had not yet been forwarded. The common carrier informed the licensee on 4/6/20 that the three packages could not be located within its system, all flights were cancelled from JFK to Boston due to the COVID-19 situation, and affected freight would be forwarded via ground. The licensee continues to work with the common carrier to locate the packages. There is no significant public health and safety concern due to the package radiation levels being at background. * * * UPDATE ON 4/9/2020 AT 1410 EDT FROM ANTHONY CARPENITO TO JEFFREY WHITED * * * The following was received from the Commonwealth of Massachusetts via email: "The licensee (PerkinElmer) on 4/9/2020 reported to this Agency [the Massachusetts Radiation Control Program] that three packages previously reported as missing were found in [the common] carrier's warehouse at JFK Airport in NY. The licensee stated that the packages were reportedly intact, unopened and undamaged. The licensee stated that the packages are expected to be ground transported to licensee in Boston for arrival on 4/10/2020. The licensee stated that a comprehensive incoming package survey will be performed on packages upon arrival at licensee facility. This Agency considers this event to still be OPEN until licensee confirmation of package arrival in regulatory-acceptable condition." Notified R1DO (Lilliendahl), NMSS Event Notifications, and ILTAB via email. * * * UPDATE ON 4/10/2020 AT 1635 EDT FROM ANTHONY CARPENITO TO OSSY FONT * * * The following was received from the Commonwealth of Massachusetts via email: "The licensee (PerkinElmer) on 4/10/2020 reported to this Agency that three subject packages were received at the licensee's facility on the afternoon of 4/10/20. The licensee performed an incoming package survey and determined the outside of the packages were not radioactively contaminated, there was no physical damage to the packages, and the inner packaging and contents remained intact. The Agency expects this event to remain OPEN until all details, including action docket numbers, are compiled and relevant documentation is completed." Notified R1DO (Lilliendahl), NMSS Event Notifications, and ILTAB via email. * * * UPDATE ON 4/23/2020 AT 1435 EDT FROM ANTHONY CARPENITO TO CATY NOLAN * * * The following was received from the Commonwealth of Massachusetts via email: "Carrier corrective action includes retraining of employees. Agency considers this event to be CLOSED." Massachusetts Event Number: 16-4134. NMED Item Number: 200171 Notified R1DO (Arner), NMSS Event Notifications, and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-04-14
54642 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2020-04-06 | 2020-04-06 15:28 | 2020-04-06 | AGREEMENT STATE REPORT - IMPROPER CONTROL OF A SEALED SOURCE The following information is a summary received from the state of North Dakota via telephone: On April 5, 2020, one of the licensee's sealed sources was temporarily in the possession of a non-authorized user. One of the owners, who is not an authorized user, took possession of four of the company's radiography vehicles and a sealed source was still in one of the vehicles. The source was subsequently retrieved, verified not to have been tampered with, and is back in storage. The source contains 88 Ci of Ir-192. North Dakota has notified their R4 Agreement State Officer (Erickson). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2020-04-14
54641 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-04-03 | 2020-04-06 14:09 | 2020-04-07 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following was received from the State of Pennsylvania via E-mail: "The [PA DEP Bureau of Radiation Protection] Department received notification from a licensee on April 3, 2020 of a medical event involving Y-90 TheraSphere microspheres. The licensee believes a patient undergoing a multiple lobe injection of the liver received only 62.7 percent of the prescribed dose in one of the lobes. The second lobe is believed to have received the correct dose. The DEP is currently in contact with the licensee and will update this event as soon as more information is provided. "The Department will perform a reactive inspection as soon as possible." Pennsylvania Event Report ID No.: PA200007 * * * UPDATE ON 04/07/2020 AT 1353 EDT FROM JOHN CHIPPO TO JEFFREY WHITED * * * The following was received from the State of Pennsylvania via E-mail: "The patient was prescribed TheraSphere Y-90 Microspheres at 2.47 GBq total with 2.25 Gbq prescribed to the liver because of 9.1 percent lung shunt. The licensee reports total dose 1.536 GBq, and 1.4 GBq to liver. Ultimately only 62.7 percent (75.3 Gy) of the planned dose was able to be administered to segment 6 of the liver. While attempting to administer the Y-90 dose to treat a lesion in Segment 6 of the liver there was significant resistance to flow. The AU evaluated the microcatheter system to ensure that there were no kinks along the catheter course external to the patient or visualized internally under fluoroscopy. The licensee believes the issue came from blockage at or before the 'E' site on the labeled tubing of the administration set, given that when it was disconnected from the microcatheter at that location, they were able to successfully flush the catheter. The patient then had a subsequent segment 7 segmentectomy using tubing from a box set from a different lot number without incident. No adverse effects to the patient are anticipated and the patient and referring physician were notified the day of the event." Notified R1DO (Lilliendahl) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | Non Emergency | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-04-14
54640 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2020-04-04 09:30 | 2020-04-04 18:43 | 2020-04-04 | OFFSITE NOTIFICATION At approximately 0930 EDT on April 4, 2020, the New Hanover County Deputy Fire Marshall was notified per state code requirements that the fire alarm system and accompanying fire pumps encompassing the fuel manufacturing operation (FMO) were placed on backup power due to a planned power outage. Additional compensatory measures were enacted. Power was restored at approximately 1800 EDT on April 4, 2020. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-04-13
54639 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2020-04-04 01:15 | 2020-04-04 05:31 | 2020-04-04 | AUTOMATIC REACTOR TRIP "At 0114 [CDT] on April 04, 2020 the plant was in Mode 1 at 100 percent power when a Digital Feedwater Trouble alarm was received unexpectedly. Operators identified a full feedwater demand signal and lowering level in the 'C' Steam Generator. At 0115 a Reactor Trip signal for Low Steam Generator Level was received. All systems responded as expected. A Feedwater Isolation signal was received due to the reactor trip with RCS average temperature less than 564 degrees Fahrenheit. Auxiliary Feedwater started on a valid actuation signal to restore and maintain Steam Generator levels. The Plant is being maintained stable in Mode 3 with no complications. "The NRC Resident Inspector has been notified of the Reactor Trip." All control rods fully inserted from the reactor trip signal, and decay heat is being removed via the Auxiliary Feedwater and Steam Dump Systems. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-04-04
54638 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-28 | 2020-04-03 16:59 | 2020-04-03 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following summary was received from the state of Colorado via email: The licensee is unable to locate three tritium exit signs with an activity of 6 Ci each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-13
54637 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-05 | 2020-04-03 16:20 | 2020-04-03 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following summary was received from the state of Colorado via email: The licensee is unable to locate a tritium exit sign with an activity of 11.5 Ci. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-13
54636 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-05-10 | 2020-04-03 13:46 | 2020-04-03 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following summary was received from the state of Colorado via email: The licensee is unable to locate 16 tritium exit signs. Management claims the signs are not on their property. Each sign has an activity of 6 Ci. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-13
54635 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-14 | 2020-04-03 11:25 | 2020-04-03 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following summary was received from the state of Colorado via email: The licensee had two tritium exit signs, containing 6.2 Ci each, removed and replaced with non-radioactive signs. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-13
54634 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-01-03 | 2020-04-02 17:19 | 2020-04-02 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the state of Colorado via email: "Seventy-five tritium exit signs, containing 6.0 Curies each, was determined unaccounted for and lost during a walk down of the property. "Initial Date Reported: 10/29/19 "Final Decision Material Lost Date: 1/3/20" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-10
54633 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2020-04-02 12:30 | 2020-04-02 16:11 | 2020-04-02 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following is a synopsis of information received via e-mail: On April 2, 2020, at 1230 EDT, a portable density gauge was damaged by a roller at a construction site. The density gauge is a Troxler model 3430, serial number 27555 containing 9 milliCuries of cesium-137 and 44 milliCuries of americium-241/beryllium. The source was not damaged and there was no exposure or health effects to the public. An investigation is ongoing. New Jersey event report no. 749233. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2020-04-10
54632 | 0 | WATERFORD | 3 |  |  | [3] CE | 2020-04-01 10:02 | 2020-04-01 21:05 | 2020-04-01 | FITNESS FOR DUTY (FFD) POLICY VIOLATION On April 1, 2020, a licensed senior reactor operator, returning from a leave of absence, disclosed a Fitness-For-Duty policy violation, which occurred on July 29, 2019. The individual's site access has been removed. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2020-04-01
54631 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2020-04-01 16:25 | 2020-04-01 19:11 | 2020-04-01 | AUTOMATIC REACTOR TRIP DUE TO CIRCUIT FAULT On April 1, 2020, at 1625 EDT, Milllstone Unit 3 was in Mode 1, at 100 percent power, when an automatic reactor trip occurred following a main generator trip. The cause was due to a circuit fault between the main generator breaker and the offsite switchyard. The reactor trip was not complicated and the reactor remains stable in Mode 3. One of the two offsite electrical sources remain inoperable with an investigation of the circuit fault underway. Decay heat removal is maintained by the main condenser. There was no effect on Unit 2. The NRC Resident Inspector was notified. The licensee notified State and local government agencies. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-04-01
54630 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2020-04-01 12:02 | 2020-04-01 19:07 | 2020-04-01 | FITNESS-FOR-DUTY REPORT - LICENSED OPERATOR CONFIRMED POSITIVE FOR ALCOHOL A licensed operator had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2020-04-01
54629 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-07-01 | 2020-04-01 14:03 | 2020-04-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the State of Colorado via email: One tritium exit sign, containing 6.2 Curies, was determined to be lost after not being found on the property by new management. Initial Date Reported: 7/1/2019 Final Decision Material Lost Date: 7/1/2019 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-09
54628 | 0 | IDAHO STATE UNIVERSITY |  |  |  | 0.005 KW AGN-201M #103 | 2020-03-31 17:50 | 2020-04-01 14:40 | 2020-04-03 | NOTIFICATION OF A NON-EMERGENCY UNUSUAL EVENT DUE TO A SEISMIC EVENT The following is a summary of information received from the Idaho State University Reactor Facility via phone conversation: At 1750 MDT on March 31, 2020, the licensee declared a Notification of Unusual Event due to seismic activity felt from an earthquake originating in southern Idaho. The facility was closed due to the suspension of all campus activities set forth by the pandemic response. The reactor was shutdown at the time of the earthquake and is being constantly monitored by the campus public safety office. Inspections of the facility will be performed. The licensee notified the NRR Project Manager (Yin). * * * UPDATE ON 4/3/20 AT 1532 EDT FROM MARY LOU DUNZIK-GOUGAR TO ANDREW WAUGH * * * The licensee has finished conducting visual inspections and monitoring activity levels throughout the facility. All indications came back normal. The licensee also verified the seismic indicator was still in its proper position. Notified NRR PM (Yin) and NPR (Reed). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | ID | NPR | [5 empty] | 0 | 2020-04-01
54627 | 0 | WASHINGTON STATE UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2020-03-31 16:55 | 2020-04-01 14:03 | 2020-04-01 | NOTIFICATION OF A NON-EMERGENCY UNUSUAL EVENT DUE TO A SEISMIC EVENT The following is a summary of information received from the Washington State University Reactor Facility via phone conversation: At 1655 PDT on March 31, 2020, the licensee declared a Notification of Unusual Event due to seismic activity felt from an earthquake originating in southern Idaho. Operators felt the seismic activity and entered their emergency planning procedures to inspect for any damages to the reactor facility. There were no injured personnel and the reactor was shutdown at the time of the earthquake. Initial assessments revealed no damages or effects to the reactor or to the facility. Additional walk downs are in progress. The licensee notified the NRR Project Manager (Hardesty). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | WA | NPR | [5 empty] | 0 | 2020-04-01
54626 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-02-24 | 2020-03-31 17:12 | 2020-03-31 | AGREEMENT STATE REPORT - LOST STATIC CONTROL DEVICE The following was received from the State of Texas via email: "On March 31, 2020, the Texas Department of State Health Services (Agency) received a letter that had been originally sent to the Texas Commission on Environmental Quality, received March 3, 2020, which was forwarded via email. The letter was reporting a lost static control device: NRD Neutralizer model P-2021-Z705, SN: A2LP525, containing 10 milliCuries of polonium-210. This is a general license device. It was last used on February 20, 2020, and then replaced. On February 25, 2020, [employees at Gemini Sign Products] realized the box containing the device (to be shipped back to manufacturer) was missing. It was determined that on February 24, 2020, the device and its associated paperwork, which was in a box in an office awaiting paperwork completion/packing for transit back to the manufacturer, was mistaken by a custodian for waste, and it was thrown away in an outdoor dumpster. The dumpster was searched, but the waste had already been picked up and they learned from the waste company that the contents of that load were already at the landfill and buried. The report included the company's corrective actions: reminders to staff about the equipment and the regulations associated with it and new policy and procedure for changing out the devices in the future. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident Number: I-9757 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-04-08
54625 | 0 | UNIV OF UTAH |  |  |  | 100 KW TRIGA MARK I | 2020-03-31 12:17 | 2020-03-31 15:44 | 2020-03-31 | TECHNICAL SPECIFICATION NON-COMPLIANCE The following is a summary of information received from the University of Utah Reactor Facility via email: At 1217 MDT, on 3/31/2020, during a test of reactor systems, operators discovered that the safety control rod would not drop as expected after magnet power was secured. The safety control rod was manually driven from the 100 percent to 98 percent withdraw position, where it then dropped on its own to the fully inserted position. The reactor was shutdown during safety control rod testing, with the shim and regulating rod fully inserted. As a result, the licensee was not in compliance with Technical Specification 3.2.1.2, which requires the scram time to not exceed two seconds. The reactor will remain shutdown until the rod is inspected and repaired. The licensee notified the NRR Project Manager (Yin). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | UT | NPR | [5 empty] | 0 | 2020-03-31
54624 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-05-30 | 2020-03-30 17:40 | 2020-03-30 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was summarized from the email received from the state of Colorado: One tritium exit sign, containing 10.0 Curies, was determined lost after renovation. Initial Date Reported: 5/30/18 Final Decision Material Lost Date: 5/30/18 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-07
54623 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-03-27 | 2020-03-27 20:22 | 2020-03-27 | AGREEMENT STATE REPORT - UNDERDOSE OF PATIENT MEDICAL EVENT The following was received from the State of Texas via email: "On March 27, 2020, the licensee reported that at the completion of a procedure during which 26 milliCuries of Yttrium-90 Sirspheres were administered to a patient, the assay of the tubing, vial, catheter, etc., revealed that the patient had only received approximately 16 milliCuries of the administered dose. Approximately 10 milliCuries were still in the equipment. The authorized user determined this was not the result of vascular stasis. The licensee plans to hold the administration equipment for decay for approximately seven days at which time they will assay and inspect the equipment and attempt to determine the cause. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident Number: 9755 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-04-06
54622 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2020-03-05 | 2020-03-27 15:20 | 2020-03-27 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON DENSITY GAUGE The following is a synopsis of information provided by the Nebraska, Department of Health & Human Services, via phone notification: Licensee reported to the Nebraska Department of Health and Human Services on March, 24, 2020, that during their 6 month check of the shutter functionality on March 5, 2020, the shutter on a density gauge would not close all the way. The density gauge is an Ohmart/Vega Corporation model SH-F2 density gauge with a Cs-137 500 milliCurie source. The serial number for the gauge is 9103GK. The gauge is installed in a process system and provides no threat to personnel. The licensee has contacted the gauge manufacturer for repair. Nebraska report number NE20004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-04-06
54621 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2020-03-19 | 2020-03-27 15:18 | 2020-03-27 | PART 21 NOTIFICATION - TRANSDUCER DEFECT The following is a summary of information obtained from Palo Verde via email: During pre-installation testing, five Masoneilan Model transducers were identified as unable to be calibrated prior to installation. These transducers were received by the vendor as safety-related components and are used to provide remote control operation of the Atmospheric Dump Valves (ADVs). The ADVs provide a safety grade method for cooling the unit to Shutdown Cooling System entry conditions, should Palo Verde's preferred heat sink via the Steam Bypass Control System to the condenser and/or atmosphere not be available. The transducer receives a 4-20 mA signal and translates it to a 3-15 psi output to the ADV positioner. This is accomplished by varying the supply air from 23-30 psi down to the appropriate 3-15 psi signal. Palo Verde provided an Interim 10 CFR 21 Report for the five Masoneilan Model 8005N transducers, Part 21 log number 2019-36-00, ML 19323C971, which was submitted by Arizona Public Service (APS) Company on November 15, 2019. An evaluation of the transducers was completed on March 19, 2020. The evaluation concluded that the inability of the transducers to be calibrated represented a defect. The licensees affected are undetermined at this time. Palo Verde has been in communication with the vendor. The vendor has currently not provided an extent of condition. Point of Contact: Lorraine Weaver (602) 448-5915 | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2020-03-27
54620 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-02-02 | 2020-03-26 17:08 | 2020-03-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the state of Colorado via email: "Two tritium exit signs, containing 6.2 Curies each, was determined lost during annual inventory. "Initial Date Reported: 12/16/17 "Final Decision Material Lost Date: 2/2/18" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-03
54619 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-05-09 | 2020-03-26 15:29 | 2020-03-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the state of Colorado via email: "Two tritium exit signs, containing 6.0 Curies each, was determined lost after a change in management. "Initial Date Reported: 12/18/17 "Final Decision Material Lost Date: 5/9/18" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-03
54618 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-03-26 | 2020-03-26 14:25 | 2020-03-26 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENISTY GAUGE CASE The following was received via email: "[The licensee] notified the [Florida Bureau of Radiation Control] BRC that a Soil Moisture Density Gauge was 'bumped over' at a construction site in [Clearwater, FL] by a machine while in use during a standard count. [The licensee] claims there was no damage to the sources, only damage to the case. The area has been cordoned off, no information on site exclusion prior to the impact has been reported. The [Radiation Safety Officer] RSO has not returned phone calls at this time. The [Florida State Watch Office] FL SWO and [Department of Environmental Protection] DEP have contacted the BRC about this incident. An inspector from [the Florida western office] is requested at this time." Florida Incident Report Number: FL20-045 * * * UPDATE ON 03/26/2020 AT 1533 EDT FROM MARK SEIDENSTICKER TO CATY NOLAN * * * The following was received via phone call: The gauge was bumped and dragged approximately 10 feet at the construction site during a calibration. The source was retracted. There was no release or visible damage. Notified R4DO (Kellar) and NMSS Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-04-03
54617 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-07-01 | 2020-03-26 12:02 | 2020-03-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Colorado via email: "One tritium exit sign, containing 6.2 Curies, was determined lost after it was removed during renovation. "Initial Date Reported: 7/1/19 "Final Decision Material Lost Date: 7/1/19" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-03
54616 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-06-25 | 2020-03-26 10:46 | 2020-03-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Colorado via email: "A tritium exit sign, containing 7.09 Ci, was knocked off wall at the Boulder Rural Fire Dept. and assumed to have been discarded in the dumpster." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-03
54615 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-06-29 | 2020-03-26 10:13 | 2020-03-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the state of Colorado via email: "Two tritium exit signs, containing 11.4 Curies each was determined lost. "Initial Date Reported: 6/29/18 "Final Decision Material Lost Date: 6/29/18" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_we | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-03
54614 | -1 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-03-26 03:00 | 2020-03-26 10:45 | 2020-03-29 | DEGRADED CONDITION "On March 26, 2020, while McGuire Unit 2 was shut down for a scheduled refueling outage, the reactor vessel head penetrations were being examined in accordance with the in-service Inspection Program. Ultrasonic examinations identified a relevant indication in the Control Rod Drive Mechanism nozzle number 35 that did not meet the acceptance criteria under ASME, Section XI IWB-3600, 'Analytic Evaluation of Flaws.' Actions to address the relevant indication will be taken in accordance with the applicable codes, standards, and regulations. "This event is being reported as an eight-hour non-emergency notification per 10 CFR 50.72(b)(3)(ii)(A). "The relevant indication has no impact on the health and safety of the public or station employees. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 3/29/2020 AT 1700 EDT FROM TOM BERNARD TO BRIAN P. SMITH * * * "McGuire is retracting the eight hour non-emergency notification made on March 26, 2020, at 10:45 ET (EN#54614). A subsequent evaluation determined that the suspect indication identified during ultrasonic examination of Control Rod Drive Mechanism nozzle number 35 is not service induced nor representative of primary water stress corrosion cracking (PWSCC). The indication has been classified as "non-relevant" and is not reportable as a degraded condition. "The senior NRC Resident Inspection has been notified." Notified R2DO (Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2020-03-26
54613 | 0 | ALT & WITZIG ENGINEERING |  |  |  |  | 2020-03-26 | 2020-03-26 10:00 | 2020-03-26 | LOST AND FOUND DENSITY GAUGE On 3/26/2020, at 0730 CDT, a CPN density gauge (Model CPN Corp MC1-DR, S/N 60103007; 10 milliCuries of Cesium-137 and 50 mCi of Americium-241 source) was reported stolen out of a technician's vehicle and was recovered. The licensee notified the Indianapolis Police Department and the density gauge was recovered when a bystander found the case abandoned on the street. The licensee inspected and surveyed the properly secured density gauge and observed no damage or leakage. The licensee states there was no radiological impact to the public. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2020-04-03
54612 | 0 | SAN ONOFRE |  |  |  | ISFSI | 2020-03-25 20:00 | 2020-03-26 01:15 | 2020-03-26 | OFFSITE NOTIFICATION FOR SEWAGE RELEASE "On 3/25/2020, SONGS [San Onofre Nuclear Generating Station] made required formal notifications to the California Office of Emergency Services at 2107 PDT, the San Diego Regional Water Quality Review Board at 2123 PDT, the San Diego Department of Environmental Health (CUPA) [Certified Unified Program Agency] at 2104 PDT, the National Response Center (NRC) at 2115 PDT, and the San Diego Coast Guard at 2149 PDT, concerning an approximate 7,000 gallon release of partially treated sewage to the Pacific Ocean. "Both Sewage Treatment Plant effluent pumps were shut down and a state certified vendor is working to bring the treatment plant back to service." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE NOTIFICATION | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-03-26
54611 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2020-03-25 12:40 | 2020-03-25 15:28 | 2020-03-25 | MANUAL TRIP DUE TO LOSS OF REACTOR COOLANT PUMPS "At 1240 [EDT] on March 25, 2020, with the Unit in Mode 2 at approximately 0% [zero percent] power starting up from a refueling outage, the reactor was manually tripped due to a trip of two of four Reactor Coolant Pumps. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the main condenser. The cause of the Reactor Coolant Pump trips is under investigation. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-03-25
54610 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-02-13 | 2020-03-25 15:00 | 2020-03-25 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Colorado via email. "One tritium exit sign, containing 11.50 Ci, was determined lost. [The] tenant claims the exit sign was never delivered or installed. "Initial date reported: 2/13/20 "Final Decision Material Lost Date: 2/13/20" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-02
54609 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-12-30 | 2020-03-25 12:22 | 2020-03-25 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR The following was received from the state of Colorado via email. "One polonium-210 static eliminator, containing 0.01 Ci, was determined lost. [The] current owner believes [the] static eliminator belonged to [the] previous owner. "Initial date reported: 12/30/18 "Final Decision Material Lost Date: 12/30/18" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-02
54608 | 0 | PA DEPT OF ENVIRONMENTAL PROTECTION |  |  |  |  | 2020-03-13 | 2020-03-25 11:58 | 2020-03-25 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the Commonwealth of Pennsylvania via email: "The [Pennsylvania] Department [of Environmental Protection] received notification from a licensee on March 23, 2020 of the loss or theft of four tritium exit signs during shipment from the manufacturer/distributor in Canada to distributer/installer in [Winter Haven,] Florida. The tritium exit signs are model number 880-20-1-BK-BA-MB, 12.57 Curies each for a total of 50.28 Curies. The serial numbers are: H135434, H135435, H135436, H135437. The shipper believes the package was delivered on December 5, 2019, but the Florida installer didn't determine the material to be lost until March 13, 2020. An investigation with [the common carrier] has already begun to find the package. The [Department] will update this event as soon as more information is provided. "The Department will perform a reactive inspection as soon as possible." PA Event Report ID No: PA200006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-04-02
54607 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-03-25 00:56 | 2020-03-25 03:30 | 2020-03-25 | MANUAL TRIP DUE TO FAILURE OF A ROD CONTROL MOTOR GENERATOR "At 0056 EDTon March 25, 2020, with Unit 1 at 17 percent power during a unit power ascension, the reactor was manually tripped due to the failure of the 11 Rod Control Motor Generator caused by a malfunction of its associated Voltage Regulator. The trip was not complex, with all systems responding normally post-trip. An actuation of the Auxiliary Feedwater system occurred following the manual reactor trip as expected due to low level in the steam generators. The unit is stable in Mode 3. Decay heat is being removed by the Atmospheric Steam Dumps and Auxiliary Feedwater System. Salem Unit 2 was not affected. "Due to the actuation of the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B), This event is also being reported as an eight hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feedwater System. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident lnspector has been notified." | 0 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-03-25
54606 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-21 | 2020-03-24 17:25 | 2020-03-24 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following summary was received from the state of Colorado via email: The State is reporting four (4) lost tritium exit signs, containing 10 Ci each. The signs were not accounted for during annual registration. The licensee stated that the signs were never installed in the facility. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-01
54605 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-03-24 10:46 | 2020-03-24 17:15 | 2020-03-24 | SPECIFIED SYSTEM ACTUATION - AUTO START EMERGENCY DIESEL GENERATORS "At 1046 CDT on 3/24/2020, with Unit 1 defueled and Unit 2 in Mode 1 at 100 percent power, the South Texas Project (STP) South switchyard electrical bus was deenergized. This resulted in a loss of power to Standby Transformer 2 which was supplying power to the Engineered Safety Features (ESF) 4160v busses for Unit 1 A- and C-Trains, and Unit 2 B-Train. Emergency Diesel Generators (EDGs) 11, 13, and 22 automatically started in response to the undervoltage condition. "The cause for the loss of the South switchyard electrical bus was an error in relay testing in the switchyard. "This event is reportable under 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in the valid actuation of emergency AC electrical power systems (50.72(b)(3)(iv)(B)(8)) as well as the Unit 1 A- and C-Train and Unit 2 B-Train Reactor Containment Fan Coolers (50.72(b)(3)(iv)(B)(7)) and Unit 2 B-Train Auxiliary Feedwater pump (50.72(b)(3)(iv)(B)(6)). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2020-03-24
54604 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-19 | 2020-03-24 16:31 | 2020-03-24 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following summary was received from the state of Colorado via email: The State is reporting one lost tritium exit sign, containing 9.21 Ci. The sign was confirmed lost during a walkdown for annual registration. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-01
54603 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2020-03-24 12:05 | 2020-03-24 16:02 | 2020-03-24 | TECHNICAL SPECIFICATION-REQUIRED SHUTDOWN DUE TO UNIDENTIFIED LEAKAGE "At 1205 Eastern Daylight Time (EDT) on March 24, 2020, a Technical Specification-required shutdown was initiated on Unit 1 due to indication of a leak in the drywell. Technical Specification Action 3.4.4.A, Unidentified Reactor Coolant System (RCS) leakage increase not within limit, requires RCS leakage to be reduced to within limits within 8 hours. "It was expected that the leakage would not have been reduced to within limits within the required Technical Specification completion time; therefore, this event is being reported in accordance with 10 CFR 50.72(b)(2)(i). "Reactor water level reached low level 1 (LL1) following the reactor shutdown. The LL1 signal causes Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves), and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL1 isolations occurred as designed; the Group 8 valves were closed at the time of the event. Due to the valid Primary Containment Isolation System (PCIS) actuation, this event is also being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "Unit 2 is not affected by this event. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-03-24
54602 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-11-30 | 2020-03-24 09:11 | 2020-03-24 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following summary was received from the state of Colorado via email: Three tritium exit signs, containing 11.5 Ci each, were determined lost. They were apparently removed during a renovation in 2002. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-04-01
54601 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2020-03-03 | 2020-03-23 16:58 | 2020-03-23 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION (ABNORMAL OCCURRENCE) The following was received from the Rhode Island Department of Health (RIDOH; the Department) via email: "On March 4, 2020, the Department's staff at RIDOH, Radiation Control Program became aware of a medical event (ME) that occurred at the Rhode Island Hospital, Department of Radiation Oncology in Providence on March 3, 2020. The ME is reportable as per 10 CFR 35.3045(a)(1)(i)(A) and meets the criteria for an Abnormal Occurrence. "On March 3, 2020, a patient underwent Gamma Knife treatment of a left vestibular schwannoma. At the conclusion of the treatment it was discovered that the location of the anterior screws securing the patient's head in the treatment position had moved. Before the patient was moved from the treatment table, the patient's position was observed by the radiation oncologist, neurosurgeon, and medical physicist. It is unknown at this time what contributed to the event and how the screws securing the patient in the treatment position had shifted from the initial position. Based on information provided by the patient and other participants associated with this event, a delivered dose was estimated using the GammaPlan Treatment Planning System. The estimated delivery to the target coverage area (volume of tissue receiving dose) was 44 percent. The estimated dose to the target was 4 Gy (400 rad). An unintended dose to a region of the left temporal lobe within the brain was estimated to be 13.6 Gy (1,360 rad). On the day of the incident, the attending neurosurgeon spoke directly with the patient informing the patient that the stereotactic frame had disengaged from his head at some point midway through the treatment and resulted in an unclear radiation dose to the tumor. The patient was informed of the estimated dose and told of the licensee's plan to obtain a follow-up brain MRI within 1-2 weeks after treatment and approximately 3 months after treatment." The licensee is taking a number of corrective actions, including having the radiation therapist ensure that the patient understands that any movement of their head within the headframe is not anticipated and should be communicated immediately. Event Report ID No: RI2020-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2020-03-31
54600 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-20 | 2020-03-23 14:53 | 2020-03-23 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following summary was received from the state of Colorado via email: Four tritium exit signs, containing 7.5 Ci each, were determined lost, disposed of before the current manager took the management position. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-31
54599 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2020-03-23 10:13 | 2020-03-23 13:36 | 2020-03-23 | AUTOMATIC REACTOR TRIP "On March 23, 2020, at 1013 EDT, with Harris Nuclear Plant Unit 1 in Mode 1, at 100 percent power, an unplanned actuation of the reactor protection system occurred. This resulted in an automatic reactor trip. The trip occurred during the restoration of the auto-stop turbine trip function during a planned maintenance evolution. "All safety systems functioned as expected. Auxiliary Feedwater started as designed and was secured. Steam generator levels are being maintained by normal feedwater through the feedwater regulator bypass valves. Decay heat is being removed by using the condenser steam dump flow path. "Due to the unplanned Reactor Protection System actuation while critical and the expected Auxiliary Feedwater actuation, this event is being reported as a four hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and an eight hour, non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-03-23
54598 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-13 | 2020-03-23 11:30 | 2020-03-23 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following is a summary of information received from the state of Colorado via email: Two tritium exit signs (6.5 Ci each) were not found during a walk down of the facility. Management claims they were not received or installed. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-31
54597 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2020-03-22 12:55 | 2020-03-22 16:39 | 2020-03-22 | MANUAL REACTOR SCRAM "At 1255 EDT on March 22, 2020, with Unit 1 in Mode 2, stabilized at 2 percent power, coming out of a refueling outage, all 4 main turbine Bypass Valves (BPVs) opened unexpectedly. As a result, the main control room inserted a manual reactor scram. All control rods inserted as expected during the scram. "In accordance with plant procedures, the main control room closed all Main Steam Line Isolation Valves (MSIVs) to arrest the cooldown resulting from BPVs remaining open. The condensate system remained aligned for injection and pressure control was initially via main steam line drains. RHR [residual heat removal] shutdown cooling was placed in operation for decay heat removal and pressure control once the MSIVs were closed. "All systems responded as designed, with the exception of the BPVs. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." There was no impact to Unit 2. | 0 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-03-22
54596 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-03-21 16:44 | 2020-03-21 23:46 | 2020-03-22 | AUTOMATIC ACTUATION OF THE 1B EMERGENCY DIESEL GENERATOR "At 1644 EDT with Unit 1 in Mode 6 at 0 percent power, an actuation of the Unit 1 Bravo Train Emergency Diesel Generator system (EDG) occurred during Engineered Safety Feature Actuation System (ESFAS) testing. The reason for the EDG auto-start signal was a loss of voltage on the Bravo train safety related electrical bus due to the EDG output breaker opening. The EDG was already running at the time of the loss of voltage on the bus. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the EDG system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." There was no impact to Unit 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2020-03-22
54595 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2020-03-20 | 2020-03-20 18:30 | 2020-03-25 | AGREEMENT STATE REPORT - UNPLANNED DOSE TO AN ORGAN The following was received from the state of Wisconsin's Radiation Protection Section [the Department] via email: "On March 20, 2020, the [Wisconsin Radiation Protection Section] Department was notified by the licensee of a medical event which occurred the same day. The licensee was performing the first fraction of a vaginal cylinder treatment using a Varian VariSource iX high dose rate remote afterloader unit. Licensee staff had difficulty removing the cylinder post-treatment, and they determined that the cylinder had perforated the patient's tissue at some point following pre-treatment imaging. The licensee estimates the cylinder moved 3-4 cm from its original position. Dose reconstruction is ongoing, but is expected to exceed the 0.5 Sv threshold to the bowel. This is all the information available at this time. The Department will determine follow-up actions and provide additional information when available." * * * UPDATE ON 3/25/20 AT 1612 EDT FROM MEGAN SHOBER TO BETHANY CECERE * * * "The Department performed an investigation on March 25, 2020 to review this incident. For this fraction, the patient was prescribed a 6 Gy dose to the surface of the vaginal cylinder. Using CT imaging the licensee confirmed the proper placement of the cylinder prior to treatment. The licensee performed all pre-treatment checks, connected the patient to the HDR unit, and initiated treatment. Everything appeared to be as expected. However, following treatment it was very difficult for the authorized user to remove the cylinder; there appeared to be a vacuum suction seal. The licensee determined that the cylinder had been pulled an additional 3.5 cm into the patient, perforating the vaginal wall and protruding into the bowel space. The licensee believes that the bowel conformed to the shape of the cylinder during part or all of treatment, causing a much larger volume of the bowel to receive an elevated radiation dose as compared to the treatment plan. Based on the prescribed dose, the maximum unintended dose to the bowel is 6 Gy. The patient and referring physician were immediately informed of the event. The authorized user does not expect the patient to experience any radiological consequences from this event." Wisconsin Event Report ID No.: WI200010 Notified R3DO (Hanna) and NMSS Events Notification Email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2020-03-30
54594 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2020-03-20 10:25 | 2020-03-20 17:47 | 2020-03-20 | LOW PRESSURE COOLANT INJECTION UNPLANNED INOPERABILITY "On March 20, 2020, at 1025 hours [CDT], Unit 2 MCC [motor control center] 28/29-5 failed to transfer to its alternate feed during surveillance testing. This would result in MCC 28/29-5 being de-energized in the event of a DBA LOCA [design basis accident loss of coolant accident] in which the Unit 1 Emergency Diesel Generator fails to energize Bus 29. Consequently, the LPCI [low pressure coolant injection] Injection Valve (MO 2-1001-29A/B) would not have power to open on the loop selected by LPCI Loop Select. This renders both divisions of the LPCI mode of Residual Heat Removal system inoperable. Technical Specification 3.5.1, Condition E had previously been entered during testing, requiring restoration of LPCI in 72 hours. No other ECCS [emergency core cooling] systems were inoperable at the time of the event. Troubleshooting and repairs are in progress. "This event is reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function." The plant is still in its 72-hr. LCO action statement. The licensee has notified the NRC Resident Inspector and the state of Illinois Emergency Management Agency. | 0 | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-03-20
54593 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-10 | 2020-03-20 16:09 | 2020-03-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following is a summary of information received from the state of Colorado via email: The State is reporting 71 lost tritium exit signs, each containing 7.09 Ci. They were confirmed lost through annual registration. The signs were likely lost during renovations. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-30
54592 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-29 | 2020-03-20 13:57 | 2020-03-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following is a summary of information received from the state of Colorado via email: A 5.75 Ci tritium exit sign was confirmed lost through annual registration. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-30
54591 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-11-26 | 2020-03-20 10:00 | 2020-03-20 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATOR The following information was summarized from information received from the state of Colorado via email: On November 11, 2018, Karcher North America reported that one static eliminator was lost. The device contained 0.01 Ci of radioactive material. The radioactive material was not identified. Research identified that alpha emitters, such as poloniun-210, were normally used in static eliminators. * * * UPDATE ON 03/20/2020 AT 1259 EDT FROM KATHRYN MOTE TO OSSY FONT * * * The following update was received from the state of Colorado via email: The State notified the NRC that the lost radioactive material was polonium-210. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-30
54590 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-05-19 | 2020-03-19 16:56 | 2020-03-19 | COLORADO AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was summarized from the information received from the state of Colorado via email: In April 2018, the Colorado Department of Corrections - Territorial Facility identified that 19 tritium exit signs were missing. On 5/9/19, Territorial determined that the signs were lost. The exit signs contained 219 Ci of tritium in total. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-27
54589 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-05-19 | 2020-03-19 16:44 | 2020-03-19 | COLORADO AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was summarized from the information received from the state of Colorado via email: In April 2018, the Colorado Department of Corrections - Fremont Facility identified that a tritium exit sign was missing. On 5/9/19, Fremont determined that the sign was lost. The exit sign contained 11.47 Ci of tritium. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-27
54588 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2020-03-19 | 2020-03-19 16:38 | 2020-03-19 | PART 21 NOTIFICATION - TEST STAND DEFICIENCY The following is a summary of information obtained from Engine Systems, INC. (ESI) via fax: On February 14, 2019, ESI determined that all new P/N H40084720 EMD fuel injectors they supplied are considered suspect. The endurance test stand utilized for new EMD fuel injectors was found to contain a deficiency that may damage injectors during the testing process. There is a potential for the actuating stem of the endurance test stand to strike the injector follower off center, creating side loading that results in inadvertent rubbing between the follower and body. The condition is exacerbated by a lack of continuous lubrication from the test stand. Over the 2-hour test duration, the running surface of the follower scores and metal particles are introduced into the top end of the injector. The migration of these particles through the injector could initiate a seizure. An improperly functioning fuel injector could affect the load carrying capability of the diesel engine and adversely affect the diesel's ability to perform its safety-related function. The licensees affected are Columbia, St. Lucie, Dresden, Fitzpatrick, Point Beach, Turkey Point, Quad Cities, and Grand Gulf. Points of Contact: John Kriesel, Engineering Manager and Dan Roberts, Quality Manager at Engine Systems Inc. 175 Freight Rd. Rocky Mount, NC 27804. Office number: 252-977-2720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-03-19
54587 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-03-17 15:58 | 2020-03-17 19:38 | 2020-03-17 | NOTIFICATION TO OTHER GOVERNMENT AGENCY "At 1532 CDT, on 3/17/2020, it was reported to the Unit 1 Control Room that less than one gallon of hydraulic oil was spilled into the Colorado River during dredging activities. Cleanup using oil booms was completed at 1747 CDT. The cause of the hydraulic oil spill is under investigation. "The Texas General Land Office was notified at 1558 CDT. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-03-17
54586 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-03-16 | 2020-03-17 10:39 | 2020-03-17 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE GUIDE TUBE DAMAGED The following was received from the State of Texas via email: "On March 17, 2020, the Texas of Department of State Health (Agency) was notified that on March 16, 2020, one of the licensee's radiography crews was performing work at a temporary job site near Van Horn, Texas, when a piece of pipe fell onto the guide tube and they were unable to retract the source. A person authorized for source retrieval was dispatched and was able to retrieve the source and secure it inside the exposure device. The source retriever's pocket dosimeter had a reading of 155 millirem at the conclusion of the retrieval. The licensee will send the retriever's and the crew's dosimetry badges for processing. There were no other exposures as a result of this event. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300. "Device Info: QSA Delta 880, SN: D5797, Source Info: 59.4 curies, Iridium-192, SN: 93949G" Texas Incident Number: 9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-03-25
54585 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-03-13 | 2020-03-13 19:28 | 2020-03-13 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following was received from the State of Texas via email: "On March 13, 2020, [the Texas Department of State Health Services] was notified by the Houston Methodist Hospital of a medical event. The patient was to receive 18.4 Gy of therapeutic dose from a Novoste Beta-Cath system Sr-90 source (system serial no. 89670, source train serial no. za925). When the procedure began, the command was sent to the system to deliver the source. The source did not appear within the fluoro field as expected after 10 seconds and the command was sent to the system to retract the source. The source failed to retract. The oncologist manually removed the catheter from the patient and found the source stuck inside. It is now back in the system. The licensee has been reminded that they need to notify the referring physician within 24 hours. An investigation into this event is ongoing. More information will be provided when obtained in accordance with SA-300." Texas Incident Number: 9751 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-03-23
54584 | 0 | FLOWSERVE |  |  |  |  | 2020-03-12 | 2020-03-12 17:08 | 2020-06-11 | INTERIM PART 21 NOTIFICATION - DEFECTIVE SOLENOID VALVES The following is a summary of information that was obtained from Flowserve via facsimile: On January 13, 2020, and January 14, 2020, two Flowserve Model 38878-8, 3-way, 2-postion solenoids valves supplied to Seabrook Station for use on the feed water isolation valve actuator failed bench testing. The failed solenoid valves were returned to Flowserve for evaluation. The evaluation of these solenoid valves will be completed by June 11, 2020. Point of Contact: Matt Hobbs, PE Engineering Manager Office: 919-334-7127 MHobbs@flowserve.com * * * UPDATE ON 6/11/20 AT 1235 EST FROM MEGAN STRONG TO THOMAS KENDZIA * * * The following is a summary of the information provided by the vendor via fax and email: Testing at Flowserve determined that valves did not reposition when actuated and were failed. Disassembly determined that one valve had unidentified foreign material that was preventing valve from actuating, and the other valve had been partially disassembled and then reassembled, resulting in damage that caused the valve to not actuate. Flowsever determined that these conditions would have caused failure of the assembly and test performed at Flowserve before the valves were shipped and therefore occurred after Flowserve shipped the valves. Flowserve concluded that these two solenoid valve failures are not defects or deviations that occurred at Flowserve that would be associated with substantial safety hazards. Notified R1DO (Jackson) and Part 21/50.55 Reactors Group (by email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | Interim Eval Of Deviation | [9 empty] | Non Emergency | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2020-03-12
54583 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-02-03 | 2020-03-11 18:48 | 2020-03-11 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF A Cs-137 SOURCE The following information was received from the state of Florida via email: "St. Joseph's called the BRC [Bureau of Radiation Control] to notify that a source was unintentionally removed from their facility. They had contracted with North American Philips to trade in an old PET/CT Scanner and replace it with a new one. The licensee had cleared and reserved the room for the contractor to work in for a week. The old scanner had a sealed Cs-137 calibration source inside [16.57 milliCuries], and when the contractor removed it, they did not remove the source and leave it with the licensee as was agreed. The contractor notified the licensee when they realized they had possession of the source. The source is now at the North American Philips site in Nashville, TN. The new PET/CT will not have the referenced source; North American Philips has offered to dispose of it through Bionomics. The licensee has expressed willingness to proceed with that option rather than have the source returned. Since the contractor, rather than the licensee, misappropriated the source, an on-site visit from an inspector is not requested at this time." Florida Incident Number: FL20-034 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-03-19
54582 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2020-01-27 | 2020-03-11 16:38 | 2020-03-11 | AGREEMENT STATE REPORT - MISSING IODINE-125 SEED The following information was received from the state of New York via email: "On February 13, 2020, the Department [New York State Department of Health] was notified of a missing I-125 localization seed (Activity: approximately 252 microCuries) at Roswell Park Cancer Institute in Buffalo, New York." "An l-125 localization seed was removed from a patient, along with a specimen, in a procedure that took place on January 27, 2020. The seed and specimen are believed to have been delivered to the facility's Pathology Department. The RSO [Radiation Safety Officer] was informed of the missing seed on February 10, 2020. Currently, the facility is trying to locate the missing seed. Updates will be provided as they become available." New York Event Report ID No. NYDOH-20-01 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2020-03-19
54581 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2020-03-11 08:15 | 2020-03-11 11:48 | 2020-03-11 | AGREEMENT STATE REPORT - STOLEN GAUGE The following information was received from the state of South Carolina via email: "On March 11, 2020, the Department [South Carolina Department of Health and Environmental Control (SCDHEC)] was notified by the licensee at approximately 0815 [EDT] that a portable gauging device had been stolen from the licensee's storage location at 19 Highway 90 East, Little River. The gauging device is an Instrotek Model 3500 [moisture density gauge], serial number 722. This device contains 10 milliCuries of Cs-137 and 40 milliCuries of Am-241:Be. The licensee stated that the theft has been reported to local law enforcement. SCDHEC has notified the South Carolina Law Enforcement Division's Fusion Center." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2020-03-19
54580 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2020-03-10 | 2020-03-10 22:51 | 2020-03-10 | AGREEMENT STATE REPORT - LOST AND FOUND TROXLER MOISTURE DENSITY GAUGE The following information was received from the state of Utah via email: "On March 10, 2020, a member of the public was traveling on the road at about 500 North State Street in La Verkin, Utah. The individual saw a Troxler gauge (Model 3430) sitting in the middle of the road. He stopped picked it up and placed it in his truck. The gauge was not in a transport case, but the source rod was locked in the safe position, the individual took a couple of pictures of the gauge. The individual must have been familiar with portable gauges because he contacted an Engineering and Testing Company (Geotechnical Testing Services UT [GTS] 2700439) located in St. George. This licensee did not own the gauge, but told the individual to place the gauge in a secure location and stay away from it. GTS contacted the Division's [Utah Division of Radiation Control] emergency line to report that a gauge was found even though it was not theirs. This report was made at about 5:20 PM [MDT]. "There is another engineering company (Landmark Testing & Engineering, Inc. UT 2700428) in St George. The individual from GTS contacted an individual they knew who worked for Landmark Testing. "The Duty Officer manning the emergency line made contact with the Section Manager for the Radioactive Materials Section at about 6:25 PM and informed him of the report. The Section Manager contacted the GTS personnel at about 6:36 PM to interview him about the particulars of the report. The information was relayed to the Section Manager. In addition, the GTS personnel informed the Section Manager that the gauge belonged to Landmark Testing & Engineering and that they were on their way to pick up the gauge. In addition, the GTS personnel were able to send a couple of pictures of the gauge that showed the casing on the gauge was cracked near the source handle and the casing was slightly separated in the front from the base of the gauge. The model (3430) and serial number (26770) were visible in the photos. "The Section Manager contacted a staff member at about 6:52 PM, so that a report could be made to NRC. He had tried to contact the member of the public who had located the gauge, but had been unable to reach him. "At the time of this report, the licensee (Landmark) had not reported the missing/found gauge to the Division. Further investigation of this matter will be conducted by the Division [Utah Division of Radiation Control] tomorrow. An update will be sent when more information is gathered." Troxler gauges nominally contain 8 mCi of Cs-137 and 40 mCi of Am/Be. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2020-03-18
54579 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-03-10 | 2020-03-10 18:21 | 2020-03-10 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER The following information was received from the state of Texas via email: "On 10 March, 2020, the Agency [Texas Department of State Health Services] was notified of a gauge with a stuck shutter in the open position. The gauge is a Berthold Model LB7440L with a 5 mCi Cs-137 source with serial 186-1-88. This gauge normally operates with the shutter in the open position. There is no increased risk of exposure to any individual. An investigation into this event is ongoing." Texas Incident #: 9750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-03-18
54578 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2020-03-09 | 2020-03-10 16:13 | 2020-03-10 | AGREEMENT STATE REPORT - LOST IODINE-125 SEED The following information was received from the state of Utah via email: "Late in the evening on March 9, 2020, an individual in the pathology lab was examining an excised tissue sample that contained one 286 microCurie Iodine-125 seed used in a radioactive seed localization procedure. During the examination, the seed fell out of the tissue sample and went down the sink drain. The individual blocked off the drain, and the licensee waited until the morning of the 10th to remove the sink's p-trap to look for the seed. The licensee was unable to locate the seed, and assumes that the seed is lost. The Division [Utah Division of Radiation Control] will be performing an on-site investigation soon." Utah Report ID number: UT200002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2020-03-18
54577 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2020-03-07 | 2020-03-09 17:46 | 2020-03-09 | AGREEMENT STATE REPORT -- BROKEN RADIOGRAPHY CAMERA IN SHIELDED POSITION The following is a synopsis of a facsimile that was received from the State of Alabama: On March 9, 2020 at 0825 CDT, the State of Alabama Department of Public Health, Office of Radiation Control, Radioactive Materials Compliance Branch, was notified by licensee Acuren, Inc., that a radiographer attempted to unlock the locking mechanism of an 880D radiography camera and the key broke off in the lock. The licensee stated that the camera is still locked, is now "red-tagged," and is in storage until it can be sent to its vendor QSA for repair. The source was not exposed at the time and it is in the shielded position. Radiation surveys of the device are normal for a shielded position. This event occurred on March 7, 2020. Alabama Event Number: 20-05 The source is believed to be Ir-192. The source strength was not reported. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2020-03-17
54576 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2020-02-23 | 2020-03-09 13:08 | 2020-03-09 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received via email: "The licensee reported a stuck open shutter on an IMS model 5221-02 fixed gauging device. The manufacturer arrived on site 2/26/2020 and determined the cause to be a faulty solenoid valve on the air supply to the shutter. The valve was replaced and shutter was then determined to be working properly." Iowa Item Number: IA200001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2020-03-17
54575 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-08-02 | 2020-03-09 12:27 | 2020-03-09 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the State of Colorado via email: "The licensee reported to the State of Colorado two exit signs missing after renovation. "Initial date reported: 8/2/17 "Final Decision Material Lost date: 3/5/20" The exit signs have an activity of 7.5 Ci each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-17
54574 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-01-30 | 2020-03-09 10:28 | 2020-03-09 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the State of Colorado via email: "Discrepancies found in 2019 inventory registration compared to previous annual registrations resulted in 17 missing exit signs. "Initial date reported: 7/10/19 "Final Decision Material Lost date: 1/30/20" The exit signs have an activity of 7.5 Ci each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-17
54573 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-03-07 | 2020-03-07 13:38 | 2020-03-07 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE ON TRUCK STOLEN AT GUNPOINT "On March 7th, Kumar and Associates, Inc. (Denver) License No. CO 778-01 reported a stolen truck at gunpoint from the technician. The truck had on board a Troxler 3440 series nuclear density gauge with a standard load of not more than 333 MBq (9 mCi) of cesium-137 and 1.63 GBq (44 mCi) of americium-241: beryllium; or 2.44 MBq (66 microCi) of californium-252. The event took place in Lakewood, Colorado. The Lakewood police have been notified and they are aware that the truck has a density gauge on board. The police department is currently searching for the truck. "This event is still ongoing." Colorado Report ID Number: CO200016 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-16
54572 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2020-03-06 | 2020-03-06 15:14 | 2020-03-06 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following is a synopsis of information received via E-mail: At 1430 EST on 3/6/2020, the Bristol Myers Squibb Radiation Safety Officer made a notification to the New Jersey Bureau of Environmental Radiation that following the Tritium exit sign inventory for their campus, six exit signs were unaccounted for. The exit signs contained a total of approximately 130 Curies of Tritium. New Jersey State Event Report ID Number: TBD THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2020-03-16
54571 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-07-16 | 2020-03-06 14:02 | 2020-03-06 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following is a synopsis of information received from the State of Colorado via email: On 7/16/18, the Colorado Department of Health, Hazardous Materials and Waste Management, was informed by the licensee that, after performing a walk-down of their property, two of the three exit signs containing Tritium could not be located. The event occurred in Colorado Springs, Colorado. The missing exit signs had an activity of 9.21 Ci Tritium each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-16
54570 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2020-03-06 07:30 | 2020-03-06 14:19 | 2020-03-06 | FITNESS-FOR-DUTY - CONTRACT SUPERVISOR VIOLATED THE FFD POLICY A non-licensed contract supervisor had a confirmed positive for a controlled substance during an initial Fitness For Duty screening test. The individuals plant access has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Startup | Power Operation | Power Operation | Startup | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2020-03-06
54569 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2020-03-05 21:00 | 2020-03-05 21:14 | 2020-03-05 | PLANNED PLANT COMPUTER OUTAGE FOR SYSTEM UPGRADE "On March 05, 2020, at 2100 EST, the site commenced a planned upgrade of the main plant computer system (MPCS). During this upgrade, the normal computer data will not be available to the emergency response facilities, but compensatory capabilities will be in place. The scheduled duration for the MPCS upgrade is 96 hours. Since the compensatory measures will be in place in excess of 72 hours, this condition is being reported pursuant to 10 CFR 50.72(b)(3)(xiii). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-03-05
54568 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-08-30 | 2020-03-05 17:11 | 2020-03-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information is a synopsis of an email received from the state of Colorado: The licensee has reported that they are unable to locate three tritium exit signs. Each exit sign has an activity of 10 Ci. The current service manager states that it is possible the previous owner may have taken the signs. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-13
54567 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2020-03-05 12:35 | 2020-03-05 16:48 | 2020-03-05 | SECONDARY CONTAINMENT MOMENTARILY INOPERABLE "On March 05, 2020, at 1235 EST, with the reactor at 100 percent core thermal power and steady state conditions, plant personnel notified the main control room that both doors in the secondary containment airlock on the reactor building fifth floor were opened simultaneously for a period of approximately three seconds (i.e., from 12:35:00 to 12:35:03 EST). The failure of this interlock, which is intended to prevent both doors from being opened simultaneously, resulted in the Technical Specification (TS) Surveillance Requirement (SR) 3 .6.4.1.3 not being met. The maximum secondary containment pressure observed during that time remained within TS limits. There were no radiological releases associated with this event. "Declaring secondary containment inoperable as a result of not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2020-03-05
54566 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-07-29 | 2020-03-05 11:42 | 2020-03-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received from the State of Colorado via email: "The current manager of Rodeway Inn reported 7 lost tritium exit signs when conducting the annual reconciliation." The exit signs have an activity of 7.5 Ci each. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-13
54565 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-06-29 | 2020-03-05 11:41 | 2020-03-05 | AGREEMENT STATE REPORT - LOST IODINE-125 SEED The following information was received from the State of Georgia via email: "On June 29, 2018, it was brought to the [Piedmont Fayette Hospital Radiation Safety Officer's] RSO's attention that a radioactive seed containing 62 microCuries of Iodine-125 was unaccounted for and could not be located. The seed was manufactured by Best Medical International, Inc., Model 2301. The physical form is a double wall titanium tube containing a tungsten x-ray marker that is coated with I-125. The source serial/lot number is 45876A-26. The source was calibrated at 100 microCuries on 5/11/2018. On the morning of the seed implantation procedure, 6/27/2018, the source measured at 62 microCuries in the dose calibrator in the hot lab. "The seed had been used for localization of a breast lesion. Tissue was extracted from the patient and the specimen was reported to have contained the seed at the time of specimen radiography. Following this radiography procedure, the seed appears to have been lost. All efforts were made by staff on-site to locate and search for the seed in all possible locations, with no success. The patient was brought back in for radiology procedures to ensure that the seed was not still contained in the patient. Results of x-rays showed that the seed was not present in the patient. According to the RSO, it is likely that the seed was disposed of along with the trash collected after the procedure, or possibly washed down the floor drain in the specimen radiography room. "According to the RSO, this is a best guess as to the fate of the seed. No individual members of the public or staff were likely to have been exposed to significant doses of radiation, based on the available information submitted to EPD [Georgia Environmental Protection Division]." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-13
54564 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2016-08-09 | 2020-03-05 11:08 | 2020-03-05 | AGREEMENT STATE REPORT - LOST I-125 SOURCE The following was received from the State of Georgia via e-mail: "The Georgia Radiation Materials Program received a call from the [Radiation Safety Officer] RSO from Grady Memorial Hospital on August 12, 2016, stating the [200 microCurie] I-125 seed used for localization of non-palpable lesions was lost. The doctor performing the procedure stated the seed went into the tube of the suction tank. A survey of the suction tank, hallways and operating room did not uncover the lost source. The tissue, removed from the patient, which was transferred to pathology, also did not contain the source. The surveys of the hallway and operating room were performed after the hospital was notified. The RSO recommends bringing the patient back in the hospital to be surveyed to verify if the source was ever removed from the patient. At the time of the call, the RSO has been unable to speak to the doctor. The doctor is a surgeon and not an authorized user. The RSO stated the tube to the suction tank cannot be found and it may have made its way into the biohazard container. The RSO will follow-up with the biohazard department to see if the tube can be traced down so the tube can be surveyed to determine if the source became lodged within it. The RSO is also trying to follow-up with the doctor for more information." NMED Report ID: 160362 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-13
54563 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-11-06 | 2020-03-05 11:08 | 2020-03-05 | AGREEMENT STATE REPORT - LEAKING CESIUM-137 SOURCE The following information was received from the State of Georgia via email: "[The Radiation Safety Officer] of Phoenix Technology reported a leaking cesium-137 source from one of their clients (Myers Cardiology). During a source change out on November 6, 2017, it was noted that the old source was leaking. The activity of the leaking source is 203 microCuries, and the leak test results are 26 nanoCuries. The leaking source was placed inside a protective pig and inside a plastic bag labeled as a damaged source. The source has been sent to Pinestar Technologies in Pennsylvania for proper disposal." Source Manufacturer: IPL Source Model No.: MED-3550 Source Serial No.: 986-15-17 Georgia Item Number: GA170001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-13
54562 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2020-03-04 12:05 | 2020-03-04 15:35 | 2020-03-04 | MANUAL SCRAM IN THE TURBINE CONTROL SYSTEM "At 1205 EST, on March 4, 2020, Nine Mile Point Unit 2 initiated a manual reactor scram due to lowering Electrohydraulic Control System (EHC) level in the turbine control system. The cause of the lowering level was a leak in the EHC system piping. "All control rods inserted. There were no safety system actuations. The cause of the EHC leak is being investigated. "The NRC Resident has been notified." Additionally, the licensee notified the New York State Public Service Commission. | 0 | 0 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2020-03-04
54561 | -1 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-03-04 08:18 | 2020-03-04 12:24 | 2020-03-05 | NOTIFICATION TO OTHER GOVERNMENT AGENCY "On March 4, 2020, an actual Unusual Event code was inadvertently sent to an offsite agency, Institute of Nuclear Power Operations (INPO), and to a former NRC Resident Inspector during a planned emergency response drill. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 3/5/2020 AT 1554 EST FROM RONALD ROHAN TO DONALD NORWOOD * * * Based on further review of the NRC reporting guidance relative to these criteria, STP has concluded that this condition is below the reporting threshold outlined in NUREG-1022 Revision 3. NUREG-1022 states the following (page 54): 'Licensees generally do not have to report media and government interactions unless they are related to the radiological health and safety of the public or on-site personnel, or protection of the environment. "The condition originally reported in EN 54561 is not a news release or government notification and has no impact on the radiological health and safety of the public or on-site personnel, or protection of the environment. Therefore, STP is retracting EN 54561. "The NRC Resident Inspector was notified on 3/5/2020 at 1310 CST." Notified R4DO Rick Deese. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-03-04
54560 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2020-03-03 20:50 | 2020-03-04 02:07 | 2020-05-04 | REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 2050 MST on March 3, 2020, Unit 2 reactor automatically tripped on Low Steam Generator (SG) Number 1 level signal from the Reactor Protection System. The low SG level occurred as the result of a trip of both Main Feedwater Pumps, which tripped during restoration of power to the Main Feedwater Pump Lube oil control panel. Auxiliary Feedwater (AFAS-1 and AFAS-2) actuated due to low SG levels in both SG post reactor trip as designed. This event is being reported as a reactor protection system and a specified system actuation in accordance with the reporting criteria of 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "Following the reactor trip, all [control element assemblies] CEAs inserted fully into the core. All systems operated as expected. No emergency plan classification was required per the Emergency Plan. Safety related busses remained powered during the event from offsite power and the offsite power grid is stable. Unit 2 is stable and in Mode 3. Steam Generators are being fed via the class 1E powered motor driven auxiliary feedwater pump. "The NRC Senior Resident Inspector has been informed." Units 1 and 3 were unaffected by the trip and remain at 100 percent power. * * * UPDATE FROM ALLAN BRIEFE TO DONALD NORWOOD AT 1231 EDT ON 5/4/2020 * * * "The event reported on March 4, 2020 (EN 54560) also included actuations of the Emergency Diesel Generators in response to the AFAS-1 and AFAS-2 actuations. The Class 4.16kV buses remained energized from off-site power. "The NRC Senior Resident Inspector has been informed." Notified R4DO (Drake). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS Actuation - Critical | Valid Specif Sys Actuation |  |  | IMode2: Power Operation; FMode2: Hot Standby | Non Emergency | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-03-04
54559 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2020-03-03 04:16 | 2020-03-03 12:18 | 2020-03-03 | EMERGENCY DIESEL GENERATOR ACTUATION "At 0416 CST on March 3, 2020, with Browns Ferry Unit 3 in Mode 5, there was a partial loss of 161kV power due to a trip and re-closure of the feeder breaker supplying the Common Station Service Transformer (CSST) A. Unit 3 lost power to the 1A Start Bus and the 3A Unit Board, which supplies power to the 3EA and 3EB 4kV Shutdown Boards. The loss of the 4kV Shutdown Boards resulted in an auto actuation of the 3A and 3B Emergency Diesel Generators (EDG). The 3C EDG and 3EC 4kV Shutdown Board were removed from service for maintenance at the time of the loss of power, and the 3ED 4kV Shutdown Board continued to be powered from the 3B Unit Board. "All systems responded as expected for the loss of power. "This event requires an 8 hour report per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact to the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The partial loss of power was caused by a storm in the area. Offsite power has been restored to the CSST and the EDGs have been secured. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2020-03-03
54558 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-03-02 16:30 | 2020-03-03 11:46 | 2020-03-03 | AGREEMENT STATE REPORT - SOURCE FAILED TO RETRACT The following information was received from the Florida Bureau of Radiation Control (the Bureau) via email: "On 3/2/2020 at 1850 EST, [the licensee's Radiation Safety Officer (RSO)] called to report that a radiography source uncoupled from its drive cable, but remained in its sleeve during an x-ray of a processing tank. The time of the incident was approximately 1630 EST. On site materials were used to shield and secure the source which was subsequently locked in the licensee's storage facility. No abnormal or excessive doses were reported. [The licensee] will provide a written report to the Bureau within 10 business days." The gauge is a QSA Global model 880 Delta (S/N: D4132) with a 76 Ci Ir-192 source (S/N: 94135G). Florida Incident Number: FL20-025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-03-11
54557 | 0 | OCEANEERING INTERNATIONAL |  |  |  |  | 2020-03-02 17:50 | 2020-03-02 22:31 | 2020-03-02 | RADIOGRAPHY CAMERA LOST OVERBOARD The licensee reported that a SPEC 150 Model G-60 (s/n: 1507) camera was lost when it fell overboard in the WD73-A area of the Gulf of Mexico. The device contained an 18 Ci iridium-192 source (s/n: 2604). The licensee stated that they will not attempt to retrieve the device. They will also notify the Louisiana Department of Environmental Quality. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2020-03-10
54556 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-03-02 14:52 | 2020-03-02 20:45 | 2020-03-02 | FITNESS-FOR-DUTY REPORT - CONTRACT SUPERVISOR CONFIRMED POSITIVE TEST A non-licensed contract employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2020-03-02
54555 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-06-08 | 2020-03-02 16:28 | 2020-03-02 | AGREEMENT STATE REPORT - 90 LOST TRITIUM EXIT SIGNS The following information was received via E-mail: "The Cinemark - Number 346 - Greeley Manager reported 90 lost tritium exit signs when conducting the annual reconciliation." According to the Colorado General License Coordinator, the licensee says that the signs were not installed during construction and believes that the signs were never delivered. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-10
54554 | -1 | MAGRUDER PAVING, LLC |  |  |  |  | 2020-02-29 | 2020-03-02 12:45 | 2020-03-16 | STOLEN PORTABLE DENSITY MOISTURE GAUGE The licensee left a locked trailer at a job site in Rolla, Missouri Friday evening, 2/28/2020. The trailer contained a locked case, which was chained and locked to the trailer. The case contained a Seaman's portable density moisture gauge, Model Number C300, Serial Number 21274, with a 4.5 mCi Radium-226 source. The trailer, with the gauge inside, was stolen from the job site sometime between Friday evening 2/28/2020 and mid-day Saturday 2/29/2020 when employees of the licensee returned to the job site. The trailer is an enclosed trailer, approximately 14 feet in length, white in color, with no lettering or other readily distinguishable markings on the outside. The licensee notified the Phelps' county sheriff's office. The sheriff's office issued report number 20200263 for this event. * * * RETRACTION ON 3/16/2020 AT 1227 EDT FROM DWAYNE MULLER TO BETHANY CECERE * * * This event is being retracted because the trailer was not stolen. The trailer was moved to the corporate location, but all parties were not aware of the move. The licensee notified the NRC R3 Inspector (O'Dowd) and the Phelps' county sheriff's office. Notified R3DO (Hanna), NMSS Events, and ILTAB. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2020-03-10
54553 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-03-01 | 2020-03-01 13:52 | 2020-03-01 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF RADIOACTIVE MATERIAL The following information was received via E-mail: This event occurred in Austin, Texas. "On March 1, 2020, one of the licensee's technicians had pulled off the road and was parked in a parking area, sleeping, when local law enforcement pulled up. Local law enforcement wanted to take the technician in for suspicion of DWI. At approximately 0800 CST the technician called the site radiation safety officer and told him of the situation. "Law enforcement stayed with the technician until the tow truck came and took the vehicle to impound at approximately 0830 CST. The vehicle was locked, the alarm on the dark room was activated and the technician took all the keys to the dark room and camera with him. The vehicle was carrying a radiography camera (Spec 150) containing an 80 Curie Iridium-192 source. "The licensee dispatched employees to the impound yard and they arrived at approximately 1015 CST and provided surveillance of the vehicle until it was released to them. They verified that the alarm system on the dark room was still armed and that the camera was present. The truck is being returned to the licensee's facility. "At last report from the licensee, law enforcement had not performed any testing to determine if the technician was under-the-influence. More information will be provided as it is obtained in accordance with SA-300." Texas Incident Number: Not Yet Assigned | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-03-09
54552 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-02-11 | 2020-02-28 15:54 | 2020-02-28 | AGREEMENT STATE REPORT - TWO PERSONNEL EXCEEDED ANNUAL DOSE LIMIT The following was received from the state of Louisiana via email: "On February 11, 2020, Source Production & Equipment Company, Inc. (SPEC) contacted Louisiana Department of Environmental Quality, Emergency & Radiation Services Division, Radiation Section, by email to report that two employees had exceeded their annual five rem limit for the 2019 year. Both employees worked at SPEC in the hot cell room manufacturing Se-75, Ir-192, and Co-60 sources for industrial radiography. Hot Cell employee number 1 received an estimated TEDE of 5,028 mR and Hot Cell Employee number 2 received an estimated TEDE of 5,687 mR for 2019 year." Event Report ID No.: LA20200003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-03-09
54551 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2020-02-19 | 2020-02-28 10:17 | 2020-02-28 | AGREEMENT STATE REPORT - LOSS OF DEVICES CONTAINING AM-241 The following was received from the Tennessee Division of Radiological Health via email: "During a recent inventory at Blues City Brewery, the environmental health and safety manager discovered that two devices [Industrial Dynamics CI-2GV/3] were missing. Devices had been out of use for 1 - 2 years. Actual activity [of the Am-241 sources] are unknown at this point. The activity will be reported during the follow-up report." Incident Report No.: TN-20-038 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-03-09
54550 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-01-18 | 2020-02-28 06:54 | 2020-02-28 | AGREEMENT STATE REPORT - IMPROPER DISPOSAL OF I-125 SEED The following is a summary of emails received from the Georgia Department of Natural Resources (the state): On 01/18/2019, the licensee performed a Radioactive Seed Localization (RSL) using 81 microCi of I-125. The tissue and seed were transported to pathology where the pathologist misidentified the seed as a straight clip-non-radioactive and the material was designated for disposal. The Nuclear Technologist realized on 02/06/2019, through paperwork, that the seed could not be accounted for and had improperly gone out through the ordinary waste process at the hospital. On 03/04/2019, the state's reactive inspection report found that the RSL procedure was a two seed implantation. A documentation problem occurred when two separate I-125 seed tracking documents were used instead of one. When the tissue containing the seeds was excised and taken to pathology in a cup, only a single document showing one seed implant made it to pathology. The second document did not arrive, so pathology was unaware that there were two seed implants. This led to one of the seeds being mistaken for a clip. The cup that the tissue was transported in was surveyed at pathology and there was the expected readout, which was attributed to a single seed. Corrective actions include to document seeds acquired for implantation on a single sheet of paper. Efforts were being made to discontinue the RSL program and replace it with a radiofrequency seed localization system that involves no radioactivity. The incident was closed on 03/04 2019. Incident Report No.: GA-2019-10 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-09
54549 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-05-02 | 2020-02-28 06:54 | 2020-02-28 | AGREEMENT STATE REPORT - BROKEN DENSITY GAUGE SHUTTER The following is a summary of emails received from the Georgia Department of Natural Resources (the state): On 05/02/2019, the licensee discovered a broken shutter on an Ohmart DSGX GEN2000 fixed density gauge during semi-annual leak testing. The gauge is roughly 15 to 20 feet in the air and contained a 20 mCi Cs-137 source (A-2102 source/SN 61798). The source was barricaded and warnings posted. The source was determined not to be leaking. At the time a reactive inspection was performed. On 08/01/2019, an update was sent to the state. An offsite authorized technician attempted to repair the shutter but was unsuccessful. The radiation source remained in service and barricaded and the RSO continued to actively monitor the source with no leakage detected. The licensee was obtaining a quote for removal/proper disposal and the purchase of a new radiation source for replacement, but the source continues to be operational with no additional risk to workers. The incident was closed on 08/01/2019. Incident Report No.: GA-2019-15 * * * UPDATE ON 2/28/2020 AT 1406 EST FROM GREG REESE TO THOMAS KENDZIA * * * Gauge was replaced and sent to QSA Global for disposal. Source was received at QSA Global on 01/13/2020 and verified to not be leaking. Notified R1DO (Ferdas) and NMSS Event Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-09
54548 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-02-24 | 2020-02-27 15:54 | 2020-02-27 | MEDICAL EVENT - HDR UNDERDOSE TO PATIENT The following information was received from the state of Florida via E-mail: "[The licensee] reported to the BRC [Bureau of Radiation Control] on 25 Feb 2020, and e-mailed an incident report on 26 Feb 2020 at 1224 EST that on 24 Feb 2020 at 1315 EST an HDR [high dose rate] incident occurred to a patient receiving skin therapy. "The patient was prescribed 7.5 Gray x 5 fractions, on five different parts of the left hand. On the first dose of the first fraction, it was observed that catheter numbers 1 - 15 were reversed, causing an underdose to the patient by 56.25 percent. No Authorized Users were exposed to the source or otherwise contaminated." Florida Incident Number: FL20-022 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-03-06
54547 | 0 | VETERANS HEALTH ADMINISTRATION |  |  |  |  | 2020-02-27 06:10 | 2020-02-27 10:38 | 2020-02-27 | NON-AGREEMENT STATE REPORT - EXTERNALLY CONTAMINATED PACKAGE The following was received from the Veterans Health Administration via E-mail: "Per 10 CFR 20.1906(d), Veterans Health Administration (VHA) National Health Physics Program is reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. "The package was received Thursday, February 27, 2020, at around 0710 EST by the North Florida/South Georgia Veterans Health System [Permit No.: 0912467-02] in Gainesville, Florida. This facility holds permit number 09-12467-02 under the VHA master materials license. "The package was checked-in and surveyed upon receipt around 0710 EST. Wipe tests performed on the external surface of the entire package indicated a removable contamination level of around 560 dpm/cm2 as compared to the regulatory limit of 240 dpm/cm2 for beta-gamma emitters. Removable contamination level on the bottom surface of the package, indicated a removable contamination level of around 413 dpm/cm2 as compared to the regulatory limit of 240 dpm/cm2 for beta-gamma emitters. "The package contained three unit doses consisting of a 6 mCi dose of Tc-99m Mebrofenin (calibrated for 1330), a 25 mCi dose of Tc-99m Sestamibi (calibrated for 0930), and a 1 mCi dose of Tc-99m Sulfur Colloid (calibrated for 0800). "The dosage was shipped from Triad Isotopes, out of Jacksonville, Florida, who was also the delivery carrier. The facility Radiation Safety Officer immediately notified the delivery carrier by phone about the contaminated package around 0730 EST. "The patient dosages inside the package were not impacted and were able to be used. As corrective actions, the packaging materials were bagged in plastic and set aside in a restricted area at the facility. "VHA National Health Physics Program, who manages the master materials license, was notified of the incident around 0840 EST. "In addition, the licensee is notifying their NRC Region III project manager (Parker) of the event by inclusion in this email." The external contamination was Tc-99m and the package will be held until the isotope has decayed prior to returning it to the pharmacy. * * * UPDATE FROM THE STATE OF FLORIDA, BUREAU OF RADIATION CONTROL TO DONALD NORWOOD AT 1725 EST ON 2/28/2020 * * * The following is a synopsis of information received via E-mail: Reporting Organization: State of Florida Bureau of Radiation Control NRC Notified By: Matthew Senison Licensee: Jubilant DraxImage Radiopharmacies, Inc. City, State: Jacksonville, Florida License Number: 4587-5 Jubilant, Jacksonville received a call from the VHA in Gainesville, Florida about a delivery bag which had been delivered around 0710 EST that was contaminated on the outside. Jubilant, Jacksonville then notified their RSO who notified Jubilant's corporate RSO. Jubilant, Jacksonville personnel reviewed surveys and DOT documentation and found no removable contamination. They immediately pulled all six carts that are used in the pharmacy and wipe tested and surveyed each cart using a single channel analyzer and found only background. The driver is a third party (MDS) and had just returned. Jubilant, Jacksonville personnel surveyed and wipe tested the entire van and found it to also be at background. The Jubilant, Jacksonville RSO then called the VHA's RSO to relay that three patient doses were in the bag and no removable contamination had been found in the bag nor on the doses. VHA's RSO stated that she was notifying the NRC who would notify BRC. Since the NRC report shows the activity was Tc-99m, and neither party could find the source; at this point greater than five half-lives have passed, so there are no current plans to deploy investigators to either facility at this time. Florida Incident Number: FL20-023 (2) Notified R1DO (Ferdas), R3DO (Orth), and the NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2020-03-06
54546 | 0 | UNIV OF NEW MEXICO |  |  |  | 0.005 KW AGN-201M #112 | 2020-02-25 13:30 | 2020-02-26 18:15 | 2020-02-26 | TECHNICAL SPECIFICATION NON-COMPLIANCE The following is a summary received from the University of New Mexico Reactor Facility via email: At 1330 MST, February 25, 2020, a pre-operational checkout was being performed on the reactor while it was shutdown. The pre-operational checkout includes confirming operation of the rod interlocks, scram systems, and control rods. The interlock check was performed and all requirements were fulfilled. During the manual scram test, Operators determined that only Safety Rod #2 and the Coarse Control Rod scrammed. Safety Rod #1 was still attached to the magnet and was being driven out along with the drive motor. As a result, the licensee was not in compliance with Limiting Conditions for Operations, Section 3.2a, which requires the fine control rod, coarse control rod, and the two safety rods be operable and the carriage position of the fine and coarse control rods be displayed at the console whenever any rod is above its lower limit. Operators performed a series of tests to determine the cause of the problem. Operators determined that the rod and plate were sticking to the magnet, but could not be separated when the rod was subject to downward force. Corrective actions included cleaning the plate and magnet, and breaking any potential air seals at the plate. After a series of satisfactory tests, Safety Rod #1 was returned to operable condition and reinstalled in the reactor. The rod was tested to reassure it would scram in its original configuration. The issue with Safety Rod #1 did not affect the shutdown margin of the reactor, and at no time was the reactor operated when Safety Rod #1 was not in operable condition. This notification is required per Technical Specification 6.9. The licensee notified the NRR Project Manager (Helvenston). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | NM | NPR | [5 empty] | 0 | 2020-02-26
54545 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-13 | 2020-02-26 14:11 | 2020-02-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Colorado by email: "One tritium exit sign reported as never received or installed when conducting the annual reconciliation." The initial date reported to the State was December 13, 2017. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-05
54544 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-02-24 13:15 | 2020-02-25 18:03 | 2020-02-25 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following was received from the state of Florida via email: "On 24 Feb. 2020, at 1315 EST, an underdose of radiation to a patient receiving skin therapy occurred. The patient was scheduled to receive five fractions, at 7.5 grays per fraction, on five different parts of the left hand per fraction. On the first dose of the first fraction, it was observed that catheter numbers 1 - 15 were reversed, causing an underdose to the patient. No Authorized Users were exposed to the source or otherwise contaminated. The licensee has agreed to submit further information on 26 Feb 2020. Since the cause of this incident is machine generated, in accordance with BRC [State of Florida Bureau of Radiation Control] procedures, it is not being given an incident number, and is being forwarded to ERCX [the X-Ray Machine Section of the BRC]." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-03-04
54543 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-02-21 | 2020-02-25 17:27 | 2020-02-25 | AGREEMENT STATE REPORT - STOLEN FLUORESCENCE ANALYZER EQUIPMENT The following report was received from the state of Illinois via email: "The Agency [Illinois Emergency Management Agency] was notified by the Radiation Safety Officer (RSO) of the Illinois Department of Public Health (IDPH) that an XRF [X-ray fluorescence] instrument was stolen the morning of 2/21/20 in Peoria, IL. The RSO was made aware of the theft at approximately 1030 [CST] today. The vehicle had been parked overnight in the driveway of an IDPH employee who works out of the Peoria field office (site #2 on IL license). The gauge was locked in the trunk, in addition to having a lock on the case itself. However, the vehicle had been left running while the user went back into their home to retrieve a laptop, and upon their return they realized the vehicle had been stolen. Peoria Police were notified and informed of the instrument and radiation source in the trunk. The XRF is model XLP303A, serial number 14472; and the source serial number is TR2743. The IDPH will keep the Agency updated if they receive any additional information related to the vehicle or XRF instrument. The theft appears to be incidental to the theft of a vehicle and not an intentional diversion of radioactive material. The sources contained within these devices are IAEA category 5, meaning no one could be permanently injured and the amount of radioactive material, even if dispersed, could not permanently injure anyone." Illinois report no.: IL200006 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-03-04
54542 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-02-20 | 2020-02-25 13:49 | 2020-02-25 | AGREEMENT STATE REPORT - GAUGE FAILURE The following report was received via email from the Commonwealth of Pennsylvania: "During an inspection on February 20, 2020, an above normal reading on a Cesium-137 level gauge source head was discovered. Radiation measurements ranged from approximately 15 to 45 millirem per hour at one foot from the back of the source holder cap. It should be noted this gauge is located 11.5 feet off the ground, in an area with no stationed personnel or foot traffic. The device is a Kayray Model 7062B level gauge (Serial No. 21462) containing 25 milliCuries of Cs-137. The licensee immediately removed the device from service, the area was secured to ensure background radiation levels, and the manufacturer was contacted to initiate either a repair or replacement of the gauge. The area will remain secured until the device is able to be put into service again." PA incident number: PA200005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-03-04
54541 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-12-18 | 2020-02-25 06:28 | 2020-02-25 | AGREEMENT STATE REPORT - LEAKING PROMETHIUM-147 SOURCE The following information was received from the state of Georgia via email: "On December 11, 2018, [Honeywell International] tested a sealed source for leakage or contamination and received results on December 21, 2018. The result from [their] vendor [was] 0.0113 +/- 0.0002 microCuries. This result is above the limit of 0.005 microCuries. "The capsule has been isolated and there [was] no loose contamination detected in [their] facility. [Honeywell] will contact the vendor and arrange to return the capsule after the new year." The source capsule, Model PHC.C2, serial no. AE5051, was manufactured with 2 Ci of Pm-147. The capsule was returned to Eckert & Ziegler who received it on 3/4/2019. The state of Georgia considers this matter closed. NMED Incident # 190022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-04
54540 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-02-24 | 2020-02-24 19:10 | 2020-06-18 | AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE The following is a synopsis of a event reported by the state of Texas via email and phone call: On February 24, 2020, the Texas Department of State Health Services (Agency) was contacted by the Braun Intertec Corporation RSO to report a stolen moisture density gauge. The gauge was last seen on February 19, 2020 at the end of work in McKinney Texas. It was locked in a box in the back of a truck which was then driven to Euless, Texas where it reported to stay until February 24, 2020. The truck was then driven to a jobsite in Richardson, TX on February 24, 2020 at which point the employee realized that the locks were gone and the moisture density gauge was removed from the box in the back of the truck. Euless Police were notified. The activity for the density gauge is estimated to be 10 mCi Cs-137 and 40 mCi of Am241/Be. An investigation into this event is ongoing. More information will be provided when obtained in accordance with SA- 300. Texas Incident number: 9746 * * * UPDATE ON 6/18/20 AT 1721 EDT FROM KAREN BLANCHARD TO ANDREW WAUGH * * * The following information was received from the state of Texas via email: "On June 17, 2020, the Agency was notified by a steel mill in Midlothian, Texas, that it had found a moisture/density gauge in a load of metal from a recycler. The serial number was checked and it was determined to be this licensee's gauge that was stolen February 24, 2020. The licensee was notified and picked up the device on June 18, 2020. The licensee transported the device to a manufacturer's facility in Arlington, Texas, and transferred it for disposal. The manufacturer will complete leak tests and provide the licensee with the results. [There were] no exposures that would exceed any regulatory limit at the steel mill. Investigation will continue to determine if any exposures occurred at the recycler and if the recycler can provide information on where, or from whom, it got the device. "More information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Warnick), NMSS Events Notification (email), ILTAB (email), and CNSNS (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-03-03
54538 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2020-02-23 21:23 | 2020-02-24 14:41 | 2020-02-24 | OFFSITE NOTIFICATION "At 2100 (EST) on February 23rd, 2020, the New Hanover County Deputy Fire Marshall was notified per State code requirements that a fire door for Fuel Manufacturing Operation (FMO) Dry Conversion Process (DCP) Line 1 conversion area remained open and unattended for an extended time. DCP Line 1 was shut down for maintenance at the time and all Special Nuclear Material (SNM) had been removed prior to work beginning. Compensatory measures have been enacted. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will notify NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2020-02-24
54537 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-04-03 | 2020-02-24 14:20 | 2020-02-24 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER The following is a synopsis of a email from the state of Georgia: On April 3, 2018, the Georgia Radioactive Material Program was informed that a fixed nuclear gauge on the number 4 Digester had a shutter stuck in the open position (normal operation mode). The shutter was made operable on the same day, that the report was made to the state of Georgia. The gauge is a Kay Ray 7063-P and serial number 9132. The gauge contains 500 mCi of Cs-137. The gauge is in service with all radiation readings acceptable. There was no risk of exposure to employees or members of the public. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2020-03-03
54536 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-21 | 2020-02-21 14:57 | 2020-02-21 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Colorado by email: "Reported one lost tritium exit sign when conducting the annual reconciliation." The initial date reported to the State was verbally in 2016. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-03-02
54535 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2020-02-20 | 2020-02-21 10:30 | 2020-02-21 | AGREEMENT STATE REPORT - ABANDONED PORTABLE MOISTURE DENSITY GAUGE The following was received from the state of New Jersey via email: "A local Police Department informed [NJ Department Radioactive Materials Program] that a suspicious package was discovered behind a deli/apartment building. Hazmat officials responded. The package was identified as the transport container for a portable moisture density gauge. Labeling on the container identified the gauge as a CPN International, Inc., MC Series Portaprobe, serial number M380404223. The labeling further stated that the gauge contained a Cs-137/Am-241/Be source. The listed activities were 10 mCi of Cs-137 as of 11/19/97 and 50 mCi of Am-241/Be as of 6/6/97. The shipping container appeared intact, with appropriate cautionary labeling. The highest exposure rate reported was 0.9 mR/hr at two feet from the container. The licensee reportedly told officials on the scene that they were out of business and could not explain how the device got to the location where it was found. Due to the lack of security that allowed the device to be moved to the location where it was found, we were not confident that the licensee would be able to secure the item if it was returned to them. The hazmat team secured the device overnight at their office location. The device will be secured pending completion of the investigation and subsequent proper disposition of the device. "The State of New Jersey Department of Environmental Protection's Bureau of Environmental Radiation was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2020-03-02
54534 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-02-19 | 2020-02-20 17:50 | 2020-02-20 | AGREEMENT STATE REPORT - UNDERDOSE OF YTTRIUM-90 DURING TREATMENT "On February 20, 2020, the Radiation Safety Officer for the Licensee notified this Agency of a medical event involving yttrium-90 Theraspheres. The prescribed dose was 120 Gy but only 85.2 Gy was administered with the remaining intended dose left in the tubing. The remainder could not be flushed out and the procedure was halted. The Licensee will meet with the manufacturer next week at the Licensee's facility to address this issue. This investigation is ongoing. More information will be provided when obtained in accordance with SA-300." Texas Incident Number: I-9745 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-02-28
54533 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2020-02-20 12:40 | 2020-02-20 15:04 | 2020-02-20 | UNANALYZED CONDITION - UNPROTECTED DC CONTROL CIRCUITS [On February 20, 2020, at 1240 EST, the Licensee determined the following information:] "This notification is in reference to reports EN 54130 and LER 2019-002, which were retracted. James A. FitzPatrick Nuclear Power Plant received additional information on the technical basis for the retraction. Further review, including testing of the terminal blocks, demonstrated that the short circuit current would result in heat levels in excess of cable insulation ratings. "Unprotected DC control circuits for non-safety related DC motors are routed between separate fire areas. A postulated fire in one area can cause a short circuit and potentially result in secondary fires or cable fires in other fire areas where the cables are routed. The secondary fires or cable failures degrade the degree of separation for redundant safe shutdown trains and are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B). "Compensatory actions per the Technical Requirements Manual (TRM) for affected fire areas have been implemented. A modification to install fuses in the control circuits for 94P-2(M), 31P-7A(M), 31P-7B(M), and 94P-13(M) has been scheduled and shall correct this condition." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2020-02-20
54532 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-02-19 09:36 | 2020-02-19 10:20 | 2020-02-19 | MANUAL REACTOR TRIP DUE TO LOSS OF CONTROL OF STEAM GENERATOR WATER LEVEL "At 0936 EST on February 19, 2020, the Watts Bar Unit 1 reactor was manually tripped while operating at 100 percent power in response to loss of control of water level for steam generator number 3. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. There is no impact to Unit 2. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four-hour report under 10 CFR 50. 72(b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight-hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-02-19
54531 | -1 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-02-19 09:57 | 2020-02-19 10:20 | 2020-02-20 | NOTIFICATION OF UNUSUAL EVENT DUE TO FIRE IN CONTROL BUILDING "At 0957 EST on February 19, 2020, a Notification of Unusual Event [NOUE] has been determined to be present at the Watts Bar plant Unit 1 under criteria HU4 for a fire potentially degrading the safety of the plant (fire for more than 15 minutes). "The NRC Senior Resident Inspector has been notified for this event." Notified DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 02/19/2020 AT 1151 EST FROM ANDREW WALDMANN TO DONALD NORWOOD * * * The fire was declared extinguished at 1033 EST. The NOUE was terminated at 1126 EST. The investigation into the cause of the fire is in progress. Notified R2DO (Musser), NRR EO (Miller), and IRD MOC (Kennedy). Additionally, notified DHS SWO, FEMA Operations Center, CISA IOCC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * RETRACTION ON 2/20/2020 AT 1453 EST FROM MICHAEL BUTHEY TO RICHARD L. SMITH * * * "Watts Bar Nuclear Plant (WBN) is retracting Event Notice 54531 (NOUE notification) based on the following additional information. "WBN reported a condition that was determined to meet the definition of a FIRE in the plant Emergency Preparedness Implementing Procedures (EPIP) based on indications available to the decision-maker at the time the declaration was made. A fire, without observation of flame, is considered present if large quantities of smoke and heat are observed. "Moderate quantities of smoke were observed coming from an electrical cabinet not required to support safe plant operation. Once Fire Brigade personnel were able to access the affected room, no evidence of flame or significant heat was observed. Plant personnel ultimately determined that an overheated electrical component (transformer) resulted in the smoke. As such, the actual conditions did not meet the EPIP definition of a fire." The NRC Resident Inspector has been notified of this retraction. Notified R2DO (Musser), NRR EO (Miller), and IRD MOC (Kennedy). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2020-02-19
54530 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-02-18 09:15 | 2020-02-18 20:20 | 2020-02-18 | NON-LICENSED SUPERVISORY PERSONNEL VIOLATED FFD POLICY "On February 18, 2020 a non-licensed contractor supervisor violated the station's FFD policy. The employee's unescorted access to South Texas has been terminated. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2020-02-18
54529 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-02-17 17:17 | 2020-02-17 19:23 | 2020-02-17 | NOTIFICATION TO OTHER GOVERNMENT AGENCY "At 1647 CST on 2/17/2020, it was determined that approximately two quarts of hydraulic oil were spilled into the Colorado River during preparation for dredging activities. Cleanup using an oil dispersant and oil booms is underway. The cause of the hydraulic oil spill is under investigation. "The Texas General Land Office was notified at 1717 CST. Additional reports were made to the Texas Commission of Environmental Quality, the Environmental Protection Agency National Response Center, and the Matagorda County Local Emergency Planning Committee. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-02-17
54528 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2020-02-17 08:50 | 2020-02-17 14:51 | 2020-02-17 | TRANSPORT OF POTENTIALLY CONTAMINATED PERSON TO A MEDICAL FACILITY "At 0850 CST, on 2/17/2020, the Control Room was notified of a personnel medical event. The individual was transported to a local hospital via ambulance. At the time of transport, the individual was considered to be potentially contaminated because complete surveys could not be performed prior to transfer. Upon arrival at the hospital, the individual and clothing were surveyed by an accompanying Site Radiation Protection Technician and no contamination was found. "This report is being made pursuant to 10 CFR 50.72(b)(3)(xii). "The NRC Resident Inspector has been notified." The individual was not performing any work related activities at the time of event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2020-02-17
54527 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2020-02-14 14:44 | 2020-02-14 16:37 | 2020-02-14 | AGREEMENT STATE REPORT - MISSING TRITIUM WATCHES The following is a synopsis of an email received from the Maine Radiation Control Program: Fifty-two [self-luminous] watches containing 100 milliCuries each of Tritium were reported as missing or stolen from a shipment delivered to OKO International of Deerfield Beach, Florida. The watches were in transit from Hong Kong to Windsor, Maine. They were part of a shipment of 32 boxes containing a total of 2365 watches. Seven boxes were torn during transport and were re-packaged into five boxes. Upon arrival in Florida, there were 52 watches missing. The brand of watch is reported as an Aragon, with no model or serial number provided yet. Transport was via a common carrier. The licensee reported the theft to the Maine Radiation Control Department at 1444 [EST] on Friday, February 14, 2020. An open investigation is still ongoing with the state of Maine. Maine Incident No.: ME 20-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-02-24
54526 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-02-13 13:45 | 2020-02-14 16:01 | 2020-08-11 | <br><br>EN Revision Imported Date : 8/12/2020<br><br>EN Revision Text: AGREEMENT STATE REPORT - UNDERDOSE OF YTTRIUM-90 DURING TREATMENT "A medical event was reported to the Massachusetts Radiation Control Program on Friday, February 14, 2020. A patient receiving a therapeutic radiation dose to the right lobe of the liver using Y-90 Theraspheres in 2 fractionated doses was intended to receive 135 Grays for each fraction. The patient was administered 45.5 Grays for the first fraction and 129.4 Grays for the second. The first fraction underdosed the right lobe of the liver by greater than 50 percent and differed from the prescribed dose by greater than 0.5 Sv (50 rem) effective dose equivalent. The actual underdose for the first fraction was 8,950 rads. This exceeds the reporting limits of 10 CFR 35.3045(a)(1)(i)(c), 'Report and Notification of a Medical Event,' and 105 CMR 120.594(A)(1)(a)(3). "The licensee is investigating the cause of the event and will be reporting the results to the Massachusetts Radiation Control Program. " * * * UPDATE ON 8/11/2020 AT 1715 EDT FROM SZYMON MUDREWICZ TO BETHANY CECERE * * * "Medical event no. 14-4085 was reported to the Massachusetts Radiation Control Program (hereafter, 'Agency') by Massachusetts General Hospital (hereafter, 'licensee') on 02/14/2020 involving administration of TheraSphere Y-90 microspheres to a patient for liver cancer treatment. The patient was scheduled to receive two doses on 02/13/2020 to the right lobe and segment 4 of the liver; 1.59 GBq and 0.29 GBq, respectively. Administration of both doses went accordingly and no unusual signs were observed by the authorized used conducting the administration. There were no problems with the flow of liquid through the microcatheter, no excessive pressure was needed to push the spheres, no leaks were observed, and there were no visual indicators that spheres were collecting at junctions in the tubing. The RADOS dosimeter, supplied with the delivery system, was reading 0.0 mR/hr at conclusion of each dose delivery indicating minimal residual activity inside the delivery system. After each dose the microcatheter and delivery system tubing are placed in a waste container - for storage to decay - where the dose is measured to calculate the activity of any residual microspheres that were not delivered. The calculations were performed the morning of 02/14/2020 and it was determined that only 0.512 GBq (33.7%) of the first dose was delivered to the target site, whereas as 0.273 GBq (95.9%) of the second was delivered to the target site. These calculations identified a possible occlusion in either the microcatheter or delivery set tubing and also identified a malfunctioning dosimeter. No physiological risk to patient health was identified. "The Agency considers this event closed." Notified R1DO (Gray) and NMSS Events Notification (email) A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-02-24
54525 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2020-02-14 00:25 | 2020-02-14 03:36 | 2020-02-14 | MANUAL REACTOR SCRAM DUE TO RISING CONDENSER BACKPRESSURE "At 0025 EST on February 14, 2020, Susquehanna Steam Electric Station Unit 2 reactor was manually scrammed due to rising Main Condenser backpressure caused by a loss of the Unit 2 Offgas Recombiner. "Unit 2 reactor was being operated at maximum facility output, approximately 98% RTP, when at 0012 EST, Unit 2 Recombiner 0C145 Panel Trouble and 2C198 HWC Panel Trouble alarms were received along with rising Main Condenser backpressure. Initial Main Condenser backpressure was 2.6 in HgA and was rising at approximately 0.3 HgA/min. A Recirc Lim 2 was inserted to lower reactor power and condenser backpressure continued to rise following the reduction in reactor power. A manual scram was inserted at 0025 EST by placing the Mode Switch to Shutdown when condenser backpressure rose to 6 in HgA. All control rods inserted. Reactor water level lowered to -30 inches causing Level 3 (+13 inches) isolation and partial (Division 2) Level 2 (-38 inches) isolation. No ECCS actuations occurred and RCIC initiated. The Operations crew subsequently maintained reactor water level at the normal operating band using Reactor Feed Water. No steam relief valves opened. The Reactor Recirculation Pumps remained in service. "The reactor is currently stable in Mode 3. Investigation into the cause of the loss of Unit 2 recombiner is underway. "The NRC Senior Resident Inspector was notified. A voluntary notification to PEMA and press release will occur." | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-02-14
54524 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-02-13 10:25 | 2020-02-13 17:17 | 2020-02-13 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On February 13, 2020, at 1025 hours [PST], during the performance of the quarterly control rod exercise surveillance test, Shutdown Bank 'B' Group 1 became misaligned greater than 12 steps from its group demand position. In accordance with Technical Specification 3.1.4, 'Rod Group Alignment Limits,' Action D, a Unit 2 shutdown to Mode 3 was commenced at 1233 hours. Investigation into the cause of the rod bank misalignment is in progress. "There is no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 51 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N |  | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2020-02-13
54523 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-02-12 18:00 | 2020-02-12 21:51 | 2020-02-12 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 1800 EST, on February 12, 2020, with Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped due to a turbine trip. The trip was not complex, with all systems responding normally post trip. Because of the reactor trip, the Auxiliary Feedwater (AFW) System actuated as expected due to on ATWS Mitigation System Actuation Circuitry (AMSAC) signal. The AFW pumps started as designed when the valid system actuation was received. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the main condenser using the condenser steam dump valves. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as an 4-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified. "The site remains in a normal electrical lineup." The cause of the turbine trip is under investigation. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-02-12
54522 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-02-11 | 2020-02-12 19:00 | 2020-02-12 | AGREEMENT STATE REPORT - LOST BRACHYTHERAPY SEED The following was received from the state of Arizona via email: "The Department [Arizona Department of Health Services] has received notification from the licensee (Scottsdale Healthcare dba Honorhealth Scottsdale Shea Medical Center) that one brachytherapy seed has been lost. It is assumed that the seed went down the drain of an autopsy table on 02/11/2020. All other seeds are accounted for and stored in the licensee's brachytherapy hot lab. The seed model is Civadot, and the isotope is Palladium-103. The Lot ID from which the seed originated is CSH-201. The calibrated activity of the seed on 12/10/2019 was 0.783 mCi (29.0 MBq). The calculated activity as of 02/12/2020 is 0.058 mCi (2.15 MBq). The Department has requested additional information and continues to investigate the event." Arizona Incident Number: 20-003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-02-20
54521 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-02-11 | 2020-02-11 22:30 | 2020-02-11 | AGREEMENT STATE REPORT - QSA EXPOSURE DEVICE OPEN SHUTTER AND CAP The following information was received from the state of Texas via email: "On February 11, 2020, the Agency [Texas Department of State Health Services] was notified of an event by the licensee's consultant. The consultant stated the licensee had purchased a QSA 880 exposure device containing a 111 Curie iridium - 192 source from a licensee in Houston, Texas. The licensee's Radiation Safety Officer (RSO) picked up the shipment at the common carrier shipping building in Amarillo, Texas and placed [it] in the back of his pickup truck. The RSO then surveyed the package. The RSO found readings of 40 millirem per hour (mR/hr) on three sides, but 400 mR/hr of the fourth side. The RSO confirmed the reading with a second meter. The RSO contacted the consultant and the consultant had the RSO tape a self-reading dosimeter (SRD) to the side of the box with the highest reading and leave it there for 10 minutes. After ten minutes the RSO read the SRD and found it reading 50 millirem. "The RSO contacted the company manager (CM) in Dumas, Texas. The CM brought two additional meters to the common carrier location. New readings were taken and the highest dose rate was now 700 mR/hr. The RSO moved the truck to a remote area at the common carrier facility and placed barriers up. The consultant stated they have contacted the licensee who shipped the device who has provided pictures on how the device was packed for shipment. "The RSO is qualified for source retrieval. It was decided that they would get a power screw driver (to minimize time in the area) and remove the top of the box and inspect the exposure device. "At 2116 CST, the Agency was notified by the licensee that they had open the transportation container and inspected the device. The RSO found that both the shutter and cap were opened. The RSO closed the shutter and cap using a remote handling tool. A dose rate taken after closing the shutter and cap was 40 mR/hr. The licensee is transporting the device to its storage location. "The licensee was instructed to provide dose estimates for any individual who may have been exposed. Additional information will be provided as it is received in accordance with SA300." Exposure received from closure of the door and cap was approximately 3 millirem. Texas Incident Number: 9742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-02-19
54520 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2020-02-11 | 2020-02-11 17:09 | 2020-02-11 | PART 21 REPORT - AMETEK 85-RP2675-01 POWER SUPPLY MOUNTING HARDWARE The following is a synopsis of a Part 21 report received by email: "SUMMARY - AMETEK Solidstate Controls recently discovered a concern with the structural integrity of the 85-RP2675-01 Rack Mounted Power supply. While qualifying a replacement part for an obsolete breaker, the left panel of the power supply came loose after the hardware had sheared during the seismic simulation testing of the qualification. The loss of structural integrity of the power supply led to internal shorting and a premature stoppage of the simulation testing. "PROBLEM - During a seismic event, a structural failure of the power supply enclosure resulting in a loss of output could occur. At this point, it is suspected that the failure is related to a variation in the components that increased strain on the power supply enclosure, and it is indeterminate if there is a widespread deviation. It is also possible that the cause of the failure is attributed to inadequately sized hardware that supports the bottom panel of the power supply. In the current design, there are 3 #10-32 machine screws through each of the side panels that fasten to the bottom panel to support the transformer. "AMETEK is unable to identify the actual structural support of power supplies in the field. In the recent testing performed, no support was provided under the power supply during the testing. If there is support in the end application from the bottom of the power supply, there may not be a structural concern as the connection screws would not be exposed to the same forces. In this instance, the power supply had been exposed to a peak acceleration of approximately 4.8 giga second. It should also be noted that acceptable results have been obtained in previous seismic tests and changes have not been made to the structure of the power supply since its initial design in 1996. "ACTION RECOMMENDED - At this time, there are no actions to take as the evaluation is ongoing. The next step is to determine if the screws are likely to become overstrained with enough seismic force. To do this, AMETEK is repeating the test with two new power supplies. One power supply will not have any changes made to the structure while the second power supply will be enhanced to improve its seismic withstand capabilities. "The enhancement is an increase in the size of the hardware to 1/4 inch bolts that connects the side panels to the bottom panel through 5/16 inch through holes with a nut and washers. In combination, these changes will increase the force required to shear the hardware [and] reduce the force on the bolt itself by allowing some movement to dampen the forces during a seismic event. While AMETEK believes this solution will be suitable, it has not been validated with a follow up seismic simulation test. Additionally, AMETEK is unable to determine the criticality of the applications the power supplies are installed in and if the safety function is required to be maintained during a seismic event, which will determine the need to take corrective actions. "A report of the next seismic test results will follow upon completion as a final evaluation. The current expected date for completion is May, 2020. For questions or clarifications in the meantime, please contact Ethan Salsbury, Quality Director, at 1-614-410-6293." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2020-02-11
54519 | 0 | C&D TECHNOLOGIES, INC. |  |  |  |  | 2020-02-03 | 2020-02-11 17:07 | 2020-02-11 | PART 21 REPORT - CONTAINER FAILURE IN KCR-07 BATTERIES The following is a synopsis of a Part 21 report received by email: "On December 6, 2019, Browns Ferry Nuclear Plant notified C&D of an issue with a KCR-07 battery where a crack had developed in the container wall, and electrolyte levels had dropped below the low-level line. C&D issued a Return Material Authorization to the customer, and the batteries were returned and analyzed. On February 3, 2020, this battery was analyzed, and the cause of the crack was determined to be caused by expansion of the post seals directly stressing the container walls. Although this unit passed capacity testing after return to C&D, undetected loss of electrolyte in field units could impact the operability of KCR-07 systems in the field. Accordingly, C&D is submitting this report to the NRC and notifying C&D's customers that use KCR-07 batteries[, manufactured prior to January 2012,] of this report. "The battery manufacturing date is on the label. "C&D implemented corrective actions to eliminate expansion of the positive post seal and to reinforce cover designs in 2011. Information from laboratory testing and field experience has shown that these corrective actions were effective at eliminating excessive stress in the post seal, cover, and container. "If you have any questions or wish to discuss this matter or this report, please contact: Robert Malley, VP Customer Experience, bmalley@cdtechno.com, (215) 619-7830 [or] Kristen Jamison, Nuclear Applications Engineer, kjamison@cdtechno.com, (215) 775-1306." The following Utilities/Plants are affected: Exelon Fitzpatrick, Exelon Limerick, First Energy Perry, TVA Browns Ferry, TVA Sequoyah, TVA Watts Bar. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-02-11
54518 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-02-11 14:37 | 2020-02-11 16:56 | 2020-02-25 | AGREEMENT STATE REPORT - LOST CS-137 SHIPMENT The following was received from the Commonwealth of Massachusetts by email: "The licensee (QSA Global, Inc.) made [a] telephone notification at 1532 EST on February 11, 2020 to the Agency (Massachusetts Radiation Control Program) that it discovered on same day, February 11, 2020 at 1437 EST, that a shipment destined for Beijing, China, last known to be at the carrier's hub in Memphis, TN, is missing. "The licensee reported that the missing shipment is a Type A, Yellow II labeled package, UN3332, containing a single 62.9 GBq (1.7 Curies), QSA Global, Inc. Model CDC.CY3 cesium-137 gamma gauging sealed source, serial number A3585. "The licensee reported that the package was shipped for export from its facility in Burlington, Massachusetts on February 3, 2020 and that the carrier reported on February 6, 2020 that the package will stay at the carrier's Memphis, TN hub until further notice due to the coronavirus outbreak. "The licensee reported that the shipment is missing in the common carrier's system and that there is the possibility that it went un-manifested to China. The licensee additionally reported that the customer will be contacted and sent a photo to see if they have received the package. "The licensee reported that the consignee is Beijing Shucheng Science and Technology Development Co., Beijing, China under NRC export license PXB11a.03. "The reporting requirement is immediate and is of 105 CMR 120.281(A)(1), missing licensed radioactive materials in aggregate quantity equal to or greater than 1,000 times quantity specified in 105 CMR 120.297, Appendix C. "The Agency considers this event to be open." * * * UPDATE ON 2/25/2020 AT 1406 EST FROM JOSHUA DAEHLER TO BETHANY CECERE * * * The following was received from the Commonwealth of Massachusetts by email: "On February 24, 2020, the Tennessee Division of Radiological Health informed the Agency (Massachusetts Radiation Control Program) that the package was found by the carrier to be at the carrier's hub in Memphis, TN." Notified R1DO (Ferdas), ILTAB, and NMSS Events Notification Group (by email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-02-19
54517 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-02-11 10:07 | 2020-02-11 14:45 | 2020-02-11 | FITNESS-FOR-DUTY REPORT - POLICY VIOLATION "On February 11, 2020, a licensed Senior Reactor Operator violated the station's fitness-for-duty policy. The employee's access to South Texas has been terminated. "The NRC Resident Inspector has been notified." The employee tested positive on a follow-up test for alcohol. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2020-02-11
54516 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-02-22 | 2020-02-07 15:21 | 2020-02-07 | AGREEMENT STATE REPORT - REPORTABLE EQUIPMENT FAILURE The following information was received via E-mail: "A reportable equipment failure occurred on February 22, 2019 at a panoramic irradiator licensee in Libertyville, IL. The equipment failure was not reported to Illinois Emergency Management Agency (IEMA), but identified during a February 6, 2020 routine inspection. The affected equipment has since been repaired and no impacts to health or security were identified. "IEMA inspectors conducted a routine inspection at Isomedix Operations d/b/a Steris, Libertyville location, on February 6, 2020. During a review of licensee files, it was determined that on the evening of February 22, 2019, required safety equipment became disabled as a result of the cell flooding. This is reportable, at a minimum, under 32 Ill. Adm. Code 340.1220c2. Inspection findings indicate that on or about 1817 CST February 22, 2019, a coupler on a 2 inch sprinkler line in the maze of the cell broke during processing. The cell consequently flooded and began to flood the warehouse. An emergency console stop was executed at approximately 1821 CST and both racks submerged. At 1824 CST, the pool high water alarm was tripped. Inspector review of the console event log indicates within the next 80 minutes the smoke detector, exhaust fans, collision bar, inside roof plug, low air pressure, high temperature, main panel communications and loss of 110 VAC and 24VDC faults were logged. "It was also noted that at 2024 CST on February 22, 2019, the source racks were moved back up. At 2024 CST, the deionizer radiation monitor alarmed. A number of alarms and faults continued until approximately 1121 CST on 2/23/19. Reportedly, up to four inches of water covered the pool and the entirety of the warehouse. The fire department was needed to shut off the main feeding the sprinklers. Inspection findings indicate, at a minimum, high and low water monitors as well as the deionizer radiation monitor were disabled due to the wiring being flooded and shorted in the trough. The wiring for multiple components were replaced and plumbers contracted to repair the sprinkler system the following day. The licensee has moved to a manually initiated dry fire suppression system. Dosimetry was evaluated and no unusual exposures noted. Interviews of staff involved indicate security systems were not impacted. Leak tests were performed on February 22, 2019. This incident remains under investigation. "There is no evidence of intentional disruption of safety or security systems." Event Report ID No.: IL200005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-02-17
54515 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-02-07 10:12 | 2020-02-07 14:32 | 2020-02-07 | AGREEMENT STATE REPORT - LOST OR MISSING SOURCE The following is a synopses of the Louisiana Department of Environmental Quality email notification to the NRC: On February 7, 2020 at 1012 EST, the Alpha-Omega Services, Inc., Radiation Safety Officer, contacted the Louisiana Department of Environmental Quality by email to report that a High Dose Rate Ir-192 source cannot be located. The source was in transit to Golden, Colorado and was last located at the Common Carrier hub in Memphis, Tennessee. The source serial number is 02-01-2012-001-012220-11606-02. The current activity of the Ir-192 source is 9.987 Ci. Event Report ID No.: LA20200002 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2020-02-17
54514 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2020-02-02 | 2020-02-07 11:52 | 2020-02-07 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the state of Minnesota via email: "Lu-177 administration was performed on February 4, 2020. The administration team did not start the patient on amino acids prior to the administration. Upon discovery of the error, the acids were started. This resulted in an unintended dose to the kidneys. The Radiation Safety Officer (RSO) and staff were notified on February 5, 2020. They determined it was a medical event on February 7, 2020 at 0930 CST. The event was reported to the Minnesota Department of Health (MDH) at 1000 CST on February 7, 2020. The intended dose to the kidney was 490 Rem. The delivered dose to the kidney was 740 Rem (this was their 'best case scenario' calculation). This would fall under 4731.4525 Subpart 1 Item C.: 'a dose to the skin or an organ or tissue other than the treatment site that exceeds 50 Rem and exceeds 50 percent of the dose expected from the administration defined in the written directive.'" This event is still under investigation with MDH. Minnesota Event Report ID: MN200002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2020-02-17
54513 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2020-02-06 07:15 | 2020-02-07 09:23 | 2020-02-07 | AGREEMENT STATE REPORT - FIXED PROCESS GAUGE SHUTTER MALFUNCTION The following was received from the Commonwealth of Kentucky via email: "The KY RHB [Kentucky Radiation Health Branch] was notified via email on 2/6/2020 (1559 EST) by a representative from specifically licensed facility, Big Rivers Electric Corp., that at 0715 on Thursday, 2/6/2020, one fixed gauging device (Kay Ray Model 7062BP, Serial Number 20086), containing 100 milliCuries Cs-137 (source serial No. 17400V; assay date 10/30/1985) had developed a potential problem while the shutter arm was moving freely. Survey results showed that the shutter remained in the shut position. The gauge is mounted on a pipe, and manned entry is not of concern, and the plant personnel have been notified that there is no access allowed to the affected pipe. All operational and maintenance activities will be delayed until the device has been removed for repair by a service provider. The licensee will be contacting a licensed service provider to remediate this situation. This is being reported under 10 CFR 30.50(b)(2)." Kentucky Event Report ID No.: KY200001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2020-02-17
54512 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2020-02-05 | 2020-02-05 21:55 | 2020-02-05 | AGREEMENT STATE REPORT - LOST GAUGING SOURCE The following was sent by the Illinois Emergency Management Agency (IEMA) via email: "The Corporate H & S Mgr. [Health & Safety Manager] at PepsiCo/Quaker Oats reported the loss of an ATl-100S/500 microCurie [Sr-90] general licensed gauging source (SN 30056). They were doing leak tests this morning and found that the whole packaging unit had been removed presumably by Dudek Scrap during a remodel some time ago. They are checking on dates and will contact the scrap dealer to try and find it. IEMA inspectors plan to investigate on 2/6/20 to confirm details at the user's site and also will visit the scrap yard to see if the source is recoverable. At the moment this is considered an accidental loss due to poor oversight and is not related to any criminal theft or diversion." Item Number: IL200004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2020-02-13
54511 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-02-04 | 2020-02-05 09:31 | 2020-02-05 | AGREEMENT STATE REPORT - BRACHYTHERAPY SOURCE FAILED TO RETRACT The following information was received from the state of Texas via email: "The Methodist Hospital reported a source retraction failure during an intravascular Brachytherapy treatment performed on 2/4/2020. The intravascular brachytherapy system (Best Vascular Model A-1000 Serial #89670) contained a 1.3 GBq (35.2 mCi) Sr-90 source (AEA Model SICW.2 Serial #ZA925). The patient was treated as prescribed and the source was completely out of the patient. As it was retracting into the device, it didn't go into home position. The device was immediately placed in the emergency equipment box (shielding box) per manufacturer's instructions for response to this type of occurrence. There was no underexposure or overexposure to the patient. The manufacturer has been contacted to investigate and conduct repairs. Additional information in accordance with SA-300 will be provided." Texas Incident No.: 9739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-02-13
54510 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2020-01-29 | 2020-02-03 13:42 | 2020-02-03 | AGREEMENT STATE REPORT - INCORRECT ORGAN RECEIVED TREATMENT The following was received from the South Carolina Department of Health and Environmental Control via email: "The South Carolina Department of Health and Environmental Control was notified on 02/03/2020 of a potential medical event involving a prostate seed implant. The procedure occurred on 01/29/2020, and the licensee's radiation safety officer was notified of the potential medical event on 02/03/2020. The prescribed dose to the prostate was 145 Gray, with 76 seeds being implanted. Total activity of the seeds is being reported as 26.6 milliCuries. The licensee is reporting that the seeds were implanted into the bladder and not the prostate. As of 01/31/2020, 41 seeds of the implanted 76 seeds were still implanted in the patient. The licensee is also reporting the loss of 35 seeds. The prostate seed manufacturer is ISOAID, LLC ADVANTAGE I-125. The model of the seeds is IAI-125A. This event is still under investigation by the licensee and the South Carolina Department of Health and Environmental Control." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. Notified R1DO (Henrion) and NMSS Events (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2020-02-11
54509 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2020-02-03 09:15 | 2020-02-03 09:16 | 2020-02-03 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO PLANNED TSC AND OSC UPGRADES "At 0915 EST on February 3, 2020, planned upgrades to the Technical Support Center (TSC) and Operations Support Center (OSC) will begin. The work includes upgrades to furniture, carpet, telecommunications, celling tiles, and HVAC vent covers and the installation of new Audio-Visual equipment to include monitors, speakers, and microphones. The work duration is approximately eight weeks. "If an emergency is declared requiring TSC and OSC activation during this period, the TSC and OSC will be staffed and activated at the alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the TSC and OSC planned upgrades and the need to assemble and staff the alternate location during an emergency. "This is an eight-hour, non-emergency notification for a planned loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "There is no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-02-03
54508 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2020-02-01 18:45 | 2020-02-01 23:06 | 2020-02-01 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO CONTAINMENT PURGE VALVE EXCESSIVE LEAKAGE At 1845 CST on 2/1/2020, during surveillance testing (STS PE-015, Containment Purge Valve Leakage Test) containment leakage in excess of Technical Specification requirements was observed. A Technical Specification required shutdown was initiated at 2030 CST and Mode 3 was achieved at 2154 CST. All systems functioned as required during and following shutdown. The unit is proceeding to Mode 5. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2020-02-01
54507 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2020-02-01 11:50 | 2020-02-01 16:29 | 2020-03-16 | LOW PRESSURE CORE SPRAY INOPERABLE "At 1150 EST on 2/1/2020, it was discovered that the Low Pressure Core Spray System was inoperable due to a divisional battery voltage being out-of-specification. Therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). The Low Pressure Core Spray is a single train safety system in Modes 1, 2, and 3. Low Pressure Core Spray was restored to operable, restoring function at 1230 on 2/1/2020. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 03/16/2020 AT 1156 EDT FROM JOHN NAKEL TO BETHANY CECERE * * * "On February 01, 2020, event notification (EN-54507) was made to the NRC for Low Pressure Core Spray (LPCS) inoperability. This notification was made due to high DC bus voltages resulting in LPCS being declared inoperable which resulted in a loss of safety function. "An Engineering Evaluation Request (EER) was performed to determine an upper limit for DC bus voltage. This EER determined that LPCS could perform its required functions with a voltage increase of up to 150V DC if the duration was not greater than two hours. "The elevated voltage was experienced for approximately 59 minutes. The maximum voltage experienced was 147.07V DC. Therefore, LPCS remained operable and no loss of safety function existed. "The NRC Resident Inspector has been briefed on the evaluation results and informed of this retraction." Notified R3DO (Hanna). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-02-01
54506 | 0 | FAIRBANKS MORSE |  |  |  |  | 2020-01-31 | 2020-01-31 16:32 | 2020-01-31 | Part 21 - UNKNOWN TIGHTNESS OF CAM THRUST LOCK NUT ASSEMBLY The following information is a summary of information received via facsimile: On January 31, 2020, Fairbanks Morse (FM) submitted information of a defect or failure of the unknown tightness of the opposed piston (OP) diesel engine cam thrust lock washer and lock nut assembly for emergency diesel generators (EDGs). FM assembled and completed a factory acceptance test on a 1000 rpm new opposed piston diesel engine generator set. Upon post-test inspection it was discovered that the lock nut and lock washer had fallen off of the camshaft. The failure did not prevent the engine from starting, accelerating to rated speed as well as accepting and sustaining rated load. The failure does not result in an immediate engine shutdown or load rejection. The timing chain restrains the camshaft adequately for the engine to perform its emergency function. However, it cannot be concluded that the engine would continue to operate for the entire duration of its safety function. This Part 21 notification is being issued for subject engines with less than 98 hours of operation since the camshaft lock nut assembly was tightened. This Part 21 notification is being applied only to engines with less than 98 operating hours since the cam lock nut assembly was tightened for the following two reasons: 1) There are no known occurrences of cam lock nut assembly failures on any 900 rpm FM OP engines. All FM OP engines in service as EDGs in the United States are 900 rpm and 2) A laboratory analysis of the failed components conclusively shows this failure is an infant mortality. In the event the cam lock nut is loose, the lock washer will fail very quickly upon engine operation. FM has defined the appropriate tightening value to the cam lock nut assembly in Service Information Letter SIL-40 and has provided this guidance to all licensees that possess FM OP engines. FM has updated all internal engineering specifications and manufacturing instructions to include the newly specified tightening requirements. There are no 10 CFR 50 Appendix B FM OP engines being newly constructed. A list of affected customers are: Exelon - Peach Bottom Nuclear Generating Station and Southern Nuclear / Georgia Power - Hatch Nuclear Power Plant FM Notification Report Serial Number 20-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-01-31
54505 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-01-31 | 2020-01-31 15:35 | 2020-01-31 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE RUN OVER BY VEHICLE The following information was received via E-mail: "The Department [Arizona Department of Health Services] received notification from the licensee that a technician had backed up over a portable moisture density gauge with their truck. The gauge is a Troxler 3430, Serial Number 35062, containing approximately 8 milliCuries of cesium-137 and 40 milliCuries of americium-241:beryllium. The Department has requested additional information and continues to investigate the event. Arizona Incident: 20-002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-02-10
54504 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2020-01-31 | 2020-01-31 14:56 | 2020-02-03 | GAMMA ALARM FIXED RADIATION PORTAL MONITOR The following was received from the state of Florida Bureau of Radiation Control via fax: "[Customs and Border Protection] CBP called the [Bureau of Radiation Control Incident Response Center] BRC IRC to report that at 1105 EST, CBP had a gamma alarm from a fixed radiation portal monitor for a 20 ft. sea container manifested as containing PVC Leather, Buckles, and Grommets. A CBP officer inspected the container using a RadSeeker DL RIID (1.5x1.5in LaBr3). The RIID identified Th-232, and this was confirmed manually by CBP lab personnel using PeakEasy gamma spectroscopy software. The highest reported dose rate was 103 microR/hr at contact with the sea container (1034 cps at contact); this is approximately 9-10 times the average background dose rate for this location. The radiation was distributed throughout the entire length of the container. Guidance requested as to whether or not CBP should refuse entry on the shipment, or if it is acceptable to release it into commerce. There are concerns as to whether or not this product may contain one-twentieth of one percent (0.05 percent) or more by weight of Th-232, violate other radiological regulations, or pose additional concerns." Notified R1DO (Henrion), NMSS Events (email), OIP Notifications Resource (email) Florida Incident Number: FL20-011 * * * UPDATE ON 2/3/20 AT 1400 EST FROM MATTHEW SENISON TO KERBY SCALES * * * "This morning between 0800 and 0900 EST, [BRC IRC] inspector went to the Blount Island Marine Terminal in Jacksonville, FL to inspect a container that US Customs and Border Protection had identified as having higher than background levels of radiation. The container was opened for [the inspector], and [the inspector] found the items in the container did match the information that was reported to the Bureau of Radiation Control (BRC). Specifically, spools of faux-leather, and boxes that contained plastic grommets and buckles. These items were manufactured or assembled in China for delivery to a pool cover supply company in Apopka, FL. The boxes did not contain radiation levels above background. The spools of faux-leather had slightly higher than background levels of radiation when unrolled. Their spindles were made of cardboard and did not have higher than background levels of radiation. When the faux-leather was rolled up, the radioactivity increased. "The BRC has given the guidance that the container and its contents may be released, but this has not happened yet. If it is released, the BRC is of the opinion that the intended recipient should be surveyed for radiation, in case this is a common occurrence." Notified R1DO (Henrion), NMSS Events (email), and OIP Notifications Resource (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-02-10
54503 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2020-01-31 05:55 | 2020-01-31 09:46 | 2020-01-31 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 0555 [EST], on January 31, 2020, James A. FitzPatrick was at 38 percent power when an automatic scram occurred as a result of a main turbine trip on high Reactor Pressure Vessel (RPV) water level. The plant was at reduced power in preparation for maintenance activities. The 'A' Reactor Feed Pump (RFP) was being removed from service when a perturbation in reactor water level reached the high RPV water level setpoint. This resulted in a main turbine trip and 'B' RFP trip. "The automatic scram inserted all control rods. A subsequent low water level resulted in a successful Group 2 isolation. The plant is stable in Mode 3 with the 'B' RFP maintaining RPV water level. The initiation of the reactor protection systems (RPS) due to the automatic scram signal at critical power is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The general containment Group 2 isolations are reportable per 10 CFR 50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector, and the State and Local government for the scram. Decay heat is being removed via the main condenser. | 0 | 0 | 0 | 38 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-01-31
54502 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-01-30 11:45 | 2020-01-30 17:15 | 2020-02-03 | FITNESS-FOR-DUTY - CONTRACTOR SUPERVISOR VIOLATED THE FFD POLICY On January 30, 2020, a non-licensed contractor supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's unescorted access to the plant has been terminated. The NRC Resident Inspector has been notified. * * * UPDATE ON 2/3/2020 AT 1223 EST FROM WILLIAM HERZOG TO BETHANY CECERE * * * The initial NRC report wording was incorrect. Specifically, the non-licensed supervisory personnel violated the fitness for duty policy, they did not have a confirmed positive for-cause fitness-for-duty test. The title of this event is corrected. Notified R4DO (Taylor) and FFD Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2020-01-30
54501 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2020-01-29 | 2020-01-30 16:04 | 2020-01-30 | AGREEMENT STATE REPORT - STOLEN SOURCE The following report was received from the Arizona Department of Health Services (Department) via email: "The Department received notification from the licensee that they reported their RMD XRF Lead-Based Paint Analyzer, serial number 1115, stolen on January 29, 2020. The analyzer possesses approximately 1 milliCurie of Co-57. The licensee shipped the equipment to Protec Instrument Corporation in Waltham, MA for resourcing. It was received by Protec Instruments on September 11, 2019. Since that date, the licensee stated that they have not heard from the company and have called and left messages for months with no response. "The licensee contacted their equipment insurance company to process a claim and were told that they would need to report the equipment stolen. They reported the equipment stolen to the Flagstaff Police Department and the report number is P20-01171. The Department has requested additional information and continues to investigate the event." Arizona Incident: 20-001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2020-02-07
54500 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2020-01-29 | 2020-01-29 17:30 | 2020-01-29 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS This is a summary of information received from the state of Nebraska via a phone call: On 1/29/2020, the licensee notified Nebraska that they are currently unable to locate 31 tritium exit signs. The tritium exit signs have all been replaced by LED signs, but management has been unable to locate the disposal records and are considering the signs lost at this time. 29 of the signs contain approximately 9.21 Ci of tritium each and 2 of the signs contain approximately 7.09 Ci of tritium each. Nebraska incident number: NE200002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-02-06
54499 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-01-29 | 2020-01-29 16:38 | 2020-01-29 | TEXAS AGREEMENT STATE REPORT - CONTAMINATION EVENT RESULTING IN RESTRICTED ACCESS The following is a summary of information obtained from the state of Texas via email: On January 28, 2020, the licensee notified the Agency [Texas Department of State Health Services], that it had discovered a load of soil containing Radium-228, collected during remediation/decommissioning activities for another licensee, had been taken to the municipal landfill in error. The soil was taken to the landfill on January 15, 2020, and was identified by the licensee on January 24, 2020. The error was identified while processing sample reports and other paperwork. A sample indicated the material had a concentration of 776 picoCuries of Radium-228 per gram. The Agency has confirmed the material does not pose a risk of becoming an uncontrolled contamination event, because it is in a cell at the landfill with clean soil covering it. The area has been cordoned off and the material does not pose a risk of exposure to any individual. The licensee has coordinated with the landfill to go onsite February 3, 2020, to take surveys and get information to develop a plan to recover the material so it can be properly disposed of. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300. Texas Incident No.: 9736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-02-06
54498 | 0 | CHRISTIANA CARE |  |  |  |  | 2020-01-28 | 2020-01-29 15:28 | 2020-01-29 | RADIATION DOSE TO A FETUS On January 9, 2020, a patient received Lu-177 treatment. The dose prescribed was 203.5 milliCuries. On January 28, 2020, the Authorized User was informed by the patient's physician that the patient was pregnant at the time of treatment. The Authorized User informed the patient. The initial dose to the fetus was calculated to be 143 milligray (14.3 rem). The licensee has hired a consultant to determine if the calculated dose is correct. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 35.3047(a) |  |  |  | 0 | 2020-02-06
54497 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-01-29 | 2020-01-29 14:31 | 2020-01-30 | AGREEMENT STATE REPORT - STOLEN NUCLEAR DENSITY GAUGE The following was received from the Pennsylvania Bureau of Radiation Protection (the Department) via email: "On January 29, 2020, the licensee informed the Department that one of their vehicles, with a nuclear density gauge in the trunk, was stolen earlier that day. The licensee has filed a police report. The Department has been in contact with the licensee and will update this event as soon as more information is provided." The gauge is a CPN International, Model MC-1 DR-P (Serial Number: M7077803), with a 10 mCi Cs-137 source and a 50 mCi Am-241/Be source. PA Event Report ID No.: PA200002 * * * UPDATE ON 1/30/2020 AT 1346 EST FROM JOHN CHIPPO TO ANDREW WAUGH * * * The following was received from the Pennsylvania Bureau of Radiation Protection (the Department) via email: "At approximately 2250 EST on January 29, 2020 the licensee informed the Department the stolen car had been recovered with the gauge still padlocked in the trunk of the car and secured with a padlocked chain. The employee had started his car and then returned to his house to get his lunch, and the car was stolen during this time." Notified R1DO (Henrion), NMSS Events (email), ILTAB (email), and CNSC (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2020-02-06
54496 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2020-01-28 07:05 | 2020-01-28 08:01 | 2020-01-29 | SECURITY BARRIER PENETRATION "Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector." * * * RETRACTION ON 1/29/2020 AT 1527 EST FROM CHRIS TERRY TO ANDREW WAUGH * * * The licensee is retracting this event, because they determined that it does not meet the reporting requirements of 10 CFR 73 Appendix G. Notified R2DO (Baptist) via phone and IR MOC (Gott), ILTAB, NMSS Events, Fuels Group, and 73.71 Safeguards Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2020-01-28
54495 | -1 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2020-01-26 23:54 | 2020-01-27 09:29 | 2020-01-29 | INADVERTENT ACTIVATION OF AN EARLY WARNING SIREN "At 2354 EST, on January 26, 2020, officials with the State Emergency Operations Center and Newberry County, SC were notified of an apparent inadvertent actuation of a single siren in the VC Summer Early Warning Siren System (EWSS). "[VC Summer Nuclear Station] VCSNS received a report of siren actuation from a local resident at approximately 2340 EST. The EWSS indication at the Emergency Operations Facility showed siren #35 had actuated. A reset of the EWSS was performed. VCSNS is working to confirm actual siren activation and troubleshoot the issue. This event is still under investigation. "This is a non-emergency notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." The Licensee notified state and local agencies. * * * RETRACTION ON 1/29/2020 AT 1502 EST FROM HANK KIRKLAND TO ANDREW WAUGH * * * "The investigation of this event has concluded that EWSS siren #35 did not actuate. This conclusion was reached after interviewing residents who reside directly across the street from EWSS Siren #35, who confirmed that this siren did not actuate. Also, maintenance personnel investigations concluded that the local activation indication was erroneous, due to observed battery readings being normal. Had the siren actuated, its batteries would have been depleted or nearly depleted." The NRC Resident Inspector has been notified. Notified R2DO (Baptist). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2020-01-27
54494 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2020-01-24 13:24 | 2020-01-24 17:50 | 2020-01-24 | AGREEMENT STATE REPORT - FIXED GAUGE DAMAGED The following summary was received from the Oregon Public Health Division via phone: The licensee reported that the handle of a fixed gauge used as a level indicator broke off. The device contains Cs-137 and the shutter is in the closed position. The device will not be used until it is repaired by an authorized party. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2020-02-03
54493 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2020-01-21 10:15 | 2020-01-23 21:32 | 2020-01-23 | AGREEMENT STATE REPORT - FOUND SOURCE The following is a synopses of a report received from the Utah Department of Environmental Quality (the Division) via email: On January 21, 2020, a licensee left a message for the Division that a source had been found lying outside of the locked gate of one of the licensee's facilities. The licensee reported that it was not their source, but they moved it inside of their facility in order to secure the source and keep a member of the public from finding it. The licensee did not have much information regarding the source when staff spoke with them, but sent a picture of the source that was found. The picture showed a small can labeled with a Beckman Instruments, Inc. label. The label stated that the can contained 40 microcuries of Cs-137 assayed on July 30, 1981. The label was consistent with a generally licensed source and appeared to have been manufactured in CA. The licensee did not know where the source came from or why it was deposited close to their entrance gate. A member of the Division's staff will go to the licensee's facility tomorrow to read the serial number and the full label from the can. Utah Event Report ID #: UT200001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2020-01-31
54492 | -1 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2020-01-22 16:23 | 2020-01-22 19:00 | 2020-01-27 | REQUIRED PROCEDURAL CONTROLS WERE NOT FOLLOWED "Urenco USA is conservatively reporting a condition in that Uranic bearing material was placed into the Small Component Decontamination Train (SCDT) without meeting all conditions of IROFS54a and IROFS54b. "IROFS54a and IROFS54b are Mass Controls that ensure the configuration of the SCDT remains sub-critical. Bookkeeping elements of the IROFS were performed correctly and the masses of the components were determined properly. However the visual inspection of the SCDT to ensure it is empty, prior to introducing components, was not performed in accordance with procedure instructions. "The components were removed and the visual inspection was performed which confirmed the SCDT was in fact empty. "The facility was and remains in a safe and stable configuration." The licensee will notify NRC Region 2 tomorrow. * * * RETRACTION ON 1/24/20 AT 1130 EST FROM BLAKE BIXENMAN TO RODNEY CLAGG * * * "This event was determined to not be reportable. "Consistent with NRC FCSS ISG-12, Rev 1, 10 CFR Part 70, Appendix A - Reportable Safety Events, UUSA has concluded that EN54492 was not reportable. All situations where IROFS have failed or degraded are reportable under Paragraphs (a)(4) or (b)(2), exceptions include the following: The capabilities of the degraded IROFS are still sufficient to meet the performance requirements of 10 CFR 70.61. "On 01-17-2020, UUSA completed a discharge of material to the slab tanks in the Liquid Effluent Collection Treatment & Storage (LECTS) Room. Upon completion of decontamination activities in the SCDT, procedurally required actions were performed to ensure all in process uranic material was removed and verification of the uranic material hold-up value was still valid in accordance with IROFS54a&b. IROFS54a&b tags and locks were then installed indicating the IROFS functions had been performed. "On 01-22-2020, a new work evolution began which included bookkeeping measurements to ensure the calculated mass of uranium was below the allowable threshold prior to introduction to the SCDT. In summary, all requirements of the IROFS54a&b boundary were functionally complete and the capabilities of the degraded IROFS remained sufficient to meet the performance requirements of 10 CFR 70.61." Notified the R2DO (Coovert) and NMSS Events Notification (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2020-01-22
54491 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2020-01-21 20:05 | 2020-01-22 17:50 | 2020-01-22 | FITNESS FOR DUTY (FFD) ISSUE INVOLVING CONTRACT PERSONNEL "At 2005 EST on January 21, 2020, Hatch Security was informed that a contract worker covered by 10 CFR 26.719(b) had been involved in a legal action as defined in 10 CFR 26.5. The contract worker's plant access has been suspended." The NRC Resident Inspector has been notified. | 90 | 100 | 0 | 90 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2020-01-22
54490 | -1 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2020-01-22 | 2020-01-22 17:46 | 2020-01-23 | AGREEMENT STATE REPORT - MISSING SELF LUMINOUS SIGNS CONTAINING TRITIUM The following was received via phone notification from the State of Nebraska Department of Radiological Health (NDRH): On January 22, 2020, the NDRH received notification in the mail that during the annual survey, the Gateway Mall identified that 2 self luminous signs were missing and 7 signs that were removed during construction were unaccounted for. These signs contained tritium (H3), originally in the amount of 11.5 Curies each. NDRH is going to follow-up on this event. * * * UPDATE ON 1/23/2020 AT 1032 EST FROM DEB WILSON TO ANDREW WAUGH * * * It was identified that eight of the tritium signs contained 11.5 Curies each and one of the signs contained 20 Curies. The Gateway Mall will follow up with the construction company to verify whether the signs have been properly disposed of as well as double checking with the maintenance shop to see if the report of the missing signs had been made in error. Notified R4DO (Silvia), ILTAB (email), and NMSS Events (email). * * * RETRACTION ON 1/23/2020 AT 1434 EST FROM DEB WILSON TO THOMAS KENDZIA * * * "Gateway Mall General Manager was able to contact the construction company. It was determined that the signs had been removed from service by the construction company and stored at Gateway Mall. Signs reported missing in the maintenance shop were located as well. All nine signs have been located and accounted for." Notified R4DO (Silvia), ILTAB (email), and NMSS Events (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2020-01-30
54489 | 0 | TILDEN MINING COMPANY |  |  |  |  | 2020-01-22 12:19 | 2020-01-22 12:19 | 2020-01-22 | GAUGE SHUTTER STUCK OPEN During biannual inventory/shutter check maintenance the licensee identified a gauge shutter stuck open on the 6A pebble mill cyclone underflow. The gauge is a Kay Ray Model #7050, Serial #1397 containing 1000 milllicurie of Cs 137. The issue is not a risk to personnel. The licensee will replace the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-01-30
54488 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2020-01-22 07:06 | 2020-01-22 08:59 | 2020-01-22 | SAFEGUARDS REPORT - CONTRABAND IN THE PROTECTED AREA Actual introduction of contraband into protected area. The licensee notified the NRC Resident Inspector. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2020-01-22
54487 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2020-01-21 22:18 | 2020-01-22 04:34 | 2020-02-20 | CONTAINMENT RELIEF VALVES INOPERABLE "At 22:18 (EST) on 1/21/20, it was discovered that all Unit 1 containment vacuum relief isolation valves were closed and all vacuum relief lines were simultaneously inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). The isolation valves were opened and the vacuum relief valves were restored to operable. "There is no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." * * * UPDATE ON 02/20/2020 AT 1626 EST FROM FRANK SCHULTE TO BRIAN P. SMITH * * * "At 1549 (EST), February 20, 2020, a completed engineering evaluation of the condition initially reported on January 22, 2020 determined that the inoperability of the Sequoyah Unit 1 Containment Vacuum Relief System affected the ability to protect containment against an external pressure event. This condition is not bounded by existing design and licensing documents; however, it poses no impact to the health and safety of the public or plant personnel. The condition was resolved when isolation valves were opened on January 21, 2020 and the vacuum relief lines were restored to an operable status. Therefore, this event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(B), "an unanalyzed condition that significantly degrades plant safety." "Subsequent to the initial notification, continued evaluation of the reported condition has concluded that the isolation of the containment vacuum relief function did not prevent the fulfillment of a safety function that is needed to control the release of radioactive material; nor mitigate the consequences of an accident therefore this event is not reportable under 10 CFR 50.72(b)(3)(v), "Event or Condition that could have prevented fulfillment of a safety function. "The NRC Resident has been notified." Notified R2DO (Musser) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2020-01-22
54486 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-01-21 | 2020-01-21 19:03 | 2020-01-21 | TEXAS AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the state of Texas via email: "On January 21, 2020, the licensee notified the Agency [Texas Department of State Health Services], that one of its company trucks with one of its moisture/density gauges had been stolen from its facility. The technician had pulled the truck into the licensee's yard (fenced area but gate open) and pulled up to the building. He turned off the truck, but left the keys in it, while he took a test sample inside the building. The licensee's video surveillance shows an individual walked into the yard and stole the truck which had a Troxler model 3440 moisture/density gauge in the bed. The gauge has a lock on the insertion rod. The gauge is inside its transport case which has a lock. The transport case is inside a metal box that is bolted in the bed of the pickup that also has a lock. However, the keys to these locks are on the same key ring as the truck ignition key. The licensee immediately notified the local police department who responded to the facility and is investigating. An investigation into this event is ongoing. "More information will be provided as it is obtained in accordance with SA-300. "Gauge info: Troxler 3440 SN: 27798 Sources: Am-241/Be: 40 mCi, SN: 479223; Cs-137: 8 mCi, SN: 750-9353" Texas Incident No. I-9734 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-01-29
54485 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2020-01-21 | 2020-01-21 16:12 | 2020-01-21 | PART 21 REPORT - TARGET ROCK 1" and 2" FAIL CLOSED SOLENOID OPERATED VALVE ASSEMBLIES UNAUTHORIZED MODIFICATION DURING ASSEMBLY The following was received via email: "Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply. "Condition 1 (Modified Fixed Core) "The purpose of the fixed core is to provide the proper amount of magnetic pull force between itself and the plunger when the solenoid coil is energized. The fixed core is installed within the bonnet assembly and "fixed" in place by a "dimpling" process which captures a machined groove on the fixed core. During Assembly & Testing of a TR Solenoid Operated Valve, a fixed core unexpectedly came out of the bonnet assembly. Further inspections of the fixed core revealed unauthorized modification to the part beyond its design basis to force installation into the bonnet assembly. In the event a modified fixed core was to dislodge from its location within the bonnet, the specific valve assembly would fail to operate to the open position when the solenoid is energized and would remain in its fail safe closed position. "Condition 2 (Main Disc Lift Misadjustment): "The objective of the disc lift adjustment is to ensure the main disc is in contact with the bonnet base, which provides an "up stop" position while maintaining a minimum clearance between the plunger and the fixed core. Excessive clearance between the plunger and the fixed core reduces the available magnetic force. Conversely, improper adjustment, allowing contact between the plunger and the fixed core, may cause impact damage to the assembly during full pressure/temperature actuation and reduces the maximum flow (Cv) through the valve assembly. It was noted that a disc lift adjustment was not adjusted properly and would reduce the maximum flow. "The date on which the information of such defect or failure to comply was obtained. "Condition 1 (Modified Fixed Core): "During the investigation of the suspect technician, TR identified conditions, which required independent inquiry and subsequently confirmed intentional modification of the fixed core. On December 5, 2019, TR Engineering confirmed the condition. "Condition 2 (Main Disc Lift Misadjustment): "On November 22, 2019, TR Engineering performed a worst case Cv calculation to determine the amount of restricted flow that would result in the event a 1" y-body valve assembly was short stroked. This would reduce the flow of a 1" y-body valve assembly from a rated Cv of 15 to approximately a Cv of 14. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "Condition 1 (Modified Fixed Core): "The discrepant bonnet assembly/fixed core was documented on a NCR (Non Conformance Report) and scrapped. A new bonnet assembly was issued to the valve kit. The valve assembly was reassembled, retested and successfully passed all required production testing. This was an unauthorized modification performed by a single individual (suspect technician). Four additional A& T technicians involved in the bonnet dimpling process were interviewed. All four technicians stated they have never intentionally modified components nor have they ever seen anyone intentionally modifying components in any form. TR investigation considers this to be isolated to the suspect technician. The suspect technician no longer works for the company. "Condition 2 (Main Disc Lift Misadjustment): "The initial valve assembly was readjusted in accordance with the applicable technical manual and solenoid valve adjustment procedure. The valve assembly was re-tested per the applicable production test procedure and successfully passed all required testing. Upon further investigation of valves assembled by the suspect technician, an additional 3 of 10 valve assemblies were verified to have misadjusted main disc lift. The misadjusted valves were readjusted, tested and successfully passed all production testing prior to shipment. All technicians working on solenoid valve assemblies were given an individual technician qualification exam to determine their understanding of this adjustment in accordance with the existing work instructions. Each technician was tested individually, with Engineering present as a witness. All technicians demonstrated a clear understanding and followed the necessary instructions/procedures to properly adjust the disc lift. TR determined the suspect technician did not follow the official work instructions for the disc lift adjustment in an effort to save time during this process. TR investigation concludes this defect is isolated to the suspect technician. The suspect technician no longer works for the company. This was the same technician involved in Condition 1. "Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "Condition 1 (Modified Fixed Core): "TR performs production testing on all valve assemblies prior to shipment. TR considers this testing adequate screening to identify this condition at the factory. Satisfactory testing provides reasonable assurance the stated condition does not exist in shipped product. However, TR recommends un-installed bonnet assemblies and complete valve assemblies be returned to TR for re-inspection. This condition potentially affects valve models and bonnet assemblies detailed in Attachment 1 manufactured between 1/1/2018 and 10/31/2019. Any installed valves containing these parts should be reviewed and evaluated for history of operational testing anomalies. Many of these installed valves are subject to regular plant testing, such as 1 OCFR50 Appendix J. Satisfactory performance in this testing will provide reasonable assurance of an acceptable valve condition. "Condition 2 (Main Disc Lift Misadjustment): "All un-installed Valve Assemblies should be checked to determine if a misadjustment of the main disc lift exists. Although the process to check for a misadjusted valve is not difficult, it requires partial valve disassembly. The instructions for proper adjustment are located in the valve specific Technical Manual. Any 1" Y-body solenoid valve assemblies that have been installed should be reviewed and evaluated by each end user regarding the acceptability of having a lower flow (Cv) rating of 14 in lieu of 15 for the specific system in which they are installed. Any opportunity to disassemble the valve assembly for inspection and readjustment is recommended. This condition potentially affects valve models detailed in Attachment 1 manufactured between 7/1/2015 and 10/31/2019. "Should you have any questions regarding this matter, please contact Michael Cinque, General Manager at (631) 293-3800 Very Truly Yours, Michael Cinque General Manager Target Rock, Business Unit of Curtiss-Wright Flow Control Corporation" Affected sites are Arkansas Nuclear One, Beaver Valley, Brunswick, Calvert Cliffs, Farley, Fitzpatrick, Hope Creek, Millstone, Nine Mile Point, Oconee, Palo Verde, Sequoyah, Shearon Harris, St. Lucie, South Texas Project, Vogtle, Watts Bar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 1 | 2020-01-21
54484 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2019-12-18 22:15 | 2020-01-17 17:00 | 2020-01-17 | NORTH DAKOTA AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information is summarized from an email received from the state of North Dakota: At approximately 2215 MST on 12/18/2019, while setting up for a radiography shot, the radiography team experienced a source disconnect. When the team realized a disconnect occurred, they established a 2 mR/hr. boundary and contacted the radiation safety officer (RSO). The RSO arrived on site and was able to retrieve the source back into the shielded position. No overexposures were reported. The licensee removed the camera from service and returned it to their facility in Bismarck, ND. The licensee determined that poor camera maintenance and personnel error contributed to the guide tube being only partially connected to the camera which led to the disconnect. The radiography crew was briefed on the cause of the event and the proper steps to maintain and inspect a camera prior to use. The camera was a SPEC 150, serial number 2592 , with a 66 Ci Ir-192 source, serial number AK 2405. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2020-01-27
54483 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2020-01-16 14:45 | 2020-01-17 11:57 | 2020-01-17 | ALABAMA AGREEMENT STATE REPORT - PATIENT RECEIVED GREATER DOSE THAN PRESCRIBED The following information was received from the state of Alabama via facsimile: "On January 16, 2020 at approximately 1445 CST, [the radiation safety officer (RSO)] of Alabama licensee East Alabama Medical Center notified the Alabama Office of Radiation Control [the Agency] that a patient apparently received more dose than prescribed during a treatment via HDR [high dose rate] afterloader on or around Thursday, 1/9/2020. [The RSO] stated that he noted the matter yesterday (1/15/20 at around 1530); he stated that the physician associated with the patient's case confirmed [the RSO's] concerns about the patient's dose. [The RSO] reported that the patient apparently received dose in 1 fraction that was to be administered over 2-3 fractions. The Agency has no further information on this matter as of the date of submission of this memo. "Of note, East Alabama Medical Center is authorized to possess and use an Elekta Flexitron model 136149A02 HDR medical irradiator under Alabama license 105, with a maximum of 12 Ci of Ir-192." Alabama Event 20-01 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2020-01-27
54482 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-01-15 | 2020-01-16 14:47 | 2020-01-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following was received from the Texas Department of State Health Services (the Agency) via email: "On January 16, 2020, the Agency was notified by a licensee of a source disconnect event. The licensee stated that on January 15, 2020, a crew using a QSA Spec-150 camera with 76 Curies of iridium-192 were unable to retract the source back into the camera. The source was recovered and returned to the shielded position. The licensee suspects that the source was not properly connected to the drive cable, allowing the source to be pushed inside the guide tube but unable to retract it. The licensee stated that the individuals that performed the recovery received 50 mR to 60 mR of exposure, and that no overexposures are suspected as a result of the event. Investigation is ongoing. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-01-24
54481 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2020-01-15 | 2020-01-15 16:16 | 2020-01-15 | AGREEMENT STATE REPORT - STUCK PROCESS GAUGE SHUTTER The following information was received via E-mail: "On January 15, 2020, at 1400 CST, the DOW Chemical Radiation Safety Officer contacted the supervisor of the Louisiana Department of Environmental Quality/ERSD/Radiation Section to report that a shutter failed to shut during routine maintenance. The shutter which failed to shut was found on January 14, 2020, at approximately 1500 CST, at DOW Chemicals Company. The shutter is stuck in the open condition and does not effect operation. The gauge is a Vega Americas model number SHF2B, s/n 38953125, with a 500 mCi Cs-137 sealed source, s/n 0368CR. The licensee has contacted the contractor for repair and is awaiting a date and time for the repair." Event Report ID No.: LA20200001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2020-01-23
54480 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2020-01-15 08:00 | 2020-01-15 16:18 | 2020-01-15 | SHERRY COOKING WINE FOUND IN PROTECTED AREA "In response to Event notification Report 54473, submitted by BWXT NFS [Nuclear Fuel Services] (SNM-124), BWXT NOG-L [Nuclear Operations Group - Lynchburg] conducted an extent of condition review of the onsite cafeteria. The review resulted in the discovery of two (2) bottles of sherry cooking wine with an identified alcohol content of 17 percent. The items were discovered in the BWXT NOG-L cafeteria located within the Protected Area (PA). Upon discovery, the items remained in the control of NOG-L FFD [Fitness for Duty] Program Personnel, until they were removed from the protected area and disposed of accordingly. There are no indications that the items were used for personal consumption. One bottle was sealed, and the unsealed bottle was being utilized for cooking purposes. Neither container displayed the FDA alcohol warning statement on the label nor is sherry cooking wine regulated under Virginia ABC laws as an alcoholic beverage. The NOG-L Security Department has entered the incident into the Corrective Action System (C/A: 202000063)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 1 | 2020-01-23
54479 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2020-01-14 | 2020-01-15 11:42 | 2020-01-15 | AGREEMENT STATE REPORT - Cs-137 SOURCE FOUND AT A SCRAP YARD The following information was received via E-mail: "An unknown device was discovered at a metal scrap yard in Ohio. The device has no markings or labels. A Cs-137 source of unknown activity was identified in the device. No loose contamination was detected. Maximum dose rate on the device is 500 mr/hr and 6 mr/hr at one meter. The device is secure at the facility pending disposal. The Ohio Department of Health will continue to track down the origin of the source." Ohio Item Number: OH200001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2020-01-23
54478 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2020-01-14 12:45 | 2020-01-14 17:56 | 2020-01-15 | AGREEMENT STATE REPORT - LOST CATEGORY 1 SHIPMENT The following summary was initially reported by the Massachusetts Department of Public Health (DEP) and subsequently reported by the Tennessee Department of Environment and Conservation (DEC), both via phone: The MA DEP was notified by QSA Global, Inc. that a shipping container containing 12,400 Ci of Ir-192 did not arrive at their facility as expected. The original shipment had six (6) containers but only five (5) arrived at the Burlington, MA location. The last known location of the missing container was at the [Common Carrier] facility in Memphis, TN. QSA Global was in the process of notifying local law enforcement in Tennessee. Massachusetts DPH does not believe this event to be a theft or diversion. Additionally, TN DEC was notified by [the Common Carrier] of the missing container and that a search was in progress. Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, CISA IOCC, EPA Emergency Ops Center, FDA Emergency Ops Center (email), DHS Nuclear SSA (email), FEMA NWC (email), FEMA NRCC SASC (email), and DNDO-JAC (email). * * * UPDATE ON 1/15/2020 AT 1035 EST FROM SZYMON MUDREWICZ TO THOMAS KENDZIA * * * The following was reported by the Massachusetts Department of Public Health (DEP) via phone and email: "At 1015 EST this morning, MA DEP was notified [by QSA Global] that the package was located by [the Common Carrier] in Memphis, TN last evening. It has been delivered to Burlington this morning, not damaged, and is in the possession of the Licensee, QSA Global, in Burlington, MA. MA DEP will continue to investigate the event." Notified R1DO (Dentel), NMSS DDD (Williams), IRDM (Grant), ILTAB (Pearson), ILTAB (email), NMSS DAY (Rivera-Capella), INES (Milligan), NMSS Event Notification (email), NMSSDHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, CISA IOCC, EPA Emergency Ops Center, FDA Emergency Ops Center (email), DHS Nuclear SSA (email), FEMA NWC (email), FEMA NRCC SASC (email), and DNDO-JAC (email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 1" LEVEL OF RADIOACTIVE MATERIAL Category 1 sources, if not safely managed or securely protected would be likely to cause permanent injury to a person who handled them, or were otherwise in contact with them, for more than a few minutes. It would probably be fatal to be close to this amount of unshielded material for a period of a few minutes to an hour. These sources are typically used in practices such as radiothermal generators, irradiators and radiation teletherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2020-01-22
54477 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-08-20 | 2020-01-14 15:52 | 2020-01-14 | AGREEMENT STATE - LESS THAN PRESCRIBED DOSE RECEIVED The following was received from the State of Kentucky via e-mail: "The University of Kentucky reported that a patient received less dose than prescribed on 8/20/2019. The patient was prescribed to receive 429.2 MBq (11.6 mCi) of Y-90 microspheres (Sirtex Medical model SIR- Spheres). A microsphere dose of 425.5 MBq (11.5 mCi) was drawn from the unit vial into the administration vial. However, the patient only received an activity of 316.72 MBq (8.56 mCi), which is 26.2 percent less than prescribed, because some microspheres remained in the administration system. Additionally, it was difficult to draw 429.2 MBq (11.6 mCi) from the 7.13 GBq (192.6 mCi) in the unit vial as it represented only a small portion of the whole. The patient and referring physician were notified. Corrective actions included ordering a dose calibrated to more closely provide the activity needed for the date and time of administration. If the activity to be administered is low, the university will ensure that the activity drawn is 10 percent greater than prescribed. More flushes of the system will also be performed in hopes of pushing more of the residual activity into the patient." Kentucky Incident Number - 190008. NMED Item Number - 190442 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2020-01-22
54476 | 0 | UNITED CONTROLS INTERNATIONAL |  |  |  |  | 2019-12-27 | 2020-01-14 10:37 | 2020-01-14 | PART 21 - INCORRECT TIP MATERIAL USED ON GAUGES On December 27, 2019, United Controls International received a Product Advisory Letter from Ashcroft Inc. dated December 2, 2019 informing of a potential error in the tip material used on Ashcroft 2 « inch and 3 « inch model 1009, 63 mm model 2008, 63 mm and 100 mm model 1008 industrial gauges along with Weksler 3 « inch regal gauges. Due to a supplier issue, 304SS tip material may have been supplied on the subject gauges instead of the specified 316SS material. In certain applications the 304SS tip material may be subject to accelerated oxidation or degradation, resulting in potential release of process media. However, no detrimental effects are expected in non-corrosive applications. Hatch and Farley have been identified as the affected plants and have been notified of this issue. Please contact Wesley Hickle, Engineering Manager, at (770) 496-1406 ext. 165 or whickle@unitedcontrols.com for any questions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-01-14
54475 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2020-01-12 | 2020-01-13 17:47 | 2020-01-13 | AGREEMENT STATE - FIXED GAUGE STUCK SHUTTER The following was received from the agreement state via e-mail: "On January 13, 2020, a licensee reported to the Agency that on January 12, 2020, it had discovered a shutter on a fixed nuclear gauge was stuck in the open position, which is the normal operating position for the gauge. The device is a Ronan SA-1 containing 5 milliCuries of Cs-137. The licensee stated that there is no concern of overexposures due to this equipment malfunction. A service company has been onsite and plans to remove the gauge on January 17, 2020. At that time, a decision will be made whether to repair or replace the gauge. An investigation into this event is ongoing and more information will be provided as it is obtained in accordance with SA-300." Source: Cesium-137, 5 milliCuries (original activity 10/07/1996), SN: 2263GQ, manufactured by Amersham Texas Incident 9731. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2020-01-21
54474 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2020-01-13 10:13 | 2020-01-13 15:08 | 2020-01-13 | NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed contract employee supervisor tested positive for alcohol at another facility. The employee's access to Fermi 2 has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2020-01-13
54473 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2020-01-13 | 2020-01-13 15:05 | 2020-01-13 | ALCOHOL DISCOVERED IN CAFETERIA "Six bottles of flavoring extracts (rum, peppermint, lemon, and almond) containing varying amounts of alcohol content (12 -84 percent) were located in the NFS onsite cafeteria. The items were turned over to NFS Security for control and disposition as necessary. NFS Security and the Plant Superintendent conducted an additional search of the cafeteria and did not identify any additional items. There was no indication that the items had been utilized for consumption by any onsite personnel. A problem was entered in the site Problem Identification Resolution Correction System (PIRCS) for reference (P78223)." The cafeteria is located inside the protected area. The event was terminated at 1200 EST. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.719 |  |  |  | 0 | 2020-01-21
54472 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-01-13 09:10 | 2020-01-13 09:17 | 2020-01-13 | PLANNED TECHNICAL SUPPORT CENTER POWER MODIFICATION "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "A planned modification to the Technical Support Center (TSC) power supplies started on January 13, 2020. The work activity includes installation of a permanent back-up diesel generator and rewiring of automatic and manual power transfer switches. The work duration is approximately three weeks. "If an emergency is declared requiring TSC activation during this period, the Emergency Coordinator and the TSC staff will assemble and staff the alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the TSC modification and the need to assemble and staff the alternate location during an emergency. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-01-13
54471 | 0 | CARRIER CORPORATION |  |  |  |  | 2020-01-10 | 2020-01-10 13:44 | 2020-03-09 | PART 21 - FAILED OIL PUMP DUE TO IMPROPER MOTOR ASSEMBLY The following was received via facsimile: "Duke Energy via Mr. James M. Smith issued a letter to Carrier Corporation's Customer Service Organization on November 21, 2019 reporting that on November 4, 2019, a Carrier 17FA999-1200-107 Oil Pump (Duke Energy UTC Number 30110654) failed rendering one train of the Control Room Area Chilled Water System inoperable. A failure investigation by Duke Energy representatives determined that the oil pump, which had been in service for less than two months, had a broken shaft and failed due to improperly assembled oil pump motor assembly. The failed oil pump and a replacement (spare) oil pump in the warehouse (Duke Energy UTC Number 30078287) both had loose fasteners and unstaked alignment pins. "Prior to Duke Energy's November 21, 2019 notice, Carrier issued a corrective action to their supplier on April 28, 2017 to address failures with a different non-safety related oil pump (Carrier Model 17FA512- 968) at a non-nuclear facility. The corrective action applied to all 17FA oil pump assemblies supplied to Carrier after April 28, 2017, including both safety and non-safety related oil pumps. The corrective action consisted of cleaning of threaded holes and application of red Loctite, ensuring specified torque requirements are met using a calibrated digital torque wrench, and verifying the staking operation. Both oil pump issues described by Duke Energy in the November 21, 2019 notice concerned oil pumps built prior to the April 28, 2017 corrective action. Carrier is not aware of reports of any other defects in pumps in the same series in either nuclear or non-nuclear applications built since the corrective action. "Carrier will provide a final report to the U.S. Nuclear Regulatory Commission no later than March 11, 2020. If you have questions regarding this matter, please contact the undersigned." David Kwasigroch, Associate Director of Engineering, (315) 432-3461, dave.kwasigroch@carrier.com. This issue affects McGuire Nuclear Station. * * * UPDATE ON 3/9/20 AT 1102 EDT FROM DAVID KWASIGROCH TO BETHANY CECERE * * * The following is a synopsis of the additional information in the final report, as received via fax: "Carrier issued a corrective action to our supplier on April 28, 2017 to address failures with a different non-safety related oil pump (Carrier Model 17FA5l2-968) at a non-nuclear facility. The corrective action was applied to all 17FA oil pump assemblies supplied to Carrier after April 28, 2017, including both safety and non-safety related oil pumps. The corrective action consisted of cleaning of threaded holes and application of red Loctite, ensuring specified torque requirements are met using a calibrated digital torque wrench, and verifying the staking operation. "Additional design modifications are being implemented, which consist of: adding an additional set screw with Nylok Patch into the motor housing to secure the stator, installing pressed in dowel pins to hold the pump cover and pump housing together, and the addition of lock tab washers with TorQ-Patch cover bolts to keep the bolts more secure. "Carrier's records indicate that four affected pumps were supplied to three nuclear facilities: the two pumps that were the subject of Duke Energy's notice; one pump supplied to Dominion Energy, Inc.; and one pump supplied to Susquehanna Nuclear, LLC. Carrier mailed letters to the three nuclear facilities on March 5, 2020, to coordinate replacement of the affected pumps. It is not known whether the pumps supplied to Dominion Energy, Inc., or Susquehanna Nuclear, LLC were improperly assembled." Notified R1DO (Finney), R2DO (Davis), and Part 21/50.55 Reactors Group (by email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2020-01-10
54470 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2020-01-09 11:32 | 2020-01-09 19:25 | 2020-01-09 | LOSS OF CHILLERS "The Division I Control Building Chiller 'A' failed to start during post maintenance testing. By design, the Division II Control Building Chiller 'B' should have started automatically but did not. Operators then manually placed the Division I Control Building Chiller 'C' in service. "This condition rendered both Divisions of the Control Building Air Conditioning System Inoperable. The applicable LCO was entered and exited 10 minutes later with all required actions and completion times met. The cause of the failure is not known at this time. The plant was at 100% power at the time of the event and is currently stable at 100% power." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2020-01-09
54469 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2019-12-30 | 2020-01-09 12:50 | 2020-02-06 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE COULDN'T BE RETRACTED The following was received from the Agreement State via e-mail: "RSO reported inability to retract a 40.2 Ci Ir-192 source (Source Model A424-9), (Source Serial No. 89706G) into the Sentinel/QSA 880 Delta exposure device (Serial No. D12297) during the period of 12/31/2019 to 1/1/2020. "Licensee notified of 24 hour reporting requirement and to send written 30-day report." Mississippi report number: MS-200001. * * * UPDATE ON 02/06/2020 AT 1321 EST FROM ROBERT SIMS TO BETHANY CECERE * * * The state of Mississippi sent the following update by email: "[State Health Physicists] investigated the inability to retract the source, and the RSO reported that corrosion inside the crank cables caused the cable to hang up. The crew followed their emergency procedures and called the RSO. The RSO retracted the source into the fully shielded position and OSL [optically stimulated luminescence] badges were processed showing that no over exposure occurred, and the occupation exposure limits were maintained in compliance." Notified R4DO (Taylor) and NMSS Events Group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2020-01-17
54468 | 0 | VT DEPARTMENT OF HEALTH |  |  |  |  | 2019-11-27 | 2020-01-09 07:33 | 2020-01-09 | AGREEMENT STATE REPORT - IODINE-125 PROSTATE IMPLANT SEED The following is a synopsis of a report from the Vermont (VT) Department of Health (the Department): On November 27, 2019, a prostate seed implant (PSI) procedure using Iodine-125 (I-125) seeds was performed. During the latter part of the procedure, while loading one last, extra needle for the radiation oncologist (the Authorized User), the authorized medical physicist (AMP) lost control of one I-125 seed. A number of surveys were conducted immediately following the loss of the seed, producing only background readings. On December 4, 2019, a Department Senior Radiological Health Specialist conducted a follow-up survey in the PSI procedure room and waste storage areas. The lost seed was not located. As a corrective action, the licensee may consider ordering additional seeds in the form of preloaded needles to avoid handling individual prostate seeds. The lost prostate seed is believed to have fallen into the bore of the implanting needle and was subsequently implanted into the prostate. This is not believed to have any clinical significance on the resulting absorbed dose to the prostate, urethra, or rectum. The patient had 76 prostate seeds planned to be implanted and a single extra seed would result in approximately 1 percent additional absorbed dose to the treatment volume. As verification, a post-implant treatment plan was calculated with an extra prostate seed placed near the location of the last needle within the treatment volume. The resulting dose metrics confirmed that absorbed doses increased by about 1 percent. The potential radiation exposure to an individual that is continuously present near the lost seed was evaluated and determined to be less than the 0.1 rem annual public exposure limit. No personnel contamination occurred as a result of this event. VT Incident Number: VT19-002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VT | OTH | AGR |  |  |  |  | 0 | 2020-01-17
54467 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2020-01-08 | 2020-01-08 16:44 | 2020-01-08 | PART 21 - INADEQUATE SELENIUM SURGE SUPPRESSOR THREAD MODIFICATION The following is a summary of information that was received via facsimile: On November 14, 2019, Engine Systems, Inc. obtained information of a defect or failure to comply associated with selenium surge suppressors. Three batches of suppressors supplied by Engine Services, Inc. between 2011 and 2013 utilize a thread modification that is inadequate for the application. The design specifies the use of a single 1/4-20 x 2-3/4" long bolt to compress the stack of selenium cells as well as mount the suppressor. Contrary to this requirement, the manufacturer used a #8-32 screw through the body of the stack and added a modified bolt to obtain the required 1/4-20 mounting threads. The modified bolt consisted of a 1/4-20 x 5/8" long bolt that was drilled and tapped in the head to accept #8-32 threads. An attempt to install the selenium surge suppressor by tightening the corresponding mounting nut may result in failure of the modified bolt threads. Use of this thread modifier significantly reduces the strength of the mounting threads. Failure of the mounting threads creates the possibility of the suppressor dislodging with the potential to electrically short between the positive and negative plates of the rectifier assembly. An electrical short would affect output of the voltage regulator system, which may prevent the emergency diesel generator set from performing its safety-related function. This issue is therefore considered to be a reportable defect as defined by 10 CFR Part 21. The affected part number is 8403049. A list of affected customers include: Point Beach Nuclear Plant and Surry Power Station. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2020-01-08
54466 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2020-01-07 18:55 | 2020-01-08 02:49 | 2020-01-08 | LOSS OF SEISMIC ASSESSMENT INSTRUMENTATION "On January 7, 2020, Columbia Generating Station (CGS) experienced an equipment failure that resulted in a loss of the seismic assessment instrumentation. This is being reported as a major loss of emergency assessment capability in accordance with regulation 10 CFR 50.72(b)(3)(xiii). No other plant systems were affected. "Compensatory measures have been implemented and will remain in place until the seismic system has been restored. "The NRC resident has been notified." Licensee received a design basis earthquake alarm, but no other local indication of seismic activity, nor on the U.S. Geological Survey website. Licensee compensatory measures include local readings on seismic instrumentation. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2020-01-08
54465 | -1 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2020-01-07 13:41 | 2020-01-07 19:09 | 2020-01-23 | CHILL WATER SYSTEM INOPERABLE "At 1341[EST], on 01/07/20, it was discovered all trains of the Chilled Water System were simultaneously Inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D). During this event, the Bravo train chiller was operating in a maintenance run and the temporary chiller was available and placed in service promptly to restore the safety function. "The control room area cooling safety function was restored at time 1435 [EST] when one required train was declared Operable. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 1/23/2020 AT 1718 EST FROM JERRY COLLIER TO THOMAS KENDZIA * * * "The purpose of this notification is to retract a previous report made on January 7, 2020, at 1909 EST (EN#54465). A subsequent evaluation determined that the Bravo train chiller, which was running at the time of the event, would be able to perform its safety function and was operable at the time of the event. Therefore, there was no loss of safety function. "The NRC Senior Resident Inspector has been notified." Notified R2DO (Coovert). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2020-01-07
54464 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2020-01-07 | 2020-01-07 13:11 | 2020-01-07 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following was received from the State of Colorado via email: "On January 7, 2020, DBI, Inc. reported a source disconnect for an industrial radiography source. The disconnect occurred on the first exposure of the day. The radiographer and assistant extended their boundaries and were able to restrict access at the location. The radiation safety officer was contacted and was successfully able to recover the source into a shielded container. The industrial radiography device was a QSA 880 delta and the source was an Ir-192 source with approximately 42 Curies. "An onsite investigation will be scheduled in the future." Event Report ID No.: CO200001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2020-01-15
54463 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2020-01-04 11:09 | 2020-01-04 15:00 | 2020-01-04 | PRIMARY CONTAINMENT DEGRADED "At 1109 [EST] on 01/04/2020, it was determined that the primary containment leakage rate did not meet value La, defined in 10 CFR 50, Appendix J, 'Primary Reactor Containment Leakage Testing for Water-Cooled Power Reactors'. An additional, tested valve has been closed to maintain leakage below maximum allowable leakage, La. This event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2020-01-04
54462 | 0 | BAYER CROPSCIENCE |  |  |  |  | 2020-01-02 | 2020-01-03 13:15 | 2020-01-03 | STUCK OPEN PROCESS GAUGE SHUTTER On 1/2/2020, it was discovered that the shutter on a centrifuge process level gauge was stuck in the open position. The gauge is a Berthold model LB7442F, serial number 6005 containing a 3000 mCi Cs-137 source. The source serial number is 5559GN. The shutter is normally open during process operation and closed during maintenance. Red tape and plywood have been erected in order to prevent inadvertent personnel entry into the area. No over-exposures have occurred. A Berthold representative should be on-site next week to repair the shutter. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2020-01-13
54461 | 0 | ALLIANCE HEALTH SERVICES |  |  |  |  | 2020-01-02 07:00 | 2020-01-02 13:47 | 2020-01-02 | UNPLANNED CONTAMINATION ON PET CT SCANNER MOBILE UNIT The following is a summary of information received from Alliance Health Services (Alliance) via the phone: At approximately 0800 CST on January 2, 2020, a mobile PET CT scanner unit was received by Alliance from CardioNavix at the Henry Ford Medical Center in West Bloomfield, MI with rubidium-82 contamination on the top exterior surface of the generator cart. The initial wipes on the surface of the generator cart were 17,697 dpm and 112,368 dpm (2 different areas of the top of the cart). No other contamination was found. The contaminated generator cart is located inside the mobile unit with limited access. The unit has not been used since the discovery of contamination. No personnel were contaminated. The licensee notified CardioNavix and the unit will be picked up by CardioNavix later today. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2020-01-10
54460 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2020-01-01 12:53 | 2020-01-01 16:57 | 2020-01-01 | MANUAL REACTOR TRIP AND SPECIFIED SYSTEM ACTUATION "At 1253 [CST] Unit 2 Reactor was manually tripped due to a trip of both Main Feed Pumps. During an evolution to secure Circulating Water Pump 2-01, vacuum was reduced in the auxiliary condensers for both Main Feed Pumps causing both Main Feed Pumps to trip. Both Motor Driven and the Turbine Driven Auxiliary Feedwater Pumps started due to steam generator Lo-Lo levels. "Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-0078. The Emergency Response Guideline Network has been exited. Decay heat is being rejected to the Main Condenser via the Steam Dump Valves." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2020-01-01
54459 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-12-31 16:45 | 2019-12-31 18:00 | 2019-12-31 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL DELIVERED TO WRONG ADDRESS The following information is a summary obtained from the Commonwealth of Massachusetts via email and telephone conversation: "A single package containing eight Iridium-192 sources was bound for Canada, but was delivered to Kaiser Permanente Medical Center in Honolulu, Hawaii. A person at the hospital contacted QSA Global's distribution manager and notified them of the mis-shipment and that the shipment was unopened and secured at their facility. The reason for the mis-shipment is not known at this time. The shipping company and Commonwealth of Massachusetts have initiated an investigation and the licensee is arranging for delivery of the shipment to its intended destination." Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | HI | OTH | AGR |  |  |  |  | 0 | 2020-01-08
54458 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-12-30 | 2019-12-30 17:26 | 2019-12-30 | AGREEMENT STATE REPORT - UNACCOUNTED MATERIAL The following is a summary received from the Florida Bureau of Radiation Control via email: The now closed Christ Medical Center facility is involved in bankruptcy and other litigation. The Florida Bureau of Radiation Control could not remove the radioactive material from the facility until assets were settled. The facility is now in contract for purchase. The real estate agent stated that he would open the facility for the Florida Bureau of Radiation inspector to review and determine if the five devices containing radiological material are still present. The Florida Bureau of Radiation inspector will inspect the facility and take custody of the sources. Florida Incident Number: FL19-155 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2020-01-07
54457 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2019-12-27 07:04 | 2019-12-27 07:53 | 2019-12-27 | MANUAL TRIP DUE TO FEEDWATER PUMP TRIP This is a synopsis of initial information received via phone: On December 27, 2019, at 0705 EST, while Unit 2 was at 100 percent (Mode 1), the 'A' Main Feedwater Pump tripped due to an unknown cause. The reactor was manually tripped and is currently at zero (0) percent power (Mode 3). Decay heat is being removed via Auxiliary Feedwater. The 'B' Feedwater pump is operable. There was no impact on Unit 3. The licensee notified the NRC Resident Inspector. Additionally, Connecticut Department of Environmental Protection, Waterford Dispatch, and East Lyme Emergency Management Division will be notified. * * * UPDATE ON 12/27/2019 AT 1330 EST FROM JASON PARIS TO CATY NOLAN * * * "This is an update to NRC Event Number 54457. "At 0704 EST, on 12/27/2019, with Millstone Unit 2 operating at 100 percent power, operators inserted a manual reactor trip. The trip was initiated due to a trip of the 'A' Main Feedwater Pump. "The Auxiliary Feedwater System (AFW) automatically actuated as required. "All control and shutdown rods fully inserted. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the transient. Unit 2 is currently stable at normal operating pressure and temperature in Mode 3, Hot Standby. Reactor Coolant System (RCS) temperature is being maintained by the steam dump system with all Reactor Coolant Pumps (RCPs) in service. Main Feedwater has been secured, and Auxiliary Feedwater is in service. The electrical system is in normal alignment. "There was no impact on Unit 3. There was no impact to the health and safety of the public or plant personnel. "Due to Reactor Protection System (RPS) actuation while critical, this event was reported as a four hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B); and an eight hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in a valid actuation of the AFW system." The licensee will notify the NRC Resident Inspector of the update. Notified R1DO (Cherubini). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-12-27
54456 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-12-20 | 2019-12-23 14:19 | 2019-12-23 | AGREEMENT STATE REPORT - THREE GAUGE SHUTTERS INOPERABLE The following was received via email from the state of Texas: "On December 23, 2019, the licensee notified the Agency [Texas Department of State Health Services] that late, after hours, on December 20, 2019, it had discovered during routine gauge inspections that the shutters on three (3) of their Berthold Model LB 7440 gauges were inoperable. The shutters are in the open position which is the normal operating position for the gauges. Two of the gauges contain 100 milliCuries of cesium-137 each and the third contains 10 milliCuries of cesium-137. Due to their location, there is no increased risk of exposure to any persons. The licensee is in the process of scheduling repairs. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." TX Incident # 9729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-12-31
54455 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-12-20 | 2019-12-23 13:49 | 2019-12-23 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following is a synopsis of an email from the state of Florida: On December 20th, 2019, a patient was prescribed and administered a yttrium-90 treatment. The patient received 25 percent of the prescribed dose as reported by the Radiation Safety Officer (RSO) to the Florida Bureau of Radiation Control on December 23. Further details, including actual prescription amounts, are awaiting a submitted report by the hospital's Interventional Radiology Department. FL Incident Number: FL19-154 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-12-31
54454 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-10-21 | 2019-12-20 12:20 | 2019-12-20 | AGREEMENT STATE REPORT - TWO LOST Po-210 IONIZERS The following was received from the New York State Department of Health (NYSDOH) via fax: "On October 22, 2019, the Department [New York State Department of Health] was notified by e-mail of two lost static elimination devices, NRD, LLC Model P-2042 1000 'Nuclespot Ionizer', S/N A2LL994 and A2LC660. The devices has a maximum activity of 5 millicuries of Polonium-210 at the time of manufacture. Based on the information provided to the Department, the activity of the device on October 21, 2019 (date of discovery) would be approximately 0.8 and 0.14 millicuries, respectfully. "The licensee [Buffalo Pharmacies] indicated that the devices had not been used in quite some time and that the facility at which the devices were used had recently closed. Between the lack of use and the closing of the facility, the devices has been deemed lost." EVENT REPORT ID NO.: NYDOH-19-10 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-12-30
54453 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-12-19 21:21 | 2019-12-20 06:43 | 2019-12-20 | TECHNICAL SPECIFICATION DEVIATION "On December 19, 2019, at 2121 CST, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to a seized servomotor on the regulating blade drive mechanism during reactor operation. This notification is required per MURR Technical Specification (TS) 6.6.c(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by TS 1.1, had occurred. MURR was not in compliance with all Limiting Conditions for Operations (LCOs), specifically TS 3.2.a, which states, 'All control blades, including the regulating blade, shall be operable during reactor operation.' The regulating blade drive mechanism was removed, a new motor installed, and then the regulating blade drive mechanism was reinstalled and all its functions were tested satisfactorily. Permission from the Reactor Facility Director was obtained per TS 6.6.c(4) prior to starting up the reactor later on December 20. "A detailed event report will follow within 14 days as required by TS 6.6.c(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2019-12-20
54452 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-12-18 09:08 | 2019-12-18 15:27 | 2019-12-18 | SECONDARY CONTAINMENT PRESSURE DEGRADED "On December 18, 2019, at 0908 EST, with the East and Center Reactor Building HVAC (RBHVAC) trains in service, secondary containment pressure degraded to the point where the Technical Specification (TS) requirement for secondary containment pressure was not met and secondary containment was declared inoperable. Secondary containment pressure did not meet the TS required limit for approximately four minutes. The maximum secondary containment pressure observed during that time was approximately 0.064 inches of vacuum water gauge. "Secondary containment pressure was returned to within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) by starting Division 1 of the Standby Gas Treatment System (SGTS). Secondary containment was declared Operable at 0912 EST. A modulating damper associated with the Center train of RBHVAC was identified as not properly controlling; an investigation is in progress. RBHVAC was manually secured to support problem identification and resolution. Secondary containment pressure is currently stable with Division 1 SGTS in service. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-12-18
54451 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2016-12-05 | 2019-12-18 12:20 | 2019-12-20 | AGREEMENT STATE REPORT - TWO LOST Po-210 IONIZERS The following was received from the New York State Department of Health (NYSDOH) via fax: "NYSDOH was notified in writing by an administrator for Emagin Corporation on December 18, 2019 (letter dated December 5, 2019), that two Nuclecel In-Line Ionizers had been lost and unable to be located at the licensee's facility in Hopewell Junction, New York. "These two devices are NRD, LLC P-2021 ionizers. Both devices contain sealed Po-210 sources with 10 mCi per device (assayed at the time of production). The device serial numbers are A2JY966 with source s/n 057171, and A2HM243 with source s/n 047955. Both sources are believed to be decayed down to greater than 14 half-lives to date. "According to the licensee, these sources were identified as lost during periodic housecleaning of their facility clean room approximately three years ago. The licensee attempted to locate the devices at that time and continues to attempt to locate the devices. The licensee also states that NRD, LLC verified that the devices in question were not returned to their facility. "NYSDOH will continue to monitor this incident under NYSDOH Incident No. 1312. The licensee will be providing additional information on the event, corrective actions, and steps to prevent recurrence in the future." EVENT REPORT ID NO.: NY-19-11 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-12-26
54450 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-12-17 14:50 | 2019-12-17 22:42 | 2019-12-18 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following was received from the Florida Department of Health via email: "[The Radiation Safety Officer (RSO)] reported an incident involving a damaged Troxler Soil Moisture Density Gauge. The 2 sources [Cs-137 (8 mCi); Am-Be (40 mCi)] were not damaged or dislodged. The only damage was to the operator handle. At approximately [1450 EST], the gauge was bumped by a bulldozer [at a temporary work site in Ocala, FL], damaging the handle. The gauge is repairable. [The RSO] will follow-up his initial report with a written report on Wednesday, December 18, 2019. No further action is required." Event Incident Number: FL19-151 * * * UPDATE ON 12/18/2019 AT 1110 EST FROM MATTHEW SENISON TO ANDREW WAUGH * * * The following was received from the Florida Department of Health via email: The sources are currently in the licensee's possession. The State will dispatch an inspector for this incident and pictures of the gauge, a leak test, and a report including corrective actions taken to prevent re-occurrence will be required. Notified R1DO (Werkheiser) and NMSS Events (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-12-25
54449 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2019-12-17 19:29 | 2019-12-17 21:10 | 2019-12-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN At 1929 EST, on 12/17/19, Millstone Unit 3 began preparations for shutting down the reactor as the 'A' Emergency Diesel Generator (EDG) could not be restored to operable status within the 14-day outage time, requiring a Technical Specification (Tech Spec) shutdown. Per Tech Spec 3.8.1.1., the reactor must be in Hot Standby in six (6) hours, and Cold Shutdown within the following 30 hours. Hot Standby is estimated by midnight, and Cold Shutdown by 1800 EST on 12/18/19. All other safety and shutdown systems are operable. Decay heat removal will be through the Shut Down Cooling and Residual Heat Removal systems. There was no impact to Unit 2. There was no impact to the health and safety of the public or plant personnel. The licensee notified the state of Connecticut, Waterford County, and the NRC Resident Inspector. | 0 | 0 | 25 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2019-12-17
54448 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-12-13 | 2019-12-17 10:44 | 2020-01-09 | AGREEMENT STATE REPORT - HIGH DOSE RATE APPLICATOR DISLODGED The following was received from the PA Department Bureau of Radiation Protection (DEP) via fax: "On December 16, 2019, the medical physicist for the licensee verbally reported that during an HDR [high dose rate] treatment using a Varian Model VariSource IX with a Tandem & Ovoid applicator, the applicator was found dislodged at the end of the treatment period. This was fraction 4 of 5 planned fractions. It is unknown at this time how long the applicator was not in the planned position or what caused it to move. The prescribed dose was 600 cGy from a 5.126 Ci Iridium-192 source. No further information is available at this time. The DEP will update this event as soon as more information is provided." Event Report ID No: PA190029 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE ON 1/9/20 AT 1:17 PM FROM JOHN CHIPPO TO KARL DIEDERICH * * * The following information was received from the Agreement State via fax: "The patient was seen on 12/27/2019, 12/30/2019, and 1/6/2020 for follow-up appointments. Observed skin effects were described as 'moist desquamation' due to the applicator being dislodged from the vaginal canal and positioned against the skin. The patient is being treated with Silvadene topical cream and will be followed up with regular skin checks. Based on the evidence observed, the licensee assumes that the applicator was against the skin long enough to deliver a skin dose in the range of 10-30 Gy. This dose makes the event a potential Abnormal Occurrence. The Department has performed a reactive inspection and continues to investigate the event." Notified R1DO (Schroeder) and NMSS group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-12-25
54447 | -1 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2019-12-16 17:35 | 2019-12-16 20:27 | 2019-12-17 | SAFEGUARDS REPORT The actual or attempted introduction of contraband into a protected area, material access area, vital area, or transport. The individual's access has been suspended. * * * RETRACTION ON 12/17/19 AT 0917 EST FROM WYATT PADGETT TO CATY NOLAN * * * "This event was determined to not be a reportable event. "The event was reported under 10 CFR 73 Appendix G I(d): The actual or attempted introduction of contraband into a protected area, material access area, vital area, or transport. "UUSA [Urenco USA] falls under the provisions of 10 CFR 73.67, 'Licensee possessing special nuclear material of low strategic significance.' (Category III Facility) "In accordance with 10 CFR 73.71 (b)(1), UUSA shall notify the NRC Operations Center within 1 hour of discovery of the safeguards events described in paragraph I(a)(1) of appendix G and is not required to report events described in I(a)(2), (a)(3), (b), and (c) of appendix G or safeguards events described in paragraph 1(d) of appendix G to Part 73." Notified R2DO (Bonser), and NMSS Events and Part 73 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2019-12-16
54446 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-12-16 03:58 | 2019-12-16 09:12 | 2019-12-16 | EMERGENCY DIESEL GENERATOR AUTOSTART DUE TO LOSS OF POWER TO 1B SHUTDOWN BOARD "At 0358 EST, on 12/16/2019, with Unit 1 in Mode 1 at 100 [percent] power and Unit 2 in Mode 1 at 47 [percent] power, a valid actuation of the Emergency Diesel Generators (EDG) occurred. The reason for the emergency diesel generator auto start was that the normal feeder breaker from the 1C 6.9KV Unit Board to the 1B-B 6.9KV Shutdown Board (SDBD) tripped due to the breaker's 51G relay actuating causing an under-voltage signal on the 1B-B 6.9KV Shutdown Board. All 4 Emergency Diesel Generators automatically started as designed when the 6.9KV Shutdown Board under-voltage signal was received. "The 1B-B 6.9KV Shutdown Board was automatically energized from the 1B-B 6.9KV Diesel Generator. All required 6.9KV loads were sequenced back on to the 1B-B 6.9KV Shutdown Board as designed after the board was energized from its emergency diesel generator. The remainder of the electrical system is in normal alignment. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in a valid actuation of the Emergency Diesel Generators. "There was no impact to the health and safety of the public or plant personnel. "The NRC Senior Resident has been notified." | 100 | 47 | 0 | 100 | 47 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-12-16
54445 | 0 | WASHINGTON UNIVERSITY IN ST. LOUIS |  |  |  |  | 2019-12-13 | 2019-12-13 20:37 | 2019-12-13 | MICROSPHERES DEPOSITED TO DIFFERENT SEGMENT OF LIVER The following is a synopsis of a telephonic report: On 12/6/19, a patient was administered Y-90 microspheres, intended for segment 4 of the liver. On 12/13/19, the post-administration imaging was interpreted and examined. It was determined that, despite taking precautions of blood vessel embolization to limit the microspheres from other segments, some of the microspheres deposited in segment 2 as well as segment 4. The patient was notified. No adverse effects are expected as the microspheres all went to the same lobe of the liver, and within about 95 percent of the prescribed dose. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2019-12-23
54444 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-12-13 | 2019-12-13 14:50 | 2019-12-13 | AGREEMENT STATE REPORT - I-125 SEED MISTAKENLY INCINERATED The following was received from the Florida Bureau of Radiation Control (the Bureau) via email: "I-125 therapy seed (243 microCi) was mistakenly incinerated with medical waste. Pathologist mistook metal clip for seed and included it in the material to be incinerated. This information is from a preliminary phone report [to the Bureau]; a full written report with radioactive source info will be submitted via email." Incident Number: FL19-148 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-12-23
54443 | 0 | BASF CORPORATION |  |  |  |  | 2019-12-13 | 2019-12-13 14:46 | 2019-12-13 | LOST TRITIUM EXIT SIGNS The following is a synopsis of a telephonic report: An electrical contractor did not follow disposal instructions and disposed of eight (8) tritium exit signs (approximately 9.5 Ci each) in a dumpster on 12/2/19. The dumpster was removed on 12/4/19. The licensee discovered the error on 12/13/19 when they could locate two of the ten signs planned for removal. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-12-23
54442 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-11-22 | 2019-12-13 14:39 | 2019-12-13 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE DURING MEDICAL TREATMENT The following was received from the Florida Bureau of Radiation Control (the Bureau) via email: "At [licensee], on or around 1745 EST 22 November 2019, a male patient being treated with Y-90 theraspheres had a blockage on the catheter. The Interventional Radiologist increased the pressure on the line, rupturing the intubation tube. No contamination of staff, only patient. Decontamination of the room and patient followed, no contamination on skin, only gown and tube. Vials were disposed of with waste, so no batch numbers of spheres are available at this time. Problems with imaging occurred, so there are no images at this time. The Radiation Safety Officer (RSO) has asked for reports with more information from Interventional Radiologist (IR) and Radiation Oncologist Authorized User (ROAU). IR and ROAU disagree on how much activity the patient received before the rupture; patient was prescribed 15 mCi. Patient will return for further treatment. The Bureau has been notified and an inspector will be assigned to investigate." Incident Number: FL19-141 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-12-23
54441 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-12-05 | 2019-12-13 10:17 | 2019-12-13 | AGREEMENT STATE REPORT - MEDICAL MIS-ADMINISTRATION The following report was received from the Georgia radioactive materials program environmental protection division via email: "Augusta University Medical Center had an incident yesterday (December 5, 2019) in the Interventional Radiology (IR) Suite during a Y-90 TheraSphere procedure. "The Y-90 TheraSphere delivery was performed in the usual fashion, per TheraSphere protocol, with 3 flushes of the administration vial. Both delivery and nuclear medicine pre-procedure preparation was performed per standard radiopharmaceutical (TheraSphere) protocol. During administration, the remaining undelivered dose became stuck/trapped in the transport vial and could not be administered. "About 40 percent of the prescribed radiation dose was delivered to the patient, which is less than the criteria in Rule 391-3-17-.05.(115)a.1(i), which states, 'The total dose delivered differs from the prescribed dose by 20 percent or more.' "A small amount of the Y-90 microspheres spilled onto the administration table, which was covered with absorbent towels. Augusta University staff isolated the contamination, scanned all IR Suite staff to ensure the contamination was not spread outside the immediate area, and called for assistance with clean-up. All contamination was located and cleaned-up, and all swipes have been counted and the results show no residual contamination in the suite or on any equipment in the suite. All radioactive material has been collected and is being stored and managed as radioactive waste. "A formal written notification to your office will be submitted within 15 days of the event. This formal written notification will include all of the information required by Rule 391-3-17-.05.(115)." Georgia Incident No.: 22 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-12-23
54440 | 0 | WESTINGHOUSE |  |  |  |  | 2019-12-12 | 2019-12-12 19:24 | 2019-12-12 | PART 21 REPORT - FRACTURED AND DISLOCATED CONTROL ROD DRIVE MECHANISM THERMAL SLEEVE "During a 2019 planned outage at a Westinghouse plant, site personnel identified a fractured and dislocated control rod drive mechanism (CRDM) thermal sleeve. The fracture occurred just beneath the worn area of the flange in the full cross-section of the thermal sleeve tube. A stress concentration exists at this transition. Previous operating experience (OE) with thermal sleeve failures did not include a cross-sectional thermal sleeve fracture such as this. "Additional data supplied from the affected plant showed evidence of additional thermal sleeve locations with crack-like indications in the flange collar region (i.e., evidence of degradation but not failure). Although there was no evidence that control rod motion was hindered, Westinghouse is conservatively reporting this condition as having the potential to create a SSH (substantial safety hazard), were it to remain uncorrected. "Based on new OE provided to Westinghouse, a defect has been identified that is associated with a previously unseen form of thermal sleeve degradation (i.e., mechanical fatigue and fracture that leads to flange separation). Control rod functionality could become adversely impacted not only due to the flange wear reported in LTR-NRC-18-34, but due to the additional coincident fracture and separation of the thermal sleeve tube from its flange. This condition could exist prior to reaching the flange wear criteria established in PWROG-16003-P, Revision 2. The information supplied in PWROG-16003-P, Revision 2 and NSAL-18-1 also does not address this new OE. If no action is taken to monitor and/or correct this condition, an SSH could occur if the insertion of more than one control rod is prevented. "The probability for this to result in a SSH is low given that this is the very first observance of this phenomenon. Westinghouse does not expect that an affected plant would experience two or more stuck control rods during its current operating cycle. Even if multiple stuck control rods were to occur, such an event would be bounded by the licensee's ATWS analysis. Based on known wear conditions and wear rates, plants can safely operate for at least one cycle or until the next opportunity to perform a visual inspection. "The potentially affected plants listed below are Westinghouse design plants that: 1. Operate with higher upper head bypass flow conditions, known as 'T-cold' head plants, and 2. Operate with thermal sleeves containing a collar (or upper centering pad ring) just below the flange. Asco 2, Braidwood 1, Braidwood 2, Byron 1, Byron 2, Callaway 1, Catawba 1, Catawba 2, Comanche Peak 1, Comanche Peak 2, Doel 4, Hanbit 1, Hanbit 2, Kori 3, Kori 4, Maanshan 1, Maanshan 2, Seabrook, Sizewell B, Tihange 3, Vogtle 1, Vogtle 2, and Wolf Creek. "A Westinghouse communication will be supplied to affected licensees in early 2020 to inform them that this defect has been reported. The communication will provide updated recommendations concerning future inspection guidance." The person informing the Nuclear Regulatory Commission: Camille T. Zozula Westinghouse Electric Company 1000 Westinghouse Drive Cranberry Township, Pennsylvania 16066 Direct tel: (412) 374-2577 Direct fax: (724) 940-8542 e-mail: zozulact@westinghouse.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-12-12
54439 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-12-11 | 2019-12-12 12:26 | 2020-05-28 | AGREEMENT STATE REPORT - DOSE DELIVERED LESS THAN PRESCRIBED The following was received from the Florida Bureau of Radiation Control (the Bureau) via email: "[The licensee] reported that during a prostate treatment using 50 I-125 seeds, 20 of the seeds became stuck in the applicator and only 30 were inserted into the patient. All of the seeds were accounted for and the patient did not receive any additional exposure or suffer any harm. The remaining treatment dose will be fractionated and delivered at a later time. An additional detailed report containing make, model of seeds, activity, etc. will be forwarded to the Bureau's office later this week." Incident Number: FL19-146 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE ON MAY 28, 2020 AT 0820 EDT FROM MATT SENISON TO BRIAN LIN * * * The following update was received from the Bureau via email: "[On December 11, 2019], the licensee reported that during a prostate treatment using 50 I-125 seeds, the two Mick applicators suffered jams that could not be cleared. After attempts were unsuccessful at restoring function, the user terminated the procedure before the full implant could be completed. Of the 50 Seeds planned for implantation, 30 were successfully inserted into the patient. No I-125 seeds were lost and no spills or contamination occurred. Radiological review of seed placement determined that an adequate number of seeds were placed and dosing achieved in the target area. No further surgical intervention indicated. The patient will be followed with radiological studies and with PSA [prostate specific antigen] labs as previously planned." Notified R1DO (DeBoer) and NMSS Events Notification via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-12-20
54438 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-12-12 04:33 | 2019-12-12 08:14 | 2020-03-03 | MANUAL REACTOR TRIP DUE TO A LOSS OF HEATER DRAIN TANK PUMP FLOW "At 0432 EST, on 12/12/19, Sequoyah Unit 2 experienced a manual reactor trip. The trip was initiated due to a loss all number 3 Feedwater Heater Drain Tank pump flow; plant procedures directed a manual reactor trip if power is greater than 80 percent. "The Auxiliary Feedwater System (AFW) automatically actuated as required when the expected post trip feedwater isolation actuation actuated. Reactor Coolant System (RCS) temperature is being maintained by the steam dump system with all 4 Reactor Coolant Pumps (RCPs) in service. "All control and shutdown rods fully inserted. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the transient. Unit 2 is currently stable at normal operating temperature and normal operating pressure in Mode 3. The electrical system is in a normal alignment. "There was no impact on U1. There was no impact to the health and safety of the public or plant personnel. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a four hour, non-emergency notification per 10CFR50.72(b)(2)(iv)(B) and an 8 hour non-emergency notification accordance with 10CFR50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system." The NRC Resident Inspector was notified. * * * UPDATE ON 03/03/2020 AT 1320 FROM JAKE OLIVIER TO OSSY FONT * * * "The following update to the EN submitted on 12/12/19 is being made to provide clarification on reporting criteria originally described in paragraph five of EN 54438: "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The NRC Resident Inspector was notified. Notifed R2DO (Davis). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-12-12
54437 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-12-11 13:56 | 2019-12-11 15:06 | 2019-12-11 | POTENTIAL TORNADO MISSILE VULNERABILITIES "On December 11, 2019, at 1356 EST, it was concluded that certain safety-related equipment is vulnerable to design basis tornado missiles which could render the equipment inoperable and not able to perform its design function. This applies to the following Technical Specification equipment: "1. Component cooling water piping for the 'A' spent fuel cooling water system heat exchanger. This heat exchanger is vulnerable to a horizontal missile traveling through the roll-up door, which would challenge operability of the Technical Specification required component cooling system equipment. 2. All three emergency service water pumps and their diesel fuel oil supply tank. The emergency service water pumps and diesel fuel oil tank are vulnerable to a horizontal missile penetrating the missile screens. 3. Certain component cooling water system pump discharge piping is vulnerable from a vertical missile penetrating the auxiliary building roof. 4. The Unit 1 Auxiliary Feedwater (AFW) system pumps and the pump suction and discharge piping are vulnerable to a missile traveling through the screens on the sides and roof of the main steam valve house. This vulnerability also exists for the Unit 2 AFW. 5. The Unit 2 Service Water (SW) supply valves to the river water make-up pump are vulnerable to a vertical missile traveling through the turbine building roof. A missile strike on the piping or valves could cause an unisolable leak or pipe break on this non-essential SW piping which could result in inability to maintain Technical Specification required intake canal inventory. "These conditions are reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. There are no current operational challenges to either unit due to the tornado missile vulnerabilities. "Identified SSCs [structures, systems, and components] were declared inoperable [at 1356] and NRC Enforcement Guidance Memorandum 15-002, Rev. 1, 'Enforcement Discretion for Tornado Generated Missile Protection Noncompliance,' was implemented. Initial compensatory measures were implemented, per the guidance of NRC Interim Staff Guidance DSS-ISG-2016-01 Appendix A, within the time allowed by the applicable Limiting Conditions for Operation (LCOs) and the associated systems were then declared operable, but nonconforming." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2019-12-11
54436 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-12-10 00:12 | 2019-12-11 09:10 | 2019-12-11 | TECHNICAL SPECIFICATION VIOLATION REQUIRING SHUTDOWN The following information was received via phone and email. "On December 10, 2019, at 0012 CST, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to a failure of the regulating blade drive mechanism during reactor operation. MURR was not in compliance with all Limiting Conditions for Operations (LCOs), specifically S 3.2.a, which states, 'All control blades, including the regulating blade, shall be operable during reactor operation.' The regulating blade drive mechanism was removed, repaired, reinstalled, and all its functions were tested satisfactorily. Permission from the Reactor Facility Director was obtained per TS 6.6.c(4) prior to starting up the reactor later on December 10." Notification to the NRC Operations Center is required per TS 6.6.c(1) to report that an Abnormal Occurrence, as defined by TS 1.1.b, occurred. MURR was not in compliance with all of the Limiting Conditions for Operations as established in TS Section 3.0. "A detailed event report will follow within 14 days as required by TS 6.6.c(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2019-12-11
54435 | 0 | GENERAL ATOMICS |  |  |  |  | 2019-10-17 | 2019-12-10 18:30 | 2019-12-10 | PART 21 - HARDWARE FAILURE IN RADIATION MONITORING SYSTEM The following is a summary of information received from General Atomics via fax: On October 17, 2019, General Atomics (GA) identified a hardware failure in GA's Model RP-2C radiation monitoring system, manufactured and supplied by GA's Electromagnetic Systems Group (GA-EMS). The RP-2C radiation monitoring systems are used for post-accident monitoring of the containment area. The defect would prevent the RP-2C from sensing a high radiation condition. This could present a potential safety hazard to personnel by not indicating the actual radiation value and by not actuating the plant systems connected to the alarm relays. It is noted that there are typically redundant high range containment monitoring systems available to the control room operators, and the operators would be able to rely on the remaining operable channels during an accident. GA-EMS will issue a Quality Bulleting to the affected sites that will include additional detail in identifying affected modules and what to do if a defect is found. Sites are advised to continue performing their normal surveillance testing of the RP-2C module by utilizing the front panel CHECK test feature. If you have any questions or need additional information concerning this report please contact Michael Grogan, Senior Director of Licensing, at (858) 455-2809 or Michael.Grogan@ga.com. Technical questions can be directed to Arthur Evans at (858) 964-6948. The following plants are affected: FitzPatrick, Millstone, Peach Bottom, Pilgrim, Susquehanna, Catawba, McGuire, Saint Lucie, Sequoyah, Turkey Point, Watts Bar, Fermi, LaSalle, Palisades, Point Beach, Prairie Island, Quad Cities, Arkansas Nuclear One, Columbia Generating Station, Crystal River, Kewaunee, San Onofre, Zion. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-12-10
54434 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-11-12 | 2019-12-10 13:25 | 2019-12-10 | AGREEMENT STATE REPORT - LOST LICENSED NUCLEAR MATERIAL This is a summary of information received from the state of Nebraska via a phone call: On November 12, 2019, the licensee packaged low level waste into 55-gallon barrels to be shipped to a disposal facility. On December 3, 2019, the disposal facility arrived to pick up the waste and discovered that one of the barrels was missing. The missing barrel contained 11 mCi of C-14. It is believed that the waste was improperly disposed of in another waste stream. The investigation is ongoing at this time and the event is open with the state of Nebraska. Nebraska incident number: NE190004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-12-18
54433 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-12-10 09:20 | 2019-12-10 11:04 | 2020-01-24 | PLANNED LOSS OF EMERGENCY RESPONSE FACILITIES AND EQUIPMENT "At 0920 CST on December 10, 2019, Comanche Peak began a planned modification on the Unit 1 Plant Computer System. During this modification, the ability to perform emergency assessment in the Technical Support Center (TSC) and the Emergency Operations Facility (EOF) will be impacted. Since the ability to perform emergency assessment is not expected to be restored within 72 hours, this is reportable per 10CFR50.72(b)(3)(xiii) as an event that results in a loss of emergency assessment capability. "During this modification, the Control Room will continue to have the ability to perform emergency assessment. If an Alert, Site Area Emergency, or General Emergency is declared during this modification, communicators dedicated to performing emergency assessment will be stationed in the Control Room, TSC, and EOF. The Plant Computer System modification is scheduled to be completed on December 22, 2019, and a follow-up ENS notification will be made once the Unit 1 Plant Computer System is declared functional. "The NRC Resident Inspector has been informed." * * * UPDATE ON 1/24/20 AT 1034 EST FROM THOMAS BOWDEN TO RODNEY CLAGG * * * Licensee provided an update to inform that as of 0853 CST on 1/24/20, the modification is complete and the emergency assessment capabilities of the TSC and EOF have been restored. Notified R4DO (Silva) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-12-10
54432 | -1 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-12-09 | 2019-12-10 10:14 | 2019-12-20 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN This is a summary of information received from the state of Nebraska via a phone call: On December 2, 2019, the state of Nebraska identified a lost tritium exit sign that was improperly transferred by the licensee to the state of Wisconsin. The general licensee indicated that they transferred the exit sign to a electronics company in Wisconsin, which was not licensed to possess radioactive materials. It is believed that the sign was reused by the electric company. The company was contacted and is working with the Wisconsin Department of Health on ascertaining the exit sign's location. The tritium exit sign is a Isolite model 2000 (S/N: H114041) with an activity of 12.57 Ci. No further investigation is planned at this time and Nebraska has closed the event. Nebraska incident number: NE190006 * * * RETRACTION ON 12/20/2019 AT 1011 EST FROM DEB WILSON TO ANDREW WAUGH * * * This is a summary of information received from the state of Nebraska via email: On 12/12/2019 the Wisconsin Radioactive Program confirmed the sign (S/N: H114041) had been found and installed in Joliet, IL. Notified R4DO (Drake) and NMSS Events (email). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-12-18
54431 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-31 19:19 | 2019-12-10 09:52 | 2019-12-10 | INVALID ACTUATION OF THE UNIT 2 TURBINE DRIVEN AUXILIARY FEEDWATER PUMP (TDAFWP) "This report describes an invalid actuation of the Unit 2 Turbine Driven Auxiliary Feedwater Pump that occurred on October 31, 2019. This report is being made in accordance with 10CFR50.73(a)(1), which states, in part, 'In the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than actuation of the Reactor Protection System (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' "On October 31, 2019, Comanche Peak Nuclear Power Plant Unit 2 was in Mode 1 operating at 100% power. At 1919 CDT, the Main Steam Line 2-01 steam supply valve to the TDAFWP opened due to a loss of continuity between the fuse supplying control power to the valve positioner and the fuse clips. Operators initiated a 50MW load reduction to maintain power less than 100%. The steam supply to the TDAFWP was closed, the TDAFWP was stopped, and the fuse clips were tightened. Unit 2 was returned to full power at 2055 CDT. "The specific train and system that actuated was the third AFW train on Unit 2. The train actuation was complete and during the TDAFWP start the system started and functioned correctly. "The NRC Resident Inspector was notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-12-10
54430 | 0 | COMANCHE PEAK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-12-09 21:26 | 2019-12-10 00:03 | 2019-12-10 | MAIN STEAM LINE (MSL) RADIATION MONITOR TO BE NON-FUNCTIONAL "1-RE-2328 Main Steam Line #1-04 MSL181 received an operate failure on loss of counts. At time 2126 [CDT], the radiation monitor was declared non-functional. "With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 1-04 could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant (CPNPP) has assurance of steam generator integrity and fuel cladding integrity. There is a negligible safety significance to the current condition from a public health and safety perspective. "Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 radiation monitor serves as a backup with alarm function and additionally Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL 1-04. "Corrective actions are being pursued to restore 1-RE-2328 to functional status. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-12-10
54429 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-05-15 | 2019-12-09 16:45 | 2019-12-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN This is a summary of information received from the state of Nebraska via a phone call: On November 20, 2019, the state of Nebraska identified a lost tritium exit sign during their quarterly reports. The general licensee indicated that they improperly disposed of the exit sign by donating it to a second-hand store on May 15, 2019. The exit sign has not been located at this time. The second-hand store turns over their inventory every six months, so it is believed that the exit sign has been sold or disposed of. The tritium exit sign is a Betalux model BX-20-BK (S/N: C167432) with an activity of 17.51 Ci. No further investigation is planned at this time and Nebraska has closed the event. Nebraska incident number: NE190005 * * * UPDATE ON 12/19/2019 AT 1217 EST FROM DEB WILSON TO BRIAN LIN * * * The following was received from the state of Nebraska via email: "On 11/20/2019, Dr. Michael Meyer, M.D. left a message reporting the loss of an exit sign that contained 17.51 Curies of Tritium, indicating he had donated the sign to Goodwill at 156th Street and Maple Road in Omaha approximately May 15, 2019. On 11/21/2019, the department [Nebraska Division of Public Health] spoke with the manager of the donation site who was unable to locate the sign. On 11/22/2019 the department spoke with Dr. Meyer again to see if he had obtained a receipt for his donation as he could not remember the exact date it was disposed of. He claimed it was put in a box with some clothes and taken to the drop-off site. Dr. Meyer did not obtain a receipt and Goodwill does not keep copies of donation receipts. The department then spoke with Goodwill's Director of Operations on 11/25/2019. The Director stated that all donations are processed within 24 hours of receipt and Goodwill does not have inventory tracking detailed enough to be able to tell if/when it was sold. Inventory is turned over every six months and after the six month period unsold items are taken to the landfill. There will be no further follow-up." Notified R4DO (Josey) and NMSS Events (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-12-17
54428 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-12-09 | 2019-12-09 10:08 | 2019-12-09 | AGREEMENT STATE REPORT - LOST AND FOUND MOISTURE DENSITY GAUGE The following was received via email from the Arizona Department of Health Services: "On December 9, 2019, the Department [Arizona Department of Health Services] was notified of a stolen portable gauge. Shortly after the initial notification, the licensee called back to update their notification and said the truck was impounded with the gauge secured in a metal box in the back of the truck. The gauge is an Instrotek Xplorer 3500. The Department is continuing to investigate the event. "Additional information will be provided as it is received in accordance with SA-300." Arizona incident number 19-031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-12-17
54427 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2019-12-06 13:28 | 2019-12-06 15:33 | 2019-12-06 | AGREEMENT STATE REPORT - DOSE DELIVERED DIFFERED BY MORE THAN 20 PERCENT The following was received from the Kansas Department of Health and Environment via email: "On December 6, 2019, at 1328 [CST], [the University of Kansas Hospital Authority] reported a medical event involving Y-90 Microspheres to the Kansas Radiation Control Program (RCP). The licensee stated that the patient had unusually small blood vessel feeding the tumor and prevented a larger than anticipated dose to the tumor. An initial written report was received at 1354 [CST] from the RSO [Radiation Safety Officer] stating that there were no errors or problems during the procedure administration. The dose differed by more than 20 percent, though the physician stated that the dose was therapeutic and will not plan to retreat. There was no report of contamination at the facility or of the patient. "The Kansas RCP is preparing for an onsite investigation to review the incident. That investigation will be the basis for a final NMED report to follow." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2019-12-16
54426 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2019-12-06 | 2019-12-06 15:19 | 2019-12-06 | AGREEMENT STATE REPORT - DENSITY GAUGE FOUND AT SCRAP YARD The following was received from the Wisconsin Department of Health Services Radiation Protection Section (the Department) via email: "On December 6, 2019, the Department was notified by a local scrap facility that they had refused a load of material on December 4 after setting off portal monitors at their site. No reports were made at that time. On December 6, safety staff from the scrap facility assisted in characterization of the material at the originating location. The device was identified as a Seaman Nuclear Density Gauge (Model R-75, SN: 3032). These are manufactured with a maximum activity of 5 mCi Radium-226. No residual contamination was identified in any areas the gauge had been. "The Department has dispatched inspectors to perform their own investigation and characterization of the material, and will provide updates as they become available." * * * UPDATE ON 12/06/019 AT 1805 EST FROM KYLE WALTON TO OSSY FONT * * * The following update was received from the Wisconsin Department of Health Services (the Department) via email: "Inspectors arrived at the originating location. The material is currently secured in a cargo container away from members of the public. Surveys and swipes do not indicate a leaking source or removable contamination. Surface readings of up to 13 mR/h were observed. The manufacturer has been contacted to identify the last known owner of the gauge." Event Report ID No.: WI190016 Notified R3DO (Daley) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2019-12-16
54425 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2019-12-05 08:10 | 2019-12-05 16:03 | 2019-12-30 | FIRE DOOR DISCOVERED UNLATCHED The following was received via email from Cooper Nuclear Station: "At 0810 [CST], on 12/5/19, Operations personnel discovered BLDG-DOOR-R209, FIRE DOOR BETWEEN CRITICAL SWITCHGEAR ROOMS F & G, was unlatched. The door was immediately latched upon discovery. Based on door logs, the door separating the two critical switchgear rooms was inadvertently left unlatched for approximately 5 minutes. This door is a Steam Exclusion Boundary (SEB) door. It is required to be closed and latched when the Auxiliary Steam Boiler is in service due to Auxiliary Steam piping passing through Critical Switchgear Room 'G'. If a steam line break was to occur with the door unlatched, steam could render both Critical Switchgear busses inoperable. "This is being reported under 10 CFR 50.72(b)(3)(ii)(B), Unanalyzed Condition, and 10 CFR 50.72(b)(3)(v), Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (B) remove residual heat and to (D) mitigate consequences of an accident. "There was no impact on the health and safety of the public or plant personnel." The door closes automatically and appeared to have been left unlatched by the last person passing through. The door was tested and latches as required. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 12/30/2019 AT 1129 EST FROM DAVE VANDERKAMP TO ANDREW WAUGH * * * CNS is retracting the 8-hour notification made for event notification 54425 which occurred on December 5, 2019 at 0810 CST. Subsequent engineering evaluation demonstrates the essential equipment located in critical switchgear room 'F' would have remained within the design limits in the event of a postulated auxiliary steam line break in critical switchgear room 'G' with door R209 open. As a result, the safety function would have been maintained and there was no unanalyzed condition that would significantly degrade plant safety. The licensee notified the NRC Resident Inspector. Notified R4DO (Warnick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2019-12-05
54424 | 0 | EMERSON PROCESS MANAGEMENT |  |  |  |  | 2019-11-06 | 2019-12-05 14:45 | 2020-02-26 | PART 21 REPORT - POTENTIAL DEVIATION OF PRESSURE TRANSMITTERS DUE TO TEMPERATURE RISE The following information was received from Emerson Rosemount Nuclear Instruments, Inc. via fax: "Rosemount Nuclear Instruments, Inc. (RNII) is providing an interim evaluation report on the treatment of temperature rise due to electronics self-heating in qualified life thermal aging calculations on Model 1153 and 1154 [inclusive of 1153 Series B, 1153 Series D, 1154, and 1154 Series H] pressure transmitters. The evaluation is being conducted to determine if modifications to the currently specified qualified life are warranted. "Qualification programs for 1153 and 1154 pressure transmitters were structured to comply with the requirements of IEEE standard 323-1974 which requires aging to establish a qualified life prior to design basis event testing. Thermal aging is considered a significant aging mechanism; therefore, accelerated thermal aging was conducted on type test specimens as described in RNII qualification reports D8300040 and D8700096. These reports document the thermal aging basis for all 1153 and 1154 models identified in section 1.0. In both type test programs, temperature rise due to electronics self-heating was present during thermal aging and was consistent with expected in service normal operating conditions. "These evaluations are expected to be complete by February 28, 2020. "If there are any questions, or you require additional information related to this issue, please contact Nathan Schukei (952) 949-5213 or Paul Schmeling (952) 949-5359." There are currently no known affected customers. * * * UPDATE ON 2/26/20 AT 1454 EST FROM JEFF CHIVERS TO KERBY SCALES * * * The following is a summary of the information provided by the vendor via fax: "Rosemount Nuclear Instrument Inc. (RNII) analysis of both 1150 series and 3150 series included electronics thermal imaging to characterize the thermal distribution on electronic assemblies, as well as direct in situ temperature measurements of qualified life limiting components. Specifically, temperature measurements were taken on limiting components to quantify actual temperature rise for both the original qualification accelerated aging conditions as well as for normal operating conditions. "The analysis demonstrates that temperature rise due to electronics self-heating on limiting components is application dependent. As a result, the calculated qualified life will be application dependent. In many application conditions, the originally established qualified life calculations will remain conservative with respect to the updated calculations (i.e. the updated qualified life will be longer than the originally established qualified life). In applications where the originally established qualified life calculations may not be conservative (i.e. the updated qualified life will be shorter than the originally established qualified life), RNII believes there is no impact to the safety function of either the 1150 series or 3150 series pressure transmitters due to any difference in calculated qualified life because long term aging information obtained from the limiting component supplier, supported by RNII independent internal testing, demonstrates insignificant change over time in the electrical parameters of the limiting components for the temperatures and operating conditions in question. "To provide a more accurate model to account for electronics temperature rise in Arrhenius calculations, RNII is revising our temperature inputs into the Arrhenius accelerated aging calculation methodology for both 1150 series and 3150 series pressure transmitters. This revised methodology will be provided separately to end users. "RNII does not believe this issue presents a risk to the safety function of the 1150 and 3150 series pressure transmitters. RNII recommends end users evaluate the significance of this notice to their specific pressure transmitter applications. If there are any questions, please contact our Technical Support Engineers at 952-949-5200 (RNll.lnfo@emerson.com) or Nathan Schukel at 952-949-5213." Notified R1DO (Ferdas), R2DO (Davis), R3DO (Orth), R4DO (Kozal), and Part 21/50.55 Reactors, Part 21 Materials, NMSS _Events via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2019-12-05
54423 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2019-12-05 12:20 | 2019-12-05 13:30 | 2019-12-05 | OFFSITE NOTIFICATION DUE TO DECEASED MANATEE IN OWNER CONTROLLED AREA "This 4-hour non-emergency notification to the NRC is being made on a notification to another government agency per 10 CFR 50.72(b)(2)(xi). "On 12/5/2019, at 0719 EST, a deceased manatee was identified in the Owner Controlled Area. The Federal Fish and Wildlife Service and the Florida Fish and Wildlife Conservation Commission (FWCC) were notified on 12/5/2019, at 1220 EST. "Miami-Dade County was notified on 12/5/2019, at 1245 EST. A courtesy call to the Florida Department of Environmental Protection was made on 12/5/2019, at 1300 EST. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-12-05
54422 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-12-04 14:30 | 2019-12-05 13:20 | 2019-12-05 | FIRE SPRINKLER LINE OUT OF SERVICE The following was received via email from Global Nuclear Fuels - Americas, LLC: "At 1430 EST, on December 4, 2019, the New Hanover County Deputy Fire Marshall was notified that a section of fire sprinkler line supporting the Fuel Manufacturing Operation (FMO) was unable to perform its intended function. The sprinkler line supported a small section of office area. No areas supporting fuel manufacturing were affected. The fire sprinkler pipeline was returned to operation at approximately 1920 EST on December 4, 2019. The New Hanover County Deputy Fire Marshall was informed of system restoration. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will notify the NRC Resident Inspector and the Region. Notified R2DO (Blamey) and NMSS (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-12-05
54421 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2019-12-04 18:00 | 2019-12-05 10:41 | 2019-12-05 | ANNUAL SURVEILLANCE NOT COMPLETED The following was received via email from Kansas State University Nuclear Reactor Facility: "Per Technical Specification 4.7.3, fuel elements comprising approximately 1/3 of the core shall be visually inspected annually for corrosion and mechanical damage such that the entire core shall be inspected at a 3-year intervals. Due to an inspection tracking sheet sorting error, four fuel elements were not marked to be inspected and are currently outside of the required surveillance frequency. Failure to perform a surveillance within the required time interval shall result in the component being inoperable. "The reactor is and will remain shutdown until review by the Reactor Safeguards Committee of corrective actions in accordance with the Technical Specifications. "A written report will be submitted within ten days summarizing the reportable occurrence." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | KS | NPR | [5 empty] | 0 | 2019-12-05
54420 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2019-12-04 16:15 | 2019-12-04 16:31 | 2019-12-12 | LOST AND FOUND SPECIAL NUCLEAR MATERIAL BWXT Nuclear Operations Group-Lynchburg (the licensee) notified the NRC of Special Nuclear Material (SNM) being lost and eventually found. During the investigation, the licensee determined that they could not rule out an attempt to commit an unlawful diversion of SNM. The licensee will notify the NRC Resident Inspector and the Region. Notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC, EPA Emergency Ops Center, FDA Emergency Ops Center (email), DHS Nuclear SSA (email), FEMA NWC (email), FEMA NRCC SASC (email), and DNDO-JAC (email). * * * RETRACTION ON 12/12/2019 AT 1537 FROM STEPHEN SUBOSITS TO OSSY FONT * * * The licensee notified the NRC that after further investigation, the material was located in a different area due to human error and did not represent an attempted diversion. Notified R2DO (Bonser) and, via email, ILTAB (Pearson), NMSS Events Notification, IRD MOC (Kennedy), and 73.71 Safeguards Group. Additionally notified DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, CISA IOCC, EPA Emergency Ops Center, FDA Emergency Ops Center (email), DHS Nuclear SSA (email), FEMA NWC (email), FEMA NRCC SASC (email), and DNDO-JAC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.11(a) |  |  |  | 1 | 2019-12-12
54419 | 0 | RHODE ISLAND ATOMIC ENERGY COMM |  |  |  | 2000 KW POOL | 2019-12-04 14:23 | 2019-12-04 14:33 | 2019-12-04 | ANNUAL SURVEILLANCE NOT COMPLETED This is a summary of a call received from the Rhode Island Nuclear Science Center (the facility) as required by Technical Specification (TS) 6.7.2.1.1: The facility identified a missed annual surveillance for their shim safety blades drop time as required by TS 4.2.1. The facility, a Materials Testing Reactor used for research, was not in operation. The licensee stated the last surveillance was performed in August 2018. Additionally, they stated the reactor will not be operated until the surveillance is completed and meets the shim safety blades requirements in TS 3.2.2. The licensee also notified the Project Manager and Facility Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | RI | NPR | [5 empty] | 0 | 2019-12-04
54418 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-12-02 13:31 | 2019-12-02 14:30 | 2019-12-02 | SAFEGUARDS REPORT An actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-12-02
54417 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-11-30 11:00 | 2019-11-30 19:48 | 2019-11-30 | BOTH TRAINS OF CONTAINMENT SPRAY REMOVED FROM SERVICE "On November 30, 2019, at 1100 PST, with Unit 2 in Mode 4, Operations identified that both trains of containment spray had been removed from service earlier at approximately 0217 hours as part of preparations for a planned Mode 5 entry. The containment spray pumps are required to be operable (along with the containment fan cooler units) in Modes 1 through 4 in accordance with Technical Specification 3.6.6. With both containment spray pumps inoperable, TS 3.6.6 Action F requires the Unit to be shut down in accordance with TS 3.0.3. At 1125 hours, both trains of containment spray were returned to operable and the required actions of TS 3.6.6 and TS 3.0.3 were exited. "The five containment fan cooler units remained operable for the duration of the occurrence. "This notification is being made in accordance with the requirement of 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented fulfillment of a safety function, and 10 CFR 50.72(b)(3)(ii) as an event or condition that may have resulted in the plant being in an unanalyzed condition. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-11-30
54416 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-11-27 | 2019-11-29 09:47 | 2019-11-29 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received from the Commonwealth of Kentucky via email: "Kentucky Radiation Health Branch (KYRHB) was notified by email on November 27, 2019, of an on/off shutter equipment failure on two separate fixed gauging devices (Ronan SA1-F37, Serial Numbers 9472GK and 1079GK; Cs-137 activity 500 milliCi each). Kentucky Licensee, Arkema, Inc. reports November 27, 2019 during a required 6-month check, techs discovered the shutter was not closing. Verified by survey meter, the readings did not close fully as expected. Survey numbers were not reported, but a full report will be submitted on December 2, 2019. The Licensee RSO [Radiation Safety Officer] notified plant operations department and the safety department that entry into the vessels is only via a sealed manway, and that entry is not permitted until the shutter mechanism has been repaired, or the gauges have been replaced. Ronan Engineering is scheduled to be notified after the Thanksgiving break. The licensee will provide timely updates to the KYRHB and the licensee will reinstruct employees of event reporting criteria." Kentucky Event Report ID No.: KY190011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-12-09
54415 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-11-26 | 2019-11-26 16:28 | 2019-11-26 | AGREEMENT STATE REPORT - PORTABLE NUCLEAR GAUGE RUN OVER AT JOB SITE The following report was received from the North Carolina Department of Health and Human Services via email: "RMB [North Carolina Radioactive Materials Branch] received a report of a portable nuclear gauge that was run over at a job site. The gauge was cordoned off and is away from any pedestrian areas. At the time of this report, based on on-site photos provided by the licensee; the source rod is retracted and is undamaged and initial surveys show no leakage. Gauge outer housing appears damaged but intact. Intertek will be arriving to take possession of the gauge to transport for repair. Inspector has been dispatched to conduct an on-site investigation. Additional information will be provided to update, complete & close this report. Our [North Carolina Department of Health and Human Services] investigation is ongoing." The gauge is a Troxler model number 3430. NC Event Report ID. NO.: 190041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-12-04
54414 | -1 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2019-11-25 | 2019-11-26 15:04 | 2019-12-02 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILED TO CLOSE DURING SEMI-ANNUAL TESTING The following report was received from the Virginia Department of Health via email: "On November 25, 2019 a licensee reported that the shutter of a fixed gauge used to measure the level of material inside a process vessel might have failed to close during the semi-annual radiological testing. The gauge is a Ronan Engineering, Model SA1-F37, serial number M7407, containing 40 mCi of Cs-137. The shutter arm is actuating, but the radiation reading at approximately 3 inches below the source remained the same (0.8 mR/hr) when the shutter was opened and closed. The source is located approximately 10 feet from the ground level and is only accessible by a stepladder. There are no routine activities that bring employees in close proximity to the source. There was no public exposure or environmental release from this event. The licensee has contacted the manufacturer for further investigation. "The Virginia Office of Radiological Health will review the licensee's written report and determine additional actions to be taken." Event Report ID No.: VA-19-006 * * * RETRACTION ON 12/2/19 AT 1255 EST FROM ASFAW FENTA TO KERBY SCALES * * * The following was received from the Virginia Department of Health via email: "Please retract the incident report that was submitted on November 26, 2019. "The licensee was advised by Ronan Engineering to take measurements directly from the detector side by closing and opening the shutter instead of taking a reading at approximately 3 inches below the source. On November 27, 2019, the licensee retested the shutter by measuring directly to the detector side and found 0.4 mR/hr when the shutter was opened and 0.2 mR/hr when the shutter was closed. The licensee reported to the agency that the gauge was working properly. There was no problem on the gauge; rather, it was an error on the measurement technique." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2019-12-04
54413 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-11-26 | 2019-11-26 15:00 | 2019-12-11 | AGREEMENT STATE REPORT - LOSS OF A NUCLEAR DENSITY GAUGE The following report was received from the Pennsylvania Bureau of Radiation Protection via email: "On November 26, 2019 a lawyer representing the licensee reported the event via telephone. The licensee is Larson Design Group, USNRC Radioactive Material License No. 47-35062-01, PA reciprocity license PA-R0218. Details are sparse at this time. The lawyer stated an employee wrecked a vehicle carrying a nuclear gauge (with Cesium 137 and Americium 241) in a ditch late Friday night. He had a friend pick him up, leaving the vehicle and gauge unattended. At some point police found the vehicle and impounded it. The police recognized the radioactive material shipping case in the vehicle. They allowed the employee to claim the vehicle only after producing documentation indicating he was authorized to possess it. It is believed the gauge never left the vehicle and it is back in possession of the licensee. The DEP [Department of Environmental Protection] will update this event as soon as more information is provided." PA Event Report ID No.: 190028 * * * UPDATE FROM JOHN CHIPPO TO KARL DIEDERICH AT 1004 EST ON 12/11/19 * * * The following update was received from the Pennsylvania Bureau of Radiation Protection via fax: "The nuclear gauge was a Troxler 3440 (S/N: 33739) containing 8.1 mCi of Cs-137 and 40 mCi of Am-241/Be. The gauge was impounded by police and was out of the licensee's control for approximately 60 hours. The employee responsible has had his employment terminated. As part of corrective actions, the licensee will review its training practices and update as necessary." Notified R1DO (Lally) and (via e-mail) NMSS Events group, ILTAB, and CNSC. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | WV | OTH | AGR |  |  |  |  | 0 | 2019-12-04
54412 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-11-26 | 2019-11-26 13:53 | 2019-11-27 | AGREEMENT STATE REPORT - POSSIBLE FOUND RADIOACTIVE MATERIAL The following information was received via phone call: A member of the public earlier today identified a container on National Forest Service land near Globe, Arizona that is labeled as having radioactive material. Pictures of the container show "B of E permit 681, Serial Number D-8011, Radiation, Return to Dow Chemical Company, Rocky Flats." This is an initial report. Arizona Department of Health Services personnel will investigate presently and provide an update. * * * UPDATE AT 1403 EDT ON 11/27/19 FROM BRIAN GORETZKI TO JEFF HERRERA * * * The following update was received from the Arizona Department of Health Services via email: "The container turned out to be a metal lid based on the orientation of the data plaques and the safety top. We [Arizona Department of Health Services] performed exposure and contamination surveys onsite and everything came back at background." Notified the R4DO (Pick) and NMSS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-12-04
54411 | 0 | TERRACON CONSULTANTS |  |  |  |  | 2019-11-25 17:00 | 2019-11-25 22:16 | 2019-11-25 | LOST AND FOUND NUCLEAR DENSITY GAUGE At approximately 1500 EST, on 11/25/2019, a technician departed a job site when they realized that they left the tailgate opened and the density gauge was no longer in the back of the truck. The technician turned around to look for the gauge, however, the gauge could not be found. The licensee searched for the gauge for approximately 4 hours and then contacted local law enforcement. The gauge was reported by local law enforcement to have been picked up at approximately 1630 EST. The licensee went to the police department to examine the gauge and it was reported not to be leaking. The gauge information is a Humboldt model 5001C, Serial Number 2301 containing 10 milliCuries of Cs-137 and 40 milliCuries of Am-241. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-12-03
54410 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-11-21 | 2019-11-25 20:00 | 2019-11-26 | AGREEMENT STATE REPORT - LOST I-125 SEED The following report was received from the Arizona Department of Health Services (Department) via email: "On November 25, 2019, the Department was notified of a lost I-125 seed. The licensee believes that the seed was most likely lost in pathology on November 21, 2019. The Department is continuing to investigate the event." Arizona Incident: 19-028. * * * UPDATE SENT BY BRAIN GORETZKI RECEIVED BY RICHARD SMITH ON NOVEMBER 26, 2019 AT 9:45 EST * * * The following was received via email from the state of Arizona: Vender for the I-125 seed was Isoaid, description of the seed was 5 cm stranded seed, Lot Number 63917-5, and activity was 0.197mCi I-125. Notified: R4DO (Pick). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-12-03
54409 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2019-11-25 08:54 | 2019-11-25 18:20 | 2019-11-27 | TEMPORARY PROCESS RADIATION MONITORING SAMPLE CART NON FUNCTIONAL "At 1245 PST, on November 23, 2019, the Turbine Building Process Radiation Monitoring Sample Rack (TEA-SR-26) was declared non-functional and taken out of service to perform planned preventive maintenance per procedure. The temporary sample cart was placed in service as an alternate method per plant procedures. "At 0854 PST, on November 25, 2019, it was discovered that the temporary sample cart had a broken belt. At that time neither the Turbine Building Process Radiation Monitoring Sample Rack nor the temporary sample cart could be returned to service. "At 1300 PST, on November 25, 2019, the temporary sample cart was returned to service following repairs. This restored the required compensatory measures for TEA-SR-26. "This event is being reported as a major loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "There was no impact to the health and safety of the public or plant personnel." The NRC Resident Inspector has been notified. * * * UPDATE ON 11/27/2019 AT 0655 EST FROM SEAN KEEHN TO BRIAN LIN * * * "At 2057 PST, on November 26, 2019, it was discovered that the temporary sample cart had lost power and was not in service. At this time, neither TEA-SR-26 nor the temporary sample cart were in service, this was a subsequent failure of the temporary sample cart, and at the time the station had been unsuccessful at restoring a reliable alternate sampling method following the failure that occurred at 0854 PST, on November 25, 2019. "At 2350 PST, on November 26, 2019, the temporary sample cart was returned to service following repairs. This restored the required compensatory measures for TEA-SR-26. "The NRC Resident Inspector will be notified." Notified the R4DO (Pick) via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-11-25
54408 | 0 | VT OFFICE OF RADIOLOGICAL HEALTH |  |  |  |  | 2019-11-18 | 2019-11-20 15:48 | 2019-11-26 | AGREEMENT STATE REPORT - PATIENT UNDERDOSAGE OF Y-90 RESIN SIR-SPHERES The following report was received from the Vermont Department of Health via email: "Medical Event: Y90 resin Sir-Spheres treatment infusion aborted due to kinked microcatheter. 99.5 [percent] of the drawn dose was not delivered to the treatment site. Contamination of IR [interventional radiology] suite floor detected. Contamination of infusion paraphernalia (gloves, shoe covers, gauze, towels) detected. Contaminated items were contained and floor was decontaminated to acceptable levels by RSO [Radiation Safety Officer]. "Date of Event: 11/18/2019 "11/18/19 AU [Authorized User] notified referring physician and patient of the medical event 11/19/19 RSO contacted State of Vermont 11/19/19 NRC contacted for clarification of event 11/20/19 RSO contacted Sirtex "Incident Details: Terumo Progreat, I.D. 0.027[inches] (0.7mm), 130cm length, was used initially to access treatment site. Boston Scientific, I.D. 0.021[inches] (0.5mm), 130cm length, was used to access treatment site after unsuccessful attempt with Progreat. "IR [Interventional Radiologist] Fellow assembled the delivery device. "The original dose measurement was 2.2 mR/hr at 1230 [EST]. The Nalgene with undelivered dose vial and the second Nalgene with delivery catheter were measured in exactly the same setup as original dose measurement. The total residual in the 2 Nalgene containers were 1.9 mR/hr + 0.25 mR/hr = 2.15 mR/hr at 1430. With 2 hours decay correction, the Nalgene containers reading should be 2.15 x 1.02 = 2.19 mR/hr. "2.19 / 2.2 = 0.995 or 99.5 [percent] for Vial + Catheter. Therefore, about 0.5 [percent] of the drawn dose (44.3 mCi) was lost. 0.5 [percent] of 44.3 mCi is 0.2 mCi (This is the calculated amount of Y90 lost) "The DAVYR [Dosimetry and Activity Visualizer for Y-90 Radioembolization] application provides the following liver dose calculation based on the partition model: Liver = 27.5 Gy for a 1.5 GBq (or 40.5 mCi) dose delivery. This is based on 100 [percent] of prescribed dose being delivered. "In the worst-case scenario where all the lost activity (0.2 mCi) was delivered to the patient, the liver dose calculation is: Liver = 27.5 Gy x (0.2 mCi / 40.5 mCi) = 0.14 Gy (or 14 rem) "The only way to properly measure the bags of contaminated paraphernalia (towels, gloves, gauze, shoe covers) in the same setup as the original dose measurement would involve transferring the contents into several Nalgene containers. This can be done next day to properly account for lost Y90 activity. "Medical event criteria - the byproduct material administration has to meet the following (10 CFR 35.3045): "1. The dose differs from a dose that would have resulted from the prescribed dosage by more than 50 rem to an organ or tissue. The unintended dose to any organ or tissue from the lost 0.2 mCi Y90 would be similar to the Liver dose calculated above (14 rem) and does not exceed 50 rem difference. Note: The highest delivered dose to Liver from the lost Y90 is calculated to be 14 rem. This is below the target dose of 110 Gy (or 11,000 rem) and does exceed the 50 rem difference; however, this was a medical safety decision resulting from unforeseen microcatheter kinking due to patient anatomy. "2. The total dose delivered differs from the prescribed dose by 20 [percent] or more. Yes, the total dose delivered is calculated to be about 0.2 mCi and is much below the prescribed dose of 40.5 mCi. A medical safety decision to abort the infusion was due to an unforeseen device event (kinked microcatheter) that prevented the safe delivery of Y90 microspheres." * * * UPDATE ON 11/26/19 AT 0738 EST FROM FRANCIS ONEILL TO OSSY FONT * * * The following update was received from the Vermont Department of Health via email: "As a follow up to Event Number 54408, Y-90 Sirsphere event, the calculated dose to the unintended organ, the pancreas, is 14 Rem or 0.14 Gray." Notified R1DO (Henrion) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VT | OTH | AGR |  |  |  |  | 0 | 2019-12-03
54407 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-11-20 | 2019-11-22 14:46 | 2019-11-22 | AGREEMENT STATE REPORT - AIRCRAFT INSTRUMENT WITH RADIUM-226 PAINTED DIAL FOUND The following information was received via E-mail: "On 11/20/2019, Massachusetts Radiation Control Program (MARCP) was informed by Schnitzer Steel Industries, Inc., that a scrap metal shipment from Devens Recycling in Danvers, MA set off the radiation monitor alarm. The vehicle was redirected back to Devens Recycling for follow-up survey and mitigation in accordance with MA RCP DOT Special Permit MA-MA-19-11. On 11/21/2019, the material was identified and segregated from the scrap metal load by an independent radiation consultant. The radioactive material discovered was radium-226 painted on the dial of an abandoned (lost), old Aircraft Altimeter instrument. The dose rate at 6 inches from the instrument was 150 microR/hr. The background dose rate was 20 microR/hour. The radiation survey instrument used to locate the source was a Ludlum Model 193-6. A Ludlum Model 9DP-1 ion chamber was used for direct measurements on the instrument. A Ludlum Model 702 Multi Channel Analyzer was used to identify the radioisotope. The radium-226 activity was estimated to be approximately 4.73 microCuries based on the dose rate measured. This material is being stored in a sealed polyethylene bag placed in a sealed 55 gallon drum and labeled as radioactive material held for disposal. "This activity meets the 30-day event report requirement for lost or abandoned radioactive material greater than 10 times the quantities specified in 10 CFR 20 Appendix C, or the Massachusetts equivalent, 105 CMR 120.297 Appendix C, which is ten times reportable quantity for Radium-226 (1 microCurie). "The Agency [MARCP] considers this event to be open until proper disposal of this instrument is confirmed." Massachusetts Docket No.: TBD THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-12-02
54406 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-11-18 11:00 | 2019-11-22 14:46 | 2019-11-22 | AGREEMENT STATE REPORT - AIRCRAFT INSTRUMENT WITH RADIUM-226 PAINTED DIAL FOUND The following information was received via E-mail: "On 11/18/2019, Massachusetts Radiation Control Program (MARCP) was informed by Schnitzer Steel Industries, Inc., that a scrap metal shipment from Devens Recycling in Danvers, MA set off the radiation monitor alarm. The vehicle was redirected back to Devens Recycling for follow-up survey and mitigation in accordance with MA RCP DOT Special Permit MA-MA-19-10. On 11/19/2019, the material was identified and segregated from the scrap metal load by an independent radiation consultant. The radioactive material discovered was radium-226 painted on the dial of an abandoned (lost), old Aircraft Turn/Slip Coordinator instrument. The dose rate at 6 inches from the instrument was 200 microR/hr. The background dose rate was 20 microR/hour. The radiation survey instrument used to locate the source was a Ludlum Model 193-6. A Ludlum Model 9DP-1 ion chamber was used for direct measurements on the instrument. A Ludlum Model 702 Multi Channel Analyzer was used to identify the radioisotope. The radium-226 activity was estimated to be approximately 6.31 microCuries based on the dose rate measured. This material is being stored in a sealed polyethylene bag placed in a sealed 55 gallon drum and labeled as radioactive material held for disposal. "This activity meets the 30-day event report requirement for lost or abandoned radioactive material greater than 10 times the quantities specified in 10 CFR 20 Appendix C, or the Massachusetts equivalent, 105 CMR 120.297 Appendix C, which is ten times reportable quantity for Radium-226 (1 microCurie). "The Agency [MARCP] considers this event to be open until proper disposal of this instrument is confirmed." Massachusetts Docket No.: 23-3968 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-12-02
54405 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-11-19 | 2019-11-22 11:10 | 2019-11-22 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received via email from the Louisiana Department of Environmental Quality (the department): "On 11/21/2019, at 1245 [CST], [the licensee] called [the department] to report that a stuck shutter [model - OHMART SH-F1 with 50 mCi of Cs-137] was found during the annual shutter check test. An equipment malfunction, which was a stuck shutter, was found on 11/19/2019, at approximately 1030 [CST] at BASF Corporation Chemicals Division. The shutter is stuck in the open condition and does not affect operation. "BASF has contacted BBP Sales, Inc. to come in to replace the handle and any other parts needing replacing." Event Report ID No.: LA190013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-12-02
54404 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-11-21 15:14 | 2019-11-22 10:50 | 2019-11-22 | AGREEMENT STATE REPORT - LOST RADIOGRAPHY SOURCE The following information was received via E-mail from the Commonwealth of Massachusetts: "The licensee (QSA Global, Inc.) made telephone notification at 0948 EST, on November 22, 2019, preceded by E-mail to the Agency (Massachusetts Radiation Control Program) day prior, that licensee was notified by carrier on November 21, 2019, that an incoming shipment from Edmonton, Canada and destined for QSA Global, Inc., Burlington, Massachusetts is missing. "The licensee provided that the shipment missing is a Model 650L source changer, serial number 2239, Type B(U) package, Yellow II, UN2916, containing a single 11.9 curie (440 GBq) iridium-192 radiography source. "The licensee provided that the shipper is Acuren Group Inc. and that the date of exportation was supposed to be October 22, 2019. The activity of the shipment was 584 GBq (15.8) curies of iridium on October 22, 2019. "The licensee reported that an active search by the carrier is underway to find the missing materials and that so far the carrier performed search of expected travel location in Boston, Massachusetts without finding the package and is tracing the expected route back through Canada, the shipment origin. "The reporting requirement is immediate and is of 105 CMR 120.281(A)(1), missing licensed radioactive materials in aggregate quantity equal to or greater than 1,000 times quantity specified in 105 CMR 120.297, Appendix C. "The Agency considers this event to be open." * * * UPDATE FROM JOSHUA DAEHLER TO DONALD NORWOOD AT 1310 EST ON 11/22/2019 * * * The following information was received via E-mail from the Commonwealth of Massachusetts: "At 1231 EST today (November 22, 2019), the licensee provided update to the Agency (Massachusetts Radiation Control Program) that the source was found; that this was a clerical error, and at no time was the shipment lost or missing. The source had been delivered on November 14, 2019, but put into the QSA Global, Inc.'s system under the wrong tracking number. "The licensee also submitted that as a notification was made, it will write the 30-day report and forward it to the Agency. In addition a QSA Condition Report will be generated to address the receipt issue." Notified R1DO (Cahill), ILTAB (Davis), and the NMSS Events Notifications E-mail group. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-12-02
54403 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2019-11-21 12:25 | 2019-11-21 21:11 | 2020-01-10 | UNIT 1 HIGH PRESSURE CORE SPRAY INOPERABLE "On 11/21/2019, at 1225 CST, as a result of Division 4 DC bus voltage oscillations, bus voltage lowered to less than the required improved technical specification (ITS) voltage of 127.6 VDC. This resulted in declaring High Pressure Core Spray (HPCS) system inoperable per technical specification LCO 3.8.4 and 3.8.9 actions. Division 4 DC bus voltage was restored to greater than 127.6 VDC at 1227 CST. The HPCS system remains inoperable due to Division 4 DC battery charger inoperability. "Since HPCS is an emergency core cooling system and is a single train safety system, this condition is reportable under 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." Clinton Power Station has implemented required compensatory actions due to the Division 4 DC battery charger and HPCS remaining inoperable. * * * RETRACTION ON 1/10/20 AT 1145 EST FROM JACOB HENRY TO KARL DIEDERICH * * * "The purpose of this notification is to retract a previous report made on 11/21/2019 (EN 54403) under 10 CFR 50.72(b)(3)(v)(D). Subsequent to the initial notification, the event and the NRC guidance in NUREG-1022 pertaining to 10 CFR 50.72(b)(3)(v)(D) were reviewed further. The evaluation determined that the Division 4 DC bus voltage oscillations were caused by a degraded but operable charger. The Division 4 battery remained fully charged during the event and its operability was not impacted. Therefore, the HPCS system remained Operable. "Under these circumstances, this event does not represent an inoperability of an accident mitigation system under 10 CFR 50.72(b)(3)(v)(D). Therefore, EN 54403 is retracted. "The NRC Resident Inspector has been notified." Notified R3DO (Hanna). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-11-21
54402 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2019-11-19 16:00 | 2019-11-21 14:53 | 2020-01-16 | AGREEMENT STATE REPORT - DENSITY GAUGE DAMAGED The following was received from the State of Arkansas via email: "The [Arkansas] Department [of Health] received notification on November 20, 2019, from licensee Professional Services Industries, Inc., that a Troxler gauge model 3430 had been struck by a skid-steer while performing routine measurements at a road construction site. The gauge was not being used at the time it was struck and the sources were in the shielded position. "Upon review of the event, it was noted that the technician quickly created a thirty foot containment barrier and notified his company's Radiation Safety Officer (RSO). The RSO for Professional Services Industries mobilized to the event location. "Once onsite, the RSO surveyed the immediate area around the damaged gauge and the gauge itself. The RSO determined that no radiation measurements were found to be above normal levels for that model of portable gauge. A leak test of the sealed sources was immediately conducted and the remnants of the gauge were collected and returned to the permanent storage location on November 19, 2019. The RSO and the Authorized User operating the portable gauge were wearing dosimetry. "The Arkansas Department of Health considers this investigation open pending receipt and review of the licensee's 30 day report." Arkansas Event No.: AR-2019-005 * * * UPDATE 0N 1/16/2020 AT 1035 EST FROM CHRIS TALLEY TO THOMAS KENDZIA * * * The following was received from the Arkansas Department of Health via email: "Upon review of the licensees 30 Day Report, received December 26, 2019, it was noted that the dosimetry badges worn by the Authorized User and RSO during the retrieval and transportation of the sources showed no measurable dose. The dosimetry badges worn were issued to the users on October 15, 2019 and the event occurred on November 19, 2019. "The report contained leak test results for the sources taken immediately following the event, November 19, 2019. The results for the leak tests in both instances were measured to be below 185 Bq (0.001microCi), considering the sources to be non-leaking sources. "The company conducted mandatory safety meetings with all staff in the PSI-Sherwood office who work with the portable gauges as a result of the event. Topics discussed during the meetings and e-mail included radiation safety, gauge security, and gauge control. The company also has re-trained the individual authorized user responsible for the gauge during the event via a 're-entrance' exam. "The radioactive sources and associated nuclear gauge remnants were returned to the manufacturer for disposal. The sources are now listed under North Carolina Radioactive Materials License #032-0182-1. "The [Arkansas] Department [of Health] considers this event to be closed, providing that no new information is received." Notified the R4DO (Young) and the NMSS Events Notification group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2019-11-29
54401 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-11-20 21:44 | 2019-11-21 04:02 | 2019-11-21 | UNIT 2 AUXILIARY FEED PUMPS INOPERABLE "At 2144 EST, on 11/20/2019, all three auxiliary feedwater pumps for Unit 2 were declared Inoperable due to check valve leakage causing the turbine driven auxiliary feedwater pump to rotate backwards and subsequently trip. At this time, two of the Unit 1 motor driven auxiliary feedwater pumps were still able to provide cross-tied feedwater in the event of a design basis accident. "At 2203 EST, the two motor driven auxiliary feedwater pumps on Unit 2 were declared operable once the discharge isolation valves for the turbine driven auxiliary feedwater pump were closed, thus preventing backflow through the turbine driven auxiliary feedwater pump and ensuring forward flow of the motor driven auxiliary feedwater pumps. "This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function. "There is no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." Unit 2 is in a 72-hour LCO 3.6.F.1 for turbine driven auxiliary feedwater pump inoperability. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-11-21
54400 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2019-11-20 10:00 | 2019-11-20 17:10 | 2019-11-20 | AGREEMENT STATE REPORT - DENSITY GAUGE DAMAGED The following was received from the State of Washington via email: "A portable gauge (CPN MC-1 DRP, S/N MD10306057, last leak test 7/18/2019) was run over by a skid-steer at a temporary job site. The gauge operator stated that he was performing measurements and set the gauge down when the skid-steer operator did not fully check his surroundings and backed over the gauge. The gauge operator immediately had everyone move to the edge of the site and they are holding there until the gauge is removed from the site and it is verified that the sources were not compromised. [WA State Department of Health] personnel arrived to the location and assisted in performing surveys to verify whether the sealed sources had been compromised. Field screening of wipes found no removable contamination, and the source rod was able to be retracted. An inspector will perform an investigation with the licensee during the routine inspection scheduled for 11/21/2019. More information to follow in an update." Washington Incident No.: 19-032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2019-11-28
54399 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2019-11-06 | 2019-11-20 17:04 | 2019-11-20 | AGREEMENT STATE REPORT - MISADMINISTRATION OF RADIONUCLIDE The following was received from the State of Oklahoma via email: "[The Oklahoma Department of Environmental Quality (ODEQ)] was notified by phone today that on November 6, Oklahoma licensee Blackwell Hospital Trust Authority (OK-32140-01) had administered a dose of Tc-99m Sestamibi to a patient that [the dose] was 24-hours old. The RSO reported that she had learned of the incident today and that the dose was administered to the intended patient. The activity of the dose originally is unknown at this time. "The licensee will be investigating the event further to determine the details of what happened. "[The ODEQ] will update this notice with more information as [the ODEQ] receives it." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2019-11-28
54398 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-11-20 13:00 | 2019-11-20 16:52 | 2019-11-20 | AGREEMENT STATE REPORT - IODINE 125 SEED MIGRATED FROM IMPLANT LOCATION The following was received from the State of New York via fax: "The New York State Department of Health (NYSDOH) was notified by a NYS medical licensee that they had an incident where an lodine-125 seed (200 microCi assayed on 11/12/2019) had migrated from the original implant location in the left breast of a female patient. "According to the licensee, two seeds were implanted on 11/18/2019 for localization during an 11/20/2019 procedure. During this procedure on 11/20/2019, it was noticed by the surgeon that one of the seeds had migrated about 2 inches from its original implant location. The surgeon and radiologist concluded that any attempt to retrieve the seed in question would compromise patient care. The seed was not retrieved as a result. "The facility contacted the New York State Department of Health two hours after the licensee determined that the lodine-125 localization seed could not be retrieved from the patient and will be submitting a written report within the required timeframe. "DOH will continue to monitor this incident." New York State incident No.: 19-07 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-11-28
54397 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2019-11-19 | 2019-11-20 16:39 | 2019-11-20 | AGREEMENT STATE REPORT - DOSE LESS THAN PRESCRIBED DELIVERED TO TREATMENT SITE The following information was received via E-mail: "On November 20, 2019, the licensee notified the Virginia Office of Radiological Health (ORH) that a medical event occurred as a result of treating a patient using a High Dose Remote Afterloader Unit (HDR). According to the written directive, 18 Gray (Gy) dose to the neck, in three (3) fractions of 6 Gy, was prescribed. On November 19, 2019, the first of the three fractions was delivered. However, the dose was delivered at 91.5 cm instead of the intended 118.1 cm. This resulted in a dose to the treatment site of approximately 0.3 Gy. "The report indicated that the error was discovered on November 20, 2019 at 0830 EST after the medical physicist re-measured the guide tube and catheter. It was discovered that the guide tube and catheter were not connected properly and this caused the dose to be delivered at 91.5 cm. "The prescribing physician and the patient were notified immediately (at 0915 EST). "ORH will review the licensee's written report and determine additional actions to be taken." Virginia Event Report ID No.: VA-19-005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2019-11-28
54396 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-11-15 11:18 | 2019-11-20 14:04 | 2019-11-20 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL FOUND IN WASTE TRANSFER TRUCK The following report was received from the State of California via email: "[The] Division Manager from Burrtec Waste Industries, Inc., reported on November 15, 2019 that his route truck activated the radiation alarm at Sun Valley Paper Stock, Inc. "Truck No. 1087, License Plate No. 7Y45540 driven by [a] Burrtec employee arrived at the transfer station at about 1130 PST on the same day. [A California Department of Public Health (CDPH), Health Physicist] arrived at the transfer station around 1430 PST and met with [the] Plant Manager. Using the FLIR Identifinder 2, the nuclide was identified as Ra-226. [The CDPH Health Physicist] contacted [the] Director of Radiation Management about the incident and the nuclide that was identified. Before [the CDPH Health Physicist] left he made arrangements with [the Plant Manager] that he will be back on Tuesday November 19, 2019 to dump the entire contents of the transfer truck to locate the radiation source and take custody of it. "On November 19, 2019, [a CDPH and a Los Angeles County Public Health (LACPH), Health Physicist] arrived at the transfer station at 1000 PST. The entire contents of the truck was dumped, and surveyed. Using the FLIR Identifinder 2 [the Health Physicists] were able to locate the radioactive source containing Ra-226. The radioactive source was a piece of metallic object. It was placed in a gallon size ziploc bag. Using a Ludlum 26-3, no contamination was noted. Using a Victoreen 451, background was 5 microR/hr, the gross exposure rate from surface was 54mR/hr, 4.8mR/hr at 1 ft, and 0.48mR/hr at 3 ft and calculated activity of 544 microCuries. The rest of the trash was surveyed and no other sources were noted. An authorization to bury form was emailed to [the Plant Manager] on the same day for the rest of the load. [The] LACPH Health Physicist took possession of the metal item and transported it to a secure location facility." California incident No.: 111519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-11-28
54395 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2019-11-14 | 2019-11-20 09:28 | 2019-11-20 | TENNESSEE AGREEMENT STATE REPORT - MEDICAL EVENT THAT RESULTED IN SKIN INJURY The following information was received from the state of Tennessee via email: "Patient treated with Lutathera (Lu-177 dotatate) on November 14, 2019. It was determined during her infusion that the Foley catheter was leaking. After the leak was identified, proper decontamination procedures were performed. The patient was instructed upon discharge that there was a chance for potential skin injury. Licensee reported that the estimated skin dose was 7 Gray (Gy). On November 18, 2019, the patient informed her provider that there was skin irritation in the peri-gluteal and peri-labia areas. It was determined that this was skin injury consistent with radiation injury. A follow-up report will be submitted upon receipt of a written report from the licensee." Tennessee Event Report ID No.: TN-19-161 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2019-11-28
54394 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2019-11-17 | 2019-11-18 19:15 | 2019-11-20 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of Washington via email: "At Selah-Home Ranch, the ranch manager noticed on Sunday morning, November 17, 2019, that someone had broken into the ranch shop building. The doors on the building had been forced open, the locked storage closet inside the building was also forced open, and the lock on a storage locker inside the storage closet was cut. Two CPN International model 503 portable nuclear gauges were stored inside the storage locker in locked storage cases. Both portable nuclear gauges were removed from the ranch shop building by the thief. One CPN International model 503 portable nuclear gauge (serial number H310606212) was found outside the ranch shop building, undamaged and still in its carrying case. The other portable nuclear gauge (believed to be serial number H35066208) is missing and stolen (approximately 50 milliCuries of americium-241/beryllium). The Zirkle Fruit Company is in the process of confirming the serial number of the stolen gauge (Sealed Source and Device Registry Number CA-0208-D-104-S). "Zirkle Fruit Company has notified the Yakima County Sheriff. The case number is 19C20517." * * * UPDATE AT 1901 EST ON 11/20/19 FROM JAMES KILLINGBECK TO THOMAS KENDZIA * * * The following update was received from the State of Washington via email: "The correct serial number of the CPN International model 503 moisture gauge that was stolen is: H371204057." Notified via email the R4DO (O'Keefe), ILTAB, NMSS Events, CNSNS (Mexico). Washington State Event No: WA-19-031 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2019-11-26
54393 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-11-05 | 2019-11-18 16:38 | 2019-11-18 | TEXAS AGREEMENT STATE REPORT - GAUGE SHUTTERS STUCK OPEN The following information was received from the State of Texas via email and phone call: "On November 18, 2019, the licensee's radiation safety officer (RSO) notified the Agency [Texas Department of State Health Services] that on November 5, 2019, during routine shutter checks on fixed nuclear gauges at their facility, it was discovered that shutters on three Ohmart model SHD-30 gauges and one Ohmart model SHD-45 gauge were stuck in the open position. These gauges normally operate with the shutters in the open position. There is no increased risk of exposure to any individual. The RSO stated the shutter checks were performed on November 5, 2019, but an email was not sent to the RSO until November 8, 2019. The RSO did not see the email until today, November 18, 2019. After seeing the email, the RSO immediately contacted a service company who responded and was onsite during the RSO's call to the Agency. "Gauge and source information: Ohmart Model SHD-30 - 120 mCi Cs-137 - SN: M5149 Ohmart Model SHD-30 - 120 mCi Cs-137 - SN: M5150 Ohmart Model SHD-30 - 120 mCi Cs-137 - SN: M6017 Ohmart Model SHD-45 - 375 mCi Cs-137 - SN: M5189 "The RSO also reported that two other gauges, one SHD-30 and one SHD-45, have broken handles that need repair. The shutters on these two gauges can still be operated. "An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident No: 9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-11-26
54392 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-11-15 | 2019-11-16 21:06 | 2019-11-16 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON NUCLEAR PROCESS GAUGE The following summary report was received from the North Carolina Radioactive Materials Branch via email: "This happened 11/15/19 and [the Nucor Environmental Manager] was made aware of the incident around [1400 EST], yesterday. "Nucor Steel has a 2015 fixed nuclear gauge in a c-frame that was due for maintenance. The gauge was deemed offline and they rolled the c-frame to a locked location where they were to perform scheduled maintenance. It was at this time that they discovered the shutter was stuck open. They tried to close the shutter (with air) but it would not close. [The Nucor Environmental Manager] explained that they roll the gauge by motor, and that during this time the shutter was opened. No employee was exposed to radiation. This gauge is exposed to the elements and [the Nucor Environmental Manager] believes there is dirt inhibiting the shutter from closing. Since they could not get it to close, they rolled the gauge back to its normal online position where it can be open and not at risk to employees. [The Nucor Environmental Manager] stated there is no damage to the source and there [are] not any leaks. "[The Nucor Environmental Manager] called the manufacturer to come perform maintenance yesterday. They arrived at his facility around [1400] today and are currently working on the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-11-25
54391 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-11-15 23:53 | 2019-11-16 03:02 | 2019-11-16 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 2353 EST on November 15, 2019, a Main Control Room (MCR) alarm was received for low control room positive pressure. "At 2355 EST, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10 Control Room Emergency Ventilation System (CREVS) was declared not met for both trains. Watts Bar Unit 1 and Unit 2 entered Condition B. "At 2355 EST on November 15, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10 Condition B was exited for both units. "This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." See similar EN #54390. The licensee has taken compensatory measures while investigating the cause. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-11-16
54390 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-11-15 22:34 | 2019-11-16 03:02 | 2019-11-16 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 2234 Eastern Standard Time (EST) on November 15, 2019, a Main Control Room (MCR) alarm was received for low control room positive pressure. "At 2236 EST, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10 Control Room Emergency Ventilation System (CREVS) was declared not met for both trains. Watts Bar Unit 1 and Unit 2 entered Condition B. "At 2236 EST on November 15, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10 Condition B was exited for both units. "This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-11-16
54389 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2019-11-15 | 2019-11-15 19:17 | 2019-11-15 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following report was received from the Kansas Department of Health and Environmental Services via email: "The gauge operator stepped approximately 15 feet away from the gauge to observe fill material being placed and a bulldozer backed over the gauge, clipping the corner of it. The gauge was not in use at the time and the source was not out. The only damage is to the yellow housing and a crack in the grey battery housing. "The RSO [Radiation Safety Officer] conducted radiological surveys using a SE International Radiation Alert Monitor 4 and obtained background readings only. "The gauge will be returned to the office and put into secure storage until it can be returned to the manufacturer for repair. "Follow-up information will be provided to NRC." The density gauge was a Troxler model 3430, serial number 25943, containing 333 MBq of Cs-137 and 1,628 GBq of Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2019-11-25
54388 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2019-11-15 08:57 | 2019-11-15 13:56 | 2019-12-17 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following was received from the Maine Radiation Control Program via fax: "At 0857 [EST on November 15, 2019,] NETCo, Inc. notified the state of Maine Radiation Control Progam [the State] that they had received leak test results from their vendor [Radiation Safety & Control Services] RSCS. One the test results indicated the Ni-63 source in a replacement component to a SAFRAN Morpho Detection Trace device was leaking. Two additional tests on components with Ni-63 sources reported detectable activity but less than 0.0005 microCi. The source contains 10.0 mCi of Ni-63 and the leak test result was 0.1968 microCi on the leaking source. "The RSO at NETCo has surveyed the work area where the leak tests were performed along with the storage container and bag that they arrived in. No detectable activity was found. NETCo will be also performing smear tests of all the areas that came in contact with the sources. The sources (components) in question will be put in a one gallon paint can awaiting proper disposal in our locked cabinet. "The State has sent an inspector to perform additional surveys. Licensee will be providing a full report to the State as information becomes available." * * * UPDATE ON 12/17/19 AT 1415 FROM TOM HILLMAN TO OSSY FONT * * * The following was received from the State via email: "The licensee and the State performed surveys and wipe samples. All surveys results were not above background. Wipe samples were all below 0.005 microCi. The wipe on the leaking source was slightly elevated but below the 0.005 microCi. The license notified the shipper of the sources, a radiation officer at Beaver Valley Power Plant. The sources were shipped for disposal and plans for disposal will continue." The state has closed the event. Notified R1DO (Werkheiser) and NMSS Events Notification. Maine Event Report ID No.: ME 19-002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2019-11-25
54387 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-11-15 | 2019-11-15 13:30 | 2019-11-15 | AGREEMENT STATE REPORT - LOST/STOLEN TRITIUM EXIT SIGN The following report was received from the Arizona Department of Health Services via email: "The Department received notification that one (1) tritium exit sign has been lost/stolen. The Department has requested additional information and continues to investigate the event." Arizona Incident Number: 19-027 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-11-25
54385 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-11-08 | 2019-11-14 10:40 | 2019-11-15 | AGREEMENT STATE REPORT - DOSE DELIVERED DIFFERS BY MORE THAN 20 PERCENT The following was received from the Pennsylvania Department of Environmental Protection (DEP; the Department) via email: "The Department received initial verbal notification from a licensee on November 8, 2019 of a possible reportable event with a detailed report on November 13, 2019 that on November 8, 2019 a reportable event occurred during an eye plaque implant (Theragenics model AgX100) containing 13 lodine-125 seeds. The seed activity was 3.728 mCi per seed for a total activity of 48.46 mCi. The prescribed dose was 8,500 rad with a planned treatment time of 101 hours. The implant was placed at 0745 [EDT] on 11/8/19. At approximately 0815 the patient complained of excessive pain. It is believed that the eye plaque had become dislodged from its proper position. It was removed at 1731 the same day. The licensee initial worst-case dose estimate to the normal sclera, conjunctiva and cornea is 1,899 rad at a depth of 1 mm for an 8.5 hour exposure. The dose at 2mm for this same time period is 1,425 rad. Both the patient and surgeon were notified. The effects on the patient are currently being evaluated. The DEP will update this event as soon as more information is provided." Event Report ID No: PA190027 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-11-22
54384 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2019-11-12 16:01 | 2019-11-12 18:23 | 2019-11-12 | OFFSITE NOTIFICATION DUE TO AN ONSITE FATALITY "This report is being made pursuant to 10CFR50.72(b)(2)(xi), 'News Release or Notification of Other Government Agency'. The Main Control Room received a report from on-site Maintenance personnel performing diving activities at the lake screen house that communications with a diver had been lost. Onsite and offsite emergency responders were dispatched. The diver was removed from the water but was unresponsive. At 1601 [CST], the LaSalle County Station Operating Department was notified by emergency responders on-site that the individual was deceased. "The Grundy County Sheriff, LaSalle County Sheriff, Seneca Emergency Services, and NRC Senior Resident Inspector have been notified. A press release is planned" | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-11-12
54383 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-10-30 | 2019-11-12 16:14 | 2019-11-12 | AGREEMENT STATE REPORT - UNDERDOSE BY 20 PERCENT OR MORE The following was received from the Ohio Department of Heath via email: "On 11/30/2019, the licensee notified the Ohio Department of Heath of a medical event involving a prostate seed implant. The licensee stated that it appears the implant template shifted prior to seed placement and resulted in a 48 percent underdose. The patient and referring physician have been notified." Isotope: Cs-131, 104.377 MBq Intended dose: 11000 rad Given dose: 6820 rad Item Number: OH190015 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-11-20
54382 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-11-12 06:00 | 2019-11-12 10:32 | 2020-01-31 | EMERGENCY OPERATIONS FACILITY OUT OF SERVICE "On November 12, 2019, the Central Emergency Control Center (CECC) was removed from service for a planned facility upgrade project. The CECC is a common Emergency Operations Facility (EOF) for the TVA Nuclear sites (Browns Ferry / Sequoyah / Watts Bar). The duration of the upgrade project is approximately 75 days. "If an emergency is declared requiring CECC activation during this period, an alternate CECC will be used. During this period, the alternate CECC will be staffed and activated using existing emergency procedures. "This is an eight-hour, non-emergency notification for a Loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the CECC will be unavailable for more than 72 hours. "The Emergency Response Organization has been notified that the CECC will be unavailable during the upgrade project and to report to the alternate CECC in the event of an emergency. There is no impact on the health and safety of the public or plant employees. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1316 EST ON 11/14/19 FROM BARUCH CALKIN TO JEFF HERRERA * * * The event information was updated to indicate that the event occurred at 0700 EST. The NRC Resident Inspector has been notified. Notified the R2DO(Musser). * * * UPDATE FROM ALAN PRUCHA TO KERBY SCALES AT 1526 EST ON 1/31/2020 * * * "The CECC facility upgrade project is sufficiently complete such that the CECC was returned to a functional status at 1350 CST on January 31, 2020. "The NRC Resident Inspector has been notified." Notified R2DO (Baptist). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-11-12
54381 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-11-09 | 2019-11-12 08:42 | 2019-11-12 | AGREEMENT STATE REPORT - DAMAGED SHUTTER ON GAUGE The following was received from the Alabama Office of Radiation Control (AORC) via fax: "On Saturday, November 9, 2019, Alabama Emergency Management Agency (AEMA) reported to [the AORC] Duty Officer a damaged gauge that had been reported from Nucor Steel Tuscaloosa. AEMA stated that the damage was minimal and with no releases to the general public. This information was reported by the Environmentalist with Nucor Steel Tuscaloosa. "The Duty Officer contacted the Environmentalist and he stated that an over fill had occurred and damaged the locking pin on the shutter of the gauge. Surveys revealed no damage to the shielding of the gauge, but the gauge will be kept secure in the caster mold until Ronan arrives for assessment of damage. The shutter mechanism is functioning, but cannot be locked in the closed position. "As of today [November 12, 2019], 0730 CST, the gauge is secure, but unlockable. The licensee has contacted the manufacturer for assessment and repair. Ronan is scheduled to arrive on November 14, 2019. The incident remains open until the appropriate repairs are completed." Alabama Incident 19-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2019-11-20
54380 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-11-12 07:00 | 2019-11-12 08:28 | 2020-01-31 | EMERGENCY OPERATIONS FACILITY OUT OF SERVICE "On November 12, 2019, the Central Emergency Control Center (CECC) was removed from service for a planned facility upgrade project. The CECC is a common Emergency Operations Facility (EOF) for the TVA Nuclear sites (Browns Ferry / Sequoyah / Watts Bar). The duration of the upgrade project is approximately 75 days. "If an emergency is declared requiring CECC activation during this period, an alternate CECC will be used. During this period, the alternate CECC will be staffed and activated using existing emergency procedures. "This is an eight-hour, non-emergency notification for a Loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the CECC will be unavailable for more than 72 hours. "The Emergency Response Organization has been notified that the CECC will be unavailable during the upgrade project and to report to the alternate CECC in the event of an emergency. There is no impact on the health and safety of the public or plant employees. "The NRC Resident Inspector has been notified." * * * UPDATE FROM BRYAN KLEIN TO DONALD NORWOOD AT 1450 EST ON 1/31/2020 * * * "The CECC facility upgrade project is sufficiently complete such that the CECC was returned to a functional status at 1400 EDT on January 31, 2020. "The NRC Resident Inspector has been notified." Notified R2DO (Baptist). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-11-12
54379 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-11-12 07:00 | 2019-11-12 07:57 | 2020-01-31 | EMERGENCY OPERATIONS FACILITY OUT OF SERVICE "On November 12, 2019, the Central Emergency Control Center (CECC) was removed from service for a planned facility upgrade project. The CECC is a common Emergency Operations Facility (EOF) for the TVA Nuclear sites (Browns Ferry / Sequoyah / Watts Bar). The duration of the upgrade project is approximately 75 days. "If an emergency is declared requiring CECC activation during this period, an alternate CECC will be used. During this period, the alternate CECC will be staffed and activated using existing emergency procedures. "This is an eight-hour, non-emergency notification for a Loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the CECC will be unavailable for more than 72 hours. "The Emergency Response Organization has been notified that the CECC will be unavailable during the upgrade project and to report to the alternate CECC in the event of an emergency. There is no impact on the health and safety of the public or plant employees. "The NRC Resident Inspector has been notified." * * * UPDATE FROM JUSTIN GALLAGHER TO KERBY SCALES AT 1620 EST ON 1/31/2020 * * * "The CECC facility upgrade project is sufficiently complete such that the CECC was returned to a functional status at 1400 EST on January 31, 2020. "The NRC Resident Inspector has been notified." Notified R2DO (Baptist) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-11-12
54378 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2019-11-09 06:35 | 2019-11-09 13:28 | 2019-11-09 | BOTH SOURCE RANGE INSTRUMENTS FOUND INOPERABLE "At November 9, 2019, at 0635 EST, it was discovered that both source range instrumentation channels were simultaneously inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(A). The neutron flux monitoring system was OPERABLE during this time period. "NRC Resident Inspectors have been notified." It was determined that with one of two source range instruments out of service for planned maintenance, an operator found the other operable source range instrument out-of-calibration. Upon further investigation, the out-of-calibration instrument had a bad potentiometer with its power supply, thus rendering both instruments inoperable. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2019-11-09
54377 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-11-06 | 2019-11-07 14:55 | 2019-11-07 | TEXAS AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was obtained from the state of Texas via email: "On November 7, 2019, the licensee's radiation safety officer (RSO) notified the Agency [Texas Department of State Health Services] that at approximately 2000 CST on November 6, 2019, one of their industrial radiography crews had been unable to retract a 113 Curie iridium-192 source (model 702, SN: TT2307) into a QSA 880 Delta exposure device (SN: D7727) at a temporary job site in Sonora, Texas. The RSO stated the drive cable had broken at the ball stop. Source retrieval was performed by authorized employees. The initial radiographers' and another of the licensee employee's self-reading pocket dosimeters read 13 and 14 mR. The two authorized source retrievers' self-reading pocket dosimeters had readings of approximately 300 mR. All dosimetry badges are being sent for immediate processing. There were no other persons in the area so there was no risk of exposure to any member of the public. The RSO and staff will examine the crank assembly and drive cable when it gets to their location on November 8, 2019. The RSO also plans to send the crank assembly/drive cable for evaluation by a third party service/repair company. The exposure device was tested multiple times using a different set of cranks following the retrieval and it operated properly. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident No: 9723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-11-15
54376 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-11-05 | 2019-11-07 14:08 | 2019-11-19 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the Commonwealth of Pennsylvania via email: "The Department [Pennsylvania Department of Environmental Protection] received notification from a licensee on November 6, 2019 that on October 8, 2019 they performed a prostate seed implant on a patient including seventy (70) stranded I-125 seeds that were implanted into the prostate treatment volume. They were Best Medical, Model 2301, Lot 48917, at 0.350 mCi per seed and 24.5 mCi total activity. The patient had an appointment on November 5, 2019 for a 30-day post-plan analysis. The CT from November 5, 2019 noted 2 seeds that were outside the prostate volume in the peril-prostatic fat. The post-plan analysis showed that 68 of 70 seeds are within the treatment volume and 94.4 percent of the treatment volume is covered by the prescription dose, which are within appropriate specifications for a prostate seed implant. The two seeds in question are considered discontinuous from the treatment volume. The licensee believes when the needle was retracted, the strand of seeds drug back with the needle and was deposited inferior from their intended location. An analysis was performed by the licensee and no adverse effects to the patient are expected. Both the patient and referring physician were notified. The Department will update this event as soon as more information is provided." Pennsylvania Event Report ID No: PA190026 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 11/19/19 AT 1148 EST FROM JOHN CHIPPO TO THOMAS KENDZIA * * * The following was received from the Commonwealth of Pennsylvania via fax: "As a result of a reactive inspection by the Department and an extensive review by the licensee, the licensee has determined the tissue containing the two seeds is within the contiguous peril-prostatic fat, which is actually physically adjacent to or touching the prostate, therefore this is not a reportable event. Further, changes noted in the radiograph taken on the day of the implant and the post-plan CT can be accounted for by the difference in patient positioning; from the lithotomy position for the implant image to the supine position for the post-plan image." Notified the R1DO (Cahill) and NMSS Event Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-11-15
54375 | 0 | FRONEK ANCHOR/DARLING ENTERPRISES |  |  |  |  | 2019-11-06 | 2019-11-06 21:07 | 2019-11-06 | PART 21 NOTIFICATION - DEGRADED SNUBBER HYDRAULIC FLUID Below is a summary of a Part 21notification received from the vendor via facsimile: The vendor, via a testing facility, identified another batch of contaminated hydraulic snubber fluid. The fluid batch number is 16DLVS852, manufactured on 4/17/16 by Momentive Performance Materials, Leverkusen, Germany. Licensees that were supplied the contaminated fluid were identified as: Palisades, Pilgrim, Browns Ferry and Sequoyah. Previous batches were identified under the Part 21 process by Lake Engineering Co. as follows: Batch Number (followed by ADAMS Ascension Number) AD965 - ML070180491 and ML070300154 ZJS1518 - ML19077A096, ML19136A044 and ML19199A034 11KLVS145 - ML18211A302, ML18295A199, ML19008A043 and ML19071A112 14ELVS145 - ML17128A465, ML17212A628, ML17313A471, ML17355A139 and ML19121A155 For further information, please contact: Walter Paszul, PE General / Engineering Manager E-Mail: walter@fronekgrp.com Phone No: ( 603) 528-1931 Fax No: ( 603) 528-6381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NH | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2019-11-06
54374 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2019-11-06 | 2019-11-06 17:04 | 2019-11-06 | AGREEMENT STATE REPORT - POTENTIAL LOST SOURCE The following is a summary of an email received from the Kansas Department of Health and Environment's Radioactive Materials Team: Apex Environmental reported that they sent their X-ray fluorescence to Massachusetts via a common carrier to be resourced. They have a delivery receipt, but have been unsuccessful in contacting the company. Perhaps the device is being held for payment. The State has requested additional information from Apex and will follow up with Massachusetts' Radiation Control Program and the vendor to determine the status of the device. Kansas Event Report ID No: KS190010 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2019-11-14
54373 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-11-01 | 2019-11-06 16:34 | 2019-11-06 | AGREEMENT STATE REPORT - CONTAMINATION DUE TO DISLODGED CATHETER The following was received from the Colorado Radioactive Materials Unit via email: "On 11/6/19, the Colorado Department of Public Health and Environment was notified of a potential reportable contamination event. On 11/1/19, approximately 12 hours after an I-131 MIBG [meta-iodobenzylguanidine] administration (293.6 mCi) on 10/31/19, the patient's catheter was dislodged [while asleep]. I-131 contaminated urine spilled out of the catheter and contaminated the patient, bed, bedding, and floor under the bed. Most of the spill was located under the bed. The patient was decontaminated after the spill was identified and has since been released from the facility. After the patient was released, the extent of the spill was identified by the licensee. The treatment room has not been released for unrestricted use as of 11/6/19. Dose rates taken by the licensee indicate the potential for greater than 5 times the ALI [annual limit on intake] prior to decontamination efforts." Colorado Event Report No: CO190018 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-11-14
54372 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-11-04 | 2019-11-06 09:12 | 2019-11-06 | AGREEMENT STATE REPORT - GAMMA KNIFE FAILS TO FUNCTION AS DESIGNED The following information was received via fax: "On November 4, 2019 the licensee was performing a mask treatment with the Elekta Gamma Knife Icon containing Cobalt 60. The treatment was interrupted when the High Definition Motion Management tracking system lost communication with 1 minute and 29 seconds remaining from shot B6, (planned for 2 minutes 13 seconds) and 2 minutes 36 seconds remaining for B3 (No treatment was delivered from this shot). The sources safely retracted into their home position and the software message prompted the user to reinitiate the Gamma Knife system; however, an error message occurred on each attempt to reinitiate. The system was then rebooted; however, the same error occurred again. The patient was removed from the treatment vault and a service call was made to Elekta. The onsite service engineer arrived that same day to troubleshoot and new parts were ordered and arrived on November 5, 2019. The intent is to complete the remaining treatment on November 5, 2019 once the Gamma knife repair and subsequent QA is completed. The doctor and patient were informed immediately. No overdose to anyone has occurred and no harm is expected to the patient. The [PA Bureau of Radiation Protection] will update this event as soon as more information is provided." Pennsylvania Event Report ID No: PA190025 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-11-14
54371 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-11-05 18:11 | 2019-11-06 01:17 | 2019-11-11 | TWO DIESEL GENERATORS CONCURRENTLY INOPERABLE "On November 5, 2019 at 1811 CST, station service water A and the Division 1 diesel generator (DG) were declared inoperable based on the results of an engineering evaluation of a Class 3 piping leak. This was determined to be a potential inability to fulfill a safety function due to concurrent inoperability of two emergency diesel generators. Division 3 DG was inoperable due to planned maintenance on November 4, 2019 at 0000 CST. "This event is being reported an 8-hour non-emergency notification per 10 CFR 50.72 (b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function (Accident Mitigation). "Division 3 DG and high pressure core spray have been restored, and the fulfillment of the accident mitigation safety function has been restored. "The NRC Senior Resident Inspector has been notified." * * * RETRACTION ON 11/11/19 AT 1739 EST FROM GABRIEL HARGROVE TO BETHANY CECERE * * * "This was initially reported under 10 CFR 50.72(b)(3)(v)(D). However, subsequent engineering evaluation determined that the condition did not affect safety system operability. The evaluation determined that the leakage was within allowable limits and piping structural integrity was not challenged at this time nor in the past three years. "The Division 1 DG and SSW A were at the time of discovery OPERABLE and EN54371 is being retracted." The licensee will notify the NRC Resident Inspector. Notified R4DO (Drake). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-11-06
54370 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-11-05 | 2019-11-05 19:00 | 2019-11-05 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK OPEN The following was received from the Texas Department of State Health Services (the Agency) via email: "On November 5, 2019, the licensee notified the Agency that during routine, 6-month leak tests and shutter operation checks [at their Freeport, TX location], it found the shutter on one of its Vega, model SHF-2B, fixed nuclear gauges was stuck in the open position. The gauge contains a 1,000 milliCurie cesium-137 source (SN 0325CR). The gauge normally operates with the shutter in the open position. The gauge is mounted on the side of a vessel and there is no risk of exposure to any individual. The licensee has contacted a service company to schedule repairs. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident # I-9722 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-11-13
54369 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2019-11-04 05:35 | 2019-11-04 09:06 | 2019-11-04 | MANUAL REACTOR TRIP DUE TO STEAM DUMP TRANSIENT "At 0535 [EST] on November 4, 2019, with Unit 1 in mode 1 at 15 [percent] power, the reactor was manually tripped due to the lifting of an 'A' Main Steamline Safety Valve following a Condenser Steam Dump transient. The trip response was not complex, with all systems responding normally post-trip, and all control rods fully inserted into the core. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the Main Condenser by using the Condenser Steam Dump Valves. Offsite power is available and is currently supplying Normal and Emergency busses. The plant is currently stable in mode 3. Unit 2 is unaffected by this event and remains at 100 [percent] power in mode 1. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-11-04
54368 | -1 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2019-11-02 10:40 | 2019-11-03 11:38 | 2019-12-06 | POTENTIAL OVEREXPOSURE OF RADIOGRAPHER The following was received from the Mississippi Division of Radiological Health via phone: A radiographer was exposed to a 100 Curie Ir-192 source for 8 minutes while changing film during a radiography shot. The radiographer was not wearing dosimetry and did not have a hand held radiation meter. While changing film, the radiographer realized the source had not been retracted and left the area. This was not an equipment malfunction, and the source was retracted when it was realized that the radiographer had been exposed. The radiographer reported the event to the Mistras Radiation Safety Officer (RSO). Estimated dose is 20 Rem to the hands and 19.6 to 19.7 Rem whole body. The radiographer was sent to a local hospital for bloodwork. * * * UPDATE FROM ROBERT SIMS TO HOWIE CROUCH VIA EMAIL AT 1706 EST ON 11/8/19 * * * "[A state of Mississippi Health Physicist investigator] interviewed the RSO on 11/7/2019 and investigated the incident. After reviewing and questioning the incident details, [the investigator] found the following evidence that may determine this may not have been an overexposure. The assistant radiographer retracted the source, but did not perform the bump test to fully retract the source into the locked position. This caused the assistant radiographer to believe the source was still in the collimator. When returning to change the film, he saw the red button on the camera instead of green which would indicate the source was in the locked position. The assistant was not using dosimetry, rate alarm or survey instrumentation. He appears to have panicked, came down the ladder, and couldn't get the crank to move in. The lead radiographer then grabbed the crank and cranked out and back in immediately to fully retract the source into the camera. [The investigator] reviewed compliant leak tests of camera and wipes along with maintenance and service reports before and after the incident and the RSO could not replicate any problems that would prevent them from retracting the source. There was no malfunction with the camera or the cranks. It appears that the source was in the end of the camera but not in the fully shielded position, which could allow some radiation out of the tube that the source enters. However, we do not know how much because the assistant was not wearing any dosimetry. The other assistant's dosimetry [assistant radiographer 2] only picked up 1 milliRem of dose but he was approximately 25 ft. away with steel shielding from the tank they were working on in between him and the source. [The investigator is] waiting on the emergency reading of the doses recorded on the OSL badges used by the crew and follow up doctor's visit. [The investigator] interviewed [the assistant radiographer on] 11/8/2019 at 1549 CST. [The assistant radiographer] reports that he had more blood drawn today and will provide results next week. He said he feels great and has had no sickness such as nausea, pain or redness and swelling in the hands. Will update again next week after receiving lab results." * * * UPDATE FROM ROBERT SIMS TO THOMAS KENDZIA VIA EMAIL AT 1409 EST ON 11/19/19 * * * "[A state of Mississippi Health Physicist investigator] interviewed the assistant radiographer [who was not wearing dosimetry] on 11/12/2019. [The assistant radiographer] reported that lab was drawn on 11/3/2019 and 11/8/2019. Both labs results returned within normal limits and [the assistant radiographer] has no physical symptoms of radiation sickness. [The assistant radiographer] remains at regular work duties recommended in his physician reports that he provided to [the investigator]. [The RSO] was interviewed on 11/11/2019 and provided the Landauer dosimetry report for the three RT crew members. The crew received new dosimeters on 11/1/2019 and they were sent for an emergency read the day after the incident. "[The] lead radiographer received 109 milliRem, [assistant radiographer 2 who was wearing dosimetry] received 269 milliRem and [the assistant radiographer] received 150 milliRem although he was not wearing his dosimeter during this incident. [The assistant radiographer] is also on UT and other duties until the end of the year until his new annual dose limit year starts January 1, 2020. This is upon the recommendation of [the investigator] because although it has been determined that [the assistant radiographer] did not receive an over exposure equaling or exceeding the 15 to 25 RAD to cause radiation sickness, it does not rule out if he did or did not exceed his 5 rem TEDE. The licensee's personnel believe that the source was in the end of the camera, but not in the fully locked position because the red button was showing on the QSA 880 camera when [the assistant radiographer] returned from changing the digital film plate. Due to his elevation up on the tank and the tank shielding we cannot use any of the other crew members dosimetry to make any determinations. However based on the medical reports and physical evidence it appears that [the assistant radiographer] has no physical symptoms from radiation sickness. [The assistant radiographer] will have his last lab test on 11/22/2019, if it is normal, [the assistant radiographer] states that the physician intends to release him completely from all medical care related to this incident." Notified the R4DO (O'Keefe) and NMSS Events Notification via email. * * * UPDATE AT 1333 ON 12/5/2019 FROM ROBERT SIMS TO JEFF HERRERA * * * "As the investigation continued [a state of Mississippi Health Investigator] reviewed additional information received throughout the day on 11/18/2019, but sufficient time did not exist to thoroughly review the latest findings to include them on the 11/19/2019 update. The current additional findings are as follows: [the state of Mississippi Health Physicist Investigator] Re interviewed all personnel again, and requested all lab results and Physician findings from [the assistant radiographer]. "[The assistant radiographer] willingly provided all CBC and cytogenetic lab test results that were taken on 11/3/2019, 11/8/2019, and 11/22/2019. [The assistant radiographer] stated that the physician reported the lab results to be within normal limits and the physician released [the assistant radiographer] from medical care on 11/22/2019 that had resulted from this incident. "[The state of Mississippi Health Physicist Investigator] also found during the second interview of personnel that the films that were with [the assistant radiographer] and located on the pipe during the 8 minutes that it took [the assistant radiographer] to change out the film were processed later and were acceptable images. [The state of Mississippi Health Physicist Investigator] attached the images in the file as evidence to support that [the assistant radiographer] was not overexposed. If the films had been exposed with an open source out for 8 minutes they would be blacked out from overexposure. The original exposure time to produce the radiograph with the film combination, distance and thickness of steel for this job was 1 minute. Even with digital radiography, an image receptor plate can be overexposed beyond acceptable exposure limits, and cannot be window leveled to make it an acceptable image, but this was not the case. The radiographer and RSO reported that an attempt to crank out and retract the source was made by each assistant and the radiographer when trying to retract the source after [the assistant radiographer] returned down the ladder. This would explain why the images produced were acceptable radiographs. There had been enough exposure to properly expose the film but not overexpose it. This appears to support the possibility that the source was not out the entire 8 minutes while [the assistant radiographer] was changing the film and moving the source tube on the jig. At this point [the assistant radiographer] was also down the ladder 25 feet away with the other radiographers who were wearing the required dosimetry behind the shielding of the tank. Three (3) violations were issued and corrective actions have been submitted to the Mississippi Division of Radiological Health All records are included in the 2019 Incident file at the Mississippi State Department of Health Division of Radiological Health. [The state of Mississippi Health Physicist Investigator] considers this investigation and incident closed. If you require any further information, documentation or have questions, please contact [The state of Mississippi Health Physicist Investigator]. "Mississippi Incident No.: MS-190005, NMED #190535" Notified the R4DO (Taylor) and NMSS (via email). * * * RETRACTION ON 12/6/19 AT 1452 FROM ROBERT SIMS TO CATY NOLAN * * * "A review of the incident details represented a 'substantial potential for an exposure in excess of 10 CFR 20.' However, there was not enough evidence to definitively prove there was an overexposure due to the details listed throughout this investigation. These included the assistant who was allegedly overexposed. This individual never experienced any signs of radiation sickness or erythema or redness to the hands throughout the investigation period to its close date on 12/3/2019. None of the other crew members' dosimeter readings exceeded occupational dose limits. On 12/2/2019, Mistras also requested anonymity for the individuals involved in this incident. "All documentation concerning this incident investigation is stored in Mississippi State Department of Radiological Health 2019 Incident File, under incident Report No. MS-190005." NMED #190535 Notified the R4DO (Taylor) and NMSS (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR | 20.2202(b)(1) |  |  |  | 0 | 2019-11-11
54367 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-11-03 08:00 | 2019-11-03 09:23 | 2019-12-10 | PLANNED LOSS OF EMERGENCY RESPONSE FACILITIES AND EQUIPMENT "At 0800 CST on November 3, 2019, Comanche Peak began a planned modification on the Unit 2 Plant Computer System. During this modification, the ability to perform emergency assessment in the Technical Support Center (TSC) and the Emergency Operations Facility (EOF) will be impacted. Since the ability to perform emergency assessment is not expected to be restored within 72 hours, this is reportable per 10 CFR 50.72(b)(3)(xiii) as an event that results in a loss of emergency assessment capability. "During this modification, the Control Room will continue to have the ability to perform emergency assessment. If an Alert, Site Area Emergency, or General Emergency is declared during this modification, communicators dedicated to performing emergency assessment will be stationed in the Control Room, TSC, and EOF. The Plant Computer System modification is scheduled to be completed on November 24, 2019 and a follow-up ENS notification will be made once the Unit 2 Plant Computer System is declared functional. "The NRC Resident Inspector has been informed." * * * UPDATE FROM MATT KARL TO HOWIE CROUCH AT 1104 EST ON 12/10/19 * * * Unit 2 Plant Computer System has returned to service at 0756 CST on 12/10/19. The NRC Resident Inspector has been notified. Notified R4DO (Groom). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-11-03
54366 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2019-11-02 15:15 | 2019-11-02 23:03 | 2019-11-02 | REFUELING WATER STORAGE TANK DECLARED INOPERABLE DUE TO LOW LEVEL "At 1515 on November 2, 2019, the Refueling Water Storage Tank (RWST) was declared inoperable due to a Low Head Safety Injection relief valve discharging to the Safeguards Sump during routine surveillance testing. The leakage from the Low Head Safety Injection system in conjunction with a postulated Design Basis Accident (DBA) Loss of Coolant Accident (LOCA) with transfer to Safety Injection Recirculation may result in dose exceeding the Dose Analysis of the Exclusion Area Boundary (EAB) and the Control Room, which is common to both Unit 1 and Unit 2. This condition may not be bounded by existing design and licensing documents; however, it poses no impact to the health and safety of the public or plant personnel. The Low Head Safety Injection relief valve has been isolated to prevent further leakage, and makeup to the RWST completed. At 1602 on November 2, 2019 the RWST was declared Operable. This event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(B), (C), (D) as an Unanalyzed Condition and a condition that could have prevented the Fulfillment of a Safety Function." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2019-11-02
54365 | -1 | WATERFORD | 3 |  |  | [3] CE | 2019-11-02 10:54 | 2019-11-02 12:49 | 2019-11-06 | SAFEGUARDS REPORT The licensee discovered a vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC resident inspector. * * * RETRACTION ON 11/06/2019 AT 1402 EST FROM MARIA ZAMBER * * * The licensee determined that the vulnerability was recovered in the time prescribed by their Physical Security Plan; therefore, this event is not reportable pursuant to 10 CFR 73.71. Notified R4RDO (DRAKE) and 73.71 Safeguards Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-11-02
54364 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2019-11-01 03:16 | 2019-11-01 10:03 | 2019-11-01 | HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM INOPERABLE "On November 1, 2019 at 0316 EDT, Nine Mile Point Unit 2 (NMP2) received Control Room annunciation for HPCS SYSTEM INOPERABLE and inoperable status light indication for TRIP UNITS OUT OF FILE/POWER FAIL. Initial investigation has identified a potential failed 24 vdc power supply which supplies power to the HPCS trip units for system initiation and control. The HPCS system has been declared inoperable per TS 3.5.1 resulting in an unplanned 14 day LCO. "All other plant systems functioned as required. "NMP2 is currently at 100 percent power in Mode 1. "This condition is reportable under 10 CFR 50.72(b)(3)(v)(D) as, 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.'" The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-11-01
54363 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-10-31 | 2019-10-31 17:13 | 2019-10-31 | GENERAL LICENSEE LOST THREE PORTABLE DEVICES CONTAINING AM-241 The following was received from the Illinois Emergency Management Agency (the Agency) via phone and email: During Agency [Illinois Emergency Management Agency] efforts to pursue an annual self-inspection report from a general licensee (First America Metal Corp), it was discovered that three Niton XLp-818 XRF [x-ray fluorescence analyzer] devices containing 30 milliCuries of Am-241 each could not be accounted for. The facility is located in Morris, IL. On October 28, 2019, the Agency asked for physical verification of the devices. The devices were initially shipped from the manufacturer in 2005 and 2006. Agency staff confirmed with the manufacturer that these devices had not been received or returned (confirmation received 10/31/19). The Agency again contacted the licensee on October 31, 2019. At that point, the licensee confirmed that search activities have ceased and they were officially declaring the devices as lost. Correspondence from the US Dept. of Commerce, Office of Export Enforcement, dated February 16, 2010, indicates there may have been export of Niton XRF devices by this general licensee; however, it does not appear to be related to the devices missing at this time. There is no indication of theft or intentional diversion. The quantity of material present, while not presenting an immediate exposure concern to any individuals requires immediate reporting to IEMA/NRC. By design, electronic opening of the shutter requires that the operator power on the unit and enter a password. As a precaution, the instrument will only operate for a six year period before an inspection by the manufacturer is required. Due to the fact the unit has not been serviced, the software in the instrument will not allow the instrument to be operated. In the shielded position, the radiation levels surrounding the device are indistinguishable from background. Should the tungsten source holder be manually opened, exposure rates may be up to 122 mR/hour at 5 cm. Illinois Item Number: IL190034 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-11-08
54362 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2019-10-30 00:26 | 2019-10-30 01:20 | 2019-10-30 | UNUSUAL EVENT DUE TO RELEASE OF FLAMMABLE GAS "On 10/30/19 at 0026 EDT, an Unusual Event (HU3) was declared due to a release of flammable gas to the Unit 1 Pipe Penetration area (Reactor Auxiliary Building). The hydrogen supply valve to the area has been isolated. The area is being ventilated and follow-up air sampling will be performed. "The NRC Resident Inspector has been notified." Notified DHS SWO, FEMA Ops Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE FROM FRED POLLAK TO DONALD NORWOOD AT 0521 EDT ON 10/30/2019 * * * "The Notice of Unusual Event was terminated at 0454 EDT on 10/30/19. The area has been purged and normal access restored." The licensee notified the NRC Resident Inspector. Notified R2DO (McCoy), NRR EO (Miller), and IRD (Grant). Notified DHS SWO, FEMA Ops Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Defueled; FMode1: Defueled | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2019-10-30
54361 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-10-29 | 2019-10-29 14:39 | 2019-10-29 | AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE The following report was received from the Arizona Department of Health Services (Department) via email: "The Department received notification from the licensee that a Troxler 3411 nuclear density gauge (serial number 07083) was stolen from the back of a licensee's truck. The gauge contains approximately 8 mCi of Cs-137 and 40 mCi of Am-241. The Phoenix police department was notified at approximately 0730 MST [on 10/29/2019] and a police report was filed (Report Number 19-1879828). The Department has requested additional information and continues to investigate the event." Arizona Incident Number: 19-026 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-11-06
54360 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-29 09:19 | 2019-10-29 13:58 | 2019-10-29 | INADVERTENT ACTUATION OF SIRENS "At approximately 0945 CDT, on 10/29/2019, the Braidwood Station main control room was notified of the inadvertent actuation of 17 full sounding sirens affecting Braidwood Station in Will County, Illinois. Will County notified Exelon of the inadvertent actuation that occurred on 10/29/2019, at 0919 CDT, during the performance of regular maintenance on the siren equipment at the Laraway Communication Center at the Will County Sheriff Dispatch Center. "This event is reportable per 10 CFR 50.72(b)(2)(xi), News Release or Notification of Other Government Agencies. "The Braidwood NRC Resident Inspector has been notified." The siren equipment has been repaired and restored to service. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-10-29
54359 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2019-10-29 09:09 | 2019-10-29 13:25 | 2019-10-29 | FITNESS FOR DUTY - CONTRACT SUPERVISOR FAILED RANDOM TEST A contract employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's badge has been confiscated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2019-10-29
54358 | 0 | DRESDEN | 2 | 3 |  | [2] GE-3,[3] GE-3 | 2019-10-29 09:19 | 2019-10-29 13:12 | 2019-10-29 | INADVERTENT ACTUATION OF SIRENS "At approximately 0945 CDT, on 10/29/2019, the Dresden Station main control room was notified of the inadvertent actuation of nine full sounding sirens affecting Dresden Station in Will County Illinois. Will County notified Exelon of the inadvertent actuation that occurred on 10/29/2019, at 0919 CDT, during the performance of regular maintenance on the siren equipment at the Laraway Communication Center, the Will County Sheriff Dispatch Center. "This event is reportable per 10 CFR 50.72(b)(2)(xi), News Release or Notification of Other Government Agencies. "The Dresden NRC Resident has been notified." The siren equipment has been repaired and sirens have been returned to service. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-10-29
54357 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2019-10-29 03:15 | 2019-10-29 12:56 | 2019-10-29 | AGREEMENT STATE REPORT - STOLEN SOURCES The following information was received via email: "Licensee called [the Mississippi Division of Radiological Health] to report a carjacking of one of its drivers carrying two packages of PET doses. The carjacking occurred at approximately 0315 CDT at a gas station in Jackson, MS. The local law enforcement was notified. The vehicle has still not been recovered." Stolen sources were F-18. Source 1 had an activity of 6000.627 mCi at 0149 CDT and source 2 had an activity of 1694.932 mCi at 0151 CDT. Incident Report No.: MS-190004 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2019-11-06
54356 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-10-28 | 2019-10-28 12:27 | 2019-10-28 | AGREEMENT STATE REPORT - LOST SEALED SOURCE GAUGE The following was received from the Illinois Emergency Management Agency (the Agency) via phone and email: "During Agency efforts to pursue an annual self-inspection report from a general licensee (Midwest Industrial Metals), it was discovered that a Niton XLp-818 XRF device containing 30 milliCuries of Am-241 could not be accounted for. According to licensee staff, the device was sent to the manufacturer for repair/evaluation. The licensee elected not to have the device repaired and it was returned to them. In June of 2019, the Agency asked for a physical verification of the device. Agency staff again contacted the licensee on October 28, 2019. At that point, the licensee confirmed that search activities have ceased and they were officially declaring the device as lost. The licensee reports that there is no indication of theft or intentional diversion. This matter will remain open pending appropriate enforcement action." Item Number: IL190031 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-11-05
54355 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2019-10-27 16:05 | 2019-10-27 22:36 | 2019-10-27 | WATER FOUND IN CONTROL ROOM EMERGENCY VENTILATION AIR FILTRATION UNIT "On October 27, 2019, at 1605 CDT, the Control Room Emergency Ventilation (CREV) was declared inoperable due to finding water in the system's Air Filtration Unit (AFU) filter enclosure. Technical Specification 3.7.4, Condition A, was entered which requires the CREV system to be restored to an operable status in seven days. No other systems were out of service at the time this was declared inoperable. "The CREV system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), "Event or Condition That Could Have Prevented Fulfillment of a Safety Function," because the CREV system is a single train system required to mitigate the consequences of an accident. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-10-27
54354 | 0 | SCHMUCKER, PAUL, NOHR, & ASSOCIATES |  |  |  |  | 2019-10-26 | 2019-10-26 11:29 | 2019-10-27 | DAMAGED MOISTURE DENSITY GAUGE While in use on a job site with the source extended, a Troxler Model 3430 moisture density gauge was damaged by a skid loader. The source was able to be retracted into the shielded area of the gauge but the shield cannot be closed due to damage to the bottom shield plate. The licensee has established a 15 foot radius boundary per their emergency procedure and will be obtaining a survey meter to verify radiation levels at the boundary. The licensee will be getting local assistance to secure the source for transportation back to their storage facility. A Troxler Model 3430 normally contains a 44 mCi Am-241/Be source and a 9 mCi Cs-137 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-11-04
54353 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2019-10-25 14:35 | 2019-10-25 15:30 | 2019-10-25 | LOST AND IMMEDIATELY FOUND SPECIAL NUCLEAR MATERIAL "This is a non-emergency 10 CFR 74.11 report. "On October 25, 2019, at approximately 1435 EDT, a Westinghouse employee located at a secure Westinghouse facility, notified EH&S staff that a small package containing radioactive material had been delivered to that location. That location is a remote office building outside of the Columbia plant's Controlled Access Area. "The package was unopened and contains approximately 16 grams of uranium in uranium oxide pellet form. "There were no health or safety consequences to the public, workers or the environment. "This report has been entered into the Corrective Action Program (CAP) and the package will be properly returned to the Columbia Plant." Notified: DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA EOC, and FDA EOC. Notified via E-mail: FDA EOC, FEMA NWC, DHS NuclearSSA, FEMA NRCC SASC, and CWMD-Watch. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 74.11(a) |  |  |  | 1 | 2019-11-04
54352 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-10-24 | 2019-10-25 10:19 | 2019-10-25 | AGREEMENT STATE REPORT - FAILED SHUTTER ON A PROCESS GAUGE The following report was received from the Alabama Department of Public Health via email: "Representative reported that personnel found a gauge to have a failed shutter. Representative reported that the shutter is failed in the closed position. Representative reported that [the] gauge was discovered in the reported condition during some maintenance operations. Representative stated that the gauge was discovered in its reported condition on 10/24/2019. Representative reported this to [the] Agency [Alabama Department of Public Health] on 10/25/2019 at 0813 [CDT]. "Gauge contains source s/n 8829GK, a 500 mCi Cs-137 source. Gauge is reported as an Ohmart model SH-2. No known device issues that could have caused a failed shutter. "Licensee is in the process of ordering parts for repair. Representative stated that ABB will repair the gauge." Alabama Incident number 19-29. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2019-11-04
54351 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-24 20:51 | 2019-10-25 03:24 | 2019-10-25 | VALID UNDERVOLTAGE ACTUATION DURING EDG SEQUENCER MAINTENANCE "On October 24, 2019, at 2051 Central Time, while performing Train C Sequencer maintenance, a valid undervoltage actuation signal was sent to Unit 2 Emergency Diesel Generator (EDG) 23. The ESF Train C bus loads were shed but EDG 23 did not automatically start because it had been placed in Pull-To-Stop to support the sequencer maintenance activities. EDG 23 was taken out of Pull-To-Stop by Control Room staff to allow it to auto start and load the bus. As a result of the bus strip signal, the in service Spent Fuel Pool Cooling Pump secured. Spent Fuel Pool Cooling was restored with no measurable increase in pool temperature. "The reactor was not critical and reactor decay heat removal was not challenged throughout the event. "This actuation is reportable per 10 CFR 50.72(b)(3)(iv)(A) due to the automatic actuation of a system listed in 10 CFR 50.72(b)(3)(iv)(B). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-10-25
54350 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2019-09-06 | 2019-10-24 17:04 | 2019-10-24 | PART 21 - EMD FUEL INJECTORS SEIZED PLUNGER AND BUSHING The following is a summary of information that was received via facsimile: Engine Systems, Inc. (ESI) was notified by a nuclear customer that three of 20 recently installed fuel injectors seized after a short amount of engine run time. Examination of the plunger and bushing (P&B) from each injector identified particles consistent with the base material of the P&B embedded in the scar marks associated with seizures. The root cause of the seizures is attributed to residual machining debris from the manufacturing process. This batch of injectors had been refurbished in 2013 and the P&Bs were replaced as part of the rework activity. These part number mechanical unit fuel injectors are used on various model EMD 645 diesel engines. The engine utilizes one injector per cylinder; therefore, failure of one injector will render the associated cylinder inoperable. An EMD 645 engine will typically tolerate one inoperable cylinder and maintain rated load; however, multiple inoperable cylinders (as in the case of multiple fuel injectors) will further decrease engine output and likely prevent the engine from carrying out its required load. This adversely affects the ability of the emergency diesel generator set to perform its safety-related function. This issue only applies to injectors in inventory that have not been installed, which should be returned to ESI. For injectors that have been installed in an engine and have accumulated more than two hours of run time, then the injector is not susceptible to seizure from this type of issue and no further action is required. It has been shown that P&B seizures related to foreign material occur within the first two hours of engine operation. The affected part numbers are 40084714, 40084715, 40084720, 40084724, 40084725, 40099335, 5228895-RR, 5229250-RR, 5229315-RR, 5229325-RR, 40084714-RR, 40084720-RR, 40084723-RR, 40084724-RR, 40099335-RR. A list of affected customers by injector part number is contained in Appendix A of the Part 21 report, which include Crystal River, Turkey Point, Exelon Generation Company, Beaver Valley, Watts Bar, Clinton, Saint Lucie, Sequoyah, Fort Calhoun, Southern California Edison, Davis-Besse, Oconee, Point Beach, Kewaunee, Dresden, Surry, GE Company, Browns Ferry, Energy Northwest, Oyster Creek, Arkansas Nuclear One, Monticello, Nine Mile Point, Entergy Operations Inc., Tennessee Valley Authority, LaSalle, Perry, Quad Cities, Fitzpatrick, and River Bend. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-10-24
54349 | 0 | ARMED FORCES RADIOBIOLOGY RSCH INST |  |  |  | 1100 KW TRIGA MARK-F | 2019-10-24 | 2019-10-24 16:30 | 2019-10-24 | UNACCOUNTED FOR FISSION CHAMBER On October 24, 2019, during performance of an annual inventory, one fission chamber could not be accounted for. After a thorough search, the fission chamber was declared missing. The fission chamber was manufactured by Reuter-Stokes with a part number of: RS-P6-0805-134 and a serial number of: 14K024C5. The fission chamber contains 0.12988 grams of Uranium-235. The last known accounting of this fission chamber was during the previous annual inventory. The licensee is continuing to search for the fission chamber. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 0 | MD | NPR |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-11-01
54348 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2019-10-24 10:35 | 2019-10-24 16:25 | 2019-10-24 | AUTOMATIC DEPRESSURIZATION SYSTEM INOPERABLE "At 1035 CDT the Automatic Depressurization System (ADS) was rendered inoperable due to the failure of the 'A' Safety Vent Valve (SVV) Compressor (SVV-C4A) to manually start with SVV-C4B tagged out. System pressure slowly dropped below 131 psig (normal pressure is 165 psig). This caused the ADS safety relief valves to be declared inoperable. The station entered Technical Specification 3.5.1 Condition G. The Required Action was to be in Mode 3 in 12 hours. As a result, the station was in a condition that could have prevented the fulfillment of a safety function. "The breaker for SVV-C4B was reset and the clearance for SVV-V4B was released. System pressure was restored to greater than 131 psig at 1116 CDT which allowed exit of the action statement to be in Mode 3 in 12 hours. System parameters are currently stable in the normal pressure range. Investigation for the cause of the system failure is ongoing. "No radiological releases have occurred due to this event from the unit." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-10-24
54347 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2019-10-24 15:24 | 2019-10-24 16:24 | 2019-10-24 | OFFSITE NOTIFICATION "Holtec Decommissioning International has notified the State of New Jersey that during the conduct of Industrial Site Remediation Act (ISRA) non-radiological site investigation field sampling and analysis activities at the Oyster Creek site, soil and groundwater exceedances to New Jersey Default Impact to Groundwater Soil Levels, Residential Direct Contact Soil Remediation, Non-Residential Direct Contact Soil Remediation and Class IIA Groundwater Quality Standards were identified. These exceedances are reportable under New Jersey Administrative Code NJAC 7:26C. That notification was made at 1524 EDT." The NRC Regional Inspector and the State of New Jersey were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-10-24
54346 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-10-23 | 2019-10-24 11:51 | 2019-10-24 | INCORRECT BRACHYTHERAPY SEED SET USED FOR IMPLANTATION The following information was received via E-mail: "The licensee informed the Department [Pennsylvania Department of Radiation Protection] that a brachytherapy seed set was implanted in the wrong patient. It is reportable per 10 CFR 35.3045(a)(2)(iii)(B). "On October 23, 2019, the licensee was performing a permanent brachytherapy during which an incorrect prostate brachytherapy seed set (lsoRay Model CS-1) was brought to the procedure room and 6 Cs-131 seeds were implanted into the prostate of a patient. The procedure was stopped immediately when the error was recognized. The correct seeds were then brought to the operating room and the procedure was completed using the correct seeds. Forty Seven (47) seeds, 85 gray, (3.135 mCi) were prescribed and 3.03 mCi given. The Authorized User notified the urologist and patient this morning (10/24/19). No harm is expected to the patient. "The cause of the event is unknown at this time. The Department will perform a reactive inspection. More information will be provided as received." Pennsylvania Event Report ID No: PA190024 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-11-01
54345 | 0 | CURTISS-WRIGHT |  |  |  |  | 2019-09-04 | 2019-10-22 17:07 | 2019-10-22 | PART 21 - INCORRECTLY WIRED SOCKET SIDE QUICK DISCONNECT CONNECTORS The following information was received via fax: "To maintain compliance with 10 CFR 21, this initial notification is to document the failure to comply of basic components which were found to have a defect and were supplied to a licensed operating nuclear power plant. "On September 4, 2019 Curtiss-Wright Nuclear Division, Huntsville Operations was notified by Duke Energy - Catawba Nuclear Station of a possible deviation of a supplied EGS Quick Disconnect Connector (QDC), P/N 880701-102 (S/N: 47801 and 47802) where two socket side connectors were wired incorrectly. Condition Report (H19-4603) was generated to internally document all actions and investigations on this matter. "On October 17, 2019, the basic components with the possible deviation were returned to Curtiss-Wright and evaluated. The evaluation found that the socket sides were wired incorrectly by color code but the wire markers were correctly labeled. If installed using the wire marker delineation, the wiring would be correct, but if the basic components were installed using the color code, there could be the possibility of incorrect wiring. Since Curtiss-Wright is not privy to how the operating plant installs these connector(s), if installed using the color code it may cause a possible safety hazard and therefore considered defective. "The condition was caused by human error and was isolated to the two subject socket side QDCs. "The defected QDCs were returned and replacement connectors were built and supplied to Duke Energy - Catawba Nuclear Station. "Even though this is considered an isolated event, corrective actions to help prevent recurrence are in the process of being implemented. These include, but are not limited to, adding an additional specific peer check during manufacturing and adding a specific final inspection check to confirm actual wire insulation color code, if applicable. "Based on our evaluation these two connectors were the only ones affected by this defect. They have been removed from service and replacements have been provided. Once all corrective actions to prevent recurrence are completed, an official close out letter will be generated." If you would like to discuss this further please contact the following: Chris Covan, Quality Assurance Manager, at (256) 924-7414 or ccovan@curtisswright.com, or Tim Franchuk, Director of Quality Assurance, at (513) 201-2176 or tfranchuk@curtisswright.com. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-10-22
54344 | -1 | OZARK MEDICAL CENTER |  |  |  |  | 2019-10-22 13:30 | 2019-10-22 16:24 | 2019-10-29 | ADMINISTRATION OF DOSE TO WRONG INDIVIDUAL The following is a synopsis of information received via phone: On 10/22/19, at approximately 1330 CDT, 22.0 mCi of Tc-99m-white blood cells was administered to the wrong patient. The patient was confused and not able to correctly confirm that they were the patient receiving the dose. This patient was informed of event, but has a power of attorney who will also be notified. This patient's condition means the dose, carried by the white blood cells, will possibly end up in their bowel. Extra monitoring is being performed. The correct patient will be rescheduled. * * * RETRACTION ON 10/29/2019 AT 1257 EDT FROM JOHN MCKENZIE TO ANDREW WAUGH * * * After discussion with R3 (Gattone), Ozark Medical Center is retracting this event because the delivered dose does not exceed the reportable limits described in 10 CFR 35.3045. Notified R3DO (Riemer) and NMSS Events Notification (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2019-10-30
54343 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-10-21 02:30 | 2019-10-22 15:41 | 2019-10-22 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the California Department of Public Health Radiologic Health Branch (RHB) via email: "On 10/21/19, the RSO [radiation safety officer] contacted RHB to report a stolen moisture density gauge. The gauge is a CPN Model MC1Elite, S/N 30492, containing 50 mCi of Cs-137 and 50 mCi of Am-241. It was stolen on 10/21/19 around 0230 [PDT] from the back of a truck parked at the gauge user's residence. The gauge was being used at a temporary job site near the user's residence and it was stolen by cutting the locks securing the gauge. The licensee provided video footage of the crime taking place from a video camera at the user's residence. The licensee had contacted the Salinas Police Department to notify them of the incident (Case #19-101002). A flyer has been posted with a reward for the safe return of the gauge. RHB will be following up on this investigation." CA 5010 No.: 102119 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-10-30
54342 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-10-21 | 2019-10-21 18:58 | 2019-10-21 | AGREEMENT STATE REPORT - LOST SHIPMENT OF MO-99 GENERATORS The following was received from the Arizona Department of Health Services (the Department) via email: "The Department received notification on October 21, 2019, that a licensee's shipment of radioactive material, sent July 9, 2019, with an expected delivery date of July 18, 2019, has not been received by the intended Consignee/Receiver, and is currently unaccounted for. The shipment contained five (5) Mo-99 generators, totaling approximately 192 milliCuries (7.1 GBq). The Department has requested additional information and continues to investigate the event." Arizona incident 19-025 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-10-29
54341 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-12-29 02:20 | 2019-10-21 15:52 | 2019-10-21 | INVALID ACTUATION OF A SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. On December 29, 2018, at approximately 0220 Central Standard Time (CST), Browns Ferry Nuclear Plant (BFN), Unit 3 experienced an unexpected loss of power to the 3A Reactor Protection System (RPS) Bus due to the trip of the 3A RPS motor generator (MG) set. This resulted in Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations, and initiation of Standby Gas Treatment Trains A, B, and C and Control Room Emergency Ventilation System Train A. All affected safety systems responded as expected. "This event is being reported as a late 60 day non-emergency notification. This missed notification was identified on August 23, 2019. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The cause of the trip of the RPS MG Set was a failure of the motor winding insulation of all three phases. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Condition Reports 1478564 and 1543534. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-10-21
54340 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2019-10-21 00:50 | 2019-10-21 01:23 | 2019-10-21 | UNUSUAL EVENT DECLARED DUE TO NO CONTROL ROD MOVEMENT WITH MANUAL SCRAM ACTUATION "While Unit 3 was shutting down for 3R22 refueling outage, the mode switch was taken to shutdown position which is a manual scram signal. The manual scram signal was not received from the mode switch. A subsequent manual scram was inserted with the use of the manual scram push buttons. The Unit 3 reactor is shutdown with all rods inserted." Unit 2 was unaffected by the event and remains in Mode 1 at 100 percent power. The licensee notified the NRC Resident Inspector, Pennsylvania and Maryland State Agencies, local government. A media press release is planned. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email), FEMA Region 3 Watch Office (email). * * * UPDATE AT 0316 EDT ON 10/21/19 FROM KEVIN GROMANN TO BETHANY CECERE * * * "Conditions no longer meet an Emergency Actuation Level and will not deteriorate. Unit 3 reactor is shutdown with all control rods fully inserted. The NOUE was terminated at 0230 EDT." The licensee notified the NRC Resident Inspector, Pennsylvania and Maryland State Agencies, local government. Notified the R1DO (Jackson), NRR EO (Miller), IRDMOC (Gott), R1RA (Lew via email), NRR (Nieh via email), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email), FEMA Region 3 Watch Office (email). | 0 | 0 | 0 | 0 | 5 | 0 | 0 | -1 | 0 | N | M | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Startup | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2019-10-21
54339 | -1 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2019-10-20 10:30 | 2019-10-20 19:21 | 2019-10-24 | CONTROL ROOM ENVELOPE BREACH "At 1030 CDT, it was discovered that the loop seal on the condensate drain was empty for VUC-9 Control Room AC Unit. This creates a breach in the Control Room envelope. Unit 2 entered [Technical Specification] T.S. 3.7.6.1 Action D. Unit 1 is in Mode 6; therefore, not in a mode of applicability." Compensatory action were being performed and the licensee was in the process of sealing the loop. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM DONNA BOYD TO DONALD NORWOOD AT 1336 EDT ON 10/24/2019 * * * "This report is being retracted. The Control Room Envelope (CRE) provides a safety function which limits radiological dose to occupants to no more than 5 rem for 30 days post-accident. The dose limitation assumes the occupants are stationed within the CRE 24 hours a day for the entire 30-day period. The CRE also functions to protect occupants from potential hazards such as smoke or toxic chemicals. "The CRE is declared inoperable when a potential breach is identified, regardless of the ability to seal the breach. With respect to the event of October 20, 2019, the water level in a loop seal could not be maintained at the desired level. Subsequent evaluation determined that sufficient water was maintained in the loop seal to prevent a breach of the CRE. "The subject reporting criterion is based on the assumption that safety-related systems, structures, and components (SSCs) may no longer be capable of mitigating the consequences of an accident. In accordance with NUREG 1022, 'Event Report Guidelines 10 CFR 50.72 and 50.73,' a report may be retracted based on a revised operability determination. The CRE remained operable; therefore, this report may be retracted." The licensee notified the NRC Resident Inspector. Notified R4DO (Young). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-10-20
54338 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2019-10-18 02:07 | 2019-10-18 10:45 | 2019-11-19 | INADVERTENT OPENING OF MAIN TURBINE BYPASS VALVES POTENTIONALLY AFFECTED SAFE SHUTDOWN CAPABILITY "At 0207 [CDT], the Bypass Electro-Hydraulic Control (EHC) system was secured for planned maintenance. When the Bypass EHC pumps were secured, both of the Main Turbine Bypass Valves unexpectedly opened to approximately 4.5 percent. Plant parameters indicated no impact to Turbine Control Valve position, Reactor Pressure, Turbine First Stage Pressure, or Main Steam Line flows. There were no other abnormal indications noted. With the Turbine Bypass Valves partially open, there is a potential to affect instrumentation that trips on high Turbine First Stage Pressure. Therefore, this event is being reported as a potential loss of Safety Function. At 0256, the Bypass EHC system pumps were restored and the Turbine Bypass Valves Closed. "No radiological releases have occurred due to this event from the unit." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM THONG LE TO HOWIE CROUCH AT 1019 EST ON 11/19/19 * * * "This Event Notification was contingent on the Main Turbine Bypass Valves opening which resulted in the inoperability of Turbine First Stage Pressure monitoring instrumentation. A detailed review of system design and plant parameter trends has confirmed that the Main Turbine Bypass Valves remained closed for the duration of the event, permitting the instrumentation systems dependent on accurate Turbine First Stage Pressure to perform their respective design and licensing basis functions. Valve drift in the open direction was observed by position indication when hydraulic control pressure was removed. However, the valves were at an over-travel closed position prior to the event allowing the valves to settle at a position where an internal spring could provide closing force to the valve disc. Multiple plant parameter trends including Turbine First Stage Pressure, Reactor Pressure, Main Steam Line flows, and Main Turbine Bypass Valve discharge line temperatures indicate that the Main Turbine Bypass Valves remained closed for the duration of the event." The licensee has notified the NRC Resident Inspector. Notified R4DO (O'Keefe). | 75 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-10-18
54337 | -1 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2019-10-17 19:51 | 2019-10-18 02:28 | 2019-10-31 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY DEGRADED "At 1951 [EDT] on October 17, 2019, fretting indications on the reactor coolant system pressure boundary piping (pressurizer spray line) were identified. This condition does not appear to meet original construction code, ANSI B31.1, 1967 Edition thru summer 1971 Addenda. The condition will be resolved prior to plant startup. This event is being reported as an eight-hour non-emergency notification per 10 CFR 50.72(b)(3)(ii)(A). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." This condition will be corrected prior to the plant entering Mode 4. * * * RETRACTION ON 10/31/19 AT 1450 EDT FROM JIM SCHWER TO BETHANY CECERE * * * "An engineering evaluation has determined that the subject fretting is not considered a flaw, but instead is considered wear. Appendix F of Section III of the ASME Boiler and Pressure Vessel Code was applied and it was determined that the pressurizer spray line piping maintained its required design safety functions in the as-found condition. The wear has been repaired during the current refueling outage in accordance with the original construction code (ANSI B3l.l, 1967 Edition through summer 1971 Addenda) as well as Owner's Requirements. "The NRC Resident Inspector has been notified." Notified R1DO (Young). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2019-10-18
54336 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-10-16 | 2019-10-17 16:56 | 2019-10-17 | AGREEMENT STATE REPORT - MEDICAL EVENT The following is the summary of an email received from the state of North Carolina: A patient was scheduled for an intravascular brachytherapy treatment on 10/16/2019. The treatment utilized a Novoste transfer device with an Sr-90 source. The prescribed dose for the treatment was 23.0 Gy, which corresponds to a planned treatment time of 5 minutes and 47 seconds. The treatment was delivered and the source return process was initiated. Resistance was encountered returning the source to the transfer device and the team had to commence the emergency bail-out procedure. The catheter was extracted while it was still attached to the device and both were placed in the bail-out box. The patient, room, and box were all surveyed. The survey confirmed that the source was in the bail-out box. The box was then transferred to a designated secure location. Because of the additional time elapsed between the expected return of the source to the transfer device and the securing of the source in the bail-out box it is possible that the patient could have received an additional dose of up to 6.98 Gy. The manufacturer of the transfer device was notified of this event on 10/16/2019. The patient and referring physician were both notified on 10/17/2019. Device Information: Transfer Device Manufacturer: Novoste (Best Medical) Model: Beta Cath System Serial: 91806 Source Information: Sr-90 Manufacturer: Novoste Activity: 2.01 GBq (4/16/03) Serial: ZB607 NC Tracking Number: NC 190036 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-10-25
54335 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2019-10-16 | 2019-10-16 19:05 | 2019-10-16 | AN ITEM RELIED ON FOR SAFETY (IROFS) DETERMINED TO BE INADEQUATE The following was reported by Westinghouse Electric Company via email: "As part of a review to revalidate the design of passive safety controls, on October 16, 2019 an engineering calculation was completed which demonstrates that one of two independent and redundant passive overflow devices used in the Solvent Extraction (SOLX) process was undersized for its credited safety function. This passive overflow device is an Item Relied On For Safety (IROFS), designated as SOLX -115. The IROFS prevents the potential backflow of uranium bearing solution from the SOLX process into the commercially-provided, chemical supply drums. These drums are non-favorable geometry (NFG) containers used to add chemicals to the batch process. Upon review of the calculation, the process engineer reported the issue at 3:05 p.m. [EDT] to the Environmental Health and Safety (EH&S) department. "The design of the second, redundant passive overflow IROFS in this accident sequence (SOLX-117) has been validated and is available and reliable to perform its safety function. Under the new calculation, with no credit for SOLX-115, the overall likelihood index (OLI) for this scenario increased from -6 to -3. Therefore, the 10CFR70.61 performance requirements (OLI < -4) are not satisfied. "The process was shut down, and the NFG chemical drums were isolated from the process until appropriate controls are established. This event has been entered into the facility's Corrective Action Program (CAP)." The licensee notified the NRC Region II office (McCurry). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2019-10-16
54334 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-10-15 | 2019-10-16 17:20 | 2019-11-26 | CONTAMINATINON OF HOT LAB DUE TO BREAKING CAPSULE The following report was received from the Georgia Radioactive Materials Program via email: "A patient diagnosed with hyperthyroidism was scheduled to receive 30 mCi of Iodine-131 on Oct 15, 2019. The patient informed the AU [authorized user] that they could not swallow the capsule, so the AU proceeded to break the capsule in half and pour the contents in water to easily administer to the patient. The patient and AU were in the treatment room when the AU began to break the capsule. The AU then went to the hot lab where he successfully broke the capsule using a syringe needle. The nuclear technician inquired as to what was happening in the hot lab and realized that there may be a potential contamination issue and contacted the RSO [Radiation Safety Officer]. The areas were surveyed and determined to be contaminated with Iodine-131 was the hot lab, hallway in front of the hot lab, counter of the treatment room, scrub pants, shoes and socks. "The RSO took the scrub pants and sock and shoes and placed them in an area for DIS [decay in storage]. He proceeded to clean the area from least contaminated, the hallway and treatment room, but could not get it completely clean. The treatment room is a less used room and isolated so that room could be sealed off and secured. The hallway is posted and cordon off. Currently, the RSO is uncertain as to how much contamination is in the hot lab and has the room sealed and secured until he can further assess the area. "The staff who were working in the area consisted of the RSO, Assistant RSO, nuclear technician, and AU were monitored for thyroid uptake. Results were negative. The patient was not monitored for thyroid uptake since the patient was sitting at the opposite side of the treatment room opposite of where the contamination occurred. The floor of the room and adjacent hallway was free of contamination. In addition, the patient had a Iodine-123 uptake one week prior. So they would have had some residual Iodine-123 still in the body. The patient was never administered the Iodine-131 in water. "The RSO will prepare a full report discussing the incident, root cause and correction plan within 15 days. An associate will be assigned to the event." * * * UPDATE AT 1733 EST ON 11/26/2019 FROM IRENE BENNETT TO JEFF HERRERA * * * The following is a synopsis of a report received from the Georgia Radioactive Materials Program via email: On October 30, 2019 a reactive inspection was performed by the Georgia Radioactive Materials Program. The areas of contamination were verified to have a physical barrier to prevent inadvertent entry and signs posted to warn individuals of the contaminated areas. The Grady Memorial Hospital Radiation Safety officer (RSO) stated that the lab will not re-open until the contamination level reaches background, approximately 80 days from the time of the incident. The RSO temporarily removed the authorized user from administrating any therapeutic doses indefinitely. The RSO reported that there will be proper training for authorized users, technologists and residents who are involved in administering radioactive materials. A technologist will be required to be present in the room where I-131 is administered. Instructions will be added about not opening or breaking capsules containing radioactive materials to hospital procedures and refresher training will encompass the procedures. The physician did not think a bioassay was necessary for the patient as they were not exposed. Notified the R1DO (Henrion) and NMSS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-10-24
54333 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2019-10-16 08:29 | 2019-10-16 14:28 | 2019-10-16 | OFFSITE NOTIFICATION DUE TO THE TRANSPORT OF A POTENTIALLY CONTAMINATED PERSON OFFSITE "On October 16, 2019, at 0829 [EDT], an individual was transported for treatment to an offsite facility to address a personal medical issue. Due to the nature of the medical condition, only a partial survey could be completed prior to transport. Follow-up surveys performed by radiation protection technicians identified no radiological contamination of the worker or of the ambulance and response personnel. "This event is being reported per 10 CFR 50.72(b)(3)(xii), 'Any event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment.' The NRC Resident Inspectors have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2019-10-16
54332 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-08-20 11:33 | 2019-10-16 10:22 | 2019-10-16 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. On August 20, 2019, at approximately 1133 hours Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN), Unit 2 experienced an unexpected loss of the 2A Reactor Protection System (RPS). This resulted in Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations, and initiation of Standby Gas Treatment Trains A, B, and C and Control Room Emergency Ventilation System Train A. All affected safety systems responded as expected. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The cause of the RPS MG Set trip was dirty potentiometer windings on an Over Voltage Relay. The dirt prevented the potentiometer's wiper from contacting its windings, resulting in erratic setpoint values. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Condition Reports 1542603, 1542608, and 1542569. "The NRC Resident Inspector has been notified of this event." | 0 | 73 | 0 | 0 | 73 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-10-16
54331 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2019-10-14 | 2019-10-15 19:49 | 2019-10-15 | THREE INDIVIDUALS SENT TO HOSPITAL DUE TO CONCERNS AFTER COMPLETION OF MAINTENANCE WORK "On October 14, 2019, out of an abundance of caution, three employees were sent to the hospital after reporting an unusual taste in their mouths following completion of maintenance work on the hydrofluoric acid (HF) process equipment. "The employees stayed at the hospital overnight for observation and were released today with no work restrictions. Medical treatment was provided to one employee, therefore requiring a report to South Carolina Occupational Safety and Health Administration (SC OSHA) on October 15, 2019. "The area around the equipment was monitored for airborne concentration levels of HF with no readings approaching any safety limits in the immediate or adjoining areas. Access to the area is controlled, and the equipment remains shutdown pending completion of maintenance activities and appropriate testing before return to operation. "There were no health or safety consequences to the public or the environment, and there was no radioactive material involved. "This report has been entered into the facility Corrective Action Program (CAP)." The licensee notified the NRC Region II office (McCurry). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-10-15
54330 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2019-10-15 12:10 | 2019-10-15 19:14 | 2019-11-22 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE "On 10/15/19 at 1210 [EDT] Peach Bottom discovered a degraded spring hanger (23DBN-H39) associated with Unit 3 High Pressure Coolant Injection (HPCI) system. The hanger is located downstream of MO-3-23-14 HPCI Steam Supply Valve before the HO-3-23-4513 Turbine Stop Valve. A review of the piping and support design analysis were performed and concluded the U3 HPCI turbine inlet nozzle would potentially exceed its allowable stresses. Following Engineering review, U3 HPCI was declared inoperable at 1743 [EDT]. "This report is being submitted pursuant to 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." * * * RETRACTION ON 11/22/19 AT 0851 EST FROM DAN DULLUM TO BETHANY CECERE * * * "Additional evaluation by Engineering personnel determined that the degraded spring hanger would have no adverse effect on the subject piping or HPCI turbine nozzle structural integrity. Pressure, deadweight, and seismic stresses were within allowable limits. Non-destructive examination (NDE) of the piping and nozzle was performed to identify any signs of cracking, yielding, or defects. NDE results were satisfactory. The degraded spring hanger did not effect the Unit 3 HPCI system operability and this call is being retracted. "The NRC Resident Inspector has been notified." Notified R1DO (Cahill). | 0 | 81 | 0 | 0 | 81 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-10-15
54329 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-14 09:11 | 2019-10-15 19:10 | 2019-10-15 | MAIN STEAM LINE (MSL) RADIATION MONITOR REMOVED FROM SERVICE FOR PLANNED MAINTENANCE "At time 0911 [CDT], Main Steamline Radiation Monitor 2-RUK-2325/2327 (MAIN STEAM LINE 2-01/2-03 RADIATION MONITOR) was removed from service for planned maintenance. "Compensatory measures were in place prior to removing the monitor from service to assure adequate monitoring capability available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 radiation monitor serves as a backup with alarm function and Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL [Main Steam Line] 2-01 and MSL 2-03. "With this radiation monitor non-functional, with compensatory measures in place, and the monitor NOT expected to be returned to service within 72 hours, the condition is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant (CPNPP) has assurance of steam generator integrity and fuel cladding integrity and there is negligible safety significance to the current condition with respect to the public health and safety perspective. "Corrective actions are being pursued to complete maintenance and restore 2-RUK-2325/2327 to functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-10-15
54328 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-12 08:55 | 2019-10-12 15:54 | 2019-10-12 | FITNESS-FOR-DUTY REPORT - UNOPENED CAN OF BEER FOUND INSIDE PROTECTED AREA One unopened can of beer was discovered in a break room refrigerator within the plant's Protected Area. The individual that brought in the can of beer was identified. That individual is a Pacific Gas and Electric employee but does not normally work at Diablo Canyon. That individual was brought in to support work during the Unit 2 refueling outage. When questioned, the individual stated that the can of beer had been brought in to give to another person to see if that person liked that brand of beer (the beer was apparently from a small specialty brewery). A behavioral observation was performed on the individual who brought in the can of beer. There was no indication of alcohol use by the individual. The individual's access to the plant has been suspended pending further investigation. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2019-10-12
54327 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-10-11 | 2019-10-11 18:29 | 2019-10-11 | AGREEMENT STATE REPORT - MISADMINISTRATION OF Y-90 MICROSPHERES The following information was received from the Texas Department of State Health Services (the Agency) via E-mail: "On October 11, 2019, the Agency was contacted by the licensee's radiation safety officer (RSO) who reported a medical event had occurred at their facility. The RSO stated that the event involved a patient who was to receive a treatment with yttrium-90 microspheres. The administering physician had difficulties setting up the injection apparatus and installed an additional piece of tubing in-line with the injection tubing. Because of the additional length of tubing, the patient received only five percent of the prescribed activity. The RSO stated there would be no adverse effects on the patient. The RSO stated both the patient and the prescribing physician have been notified of the error. The RSO stated that the bulk of the microspheres (activity) remained in the tubing and no contamination was found in the area where the treatment occurred. The RSO stated the physician decided they would perform the procedure again and use the activity needed to bring total activity administered to the activity initially prescribed. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9721 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-10-21
54326 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-10-11 | 2019-10-11 16:35 | 2019-10-11 | PROCESS GAUGE STUCK SHUTTER The following information was receive from the Texas Department of State Health Services (the Agency) vial e-mail: "On October 11, 2019, the Agency was notified by the licensee's radiation safety officer (RSO) that the shutter on a Vega Americas SHLG-2 source holder containing a 5,000 milliCurie cesium-137 source was stuck in the open position. The stuck shutter was found during a routine check of the gauge. Open is the normal operating position. The RSO stated the gauge does not pose an exposure risk to any individual. The RSO stated a service company has been contacted to look at the gauge. The RSO stated they have not determined if they will repair or replace the gauge. Additional information will be provided as it is received in accordance with SA 300." Texas Incident No.: I-9720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-10-21
54325 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2019-10-11 13:00 | 2019-10-11 14:22 | 2019-10-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN INITIATED "At 1300 EDT, a Technical Specification required shutdown was initiated at Calvert Cliffs Unit 1. Technical Specification Action 3.1.4.C (Restore Control Element Assembly [CEA] alignment) was entered on 10/11/2019 at 1100 EDT, with a Required Action to reduce thermal power to less than 70 percent Rated Thermal Power and restore CEA alignment within 2 hours. This Required Action was not completed within the Completion Time; therefore, a Technical Specification required shutdown was initiated, and this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(i). "At 1345 EDT, CEA alignment was restored and Technical Specification 3.1.4 (Control Element Assembly Alignment) was met. Reactor Power is being stabilized. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 30 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2019-10-11
54324 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2018-06-06 10:30 | 2019-10-10 17:35 | 2019-10-10 | PRESSURE INSTRUMENT ISOLATION VALVE FOUND IN INCORRECT OPEN POSITION "On October 10, 2019, at approximately 1830 MDT, a responsible individual at Louisiana Energy Services LLC, dba URENCO USA, was informed that on June 5, 2018, at approximately 1600 MDT, pressure instrument isolation valve, 1001-471-1A12, was found open when it should have been shut to maintain the pressure boundary of autoclave 1LS1. The autoclave is used to homogenize UF6 and obtain samples. The autoclave pressure boundary forms IROFS10 [Item Relied on for Safety]. "Prior to the event, on May 31, 2018, annual maintenance was performed on the autoclave as required by the IROFS10 surveillance requirements. Subsequently, a homogenization and UF6 sampling was performed June 1st through June 5th on a 30B cylinder of UF6. During preparations for a subsequent homogenization cycle, valve 1001-471-1A12 was found open. The valve should have remained closed from the previous homogenization. There was not an initiating event (no release of UF6) and no initiation of an accident sequence. The valve has been shut and the IROFS boundary has been restored. The plant is in a safe configuration. "This event has been identified in UUSA's corrective action program as EV 133619 and a causal investigation is planned." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2019-10-18
54323 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2019-10-03 | 2019-10-10 15:22 | 2019-10-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE-DENSITY GAUGE The following information was received via e-mail: "A Troxler 3430 portable surface moisture-density gauge, S/N 19274, was damaged when it was hit by an excavator at a temporary job site in Shoreline, Washington. Damage included: the screws had been ripped out of the top shell of the gauge, and the metal base of the gauge was cracked on the side. The gauge operator verified that the source rod was intact and retracted into the safe position, and returned the gauge to the licensee's main office for storage, as directed by his radiation safety officer. A Washington Department of Health inspector surveyed the gauge and verified that the neutron and gamma readings were similar to the radiation profile shown in the sealed source and device registry certificate for the gauge. The inspector checked for removable radioactive material contamination on the outside of the gauge by wiping the crack in the side of the base of the gauge, the seam where the top shell joins with the metal base of the gauge, and the source rod opening and bottom plate. No removable contamination was found. The damaged gauge will be shipped for disposal in the near future. "The gauge contained a 40 mCi Am-Be source, S/N 47-14734, and a 4 mCi Cs-137 source, S/N 50-8931." Washington Reference Number: WA-19-028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2019-10-18
54322 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2019-10-10 11:22 | 2019-10-10 12:14 | 2019-10-10 | OFFSITE NOTIFICATION DUE TO ENVIRONMENTAL REPORT TO ANOTHER GOVERNMENT AGENCY "At 1122 EDT, on October 10, 2019, Duke Energy initiated voluntary notification of North Carolina State and local officials per the guidance in Nuclear Energy Institute (NEI) 07-07, 'Industry Groundwater Protection Initiative - Final Guidance Document,' due to release of tritiated water in excess of 100 gallons. "On October 8, 2019, at approximately 1300 EDT, Brunswick plant personnel drilling as part of an ongoing site project, damaged a storm drain discharge line. The resulting leak was isolated and water around the impacted area was sampled for gamma emitters and tritium. No gamma emitters were detected. The tritium concentration was below the Environmental Protection Agency (EPA) drinking water limit of 20,000 pCi/L. "The leak has been stopped and excavation and repair efforts are in progress. "This notification is being made solely as a four-hour, non-emergency notification for a notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-10-10
54321 | -1 | BARRETTS MINERALS |  |  |  |  | 2019-09-25 08:00 | 2019-10-10 11:27 | 2019-11-04 | SAFETY EQUIPMENT FAILURE - STUCK SHUTTER On September 25, 2019, at approximately 0800 MDT, while preparing to perform electrical maintenance on a density gauge, the shutter on the gauge was found stuck in the open (normal) position. Upon contacting Berthold, the device manufacturer, the licensee was instructed to contact the NRC to make this notification. The source is a Cs-137, 20 mCi source, S/N 846, manufactured in March of 1990. There is no additional exposure to plant personnel or the public due to the position of the shutter. Berthold is scheduled to replace the shield on October 29, 2019. * * * RETRACTION ON 11/4/2019 AT 0931 EST FROM ROBERT REAP TO CATY NOLAN * * * After discussion with R4 (Bolger), the licensee is retracting this event because the device is a general license device, not a specific license device, which does not meet the reporting requirements described in 10 CFR 30.50(b)(2). Device is a BSI Instrument LB 7400 series gauge. Notified R4DO (Drake) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-10-18
54320 | -1 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2019-10-09 23:40 | 2019-10-10 02:17 | 2020-03-18 | POTENTIALLY CONTAMINATED INDIVIDUAL TRANSPORTED TO AN OFFSITE MEDICAL FACILITY "At 2340 CDT, on October 09, 2019, a site contractor was transported offsite for treatment at an offsite medical facility. Due to the nature of the medical emergency, the individual was not thoroughly surveyed prior to being transported offsite. This is an eight-hour notification, non-emergency for the transportation of a contaminated person offsite. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xii). "Following the individual being transported offsite, but prior to the individual arriving at the offsite medical facility, the individual was confirmed to not be contaminated. This occurred at approximately 2350 CDT, on October 09, 2019. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 3/18/2020 AT 1350 EDT FROM RICHARD LENGFORD TO BRIAN LIN * * * "Farley Nuclear Plant is retracting this notification based on the information available at the time of the notification: Health Physics personnel had completed surveys that determined that the contract worker, ambulance, and responders were free of contamination prior to reaching the hospital. The initial report was made to alert the NRC based on the individual being potentially contaminated due to radioactive surveying being deferred to support prompt medical attention. Based on the subsequent determination that the individual was not contaminated the reporting requirements of 10CFR50.72(b)(3)(xii) are not met and this event report is being retracted. "The NRC Resident Inspector has been notified." Notified R2DO (Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2019-10-10
54319 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-10-09 13:00 | 2019-10-09 15:55 | 2019-10-09 | CONCURRENT NOTIFICATION DUE TO PLANNED MAINTENANCE ON FIRE PROTECTION SYSTEM "At 1300 (EDT) on October 9th, 2019, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the electric fire pump supporting the Fuel Manufacturing Operation (FMO) was being taken offline for maintenance. An electrical disconnect was being replaced. Compensatory measures were enacted. The pump was restored to operation at 1348 (EDT). Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will notify NRC Region 2 and the North Carolina Department of Health and Human Services Radiation Protection Branch. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-10-17
54318 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-09 10:23 | 2019-10-09 12:48 | 2019-10-09 | AUTOMATIC START OF EMERGENCY DIESEL GENERATOR AND AUXILLIARY FEEDWATER SYSTEM "At 1023 EDT, on October 9, 2019, with Unit 2 in Mode 1 and 100 percent power, an actuation of the Emergency Diesel Generator and Auxiliary Feedwater Systems occurred. The reason for the Emergency Diesel Generator auto-start was the loss of power to the 4160V 1E electrical bus 2AA02 due to a fault at an offsite electrical switchyard. The Emergency Diesel Generator started and energized the 4160V safety bus, and Auxiliary Feedwater Systems automatically started as designed when the undervoltage condition on the safety bus was detected. This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Emergency Diesel Generator and Auxiliary Feedwater Systems. "There was no impact on the health and safety of the public or plant personnel. The NRC resident has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-10-09
54317 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-09-05 | 2019-10-08 17:08 | 2019-10-08 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE STOLEN FROM JOB SITE The following report was received from the Arizona Department of Health Services via email: "The Department [Arizona Department of Health Services] received notification on October 8, 2019, that a Humboldt 5001 series, SN#5820, portable gauge was stolen from a work site in San Luis, Arizona, on September 5, 2019. The portable gauge contains 44 milliCuries of americium-241 and 11 milliCuries of cesium-137. The Arizona Department of Public Safety and the San Luis Police Department were notified of the event by the licensee on September 5th and a police report was filed. The Department [Arizona Department of Health Services] has requested additional information and continues to investigate the event." Arizona Incident Number: 19-023 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-10-16
54316 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-10-07 | 2019-10-07 19:06 | 2019-10-08 | TEXAS AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the state of Texas via email: "On October 7, 2019, the licensee notified the Agency [Texas Department of State Health Services] that one of its Troxler model 3411-B moisture density gauges, containing 40 milliCuries of americium-241/beryllium and 8 milliCuries of cesium-137, had been secured inside the bed of a technician's pickup truck at a temporary job site when the truck was stolen. The technician had driven over to and gone into a port-a-can. There were other jobsite workers in the area. When the technician came back outside, the other workers told him his pickup was being driven away - they had not realized he was not driving it until they saw him. They attempted to follow the vehicle but were unsuccessful in locating it. The local police department was notified but have not yet arrived on the scene. The licensee reported that per the technician, insertion rod on the gauge was locked, the transport case was locked and was secured with two chains to the bed of the truck, and the tailgate was locked. The licensee stated it does not appear that an exposure could result to persons in unrestricted areas. The licensee and technician are attempting to collect information from persons who were in the area. More information will be provided as it is obtained in accordance with SA-300. "Gauge: Troxler Model 3411-B, SN: 8489 "Sources: Americium-241/Beryllium, 40 milliCuries, SN: 47-4872, Cesium-137, 8 milliCuries, SN: 40-5728" Texas Incident No.: 9719 * * * UPDATED ON 10/8/19 AT 1214 EDT FROM KAREN BLANCHARD TO KERBY SCALES * * * The following update was received from Texas Department of State Health Services via email: "The licensee has notified the Agency that the vehicle and gauge were recovered by the local police at approximately 2230 CDT on October 7, 2019. The gauge was still fully secured in the vehicle as it had been when the vehicle was taken. More information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Keller), ILTAB, NMSS Events, and CSNS Mexico (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-10-15
54315 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2019-10-01 12:00 | 2019-10-07 15:07 | 2019-10-07 | AGREEMENT STATE REPORT - MISSING / RECOVERED PORTABLE DENSITY GAUGE The following was received from the Maryland Radiological Health Program via phone and email: "On October 2, 2019, at 0825 EDT, the Maryland Department of the Environment Radiological Health Program (MDE-RHP) was contacted via telephone by the Vice President and Office Manager of Engineering Consulting Services Mid-Atlantic, LLC (ECS), Maryland license number MD-03-092-01, that a portable density gauge was missing. The gauge was identified as a Troxler model 3430, S/N 34485, with nominal activities of 10 mCi Cs-137 and 40 mCi Am-241/Be. The last leak test was performed on July 23, 2019. "On October 1, 2019, at approximately 1200 EDT, ECS management started to track down the location of the portable density gauge as an internal audit revealed that this gauge was not signed out by the user. Later that afternoon, the gauge user was found at home by ECS management. The user then revealed that his vehicle was in a minor accident in Hanover, MD and the Anne Arundel County police impounded his vehicle with the gauge locked in the trunk. Multiple attempts were made to recover the portable gauge after hours on October 1, 2019 from the impoundment lot but without success. The gauge remained secured in the trunk of the vehicle while within the fenced and secured impoundment lot overnight. The Radiation Safety Officer from ECS recovered the portable density gauge at 0855 hours EDT on October 2, 2019. The gauge was found intact and returned to ECS storage. "MDE/RHP will conduct a reactive investigation." Notified R1DO (Dentel), ILTAB and NMSS (email) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2019-10-15
54314 | 0 | PAVEMENT INSPECTION TECHNOLOGIES |  |  |  |  | 2019-10-06 | 2019-10-06 19:21 | 2019-10-07 | STOLEN NUCLEAR DENSITY GAUGE FROM TRUCK The following report is a summary of the information received via phone call: On 10/6/19, the radiation safety officer (RSO) noticed that one of the company vehicles appeared to have been broken into and the windows were smashed. The RSO conducted an inventory of the density gauges and determined that one of them was missing. The RSO then contacted local law enforcement (LLEA) and reported the incident. LLEA arrived on site at approximately 1640 EDT to obtain the incident information. The incident is still under investigation. The gauge information is as follows: Manufacturer: Humboldt Model: 5001 Serial Number: 2529 Source Quantity/Activity: Am-241/Be - 50 milliCuries Cs-137 - 10 milliCuries. * * * UPDATED ON 10/7/19 AT 1404 EDT FROM CHRIS GENDUSO TO KERBY SCALES * * * The Pavement Inspection Technologies RSO reported that the gauge was recovered intact. Notified R1DO (Dentel), ILTAB and NMSS Events (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-10-14
54313 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-10-06 07:00 | 2019-10-06 16:16 | 2019-10-06 | OFFSITE NOTIFICATION DUE TO FIRE PUMP BEING TAKEN OFFLINE "At 0700 (EDT) on October 6, 2019, the New Hanover County Deputy Fire Marshall was notified per state code requirements that the fire pump supporting the Fuel Manufacturing Operation (FMO) was being taken offline for NFPA [National Fire Protection Association] required testing. Compensatory measures were enacted. The fire pump was returned to operation at 1215 (EDT) on 10/6/2019. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The NRC Region II office will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-10-06
54312 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2019-10-05 08:50 | 2019-10-05 16:29 | 2019-10-05 | INDIVIDUAL TRANSPORTED TO OFFSITE MEDICAL DUE TO INJURY "At 0850 CDT, on 10/5/2019, the control room was notified of a personnel injury in the Unit 1 containment building. The individual was considered potentially contaminated since a complete frisk could not be performed prior to transport to a local hospital. At 1234 CDT, a radiological survey determined that the individual and their clothing had trace amounts of activity that was easily removed. The employee did not sustain any life threatening injuries. "This is reportable under 10 CFR 50.72(b)(3)(xii). "Additionally, at 1135 CDT contact was made with the Arkansas Department of Health about transport of the potentially contaminated individual. This is reportable under 10 CFR 50.72(b)(2)(xi) due to notification of an offsite agency. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2019-10-05
54311 | 0 | AZZ NUCLEAR GROUP |  |  |  |  | 2019-10-04 | 2019-10-04 17:54 | 2019-10-04 | PART 21 - F10 SERIES MCC CUBICLE CONNECTION STAB ALIGNMENT The following is a summary from a part 21 report received via facsimile: "Susquehanna identified a deviation with a phase to phase to ground short that was caused by misalignment of the cubicle stabs when racking in the cubicle. The cubicle was racked into the cell and 2 of the 3 phase stab fingers engaged properly with the bus. The A phase stab fingers missed the center of the bus, however an electrical connection was maintained. This condition was estimated to be present for 3 years before the failure occurred. The deviation was originally evaluated as an installation issue, however after further evaluation, the deviation has been determined to be a failure to comply with the specification requirements. The specification requirements were reviewed and it was determined that the design of the connection stabs did not fully comply with the requirements. "The reported deviation will complete an electrical connection between the stab finger assembly and the bus, but at a possible reduced current carrying ability as only 1 side of the stab finger assembly is touching the bus. This causes less surface area contact between the stab finger and the bus, which causes less current carrying ability. The cubicle will likely function, however over time, if left uncorrected, it is possible that the connection could overheat, depending on the load of the cubicle, since the connection has a reduced surface area and/or has a higher resistance than what would be typical if the stab finger assembly was properly engaged. "The issue could extend to all F10 series MCC cubicles supplied by NLI [Nuclear Logistics Inc.] with the current design of stab assembly P/N: 5600-SA3-1. This design has been provided to Susquehanna Station, Limerick Generating Station, and Perry Nuclear. "Please contact me with any questions or comments: Tracy Bolt, Director of Quality Assurance AZZ Nuclear 7410 Pebble Drive Ft. Worth, TX 76118" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2019-10-04
54310 | 0 | ALT & WITZIG ENGINEERING |  |  |  |  | 2019-10-03 19:00 | 2019-10-04 15:57 | 2019-10-04 | STOLEN AND RECOVERED NUCLEAR DENSITY GAUGE The following is a synopsis of information received via phone: On October 3, 2019, at approximately 1900 EDT, a CPN nuclear density gauge containing 10 mCi of Cs-137 and 50 mCi of Am-241 was discovered to be stolen when the person in possession of the gauge found the storage box on his truck open and the gauge not inside. Local law enforcement was notified and subsequently recovered the gauge on October 4, 2019 at 0800 EDT. The gauge did not appear to be damaged and the lock was still intact. The gauge is now in the possession of the licensee. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-10-14
54309 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2019-03-03 | 2019-10-04 15:45 | 2019-10-04 | PART 21 - GE HITACHI PRIMARY CONTACT FINGER SURFACE DEFECT "On March 3, 2019, during overhaul activities of the medium voltage power (Magne-blast) circuit breakers, three General Electric Hitachi (GEH) Stationary Primary Contact Fingers Q0114C5382P002 were identified as having contact surfaces with a finish that was rough and unlike the typically smooth finish provided on electrical contact surfaces. These Stationary Primary Contact Fingers are the primary current carrying device for the circuit breaker. "On October 1, 2019, Arizona Public Service Company (APS) completed an evaluation of a deviation, and concluded the condition represented a defect under 10 CFR 21. "On October 4, 2019, the Palo Verde Nuclear Generating Station Vice President, Nuclear Engineering, was notified of a defect of GEH Stationary Primary Contact Fingers which met the reporting criteria of 10 CFR 21.21. "There are no medium voltage power (Magne-blast) circuit breakers with stationary primary contact fingers impacted by this condition installed in the plant. APS concluded this condition, if installed, could result in the breaker failing to perform its safety function and thus could create a substantial safety hazard. "The NRC resident inspector has been informed." | 100 | 100 | 97 | 100 | 100 | 97 | -1 | -1 | -1 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2019-10-04
54308 | 0 | US ARMY TACOM |  |  |  |  | 2019-09-17 | 2019-10-02 15:15 | 2019-10-02 | LOSS AND DISCOVERY OF TRITIUM (H-3) SOURCES "This report is for an item on U.S. Nuclear Regulatory Commission (NRC) License Number 21-32838-01, Docket Number 030-38500. A 30-day report will be sent to NRC Region III in accordance with the Code of Federal Regulations, Title 10, Part 20.2201. "On 17 September, at approximately 0855 EDT, the Marine Corps Combat Development Command (MCCDC) received a phone notification from one of their Installation Safety Managers concerning a possible radioactive device found inside a dumpster at an off base construction development site in Stafford County, VA. MCCDC Safety Personnel inspected the device and did not discover any breaches nor cracks of the large tritium vial. The device contained a tag with the radioactive symbol and the statement 'IF FOUND RETURN TO NEAREST MILITARY ACTIVITY.' The device was recovered and transported to the low-level radioactive waste storage locker on the Quantico Marine Corps Base. "Item Name: COLLIMATOR, INFINITY AIMING REFER Nomenclature: COLLIMATOR INF A M1A1 National Stock Code: 1240-00-332-1780 Model: 10556235 Serial Number: 1504 Radionuclide: Tritium (H3) Activity: 10 Curies "The Department of the Navy, Naval Sea Systems Command Detachment, Radiological Affairs Support Office, contacted the U.S. Army Tank-automotive and Armaments Command (TACOM) Safety Office via telephone on 1 October 2019. The TACOM Radiation Safety Program Manager notified NRC Region III Senior Health Physicist (Piskura) to verify if this item was reported as lost. She could not verify if the item was previously reported as lost and informed TACOM on 2 October 2019 to notify the NRC Operations Center. Additional information will be provided in the 30-day report." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-10-10
54307 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-10-02 04:15 | 2019-10-02 11:50 | 2019-10-02 | ACTUATION OF CONTAINMENT SPRAY SYSTEM "On October 2, 2019, at 0415 EDT, with Unit 2 in Mode 5 at 0 percent power, an actuation of the Unit 2 containment spray system occurred during valve strokes of the 2A train containment spray header isolations while the 2B train containment spray pump was in recirculation. The reason for the containment spray actuation was due to a conflicting procedural alignment with the 2B containment spray recirculation procedure. The containment spray system does not have an automatic function, and only receives manual actuation. The Unit 2 containment spray actuation was secured at 0416. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the containment spray system. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-10-02
54306 | 0 | ARKANSAS NUCLEAR |  |  |  |  | 2019-10-01 16:30 | 2019-10-02 11:37 | 2019-10-02 | PART 21 REPORT - ITE/GOULD J20M COIL BLOCK RELAY "On October 1, 2019, the Arkansas Nuclear One (ANO) Site Vice President was notified of a defect on an ITE/Gould J20M Coil Block Relays which met the reporting criteria of 10 CFR 21.21. "ANO is making this non-emergency notification in accordance with 10 CFR 21.21(d)(3)(I) concerning a defect on an ITE/Gould J20M Coil Block Relay which resulted in one of four safety related containment cooling fans failure to start at ANO Unit 2. On June 1, 2019, a failure occurred when the containment cooler fan hand switch was taken to 'start' during the recent Unit 2 forced outage. Troubleshooting identified the control power relay coil was found to have an open winding condition. "The Unit 2 reactor was in shutdown (Mode 5) and no impacts to nuclear or radiological safety occurred because of this event. The failure of the containment cooling fan to start would have prevented the Containment Cooling System from performing its function of providing essential cooling/environmental controls for safety related equipment inside containment. "On August 15, 2019, ANO approved a causal evaluation which determined the failure of the relay occurred due to a manufacturing defect associated with uneven varnish application on the coil windings. This defect lead to premature turn-to-turn shorting of the coils. This failure was determined to be limited to ITE/Gould relays that were part of a 1991 batch purchased by ANO. The 1991 relay batch had a manufacturing date code of 9132. "As part of the ANO evaluation, an industry operating experience review identified INPO ICES OE 242045. This OE identified another utility had purchased three relays from ANO in 2007 and subsequently experienced coil failures on two of the three relays. The utility did not issue a 10 CFR Part 21 notification. "During the ANO evaluation, NRC IN 92-27 Supplement 1 was reviewed. The IN noted the same component failure mode. However, the failure mechanism was different. The IN discussed failures associated with thermal degradation of the relay armature carriers in ganged mounting configurations. The failure mechanism at ANO is due to uneven varnish application to the coil windings. "Entergy ANO performed a Part 21 Evaluation in accordance with 10 CFR 21.21(a)(1) which was completed on September 25, 2019. This evaluation determined this defect could create a substantial safety hazard as defined in 10 CFR 21.3. "The licensee has two relays left that could be affected. One relay is installed and currently in use by the other containment cooling fan and the other relay is on parts hold in an ANO onsite warehouse. A Condition Report has been initiated to document the potential for failure of the installed control power relay. This ITE/Gould J20 is obsolete and other options are being evaluated to replace the ITE/Gould J20M Coil Block Relay. ANO has notified the utility to whom it sold the relays in 2007. ANO has also notified the vendor." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-10-02
54305 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-10-01 | 2019-10-02 11:09 | 2019-10-02 | AGREEMENT STATE REPORT - LOST RADIOGRAPHY CAMERA The following was received from the Texas Department of State Health Services (the Agency) via email: "On October 2, 2019, a licensee reported to the Agency that they could not locate one of their Industrial Nuclear Co. IR-100 radiography cameras (S/N: 4414) containing an Iridium-192 source (S/N: 850D) with approximately 6 Curies of activity. The licensee stated that he believed the source was located at one of his satellite locations in Orange, Texas. The loss was discovered after performing an inventory check. The licensee has initiated an investigation and is currently searching for the device. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9718 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-10-10
54304 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2019-10-01 14:44 | 2019-10-01 16:46 | 2019-10-01 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability occurred which could allow access to a protected area for which compensatory measures were not employed. The measures were re-established prior to this notification. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-10-01
54303 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-09-25 | 2019-10-01 09:15 | 2019-10-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via E-mail: "A general licensee reports that following a recent inventory audit, they could not account for 17 missing tritium exit signs. The missing signs could not be accounted for physically by the licensee or verified through formal documentation that the signs were sent for disposal." The signs are believed to be Safety Light Corporation model number 2040 signs. The serial numbers were not reported. NC Tracking Number: NC 190033 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-10-09
54302 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-10-01 03:07 | 2019-10-01 07:05 | 2019-10-01 | AUTOMATIC REACTOR SCRAM DURING REACTOR STARTUP "On 10/1/2019, at 0307 CDT, Unit 2 was conducting a normal reactor startup and received a valid Reactor Protection System (RPS) scram. The reactor was critical in MODE 2 at the Point of Adding Heat. Operators began withdrawing Source Range Monitor (SRM) Instrumentation per procedure. When the operator depressed the SRM Drive Out pushbutton to withdraw the last two SRMs (C and D), an unexpected full Reactor Scram was received. Annunciator indication in the Main Control Room indicated a Neutron Monitoring Scram. The Intermediate Range Monitors (IRM) D, E, F, H and G all indicated Upscale High High. There were no Emergency Core Cooling System (ECCS) or Containment Isolation System actuations. All other systems functioned as designed. "The cause of the Reactor Scram is still under investigation. "This event requires a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "This event also requires an 8-hour report per 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including: reactor scram or reactor trip, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-10-01
54301 | 0 | FLOWSERVE US INC. |  |  |  |  | 2019-09-30 | 2019-09-30 15:55 | 2019-10-22 | PART 21 - VALVE MANUFACTURE ACCEPTANCE CRITERIA The following information was received from Flowserve US Inc. via facsimile: "Description: Contrary to the requirements of ASME Section Ill - NC-4000, Flowserve Raleigh identified that they were utilizing as standard practice, the base material acceptance criteria in lieu of welding acceptance criteria for valves with temporary attachments (i.e. - Lug removal areas). This utilization of criteria has been ongoing as far back as Flowserve's Review could determine. No specific orders or customers are identified as this is systemic to the overall process of valve manufacturing at Flowserve Raleigh. "Evaluation: A review was completed of the ASME Code requirements by Flowserve Raleigh's Engineering and Metallurgical Process Control Departments with the following results: "The examination of Temporary Attachment Removal Areas, to the NB/NC-2540 Examination and Repair of Forgings and Bars, and NB/NC-2570 Examination and Repair of Statically and Centrifugally Cast Products is contrary to NB/NC-5340 and 5350 acceptance criteria. However, it can be determined that Temporary Attachment Removal Areas examined to NB/NC-2500 acceptance criteria is consistent with the acceptable surface condition resulting from a welded repair performed on the same material product form. No greater risk to pressure integrity is created by the examination of Temporary Attachment Removal Areas to NB/NC-2500 acceptance criteria. The examination of Temporary Attachment Removal Areas examined to NB/NC-2500 acceptance criteria does not result in a Risk to safety relating to pressure integrity. "Paragraph NB/NC-4435 of Article NB/NC-4000 FABRICATION AND INSTALLATION contains mandatory requirements for the examination of Components. Contrary to the requirement of NB/NC-4435 (b) (3) to examine the Nonstructural Temporary Attachment Removal Area in accordance with the Acceptance Criteria of NB/NC-5340 or NB/NC-5350 Flowserve performed these examinations in accordance with Article NB/NC-2000 in accordance with the Acceptance Standards of NB/NC-2500 for the applicable Material Product Form. NB/NC-2540 Examination and Repair of Forgings and Bars, NB/NC-2570 Examination and Repair of Statically and Centrifugally Cast Products. "ND-4435 contains no mandatory requirements for the examination of Nonstructural Temporary Attachment Removal Area. "Extent of Condition: This utilization of criteria has been ongoing as far back as Flowserve's Review could determine. No specific orders or customers are identified as this is systemic to the overall process of valve manufacturing at Flowserve Raleigh. "Corrective Actions: Flowserve Raleigh Corrective Action, (CAR-393758) has been issued, and is currently in process of determining root cause and preventive action measures. "Summation: After review by Flowserve Raleigh's Engineering and Metallurgical Process Control Departments. It is the position of Flowserve Raleigh, that in accordance with the provisions of 10 CFR Part 21, this condition, while reportable to the NRC (Nuclear Regulatory Commission), is not a significant/substantial safety hazard." Megan Strong Quality Manager office: 919-831-3220 mstrong@flowserve.com * * * UPDATE ON 10/22/19 AT 1404 EDT FROM FLOWSERVE TO OSSY FONT * * * In addition to the information previously provided, Flowserve provided the following via fax: "Scope/ Extent of Condition: This utilization of criteria has been ongoing as far back as Flowserve's Review could determine. After further review, the scope of impact was determined as cast steel valves, Class 1 and Class 2 only. Anything outside of this criterion would not have been impacted. "Corrective Actions: Flowserve Raleigh issued Corrective Action, (CAR-393758), and is continuing their process of completing the root cause and corrective actions needed to prevent recurrence. Actions that have already taken place and/or are in progress are: 1. ASME Code Training is to be developed, with application toward the criteria as outlined in this Part 21. This training is to be developed to enhance the code knowledge of Flowserve Raleigh Personnel generating Quality Assurance Plans. 2. Quality Assurance Personnel are to be trained in accordance with the applicable code requirements, to ensure adequate knowledge of the above condition. 3. Non-Destructive Examination Personnel are to be trained in accordance with the applicable code requirements, to ensure adequate knowledge of the above condition. 4. Flowserve's Quality Assurance Plans are to have their applicable NOE matrix's revised to incorporate the applicable criteria needed for the removal of temporary attachments. "Summation: After review by Flowserve Raleigh, the following is to be a summation of the above listed 10 CFR Part 21. 1. The review has determined a programmatic condition that had been existent for many years. Raleigh can only assure that any customers for whom were supplied Class 1 or Class 2 cast steel valves, prior to the issuance of this Part 21 may have this condition. 2. To date, there have not been any reported failures or technical issues as a result of this condition. 3. While the above condition is a reportable condition to the NRC, with regards to the violation of the ASME B&PVC Code, it is Flowserve Raleigh's position that it does not pose a compromised condition to safety." Notified R1DO (Bickett), R2DO (Lopez), R3DO (Stoedter), R4DO (Young) and the Part 21 group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-09-30
54300 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-07-31 16:50 | 2019-09-30 10:28 | 2019-09-30 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION DUE TO AN INVALID ACTUATION OF A CONTAINMENT ISOLATION SIGNAL "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On July 31, 2019, at approximately 1650 hours Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN), Unit 1 experienced a Primary Containment Isolation System (PCIS) Group 6 isolation during performance of surveillance procedure 1-SR-3.3.6.2.3(A), Reactor/Refueling Zone Ventilation Radiation Monitor 1-RM-90-140/142 Calibration and Functional Test. The Group 6 isolation caused the initiation of Standby Gas Treatment (SBGT) Trains A, B, and C, and Control Room Emergency Ventilation (CREV) subsystem B. Unit 1 H2O2 Analyzer and Drywell Radiation Monitor CAM, 1-RM-90-256, were declared Inoperable and Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.5 Condition B was entered. All affected safety systems responded as expected. "Plant conditions which initiate PCIS Group 6 actuations are Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "This condition was the result of two cleared fuses in the alarm logic. The apparent cause is a ground fault on the A6 Open Drain Input/Output Module. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Acton Program as Condition Report 1537358. "The NRC Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-09-30
54299 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-09-29 22:28 | 2019-09-30 01:22 | 2019-09-30 | SECONDARY CONTAINMENT PRESSURE EXCEEDED TECHNICAL SPECIFICATION REQUIREMENT "On September 29, 2019 at 2228 EDT, during a planned swap of Reactor Building HVAC trains, the exhaust fan discharge damper for the train being removed from service failed to close when the train was shutdown, which resulted in the Technical Specification (TS) for secondary containment pressure not being met for approximately 2 minutes and 15 seconds. The maximum secondary containment pressure observed during that time was approximately 0.1 inches of water gauge (positive). "Secondary containment pressure was returned to within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge (TS SR 3.6.4.1.1) by restarting the train of RBHVAC. Secondary containment pressure is currently stable. Secondary containment was declared Operable at 2235 EDT. There were no radiological releases associated with this event. "Declaring secondary containment inoperable is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The Licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-09-30
54298 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2019-09-27 15:15 | 2019-09-28 10:32 | 2019-09-28 | PROCEDURAL NONCOMPLIANCE WITH ADMINISTRATIVE ITEM RELIED ON FOR SAFETY "On September 27, 2019 at 1515 EDT, the fire protection engineer's review of the daily corrective action report identified a procedural noncompliance which affected an administrative Item Relied on for Safety (IROFS). During the morning of September 26th, a fuel oil delivery truck, escorted by plant employees, drove along the road adjacent to the Uranium Hexafluoride (UF6) cylinder storage area, violating the minimum distance requirement within the procedure. "The IROFS designation is UF6FIRE-901, which requires escort and a 60-foot spacing distance that was not fully satisfied. Instead of 60 feet, the truck drove past the area over a period of a few minutes at a distance of 20 to 30 feet from the cylinder storage area. The other IROFS in this accident sequence remained reliable and available as required. The basis for this procedural control is to provide separation so that if a fire did occur involving the fuel oil delivery truck, there would be no significant fire exposure to the stored UF6 cylinders. "This is a non-emergency event notification, and there was no release of hazardous or radiological materials. There were no health or safety consequences to the public, the employees or the environment from this procedure non-compliance. The delivery truck was escorted at all times, and the site has an on-site fire department, available to respond to any event. "Immediate Corrective Actions: Prior to any fuel trucks being escorted inside the facility fence, both designated escorts shall receive a pre-job brief from a supervisor to ensure that designated escorts understand the proper delivery route specified in the procedure." The licensee will notify NRC R2 (Vukovinsky) and the State of South Carolina. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2019-09-28
54297 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-09-26 | 2019-09-27 13:39 | 2019-09-27 | CONCURRENT REPORT FOR OFFSITE NOTIFICATION "At 1937 EDT on September 26, 2019, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire alarm system encompassing the Fuel Manufacturing Operation (FMO) was not operating as intended. Compensatory measures were enacted. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will be notifying NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-09-27
54296 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-09-26 | 2019-09-26 18:11 | 2019-09-26 | AGREEMENT STATE REPORT - SHUTTER FAILURE ON A FIXED NUCLEAR GAUGE The following information was obtained from the State of Texas via email: "On September 26, 2019, the licensee's radiation safety officer notified the Agency [Texas Department of State Health Services] that it had a shutter failure on one of its fixed nuclear gauges. The Ohmart SH-F1 gauge, containing 5 milliCuries of cesium-137 (SN: 2925 CG), is mounted on a vessel. The licensee had closed the shutter in order to do some work in the area. Upon completion of the work, the licensee was attempting to re-open the shutter when the screws holding the actuator to the shutter handle sheared. The shutter is in the fully closed position which was confirmed by survey. There were no exposures as result of this event. A service company has been scheduled to make repairs on September 27, 2019. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident No.: 9714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-10-04
54295 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-09-26 | 2019-09-26 14:47 | 2019-10-04 | AGREEMENT STATE REPORT - STOLEN MOISTURE / DENSITY GAUGE The following information was received from the State of California via email: "On September 26, 2019, the RSO [radiation safety officer] of Maurer Technical Services, (Maurer, CA RAM license 6163-30) a nuclear gauge service provider and authorized CPN/Instrotek dealer, contacted the Brea RAM/Radiologic Health Branch office to report the theft of one of their nuclear gauges that they had leased to G3 Quality, Inc. (G3). The gauge was a CPN Model MC-3, S/N M39028685 (10 mCi Cs-137 and [50 mCi] Am:Be-241). The gauge was stolen at the Hard Rock Hotel in Stateline, NV where the gauge operator was staying while working at a project in Lake Tahoe, CA. The gauge was locked to the bed of the vehicle (open bed), the alarm enabled, and left in the parking lot of the hotel on the evening of September 25, 2019 (around 2130 PDT). The gauge was discovered missing on the morning of September 26, 2019, with the handles broken off the transport case. The cab of the truck was also broken into with other items stolen, including a laptop and the front hood was broken into to defeat the vehicle alarm. A police report was taken (the specific law enforcement agency was not provided) and the loss was reported to the G3 office and then to [the Maurer RSO] who then contacted our [California Radiologic Health Branch] office. The incident is under investigation and corrective actions will be determined at a later date." CA 5010 No.: 092619 * * * UPDATE AT 1334 EDT ON 10/4/19 FROM ANDREW TAYLOR TO JEFF HERRERA * * * The following update was received from the California Department of Public Health via email: "The gauge was recovered by Local Law Enforcement near Heavenly Village in South Lake Tahoe, CA and the gauge was returned to the license on September 27, 2019." Notified the R4DO(Proulx), NMSS Events, CNSNS (Mexico). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2019-10-04
54294 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2019-09-23 15:20 | 2019-09-25 16:09 | 2019-09-25 | AGREEMENT STATE REPORT - LOST PORTABLE DENSITY GAUGE The following was received from the Maryland Radiological Health Program via phone and email: "On September 23, 2019 at 1520 EDT, the Maryland Department of the Environment Radiological Health Program (MDE/RHP) was contacted via telephone by the Assistant Radiation Safety Officer (ARSO) of Geo-Technology Associates, Inc. that a portable density gauge was missing. The gauge was identified as a CPN model MC-1DR, serial number MD50707960 with nominal activities of 10 mCi of Cs-137 and 50 mCi of Am-241:Be. The last leak test was performed on April 11, 2019. "On September 23, 2019 at approximately 1300 EDT, the density gauge was placed in the bed of a pick-up truck by the gauge operator after making measurements starting earlier in the morning for a residential development project known as Fields at Worthington. The area is located near the intersection of Baublitz Road and Worthington Ridge Road, Reisterstown, MD. Work was suspended due to equipment failure on the job site not related to the density gauge. The gauge operator proceeded to drive back to the licensee's office. After driving approximately 1.5 miles from the jobsite, the gauge operator realized that the gauge was not placed in its transportation case and pulled over near Knox Avenue. The gauge was missing from the bed of the pick-up truck. The tailgate was in the down position. The gauge operator called the ARSO at approximately 1330 EDT to report the missing gauge. "The ARSO and the construction site manager looked for the gauge in the surrounding neighborhood with no success. The event has been reported to Baltimore County Police. The Case Number is: 192661514. "MDE/RHP will conduct a reactive investigation." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2019-10-03
54293 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2019-09-25 12:03 | 2019-09-25 15:30 | 2019-11-22 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "At 1203 EDT, on September 25, 2019, during a Division 2 Emergency Equipment Service Water (EESW) pump and valve surveillance test, the Division 2 Emergency Equipment Cooling Water (EECW) Temperature Control Valve was found to be approximately 80 percent open rather than in its required full open position during fail safe testing. The Division 2 EESW system is required to support operability of the Division 2 EECW system. The Division 2 EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. An investigation is underway into the cause of the failure. This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) based on an unplanned HPCI inoperability. "The NRC Senior Resident Inspector has been notified." The licensee is in 72-hour shutdown action statement. * * * RETRACTION ON 11/21/19 AT 1547 EST FROM PAUL ANGOVE TO BRIAN LIN * * * "Subsequent engineering evaluation has determined that the EECW TCV was capable of passing sufficient flow to perform its design basis functions, including supporting the HPCI room cooler, while approximately 80% open. Therefore, HPCI remained operable and there was no loss of safety function. The event did not involve a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident under 10 CFR 50.72(b)(3)(v)(D). "EN 54293 is retracted and no Licensee Event Report under 10 CFR 50.73(a)(2)(v)(D) is required to be submitted. "The NRC Resident Inspector has been notified. " Notified R3DO (Cameron). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-09-25
54292 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2019-09-24 23:38 | 2019-09-25 08:26 | 2019-09-25 | LOSS OF HIGH PRESSURE CORE SPRAY SYSTEM "At 2338 PDT on September 24, 2019, the High Pressure Core Spray (HPCS) system was declared inoperable due to a leak on DSA-PCV-2C (2 inch Diesel Starting Air Pressure Control Valve). With one of two air headers isolated and being drained for maintenance, this leak caused the remaining starting air header for HPCS-GEN-DG3 (HPCS Diesel Generator) to lower to less than the operability limit. "Upon declaring the HPCS system inoperable, TS 3.5.1 Action B was entered. In accordance with Action B, the Reactor Core Isolation Cooling (RCIC) system was verified to be operable. Action B provides a 14 day completion time to restore HPCS to an operable status. "All other Emergency Core Cooling Systems (ECCS) were operable during this event. This event is being reported as an event or condition that could have prevented the fulfillment of a safety function credited for mitigating the consequences of an accident per 10 CFR 50.72(b)(3)(v)(D). The HPCS system is a single train system at Columbia. "The leak was isolated and starting air header pressure restored to the HPCS diesel generator at 0104 PDT on September 25, 2019, and all associated Technical Specifications were exited. "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-09-25
54291 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-09-24 09:30 | 2019-09-24 15:02 | 2019-09-24 | FITNESS-FOR-DUTY REPORT "On September 24, 2019, at 0930 EDT, a non-licensed employee contract supervisor had a confirmed positive test result for illegal drugs during a random test. The employee's access to the plant has been denied. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2019-09-24
54290 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-09-20 | 2019-09-23 15:31 | 2019-09-23 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the California Department of Public Health - Radiologic Health Branch (RHB) via email: "On 09/21/19, (Saturday), the RSO [radiation safety officer] contacted RHB and left a voicemail message to report a stolen moisture density gauge. The gauge involved is a Troxler Model 3440, S/N 28050 containing 9 mCi of Cs-137 and 44 mCi of Am-241. The gauge was stolen on 09/20/2019, between the hours of 2030 PDT and 0130 PDT, while it was charging at the user's residence. Union City Police was notified of the incident (Case # 190921007, Officer # 4740, Sarah Lings). Licensee will be posting a reward for the safe return of the gauge. "Licensee failed to contact CA Office of Emergency Services (OES) regarding immediate notification. RHB will be following up on the incident." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-10-01
54289 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-09-23 11:06 | 2019-09-23 14:15 | 2019-09-23 | AUTOMATIC REACTOR TRIP DUE TO LOWERING STEAM GENERATOR LEVELS "At 1106 CDT Braidwood Unit 1 experienced an automatic reactor trip due to lowering steam generator water levels following closure of the 1B steam generator feed water regulating valve. "The cause of the 1B steam generator feedwater regulating valve failing closed is unknown at this time and is under investigation. "Both trains of auxiliary feedwater started automatically following the reactor trip to maintain steam generator water levels. "All systems responded as expected with the exception of intermediate range nuclear instrument N-36 which was identified as being undercompensated following the reactor trip. Both source range nuclear instruments were manually energized in accordance with station procedures. Steam generator power operated relief valves lifted momentarily and reseated as designed in response to the secondary transient due to the reactor trip. The main steam dump valves are in service to the main condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. AC power is being provided by offsite power with the diesel generators in stand by and all safety systems available. There is no impact to Unit 2. "This report is being made per 10 CFR 50.72(b)(2)(iv)(B) for a RPS actuation, 4 hour notification, and per 10 CFR 50.72(b)(3)(iv)(A) for an automatic actuation of the auxiliary feedwater system, 8 hour notification. "The NRC Resident Inspector has been informed." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-09-23
54288 | 0 | ROTORK CONTROLS |  |  |  |  | 2019-06-17 | 2019-09-23 12:35 | 2019-09-23 | PART 21 REPORT - NA - TYPE ACTUATOR OUTER CLUTCH RING ANOMALY The following was received via fax: "Rotork Controls Inc. has identified a potential concern as defined under 10 CFR Part 21 with model NA1 [nuclear A-range (inside containment)] and NA5 [seismic component] nuclear safety related actuators manufactured [and shipped] between January 1, 1979 and December 31, 1982. Switch mechanism in these actuators utilize an Outer Clutch Ring ([Part number =] N40039) made from beryllium copper. [Duke Energy] has reported (4) instances of Outer Clutch Ring failure between 2000 and 2019 [at Catawba and McGuire]. All failures occurred in Outer Clutch Rings made from beryllium copper. "The number of affected actuators remaining installed is thought to be low and those still installed are approaching the end of their 40 year service life. "Rotork cannot assess the risk further. Rotork recommends licensed operators assess this potential failure mode if actuators from this date range are still installed and should consider risk if affected actuators are to remain in service beyond 40 years. "Failure of the Outer Clutch Ring results in: 1) lost travel limit switch operation in open and closed directions; 2) lost auxiliary switch operation for open and closed indication limits; 3) lost mechanical torque latch operation, if fitted. Torque limit sensing is not affected. AOP [Add-On-Pack] operation is not affected." "In 1982, Rotork changed the Outer Clutch Ring material to spring steel 'to improve setting and operation.'" Rotork Controls, Inc. 675 Mile Crossing Blvd. Rochester, New York 14624 tel: 1-585-247-2304 fax: 1-585-247-2308 www.rotork.com info@rotork.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-09-23
54287 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-09-21 08:00 | 2019-09-21 10:28 | 2019-09-21 | MANUAL TRIP DUE TO REACTOR COOLANT PUMP VIBRATION ALARM "At 0800 [CDT], with Unit 2 in Mode 1 at 100 percent [power], the reactor was manually tripped due to elevated vibration indication on the 2C reactor coolant pump exceeding annunciator response procedure trip criteria. The trip was not complex, with all systems responding normally post trip. Auxiliary Feedwater (AFW) auto actuated as expected following the manual reactor trip. "Operations responded and stabilized the plant. Decay heat is being removed via the use of AFW and subsequent steaming of the steam generators to the main condenser. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b(2)(iv)(B). In addition, this event report is being reported as an eight-hour non-emergency notification per 10 CFR50.72(B)(3)(iv)(A) for a specified system actuation. "There was no impact on the health and safety of the public or plant personnel. The NRC resident inspector has been notified." Farley reported that there was no increase in containment unidentified leakage or fluctuations with RCP seal flow during this event. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-09-21
54286 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-07-06 01:56 | 2019-09-19 14:08 | 2019-09-19 | BOTH TRAINS OF COMPONENT COOLING WATER DETERMINED INOPERABLE "10 CFR 50.72(b)(3)(v)(A, B, and D) - Event or Condition that Could Have Prevented the Fulfillment of a Safety Function Unit 2 Component Cooling water system inoperable. "On July 6, 2019, from 0156 to 1545 [EDT], it was determined that both trains of the unit 2 component cooling water system were simultaneously inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). The affected safety function was restored on July 6, 2019, at 1545 [EDT] when the 2B component cooling train was restored to operable. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." At the time of the event no other safety related systems were inoperable. The event had no impact on Unit 1. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2019-09-19
54285 | 0 | ACUREN INSPECTION INC |  |  |  |  | 2019-09-18 | 2019-09-18 15:40 | 2019-09-20 | RADIOGRAPHY CAMERA LOST DURING SHIPPING "On 9/11/2019 [Acuren Inspection in Billings Montana] shipped a camera to QSA Global for disposal, the exposure device serial number is D3869 source serial number 83052G. "Acuren has not received the receiving report from QSA. The (RSO) contacted the common carrier on Monday September 16, 2019, the common carrier initiated a search for the missing package and have not been able to find it. The last place it was scanned in was at the common carrier's facility in Memphis TN, on 9/12/2019 at 12:41AM." The source is a 30 Curie iridium 192 source. The licensee notified Region IV Materials (Erickson). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, DHS NICC, USDA Ops Center, EPA EOC, FDA EOC, FEMA NWC, DHS Nuclear SSA, FEMA NRCC SASC, DNDO-JAC. * * * UPDATE ON 09/20/19 AT 1045 EDT FROM JEREMY SCHREINER TO OSSY FONT VIA PHONE * * * The licensee notified the NRC that the common carrier located the package in Memphis, TN. The Shippers Declaration papers were ripped off. The common carrier states that the package will be delivered to Baton Rouge, LA today, 09/20/19. Notified R4DO (Taylor), IR MOC (Grant), DHS SWO, DOE Ops Center, FEMA Ops Center, DHS NICC, USDA Ops Center, EPA EOC, FDA EOC, FEMA NWC, DHS Nuclear SSA, FEMA NRCC SASC, DNDO-JAC, and ILTAB, NMSS (Williams), NMSS Events, INES (via email), CNSC(Canada via email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/MISSING CAT 2 RAD MATL IN TRANSIT | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 37.81(b) |  |  |  | 0 | 2019-09-26
54284 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-09-18 07:50 | 2019-09-18 13:42 | 2019-09-18 | LOSS OF COMMUNICATION WITH EMERGENCY OPERATIONS FACILITY "At 0750 CDT, on September 18, 2019, South Texas Project Electric Generating Station (STPEGS) experienced an unplanned loss of the Integrated Computer System (ICS) to the Emergency Operations Facility (EOF). The loss of ICS resulted in a major loss of emergency assessment capability to the STPEGS EOF for greater than 90 minutes. Assessment capability has been verified to be available in the Unit 2 Technical Support Center (TSC) and the Unit 1 and Unit 2 Control Rooms. ICS was restored to the EOF at 0932 CDT on September 18, 2019. "This report is being made pursuant to 10 CFR 50.72(b)(3)(xiii) as any event that resulted in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-09-18
54283 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2019-09-17 10:28 | 2019-09-17 14:08 | 2019-09-17 | ON-SITE NON-WORK RELATED FATALITY "Event of Public Interest performed to notify State and Local agencies for emergency vehicle response required due to an on-site non-work related illness. The individual was unresponsive and was unable to be resuscitated due to the medical issue. The individual was outside the Radiological Controlled Area (RCA) and no radioactive material or contamination was involved. "The NRC Resident Inspector was notified." Responding to the site were emergency medical services, fire, and police. The licensee notified Pennsylvania Emergency Management Agency, Dauphin County Emergency Management Agency, Cumberland County Emergency Management Agency, Lancaster County Emergency Management Agency, York County Emergency Management Agency, and Lebanon County Emergency Management Agency. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-09-17
54282 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-09-16 | 2019-09-17 13:09 | 2019-09-17 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information is a summary of an email received from the state of North Carolina: On September 16, 2019, a patient at Duke University Medical Center was prescribed 43.2 mCi of Y-90 Theraspheres to the liver, but received 89.6 mCi. While the cause of the misadministration is not clear at this time, it is known that the dose received was intended for a different patient. Both the patient and the authorized user have been informed of the incident. An inspector has been dispatched to conduct a reactive inspection for this event. North Carolina Tracking Number: 190032 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-09-25
54281 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2019-09-16 08:17 | 2019-09-16 14:35 | 2019-09-16 | ACCIDENT MITIGATION "On 9/16/19 at 0817 CDT, the Division 1 and Division 2 reactor water cleanup (RT) system differential flow instrumentation was declared inoperable due to failing downscale caused by flashing in the sensing lines that occurred during reactor cooldown for refueling outage C1R19. The Division 1 and Division 2 RT differential flow instrumentation were declared inoperable in accordance with Technical Specification 3.3.6.1 Conditions D and E which require restoring at least one division of instruments to operable status within one hour. This condition renders the leakage detection system incapable of performing its safety function, thus it is reportable under 10 CFR 50.72(b)(3)(v)(D). "In response to the above, system alignment was changed to increase subcooling to restore indication. Division 1 and 2 Division RT differential flow instrumentation were declared operable at 0852 on 9/16/19. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-09-16
54280 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-09-11 | 2019-09-13 16:28 | 2019-09-13 | AGREEMENT STATE REPORT - MISADMINISTRATION OF HIGH DOSE RATE THERAPY The following was received via email from the Massachusetts Department of Public Health - Radiation Control Program (the Agency): "On 09/13/19, a medical event was reported by Massachusetts General Hospital (MGH) (the licensee) involving the medical misadministration of HDR [high dose rate] therapy. The 59 year-old patient involved received dose to unintended tissue exceeding 50 percent of the prescribed dose defined in the written directive. The prescribed dose was 5.5 Gy over 5 fractions for a total of 27.5 Gy to the cervix. The therapy was performed using a Syeb-Neblett Template and 6 catheters including 1 tandem. The patient ultimately received the full intended dose to the tumor (high risk- CTV [clinical target volume]) and per the licensee there was no overdose to any critical structures including bladder, rectum, or bowel. A small region of the surface of the right vaginal wall (approximately 1 cm) did inadvertently receive 16.5 Gy due to the wrong treatment distances being entered into the treatment planning system for 2 of the 7 catheters by the physicist. The patient is not expected to be at an increased risk for toxicity due to this error. Both the patient and referring physician were immediately notified upon discovery. Licensee to submit written report within 15 days of discovery date. The Agency considers this event to be open and pending investigation." Event Docket # 21-3895 NMED # 190464 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-09-23
54279 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-09-12 16:40 | 2019-09-13 14:47 | 2019-09-13 | CONCURRENT REPORT FOR FIRE ALARM MAINTENANCE "At 1640 (EDT) on September 12, 2019, the New Hanover County Deputy Fire Marshall was notified, per State code requirements, that the fire alarm system encompassing the Fuel Manufacturing Operation (FMO) will be taken offline for planned maintenance. The system was taken offline at approximately 0800 on September 13, 2019. Compensatory measures were enacted. The system was returned to service at approximately 1335 on September 13, 2019. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The NRC Region, as well as the North Carolina Radioactive Materials Branch, will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-09-23
54278 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-09-13 04:27 | 2019-09-13 12:23 | 2019-09-16 | EMERGENCY OPERATING FACILITY UNAVAILABLE DUE TO ACCESS ISSUES "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. "A condition impacting access to the Emergency Operating Facility, Central Emergency Control Center (CECC), located in the TVA Chattanooga Office Complex occurred on September 13, 2019 at 0427 CDT. Fire suppression capabilities for the TVA Chattanooga Office Complex are currently impacted by a water main failure rendering access to the facility unsafe for personnel. "If an emergency is declared requiring CECC activation during this period, other emergency response centers will be activated and staffed using existing emergency planning procedures and have the capability to perform the functions normally performed by the CECC. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the condition affects the functionality of an emergency response facility. "The condition does not affect the health and safety of the public. "The NRC Resident Inspector has been notified." * * * UPDATE ON 9/19/2019 AT 1334 EDT FROM NEEL SHUKLA TO ANDREW WAUGH * * * "Water lines impacting the Chattanooga Office Complex were repaired, and as of time 0734 EDT on 9/16/19, the CECC was returned to a functional status. "The NRC Resident Inspector has been notified." Notified R2DO (Ehrhardt). | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-09-13
54277 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-09-13 05:27 | 2019-09-13 12:21 | 2019-09-16 | EMERGENCY OPERATING FACILITY UNAVAILABLE DUE TO ACCESS ISSUES "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. "A condition impacting access to the Emergency Operating Facility, Central Emergency Control Center (CECC), located in the TVA Chattanooga Office Complex occurred on September 13, 2019 at 0527 EDT. Fire suppression capabilities for the TVA Chattanooga Office Complex are currently impacted by a water main failure rendering access to the facility unsafe for personnel. "If an emergency is declared requiring CECC activation during this period, other emergency response centers will be activated and staffed using existing emergency planning procedures and have the capability to perform the functions normally performed by the CECC. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the condition affects the functionality of an emergency response facility. "The condition does not affect the health and safety of the public. "The NRC Resident Inspector has been notified." * * * UPDATE ON 9/19/2019 AT 1341 EDT FROM DEAN BAKER TO ANDREW WAUGH * * * "Water lines impacting the Chattanooga Office Complex were repaired, and as of time 0734 EDT on 9/16/19, the CECC was returned to a functional status. "The NRC Resident Inspector has been informed of this event update." Notified R2DO (Ehrhardt). | 11 | 100 | 0 | 11 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-09-13
54276 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-09-13 05:27 | 2019-09-13 11:57 | 2019-09-16 | EMERGENCY OPERATING FACILITY UNAVAILABLE DUE TO ACCESS ISSUES "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. "A condition impacting access to the Emergency Operating Facility, Central Emergency Control Center (CECC), located in the TVA Chattanooga Office Complex occurred on September 13, 2019 at 0527 EDT. Fire suppression capabilities for the TVA Chattanooga Office Complex are currently impacted by a water main failure rendering access to the facility unsafe for personnel. "If an emergency is declared requiring CECC activation during this period, other emergency response centers will be activated and staffed using existing emergency planning procedures and have the capability to perform the functions normally performed by the CECC. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the condition affects the functionality of an emergency response facility. "The condition does not affect the health and safety of the public. "The NRC Resident Inspector has been notified." * * * UPDATE ON 09/16/2019 AT 1148 EDT FROM SCOTT THOMAS TO BRIAN LIN VIA PHONE * * * Water lines impacting the Chattanooga Office Complex were repaired, and as of time 0734 EDT on 9/16/19, the CECC was returned to a functional status. The NRC Resident Inspector has been informed of this event update. Notified R2DO (Ehrhardt). | 75 | 100 | 0 | 75 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-09-13
54275 | 0 | MATERIALS TESTING, INC |  |  |  |  | 2019-09-12 11:30 | 2019-09-13 11:32 | 2019-09-13 | DAMAGED DENSITY GAUGE The following is a synopsis of information received via phone: On September 12, 2019, at approximately 1130 EDT, a Humboldt gauge (Model 5001C; S/N 3267), containing 10 mCi of Cs-137 and a 40 mCi Am-241/Be source, was damaged during a field inspection. The inspector notified the radiation safety officer (RSO) and informed him that the source was retracted at the time and the source was not damaged. The RSO instructed the inspector to place the device in the carrying case and return it to him at the office. No survey of the device was performed prior to removal from the job site. Once the device was at the office, the RSO performed a swipe test and will be sending it to Humboldt. The RSO was also going to notify the device manufacturer of the damaged gauge. No exposure is expected but personnel dosimetry badge was sent for processing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-09-23
54274 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-09-10 | 2019-09-13 09:36 | 2019-09-13 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received by the State of Illinois via email: "The Radiation Safety Officer for Americas Styrencs, LLC, called to report that on September 10, 2019, they were conducting a routine six month shutter check on a Texas Nuclear Model 5180A device and determined that the shutter was stuck in the open position. The device is 40 years old, and it originally contained 2 Curies of Cs-137. The gauge is located on a vessel which is still in active use and is exposed to ambient weather conditions. The gauge is located approximately 10 feet overhead and the beam path is not a routine work location for day-to-day operations. They will contact Thermo MeasureTech to schedule service on the device and apprise the Illinois Emergency Management Agency (Agency) on the service date. Since this device operates continuously, it will continue to function and not interrupt their operations. An Agency inspector arrived on the scene on the same day to confirm that the device was in a safe configuration for continued operations." Illinois Item Number: IL190028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-09-23
54273 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2019-09-12 13:35 | 2019-09-12 20:08 | 2019-09-12 | UNPLANNED SURFACE CONTAMINATION "Heeled 30B UF6 Cylinders arrived at Framatome at approximately 1235 (PDT) on September 12, 2019. The cylinders were inspected/surveyed for loose surface contamination at approximately 1335 (PDT). Two cylinders were identified to have greater than 24 dpm/cm2 alpha contamination limit and the 240 dpm/cm2 beta/gamma contamination limit set by DOT [Department of Transportation] and NRC. Each cylinder contained contamination on and around the valve cover. One cylinder contained 250 dpm/cm2 alpha and 2,500 dpm/cm2 beta/gamma, and another 35-40 dpm/cm2 alpha and 2,000 dpm/cm2 beta/gamma. "The top of the cylinders have been decontaminated and the valve covers have been removed and bagged. "[Title] 10 CFR 20.1906 requires immediate notification of the operations center and carrier in the event of contamination in excess of the limits specified in 49 CFR 173.443 during inspections required by 10 CFR 71.87." There were no exposures to personnel and no contamination was found on the transport vehicle. The licensee is attempting to contact Westinghouse from where the cylinders originated. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 20.1906(d)(1) |  |  |  | 0 | 2019-09-12
54272 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2019-09-11 18:24 | 2019-09-12 03:25 | 2019-09-12 | MAIN STEAM LINE RADIATION MONITOR COMMUNICATION FAILURE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "Radiation monitor RU-140 (#2 Steam Generator Main Steam Line radiation monitor) experienced a communication failure on both ports A and B. The RU-140 monitor is off line and non-functional at this time. "At least one channel of RU-140 is required to perform a Steam Generator Tube Rupture (SGTR) dose assessment. This represents an unplanned loss of radiological assessment capability for the inability to perform dose assessments that require the radiation monitor. The ability to make emergency classifications from other radiological data collection methods such as field sampling remains available. Actions have been initiated to restore the radiation monitor. "The NRC Resident Inspector has been informed." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-09-12
54271 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-09-11 17:19 | 2019-09-12 00:49 | 2019-09-12 | PRIMARY CONTAINMENT AIRLOCK DOOR NOT IN FULLY SEATED POSITION "On September 11, 2019 at 1719 CDT, plant personnel identified a condition in which the 208 foot elevation inner primary containment airlock door was not in its fully seated and latched position while the 208 foot elevation outer primary containment airlock door was opened. The 208 foot elevation outer containment airlock door was subsequently closed by the individual exiting the area. The time that both 208 foot elevation containment airlock doors were not in their fully seated and latched positions was less than 1 minute. Following this occurrence, maintenance personnel inspected the 208 foot elevation inner containment airlock door and re-positioned this door to its fully seated and latched position. There was no radioactive release as a result of this event. "This condition requires an 8-hour non-emergency notification in accordance with 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The NRC Resident Inspector has been notified." | 81 | 0 | 0 | 81 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-09-12
54270 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2019-09-11 | 2019-09-11 19:00 | 2019-09-11 | LOST / STOLEN TRITIUM EXIT SIGN The following information was received from the Arizona Department of Health Services via E-mail: "The Department [Arizona Department of Health Services] received notification that a tritium exit sign has been lost/stolen. The model is an Isolite 2040 with an activity of approximately 7.5 curies. The Department has requested additional information and continues to investigate the event." Arizona Incident Number: 19-018 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-09-19
54269 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-09-11 | 2019-09-11 18:23 | 2019-09-13 | MEDICAL EVENT - PALLADIUM-103 SEEDS IMPLANTED TO WRONG TARGET AREA The following information was received from the Texas Department of State Health Services via E-mail: "On September 11, 2019, the Agency [Texas Department of State Health Services] was notified that the licensee had identified that a medical event had occurred at its facility. The licensee reported it had discovered that the 52 palladium-103 seeds (1.292 mCi each) that had been implanted into a patient on August 1, 2019, which were intended to deliver 100 gray to the prostate, were all inferior to the patient's prostate approximately four centimeters. "The licensee has notified the referring physician and patient. The licensee stated the current plan is to implant the prostate. There are no significant adverse effects expected. "An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." * * * UPDATE RECEIVED FROM ART TUCKER TO OSSY FONT ON 09/13/19 AT 1752 EDT * * * "On September 13, 2019, the Agency received additional information on this event. The licensee's report stated that on August 1, 2019, the physician was using ultrasound imaging to locate the prostate [and] misidentified the penile bulb as the prostate. The licensee stated this occurred because the penile bulb was very similar in size (10.8 cc versus 12 cc for the prostate) and they were very close to each other. As a result, 52, 1.292 milliCurie (67.2 milliCurie total) Palladium-103 seeds were placed four centimeters inferior to the prostate. The error was not discovered until September 11, 2019 during the post-implant dosimetry review. "The estimated exposure to 90 percent of the penile bulb is 73 gray. The report stated that the patient is elderly and not sexually active; therefore, there is no increased risk of erectile dysfunction. The licensee identified the urethral structure as additional tissue at risk, but expected the effects to be the same as if the seeds had been properly placed at the prostate. The estimated dose to the prostate was 0 gray. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9710 Notified R4DO (Alexander) and NMSS Events Notification E-mail group. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-09-19
54268 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2019-09-11 12:48 | 2019-09-11 17:58 | 2019-09-11 | FITNESS-FOR-DUTY REPORT INVOLVING A CONTRACT SUPERVISOR A non-licensed contract supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty test. The individual's authorization for site access has been terminated. The NRC Resident Inspector has been notified. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2019-09-11
54267 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-09-11 10:01 | 2019-09-11 14:04 | 2019-09-11 | OFFSITE NOTIFICATION DUE TO WASTE TREATMENT LAGOON DISCHARGE TO THE SOIL "In preparation for Hurricane Dorian, the Waste Treatment Operator in Responsible Charge (ORC) decided to lower the level in the Waste Treatment Central Lagoon by treating and transferring to Process Lagoons. Piping was damaged and not noticed during a walkdown prior to pumping from waste treatment to the process lagoons. This resulted in water being discharged to the soil. "Upon discovery, the water was contained and sampled. Sample results were all below regulatory limits. The pipe was repaired. The NPDES permit requires a report to North Carolina Division of Water Resources (NC DWR). This report was made at 10:01 am on 9/11/2019. Because NC DWR was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The Licensee will be notifying the Region II office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-09-11
54266 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-09-10 19:34 | 2019-09-11 03:10 | 2019-09-11 | UNANALYZED CONDITION DUE TO LIGHTNING STRIKE "A lightning strike occurred at approximately 1502 CDT on 09/10/2019, and a resulting power surge damaged some of the security door card reader system equipment. However, this did not affect access to plant areas for personnel who were already within protected area. At 1830 on 09/10/2019, it was discovered that some of the oncoming night shift personnel could not access particular areas that required the use of security card readers. Extent of condition check at 1934 on 09/10/2019 determined that access to 1A and 3A Electric Board Rooms, which contain remote shutdown panels and Fire Safe Shutdown equipment. was prohibited for the night shift personnel. This condition is reportable under 10 CFR 50.72(b)(3)(ii)(B) - Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. Access was restored to all plant areas at 2106 on 9/10/2019. No plant events occurred during the time frame that the 1A & 3A Electric Board Rooms inaccessible that would have required access to these areas. "The NRC Resident Inspector has been notified." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2019-09-11
54265 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-09-09 | 2019-09-10 11:47 | 2019-09-12 | AGREEMENT STATE REPORT - LOST MOISTURE / DENSITY GAUGE The following information was received from the Texas Department of State Health Services via E-mail: "On September 10, 2019, the Agency [Texas Department of State Health Services] was notified by the licensee that on September 9, 2019, one of its technicians had lost a Troxler model 3440 moisture/density gauge. The gauge contained a 40 milliCurie americium-241 source and an eight milliCurie cesium-137 source. "The licensee stated the technician had been working at a temporary job site and had placed the gauge on the tailgate of the truck. The technician left the job site, to get a meal, with the gauge still setting on the tailgate. After traveling about three miles the technician noted the tailgate was down and found the gauge was missing. The technician searched on foot the path they had driven, but did not locate the gauge. On the morning of September 10, 2019, the licensee searched the path traveled by the technician, but did not find the gauge. "The licensee stated that the gauge was not in a transport case and the operating rod did not have a lock on it. Therefore, they could not say that there is no chance for an exposure to a member of the general public. The licensee stated they did not know if local law enforcement had been notified at the time of the call to the Agency, but would make sure that they call them and informed them of the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident No.: I-9708 * * * UPDATE FROM ARTHUR TUCKER TO BRIAN LIN AT 0753 EDT ON 9/12/2019 * * * The following information was received via E-mail: "On September 11, 2019, the licensee left a phone message informing the Agency [Texas Department of State health Services] that the gauge had been recovered. No additional information was provided. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Alexander), NMSS Events Notification E-mail group, CNSNS (Mexico), and ILTAB (Tucker). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub122 * * * UPDATE AT 0959 EDT ON 9/12/19 FROM ART TUCKER TO JEFF HERRERA * * * The following update was received from the Texas Department of State Health Services via email: "On September 12, 2019, the Agency was contacted by the licensee and informed that the gauge had been recovered by a member of the general public on the day of the event (September 10, 2019). The individual who found the gauge contacted the licensee using the information provided on the gauge on September 11, 2019. The individual who recovered the gauge stated they found the gauge near the location the licensee had been using the gauge. The individual who found the gauge did not provide a reason they did not call before September 11, 2019. "The gauge was inspected and was not damaged. The source was in the fully shielded position. A source leak test has been completed and sent for analysis. The individual who recovered the gauge stated they did not attempt to operate the gauge. The licensee stated they did not believe the individual who have been exposed because of this event. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Alexander), NMSS Events Notification E-mail group, CNSNS (Mexico), and ILTAB (Email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://wwwpub.iaea.org/MTCD/publications/PDF/Pub122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-09-18
54264 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2019-09-09 | 2019-09-09 16:44 | 2019-09-09 | AGREEMENT STATE REPORT - LOST SOURCES The following information is a summary of a telephone call from New York City's Health Department: On September 9, 2019, New York-Presbyterian Brooklyn Methodist Hospital was unable to locate a shipment that had arrived a few days earlier. The shipment consisted of ten I-125 seeds in a container with lead shielding. The combined activity of the ten seeds is 3.5 mCi. The licensee is continuing to investigate this event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-09-17
54263 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2019-09-07 13:09 | 2019-09-07 15:53 | 2019-09-07 | AUTOMATIC REACTOR TRIP "At 1309 EDT on September 7, 2019, with the unit in Mode 1 at approximately 95 percent power, the reactor automatically tripped during main turbine valve testing. The trip was not complex with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by the turbine bypass valves discharging steam to the main condenser. "Due to the reactor protection system actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). The cause of the reactor protection system actuation is under evaluation. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-09-07
54262 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2019-09-07 08:24 | 2019-09-07 12:01 | 2019-09-07 | AUTOMATIC REACTOR TRIP "On September 09, 2019 at 0824 EDT, with St. Lucie Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped on Low Reactor Coolant System Flow due to a trip of the 1A1 reactor coolant pump. The trip was uncomplicated with all systems responding normally post-trip. Operators responded and stabilized the plant in Mode 3. The cause of the loss of the 1A1 reactor coolant pump is currently under investigation. "St. Lucie Unit 2 was unaffected and remains in Mode 1 at 100 percent power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip." Decay heat removal is being accomplished by main feed water and the main condenser using the turbine steam bypass valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-09-07
54261 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-09-05 14:00 | 2019-09-06 15:35 | 2019-09-06 | AGREEMENT STATE - SHUTTER CONTROL MECHANISM MALFUNCTION The following was received from Kentucky Department of Health Radiation Branch (KY RHB) via email: "KY RHB was notified on 9/6/2019 by a representative from a specifically licensed facility, Big Rivers Electric Corp., that at 1400 EDT on Thursday 09/05/2019, one fixed gauging device (Kay Ray Dual Model 7080, Serial Number 13321G), containing a 100 mCi Cs-137 source (serial No. 12376-V; assay date 6/1/1981) had developed a potential problem. An investigation showed that the shutter remained partially shut when the arm of the on-off shutter mechanism was moved to the fully open position. The gauge is located 25 feet above the floor between fly ash hoppers, and was left on the hopper with the shutter in the closed position. Pending removal of the source no access has been permitted to the two affected hoppers, and all maintenance activities will be delayed until the device has ben removed. No overexposures to the public or to plant workers have been reported. The licensee will be contacting a licensed service provider to remediate this situation." Event Report ID No.: KY190010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-09-16
54260 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-08-02 | 2019-09-06 13:59 | 2019-09-06 | AGREEMENT STATE REPORT - IMPROPER DISPOSAL OF A SOURCE The following report is a synopsis of an email received from the Florida Bureau of Radiation Control: During an inventory conducted on August 2, 2019, the University of Florida discovered that a Ni-63 source was improperly sent to a scrap metal processor. The Ni-63 source (serial number: 3270) had an activity of 13.5 mCi. Florida Incident Number: FL19-098 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-09-16
54259 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-08-29 | 2019-09-06 12:44 | 2019-09-06 | AGREEMENT STATE REPORT - LOST SOURCE The following report is a synopsis of an email received from the Florida Bureau of Radiation Control (BRC): On September 6, 2019, Westrock CP, LLC called to notify the BRC of a lost Cs-137 source (serial number: S99J2804). The activity of the source as measured on approximately January 1, 1997, was 5 mCi. Westrock had planned to remove five sources during a semi-annual inventory survey, but they were unable to locate one of the sources. A more sensitive survey meter was then flown to the licensee, but it was unable to detect any activity in the area where the source was expected to be. Florida Incident Number: FL19-111 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-09-16
54258 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-08-30 12:30 | 2019-09-06 10:29 | 2019-09-06 | AGREEMENT STATE - RADIOGRAPHY CAMERA SOURCE UNABLE TO RETRACT The following was received from Kentucky Department of Health Radiation Branch (KY RHB) via email: "KY RHB was notified by telephone on 9/3/19 that at approximately 1230 EDT on 8/30/19, while performing radiography in a pipe rack, radiographers were unable to retract a 38.7 Curie Ir-192 (AEA/QSA A424-9, Serial No. 82580G) source into the exposure device (QSA 880D Serial No. D11651) using the crank mechanism. During the retracting process the cover plate on the drive became loose, enabling the internal drive cable to depart the gear system in the handle of the drive cable mechanism. "Since the issue with the drive cable could not be repaired, the incident became a retrieval situation, and the crew made appropriate notifications to the Radiation Safety Officer, manager and on-site contact. The crew established a new 2 mR boundary as required and confirmed that the area was secure. The drive cable was removed from the handle, and the source was manually retracted into the exposure device. The source was secured in the exposure device at 1435 EDT. During the 2-hours while the source was exposed, there were no overexposures to the public. "The radiographer and assistant received exposures of 80 mR and 130 mR respectively and the manager received an exposure of 5 mR. It was determined that the root cause of the incident was that the crew did not properly inspect the equipment before commencing non-destructive testing activities. It was discovered that the drive cable handle was missing four of the six screws that secure the cover plate on. This caused the drive cable to slip off the gear and partially lift the cover plate. The drive cables were immediately taken out of service and replaced with properly functioning equipment." Event Report ID No.: KY190009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-09-16
54257 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-09-05 21:15 | 2019-09-06 02:47 | 2019-11-07 | CONTAINMENT PENETRATION DISCOVERED NOT ISOLATED "At 2115 CDT on 9/5/2019, an inside containment test connection and inoperable outside containment isolation valve were discovered to be open for a containment air sample penetration. This resulted in the containment penetration not being isolated. The inside containment test connection was closed at 2322 CDT on 9/5/2019. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and (D) and 10 CFR 50.72(b)(3)(ii)(B). "There was no impact to the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." * * * UPDATE FROM PAUL BURTON TO HOWIE CROUCH AT 1342 EST ON 11/7/19 * * * "This event was originally reported on September 6, 2019 under 10 CFR 50.72(b)(3)(v)(C) and (D) and 10 CFR 50.72(b)(3)(ii)(B). Upon completion of the investigation of the event, it was determined that the event had insignificant safety consequences because the containment breach was disconnected from the Reactor Coolant System by a series of closed valves for the duration of the event. Additionally, the lines to the inside containment connection and the outside inoperable containment isolation valve that was found to be open as well as the main line connecting and passing through the penetration were one-inch diameter lines. Analysis determined that containment breaches that are less than a three-inch diameter do not lead to a large radiation release. "The event did not place the plant in an unanalyzed condition that significantly degrades plant safety. Therefore, 10 CFR 50.72(b)(3)(ii)(B) did not apply to this event and this notification is to retract reporting under that criterion." The licensee notified the NRC Resident Inspector. Notified R4DO (Drake). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2019-09-06
54256 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-04-28 22:00 | 2019-09-05 16:53 | 2019-09-05 | TECHNICAL SUPPORT CENTER VENTILATION SYSTEM OUT OF SERVICE DUE TO DISCOVERED CONDITION "This is a non-emergency eight hour notification for a loss of Emergency Assessment Capability. "A condition impacting functionality due to a loss of cooling of the Technical Support Center (TSC) ventilation system occurred on 4/28/19. Filtration capability was not impacted by this condition. Maintenance subsequently repaired the condition and the TSC ventilation system was returned to service on 5/1/19. This condition did not affect the health and safety of the public or station employees. "The NRC Resident Inspector has been notified. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as the discovered condition affected the functionality of an emergency response facility." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-09-05
54255 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2019-09-04 03:46 | 2019-09-04 16:55 | 2019-09-16 | UNPLANNED CONTAMINATION EVENT The following was received via e-mail: "On September 4, 2019, at approximately 0346 EDT, a glass component failed, resulting in an unplanned contamination event. The release was limited to an area inside of the Radiologically Controlled Area. This area is designed for radiological work. There has been no personnel contamination. Airborne radioactivity samples are below action levels. Cleanup and Decontamination activities were safely and promptly initiated, but due to the complexity and space constraints of the system components, normal access to the area is not likely be restored within 24 hours. There has been no exposures or releases to the environment or public. "The licensee has notified the NRC Resident Inspector." * * * RETRACTION ON 9/16/19 AT 1115 EDT FROM RON RICE TO BRIAN LIN * * * The following retraction information was obtained from the licensee via email: "The unplanned contamination event was decontaminated to levels that did not require access to be restricted by imposing additional radiological controls within 24 hours, so the event did not require a report per 10CFR70.50(b)(1)(i). The NRC resident inspector has been informed." Notified R2DO (Ehrhardt), NMSS Events Notification (email), and Fuels Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2019-09-24
54254 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2019-08-30 13:10 | 2019-09-03 14:36 | 2019-09-03 | AGREEMENT STATE REPORT - MOBILE LEAD SHIELD SHIPPED WITH SOURCE INSIDE The following report was received from the Maryland Department of the Environment (MDE) Radiological Health Program (RHP) via email: "On August 30, 2019, at 13:10 [EDT], the MDE-RHP was contacted by telephone by medical licensee, MedStar Franklin Square Medical Center nuclear medicine department (MD-05-032-01). "An order had been placed by the medical center's Biomedical Department through eBay for a mobile lead shield for a Co-57 flood reference source. Upon receipt of the mobile shield, a Co-57 flood source was discovered inside. Only the mobile shield was ordered. The flood source was identified as an Eckert & Ziegler Feather Lite model MED3709 (S/N 159-062), 10 mCi as of June 1, 2011. The current activity was calculated to be 4.61 microCuries at time of receipt. The medical center's Radiation Safety Officer was notified. The sealed source was leak tested and evaluated using a Capintec Captus 3000 well counter with an efficiency of 37 percent. The leak test result was less than 0.005 microCuries. "Eckert & Ziegler was contacted on August 30, 2019. The flood source was sold to Lower Oconne Community Hospital. The Co-57 flood source was originally shipped on April 20, 2011. The community hospital closed on February 14, 2014. The Georgia Radioactive Materials Program was contacted on August 30, 2019 at 1300 [EDT] with preliminary information concerning this sealed source. Georgia radioactive materials license No. 1389 for the community hospital was terminated June 2016. "MDE-RHP will further investigate this incident. Eckert & Ziegler will provide a Return Kit for disposal. The source is currently secured in a waste storage room at MedStar Franklin Square Medical Center." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2019-09-11
54253 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2019-09-01 17:17 | 2019-09-01 17:44 | 2019-09-03 | NOTIFICATION OF UNUSUAL EVENT DUE TO DECLARATION OF HURRICANE WARNING "A hurricane warning is in effect for St. Lucie County including the plant site. A hurricane warning was confirmed with the State Watch Office at 1717 EDT. As a matter of procedure, St. Lucie Nuclear Power Plant entered an Unusual Event classification for the hurricane warning. State and local officials have been notified by the licensee. "The NRC Resident Inspector was notified of this by the licensee. "This report is submitted in accordance with 10 CFR 50.72(a)(2)(i) due to the Notice of Unusual Event and 10 CFR 50.72(b)(2)(xi) due to the offsite notification." * * * UPDATE AT 1835 EDT ON 9/3/19 FROM SARAH LOGSDON TO JEFF HERRERA * * * "The Hurricane Warning was downgraded to a Tropical Storm Warning by the National Weather Service for St. Lucie County including the Plant Site. At time 1818 EDT on 9/3/19, St. Lucie Nuclear Power Plant has terminated from the Unusual Event Classification. "There are no changes in plant status for either unit. Both units are stable at 100 percent power. "The NRC Resident Inspector was notified." Notified the R2DO (Shaeffer), IRDMOC (Kennedy), NRR EO (Walker), R2RA (Dudes via email), NRR (Nieh via email), DHS SWO, FEMA Ops Ctr., DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), FEMA NRCC (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2019-09-01
54252 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-08-31 20:55 | 2019-09-01 00:09 | 2019-09-01 | MANUAL TRIP DUE TO LOSS OF STEAM GENERATOR LEVEL CONTROL "While operating at 100 percent power, the Watts Bar Unit 1 reactor was manually tripped at 2055 EDT on August 31, 2019 due to loss of steam generator #2 level control. The trip was not complex. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems, including Auxiliary Feedwater, actuated as designed. Operations responded and stabilized the plant. Decay heat is being removed by the Auxiliary Feedwater and the Steam Dump System. "Unit 2 is not affected. "The cause of the loss of steam generator water level control is being investigated. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv)(B). The automatic actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector was notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-09-01
54251 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-08-29 07:30 | 2019-08-30 15:54 | 2019-08-30 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following is a synopsis of information received via email from the State of California: On 8/29/2019, California's Radiologic Health Branch (RHB) was contacted by the Radiation Safety Officer (RSO) of Construction Testing and Engineering, South, Inc. to report a damaged moisture/density gauge. The gauge was damaged on 8/29/2019 at 0730 PDT, when it was run over by construction equipment at a building site located on the Marine Corps Logistic Base in Barstow, CA. It was determined that the gauge's source rod was damaged, but the source appeared to be undamaged and remained in the encapsulated container. The RSO placed the damaged gauge back in the Type A transport container and the gauge will be taken to Maurer Technical Services for evaluation and disposal. The gauge is a CPN model MC3 moisture/density gauge (serial number: M38058257) with a 0.37 GBq Cs-137 and 1.9 GBq Am-241 source. This is being reported to the NRC Operations Center as a 24-hour report under 10 CFR 30.50(b)(2) since the radioactive gauge cannot be locked in the shielded position (due to the source rod being broken). California 5010 Number: 082919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-09-09
54250 | 0 | ST LUKE'S REGIONAL MEDICAL CENTER |  |  |  |  | 2019-02-20 12:05 | 2019-08-30 15:18 | 2019-08-30 | PATIENT RECEIVED DOSE GREATER THAN PRESCRIBED DOSE Summary via phone call: This is a notification of a medical event that occurred on February 20, 2019 at 1205 MDT, in which 81 microCi of Radium-223 (Xofigo) was administered intravenously to the patient for metastatic prostate cancer that had spread to the bone. The original written directive from the patient's physician was for 56 microCi of Radium-223, however the pharmacy label was written for 81 microCi. The medical event was discovered during the Radiation Safety Officer's internal audit with the conclusion that the 81 microCi was the correct dosage at the intended organ. No adverse effect is expected for the patient. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2019-09-09
54249 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-08-28 18:00 | 2019-08-30 14:42 | 2019-08-30 | AGREEMENT STATE REPORT - PANORAMIC IRRADIATOR SOURCE FAILED TO RETRACT The following information was received via facsimile: "The New York State Department of Health (NYSDOH) was notified by the radiation safety officer (RSO) of Pall Hauppauge that they had an incident where the source did not retract completely, leaving the source partially exposed for a period of time. "According to the RSO, on August 28, 2019 at about 1800 EDT, the source at Vault 4 had gotten stuck three inches above the down (safe) position. All of the safety and alarm systems worked as designed, and the operator did not attempt to enter the irradiator or take any action. The RSO indicated he was able to free the source by lifting it 'just an inch or two' then letting it back down. "This is the same vault that had previous stuck source incidents (NY-19-05 and NY-19-06) [EN53984 and EN54025] this year. At that time Nordion removed the vault, re-conditioned it, and returned it to Pall. "The RSO contacted Nordion and they are expected to be on-site the week of September 2nd. The vault will not be used until the issue is resolved. The RSO indicated he locked out all operators' key access to the vault until Nordion is on-site. "The root cause for the source getting stuck has not yet been determined. "DOH will continue to monitor this incident. "Paul Hauppauge is licensed to possess Cobalt 60 in sealed source use in a Nordion International dry panoramic storage irradiator." NY Event Report ID No.: NY-19-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-09-09
54248 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-08-28 | 2019-08-30 11:08 | 2019-08-30 | AGREEMENT STATE REPORT - LOST I-125 SEED The following was received from the Illinois Emergency Management Agency (IEMA) via email: "Carle Foundation Hospital (Urbana, IL) reported a lost I-125 seed that occurred during a seed localization procedure in the mammography suite. The seed was 166 microCi (6.142 MBq). Three seeds were delivered for the procedure. One was used, and one was returned to the vendor. The third seed could not be found the next morning when staff performed the final inventory. It is believed the seed was thrown in the trash immediately after the procedure and went to a landfill the following morning. The investigation is ongoing and a final report to IEMA is pending." Item Number: IL 190027 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-09-09
54247 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2019-08-30 | 2019-08-30 10:51 | 2019-09-01 | AGREEMENT STATE REPORT - MISSING PORTABLE GAUGE The following is a summary of information received from the Department of Environmental Quality (DEQ) via email: At about 0910 [CDT] on 8/30/19, DEQ received a call from W2 Engineering, Oklahoma license OK-32142-01. W2 Engineering holds an Oklahoma license for portable gauges and is based in Oklahoma City. [W2 Engineering] reported that it had lost contact with one of the technicians who had been driving one of the company's vehicles with a Humboldt portable gauge (s/n 8700) in it. The last known location for [the technician] (and presumably the gauge) was at 0856 [CDT] Thursday when [the technician] made a purchase at Perry, Oklahoma. [The technician] had not made contact since then, nor had [the individual] responded to numerous messages and efforts to contact. [W2 Engineering] now considers the gauge out of the licensee's control. [W2 Engineering] has advised the [Oklahoma Highway Police], and they say the vehicle is not known to be in any of their impound yards. [W2 Engineering] has filed a report with Oklahoma City police, and a police officer is on site taking the report now. This report is based on an initial phone notification, and more information will be added when it becomes available. * * * UPDATE FROM MIKE BRODERICK TO DONALD NORWOOD AT 1717 EDT ON 9/1/2019 * * * The following information was received via E-mail: "The gauge missing from W2 engineering has been recovered along with the vehicle in Blackwell, Oklahoma. More details will be provided as they become available." Notified R4DO (Drake) and the NMSS Events Notification E-mail group. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2019-09-09
54246 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  | 20000 KW TEST | 2019-08-29 22:00 | 2019-08-29 17:48 | 2019-09-03 | DEVIATION FROM SITE SECURITY PLAN REQUIREMENTS Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures will be employed. * * * UPDATE FROM THOMAS NEWTON TO DONALD NORWOOD AT 1435 EDT ON 8/30/2019 * * * The period that the discovered vulnerability will exist has been extended. Compensatory measures will be employed. Notified NPR PM (Yin), NPR SS (Reed), NPR BPM (Montgomery) and via E-mail the 73.71 Safeguards Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | SAFEGUARDS REPORTS | [8 empty] | NON EMERGENCY | 0 | MD | NPR |  |  | 73.71(b)(1) |  |  | 1 | 2019-08-29
54245 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2019-08-28 | 2019-08-29 17:18 | 2019-08-29 | AGREEMENT STATE REPORT - SHUTTER FAILURE The following was received from the Oklahoma Department of Environmental Quality via email: "The State of Oklahoma reported that a generally-licensed Ronan Model SA-F37 fixed gauge (S/N M2265) containing 1.5 Ci of Cs-137 experienced a shutter failure during routine maintenance. The source holder is being removed from service and will be stored pending disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2019-09-06
54244 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-08-28 13:16 | 2019-08-28 19:10 | 2019-08-28 | LOSS OF HIGH PRESSSURE CORE SPRAY "On Wednesday, August 28, 2019, at 1316 CDT, Grand Gulf Nuclear Station experienced a power loss to the Control Room High Pressure Core Spray (HPCS) Instrumentation Panel due to an internal inverter failure. The power loss caused the loss of the HPCS System (a single train system). The minimum flow valve (a Primary Containment Isolation Valve) for HPCS opened due to this power loss as well. This valve was manually closed in response to this, and the outboard isolation requirement for the associated penetration [which] is closed [for the] system remained intact throughout this event. "No other accident mitigation systems were affected by this event. "The cause of this event is under investigation at this time. "The NRC Resident Inspectors were notified. "This Condition is an 8-hour reportable condition as an event or condition that could have prevented the fulfillment of a safety function, in accordance with 10 CFR 50.72(b)(3)(v)(D)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-08-28
54243 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2019-08-28 11:02 | 2019-08-28 16:35 | 2019-08-28 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE FOUND IN SCRAP YARD The following is a summary of information received from the State of Oregon via phone call: On August 28, 2019, at 1102 PDT, the Oregon Department of Health and Radiation Protection received a report from the R.S. Davis Scrap Yard, that a moisture density gauge was found in a 55 gallon drum that was crimped at the top so the gauge will not fall out. The gauge is a CPN MC-3 Porta Probe with a 10 mCi Cs-137 source and a 50 mCi Am/Be 241 source. The scrap yard employed a contractor to take radiation readings and perform a swipe test of the gauge. The gauge housing appears to be damaged but the source housing seems intact. The contractor was unable to inspect the bottom of the gauge inside the drum. The following was measured: A reading of 13 mR/hr on contact at the side A reading of 200 mR/hr on contact at the bottom A reading of 3 mR/hr one foot from the side Swipe Test results were less than background The State of Oregon Radiation Inspector believes the gauge is damaged because normal radiation readings for a similar gauge at one meter would be 0.4 mR/hr. The State of Oregon will be conducting an investigation of this event. The gauge is currently under the control of the scrap yard. Oregon Event Reference Number: 19-0037. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2019-09-05
54242 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-08-27 01:09 | 2019-08-27 02:34 | 2019-08-27 | AUTOMATIC REACTOR TRIP "At 0109 EDT, with Unit 1 in Mode 1 at 100 percent power, the reactor automatically tripped due to a dropped rod causing a negative rate trip. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by the auxiliary feedwater (AFW) and steam dump systems. Unit 2 is not affected. "Due to the reactor protection system actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-08-27
54241 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-08-26 10:35 | 2019-08-26 16:41 | 2019-08-26 | FITNESS FOR DUTY A non-licensed contract employee supervisor had a confirmed positive for an illegal drug during pre-access testing. The employee's access to the plant was denied. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2019-08-26
54240 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-08-26 11:13 | 2019-08-26 15:26 | 2019-08-26 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE/DENSITY GAUGE The following is a summary received via email from the state of Colorado: On August 26, 2019 at 11:13 MDT, the Colorado Department of Public Health and Environment was notified by Ninyo & Moore, that Troxler 3430 moisture density gauge with 9 mCi source of Cs-137 and 44 mCi source of Am/Be was stolen from Colorado School of Mines in Golden, Colorado. The Troxler gauge was last seen on August 23, 2019. Campus police were notified and they have put out a state wide notification informing state police of the missing gauge. Event Report Number: CO 190016. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-09-03
54239 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2019-08-25 11:02 | 2019-08-25 15:51 | 2019-08-25 | AUTOMATIC SCRAM DUE TO MAIN GENERATOR GROUND FAULT RELAY "On August 25, 2019, at 1102 [CDT], Quad Cities Unit 1 experienced an automatic scram from 100 percent power. All rods fully inserted and there were no complications. The trip was initiated from a main generator ground fault relay. Troubleshooting of the fault is in progress. All systems responded as designed. There were no systems inoperable and no TS [Technical Specification] action statements were in progress prior to the Reactor Scram. Reactor water level dropped below the Group 2 and Group 3 Reactor Water Level Isolation set-points as expected, and recovered via the Feedwater system. Standby Gas Treatment System auto started and Reactor Building Ventilation Isolation occurred as expected. Unit 1 remains in Mode 3. "Decay heat is being removed using the steam bypass valves to the condenser and the safety relief valves did not lift as a result of the trip. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." Unit 2 was not affected. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-08-25
54238 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2019-08-23 | 2019-08-23 12:06 | 2019-08-23 | PART 21 NOTIFICATION - LOOSE BUTTERFLY VALVE TAPER PINS Fisher Controls issued FIN 2019-01 for all Fisher type 7600, 7700, 7800, 9100, 9200, and 9500 series butterfly valves that use taper pins to secure the valve shaft to the valve disk. This does not apply to valve constructions that use straight pins or grooved straight pins. Fisher was notified on June 25, 2019 of one instance where a taper pin became loose due to incorrect installation within the valve. Fisher recommends the owners of these valve assemblies perform normal maintenance at regular intervals in order to inspect the valve assembly and replace worn, aged, and damaged parts, as well as verifying that the taper pins are correctly installed and reset them if necessary. For technical questions, please contact: Jacob Clos Quality Manager Emerson Automation Solutions Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Phone: (641) 754-2108 Jacob.Clos@Emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-08-23
54237 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-08-22 22:34 | 2019-08-23 00:33 | 2019-08-23 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM INOPERABLE "At 2234 [EDT], on 08/22/2019, while Unit [2] was at approximately 100 percent power in MODE 1, it was discovered that Unit 2 HPCI was INOPERABLE. HPCI does not have a redundant system; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." Initial evaluation is that it is a power supply issue. The system had no indications, followed by smoke from behind the circuitry, and then indications returning. This is associated with a 14-day Limiting Condition for Operation. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-08-23
54236 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2019-08-22 | 2019-08-22 16:41 | 2019-08-22 | PART 21 - CRACKED SPRAY TIP ON EMD FUEL INJECTOR The following is a summary of information received from Engine Systems, INC (ESI) via facsimile: The basic component, a fuel injector, P/N 5229250, S/N R2200, was sent to ESI for failure analysis and the spray tip was found to have a through wall crack. Inspections determined the fuel feed holes in the body of the spray tip were incorrectly drilled, resulting in one of the holes not properly penetrating the reservoir. A cracked spray tip would inhibit proper combustion of fuel within the corresponding power cylinder which could affect the carrying capability of the diesel engine. This could impact the operability of the diesel engine, thereby, preventing the emergency diesel generator set from performing its safety-related function. It is the belief of ESI that the extent of condition is limited to the single spray tip. Based on the age of the tip (repair kit purchase order (PO) date is 2001), if other tips contained the same discrepancy, it is highly likely they would have been detected or replaced. There were 20 tips in the same batch as the failed spray tip. The end user of the PO is Nine Mile Point. ESI suggests that the customer perform an inspection on the remaining 19 injectors. ESI has discontinued the affected injector repair kit. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-08-22
54235 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-08-21 11:00 | 2019-08-22 15:10 | 2019-08-23 | AGREEMENT STATE REPORT - LOST PACKAGE DURING TRANSIT The following information was received from the Massachusetts Radiation Control Program via email: "On 08/08/19, a package containing 20 mCi of P-32 was sent by PerkinElmer, Inc. (the 'licensee') to the University of Sherbrooke in Ontario, Canada (the 'customer') via the common courier which was scheduled to arrive on 08/09/19. The package never arrived. The customer notified the licensee by telephone on 08/21/19 at 1100 [EDT] of the missing package. The licensee contacted the common courier on 08/21/19 to gain more information and to try and locate the package. The common courier acknowledged they would attempt to locate the package and would call the licensee back. The common courier did not contact the licensee so on 08/22/19 at 1030 [EDT] the licensee contacted the common courier again and discovered the package could not be located and was declared missing. The licensee notified the Massachusetts Radiation Control Program (the 'Agency') by telephone on 08/22/19 at 1200 [EDT] to report a missing package containing radioactive material. "The Agency considers this event to be open." * * * UPDATE ON 08/23/2019 AT 1154 EDT FROM THE MASSACHUSETTS RADIATION CONTROL PROGRAM TO CATY NOLAN * * * The activity amount in the original report was erroneously reported as 20 mCi. The correct activity is 737 microCuries. Notified R1DO (Werkheiser), and ILTAB and NMSS Events (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-08-30
54234 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-06-27 01:30 | 2019-08-22 12:49 | 2019-08-22 | AUTOMATIC TRANSFER OF 4-kV VITAL BUS FROM AUXILIARY TO STARTUP POWER "This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) regarding an invalid Engineered Safety Feature actuation signal. "On June 27, 2019, at 0130 hours Pacific Daylight Time (PDT), with Unit 2 operating at 100 percent power, the U2 4-kV Vital Bus F was automatically transferred from its auxiliary power to its startup power due to an invalid loss of bus voltage signal. The cause of the invalid signal was due to a test jumper that was inadvertently left in place during surveillance testing. As a result, one auxiliary saltwater pump started and two containment fan cooler units started in slow speed. "At 1245 PDT, Vital Bus F was transferred back from startup power to auxiliary power which is the normal plant operating configuration. "This event was entered into the Diablo Canyon Power Plant corrective action program for resolution. This event did not result in any adverse impact on the health and safety of the public. The plant responded as expected. "In accordance with 10 CFR 50.73(a)(1), a telephone notification is being made in lieu of submitting a written Licensee Event Report. "The licensee has notified the NRC Senior Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-08-22
54233 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-08-18 17:00 | 2019-08-20 20:00 | 2019-08-20 | REFUELING WATER STORAGE TANK LEVEL LOWER THAN REQUIRED "While performing a purification on the Unit 2 Refueling Water Storage Tank (FWST), it was discovered that the single train system was inoperable due to the level being less than the required volume per SR [Surveillance Requirement] 3.5.4.2. The condition was discovered on 8/18/19 at 1700 [EDT]. The FWST level was restored to greater than the required volume per SR 3.5.4.2 at 1744 on 8/18/19. This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-08-20
54232 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2019-08-19 09:39 | 2019-08-20 18:28 | 2019-08-20 | LOSS OF PUBLIC PROMPT NOTIFICATION SYSTEM "At 0939 CDT, on 8/19/19, the National Weather Service reported to Cooper Nuclear Station that the National Warning System (NAWAS) Radio would neither transmit nor receive. The system has been intermittently available since then, but never declared fully functional. The backup notification system has been verified to be available throughout this period. Additional information from the National Weather Service received 8/20/19 at 1414 determined that the Shubert Tower transmitter is non-functional and would not be repaired until 8/21/19. The transmission outage is conservatively assumed to have begun at the first notification on 8/19/19 at 0939. The Shubert Tower transmitter activates the [EMERGENCY ALERT SYSTEM] EAS/Tone Alert Radios used for public notification. This is considered to be a major loss of the Public Prompt Notification System capability and is reportable under 10 CFR 50.72(b)(3)(xiii) when the primary notification system is or will be unavailable for greater than 24 hours with the backup system available. "The NRC Senior Resident has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-08-20
54231 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-07-30 | 2019-08-20 11:19 | 2019-08-20 | AGREEMENT STATE REPORT - INCORRECT DOSAGE ADMINISTERED The following was received via email: "On August 19, 2019, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that a medical event had occurred. The event occurred on a patient who was prescribed to receive four treatments of lutetium-177 at 200 milliCuries each. After the third treatment, the physician was supposed to change the dose of the fourth and final dose to 100 milliCuries. The radiopharmaceutical was ordered, and the dose was administered. The RSO stated that during the review of the patient's treatment, they found the pharmacy had sent a unit dose of 200 milliCuries instead of the requested 100 milliCuries. The RSO stated both the prescribing physician and the patient were notified of the error. No adverse effects are expected on the patient. "The Agency has requested additional information on this event. Additional information will be provided as it is received in accordance with SA-300." * * * UPDATE ON 8/20/19 AT 1133 EDT FROM ART TUCKER TO BETHANY CECERE * * * "On August 20, 2019, the licensee contacted the Agency and stated the treatment site was the mid-gut. The treatment was conducted on July 30, 2019. The error was discovered the day of the event. Additional information will be provided as it is received in accordance with SA-300." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-08-28
54230 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-08-16 | 2019-08-19 14:17 | 2019-08-19 | AGREEMENT STATE REPORT - PATIENT UNDER-DOSAGE The following was received via fax: "On August 16, 2019, a patient underwent a Y-90 SIR-Sphere treatment. The treatment plan was for 2 administrations of Y-90. The first administration was delivered without incident. The second administration was to be a total dosage of 12.27 mCi delivered to the right lobe of the liver. During this second administration, it was observed that the team had backflow into the administration vile. The administration was immediately halted, and the team took readings to ascertain the amount of material delivered. It was estimated that only 28 percent of the dose was delivered to the patient. The patient was verbally informed the day of the event. The referring physician was left a voicemail on the day of the event, however further attempts will be made to contact him directly." Event Report ID No.: PA190019 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-08-27
54229 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2019-08-19 09:24 | 2019-08-19 14:46 | 2019-08-19 | AUXILIARY FEEDWATER SYSTEM INOPERABLE "At 0924 EDT, on August 19, 2019, it was discovered that both trains of the Auxiliary Feedwater System were simultaneously inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(B). The door separating the two steam-driven Auxiliary Feedwater Pump Rooms was inadvertently left open during maintenance activities for more than an hour. The door was immediately closed upon discovery, restoring operability to the Auxiliary Feedwater System. The non-safety grade Motor-Driven Feedwater Pump remained operable during this time; additionally, the beyond-design basis diesel-driven Emergency Feedwater Pump also remained available. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2019-08-19
54228 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-08-18 | 2019-08-19 12:04 | 2019-08-19 | AGREEMENT STATE REPORT - DAMAGED GAUGE LOCKING MECHANISM The following report was received via fax: "On August 19, 2019, an Environmental Engineer for Nucor Steel of Tuscaloosa, Alabama notified the Office of Radiation Control [Agency] that a gauge stored in a caster mechanism had a loss of containment and damaged the locking mechanism of the gauge. The shutter mechanism is working, but the gauge cannot be locked out. "The licensee notified the Alabama Emergency Operations Center of the event on August 18, 2019, at 1757 CDT. The licensee chose to follow-up with the Agency to ensure proper notification. The Agency told the licensee to send a synopsis of the events and a plan of action to maintain or dispose of the gauge. "As of 1100 CDT today, the gauge is secure, but unlockable. The licensee has contacted the manufacturer for possible repair or disposable options. This incident remains open until a decision is made by the licensee for repair or disposal." Alabama Incident: 19-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR | 30.50(b)(2) |  |  |  | 0 | 2019-08-27
54227 | -1 | USAF DEFENSE LOGISTICS AGENCY |  |  |  |  | 2019-07-11 | 2019-08-19 12:31 | 2020-09-09 | <br><br>EN Revision Imported Date : 9/10/2020<br><br>EN Revision Text: NI-63 SOURCE INADVERTENTLY SENT TO DISPOSAL FACILITY The following is a summary of a phone call with the licensee: The U.S. Air Force Defense Logistics Agency (DLA) received report of a source which they believe has been inadvertently sent to a waste disposal facility. The source (Ni-63, 15 mCi, S/N 30306) was housed in a desktop chemical scanner, and has been in use for some time. On 4/26/2019, the scanner was sent to the U.S. Air Force Defense Reutilization and Marketing Office (DRMO). On 5/13/2019, DRMO then sent the scanner to DLA as scrap/waste, after which it was likely sent to a disposal facility. On 7/11/19, it was determined that the source has been inadvertently disposed of. DLA is currently working to determine which waste facility received the source, so recovery can be attempted. The source was last leak tested on 10/01/2018, with no leaks detected. No exposures were expected from the disposal of the source. The licensee has contacted NRC RIV (Poston-Brown). * * * RETRACTION ON 09/09/2020 AT 1418 EDT FROM RAMACHANDRA BHAT TO CATY NOLAN * * * The following is a summary of a letter received from the licensee: The IONSCAN 400B device is an exempt item as it was sold under an exempt distribution license. Since it is not a Generally Licensed (GL) item and does not meet the requirements for isotope and activity, the licensee has retracted this event notification. Notified RIV (Bolger), R4DO (Warnick), and ILTAB and NMSS (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | Lost/Stolen Lnm>10x | [9 empty] | Non Emergency | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-08-27
54226 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-08-17 | 2019-08-19 09:26 | 2019-08-28 | AGREEMENT STATE REPORT - CESIUM-137 SOURCE INVOLVED IN VEHICLE FIRE The following information was received via E-mail: "This report is sent for informational purposes. On August 17, 2019, the Agency [Texas Department of State Health Services] received a call from the answering service and was informed that a licensee had reported a fire during transport of a density gauge. The Agency called the licensee, Halliburton Energy Services and was informed of the event. The licensee stated one of their blending trucks had been traveling on highway 285 south near Orla, Texas when the driver saw sparks coming from the road behind their truck. The driver pulled over and when they went to the back of the truck they found a tire had blown out and was now burning. "The driver called for help, but by the time the fire department arrived, the truck was fully involved in the fire. The truck was transporting a 100 milliCurie cesium-137 source installed on a pipe. The licensee stated the dose rate at 30 centimeters from the gauge, taken after the fire was extinguished, was 2 millirem per hour, which is normal. The licensee stated the truck and trailer were taken to their facility and a leak test was taken on the gauge. The licensee stated the driver had pulled off the road and traffic was not restricted. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9703 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 1013 EDT ON 8/19/2019 * * * The following information was received via E-mail: "The Agency received a call from the licensee at 0856 CDT on August 19, 2019. The licensee stated they had conducted additional surveys this morning and found dose rates were as high as five millirem per hour at one meter from the gauge. The licensee contacted their manufacturing section and one of the individuals was familiar with this type of event stated the gauge shielding was probably compromised, but believed the source was undamaged. The licensee stated the gauge would be returned to its manufacturing facility for inspection. No exposure has occurred from this event. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Young) and the NMSS Events Notification E-mail group. * * * UPDATE FROM ART TUCKER TO RICHARD SMITH AT 1743 EDT ON 8/28/2019 * * * "On August 28, 2019, the licensee notified the Agency that the results of the leak test performed on the source involved in this event had come back reading 0 dpm. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Azua) and the NMSS Event Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-08-27
54225 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2019-08-14 13:00 | 2019-08-16 16:11 | 2019-08-16 | AGREEMENT STATE REPORT - VEHICLE ACCIDENT DURING RADIOPHARMACEUTICAL TRANSPORT The following was received from the State of Maryland via email: "On August 14, 2019, at 1415 EDT, the Maryland Department of the Environment (MDE) Hazardous Materials Division contacted the MDE Radiological Health Program (RHP) concerning a vehicular accident in the south bound lane of State Route 4 near the intersection of Dower House Road, east of Forestville, MD. A Prince George's County HazMat responder contacted MDE/RHP at 1430 EDT to provide details of the accident. "The initial transportation accident, as logged in at 1300 EDT, indicated the transport vehicle from Cardinal Health (MD-33-198-01) was transporting two cases of radiopharmaceuticals to two medical facilities in southern Maryland for its 'third run.' A tractor trailer collided with the rear of the transport vehicle at a controlled intersection just after the traffic light turned green. One case contained 3 lead pigs containing Tc-99m totaling 395.67 mCi. The second case contained 2 lead pigs containing Tc-99m totaling 106.90 mCi. The cases were originally marked as White 1, with a Transportation Index of 0. The cases remained fully blocked and braced following the accident. The containers were not compromised. Two senior pharmacist employees from Cardinal Health responded to the scene and took possession of the containers after carefully surveying the cases. The cases went on to be delivered to the intended destination. "The Cardinal Health office in Dublin, OH called the National Response Center at 1627 (Incident Number 1255161) to report this accident. MDE was contacted at 1645. "MDE will further investigate this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2019-08-26
54224 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2019-08-16 08:21 | 2019-08-16 15:05 | 2019-08-16 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0821 MST, on August 16, 2019, a main turbine trip occurred followed by a loss of power to all reactor coolant pumps. The Palo Verde Nuclear Generating Station (PVNGS) Unit 2 control room then received reactor protection system alarms for low departure from nucleate boiling ratio and an automatic reactor trip occurred. Following the reactor trip, auxiliary feedwater was manually started to maintain steam generator levels. A Main Steam Isolation Signal was manually initiated as directed by the Emergency Operating Procedures. Unit 2 is currently stable in Mode 3. Prior to the reactor trip, Unit 2 was operating normally at 100 percent power. "No major equipment was inoperable prior to the event that contributed to the event or challenged operator response. All control element assemblies fully inserted into the core and no emergency classification was required per the PVNGS Emergency Plan. The cause of the reactor trip is under investigation. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 2 reactor trip." Decay heat is being removed via the atmospheric steam dump valves. Units 1 and 3 were unaffected by this event. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-08-16
54223 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-08-15 13:30 | 2019-08-16 10:59 | 2019-08-16 | AGREEMENT STATE REPORT - LOST AND RECOVERED GAUGE The following report was received via email: "On August 15, 2019, the licensee's radiation safety officer (RSO) reported to the Agency [Texas Department of State Health Services] that a Troxler Model 3440 moisture-density gauge (serial number 26417) containing 8 mCi of Cs-137 and 40 mCi of Am-241/Be was stolen out of a pickup truck at a job site at 1330 CDT. The gauge was found by the technician at 1930 CDT under a debris pile at the job site. An investigation into the incident is ongoing. Additional information will be reported in accordance with SA300." Texas Incident #: 9702 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-08-26
54222 | 0 | RENSSELAER POLYTECHNIC INSTITUTE |  |  |  | 0.1 KW TANK TYPE CRITICAL FACILITY | 2019-08-14 19:00 | 2019-08-15 13:30 | 2019-08-15 | FAILURE TO MEET TECHNICAL SPECIFICATION REQUIREMENT The following synopsis was received from Rensselaer Polytechnic Institute (RPI) via phone: On August 14, 2019, at 1900 EDT, during a reactor startup and the reactor critical, the RPI reactor was scrammed due to one of the three safety system channels required by Technical Specification (TS) 3.2.6 not responding to an increase in power. Upon investigation the licensee realized that a test cable was still connected to the input of that instrument channel and the instrument was not connected to the neutron detector. The highest power level reached was 0.14 W. The licensee contacted the NRC as required by RPI TS 6.7.2. In addition, during the scram, one of the four control rods was stuck 2 inches off the bottom. Upon investigation the licensee realized that foreign material (screw) was jammed at the end of the rod. The licensee removed the screw and the control rod was fully inserted. The licensee plans to perform a rod drop test prior to resuming normal operations. There was no additional dose to the facility staff. The NRC inspector was on sight when the event occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | NY | NPR | [5 empty] | 0 | 2019-08-15
54221 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2019-08-14 16:30 | 2019-08-15 11:59 | 2019-08-15 | AGREEMENT STATE REPORT - ACCIDENT DURING SOURCE TRANSPORT The following was received from the North Dakota Department of Health via phone: A vehicle transporting a 300 mCi Cs-137 (Eckert & Ziegler Model Cs7.P03, SN CZ110) well logging source overturned when returning from a coal mine back to the storage facility. The source remained in the travel case in the vehicle. There was no fire nor injuries. The radiation safety officer arrived approximately 40 minutes after the incident and surveyed the case. No additional radiation above background was detected. The source was transported to Bismarck and a leak test performed. They are still awaiting the results. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2019-08-23
54220 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-07-26 10:03 | 2019-08-14 20:00 | 2019-08-14 | INVALID CONTAINMENT VENTILATION ISOLATION ACTUATION "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report an invalid Containment Ventilation Isolation (CVI) actuation at Watts Bar Nuclear Plant (WBN) Unit 2. "On July 26, 2019, at 1003 Eastern Daylight Time (EDT), the Train A CVI actuated due to an invalid High Radiation signal from 2-RM-90-130, Containment Purge Air Exhaust Monitor. Prior to and following the invalid High Radiation alarm, all radiation monitors except 2-RM-90-130 were stable at their normal values. All required automatic actuations occurred as designed. Upon investigation, the cause of the invalid High Radiation alarm was due to a failed ratemeter for 2-RM-90-130. "Control room operators performed appropriate checks and confirmed that the subject indication was an invalid high radiation signal. The ratemeter for 2-RM-90-130 was replaced and the monitor returned to service. At the time of the event, plant conditions for a High Radiation alarm did not exist; therefore, the CVI was invalid. "The NRC Resident Inspector was notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-08-14
54219 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2019-08-14 12:01 | 2019-08-14 14:47 | 2019-08-14 | INADVERTANT ACTIVATION OF EMERGENCY SIRENS "At 12:01 PM (EDT), on August 14, 2019, all fifty-four (54) of the Davis-Besse Nuclear Power Station Offsite Emergency Notification sirens were inadvertently activated for one minute during a planned silent test. The County Sheriff's Dispatch Office notified FirstEnergy Nuclear Operating Company of the inadvertent actuation. This notification is being made solely as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "All sirens remain functional, and the NRC Resident Inspector has been notified of the issue." The Licensee will be notifying Ottawa and Lucas counties and the state of Ohio. The inadvertent activation was by the county dispatcher. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-08-14
54218 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2019-08-13 16:00 | 2019-08-14 10:07 | 2019-08-14 | CRITICALITY ACCIDENT ALARM SYSTEM SPEAKER FAILURE "At approximately 1320 [EDT] one speaker in the Low Enriched Uranium (LEU) area was identified as not operating when a series of Public Address (PA) announcements were made. Strobe lights, however, were functioning in the area. At 1430 compensatory measures were established to limit access in the affected area to only those personnel with radio communication with the alarm room. At 1600 the system was tested and it was confirmed that the Criticality Accident Alarm System (CAAS) was not audible in the LEU area. No other areas were effected. On August 13, 2019 at approximately 1726, full compliance was restored when the speaker was replaced and satisfactorily retested. The most recent audibility test of this area had been satisfactorily performed on August 6, 2019 at approximately 1100. The licensee notified the NRC Resident Inspector on August 13, 2019 at approximately 1653." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2019-08-22
54217 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2019-08-12 13:00 | 2019-08-13 16:15 | 2019-08-13 | AGREEMENT STATE REPORT - TRANSPORTATION ACCIDENT INVOLVING A DENSITY GAUGE The following was received from the Maryland Department of the Environment Radiological Health Program (MDE RHP) via phone: "On August 12, 2019, at approximately 1330 [EDT] hours, the Maryland Department of the Environment (MDE) Hazardous Waste Enforcement Division contacted the MDE Radiological Health Program (RHP) concerning a vehicular accident that involved a nuclear density gauge. "The initial transportation accident, as logged in at 1300 hours, indicated the accident location near the 70-mile marker on west-bound I-70, near Lisbon, MD. The vehicle, identified as a box truck, was carrying a density gauge that was ejected during the accident. The gauge was observed not in its transportation case at time of arrival of Fire/EMS and Maryland State police. The company Radiation Safety Officer from Francis O. Day, Inc. responded to the scene and verified that the source was in the shielded position. The gauge was taken to Northeast Technical Services for evaluation. "The gauge was identified as a Troxler model 4640 surface thin-layer gauge, S/N 2399. This gauge has a Cs-137 sealed source with a nominal activity of 8 mCi and was last leak tested on July 14, 2019. The State trooper on scene stated that the vehicle was actually a pickup truck. The transportation case was ejected from the pickup truck along with the truck cap and the driver. The gauge left the confines of the transportation case and came to rest approximately 10 feet from the case. The chain that held the case to the truck bed broke. The driver did not survive the accident. "MDE/RHP will further investigate this event. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2019-08-21
54216 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-08-12 16:19 | 2019-08-13 12:19 | 2019-08-13 | AGREEMENT STATE REPORT - RADIOGRPAHY CAMERA SOURCE WOULD NOT RETRACT The following report was received from Louisiana Department of Environmental Quality (LDEQ) via facsimile: "On August 12, 2019, at 1619 CDT, the licensee called LDEQ to report that a source would not retract back into the shielded position. The event happened approximately at 1330 at a temporary jobsite within the Shell Refinery, Airline Highway, Norco, LA. in St. Charles Parish. "The camera was being used at this temporary jobsite. The exposure was made and the source would not retract into the shielded position. The problem was detected during the post exposure survey. The exposure levels indicated the source was still in the collimator. The reportable event was the 'drive cable' broke in the associated equipment being used with this QSA Global, Model 880 Delta exposure device. The serial number for the 880 Delta is D-7906. The source was a 91.0 Ci of Ir-192, model number A424-9, and serial number 86571G. "The [industrial radiography] crew followed the [Versa Integrity Group] VIG Safety Procedures securing and shielding the radiography source and then contacted the [Radiation Safety Officer] RSO. The three-man site crew performed the preliminary source retrieval procedures. QSA Global was contacted by the RSO to assist with the source retrieval. QSA Global arrived approximately at 1811 CDT and the source recovery ended at 1930 CDT. The drive cable and source assembly were taken to QSA Global for an equipment evaluation. "VIG personnel involved in this retrieval received a maximum exposure of 40 mrem and the other individual's exposures were less. There were no excessive exposures associated with this event. At no time did the general public receive an exposure to the source of radiation." Louisiana Event Report ID No: LA 190011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-08-21
54215 | 0 | FLOWSERVE |  |  |  |  | 2019-08-12 | 2019-08-12 17:47 | 2019-09-06 | PART 21 - NON-DESTRUCTIVE EXAMINATION PERFORMANCE OF COMPONENTS BY AN UNQUALIFIED EMPLOYEE The following is a summary of the information received from Flowserve via facsimile: Contrary to the requirements of ASME Section III & ASME NQA-1 Requirement 2, an employee of Flowserve was found to have performed Non-Destructive Examinations (Liquid Penetrant Testing - PTs) without the required certificate in accordance with ASNT SNT-TC-1A, and Flowserve's written practice. The employee was trained and tested in accordance with the written practice and ASNT requirements. Although the individual section scores were found to pass the (70 percent) minimum, the composite test requirements failed to meet the minimum 80 percent requirement. Actual composite score achieved was 79.176 percent. The extent of exposure to this condition was on examinations completed between 10/22/18 and 11/21/18. There were ten examinations, totaling 22 pieces that were completed by the employee without oversight/signature by another certified individual. The scope of impacted valves/components encompasses body, stem, cover, yoke, pin wedge, and disk. Licensees affected include Exelon Company, Pinnacle West Capital Corp, Bruce Power, Xcel Energy, Alabama Power, Entergy Nuclear Operations Inc., and FirstEnergy. Flowserve issues a corrective action, and is currently in the process of determining the root cause and prevention action measures. This will include identifying the affected valves via communications with affected customers. * * * UPDATE ON 09/06/2019 AT 1345 EDT FROM KEVIN WORTH TO JEFFREY WHITED * * * The following is a synopsis of a letter received from Flowserve: On 09/06/19, Flowserve issued its Final Report for the Part 21, noting the scope of the valves/components affected by the issue described above. Flowserve also noted the corrective actions that were taken to address the issue and detailed the specific actions taken for the individual components. Notified R1DO (Carfang), R2DO (Shaeffer), R3DO(Edwards), R4DO(O'Keefe), and Part 21/50.55 Reactors Group (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-08-12
54214 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-08-12 | 2019-08-12 14:22 | 2019-08-12 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "On August 12, 2019, the licensee's radiation safety officer (RSO) reported to the Agency [Texas Department of State Health Services] that while one of its technician's was using a Troxler Model 3440 moisture/density gauge [device #21053] to perform density testing at a temporary job site in Greenville, Texas, the tip of the insertion rod, which holds an 8 millicurie cesium-137 source, came off in the test hole. The RSO and a representative from a licensed gauge service company met at the site and recovered the source. The RSO stated the source holder, which is screwed onto the end of the insertion rod then welded, was intact with the source, spring, and spacer in place. However, it had broken off approximately 1/4 inch below the weld (below the threads). A survey of the test hole and surrounding area found no readings above background. A wipe test was taken which will be analyzed at the service company's facility, where the source and gauge are being taken for evaluation/repair, before the source is removed from the recovery pig. No overexposures are expected from this event. An investigation into this event is ongoing. Information will be provided as it is obtained in accordance with SA-300." Texas Incident: 9700 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-08-20
54213 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-02-21 | 2019-08-12 14:05 | 2019-08-12 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE DURING MEDICAL TREATMENT The following report was received from the Pennsylvania Bureau of Radiation Protection (PA DEP) via facsimile: "As a result of a Departmental [PA DEP] inspection the licensee reported an equipment failure event that occurred on February 21, 2019. The equipment was a Varian GammaMed Plus, Serial #641017, containing 6.518 Ci of lr-192. A patient was receiving her last of three fractions of treatment with total treatment time for this fraction being 222.6 seconds divided through a total of eight positions. Twenty-five seconds into treatment the unit issued an inactive source error and retracted the source. The physicist entered the room to confirm that the source was retracted. The manufacturer was called. At the manufacturer's recommendation, the console key was powered off, then back on, and the remaining treatment was initiated to continue with the untreated area. This time at 25.8 seconds into the treatment the same error occurred. The remaining treatment plan was saved into the planning computer, and the patient had the applicator removed and was sent home. Varian sent a field service representative who successfully replaced the Geiger-Muller board and functionality was verified. The patient was then rescheduled. The continued treatment on February 25, 2019 accurately reflected the partial treatment and was appropriately scaled to reflect the source decay from the previous treatment. The final portion of the treatment was delivered without incident. There was no harm or overexposure to the patient. The patient was informed at the time. The attending physician has not been notified." Event Report ID No.: PA190018 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-08-20
54212 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2019-08-11 08:40 | 2019-08-11 12:14 | 2019-08-11 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 0840 EDT, on August 11, 2019, with Unit 2 in Mode 1 at 100 percent power, the reactor automatically tripped due to a turbine trip. The trip was not complex, with all systems responding normally post trip. Because of the reactor trip, the Auxiliary Feedwater (AFW) System actuated as expected due to low water levels in the steam generators. The AFW pumps started as designed when the valid system actuation was received. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the main condenser using the turbine bypass valves. "Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a 4-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an 8-hour, non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the RPS and AFW. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The site remains in a normal electrical lineup. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-08-11
54211 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-08-11 08:14 | 2019-08-11 11:40 | 2019-08-11 | MANUAL REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE MALFUNCTION "At 0814 EDT on 8/11/19, with Unit 2 at 83 percent power during a planned load reduction, the reactor was manually tripped due to degraded feedwater flow control to the 23 Steam Generator caused by a malfunction of the associated Feedwater Regulating Valve, 23BF19. The trip was not complex, with all systems responding normally post trip. An actuation of the Auxiliary Feedwater system occurred following the manual reactor trip as expected due to low level in the steam generators. The unit is stable in Mode 3. Decay heat is being removed by the Main Steam Dumps and Auxiliary Feedwater System. "Due to the actuation of the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an eight-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feedwater System. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The licensee notified the State of New Jersey. Unit 1 remains at 100 percent power. | 0 | 0 | 0 | 0 | 83 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-08-11
54210 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2019-08-09 | 2019-08-09 14:54 | 2019-08-09 | AGREEMENT STATE REPORT - MEDICAL EVENT - UNDERDOSE TO PATIENT The following was received from the Wisconsin Radiation Protection Section via email: "On 8/9/19, the Department [State of Wisconsin Department of Health Services] was notified by ThedaCare Regional Medical Center - Appleton of a medical event. The administered TheraSphere dosage had a calibration date of 7/28/2019. The licensee intended to use a calibration date of 8/4/2019. The prescribed dose to the patient was 110 Gy. As a result of the difference in calibration dates, the delivered dose was 17.9 Gy. This was approximately 16 percent of the prescribed dose. The Department will perform a follow-up investigation and site visit." The patient will be notified. Wisconsin Event Report ID: WI190009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2019-08-19
54209 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-08-06 | 2019-08-08 11:11 | 2019-08-09 | AGREEMENT STATE REPORT - LEAKING ECKERT & ZIEGLER CS-137 VIAL SOURCE The following was report was received from the Ohio Department of Health via email: "The licensee discovered a leaking Eckert & Ziegler Cs-137 vial source. The leak test result, performed on August 6, 2019, identified 0.016 microCuries of removable activity. Notification to the Ohio Department of Health was made on August 8, 2019. The licensee will dispose of the source through a licensed waste broker. "Device model number: RV-137-250U Serial number: 171069" Ohio item number: OH190014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-08-19
54208 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-08-07 | 2019-08-09 11:14 | 2019-08-09 | AGREEMENT STATE REPORT - SHUTTER STUCK OPEN IN DAMAGED LEVEL DENSITY GAUGE The following was received from KY Department for Public Health & Safety, Radiation Health Branch (KY RHB) via fax: "KY RHB was notified by telephone on 8/8/19 by a representative from a specifically licensed facility, North American Stainless, that on 8/7/19 an event occurred when molten steel escaped a mold due to an overflow in a cooling trough, and covered access to the top portion of a Berthold Model LB300ML level gauge (Serial No. 9413), containing a 1 mCi Co-60 rod sealed source (Serial No 1820-11-5). This resulted in the shutter on-off mechanism becoming disabled. After the steel and mold had cooled, it was freed on 8/8/19 and segregated into a secure storage area. "Initial readings taken with a Ludlum 2241-3 survey instrument measured with a Ludlum 44-7 probe were less than 2 mR/hr outside the gauge storage area. No overexposures were reported. "On 8/8/19, Radiametric Technologies, a service provider located in Lorain, Ohio, requested reciprocal approval and was granted reciprocity on 8/9/19 in order to assess and remediate the situation, to be conducted on 8/13/19. "North American Stainless is reviewing the incident to avoid future repeat incidents involving mold flow issues, and a complete report will be provided once the remediation is complete." Event Report ID No KY190007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-08-19
54207 | 0 | NVI |  |  |  |  | 2019-08-09 07:25 | 2019-08-09 10:09 | 2019-08-09 | LOST RADIOGRAPHY CAMERA IN INTERNATIONAL WATERS The following is a summary of a phone call from the licensee: NVI (Non-Destructive and Visual Inspections) notified the NRC that a radiography camera with a less than 22 Ci Ir-192 source was lost when it fell into approximately 200 feet of international waters from an oil platform in South Pass Section 60-A. The camera (SPEC 150 Model 0605; Source SPEC G-60 S/N AC0160) was locked in the shielded position during setup when the radiographer slipped. The licensee does not plan to retrieve the device. Additionally, the licensee notified NRC R-IV and the Bureau of Safety and Environmental Enforcement. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-08-19
54206 | 0 | COLUMBIA GENERATING STATION |  |  |  |  | 2019-08-05 15:19 | 2019-08-08 17:03 | 2019-08-08 | PART 21 NOTIFICATION - SPECTRUM TECHNOLOGIES CONTROL POWER TRANSFORMER "Pursuant to 10 CFR 21.21(d)(3)(i), this is a non-emergency notification by Energy Northwest concerning a defect on a control power transformer (CPT) resulting in a failed starter coil while in service at Columbia Generating Station. The defect was associated with a CPT provided by Spectrum Technologies (model Micron B150-2957-1). "On June 14, 2019, a failure analysis was completed that determined that the failure of the coil occurred because the starter coil was exposed to chronic elevated temperatures. These elevated temperatures were caused by the associated control power transformer (CPT) secondary voltage being maintained outside the coil's rated voltage range. Previously on June 10, 2019, it was determined that the CPT installed in the Spectrum Technologies motor starter assembly did not meet procurement specifications resulting in a turns ratio that produced higher voltages on the motor starter coil than its rated voltage. This led to overheating and breakdown of the coil insulation that created a short between two windings. "On August 5, 2019, Energy Northwest completed a Part 21 evaluation in accordance with 10 CFR 21.21(a)(1) and determined that this deviation could create a substantial safety hazard as defined in 10 CFR 21.3. "The NRC Resident Inspector has been notified." The licensee has 14 Spectrum transformers that are continuously energized that could be affected. The one transformer that experienced the failure was out of service for maintenance at the time of discovery. Four other coils were inspected for extent of condition and no more failures were found. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-08-08
54205 | 0 | WATERFORD | 3 |  |  | [3] CE | 2019-06-25 17:13 | 2019-08-08 13:26 | 2019-08-08 | INVALID ENGINEERED SAFETY FEATURE ACTUATION SIGNAL DUE TO HUMAN ERROR "This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to provide information pertaining to an invalid Engineered Safety Feature actuation signal. "On June 25, 2019, at Waterford 3, while performing an emergent replacement of relays on the Engineered Safety Features Actuation System Train A that affected Shield Building Ventilation Train A and HVAC Equipment Room Supply Fan AH-1 3A, unintentional contact was made between two contacts on the relay, resulting in an inadvertent initiation of other relays in the sequencer circuit. This caused the starting of Low Pressure Safety Injection Pump A, Switchgear Ventilation Fan A, and Boric Acid Makeup pumps. This was a partial actuation of Engineered Safety Features Actuation System Train A. Affected plant systems started and functioned successfully. "This inadvertent actuation was caused by human error and was not a valid signal resulting from parameter inputs. The 1992 Statements of Consideration define an invalid signal to include human error. Therefore, this actuation is considered invalid. This event was entered into the Waterford 3 corrective action program for resolution. This event did not result in any adverse impact to the health and safety of the public. "In accordance with 10 CFR 50.73(a)(1), a telephone notification is being made in lieu of submitting a written Licensee Event Report. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-08-08
54204 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2019-08-07 | 2019-08-08 12:38 | 2019-08-08 | IRIDIUM-192 SOURCE LOST DURING SHIPMENT A 0.78 Curie (today's activity) Ir-192 source was lost during shipment from the Mayo Clinic in Rochester, MN to Alpha-Omega Services in Vinton, LA. The last known location was Memphis, TN with the common carrier. Its original shipment date was February 8, 2019. The licensee contacted the common carrier upon suspicion of loss on June 4, 2019. On August 7, 2019, the source had not been located and was deemed lost. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PROTECTIVE ACTION PREVENTED | LOST/STOLEN LNM>1000X | [8 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(a) | 20.2201(a)(1)(i) |  |  | 0 | 2019-08-16
54203 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2019-08-06 13:35 | 2019-08-06 17:29 | 2019-08-06 | INOPERABLE INSTRUMENTATION AFFECTS SAFE SHUTDOWN CAPABILITY "At 1335 EDT on 08/06/2019, it was discovered that reactor protection system (RPS) instrumentation functions for turbine stop valve closure and turbine control valve fast closure, end of cycle recirculation pump trip (EOC-RPT) instrumentation, and control rod block instrumentation were simultaneously inoperable due to a loss of feedwater heating; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). "RPS instrumentation, EOC-RPT instrumentation, and control rod block instrumentation functions were restored at 1422 EDT on 08/06/2019. "There was no impact on the health and safety of the public or plant personnel. "The NRC Senior Resident Inspector has been notified." | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-08-06
54202 | 0 | YALE NEW HAVEN HOSPITAL |  |  |  |  | 2019-07-02 | 2019-08-06 13:39 | 2019-08-06 | WRITTEN DIRECTIVE FOR MICRO-SPHERE LIVER TREATMENT WAS INCORRECT On 7/24/19 while preparing to administer micro-sphere liver treatment the health physicist discovered that the paperwork for a previous treatment on a different patient was incorrect. The paperwork indicated that the treatment was for the left lobe of the liver. The patient's left liver was removed in a previous surgery. The prescribing physician realized that the treatment was for the right lobe of the liver and administered treatment to the right lobe. The physician failed to correct the paperwork. The treatment was on 7/2/19. The prescribed dose was 0.77 GBq and the administered dose was 0.78 GBq. There was no harm to the patient. The licensee notified the NRC R1 Office (Tara Weidner, Penny Lanzisera). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2019-08-14
54201 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-08-05 09:36 | 2019-08-05 17:06 | 2019-08-05 | SECONDARY CONTAINMENT PERSONNEL DOOR UNABLE TO BE CLOSED AND LATCHED "On August 5, 2019, at 0936 CDT, Grand Gulf entered Technical Specification (TS) 3.6.4.1 due to a Secondary Containment personnel door, 1A401B, not being able to meet its design function. Door 1A401B was unable to be closed and latched. This condition is being reported as a loss of safety function. The station also entered 05-S-01-EP-4, Auxiliary Building Control (Secondary Containment) to address Auxiliary Building differential pressure due to the opened Secondary Containment penetration. "Actions were taken to close and latch Door 1A401B. Secondary Containment has been declared operable. TS 3.6.4.1 and 05-S-01-EP-4 were exited. "The NRC Resident Inspector was notified of the condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-08-05
54200 | 0 | IDAHO TRANSPORTATION DEPARTMENT |  |  |  |  | 2019-08-04 | 2019-08-05 15:00 | 2019-08-05 | STOLEN AND RECOVERED GAUGE On 8/4/2019, a private citizen found a gauge belonging to the Idaho Transportation Department (ITD) in the middle of the road in Caldwell, Idaho. ITD was notified and promptly sent a Radiation Safety Officer (RSO) to recover the gauge. The gauge was housed in a Type A Category 2 container. Locks to the container were cut, but there appeared to be no tampering with the gauge itself. The RSO performed surveys, all of which came back normal. The gauge was then secured and is back in ITD's possession. ITD determined the gauge had been stolen from one of their trailers at a job site in Nampa, Idaho. ITD reported this incident to the Idaho State Police and will be reaching out to local law enforcement for the criminal investigation. No other material is believed to have been stolen at this time. The gauge is a Troxler 3440 moisture density gauge with an 8 mCi Cs-137 and a 40 mCi Am-241/Be source. The source serial numbers are 7710838 and 78-7073 respectively. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-08-13
54199 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2019-08-04 17:45 | 2019-08-05 01:28 | 2019-08-05 | AVERAGE POWER RANGE MONITORS DECLARED INOPERABLE "On August 4, 2019 at 1745 [EDT], Reactor Recirculation Pump (RRP) 11 tripped. The cause for the trip is under investigation. "Following the RRP trip, the Average Power Range Monitors (APRMs) flow bias trips are inoperable due to reverse flow through RRP 11. The APRMs were restored to operable on August 4, 2019 at 1807, when the RRP 11 Discharge Blocking Valve was closed. "This 8-hour non-emergency report is being made based upon requirements of 10CFR50.72(b)(3)(v)(A) which states: 'Licensee shall notify the NRC of any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition.'" The licensee has notified the NRC Resident Inspector. | 89 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2019-08-05
54198 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2019-08-03 19:47 | 2019-08-03 23:33 | 2019-08-04 | MANUAL REACTOR TRIP AND MANUAL ACTUATION OF REACTOR CORE ISOLATION COOLING "At 1947 [EDT] on 8/3/19, with Hope Creek in Mode 1 at 37 percent power, the reactor was manually scrammed due to loss of condenser vacuum. All control rods fully inserted into the core. All safety systems responded as designed and expected. Reactor level was stabilized using Reactor Core Isolation Cooling (RCIC) and Reactor Feedwater Pumps. "Currently reactor water level is being maintained by the feedwater system and decay heat is being removed by the main condenser using the main turbine bypass valves. Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Due to the manual actuation of RCIC, this event is also being reported as an eight-hour, non-emergency notification per 10 CFR 50. 72(b )(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The plant is in its normal shutdown electrical lineup with all safe shutdown equipment available. The licensee will be notifying the state of Delaware, state of New Jersey and the Lower Alloway Creek township. | 0 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-08-04
54197 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2019-08-03 02:26 | 2019-08-03 06:47 | 2019-08-06 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR WATER LEVEL "At 0226 [CDT], an automatic scram on low reactor water level occurred due to a trip of the 'B' Reactor Feed pump. All control rods fully inserted. Reactor water level 2 was reached and the High Pressure Core Spray system, Reactor Core Isolation Cooling system, Division 3 diesel generator, Standby Gas Treatment Systems 'A' and 'B' and all shutdown safety related service water pumps started as expected. Reactor Core Isolation Cooling and High Pressure Core Spray injected as expected. All level 2 containment isolation signals occurred as expected and all level 2 containment valves closed as expected. Reactor water level is currently being controlled in band by condensate. Reactor pressure is being maintained by main turbine Bypass Valves. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(A), for ECCS discharge to RCS; 10 CFR 50.72(b)(2)(iv)(B), for RPS actuation, and 10 CFR 50.72(b)(3)(iv)(A), for specified system actuation. "The NRC Senior Resident Inspector has been notified." No safety relief valves lifted during the transient. The plant is in a normal shutdown electrical lineup with all safety equipment available. The licensee notified the Illinois Emergency Management Agency per their communications protocol. * * * UPDATE FROM DAVID LIVINGSTON TO HOWIE CROUCH AT 0321 EDT ON 8/4/19 * * * "Following automatic initiation of the High Pressure Core Spray (HPCS) System as described above, the HPCS System was manually secured following station procedures after verification that additional RPV [reactor pressure vessel] injection was no longer required. Securing HPCS injection in this manner prevents automatic restart of the system in the event of a subsequent low RPV level condition, rendering it inoperable. As the HPCS system is considered a single train safety system, this meets the reportability requirements of 10 CFR 50.72(b)(3)(v)(D). This reportable condition was identified following review of post-scram actions. The HPCS system has been restored to a Standby lineup." The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Pelke). * * * UPDATE FROM JAMES FORMAN TO KERBY SCALES AT 1545 EDT ON 8/6/19 * * * "Following the scram, the Primary Containment to Secondary Containment and the Drywell to Primary Containment differential pressure limits were exceeded. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.4, Primary Containment Pressure, and 3.6.5.4, Drywell Pressure, Actions A.1, B.1, and B.2 were entered. Primary Containment to Secondary Containment differential pressure and Drywell to Primary Containment differential pressure were restored to within the LCO limits at 1505 on 8/3/19 and the associated TS Actions were exited. This event is reportable under 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that could have prevented the fulfillment of the primary containment function due to being outside the initial conditions to ensure that drywell and containment pressures remain within design values during a loss of coolant accident. This event is also reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of the drywell and primary containment functions to control the release of radioactive material for the same reason." The licensee notified the NRC Resident Inspector. Notified R3DO (Pelke). | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2019-08-03
54196 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-08-02 | 2019-08-02 17:00 | 2019-08-02 | AGREEMENT STATE REPORT - DRIVE CABLE ON RADIOGRAPHY CAMERA SOURCE FAILED The following was received via e-mail from the Texas Department of State Health Services: "On August 2, 2019, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that a radiography crew working at a field site had experienced a source disconnect. The radiographers were using an INC IR-100 exposure device containing a 27 Curie iridium - 192 source. After one of their exposures, they could not return the source to the shielded position. The RSO stated a source recovery team was sent to the site and recovered the source. The RSO stated no overexposures occurred. The RSO stated the recovery team found that the drive cable had broken just behind the drive end connector. The RSO stated they are still investigating the event. Additional information will be provided as it is received in accordance with SA-300." Texas Event Report No: 9699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-08-12
54195 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-08-01 | 2019-08-02 15:49 | 2019-08-02 | AGREEMENT STATE REPORT - FIRE IN BUILDING CONTAINING RADIOACTIVE SOURCES We received the following notification via email from the Georgia Environmental Protection Division: "On August 2, 2019, our program [Georgia Environmental Protection Division] received a call from [the licensee] RSO, reporting a fire in a building at their facility that stored 6 radioactive sources. The fire occurred on August 1, 2019, is believed to have been caused by an electrical fire which resulted the building to burn to the ground. "The licensee searched the area, which is approximately 8'X10', in hopes to recover the sources. Only 2 of the 6 sources were recovered. However, the 2 sources are unidentifiable. The 2 sources are currently stored in a bag in a secured building. They are assuming the 4 sources were burned in the fire. The licensee did a general survey of the area but were only able to detect microrem readings. "Until the area has been determined free of contamination, the area will remain secured. The licensee will collect sample debris and wipe samples to determine if there is any contamination in the area. The samples will be sent off for analysis. "The Fire Department will not be able to enter the area to determine the cause of the fire until the area is considered free from contamination. "The licensee will be sending a follow-up report describing the incident, a current inventory of the sources damaged/lost, and current plan to determine the extent of the contamination and disposition of the sources." THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-08-12
54194 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-08-01 | 2019-08-02 11:27 | 2019-08-02 | AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE The following was received via e-mail from the Texas Department of State Health Services: "On August 2, 2019, the Agency was notified by the licensee's radiation safety officer (RSO) that a radiography crew was unable to retract a 56 Curie iridium - 192 source into a INC R100 exposure device. The radiographers set up a 2 millirem boundary and contacted the RSO. The RSO went to the scene and found that the guide tube had a sharp bend in it and would not let the source pass through the bend. The RSO straightened the guide tube and was able to return the source to the exposure device. No overexposures occurred. The guide tube has been removed from use." Texas Event Report No: 9698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-08-12
54193 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-08-01 15:30 | 2019-08-01 18:13 | 2019-08-01 | AGREEMENT STATE REPORT - POSSIBLE LOST RADIOACTIVE MATERIAL The following was received from the Colorado Department of Public Health and Environment (CDPHE) via e-mail: "The licensee reported at approximately 1530 hrs. [MDT] of August 1, 2019 to CDPHE that there was a package in the morning of August 1, 2019, with its shipping paper indicating two vials of Lu-177 (200 mCi). The licensee only has 1 vial in possession and the nuclear medicine technician who opened the package did not remember seeing two vials in the package. The package has been disposed of in the hospital dumpster before the licensee identified this. The licensee surveyed the dumpster but did not identify any source of Lu-177. The licensee contacted the vendor and is awaiting more information from the vendor regarding whether a second vial was ever shipped from the vendor to the licensee." Colorado Event Report No: CO190015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-08-09
54192 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-07-02 | 2019-08-01 14:25 | 2019-08-01 | AGREEMENT STATE REPORT - LOST AND RECOVERY OF A MOISTURE DENSITY GAUGE The following was received from the Nebraska Department of Health and Human Services via email: "Mid-State Engineering and Testing (MSET) reported the loss and recovery of a moisture/density gauge (CPN International MC Series) that contained a 1.85 GBq (50 mCi) Am-Be source and a 0.37 GBq (10 mCi) Cs-137 source. The gauge was initially believed to have been lost on July 2, 2019, somewhere between Aurora and Columbus, Nebraska, on a route that included Highways 14 and 30. The driver reported that approximately 1.5 miles west of the Highway 30 and Highway 81 intersection he had to forcefully apply the truck brakes to avoid a collision. The gauge was locked inside of a transportation case and secured to the truck with a lock and chain. When the brakes were applied, the transportation case handle was pulled out of the case and the tailgate of the truck fell open. When the truck accelerated after stopping at the intersection of Highways 30 and 81, the transportation case fell out of the vehicle. MSET attempted to locate the gauge without success. "Nebraska State Patrol, Nebraska Department of Roads, Columbus Police Department and Platte County Sheriffs Department were notified. The gauge was found by a member of the public on July 2, 2019. The member of the public contacted MSET on July 2, 2019, and the gauge was retrieved by MSET. The handle on the locked transportation case was damaged. The gauge inside did not appear to be damaged. The Nebraska Office of Radiological Health is investigating." Nebraska State Report # 190003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-08-09
54191 | 0 | WATERFORD | 3 |  |  | [3] CE | 2019-07-31 12:06 | 2019-07-31 16:20 | 2019-07-31 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE BORON INJECTION FLOW PATHS AND CHARGING PUMPS "On July 31, 2019, at 1206 CDT, Waterford 3 commenced initiation of a plant shutdown as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3. Prior to this, on July 31, 2019, at 1108 CDT, the boron injection flow paths were declared inoperable in accordance with LCO 3.1.2.2, 'Flow Paths - Operating,' and the charging pumps were declared inoperable in accordance with LCO 3.1.2.4, 'Charging Pumps-Operating.' This was due to visual examination identifying that propagation had progressed on a previously identified flaw on piping upstream of the header supplying the charging pumps. TS LCO 3.0.3 was entered due to the action statements of LCOs 3.1.2.2 and 3.1.2.4 not being met. LCO 3.0.3 requires that action shall be initiated within one hour to place the unit in a mode in which the specification does not apply by placing it in hot standby within the next 6 hours and cold shutdown within the next 30 hours. At 1206 CDT, Waterford 3 commenced direct boration to the reactor coolant system. "This condition meets the reporting criteria of 10 CFR 50.72(b)(2)(i) due to the initiation of plant shutdown required by Technical Specifications and 10 CFR 50.72(b)(3)(v)(A) and (D) due to an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to (A) shutdown the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident." | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2019-07-31
54190 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-07-30 15:21 | 2019-07-31 15:55 | 2019-08-21 | DISCOVERY OF CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "South Texas Project (STP) Unit 1 reactor head vent valve B1RCHCV0601 was declared inoperable on December 29, 2018, STP Unit 1 reactor head vent valve B1RCHCV0602 was declared inoperable on July 30, 2019. Technical Specification 3.3.3.5 requires one of two reactor head vent valves to be operable. This issue placed the plant in a 30-day Technical Specification Action. "At 0741 CDT on July 31, 2019, South Texas Project Electric Generating Station (STPEGS) made a determination based on firm evidence that reactor head vent valve B1RCHCV0602 had been inoperable since June 24, 2019. This results in a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The inoperable equipment is required for accident conditions and presents no danger to the health and safety of the public or the safe operation of the units. "The NRC Resident Inspector has been notified." * * * UPDATE FROM PAUL BURTON TO KERBY SCALES AT 1108 EDT ON 8/21/19 * * * "The Event Date and Time provided in EN# 54190 should have been reported as 7/30/2019 at 1521 CDT, since this was the time of discovery of a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." "The NRC Resident Inspector has been notified. "Notified R4DO (Young)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-07-31
54189 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-07-29 | 2019-07-31 15:20 | 2019-07-31 | AGREEMENT STATE REPORT - TRANSPORTATION ACCIDENT The following is a synopsis of information received from the Illinois Emergency Management Agency via email: On July 29, 2019, there was a vehicle accident while transporting medical radioactive materials near Tinley Park, IL. There was no release of material nor contaminated individuals. Details are pending from the licensee. This is a reportable incident under 32 Ill. Adm. Code 341.10(b)(5) as detailed in 49 CFR Part 171.15. Initial reports indicate at least one diagnostic radiopharmaceutical unit dose and a Co-57 sheet source were in transit at the time of the accident. Leak tests are pending, but initial surveys and an assessment of the radiopharmaceuticals indicates no escape of licensed material outside of the ammo can in which they were being transported. Serial number and leak test results of the sheet source as well as a description of the RAM in transit are pending. Licensee staff have reportedly taken possession of the licensed material and conducted surveys to ensure public safety. Illinois Event Report ID: IL190024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-08-08
54188 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-07-30 10:14 | 2019-07-30 15:42 | 2019-07-30 | UNPLANNED HIGH PRESSUE COOLANT INJECTION INOPERABILITY "On July 30, 2019, at 1014 EDT, the Division 2 Mechanical Draft Cooling Tower (MDCT) Fan D was declared inoperable due to a trip of the fan while placing in it high speed. The MDCT Fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. Investigation revealed that a high speed breaker control power fuse had blown. The control power fuse was replaced, the MDCT Fan D was tested satisfactorily, and HPCI was declared operable at 1431 EDT. This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) based on an unplanned HPCI inoperability." The licensee has notified the NRC Senior Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-07-30
54187 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-07-29 19:03 | 2019-07-30 13:47 | 2019-07-30 | TECHNICAL SPECIFICATION DEVIATION The following information was received via email: "On July 29, 2019, at 1903 CDT, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to a failure of the regulating blade drive mechanism during reactor operation. This email is a required notification per MURR Technical Specification (TS) 6.6.c(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by TS 1.1, had occurred. MURR was not in compliance with all Limiting Conditions for Operations (LCOs), specifically TS 3.2.a, which states, 'All control blades, including the regulating blade, shall be operable during reactor operation.' The regulating blade drive mechanism was removed, repaired, reinstalled, and all its functions were tested satisfactorily. Permission from the Reactor Facility Director was obtained per TS 6.6.c(4) prior to starting up the reactor later on July 29. Currently, MURR is at 10 MW. "A detailed event report will follow within 14 days as required by TS 6.6.c(3)." The licensee has notified the NRC Research and Test Reactor Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2019-07-30
54186 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2019-07-29 21:25 | 2019-07-30 13:24 | 2019-07-30 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following is a synopsis of information received from the Commonwealth of Virginia via email: On July 29, 2019, at approximately 2315 EDT, the Virginia Department of Health, Office of Radiological Health (Rad Health) was notified of a traffic accident involving a Troxler Gauge - model 4640B, Serial Number 2739, containing an 8 mCi Cs-137 source, source serial number 77-6508. At approximately 2125 EDT, a motorist entered a closed traffic lane and struck the gauge. Surveys by the Radiation Safety Officer (RSO) indicated that the source was likely not breached. The Rad Health Duty Officer advised the RSO that the gauge was safe to transport to the licensee's secured storage location. On July 30, 2019, Rad Health's Radioactive Materials (Rad Materials) staff visited the licensee's facility and performed contamination surveys of the gauge and the Type A package. No contamination was detected on any of the swipe samples collected. The licensee and the Rad Materials staff contacted the Troxler service department to discuss next steps. The Troxler service representative explained that they could use the swipe samples to perform a leak test. The RSO was advised that once the source is confirmed not to be leaking by Troxler, the licensee may transport the damaged gauge for repair or replacement. The RSO was advised by Rad Material staff that the Type A package label will need to be changed to correct the transport index (TI) value from 0.2 to 0.5, and the shipping papers would also need to be changed to show the new TI. Virginia Event Report ID: VA 19-005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2019-08-07
54185 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2019-07-27 19:29 | 2019-07-27 22:31 | 2019-07-27 | AUTOMATIC REACTOR SCRAM DUE TO MAIN TURBINE TRIP "At 1929 EDT on 7/27/2019, with the Unit in Mode 1 at 98 percent power, the reactor automatically scrammed due to a Main Turbine Trip. The trip was not complex, with all systems responding normally post-trip. Main Steam Isolation Valves (MSIVs) were manually closed to prevent exceeding Reactor Pressure Vessel Cooldown Rate. Rector Core Isolation Cooling (RCIC) was manually initiated to stabilize Reactor Vessel Water Level and Pressure following MSIV closure. The Main Condenser and Feedwater are available. "Operations responded and stabilized the plant. Reactor water level is being maintained via RCIC. Decay heat is being removed by discharging steam to the Main Condenser and RCIC. "The cause of the Main Turbine Trip is currently under investigation." The site is in a normal electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) |  |  | 0 | 2019-07-27
54184 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-07-25 | 2019-07-26 14:34 | 2019-07-26 | AGREEMENT STATE REPORT - SOURCE FAILED TO RETRACT The following was received via e-mail: "On Thursday, July 25, 2019, the licensee called to report an equipment failure event where, during a cardiovascular brachytherapy treatment, the source failed to retract at the end of the treatment time due to a kink in the catheter line. The unit being used was a Best Vascular, Inc., A1000 Series using the Novoste Beta-Cath 3.5 Delivery System and a Sr-90 source with a source strength of 79.3 mCi. A service engineer for Best Vascular was present during the time of treatment and was able to unkink the catheter line allowing the source to fully retract into the unit. There was no harm to the patient and no overexposure occurred." Event Report No.: PA190017 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-08-05
54183 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-07-26 10:48 | 2019-07-26 13:27 | 2019-07-26 | FITNESS FOR DUTY REPORT - CONFIRMED POSITIVE TEST FOR ALCOHOL A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2019-07-26
54182 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2017-02-08 17:30 | 2019-07-24 12:58 | 2019-07-24 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY EXPOSURE DEVICE The following is a synopsis of information received via email from the state of Maine: At approximately 1730 EST on 2/8/2017, Applus RTD had a source disconnect on a radiography exposure device at Casco Bay Steel in South Portland, Maine. The radiography exposure device was an Amersham Model 880 with an Ir-192 source. The Radiation Safety Officer (RSO) was contacted about the incident, went to the site, and helped secure the area with the help of a radiographer. The RSO replaced the drive cable and retrieved the source back into the radiography camera. The drive cable and exposure device have been taken to the manufacturer to determine the cause of the problem. The original notification for this event was made through the Nuclear Materials Event Database (NMED) under the 30-day reporting requirement due to the fact that the State felt it was not an equipment failure. During the State's review it was determined that a notification to NRC was required within 24 hours due to the equipment being disabled during the recovery operations. Maine Event Report ID No.: ME 17-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2019-08-01
54181 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-06-27 | 2019-07-24 10:37 | 2019-07-24 | AGREEMENT STATE REPORT - UNDERDOSE TO THE LIVER The following information is summarized from an email received from the state of Ohio: A patient was undergoing Y-90 Therasphere treatment of both lobes of the liver. The calculations and dose were ordered for the volume of the left lobe which was 230cc. Due to a communication error, that dose was delivered to the right lobe which had a volume of 1600cc. This represents an underdose to the right lobe. The intended dose to the right lobe was 120 Gy. The delivered dose was 17.6 Gy. The licensee is evaluating additional treatment. The patient and prescribing physician were notified. The State will be performing an investigation. Ohio report no.: OH190013 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-08-01
54180 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-07-12 | 2019-07-24 09:34 | 2019-07-24 | AGREEMENT STATE REPORT - LEAKING RADIOACTIVE SOURCE The following information was obtained from the state of Ohio via email: "[Manufacturing and Distribution] licensee received beta back-scatter on a device from customer for repair. Upon receipt, licensee conducted leak test and results indicated >185 Bq (0.005 microCi). Device contained 100 microCi Pm-147 source and is distributed under a general license. "Upon investigation, licensee determined customer had used probe on wet surface, which clogged aperture, and customer attempted to clear aperture with sharp, pointed object which damaged source. At customer's request, licensee went to customer's location to survey area of use for contamination. No contamination was found." Ohio report no.: OH190012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-08-01
54179 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2019-07-23 14:05 | 2019-07-23 19:50 | 2019-07-23 | OFFSITE NOTIFICATION "On 7/23/2019 at 1405 PDT, San Onofre Nuclear Generating Station (SONGS) made a required formal notification to the Regional Water Quality Control Board for the state of California concerning a monthly oil sample of the oil removal system. The sample was analyzed to contain 42 ppm oil. This number exceeds the daily instantaneous maximum of 20 ppm. "An additional sample was taken approximately one minute later and was analyzed to contain 8.1 ppm oil, potentially indicating a problem with the initial sample. Additional investigation is underway and a written follow-up report will be submitted to the Regional Water Quality Control Board within 5 days in accordance with the National Pollutant Discharge Elimination System permit." The licensee will inform NRC Region IV staff. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-07-23
54178 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-07-22 | 2019-07-22 19:37 | 2019-07-22 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following is a synopsis of information received via email from the state of California: On 07/22/19, the California Governor's Office of Emergency Services contacted the Radiologic Health Branch (RHB) to report an incident with a damaged moisture-density gauge at a temporary jobsite. The gauge involved is a CPN, Model MC3, S/N M39505008 containing 10 mCi of Cs-137 and 50 mCi of Am-241. The user backed up his truck into the gauge causing the probe to break off. When the user attempted to retrieve the source it became loose from the rest of the gauge assembly. The area was cordoned off and sandbags were placed on top of the gauge for shielding. The vendor, Instrotek, was located too far away to retrieve the source, but provided the Radiation Safety Officer (RSO) instructions on how to place the source in a shielded container. After the source was placed inside a Type A container the RSO measured 0.2mR/hr at one meter. The damaged gauge has been transported to the vendor for disposal. The RHB will be following up on this investigation. California 5010 Number: 072219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-07-30
54177 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-07-22 | 2019-07-22 12:30 | 2019-07-22 | AGREEMENT STATE REPORT - LOST AND RECOVERED RADIOGRAPHY CAMERA The following is a synopsis of information received verbally and via email from the Texas Department of State Health Services (the Agency): On July 22, 2019, the Agency (Texas Department of State Health Services) received a report from Harris County Hazmat that at approximately 0715 CDT a Harris County Region 3 Constable had found a Spec-150 radiography camera (s/n:1763), containing a 39 curie Ir-192 source, at the intersection of Miller Road 2 and State Highway 90 in Houston. While recovering the radiography camera, the Constable was approached by the radiographer who had lost the camera. Apparently the radiographer had placed the camera on the tailgate of his vehicle and failed to secure it before driving to a gas station. While driving away from the gas station, the radiographer noticed a law enforcement officer holding what appeared to be a radiography camera. The radiographer stopped, checked for his camera, and discovered that it was not in his possession. That is when the radiographer approached the Constable. After verification, the radiography camera was returned to the licensee. An investigation is ongoing. Texas Incident #: 9696 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-07-30
54176 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-07-21 08:26 | 2019-07-21 12:08 | 2019-07-21 | MANUAL REACTOR TRIP DUE NON-ESSENTIAL SERVICE WATER SYSTEM DEGRADED CONDITION "On July 19, 2019, DC Cook Unit 2 started experiencing degraded performance on the Unit 2 Non-Essential Service Water System (NESW) which affected one (1) NESW pump. On July 21, 2019, a second NESW pump on Unit 2 experienced degradation. On July 21, 2019, DC Cook Unit 2 elected to do a rapid downpower over approximately 40 minutes and perform a Manual Reactor Trip from 17 percent [rated thermal power] to repair the condition before any threshold was exceeded. The manual reactor trip was completed at 0826 EDT on July 21, 2019. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), Reactor Protection System (RPS), as an eight (8) hour report. "The DC Cook NRC Resident Inspector has been notified. "Unit 2 is being supplied by offsite power. All control rods fully inserted. Aux Feedwater pumps were started as required and are operating properly. Decay heat is being removed via the Steam Generator Power Operated Relief Valves following breaking Main Condenser Vacuum for expedited cooldown of the Main Turbine. Preliminary evaluation indicates all plant systems functioned normally following the reactor trip. DC Cook Unit 2 remains stable in Mode 3. No radioactive release is in progress as a result of this event." Unit 1 was not affected. | 0 | 0 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-07-21
54175 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-07-19 09:45 | 2019-07-19 13:05 | 2019-07-19 | AUTOMATIC REACTOR TRIP DUE TO MAIN STEAM ISOLATION VALVE FAILING SHUT "At 0945 [EDT] on July 19, 2019, with Unit 2 in Mode 1 and 100 percent power, the reactor automatically tripped due to Loop 2 'B' Main Steam Isolation Valve failing shut. The Auxiliary Feedwater system (AFW) started automatically as a result of the automatic reactor trip. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam lines through the steam dumps and into the condenser. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Due to the valid AFW actuation from the reactor trip, this event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "Unit 1 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified." All control rods fully inserted. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-07-19
54174 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-07-13 | 2019-07-19 10:31 | 2019-07-22 | AGREEMENT STATE REPORT - DENSITY GAUGE SHUTTER FAILED IN OPEN POSITION The following information was received via E-mail: "The shutter on a SVP generator [chlorine dioxide] ClO2 density meter failed in the open position. This failure was identified and verified on Saturday, 7/13/19. Berthold inspected the gauge while they were on site on 7/19/19 and are scheduled to come in on the next C mill outage to replace the shield. Outage is tentatively scheduled for 10/9/19. The gauge shutter normally operates in the open position so the failure poses no safety risk during normal operations. "The SVP generator density meter is Rayonier instrument loop no. 507-081. The source is Cesium-137, 500 mCi, model 2623-100, serial no. ED350A in a LB7440 housing." * * * UPDATE FROM ROGER WILSON TO DONALD NORWOOD AT 1358 EDT ON 7/19/2019 * * * The following information was received via E-mail: In the course of planning for Berthold to come on site to repair the SVP generator density meter shutter, it was discovered that our records on the source were in error. The source is model 2623 Cesium-137, 10 mCi, serial no. EA350A NOT 500 mCi, serial no. ED350. Notified R1DO (Deboer) and NMSS Events Notification E-mail group. * * * UPDATE FROM LESLINES LEVEQUE TO ANDREW WAUGH AT 1405 EDT ON 7/22/2019 * * * The following information was received via E-mail: "The broken shutter at the SVP salt cake density meter was addressed on 7/18/19. Berthold came on site and replaced the shield with a new one, moving the source from the old gauge into the new. The new shield is a model LB 7440-F-CR device, serial no. 37625-13606." Notified R1DO (Gray) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-07-29
54173 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-07-17 | 2019-07-18 19:03 | 2019-07-18 | AGREEMENT STATE REPORT - STOLEN MOISTURE-DENSITY GAUGE The following was received via e-mail: "On 07/17/19, the California Governor's Office of Emergency Services contacted the Radiologic Health Branch (RHB) to report a stolen moisture-density gauge. The gauge involved is a Troxler Model 3450A, S/N 483, containing 9 mCi of Cs-137 and 44 mCi of Am-241. The gauge was stolen out of a gauge technician's truck parked at a Motel 6 parking lot around 2100 PDT in Oakland, CA. The user had immediately called the Oakland Police Department and was advised to call back at a later time. On the morning of 7/18/19, the Oakland Police Department was contacted again and they declined to take a report due to high volume of incidents. The gauge was chained to the bed of the truck and there were guards present at the parking lot. The licensee will be posting a reward for the safe return of the gauge. RHB will be following up on this investigation." California 5010 Number: 071719 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-07-26
54172 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-07-17 | 2019-07-18 13:22 | 2019-07-18 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILURE TO RETRACT The following is an abstract of information received via E-mail: On July 17, 2019, a Capitol Ultrasonics (CU) three-person crew was making exposures on a compressor at a chemical plant at ExxonMobil Refinery, at a temporary jobsite in Baton Rouge, Louisiana. The three-person radiography crew consisted of two radiography instructors and an assistant radiographer. After performing three approximately one minute and 25 second exposures and upon completing the fourth exposure and cranking in the source, the radiography instructor noticed, after rocking the crank-out handle back and forth, that the exposure device auto-lock was not engaging. Before reaching the exposure device, the instructor noticed higher than expected survey readings. Several more attempts were made to crank in the source without success. The instructor at once contacted his Radiation Safety Officer (RSO), as well as the ExxonMobil Safety Superintendent. The crew then immediately extended their restricted area boundary to the 2 mR/hr line. Six to seven radiography technicians of the licensee maintained visual surveillance of the boundary and awaited arrival of their RSO. The exposure device was a QSA Global Model 741OP, serial number, B107, containing 15.1 Ci of Co-60, source Model number, A424-18 and source serial number, 60487B. The lead technician of the crew leading the incident response prior to the arrival of the RSO, received 30 mR on his direct-reading dosimeter (DRD). The RSO received approximately 17 mR on his DRD by the time that the source was finally placed back in the exposure device in the shielded position. An environmental scientist from the Louisiana Department of Environmental Quality made a site visit to the temporary jobsite of the incident and performed preliminary investigation to include observing the successful retrieval of the source on July 17, 2019, by QSA Global. QSA Radiation Technicians received from 40 to 78.3 mR whole body exposure as a result of performing the source retrieval. Louisiana Event Report ID No.: LA 190010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-07-26
54171 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2019-07-17 | 2019-07-17 15:35 | 2019-07-17 | AGREEMENT STATE REPORT - TWO RADIOPHARMACEUTICAL PACKAGES HAD HIGH SURFACE CONTAMINATION LEVELS WHEN DELIVERED The following information was received from the state of Maryland via email: "On July 10, 2019, a health physics consultant contacted the Maryland Department of the Environment Radiological Health Program (MDE/RHP) concerning a discovery during a routine audit conducted on July 10, 2019 at a licensed medical facility. "A review of incoming Department of Transportation wipe/survey listing reports at the licensed facility [St. Agnes Hospital in Baltimore, MD] indicated that two packages received on June 12, 2019 from the radiopharmacy had high wipe test values recorded at 400,000 dpm per 100 cm2. These values were documented for surface and contents of the packages. Both packages were labeled as White I and had no abnormal outer package surface exposure rate readings. The computer record contained a note stating that, 'dpm verified and Cardinal [Health] notified. Case stored for decay.' "The technologists did not notify the Radiation Safety Officer or MDE/RHP. The cases were opened, the doses unpacked, and used. The computer record indicated good condition for each box. One box contained one syringe of Tc-99m Ceretec at 17.25 mCi. The other box contained one vial of Tc-99m sodium pertechnetate at 104.22 mCi, one syringe of Tc-99m macro aggregated albumin at 10.61 mCi, and one syringe Tc-99m Sestamibi at 30.41 mCi. "A reactive inspection is planned [by the state of Maryland]." Cardinal Health was the radiopharmaceutical provider. The delivery vehicle and the driver were both surveyed on June 12, 2019, with negative results. No other contaminations or any overexposures were identified when the hospital performed surveys of the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2019-07-25
54170 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-07-12 | 2019-07-17 15:11 | 2019-07-17 | AGREEMENT STATE REPORT - LOST THEN FOUND SHIPMENT OF RADIOACTIVE IODINE-125 The following information was received from the Commonwealth of Massachusetts via email: "Two shipments of licensed material in the form of Iodine-125 saline, one with an activity of 1.75 Curies and the other, 1.25 Curies, were discovered not to be delivered by [a common carrier] to the licensee's authorized use site at 331 Treble Cove Road, Billerica, MA, on Friday, July 12, 2019. PerkinElmer leases authorized use space from another Massachusetts licensee, Lantheus Medical Imaging, Inc., at the same street address. PerkinElmer subsequently contacted Lantheus and [the common carrier] on 7/12/19 at approximately 1416 EDT to report the missing packages. "On Monday, July 15, [the package] containing 1.25 curies of I-125 was delivered by [the common carrier] to the PerkinElmer shipping department. [The licensee] subsequently reported to [the common carrier] that one of the packages was delivered; however, the second package containing 1.75 curies of I-125 was not. On Tuesday, July 16, [the common carrier] contacted PerkinElmer to report that both packages were delivered and that the case was closed. "On Wednesday, July 17, at 1054 EDT, [the common carrier] delivered the second package to the PerkinElmer shipping department and stated that it was just picked up from Lantheus a short time before. It had apparently been in Lantheus's possession since Monday, July 15. "An investigation of the incident is underway." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-07-25
54169 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2019-07-16 | 2019-07-17 10:24 | 2019-07-17 | AGREEMENT STATE REPORT - MEDICAL EVENT "Vanderbilt University Medical Center had a misadministration on 7/16/19. A patient was supposed to receive 14 mCi of I-131 NaI, but the technologist administered 33 mCi of I-131 NaI. The technologist will send a written report within the 15 day requirement." Item Number: TN-19-098 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2019-07-25
54168 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-07-16 14:45 | 2019-07-16 17:34 | 2019-07-16 | OFFSITE NOTIFICATION DUE TO SEWAGE SPILL ON SITE "At 1445 EDT, on 7/16/2019, during routine maintenance activities on the sanitary sewage system, a leak from an overflow line to a parking lot was discovered. The total amount leaked is estimated to be 20 gallons. Approximately 2 gallons reached gravel in an excavated section of the parking lot. A local sanitary contractor is currently responding to the site to clean the affected areas. The cause of the leak is under investigation. "As a result of some of the sewage reaching gravel, environmental reports are being made to the Michigan Department of Environmental Quality (MDEQ), the Monroe County Health Department, and the local news media. Since these reports are in the process of being made, this is considered a News Release or Notification to Other Government Agencies, therefore this event is reportable under 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-07-16
54167 | 0 | GE - HITACHI |  |  |  | 100 KW NTR (TANK) | 2019-07-16 13:26 | 2019-07-16 16:37 | 2019-07-16 | NOTIFICATION OF UNUSUAL EVENT DUE TO EARTHQUAKE FELT ON SITE At 1326 PDT, the licensee declared a notification of unusual event under emergency action level HU.1 for an earthquake felt on site. The reactor was not operating at the time of the event. There was no equipment damage or personnel injuries due to this event. The earthquake registered a 4.4 on the Richter scale with the epicenter approximately 9 miles from the facility. The licensee notified the California Office of Emergency Services. At 1357 PDT, the licensee terminated the notification of unusual event. The NRC remained in the normal mode of operations. Notified DHS SWO, FEMA Operations Center, FEMA NWC (email), DHS NICC and DHS Nuclear SSA (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 0 | CA | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2019-07-16
54166 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-07-16 11:33 | 2019-07-16 14:42 | 2019-07-16 | CONCURRENT NOTIFICATION DUE TO SPRINKLER MAINTENANCE "At 1133 EDT on July 16, 2019, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire suppression system for the Fuel Manufacturing Operation Shop Support Areas was taken offline for planned maintenance to modify sprinkler piping. Compensatory measures were enacted. The system was taken offline at approximately 0800 EDT and was returned to service at approximately 1400. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will be notifying the North Carolina Emergency Management Agency and NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-07-24
54165 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-07-16 | 2019-07-16 13:34 | 2019-11-26 | AGREEMENT STATE REPORT - GAUGE SHUTTER MALFUNCTIONED The following information was obtained from the state of Georgia via email: "The shutter on a saltcake density meter was identified as needing attention on the last inventory and Berthold was scheduled to come on the next outage to repair or replace as needed. The outage is scheduled for 7/31/19. "Today, [the licensee] identified that a saltcake pump near the gauge needs to be replaced and the gauge is listed on the pump's lockout sheet. When IM [instrument maintenance] attempted to lock out the meter as part of the established lock out, the shutter handle broke meaning the gauge cannot be locked out. (Lock out requires all energy sources affecting the pump to be locked out. The gauge is in the line ahead of the pump and about 6 feet away so does not really affect the pump.) Radiation survey at the pump showed 65 microRem/hr radiation. (500 microRem/hr at gauge surface and 134 microRem/hr at one foot) "Maintenance work at the pump will continue with a lock out variance to cite not being able to close the shutter and a proximity radiation work permit used. Berthold is still scheduled to come in 7/31/19 for gauge shutter repair. "Source is Cesium-137, 20 mCi, model P-2623-100 in LB7440 holder, serial no. 2104-6-90." * * * UPDATE FROM ROGER WILSON TO KARL DIEDERICH ON 11/26/19 AT 1:12 PM * * * The radioactive material was transferred to Berthold for disposal on 11/25/19. Notified R1DO (Henrion) and NMSS_EVENTS_NOTIFICATION (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-07-24
54164 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-07-15 | 2019-07-16 12:48 | 2019-07-16 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE DUE TO TRUCK FIRE The following report was received from the Ohio Bureau of Environmental Health and Radiation Protection via email: "The licensee [Professional Service Industries, Inc.] experienced a vehicle fire today (7/15/19) involving a Troxler 3430P gauge, S/N 70185, containing a double-encapsulated sealed source of Cs-137 (8 mCi [0.30 GBq]) plus a double-encapsulated sealed source of Am-241 (40 mCi [1.48 GBq]). "The vehicle driver pulled over on the shoulder of the interstate when he noticed smoke [coming] from the bed of the truck. The licensee believes that the cause of the fire may have been as a result of vandalism that ruptured the fuel tank. The licensee reported that such activities have occurred in the past. No one was injured. "After the fire was extinguished, the device was surveyed using a calibrated NDS Model ND-500A survey meter. The measured radiation levels of the device were 20 mR/hr at the surface, and 0.9 mR/hr at 1 meter, without the transport case. The device has been leak tested pending results and Troxler has been contacted for disposal." Item Number: OH190011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-07-24
54163 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-07-15 13:35 | 2019-07-15 16:30 | 2019-07-15 | OFFSITE NOTIIFICATION DUE TO OIL LEAK "At 1335 EDT on 7/15/2019, during dredging activities in Fermi 2's General Service Water (GSW) intake canal, a hydraulic line on the dredging machine became disconnected and approximately one quart of hydraulic oil spilled into Lake Erie. The oil leak to navigable waters has been stopped. The oil was contained within a boom, cleanup activities commenced immediately, and cleanup was completed at 1500 EDT. The cause of the oil leak is under investigation. "Environmental spill reports were made to local, state, and federal government agencies. This is considered a news release or notification to other government agencies, therefore this event is reportable under 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." The State agencies notified were Michigan Department of Environmental Protection and the Michigan Pollution Emergency Alerting System. The licensee also notified the National Response Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-07-15
54162 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-07-12 16:40 | 2019-07-12 22:50 | 2019-07-12 | INVALID AUTO ISOLATION SIGNAL OF HIGH PRESSURE COOLANT INJECTION "At 1640 CDT on 7/12/19, Unit 1 High Pressure Coolant Injection (HPCI) received an invalid auto isolation signal which closed the HPCI steam supply valves rendering HPCI inoperable. This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D), as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The isolation occurred while performing a calibration and functional check of a level switch for the Unit 1 Core Spray system. Continuity was checked across the incorrect set of contacts which completed the circuit in logic bus 'A' for the auto isolation signal in the HPCI system. There was no impact to the safety of the public or plant personnel during the time HPCI system was isolated. HPCI was returned to operable at 2110 CDT on 7/12/19. "CR 1532094 documents this condition in the Corrective Action Program." The licensee has notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-07-12
54161 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2019-07-12 01:52 | 2019-07-12 16:13 | 2019-07-12 | WASTE DRUM DAMAGED DUE TO OVER PRESSURIZATION "On July 12, 2019, at approximately 0152 EDT operations personnel in the Uranium Recycle and Recovery area of the plant reported an incident. Production packaged wet recoverable material on July 12 (3rd shift) into a closed drum at the designated drum loading station, performed the required assay measurement and placed the drum into storage. Shortly afterward, the drum pressurized forcing the lid off and some contents to disperse into the immediate vicinity. The drum contents were smoldering, smoke was observed and the smoke detector activated. Dry paper in the drum created a small fire, which was promptly extinguished without use of a water hose or a fire extinguisher. A small portion of the drums content was impacted. The drum was then separated from other stored material. There were no personnel injuries. Health Physics monitored the area with no airborne results approaching radiological limits and no personnel were affected. "The drum contained production-related contaminated wet recoverable material (e.g., mop heads, filters, and rags) and laboratory waste. The assay results showed a Uranium 235 content of 71.45 Grams. This quantity of material meets the reporting threshold noted above. "Immediate Corrective Actions. "Loading operations of wet recoverable material have been suspending pending further evaluation. Operations checked the other drums in the area with heat monitoring equipment and no additional heat generation issues were identified. This incident has been entered into the facility's corrective action program. "This incident had no impact on the health and safety of the employees, the public or the environment." The licensee notified the South Carolina Department of Health and Environmental Control and will be notifying the NRC Region II office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2019-07-12
54160 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-07-10 | 2019-07-12 14:35 | 2019-07-12 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED AT JOB SITE The following report was received from the Pennsylvania Bureau of Radiation Protection (PA DEP) via facsimile: "On July 10, 2019, a Troxler gauge was hit by a roller while on a job site at the Philadelphia Airport. The area was secured, and the PA DEP responded to the site. The gauge was not found to be leaking and was secured for shipment back to the operators' office in New Jersey. Preliminary investigation indicates the gauge operator is licensed in New Jersey, but not licensed to operate within Pennsylvania. There was no exposure to workers or the public." Gauge is a Troxler model 4640-B, Serial number: 72103 containing 8 milliCuries of Cs-137. Event Report ID No.: PA190016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-07-22
54159 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-07-11 15:30 | 2019-07-12 10:03 | 2019-07-12 | AGREEMENT STATE REPORT - OVEREXPOSURE OF RADIOGRAPHER The following report was received via email from the State of Illinois: "The Agency [Bureau of Radiation Safety Illinois Emergency Management Agency] was notified after hours on 7/11/19 by Silver Cross Hospital in New Lenox, IL that a patient had self-reported to the emergency room for a potential exposure to an 88 Ci Ir-192 radiography source. Reportedly, the exposure happened earlier in the afternoon (approximately 15:30 CDT). The assistant radiographer stated he had been working in the subject area for approximately 2 minutes when a coworker arrived with radiation detection equipment and told him that he needed to self-report to the nearest ER to determine if he had received an overexposure (15:30 CDT). The assistant radiographer arrived at the hospital around 17:00 CDT. Notification to the Agency was only received from the hospital. "Agency staff contacted the local RSO [Radiation Safety Officer], at approximately 19:00 CDT on 7/11/19 and confirmed that the assistant radiographer did in fact walk out to exchange film between shots thinking the source was retracted when in fact it was not. Shortly thereafter, the Corporate RSO, called and had additional information. The assistant radiographer worked for 2 minutes at 1 foot away from an 88 Ci Ir-192 source. This equates to about a 15 rem whole body dose. He reportedly did not grab anything with his hands that would generate blistering or erythema, but everyone will be monitoring over the next week. "The Corporate RSO was still investigating and trying to determine the exact location of the event. The assistant radiographer is at home after his hospital visit with no ill effects, and the camera is secure in Mokena, IL. Agency staff called the hospital and made sure that they were analyzing the blood for white cell count abnormalities specifically drops in lymphocyte counts. They were not sure what to check for or how often so they were put in contact with REACTS Oak Ridge for analysis SOP at approximately 20:30 CDT on 7/11/19. The NRC region 3 liaison was notified shortly thereafter. "The Corporate RSO will submit a final report and TLD results by 7/12/19. Agency staff are in route to the facility to perform a reactionary inspection and perform an onsite reenactment. This report will be updated as additional information becomes available. This investigation is ongoing." Illinois report number: IL190022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-07-22
54158 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-07-11 | 2019-07-11 15:02 | 2019-07-11 | AGREEMENT STATE - THREE FIXED GAUGES UNACCOUNTED FOR DURING TRANSFER The following report was received from the Illinois Emergency Management Agency (Agency) via email: "During Agency efforts to pursue an annual self-inspection report from a general licensee (Weber Packaging Solutions, aka Weber Marking Systems), it was discovered (3) NDC model 103 fixed gauges, containing 150 mCi of Am-241 each could not be accounted for. The company provided a sales order, dated 3/9/17, showing the sale of the gauges (incorporated into machinery) to Margot Machinery in Scotia, New York. On July 11, 2019, the Agency determined through communications with State of New York program staff and Margot Machinery that the transfer of the devices out of Illinois was not to a licensed broker or another general licensee. Margot Machinery was unaware the machinery contained any radioactive sources. Weber indicated on the sale bill (NDC Model 5400 TC gauge) but did not verify the transfer was to another general licensee or someone specifically licensed and authorized to receive the sources. Margot Machinery states they were unaware sources were present and had never taken possession of the machinery. Margot Machinery had contracted a broker (Buckeye Business in Ohio) to rig and remove the equipment. Agency efforts are ongoing to contact Buckeye Business and determine the fate of the machinery and sources. Correspondence is ongoing with State of Ohio officials. This matter remains open and the report will be updated as details become available." Illinois Item Number: IL190021 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-07-19
54157 | 0 | GE - HITACHI |  |  |  | 100 KW NTR (TANK) | 2019-07-10 14:59 | 2019-07-10 18:28 | 2019-07-11 | NOTIFICATION OF UNUSUAL EVENT On July 10, 2019, at 1459 PDT, GE Hitachi [test reactor in Sunol, California] declared an Unusual Event. Two individuals jumped a boundary fence. The individuals exited the area when approached by security. The licensee notified local law enforcement. There was no offsite release. The licensee terminated the Unusual Event at 1553 PDT on July 10, 2019. The licensee notified California Environmental Emergency Services and Alameda County law enforcement. Notified DHS SWO, DHS NICC, FEMA Operations Center, FEMA NWC (email), and NuclearSSA (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 0 | CA | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2019-07-10
54156 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2019-07-08 | 2019-07-10 15:08 | 2019-07-10 | AGREEMENT STATE REPORT - INOPERABLE FIXED GAUGE SHUTTER The following report was received from the State of Tennessee via email: "On July 8, 2019, technicians at Eastman Chemical were performing procedures that involved securing radioactive sources on the outside of a vessel. One source had rust and corrosion around the shutter mechanism. After 4 hours with lubricant on the mechanism, the shutter was still inoperable. Eastman Chemical contacted the VEGA technician and scheduled a repair appointment for 7/12/19. "Manufacturer: VEGA Model #: SHF1B Serial #: (Will be included in follow-up report) Source Serial #: 7386 CP Isotope: Cs-137 (20 mCi) "A follow-up report will be submitted within 30 days." TN Tracking Number: TN-19-090 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2019-07-18
54155 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-06-27 15:30 | 2019-07-09 14:19 | 2019-07-09 | AGREEMENT STATE - TWO DEVICES CONTAINING SEALED RADIOACTIVE SOURCES FOUND The following was received from the Commonwealth of Massachusetts via email: "This shipment containing scrap metal with radioactive material was first discovered at Sims Metal Management in North Haven, CT on June 27, 2019. As a result, SP 10656 Number CT-MA-19-01 was issued by members of the Connecticut Department of Energy and Environmental Protection and the shipment was sent back to Joseph Freedman Company in Springfield, MA. The material was received at the licensee and the radioactive items were removed, isolated, and stored in a locked 55 gallon drum on site in a secure area for further analysis. "The site hired a contract health physics service to aid in the identification of the material and to perform radiation surveys. That occurred on 7/8/19. Two devices were discovered. The contractor provided survey information and attempted isotope identification for the two devices. One source was identified as Ra-226 and the other could not be clearly identified. Since the identification of one of the two sources was in question, the Massachusetts Radiation Control Program Director visited the site on 7/9/19 carrying multiple survey instruments for additional measurements and for visual inspection of the two units. "One of the devices was identified as a Pyralarm Demonstrator Unit manufactured by Pyrotronics, Inc. The isotope was identified as Ra-226 with an approximate activity of 56 microCuries. The other device appeared to be an industrial nuclear gauge, but there were no legible markings on it other than a Radioactive Material sticker. The isotope identified was Am-241 with an approximate activity of 15 milliCuries as determined on 7/9/19. The spectra for this source contained peak energy channels in addition to the Am-241 peak that could not be readily identified given the proposed use of the device. It is possible other isotopes are there and we will continue to evaluate with the contractor until appropriate disposal by a licensed waste broker. "Dose rates provided for the Pyralarm smoke detector containing Ra-226 were 37 mR/hr at one centimeter, 0.275 mR/hr at 30 centimeters and 0.42 mR/hr at one meter inclusive of approximately 0.5 cm of lead shielding. Dose rates for the unidentified gauge containing Am-241 were measured as 85 mR/hr at 2.5 centimeters and 2.8 mR/hr at 30 centimeters. The highest dose rate on contact with the storage drum containing the two devices was 0.550 mR/hr. Wipe surveys were taken on all surfaces by the contractor and there was no radioactive contamination found. "These devices were discarded by unknown persons and are pending disposal by a licensed waste broker." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-07-17
54153 | 0 | NC DIV OF HEALTH SERVICE REGULATION |  |  |  |  | 2019-07-08 12:00 | 2019-07-09 09:06 | 2019-07-09 | AGREEMENT STATE REPORT - FOUND PORTABLE GAUGE The following report was received from the State of North Carolina: "On 7/8/19 around 1200 EDT, the North Carolina Radioactive Materials Branch (RMB) received a call from NC Emergency Management and Durham area police that a yellow package was found on the side of the road at a carwash in Durham, NC. Emergency management and police recognized the package as a possible portable gauge contained in a standard transport case. Readings were immediately taken and the package cordoned off to prevent any public exposures. RMB dispatched an inspector and was on-site within an hour of notification. It was found that the licensee who possessed the portable gauge had removed the gauge in its transport box from his vehicle earlier that morning to wash the vehicle. After finishing, the gauge fell off the vehicle when the licensee departed the car wash. Once the licensee noticed the gauge was missing, they retraced their steps back to the car wash to attempt to reclaim the gauge and were met by local police and emergency management. The gauge was left unattended for approximately 4-5 hours. The licensee is now in possession of the gauge. The RMB inspector discovered multiple violations as a result of this incident. "Gauge: Humboldt Model: HS-5001 EZ S/N: 1599 Sources: Cs-137, 10 mCi; Am:Be, 40 mCi" NC Tracking Number: 190019 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-07-17
54152 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2019-07-08 09:35 | 2019-07-08 18:40 | 2019-07-08 | FITNESS FOR DUTY - NON-LICENSED CONTRACT SUPERVISOR FAILED RANDOM SCREENING A non-licensed contract supervisor had a confirmed positive for a controlled substance during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2019-07-08
54151 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-07-05 | 2019-07-08 13:09 | 2019-07-08 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The follow was received via fax: "On July 8, 2019, the Department [Pennsylvania Department, Bureau of Radiation Protection] became aware of an under-dose event involving yttrium-90 (Y-90) SIR-Spheres. It is reportable as per 10 CFR 35.3045(a)(1)(i). "On July 5, 2019, a patient underwent a Y-90 SIR-Sphere treatment. The total dosage of 9.58 mCi was split into two equal dosages of 4.79 mCi to be administered to segments 5 and 8 of the liver. The first vial, segment 5, was successfully administered but only 75.7 percent or 3.6 mCi of the second vial was administered to segment 8. The referring physician and the patient were verbally informed. No harm is expected to the patient. "The Department will perform a reactive inspection." Event Report ID No.: PA190015 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-07-16
54150 | 0 | VIRGINIA DEPARTMENT OF HEALTH |  |  |  |  | 2019-07-05 | 2019-07-06 11:01 | 2019-07-08 | AGREEMENT STATE REPORT - LOST AND RECOVERED NUCLEAR GAUGE On July 5, 2019, the licensee discovered that a nuclear gauge was missing from their inventory. The gauge contained a Cs-137 source of approximately 10 mCi and an Am-241 source of approximately 25 mCi. The licensee notified the Virginia Department of Health and the Virginia Emergency Operations Center. On July 6, 2019, the gauge was found in a parking lot of a funeral home in Hampton, VA. The Hampton Police were notified. Following their procedures, they notified the FBI. The gauge was undamaged. The Radiation Safety Officer for the licensee is en route to retrieve the gauge. The Virginia Department of Health will supply additional details when they become known. * * * UPDATE ON 7/8/2019 AT 1156 EDT FROM MICHAEL FULLER TO JEFFREY WHITED * * * The following information was received via e-mail: "On Friday, July 5, 2019 at approximately 1600 EDT, the Virginia Office of Radiological Health (VORH) Duty Officer was notified by the Virginia Emergency Operations Center Duty Officer that a Virginia licensee, ECS-Mid Atlantic, located in Richmond, VA (Virginia radioactive materials license # 760-114-4) had reported a missing portable nuclear gauge. The gauge particulars are as follows: Manufacturer: CPN Model: MC1DR-P Serial Number: MD60303074 Source: Cs-137 containing 370 MBq (10 mCi); serial number: 2149GQ Source: Am-241 containing 1.85 GBQ (50 mCi); serial number: 5396NK "On Saturday, July 6, 2019 at approximately 1030 EDT, the VORH Duty Officer was informed that the missing gauge had been found in the parking lot of a funeral home in Hampton, VA and that local law enforcement, fire department, and Hazmat personnel were on the scene. Also, in accordance with their procedures, the local police department informed the FBI. The local Hazmat officer performed a visual and radiological survey of the transportation package (labeled Radioactive - Yellow II) and observed that everything appeared to be intact and the radiation readings indicted that the source was in the shielded position (approximately 1.6 mR/hr on contact with the transportation package). Once this information was obtained, the Hazmat officer advised the FBI of the situation (through local law enforcement) and the FBI terminated their involvement. The licensee's identity was determined from the visual inspection and was contacted immediately. The licensee's [Radiation Safety Officer] RSO immediately traveled to the scene, and at 1219 EDT informed the VORH Duty Officer that he (the RSO) had possession of the gauge and was en route back to Richmond, VA. "The licensee is conducting an investigation into the incident and believes that an employee failed to check out the gauge properly and return it to the storage location in Richmond on Wednesday, July 3, 2019 as required by company procedure, and thought that they could return it after the holiday without being detected. When the gauge was observed to be missing on Friday, July 5, 2019 by the Assistant RSO, she texted all technicians and asked who might have failed to return it. The RSO believes that the technician that failed to properly check out the gauge and check it back in panicked and abandoned it at the funeral home on Friday or Saturday. Once the investigation is completed, the licensee will provide the Virginia Office of Radiological Health with their findings. Future updates, based upon that investigation will be made." Notified R1DO (Dimitriadis) and NMSS Events Notification and ILTAB via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2019-07-15
54149 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-07-01 11:00 | 2019-07-05 09:18 | 2019-07-05 | NON-POWER REACTOR REPORT - TECHNICAL SPECIFICATION DEVIATION The following was received via e-mail: "On July 1, 2019, sometime between 1100 and 1200 CDT with the reactor shut down and during performance of electrical preventative maintenance, the University of Missouri-Columbia Research Reactor (MURR) deviated from Technical Specification (TS) 3.4 because reactor containment integrity did not exist for approximately ten (10) minutes while the reactor was not secured, as defined by TS 1.26. "During this event time, two (2) shim control rod drive mechanisms were not installed because scheduled work was in progress on these drive mechanisms. Therefore, the reactor was not secured per TS definition 1.26, but the reactor was shut down per TS definition 1.27. Also during this time, and unknown to the Control Room operators, an Electronics Technician opened the two (2) electrical motor breakers to the reactor containment system's two (2) automatically-closing doors one at a time for approximately 5 minutes each. "Though this event happened on July 1, no NRC-licensed operator knew that the automatically-closing door motor breakers had been opened on July 1 until mid-day on July 3. Once the abnormal occurrence was realized, the Reactor Facility Director was briefed on the situation on the afternoon of July 3, and he gave permission to continue reactor operation in accordance with TS 6.6.c.(4). "This email is a required notification per TS 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by TS 1.1.b, has occurred. MURR was not in compliance with all of the Limiting Conditions for Operations as established in TS Section 3.0. "A detailed event report will follow within 14 days as required by TS 6.6.c.(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | DEVIATION FROM T SPEC | [9 empty] | NON EMERGENCY | 0 | MO | NPR |  | 50.72(b)(1) |  |  |  | 0 | 2019-07-05
54148 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2019-07-04 08:44 | 2019-07-04 12:36 | 2019-07-04 | FITNESS FOR DUTY REPORT - LICENSED SUPERVISOR FAILED A RANDOM SCREENING A licensed supervisor had a confirmed positive for alcohol on a random fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Senior Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2019-07-04
54147 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2019-05-09 12:05 | 2019-07-03 18:32 | 2019-07-03 | 60-DAY TELEPHONIC NOTIFICATION OF INVALID ENGINEERED SAFETY FEATURE ACTUATION SIGNAL "This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to provide information pertaining to an invalid Engineered Safety Feature actuation signal. "On May 9, 2019, at Arkansas Nuclear One (ANO) Unit 1, while performing an Emergency Feedwater Initiation and Control (EFIC) Channel B monthly test, a test pushbutton was mispositioned, resulting in an inadvertent initiation of the Emergency Feedwater (EFW) System. "In accordance with the Engineered Safeguards Actuation System (ESAS) Trip Test portion of the surveillance, the first technician placed EFIC Train B in the tripped condition. The second technician then went to the front of the control room to verify Remote Switch Matrix (RSM) indications. The first technician recalls thinking he was given the order to reset Train B EFW Bus 1 Trip. Therefore, the first technician performed the step using three-part communication, but there is uncertainty about what was said. "Due to the amount of time the second technician spent in front of the control room, the first technician assumed Operations reset the RSM to complete the Train B reset. "The second technician returned to the ESAS cabinet and directed the first technician to perform the reset of Train B EFW Bus 1 Trip. The first technician, expecting his next action to be the trip of Train B EFW Bus 2, placed Bus 2 in the tripped condition. This put both buses of Train B EFW in trip and caused the actuation of P-7A EFW Pump. "This inadvertent actuation was caused by human error and was not a valid signal resulting from parameter inputs. The 1992 Statements of Consideration define an invalid signal to include human error. Therefore, this actuation is considered invalid. "This event was entered into ANO's corrective action program for resolution. This event did not result in any adverse impact to the health and safety of the public. The plant responded as expected. "In accordance with 10 CFR 50.73(a)(i) a telephone notification is being made in lieu of submitting a written Licensee Event Report. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-07-03
54146 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2019-07-01 | 2019-07-03 15:58 | 2019-07-03 | AGREEMENT STATE REPORT - LEAKING SOURCE The following was received from the state of Wisconsin via email: "On July 3, 2019, the Department [Wisconsin Radiation Protection Section] received a letter sent and dated July 1, 2019, from GE Healthcare of a source that was discovered to be broken and leaking following it being dropped at the licensee's facility. "The source (Sanders Medical Products, Germanium-68 Model PET-273/10 sealed source) was being transported in an open-topped lead shield on a cart within the licensee's restricted facility. While moving the cart, an employee lost their grip and the shield fell to the floor. The employee identified that a portion of the source had broken off. "Using remote handling tongs, the broken portion was returned back into the shield. Surveys were immediately performed, and no contamination was identified on the floor or the employee's hands. "Follow-up wipe tests were performed on the floor and the source. The source had removable contamination of 220 Bq. The source has been withdrawn from use and secured at the licensee's facility pending disposal. "The licensee will be performing a review of the incident and their response procedures. A follow-up inspection will be performed by the Department." Wisconsin Event Report ID No.: WI 190007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2019-07-11
54145 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-07-03 10:26 | 2019-07-03 15:24 | 2019-07-03 | OFFSITE NOTIFICATION DUE TO RADIO TRANSMITTER OUT OF SERVICE "At 1026 CDT on July 3, 2019, the National Weather Service notified the South Texas Project (STP) that the Bay City NOAA radio transmitter was out of service. This affects the tone alert radios used to notify the public in the event of an emergency condition. "This condition impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) population for the STP Electric Generating Station. The loss of the alert radio system meets the reporting criterion for 10 CFR 50.72(b)(3)(xiii). "The Matagorda County alert sirens, which are also part of the Public Prompt Notification System, remain operable. "Compensatory measures have been verified to be available should the Prompt Notification System be needed. These measures consist of a reverse 911 system available from Matagorda County as well as local law enforcement personnel who would perform route alerting for the affected areas of the EPZ. "The event has been entered into the Corrective Action Program and the NRC Resident Inspector has been notified. "A return to service time for the radio transmitter is not currently available. "Matagorda County was also notified by the National Weather Service and STP. This meets the reporting requirement for notification of an offsite agency, 10 CFR 50.72(b)(2)(xi)." * * * UPDATE FROM ROBERT TATRO TO HOWIE CROUCH @ 1615 EDT ON 7/3/19 * * * At 1321 CDT, the National Weather Service communication tower was returned to service. South Texas Project verified that the automatic notification radios have been returned to service. The licensee has notified the NRC Resident Inspector. Notified R4DO (Haire). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2019-07-03
54144 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2019-05-09 20:00 | 2019-07-03 12:42 | 2019-07-03 | 60 DAY OPTIONAL NOTIFICATION DUE TO ACTUATION OF AN EMERGENCY DIESEL GENERATOR "This 60-day optional telephone notification is being made in lieu of an LER submittal, as allowed by 10 CFR 50.73(a)(1). This notification is made pursuant to the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of one of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). "At approximately 2000 EDT on May 9, 2019, an invalid actuation of emergency diesel generator (EDG) 1 occurred. At the time, EDG 1 was removed from service for planned maintenance. The invalid actuation occurred when the starting air clearance was being lifted while simultaneously performing a Post Maintenance Test (PMT) where an external DC power source was applied to a relay that provided continuity directly to the starting air solenoids. As a result, the air start solenoids were energized causing EDG 1 to start. "EDG 1 started and functioned successfully. The actuation was complete; EDG 1 successfully started and ran unloaded. The actuation was not initiated in response to actual plant conditions, it was not an intentional manual initiation, and there were no parameters satisfying the requirements for initiation of the system. Therefore, this event has been determined to be an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-07-03
54143 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-07-01 | 2019-07-03 11:48 | 2019-07-03 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following was received via email: "On 7/2/2019, the Ohio Department of Health received a phone call from Nationwide Children's Hospital reporting a medical event. The licensee was treating acute myeloid leukemia (AML) with I-131 Iomab using a delivery system that is currently under research and development. The licensee stated the delivery system does not allow the dose vial to be seen and requires the manufacturer to set the infusion time. After the infusion, the technicians discovered the delivery system did not deliver the entire dose to the patient, resulting in an underdose of 42 percent. "The patient and referring physician have been notified. "An investigation of the event is pending." Ohio Item Number: OH190010 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-07-11
54142 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2019-07-03 09:15 | 2019-07-03 10:29 | 2019-07-03 | OFFSITE NOTIFICATION DUE TO FIRE SPRINKLER MAINTENANCE "At 0915 EST on July 3, 2019, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire suppression system for the Fuel Manufacturing Operation Shop Support Areas was taken offline for planned maintenance to modify sprinkler piping. Compensatory measures were enacted. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will be notifying the state of North Carolina and the NRC Regional Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2019-07-11
54141 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-07-02 13:30 | 2019-07-02 18:17 | 2019-07-03 | AGREEMENT STATE REPORT - LOST PORTABLE GAUGE This is a summary of information received from the state of Nebraska via phone call: On July 2, 2019, at approximately 1330 CDT, the licensee, Mid-State Engineering and Testing, lost a CPN-International MC Series Protaprobe gauge with 10 mCi Cs-137 and 50 mCi Am/Be-241 sources. This gauge is believed to be lost somewhere between Aurora and Columbus, Nebraska on the route that includes highways 14 and 30. The truck's tail gate was not closed causing the gauge to fall out of the truck. The licensee has attempted to locate the gauge but so far has been unsuccessful. The Nebraska State Patrol has been notified along with the Platte County Sheriff department. This was reported to the State of Nebraska Health and Human Services Agency at 1645 CDT. The State will be issuing a follow up written report later. * * * UPDATE ON 7/3/2019 AT 1758 EDT FROM JULIA SCHMITT TO ANDREW WAUGH * * * This is a summary of information received from the state of Nebraska via phone: On July 3, 2019, the gauge was found by a member of the public and retrieved by the licensee. The gauge does not appear to be damaged. Notified R4DO (Haire), NMSS Events (email), and ILTAB (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-07-10
54140 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-07-01 | 2019-07-02 14:50 | 2019-07-02 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the state of Illinois via email: "The Agency [Illinois Bureau of Radiation Safety] was notified at approximately 1530 CDT on 7/1/19, that a medical event had occurred at Alexian Brothers Medical Center, in Elk Grove Village. The circumstances are near identical to those in an event reported by the licensee in February of this year (EN53859). An attempted intravascular brachytherapy procedure utilizing a Novoste BetaCath 3.5F System was aborted when the source train could not successfully reach the intended treatment site after three attempts. The source train was retracted without complication and there were no indications of kinks in the delivery catheter. Aborting the procedure resulted in an underdose exceeding 20 percent of the prescribed dose (prescribed dose was 18.4 Gy of Y-90 and delivered dose was 0.0 Gy). The three attempts also resulted in an exposure exceeding 50 rem to tissue other than the treatment site (treatment site was in the circumflex artery). The source train stopped each of three times 10mm proximal to the treatment site in the junction between the left coronary artery and the circumflex artery. The inadvertently exposed region received approximately 0.98 Gy or a dose equivalent of approximately 100 rem. "A reactionary inspection was conducted by Agency staff on the morning of July 2, 2019. A written report was received by the licensee that same day in which tortuous patient anatomy was identified as the root cause. Agency inspectors will meet with the authorized user on the afternoon of July 3, 2019, to discuss each step of the intravascular brachytherapy procedure in an effort to further isolate the root cause. No adverse medical impact is expected to the patient as a result of this event, per the authorized user. Patient has been notified and referring physician was present. This report will be updated as additional information becomes available." Illinois Item Number: IL190016 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-07-10
54139 | 0 | TRI STATE MATERIALS TESTING LAB |  |  |  |  | 2019-06-30 01:00 | 2019-07-01 05:55 | 2019-07-09 | STOLEN TROXLER NUCLEAR DENSITY GAUGE At approximately 1400 EDT, on 6/30/19, a company technician discovered that his personal vehicle was stolen from his residence driveway in Tolland, CT. The vehicle contained a Troxler density gauge locked in the trunk of the vehicle. The technician contacted the Connecticut State Police and reported the stolen vehicle and the stolen density gauge. The state police are still investigating the issue. The nuclear density gauge is a Troxler model 3440, serial number 69523, containing 10 mCi of Cs-137 and 40 mCi of Am-241. * * * UPDATE ON JULY 9, 2019 AT 1008 EDT FROM HABIB CHAUDHARY TO BETHANY CECERE * * * On July 8, 2019, a State Trooper found the gauge in a portable restroom in Highland Park in Hartford, CT. Connecticut Department of Energy and Environmental Protection determined the gauge was intact. The licensee's radiation safety officer is sending the gauge for leak testing. Notified R1DO (Dimitriadis), and ILTAB and NMSS Events Notification (via email). * * * UPDATE ON JULY 9, 2019 AT 1652 EDT FROM SHAWN CHAUDHARY TO CATY NOLAN * * * "The Connecticut Department of Energy & Environmental Protection representative stated that he surveyed the gauge and cleared it since no damage was done. Tri State has also visually inspected and surveyed the gauge and found it to be intact and not tampered with. For extra precautions, a leak test of the gauge was taken and sent to a certified lab. The gauge will not be used until we have received the results from the lab. "Moving forward, all technicians have been instructed to make every attempt to drop off their gauge at Tri State Materials Testing Lab's designated gauge room every day at the end of their field work. If they cannot make it back due to weekend and night work, they must store the gauge at their home securely to prevent this type of incident recurrence." Notified R1DO (Dimitriadis), and ILTAB and NMSS Events Notification (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-07-08
54138 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2019-06-26 | 2019-06-28 16:48 | 2019-06-28 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following is a synopsis of an email from the state of Mississippi: On June 28, 2019, the Mississippi Division of Radiological Health (DRH), Radioactive Material Branch, reported that a Troxler moisture density gauge serial number 29421, was stolen on June 26 or 27, 2019, from a person's residence in Moss Point, Mississippi. The gauge was stolen from the back of the company pickup truck; the padlocks on the chains were cut and the gauge was removed from the storage box. The company Radiation Safety Officer (RSO) contacted the Moss Point Police Department. The RSO contacted the state of Mississippi Health Physicist (HP) and the state HP contacted the Department of Homeland Security. The Troxler gauge contained a 9 mCi Cs-137 and a 44 mCi Am/Be-241 sources. Mississippi Report Number: MS-190003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2019-07-08
54137 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-06-27 09:37 | 2019-06-27 16:06 | 2019-06-27 | LOSS OF POWER RESULTED IN A VALID ISOLATION SIGNAL "At 0937 EDT on 6/27/19, Susquehanna Unit 2 had a control power fuse fail that caused a loss of power to one of two power distribution systems of the Reactor Protection System. This loss of power resulted in a valid isolation signal and actuation of the Primary Containment Isolation System that affected multiple systems, and is reportable per 10 CFR 50.72(b)(3)(iv)(A)." The situation has been resolved and the plant is currently using an alternate power source. Offsite power and the Emergency Diesel Generators are still available. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-06-27
54136 | -1 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-06-26 | 2019-06-27 13:32 | 2019-07-17 | AGREEMENT STATE REPORT - BRACHYTHERAPY UNDERDOSE DUE TO DISLODGING OF DEVICE The following was received via e-mail: "A patient was planned for a HDR [high dose rate] brachytherapy vaginal cuff treatment, fraction 1 of 2, at 5 Gy per fraction. A vaginal cylinder was placed in the vaginal canal and the positioning was verified with a cone beam CT scan. The cylinder was then connected to the afterloader containing the Ir-192 source [3.449 Ci; GammaMed 232 S/N: 24-01-7273-001-020819-12601-99] and treatment commenced. Upon completion of the treatment, it was observed that the vaginal cylinder was dislodged from the initial position. The cylinder was found between the legs, outside the vaginal canal, in contact with the perineal region. The patient indicated that she had coughed at some point during the treatment, which may have contributed to the dislodgement of the cylinder. "The estimated skin dose is 5 Gy (500 rad). No erythema was observed at the time of discovery. "The patient and referring physician have been notified." Ohio Item Number: OH190009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION ON 7/17/19 AT 1342 EDT FROM MICHAEL RUBADUE TO HOWIE CROUCH * * * The following retraction information was obtained from the state of Ohio via email: "An inspection was conducted on July 15, 2019 to investigate the event. It was determined that the applicator was properly secured for the prescribed treatment, but was dislodged by the patient. Since the cause was patient intervention, this is not a medical event." Notified R3DO (Edwards) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-07-05
54135 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2019-06-25 18:00 | 2019-06-27 09:45 | 2019-06-27 | AGREEMENT STATE REPORT - POOL WATER CONDUCTIVITY EXCEEDS LIMIT The following was received via e-mail: "At approximately 1800 EDT on 6/25/2019, the conductivity of the underwater pool irradiator water rose to 308 microSiemens/cm and remained in this range throughout the night. This was in conjunction with low flow through the water circulation pump. The pump was repaired the morning of 6/26/2019 and subsequent conductivity readings have ranged from 24.3 microSiemens/cm to 13.9 microSiemens/cm. The licensee is currently on a plan of changing the deionization tanks every two days to continue cleaning the water. In addition they are working with a supplier on additional methods to clean the pool water." New Jersey Event Report Identification No.: INV190001-507147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2019-07-05
54134 | 0 | U.S. NAVAL RESEARCH LABORATORY |  |  |  |  | 2019-05-09 | 2019-06-27 09:30 | 2019-06-27 | LEAKING NI-63 SOURCES The following is a summary of the phone conversation with the licensee: Two Ni-63 sources (Agilent Technologies S/Ns PRO30 and U11381) used in an electron capture detector were found to be leaking. Both sources contained 15 mCi Ni-63. Leakages were 0.048 and 0.039 microCuries. Both sources will be transferred to Agilent Technologies for disposal. Leak tests are performed every 6-months. The last leak tests were performed on 01/08/2019. The licensee contacted NRC Region I regarding this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-07-05
54133 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2019-03-01 | 2019-06-27 09:21 | 2019-06-27 | AGREEMENT STATE REPORT - OVEREXPOSURE TO MEMBERS OF THE PUBLIC The following was received from the South Carolina Department of Health and Environmental Control (the Department) via phone: On June 26, 2019, the Department was officially notified that 22 workers (members of the public) received doses while performing vat cleaning at Fiber Industries, a polymer manufacture. Seven of those individuals received a dose exceeding the annual limit of 100 mrem, as stated in 10 CFR 20.1301. The exposures occurred in March and April 2019, after which the Department was notified of the potential overexposures. The cleaning occurred in two vessels that had the Cs-137 gauge sources in the open position but no tag out. The gauges are a level density gauge (300 mCi, 1974) and a filling dip tube (20 mCi, 1974). The doses were calculated by Chase Environmental Group based on the individuals' time in the vessels and distance from the sources. The midpoint dose estimate for the seven individuals range from 112 to 205 mrem. The Department conducted a site visit on June 14, 2019, and is currently evaluating the incident. Based on the 30-day notification provided to the Department on June 26, it is unknown if the individuals have been notified and no names were provided. Additional information will be sent to the NRC once the review is complete. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2019-07-05
54132 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-06-24 | 2019-06-26 15:45 | 2019-06-26 | AGREEMENT STATE REPORT - ADMINISTERED DOSE DIFFERENT THAN PRESCRIBED The following was received from the North Carolina Radioactive Materials Branch via email: "On 6/24/19, a patient underwent a Xofigo therapy treatment and did not receive the full dose as prescribed but had to return the following day to receive the full dose on 6/25/19. Due to the size of the patient and the fact that Xofigo doses typically arrive to the licensee in 10cc syringes, [in order] to accommodate the patient with the correct dose, the dose prescribed to the patient was split between two doses/syringes. On 6/24/19, licensee personnel delivered the first dose of 119.19 microCuries (Ra-223) which was approximately 50 percent of the prescribed dose. It was discovered after the patient was discharged that the remaining dose was still in the hot lab. The prescribing physician was immediately notified and the patient returned the following day, 6/25/19, and received the second dose of 114.5 microCuries (Ra-223). NC Radiation protection is currently investigation this incident and will follow up to close and complete this report." NC tracking number: 190021 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-07-04
54131 | 0 | WATERFORD | 3 |  |  | [3] CE | 2019-06-25 04:28 | 2019-06-25 11:09 | 2019-06-25 | CONTROL ROOM ENVELOPE INOPERABLE DUE TO BROAD RANGE GAS MONITORS BEING INOPERABLE "On June 25, 2019, at 0428 CDT, the Waterford 3 shift operating crew declared the control room envelope inoperable in accordance with Technical Specification (TS) 3.7.6.1 due to both Broad Range Gas Monitors being inoperable. Operations entered TS 3.7.6.1 action b, which requires that with one or more control room emergency air filtration trains inoperable due to inoperable control room envelope boundary in Modes 1, 2, 3, or 4, then: 1. Immediately initiate action to implement mitigating actions; 2. Within 24 hours, verify mitigating actions ensure control room envelope occupant exposures to radiological, chemical, and smoke hazards will not exceed limits; and 3. Within 90 days, restore the control room envelope boundary to operable status. "Action b.1 was completed by placing the control room in isolate mode at time 0441 CDT. This event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D), event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to (A) shutdown the reactor and maintain it in shutdown condition and (D) mitigate the consequences of an accident, due to the control room envelope being inoperable. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-06-25
54130 | -1 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2019-06-24 18:15 | 2019-06-24 21:18 | 2019-09-30 | POTENTIAL UNANALYZED CONDITION DUE TO UNPROTECTED CONTROL CIRCUITS RUNNING THROUGH MUTILPLE FIRE AREAS "During a review of industry Operating Experience it was identified that there were unprotected DC control circuits for non safety-related DC motors which are routed from the Battery Charger Rooms to other separate fire areas. Circuit Breakers used to protect the motor power conductors appear to be inadequate to protect the control conductors. The concern is that under fire safe shutdown conditions, it is postulated that a fire in one area can cause short circuits potentially resulting in secondary fires or cable fires in other fire areas where the cables are routed. The secondary fires or cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. "This condition is reportable as an 8-hour ENS report in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. Requirements of the Technical Requirements Manual (TRM) for the affected fire areas will be implemented." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM ROBERT GRAHAM TO HOWIE CROUCH AT 2045 EDT ON 9/30/19 * * * "In accordance with NUREG-1022, Sections 2.8 and 5.1.2, James A. FitzPatrick Nuclear Power Plant is retracting (formally withdrawing) Licensee Event Report (LER) Number 2019-002. "LER 2019-002 was transmitted to the NRC via letter JAFP-19-0080 dated August 23, 2019. The LER reported, under 10 CFR 50.73(a)(2)(ii)(B), the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. "Subsequent to submittal of LER 2019-002, FitzPatrick Engineering completed analyses using more accurate input conditions. This analysis has determined no credible hot short scenario will result in damage to adjacent cables in other fire zones, showing that the postulated condition would not degrade plant safety. Therefore, James A. FitzPatrick Nuclear Power Plant is retracting LER 2019-002 [and this event notification]." The licensee will notify the NRC Resident Inspector and the New York State Public Service Commission. Notified R1DO (DeFrancisco). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2019-06-24
54129 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2019-06-22 | 2019-06-24 17:37 | 2019-06-24 | AGREEMENT STATE REPORT - FOUND SOURCE The following is a synopsis of a report received from the Utah Department of Environmental Quality (the Agency) via email: At 1102 [MDT] on June 24, 2019, the Agency received a phone call from an individual who found a yellow box with radiation symbols on the outside of the box. Upon arrival at the individual's home, the Agency saw a yellow Troxler transportation case next to the driveway. The individual stated that the case was found on June 22, 2019. The Agency inspected the case and measured a contact dose rate of 40 microCuries/hr on the outside with a Bicron dose rate meter. There were no locks on the outside of the case. The Agency then opened the case and found a Troxler Model 3430, Serial Number 64033, containing 8 mCi of Cs-137 and 40 mCi of Am-241/Be. Although the source was in the shielded position, there was no lock to secure the source in the shielded position. The case was not labeled with any name or contact information. The Agency took control of the gauge and brought it back to the office and secured it. A calibration sheet was found and used to determine the owner of the gauge. It was confirmed that the gauge belonged to Transportation Alliance Engineering. The agency will conduct an inspection. Utah Event Report ID #: UT190003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2019-07-02
54128 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-06-21 | 2019-06-24 15:19 | 2019-08-01 | AGREEMENT STATE REPORT - OVEREXPOSURE DURING RADIOGRAPHY The following report was received from the Texas Department of State Health Services (the Agency) via email: "The licensee called [the Agency] to report an event involving a radiographer and trainee. They were conducting [non-destructive testing] NDT on pipe, shooting 8 second shots with a 76.3 Curie Ir-192 source and a QSA Global D888 camera. The radiographer went to the darkroom to complete some paperwork. The trainee took down film and moved the collimator to the next shot location. It was about then [the trainee] realized [the trainee] had not retracted the source. [The trainee] reported the mistake to the radiographer trainer. The trainee did not have dosimetry and did not conduct a camera survey prior to moving the camera. Both the trainer and trainee were issued RadEye G's so they did not have direct reading dosimeters. [The trainer and trainee] took the trainee's dosimeter that was left in the truck and decided to expose it to the source for a few seconds. Then they reported that [the trainee] received 145 mrem on his dosimeter. When the RSO questioned them, they told [the RSO] what had happened and [the RSO] then conducted a time dose study. Based on reenactment, the RSO determined the trainee was exposed to the source about 6 seconds. The calculations indicated the trainee may have received 1456 rem to the hand. [The RSO] didn't take credit for the collimator shielding and used 5.9 R/hr/Curie at 1 foot as the basis for the calculation. The radiographer and trainee have been placed on administrative leave pending a decision from the company's review board. [The Agency] told [the licensee] that it would be investigating this event and that it will want to interview the radiographer and trainee." The Agency believes the calculated dose may be high but will follow-up during the investigation. Texas Incident #: 9691 * * * UPDATE ON 06/27/2019 AT 1531 EDT FROM KAREN BLANCHARD TO JEFFREY WHITED * * * The following report was received from the Texas Department of State Health Services (the Agency) via email: "During an investigation, the Agency learned there had been a miscommunication in the dose the licensee reported for the radiographer trainee's hand. The dose was not 1456 rem. The licensee is working with a consultant to make both a hand and whole body dose calculation. With the information provided, it appears the calculated dose to the radiographer trainee's hand should be less than 10 rem, which is below the regulatory reporting limit. The licensee will continue to monitor the radiographer trainee's hand. More information will be provided as it is obtained in accordance with SA-300." Notified R4DO (Groom) NMSS (Rivera-Capella) and NMSS Events and INES (Milligan) via e-mail. * * * RETRACTION ON 8/1/19 AT 1725 EDT FROM KAREN BLANCHARD TO MICHAEL BLOODGOOD * * * The following retraction information was obtained from the state of Texas via email: "Miscommunication during initial incident reporting. Exposure was well below reporting requirement/no overexposure." Notified R4DO (Groom) and NMSS Event Notifications via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-07-02
54127 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-06-20 13:40 | 2019-06-20 17:59 | 2019-06-20 | INOPERABILITY OF CONTAINMENT SHIELD BUILDING "At 1340 EDT on June 20, 2019, a breach in excess of allowable margin in the Unit 2 Shield Building annulus was identified. T.S. LCO 3.6.15, Condition A was entered. The breach is expected to be repaired within the 24 hours allowed LCO time. "No other equipment issues were identified. "The Shield Building ensures that the release of radioactive material from the containment atmosphere is restricted to those leakage paths and associated leakage rates assumed in the accident analysis during a Loss of Coolant Accident (LOCA). "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C). "NRC Resident Inspector has been notified." The breach consists of a tear in a flexible boot seal for a penetration associated with the suction path for gas treatment fans. There is no release of radioactive material associated with this event. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-06-20
54126 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-06-20 | 2019-06-20 17:07 | 2019-06-20 | AGREEMENT STATE REPORT - SHUTTERS STUCK OPEN ON THREE FIXED GAUGES The following report was received from the Texas Department of State Health Services via email: "A licensee consultant reported, with authorization from the licensee RSO, that three fixed gauges; two Vega model SHF1 devices, serial no.'s 5873CN and 5801CN, containing 20 mCi Cs-137 and one Ronan SA1, SN 9500gg, containing 1000 mCi Cs-137 were found to have stuck shutters during routine inspection. The shutters are in the open position, which is their normal operating mode. The gauges remain in positon on tanks containing alkaline media and are still operating. A service company is being contacted to conduct repair/replacement. None are scheduled at this time. The gauges represent no hazard to the public due to their position." Texas Incident # 9689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-06-28
54125 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-06-17 | 2019-06-20 16:18 | 2019-06-20 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following report was received from the state of Georgia via email: "[On 6/17/2019,] the mill instrumentation group was called to check on a problem with readout from a nuclear gauge indication of high level for the number 26 chip digester. In the course of troubleshooting the problem, the Instrument Mechanic found that the gauge shutter handle would not remain locked in the [full] open position, but would slowly close as the digester operation caused the instrument to vibrate. "The gauge shutter was left in the open position with instructions for operations to notify the Instrument Mechanic if needed. As the shutter for the digester level gauges are open during normal operations, this poses no added safety risk. "Berthold was called and arrangements have been made for them to come on site on 6/27/2019 to either repair or replace the shutter." The gauge is a Berthold model LB7442 with a 50 mCi Co-60 source (serial number 526-03-09). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-06-28
54124 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-06-12 | 2019-06-19 10:00 | 2019-06-28 | AGREEMENT STATE REPORT - LEVEL GAUGE SHUTTER FUNCTIONAL PROBLEMS The following was received from the Louisiana Department of Environmental Quality via email: "On 06/13/2019, Honeywell (HW) reported that they detected [on 6/12/19] malfunctions/operational difficulties of shutters on [three level density] gauges installed on processes during the annual inspection and operational checks/tests. The gauge shutters would not function as designed by the manufacturer due to the operational environment and need of routine maintenance. HW called a service contractor, RONAN Engineering, to evaluate these situations and determine the best courses of action to correct the problems. "The sources and devices will remain installed on the processes until any repairs and maintenance are completed. This is not a radiation exposure hazard and does not pose a health and safety situation for the HW employees or the general public. "The level gauges are RONAN Engineering S/N M7549, 50 mCi Cs-137, S/N HH113 50 mCi Cs-137 and M7666 100 mCi Cs-137 sources. "This event is being reported to the NRC OP CENTER as required by Regulatory Requirement 10 CFR Part 30.50(b)(2) & LAC 33:XV 340.B." Event Report ID No.: LA-190009 * * * UPDATE FROM JOSEPH NOBLE TO DONALD NORWOOD AT 0932 EDT ON 06/28/2019 * * * The following information was received via E-mail: The last paragraph of the initial report above should be changed to read as follows: "This event is being reported to the NRC Operations Center as required by regulatory requirement 10 CFR 30.50(b)(2) and LAC 33:XV 341.B." Notified R4DO (Groom) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-06-27
54123 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-06-17 11:30 | 2019-06-18 15:57 | 2019-06-18 | AGREEMENT STATE REPORT - DAMAGE TO RADIOGRAPHY GUIDE TUBE PREVENTING RETRACTION OF SOURCE The following information was received from the Ohio Department of Health via E-mail: "On 6/17/2019, the licensee reported an incident while shooting at a client location in Bremen, Ohio. They were setting up 2 inch welds on a table in the shooting vault. The spool piece weighed approximately 40 pounds. As the radiographer cranked out the shot at approximately 1130 EDT, he immediately heard a loud noise and tried to crank the shot in, but could not get the source (Ir-192; 63.8 Curies) back into the camera. The vault door was opened slightly to see what had happened. The spool piece had fallen off the table and crushed the guide tube. The door to the vault was shut and licensee staff prepared a plan to get the source back into the camera. "The RSO [Radiation Safety Officer] made a 15 second trip into the vault to shield the source using (6) 1 inch long x 2 inch thick x 4 inch wide lead blocks. During this first entry into the vault to put the shielding down, the RSO received a dose of 20 mR. The RSO made a second trip into the vault to put more shielding down and access the situation. During this time he discovered that the drive cable was partially sheared off and the guide tube was crimped at that area. The RSO received an additional 10 mR during this trip. With the shielding in place the licensee measured approximately 0.5 mR/hr outside the shooting vault. "Proper source retrieval procedures were followed and the source was retrieved and placed into the camera using source retrieval equipment and new cranks and guide tubes. The Ohio Department of Health, Bureau of Environmental Health and Radiation Protection was contacted by phone at approximately 1430 EDT on 6/17/2019, to inform of what transpired. At no time were there any members of the public exposed. During the whole retrieval process the RSO received a total dose of 55 mR." Ohio Item Number: OH190008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-06-26
54122 | 0 | U.S. AIR FORCE RADIOISOTOPE COMM |  |  |  |  | 2019-02-27 | 2019-06-18 15:36 | 2019-06-18 | RUPTURED AUTOCLAVE VALVE WITH IDENTIFIED THORIUM-232 The following was received via email. "Between 2/27/19 and 2/28/19, an autoclave (13 inches long with 1.25 inches width) ruptured in room 2BR136 of Building 20620, at Wright Patterson Air Force Base (AFB) OH. Nobody was present at the time of the rupture. Scientists were working with unlicensed materials (potassium niobate and potassium hydroxide) at the time of the event. This autoclave originally came from Hanscom AFB . "During the investigation, the installation Radiation Safety Officer found affixed to the inside of the autoclave canister non-removable thorium-232 (31,235 dpm/100 cm2) and a significantly lesser amount of removable thorium-232. Besides the material on the autoclave, no other contamination was present. Thorium contamination might be from the raw materials used in the autoclave and/or Hanscom AFB might have used thorium in the autoclave. The licensee are investigating and conducting additional gamma spectroscopic analysis of the interior of the ruptured autoclave. "This was a historical incident that the licensee was made aware of, and is still uncertain if it is reportable. The licensee had a discussion with NRC Region IV regarding this event. After the discussion, the licensee chose to report to the NRC Operations Center in accordance with 10 CFR 40.60. To the best of the licensee's knowledge, nobody had radiation exposure or radioactive material uptake. "The licensee will provide the follow-up written report within 30 days." The Thorium-232 Appendix B annual limit on intake is 3E-3 microCuries. The licensee contacted Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 3 | OH | MAT |  | 40.60(b)(4) |  |  |  | 0 | 2019-06-26
54121 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2019-04-30 06:50 | 2019-06-17 12:56 | 2019-06-17 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION DUE TO INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a general containment isolation signal affecting multiple systems. "On April 30, 2019, at approximately 0650 CDT, a level 2 containment isolation signal was introduced when a fuse for the Nuclear Steam Supply Shutoff System was removed for a maintenance clearance. The level 2 containment isolation signal caused a trip of the Division I DC bus back-up charger, leaving only the Division I battery to carry the DC bus. At 0707 CDT the bus was de-energized when another unrelated clearance opened the battery supply breaker to the DC bus causing another containment isolation signal. This event did not affect Shutdown Cooling or any other protected Safety Related Equipment. "The containment isolation signals caused an isolation of the systems listed below. All components that were not removed from service, gagged in position, already in the expected position due to plant conditions, or de-energized due to plant condition performed as designed. "Containment Isolation valves for the following systems isolated as expected: Drywell and Containment Floor Drains, Drywell and Containment Equipment Drains, Condensate Makeup, Fire Protection Water, Service Air, Instrument Air, Reactor Water Cleanup, Spent Fuel Cooling and Cleanup, Reactor Plant Component Cooling Water, Chilled Water, Reactor Recirculation, Main Steam Drains, Reactor Building Ventilation, and Fuel Building Ventilation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-06-17
54120 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-06-14 | 2019-06-17 11:08 | 2019-06-19 | AGREEMENT STATE REPORT - EQUIPMENT FAILED TO FUNCTION AS DESIGNED The following was received by email from the Commonwealth of Pennsylvania: "On Friday, June 14, 2019, the licensee experienced an equipment failure event during a brachytherapy treatment where the source failed to retract from the patient at the end of the treatment time. The catheter was immediately manually removed from the patient and placed in the emergency container and locked up. No harm is expected to the patient and no overexposures occurred. The HDR [High Dose Rate] unit, an Elekta Flexitron Model 136149A02, contained an iridium-192 source less than 12 Curies. The vendor, Best Vascular, was immediately notified and will be on site today, June 17, 2019, to retrieve the source and repair the device. "The DEP [PA Department of Environmental Protection] will update this event as soon as more information is provided. "The DEP will perform a reactive inspection. More information will be provided as received." PA Event Report ID No: PA-190014 * * * UPDATE FROM JOHN CHIPPO TO OSSY FONT ON 6/19/19 AT 1002 (EDT) * * * The following information was received from the DEP via fax: "On Monday, June 17, 2019, a service engineer from Best Vascular was able to drive the sources into the catheter and retract them into the device several times without incident. The licensee now believes the CVBT [CardioVascular BrachyTherapy] catheter was not fully seated into the device, causing a small leak and a subsequent pressure differential which does not allow the source to fully retract into the device." The cause of the event is believed to be operator error. The DEP will perform a reactive inspection. Notified R1DO (Greives) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-06-25
54119 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-06-07 | 2019-06-14 16:57 | 2019-06-14 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received via email from the Ohio Bureau of Environmental Health and Radiation Protection (Ohio): "A stuck shutter was reported on a Berthold LB300MLT fixed gauge with a 5 mCi Cs-137 source. The stuck shutter was discovered on 6/7/19 and immediately taken out of service. The gauge was repaired on 6/14/19. "Ohio was notified on 6/14/19. The licensee reported that the cause was the source wire interfering with the shutter movement." Item Number: OH190007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-06-24
54118 | 0 | ITT ENGINEERED VALVES, LLC |  |  |  |  | 2019-06-14 | 2019-06-14 16:45 | 2019-08-20 | INITIAL PART 21 REPORT - POTENTIAL PREMATURE FAILURE OF AIRMOTOR ACTUATOR DIAPHRAGM The following is a summary of the information received from ITT Engineered Valves, LLC (ITT) via facsimile: ITT discovered one batch of ten actuator diaphragms (five at the licensee's facility and five sent to Korea) for a No. 25 Airmotor which have demonstrated a potential to fail prematurely during operation. ITT has no evidence to show that any other batch of diaphragms are at risk. ITT is in the process of determining how to evaluate the effect of the diaphragm anomaly, while determining how to define the scope of the potential defect. This initial notification will be followed by a written notification by July 14, 2019. None of the actuator diaphragms were supplied to U.S. facilities. POC: Stephen Donohue (717) 509-2200 stephen.donohue@itt.com. * * * UPDATE AT 1152 EDT ON 7/12/2019 FROM STEPHEN DONOHUE TO JEFF HERRERA * * * The following is a synopsis of a report received via email: "Initial notification of the potential defect was made to the NRC via fax on 6/14/19. The potential defect report was designated Event 54118 shortly thereafter. Per 10 CFR Part 21 requirements, this report is the 30-day written notification to support the initial fax notification. "This potential defect is limited to the #25 airmotor diaphragm only. This issue is in no way related to any other size of airmotor diaphragm, and does not have any effect on the weir diaphragm within the diaphragm valve itself (the diaphragm identified as ITT's M1 diaphragm). "Potential impact of nonconformance: "The #25 airmotor diaphragm is designated as a safety related part when the valve to which it is assembled is identified as an active valve. The normal function of the airmotor diaphragm is to seal the airmotor chamber in order to permit conversion of air pressure to a thrust that can operate (open or close) the valve. The safety function is the same as the normal function. If the diaphragm should fail, the valve would not be capable of actuation, would not be capable of producing a force that would open or close the valve, so the safety function of an active valve would be compromised if the actuator diaphragm were to fail. "The #25 airmotor diaphragm is not designated as a safety related part when the valve to which it is assembled is identified as a passive valve. A passive valve only needs to fulfill its basic valve function (to open or close at loss of air power) and is not required to operate. That is, a fail-to-close valve will still close (still maintain its primary function) if its airmotor diaphragm has failed, it will just not be able to actuate. Therefore, no safety function is compromised if the actuator diaphragm is part of a passive valve. "Affected customers: "There were two sets of valves that were constructed at the same time (late May of 2018) from the same lot of #25 airmotor diaphragms, and using the same assembly procedures. One set of five valves was never shipped, was disassembled, and found to reveal the potential defect. The other set also consisted of five valves and was shipped to a customer in South Korea. At this time, ITT does not consider any other customers to be potentially affected. "Preliminary Root Cause: "At this point in time, it is believed that the cause of the delamination of the diaphragm is excessive assembly torque upon original construction. For the five disassembled valves, during the 110 psig production test the assembler noted that an excessive amount of bolt torque was required to attain a leak-free joint at 110 psig. It was observed that the preload force continued to act upon the already extruded diaphragm edge over time, causing eventual cracking and delamination. While we have not been able to observe for an entire year, we have been able to simulate the same effect in a limited fashion on a brand new diaphragm using the same valve hardware over the last four weeks. "Future plan of action: "1. Complete testing on the fifth of five damaged diaphragms. "2. Continue to evaluate the effects of excessive torque on the #25 airmotor joint. A second valve assembly will be built with a diaphragm from stock with intentionally high assembly torque, while the first unit mentioned above will be disassembled and examined. "3. The customer noted in [the above] section will be notified and given instructions on how to assess whether the damage observed in Lancaster is also possible on the other five valves that were built in the same time period. "4. Develop a means to identify problematic diaphragms after assembly, taking advantage of the fact that excessive torque on the joint in question will result in extrusion of the diaphragm beyond the outer diameter of the covers. "5. Prepare and submit a report or interim report within 60 days of date of discovery, which will be August 13, 2019." Notified the Part 21 Reactors and Materials group (via email). * * * UPDATE AT 1725 EDT ON 8/13/2019 FROM STEPHEN DONOHUE TO THOMAS KENDZIA * * * The following is a synopsis of conclusions from the final report received via email: Testing confirmed that the cause of the diaphragm failure was due to excessive torque applied to the bolts used on the #25 airmotor joint. The excessive torque was applied due to poor finish (not flat) of the sealing surfaces. Only a batch of five valves shipped to a customer in South Korea is affected. Directions on how to inspect the supplied valves for this defect were provided as follows: "1. Measure the bolt torque on the joint. If the value for each cap screw is measured to be 72-79 in-lb, the joint was assembled correctly and the diaphragm is likely to be functional. "2. Observe whether there is significant extrusion of the outer perimeter of the diaphragm. If the diaphragm extends beyond the OD of the covers by 0.12 in. around most of the circumference, the diaphragm is likely to be overtorqued. "3. Observe the edge of the diaphragm. The edge of the diaphragm should be square and straight. Examine the edge closely, looking for splitting lines within the elastomer or separation of the elastomer from the fabric outboard of each bolt. Any such damage indicates excessive torque." Valve assembly process will be changed to ensure flat sealing surfaces and to not exceed the specified torque. The South Korea customer will be notified and provided a copy of the report. Notified the Part 21 Reactors and Materials group (via email). * * * UPDATE AT 0847 EDT ON 8/20/2019 FROM STEPHEN DONOHUE TO THOMAS KENDZIA * * * ITT Engineered Valves, LLC, revised the final report with the end user specific site information and address of company, and provided precise valve identification information. Notified the Part 21 Reactors and Materials group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-06-14
54117 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2019-06-12 16:40 | 2019-06-13 16:03 | 2019-06-27 | CALIBRATION OF ITEMS-RELIED-ON-FOR-SAFETY NOT PERFORMED AS INTENDED "Operations conducted in BWXT Nuclear Operation Group, Inc. - Lynchburg's (BWXT NOG-L) Specialty Fuel Facility (SFF) utilize flammable and toxic gases. This facility is equipped with a Facility Alarm System (FAS) that monitors for the presence of flammable and toxic gases inside the closed processes (glove boxes) and in the room environment. The detection and automated actions of the FAS are credited as an Items-Relied-on-for-Safety (IROFS). During a review of the FAS calibration methodology, it was identified that the management measure of calibrating the system was not being performed as intended by the manufacturer's instruction/guidance. SFF Operations notified BWXT NOG-L's Industrial Health and Safety (IH&S) Department of this incident and its potential implications on June 12, 2019, at 1640 EST. "SFF Operations that utilize flammable and toxic gases have not operated since the summer of 2016. The operations reliant upon these gases have been suspended and posted Out-of-Service per BWXT NOG-L Procedure QWI 02.1.17, 'Suspending and Restarting Fuel Operations', since 2017, or prior. Currently, BWXT NOG-L's internal change management process is being utilized to deactivate/remove the equipment that utilizes the flammable and toxic gases. "BWXT NOG-L is continuing to investigate the insufficiency of this management measure and its impact on the credited IROFS. As stated in FCSS [Fuel Cycle Safety and Safeguards] Interim Staff Guidance-12, Revision 1, 10 CFR Part 70 Appendix A - Reportable Safety Events: 'The twenty-four hour time period for reporting events is intended to allow licensees sufficient time to make this determination. However, if the determination cannot be completed within this time frame then the event must be reported to the NRC Operations Center within twenty-four hours of discovery.' Due to the timeliness specified by the reporting requirements, BWXT NOG-L is making a 24-hour report in accordance with 10 CFR 70 Appendix A (b)(2), 'Loss or degradation of items relied on for safety that results in failure to meet the performance requirements specified in 10 CFR 70.61'. The applicable operations will remain shutdown pending further investigation." The licensee did notify the NRC Resident and will be notifying the NRC Regional Office. * * * RETRACTION FROM CHRIS TERRY TO DONALD NORWOOD AT 1052 EDT ON 6/27/2019 * * * "On Thursday, June 13, 2019, BWXT Nuclear Operation Group, Inc. - Lynchburg (BWXT NOG-L), made a 24-hour notification in accordance with 10 CFR 70, Appendix A, (b)(2), Loss or degradation of items relied on for safety that results in failure to meet the performance requirements specified in 10 CFR 70.61. "Since the notification on June 13, 2019, BWXT NOG-L has gained a full understanding of the issue and consulted with the manufacturer of the Facility Alarm System. BWXT NOG-L, recognizes that a degraded management measure existed in regards to the calibration of the flammable and toxic gas sensors. However, it is evident that the FAS system would, and will, activate and respond prior to a hazardous concentration occurring that could lead to a potential fire or employee exposure in excess of the short-term exposure limit. The IROFS is considered to be degraded; nonetheless, the capabilities of the system are still sufficient to meet the performance requirements set forth in 10 CFR 70.61." Notified R2DO (Bonser) and the NMSS Events Notification and Fuels Group E-mail groups. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 1 | 2019-06-21
54116 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-06-12 21:27 | 2019-06-13 03:59 | 2019-06-13 | HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE "At 2127 EDT on June 12, 2019, during routine testing, the HPCI turbine experienced an overspeed trip and then subsequently restarted and ramped to the required speed. As a result, the response time of the system exceeded the 60-second acceptance criteria, thereby rendering the system inoperable. This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D). The Reactor Core Isolation Cooling (RCIC) System and Automatic Depressurization System (ADS) are operable. "The safety significance of this event is minimal. Troubleshooting activities are in progress. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-06-13
54115 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-06-11 | 2019-06-12 15:45 | 2019-06-12 | AGREEMENT STATE REPORT - PATIENT DOSAGE GREATER THAN PRESCRIBED The following report was received from the State of Florida Bureau of Radiation Control via email: "This morning, HRMC Inc. [Holmes Regional Medical Center] called to report a misadministration of Y-90 TheraSpheres to a patient, 77 y/o female. Prescribed activity was 0.304 GBq, prescribed dose was 120 grey. Administered activity was 3.0 GBq, awaiting confirmation of administered dose, BRC [Bureau of Radiation Control] assumes administered dose will be 10 times prescribed dose based on 10 times administered activity. Lot # 1999265. An authorized physician discussed this incident with the patient and a few family members. This was intended to be a one time treatment. This appears to meet the criteria for an abnormal occurrence." Florida Incident Number: FL19-078 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-06-20
54114 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-06-12 | 2019-06-12 13:11 | 2019-06-21 | AGREEMENT STATE REPORT - LOST AMERICIUM/BERYLLIUM SOURCE The following report was received from the Texas Department of State Health Services (the Agency) via email: "On June 12, 2019, the licensee's Radiation Safety Officer (RSO) notified the Agency that while performing an in-depth audit, he became aware that a 250 millicurie americium-241/beryllium source (SN: T-128) they had been licensed for was not present at their main site. Records for the source indicate the last leak test was performed in September 2017, but the source was not recorded on quarterly inventories in 2018. The RSO has been unable to find any records of transfer or disposal. The RSO is continuing record searches and interviews as well as physical searches of the licensee's facilities. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: 9686 * * * UPDATE ON 06/21/2019 AT 1605 EDT FROM KAREN BLANCHARD TO THOMAS KENDZIA * * * The following was received from the Texas Department of State Health Services via email: "On 6/21/2019, licensee notified the Agency that it located the missing source at one of its facilities." Notified the R4DO (O'KEEFE), and the NMSS Events Notification, ILTAB, and CNSNS (Mexico Nuclear Safety Commission) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-06-20
54113 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2019-06-11 20:04 | 2019-06-12 12:17 | 2019-06-12 | FITNESS FOR DUTY - CONTRACT EMPLOYEE SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL A contract employee supervisor had a confirmed positive test for alcohol during a random fitness-for-duty test. The employee's access to the plant had been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2019-06-12
54112 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-06-12 08:49 | 2019-06-12 11:55 | 2019-06-12 | LOSS OF CONTROL ROOM EMERGENCY AIR TEMPERATURE CONTROL SYSTEM "At 0849 (EDT), a significant air leak on an inline air filter was identified. At 0908, the leak on the filter was isolated. A subsequent review of this situation determined that this air leak impacted operation of the A Train of the Control Room Emergency Air Temperature Control System (CREATCS) which is required to be operable in accordance with Technical Specification 3.7.10. At the time of this event, the B Train of CREATCS was out of service for planned maintenance. "With both trains of CREATCS out of service, both Watts Bar Units entered a condition that could have prevented fulfillment of a safety function. This condition was terminated when the leaking air filter was isolated. This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D). "NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-06-12
54111 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2019-06-11 11:32 | 2019-06-11 17:55 | 2019-06-11 | NORMALLY CLOSED PRIMARY CONTAINMENT ISOLATION VALVES FOUND IN THE OPEN POSITION "At 1132 CDT on 6/11/2019, both manual primary containment isolation valves in a one-inch service air line were found open. This resulted in an open primary containment penetration. Both valves are required to be closed for Primary Containment Isolation Valve Operability. Both valves were closed and independently verified closed at 1149 CDT on 6/11/2019. "This is being reported under 10 CFR 50.72(b)(3)(v)(C) and (D), and 10 CFR 50.72(b)(3)(ii)(B). "There was no impact to the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The licensee also notified the State of Minnesota State Duty Officer. | 82 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2019-06-11
54110 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-06-11 | 2019-06-11 18:07 | 2020-04-30 | AGREEMENT STATE REPORT - PATIENT UNDER DOSAGE DUE TO AIR BEING TRAPPED IN THE DELIVERY LINE The following report was received from the Georgia Department of Natural Resources via email: "A TheraSphere Y-90 patient did not receive the full dose to the target organ that was prescribed. The administered dose differed from the prescribed dose by more than 20 [percent]. "The prescribed activity to be delivered to the patient was 2.15 GBq (58 mCi). The calculated delivered activity to the patient was 1.01 GBq (27.3 mCi). The delivered activity was determined by comparing pre-and post-administration survey meter measurements of the administration equipment, as per standard TheraSphere procedure. "Radiological Analysis: Prescribed dose to target volume (liver): 127 Gy Administered dose to target volume (liver): 59.8 Gy "Discussion and Outcome: On May 28, 2019, it was brought to the radiation safety officer's attention that a Y-90 TheraSphere administration had not delivered the full prescribed activity to the patient as intended. Upon further discussion it was noted that the performing physician noticed after connection of the line between the micro-catheter and the delivery vial that multiple air bubbles had become trapped in the line. He then created a closed system manifold using a three-way stopcock and syringes to effectively bleed out air bubbles and flush back as much of the dose as possible to the patient. The closed system prevented any spillage or contamination, and residual dose was retained in the syringes and stopcocks. Despite these actions taken by the physician, a post-administration assay of the waste container showed that the full desired activity had not made it out of the delivery equipment and into the patient. The procedure was a segmentectomy, and [the] patient will be re-evaluated in one month's time to determine if an additional therapeutic administration will be needed. "Root Cause: Human error: Air was likely trapped somewhere in the system during the initial setup of the equipment. Operator technique failed to completely purge the lines of this air. Air bubbles in the line were not visible or not noticed prior to the connection of the line. Efforts to eliminate the air and deliver the full dose to the patient were then not successful. "Corrective Actions and Actions to Prevent Further Occurrences: The nature of this event and the likely cause has been discussed with all staff involved in these procedures. "A refresher training session has been scheduled for staff involved in these procedures. This training will be provided by a representative from BTG/TheraSphere starting on June 10, 2019. "An additional step will be added to the procedure to visually and verbally confirm that there is no detectable air in the line between the micro-catheter and the dose vial prior to connection." * * * UPDATE FROM IRENE BENNETT TO HOWIE CROUCH (VIA EMAIL) ON 4/30/20 AT 1323 * * * The NMED report number from the original report was removed. The new NMED report number was not obtained. NRC Event number 54684 was also created for this event and was deleted from the database. Notified R1DO (Schroeder) and NMSS Event Notification (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-06-19
54109 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2019-06-11 13:24 | 2019-06-11 17:03 | 2019-06-11 | INADVERTENT WEEKLY TEST MESSAGE SENT TO LOCAL RADIO STATIONS "At 1324 CDT, on 6/11/19, Coffey County Emergency Management issued the following alert: "The Civil Authorities have issued a Nuclear Power Plant Warning for Coffey, KS beginning at 1323 CDT and ending at 1423 CDT (WIBW radio AM/FM). Coffey County Emergency Management Required Weekly Test. "A press release is planned to notify residents that the warning was only a test. "There was no impact to the health and safety of the public as a result of this event as the offsite response capabilities remain functional. The site is operating with no emergency conditions present. "This event is being reported under 10 CFR 50.72(b)(2)(xi), as an inadvertent notification of the IPAWS [Integrated Public Alert Warning System] system. A press release is planned. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-06-11
54108 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2019-06-11 08:20 | 2019-06-11 16:57 | 2019-06-11 | FITNESS FOR DUTY - NON-LICENSED EMPLOYEE SUPERVISOR TEST CONFIRMED POSITIVE A non-licensed contract employee supervisor had a confirmed positive for a controlled substance during a pre-access fitness for duty test. The individual's unescorted access to the plant has been terminated and the badge removed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | AR | POW |  | 26.719 |  |  |  | 0 | 2019-06-11
54107 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-05-01 | 2019-06-11 13:25 | 2019-06-11 | AGREEMENT STATE REPORT - FIXED GAUGE DEVICE SHUTTER FAILURE The following report was received from the Kentucky Department for Public Health and Safety via email: "Kentucky Radiation Health Branch (KYRHB) was notified by email, June 10, 2019, of an apparent fixed gauge device On/Off shutter equipment failure. KY Licensee Arkema, Inc. reports that on May 1, 2019, during a required 6-month check, instrument techs discovered the shutter was not closing. Verified by survey meter, the readings did not 'go down' as expected. Survey numbers are not recorded. Licensee RSO [radiation safety officer] notified plant operations department and the safety department that entry into that vessel is not permitted until the shutter mechanism has been repaired. This vessel is sealed and can contain hazardous chemicals. The only openings into the vessel are through bolted flanges or a bolted manway. The operations department controls who and when entry is allowed into any vessel. Entry into any vessel cannot be done unless the proper permits are completed, the tank is cleared, verified as clear, the source shutter is closed and verified as closed. If any of these things [are] not done then entry into the vessel is not permitted. The licensee will have a tag installed on the bolted manway stating that entry is not permitted. Ronan Engineering is scheduled to be onsite to evaluate repair or replace options. There has been no entry into this vessel in the past 6 months. The licensee will provide timely updates to KYRHB. The licensee will reinstruct employees of event reporting criteria." Kentucky Event ID: KY19006 . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-06-19
54106 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-06-07 | 2019-06-08 22:29 | 2019-06-08 | AGREEMENT STATE REPORT - DAMAGED MOISTURE-DENSITY GAUGE The following information was received via E-mail: "On [6/8/19], Cal OES (California Office of Emergency Services) contacted RHB (Radiologic Health Branch) to report an incident regarding a damaged moisture-density gauge. The incident occurred on 6/7/19, at a temporary job site located at 1627 Fulton Road, Santa Rosa, CA. The gauge involved is a CPN Model MC1, S/N M13044837, containing 10 mCi of Cs-137 and 50 mCi of Am-241. The gauge was run-over by a construction vehicle at the job site. The gauge housing has been damaged and the user was unable to retract the source rod back into shielded position. The RSO contacted a gauge vendor, Pacific Nuclear Technology (PNT), and they immediately responded to the incident at the site. The gauge was secured by PNT and transported back to their storage for disposal. Leak test performed by PNT did not indicate any contamination. The RHB will be following up on this incident." California 5010 Number: 060819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-06-17
54105 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-06-07 | 2019-06-07 16:09 | 2019-06-12 | AGREEMENT STATE REPORT - POSSIBLE NUCLEAR MATERIAL FOUND The following information was received via E-mail: "On 6/7/2019, a worker installing equipment contacted the BRC [Bureau of Radiation Control] in regards to what he believed to be radioactive material. He stated that he found a 'hot room' with boxes marked 'radioactive' that were abandoned. Due to the address, [the material] likely belongs to the listed licensee. Inspectors have been notified to contact the worker installing equipment and investigate." Florida Incident number: FL19-076 * * * UPDATE FROM MATTHEW SENISON (VIA EMAIL) TO HOWIE CROUCH AT 1100 EDT ON 6/12/19 * * * The following information was obtained from the state of Florida via email: "Upon arrival at the facility, inspector performed a radiation and contamination survey which did not reveal any levels above background. There were various shielded containers (sharps, calibration source, pharmacy transport, etc.), however there were no sources or residual radioactive material in them. All materials will be disposed of or recycled as required. Inspector removed all the Radioactive Material and Radiation Area signs and confirmed that there were no x-ray machines on site. No further action will be taken, this incident is closed." Notified R1DO (Cherubini) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-06-17
54104 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-06-07 | 2019-06-07 14:34 | 2019-06-07 | AGREEMENT STATE REPORT - LEAKING FE-55 SEALED SOURCES The following information was received via E-mail: "The licensee's Radiation Safety Officer reported on June 7, 2019 that the licensee discovered on June 6, 2019 that 31 of 34 Fe-55 sealed sources tested positive for Fe-55 contamination upon performance of leak testing of the sources in preparation for disposal of the sources. Six (6) of the 34 sealed sources exceeded reporting limits of 0.005 microCuries of removable contamination for each source. The highest removable contamination for a source was reported to be 0.025 microCuries. "All sources were used sources returned by customers accumulated by the licensee over a period of several years. The licensee is not certain at this time whether only one or more of the sources is actually leaking and contributed to the contamination of the other sources, all in the same storage container. "The sources have various manufacturer and model numbers. Most of the sources have a current activity of below one (1) millicurie and the highest activity source is currently approximately six (6) milliCuries. "All of the sources are secured in a lead storage container, inside a safe, in the licensee's source room, pending appropriate packaging and disposal of the sources. Area surveys were performed by the licensee and the licensee reports that there is no contamination outside of the storage container and no personnel exposures resultant of this event. "The licensee will provide a written report to the Agency [MA Radiation Control Program] in accordance with condition of its license within 5 days. The Agency considers this event to be open." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-06-17
54103 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-04-18 01:10 | 2019-06-06 12:02 | 2019-06-06 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION DUE TO INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a general containment isolation signal affecting multiple Main Steam Isolation Valves (MSIVs). "On April 18, 2019 at approximately 0110 EDT, during performance of an ASME reactor vessel leak check, all four inboard MSIVs closed as a result of actuation of the Main Steam Line (MSL) high flow instrumentation. The high flow signal was spurious on the 'D' channel with no flow in the MSLs. Since an actual high flow condition did not exist at the time of the actuation, the actuation was considered invalid. The MSIVs functioned as designed on actuation of the MSL high flow instrumentation. All outboard MSIVs were closed at the time of the actuation in accordance with the vessel leak check procedure. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-06-06
54102 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2019-06-05 | 2019-06-05 16:39 | 2019-10-11 | PART 21 INTERIM NOTIFICATION - FAILURE OF A SIGNAL CONVERTER SUPPLIED TO COOPER NUCLEAR PLANT The following is a summary of the information received from Engine Systems, Inc. via facsimile: ESI was notified on April 6, 2019 that a signal converter (also called a signal conditioner) that sends the Reactor Core Isolation Cooling turbine speed to the turbine controller had failed. The converter is at the manufacturer's facility undergoing testing at this time and they have been unable to complete their evaluation within 60-days. The evaluation is expected to be completed by July 31, 2019. The converter was only supplied to Cooper Nuclear Plant. * * * UPDATE FROM DAN ROBERTS TO DONALD NORWOOD AT 1710 EDT ON 7/19/2019 * * * The following is a synopsis of information received via facsimile: On June 5, 2019, Engine Systems, Inc. (ESI) issued an interim report regarding an identified deviation for which ESI was unable to complete an evaluation within the 60-day requirement. Per the interim report, ESI committed to complete the evaluation by July 31, 2019. The evaluation is now complete and the deviation is determined to be reportable in accordance with 10 CFR Part 21. ESI supplied the component which failed to comply or contained a defect. That part was a Signal Converter Transmitter, P/N SCT/4-20MA/4-20MA/24DC/-LIM-TA[DCM]. This component was only supplied to Cooper Nuclear Station. The nature of the defect was that a power inverter transformer, internal to the signal converter transmitter, failed shorted. The transformer failure adversely affected other circuit board mounted components which prevented the device from functioning properly. The signal converter transmitter is a component of a turbine control panel. Within the panel, the transmitter is used to sense the customer's remote speed setpoint input signal and convert the signal which is transmitted to the turbine control. Since the signal converter transmits the customer's remote speed setpoint input to the turbine control, operability of the device is critical to operation of the RCIC turbine control system. Therefore, a failure of the signal converter would adversely affect the RCIC turbine control system and thus may affect the safe shutdown of the reactor. At Cooper Nuclear Station, the failed component has been removed and replaced with a spare transmitter from a different batch. No further action is necessary. For ESI, the previous design transformer (used in the failed transformer) was discontinued by the transformer manufacturer in 2016 which required the signal converter transmitter manufacturer to source a new transformer. The new transformer has the same functionality with a slightly different form factor which minimizes the potential for common cause failure with the original style transformer. Therefore, no additional actions are required since a different transformer is in current use. ESI has included a verification of the current transformer design in the commercial grade dedication package. The names and addresses of the individuals reporting this information are: John Kriesel Engineering Manager Engine Systems, Inc.; 175 Freight Rd. Rocky Mount, NC 27804 Dan Roberts Quality Manager Engine Systems, Inc.; 175 Freight Rd. Rocky Mount, NC 27804 Notified R4DO (Proulx) and the Part 21/50.55 Reactors E-mail group. * * * UPDATE FROM DAN ROBERTS TO DONALD NORWOOD AT 1643 EDT ON 10/11/2019 * * * The following is a synopsis of information received via facsimile: Subsequent to the issue of the report on July 19, 2019, ESI became aware of another potential defect with the same device. As a result, ESI has amended the report to expand the extent of condition. ESI supplied the component which failed to comply or contained a defect. That part was a Signal Converter Transmitter, P/N SCT/4-20MA/4-20MA/24DC/-LIM-TA[DCM]. This component was only supplied to Cooper Nuclear Station. The nature of the defect was that four circuit board mounted components (two transistors, a capacitor, and a diode) failed, causing the device to go to zero output. These prevented the device from functioning properly. Corrective actions for Cooper Nuclear: As stated above, no further action is necessary. Corrective actions for ESI for the subsequent failure: ESI has been unable to positively determine the root cause; however, correspondence with the signal converter manufacturer indicates this may be related to the previous style transformer. While no anomalies were detected with the transformer, the failed components are electrically connected to the transformer. Verification of the current style transformer is performed in the commercial grade dedication package. The names and addresses of the individuals reporting this information are: John Kriesel Engineering Manager Engine Systems, Inc.; 175 Freight Rd. Rocky Mount, NC 27804 Dan Roberts Quality Manager Engine Systems, Inc.; 175 Freight Rd. Rocky Mount, NC 27804 Notified R4DO (Kellar) and the Part 21/50.55 Reactors E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2019-06-05
54101 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2019-06-04 16:00 | 2019-06-05 15:34 | 2019-06-05 | DEGRADATION OF AN ITEM-RELIED-ON-FOR-SAFETY "On June 4, 2019, at approximately 1600 MDT, Louisiana Energy Services dba URENCO USA identified that pressure instrument isolation valve, 1001-471-1A12, was open when it should have been shut to maintain the pressure boundary of autoclave 1LS1. The autoclave is used to homogenize UF6 and obtain samples. The autoclave pressure boundary forms IROFS10. "Recently, annual maintenance was performed on the autoclave as required by the IROFS10 surveillance requirements. Subsequently, a homogenization was started on a 30B cylinder of UF6. During the homogenization cycle, an unrelated low voltage condition on the electrical grid resulted in an automatic trip of the autoclave. The automatic trip functioned as designed. During restart of the autoclave, valve 1001-471-1A12 was found open. There was not an initiating event (no release of UF6) and no initiation of an accident sequence. The valve has been shut and the IROFS boundary has been restored. The autoclave has been returned to service and the plant is in a safe configuration. "This event has been identified in UUSA's corrective action program as EV 132253 and a causal investigation is planned." There was no impact to the health and safety of the public or plant personnel due to this event. The licensee will be notifying their NRC Region 2 Fuel Facility Inspectors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(2) |  |  |  | 1 | 2019-06-13
54100 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-06-03 | 2019-06-04 14:18 | 2019-06-04 | AGREEMENT STATE REPORT - STUCK SHUTTER ON PROCESS GAUGE The following information was received from the state of Louisiana via email: "On 06/03/2019, BCS [Blue Cube Solutions] detected a malfunction of an internal shutter of a gauge installed on a process. The gauge shutter would not function as designed by the manufacturer due to a rotor tip on an internal shutter. BCS called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. "The source and device with will remain installed on the process until the repairs are completed. This is not a radiation exposure hazard and does not pose a health and safety situation for the BCS employees or the general public. "This event is being reported to the NRC OP CENTER as required by Regulatory Requirement 10 CFR Part 30.50 (b)(2) & LAC 33:XV 340.B. "The Level Gauge is an OHMART, Model SHF-1, S/N M 6989, loaded with an approximately 120 mCi Cs-137 source, Model # A-2102." Louisiana Report ID No.: LA-190008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-06-12
54099 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2019-06-04 08:15 | 2019-06-04 11:39 | 2019-06-04 | ISSUANCE OF PRESS RELEASE DUE TO SPURIOUS ACTUATION OF EMERGENCY SIRENS "On 06/04/2019, Nebraska Public Power District will issue a press release concerning the spurious actuation of emergency sirens near Cooper Nuclear Station and Indian Cave State Park. "This is a four hour report per 10 CFR 50.72(b)(2)(xi) for any event or situation for which a news release is planned or notification to other government agencies has been or will be made which is related to heightened public or government concern." The cause of the siren actuation is still under investigation. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM TERRELL HIGGINS TO HOWIE CROUCH AT 1301 EDT ON 6/4/19 * * * "During this event, State & local government agencies (Nemaha County, Atchison County, Richardson County, and Indian Cave State Park) were contacted regarding the spurious actuation of emergency sirens. This is an update to the original Event Notification # 54099." Notified R4DO (Kellar). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-06-04
54098 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-06-04 01:45 | 2019-06-04 04:10 | 2019-06-04 | MANUAL SCRAM DURING RAPID PLANT SHUTDOWN "At 0145 EDT, on 6/4/19, Unit 2 was manually scrammed during a Rapid Plant Shutdown. At 64 percent reactor power, a Rapid Plant Shutdown was initiated due to lowering Main Condenser vacuum as a result of the loss of a plant electrical panel that powers Offgas System controls. "The shutdown was normal and the plant is stable in Hot Shutdown with normal pressure control via the Main Turbine Bypass Valves to the Main Condenser and normal level control using Feedwater and Condensate. Main Condenser Vacuum has been restored." The licensee notified the NRC Resident Inspector. Additionally, State and local government agencies were notified. Prior to restarting Unit 2, an evaluation needs to be done due to the Unit 1 Diesel currently out of service for maintenance. The Unit 1 Diesel is a power supply for some of the common systems under the Unit 2 Technical Specifications and therefore required. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-06-04
54097 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-06-01 16:18 | 2019-06-01 17:58 | 2019-06-01 | OFFSITE NOTIFICATION DUE TO GASOLINE LEAKAGE TO SITE DRAINAGE SYSTEM "On June 1,2019, at 1618 [CDT], a notification under 10 CFR 50.72(b)(2) is being made due to notification to offsite agencies as a result of gasoline leakage to the site drainage system in the owner controlled area at South Texas Project. "During a routine tour, the facilities department notified the site environmental group about a gasoline leak on fuel tank sight glass at the fuel island on site. The site environmental [group] has determined the leak amount requires notification to the Texas Commission of Environmental Quality and the Environmental Protection Agency National Response Center. "The Texas Commission of Environmental Quality was notified at 1618 on June 1, 2019, and the Environmental Protection Agency National Response Center at 1626 on June 1, 2019. "The NRC Resident Inspector has been notified." The licensee stated that approximately 1,384 gallons of gasoline leaked over a period of time. The spill is located at an equipment warehouse area at a distance from the plant. The leak has been isolated and the cleanup is expected to be completed by tomorrow. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-06-01
54096 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2019-05-31 23:45 | 2019-06-01 03:15 | 2019-06-10 | MANUAL REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "At 2345 CDT at River Bend Station (RBS) Unit 1, a manual Reactor scram was inserted in anticipation of receiving an automatic Reactor Water Level 3 (9.7") scram due to the isolation of the 'B' Heater String with the 'A' Heater String already isolated. The 'B' heater string isolation caused loss of suction and subsequent trip of the running Feed Water Pumps 'A' and 'C'. All control rods fully inserted with no issues. Subsequently Reactor level was controlled by the Reactor Core Isolation Cooling (RCIC) system. Feed Water Pump 'C' was restored 4 minutes after the initial trip and the RCIC system secured. Currently RBS-1 is stable and is being cooled down using Turbine Bypass Valves. "No radiological releases have occurred due to this event from the unit." The plant is currently under a normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1603 EDT ON 6/10/19 FROM ALFONSO CROEZE TO JEFF HERRERA * * * "This amended event notification is being made to provide additional information that was not included in the original notification made on 6/1/19 at 0315 EDT. This event was reportable under 10 CFR 50.72(b)(3)(iv)(A) which was not annotated or described in the original report. "Forty-two minutes after the Feed Water Pump 'C' was started, the pump tripped causing a Reactor Water Level 3 (9.7") RPS actuation. Feed Water was restored five minutes later using the Feed Water Pump 'A'." The NRC Resident Inspector has been notified. Notified the R4DO (Warnick). | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-06-01
54095 | 0 | PARAGON ENERGY SOLUTIONS LLC |  |  |  |  | 2019-05-29 | 2019-05-31 14:27 | 2019-07-11 | PART 21 NOTIFICATION - INTROL POSITIONERS POTENTIAL LATENT DEFECT The following is an excerpt of the Part 21 information received via email: "Introl Positioners used by stations in G32 Terry Turbine control applicators have the potential to contain a latent defect. The defect is the result of internal corrosion which has been identified in Tl Operational Amplifiers Part No.TL084CN on the SL3EX Controller Boards of the turbine throttle valve positioner. It is believed the likely cause is associated with the ingress of solder flux into the IC Chip package on the controller board due to delamination caused by the soldering process during fabrication. The corrosion over time can result in intermittent open circuiting and high resistance in the aluminum metallization. Chlorine ionic contamination can also result in high leakage currents within the component circuitry. Failures may be manifested by a reduced valve position signal disproportional to the expected demand condition, no actuation signal (i.e. throttle valve remaining full open), or other anomalous unexpected behavior. There are three TL084CN chips on each SL3EX Controller Board within the positioner assembly. There have been two documented failures to date occurring in 2015 and 2019 in installed systems. "Date determination was made: May 29, 2019 "Affected sites: Farley, SONGS, Cooper, Almaraz Trillo Nuclear Power Plant (Spain), Clinton, Harris, Wolf Creek, Point Beach, Hatch, Watts Bar, Sequoyah. "Stations are advised to work directly with Curtiss-Wright SAS via the technical contacts below. "Randy F. Iantorno Project Manager, T: 585.596.3831, M: 585.596.9248, email riantorno@curtisswright.com or Justin Pierce 585.596.3866." * * * UPDATE FROM RANDY IANTORNO (CURTISS-WRIGHT) TO DONALD NORWOOD AT 1537 EDT ON 6/7/2019 * * * The following is a synopsis of information received via E-mail: Shearon Harris Nuclear Plant experienced an overspeed trip of the Turbine Driven Auxiliary Feedwater Pump (TDAFW) on January 18, 2019 during routine system testing. Upon receipt of the initial start signal, the valve remained in the fully open position causing the TDAFW to trip on overspeed. Investigation into the overspeed trip revealed the positioner was not controlling the actuator properly in response to the governor command signal. This situation and subsequent troubleshooting led to replacement with the site spare positioner. Once installed, the system responded as expected and the suspect positioner was sent to Curtiss-Wright SAS (CW SAS) for evaluation. In a joint effort between CW SAS and Paragon Energy Solutions (PES), the positioner was tested and evaluated to determine the cause of the failure. Corrective action which has been, is being, or will be taken: - The three TI chips on the affected board have been successfully replaced at PES. The repaired positioner will be configured and returned to Shearon Harris. - The evaluation of suspect chips has been limited to those removed from the failed positioner, along with some supplied to PES by CW SAS. Work is ongoing in this area. - A complete list of potentially affected installations is listed in the PES Part 21 Report dated May 31, 2019. - Although this defect has the potential of preventing the Electronic Governor Speed Control System (EGSCS) from performing its intended safety function, it does not prevent the Terry Steam Turbine from operating. If the EGSCS fails, the turbine can be operated manually using the Trip and Throttle Valve (TTV) to control speed by regulating steam flow to the turbine. - Steps are being taken to develop a plan to replace chips on affected positioner boards. This is still in the preliminary stages and specific recommendations will follow. Notified R1DO (Carfang), R2DO (Rose), R3DO (Kozak), R4DO (Kellar), Part 21 Reactors E-mail group, and Part 21 Materials E-mail group. * * * 1058 EDT ON 7/11/2019, UPDATE FROM RANDY IANTORNO (CURTIS-WRIGHT) TO MICHAEL BLOODGOOD * * * The following was received via e-mail. "This is a follow up letter related to Curtiss-Wright SAS (CW SAS) Report no. 48 submitted on June 6, 2019 regarding the Introl positioner failure discovered at the Shearon Harris Nuclear Plant on January 18, 2019. "As reported in the initial report, the failure has been isolated to internal corrosion discovered inside TL084N Operational Amplifier chips on the SL3EX Controller Board. The cause of the failure has yet to be determined; however CW SAS and Paragon Energy Solutions (PES) continue to investigate potential causes. "CW SAS will continue working with affected sites to provide guidance on additional testing, along with developing solutions that include replacement of suspect chips on the Introl positioner control boards. To allow CW SAS to coordinate efforts on a site by site basis, this will be the final correspondence sent directly to the NRC on this matter." Notified R2DO (Ehrhardt), R3DO (McCraw), R4DO (Azua), Part 21 Reactors E-mail group, and Part 21 Materials E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-05-31
54094 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-05-29 22:10 | 2019-05-30 00:10 | 2019-05-30 | SECONDARY CONTAINMENT DECLARED INOPERABLE "On May 29, 2019, at 2210 EDT, plant personnel notified the Main Control Room that both doors in the Secondary Containment Airlock on the Reactor Building First Floor were opened simultaneously for a period of approximately two seconds. This resulted in Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. Secondary Containment pressure observed during that time remained unchanged and within TS limits. There were no radiological releases associated with this event. "Declaring Secondary Containment inoperable as a result of not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-05-30
54093 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-05-29 | 2019-05-29 16:22 | 2019-05-29 | AGREEMENT STATE REPORT - SOURCE DRIVE CABLE DISCONNECTED The following report was received from the Texas Department of State Health Services via email: "On May 29, 2019, the agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that one of their crews had suffered a source disconnect at a field site location. The exposure device being used was a QSA 880D device containing a 58.8 Curie Iridium - 192 source. The RSO stated two individuals approved for source retrieval, retrieved the source, and that no over exposures occurred due to the event. The RSO stated that during the retrieval it was found that the drive cable broke near the connector. The crank out device has been taken out of service and will be sent to the manufacturer for inspection. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-06-06
54092 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-05-27 09:40 | 2019-05-27 11:53 | 2019-05-27 | ONSITE SPILL OF CHEMICAL TOILET "On May 27, 2019 at 0940 EDT, a portable chemical toilet was found tipped over. Approximately one gallon of contents spilled to the gravel only and did not reach any waterways or storm drains. Cleanup efforts are in progress. A notification to the Michigan Department of Environmental Quality and local health department is required, as well as a press release. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(xi)." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-05-27
54091 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2019-05-26 05:12 | 2019-05-26 09:25 | 2019-05-26 | AUTOMATIC REACTOR TRIP DUE TO A REACTOR COOLANT PUMP TRIP ON GROUND FAULT "This is a 4-hour Non-Emergency 10 CFR 50.72(b)(2)(iv)(B) notification due to a Plant Protection System (PPS) actuation. Arkansas Nuclear One, Unit 2, automatically tripped from 100 percent power at 0512 CDT. The reactor automatically tripped due to 2P-32B Reactor Coolant Pump tripping as a result of grounding. "No additional equipment issues were noted. All control rods fully inserted. Emergency Feedwater (EFW) actuated and was utilized to maintain Steam Generator (SG) levels. The EFW actuation meets the 8-hour Non-Emergency Immediate Notification Criteria of 10 CFR 50.72(b)(3)(iv)(A). No Primary safety valves lifted. Main Steam Safety Valves (MSSVs) did lift initially after the trip. "The NRC Resident Inspector has been notified. "Decay heat is being removed via the steam dump valves to the main condenser. Unit 2 is in a normal shutdown electrical lineup. Unit 1 was not affected by the transient on Unit 2. The licensee notified the State of Arkansas." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-05-26
54090 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-05-25 19:30 | 2019-05-26 01:58 | 2019-05-26 | LOSS OF MAIN CONTROL ROOM AREA RADIATION MONITORS "At 1930 [CDT] on 5/25/2019, communications were lost with the main control room area radiation monitors. These detectors are used to determine if an emergency action level (EAL) has been reached for initiating condition RA3 (Radiation levels that impede access to equipment necessary for normal plant operations, cooldown, or shutdown). "This unplanned loss of the ability to evaluate an EAL for initiating condition RA3 is considered a loss of emergency classification capability and is reportable as a Major Loss of Emergency Preparedness Capabilities per 10 CFR 50.72(b)(3)(xiii). This is an 8-hour reportable notification. "Portable area radiation monitors have been established as a compensatory measure per station procedures. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-05-26
54089 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2019-05-24 20:19 | 2019-05-25 00:30 | 2019-05-25 | LICENSED EMPLOYEE FAILED A RANDOM FITNESS -FOR-DUTY TEST "A licensed employee was determined to be under the influence of alcohol during a random [fitness-for-duty] test. The employee's access to the plant has been canceled." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2019-05-25
54088 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2019-05-24 | 2019-05-24 17:43 | 2019-05-24 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE ON MOISTURE DENSITY GAUGE The following information was obtained from the Commonwealth of Virginia via email: "On May 24, 2019, the Radiation Safety Office for the licensee made a preliminary report of an incident which occurred earlier on that day. The technician extended the source rod while using a portable moisture density gauge but was unable to retract it. The technician placed the gauge, with source rod extended, in the bed of his truck and drove back to his office, approximately 15 miles. "When he arrived at his office, the other technicians were able to retract the source. A radiation survey confirmed the source was secured in its shield. The Virginia Office of Radiological Health will perform a reactive inspection to investigate this incident. This notification will be updated with additional information determined during the inspection." Virginia Event Report ID: VA 19-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2019-06-03
54087 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2019-05-24 13:10 | 2019-05-24 17:12 | 2019-05-24 | LOSS OF OFFSITE POWER DUE TO FIRE ON STARTUP TRANSFORMER "At 1310 CDT on 5/24/2019, Wolf Creek experienced a loss of offsite power to the safety-related NB02 bus, due to an external fire on a bushing on the startup transformer. The NB02 bus was reenergized when the 'B' Emergency Diesel Generator started and the output breaker automatically closed. The shutdown sequencer automatically started equipment as expected. "Due to the undervoltage condition on the NB02 bus, an AFAS-T [Auxiliary Feedwater Actuation Signal] signal was generated which started the turbine driven auxiliary feedwater pump. Turbine load was reduced to maintain reactor power less than 100% in response to the start of turbine driven and 'B' motor driven auxiliary feedwater pumps. "The fire was extinguished using a fire extinguisher at 1320 CDT. "The unit is stable at 97% power." The NB02 bus remains on the 'B' Emergency Diesel Generator (EDG). The other EDG is operable in standby. The NRC Resident Inspector was notified. | 97 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-05-24
54086 | 0 | TRACERCO |  |  |  |  | 2019-05-22 | 2019-05-24 16:22 | 2019-05-25 | LOST SOURCE DURING SHIPMENT The following is a synopsis of an event received via phone call: During a shipment from Pasadena, TX to Billings, MT, a 4 milliCurie Cobalt-60 (Co-60) source was lost in transit. The last known location was Memphis, TN. It was shipped on May 17, 2019 and was identified lost on May 22, 2019. The shipper and the common carrier are investigating. * * * UPDATE ON 05/25/2019 AT 1045 EDT FROM MONTY POPE TO JOANNA BRIDGE * * * The following is a summary of a phone call with Mr. Pope: On May 24, 2019, the source that was misplaced by the common carrier was able to be located. New shipping documents are being generated. Notified R1RDO (Arner), R4RDO (GEPFORD), ILTAB (e-mail), NMSS Events (e-mail) and CNSNS Mexico (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.p | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-06-03
54085 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2019-05-24 07:30 | 2019-05-24 13:09 | 2019-05-24 | LOW PRESSURE CORE SPRAY INOPERABLE "At 0730 [EDT] on May 24, 2019, it was discovered that the Low-Pressure Core Spray System was inoperable. At Perry, the Low-Pressure Core Spray system is considered a single train system in Modes 1, 2, and 3; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). Inoperability of the Low-Pressure Core Spray system was caused by Emergency Service Water Pump A inoperability. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-05-24
54084 | -1 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2019-05-22 12:52 | 2019-05-24 12:01 | 2019-05-30 | AGREEMENT STATE REPORT - UNDERDOSE OF Y-90 THERASPHERE TREATMENT The following information was obtained from the state of Iowa via email: "The University of Iowa Radiation Safety Officer notified the Iowa Department of Public Health (IDPH) on May 23, 2019, of a possible medical event that had occurred at the University of Iowa Hospital on May 22, 2019. The event occurred during a therapeutic Yttrium-90 (Y-90) microsphere (TheraSphere) administration to the liver. The signed written directive from the authorized user was 1.37 GBq (37.03 milliCuries). During the administration, it appeared that the spheres were being administered without incident until the point at which the flow of spheres ceased. The interventional radiologist determined that stasis had been reached, which prevented the remainder of the prescribed dose from being administered and appeared to be the only explanation for what happened. Based on the final survey reading of the source vial and tubing in the waste container, the initial determined dose was 0.586 GBq (15.84 milliCuries) which is 42% of the written directive. "The following morning, May 23, 2019, routine imaging of the patient indicated no Y-90 activity in the patient's liver or abdominal areas. A second whole-body scan to determine any migration of activity was also negative for Y-90. The University of Iowa Radiation Safety Staff initiated an investigation into the location of the remainder of activity that was not remaining in the dose vial by surveying the procedure room and patient's room which were background levels and verified correct imaging protocol for the patient. The dose vial was re-surveyed and was found to contain all the original activity and no Y-90 TheraSpheres. "The licensee's preliminary probable cause is an occluded needle in the vial that could have prevented either the flow of saline into the source vial, or the flow of microspheres out of the vial to the patient. The authorized user, the interventional radiologist, and the patient have been informed of the issue with this administration. No direct harm to the patient has occurred because no radioactivity had been delivered to the patient. "This is a preliminary report and IDPH will be conducting an investigation to provide additional updated information. Items to initially get resolved include but are not limited to the licensee's issue with how dosages are measured before and after the procedure, independently verifying that no dose had been delivered to the patient, examine the integrity of the tubing and needles used in the procedure, and communication with the manufacturer about the circumstances surrounding this event and if they or the NRC are aware of any similar events." NMED Report No.: IA190001 * * * RETRACTION AT 1641 EDT ON 5/30/19 FROM STUART JORDAN TO JEFF HERRERA * * * The following retraction was received from the Iowa Bureau of Radiological Health via email: "The Iowa Department of Public Health requests to retract the NRC Event Notification No. 54084 (Item No. IA190001) that was transmitted to the NRC Operations Center on May 24, 2019. After conversations with the licensee's radiation safety officer and review of information provided by the licensee we have determined that no detectable amount of Y-90 TheraSpheres was administered to the patient, and therefore no dose was delivered. Based on a discussion with NRC Region III Office, we have determined that the circumstances surrounding this incident do not meet the reportable medical event described in 10 CFR 35.3045." Notified the R3DO (Daley), NMSS Events (via email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2019-06-03
54083 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-04-18 02:49 | 2019-05-24 09:51 | 2019-05-24 | INVALID ACTUATION OF A UNIT 2 CONTAINMENT ISOLATION LOGIC DUE TO A BLOWN FUSE "This 60-Day telephone notification is being made per the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of Limerick Generating Station Unit 2 containment isolation logic. "On April 18, 2019, while performing a relay replacement on the Division 2/4 Main Steam Line logic, a partial containment isolation occurred due to a blown fuse. "The following systems had components that actuated due to the partial isolation: Reactor Water Clean-Up System Primary Containment Instrument Gas System Drywell Chilled Water System Reactor Enclosure Cooling Water System Core Spray System "The Residual Heat Removal System received an isolation signal; however, the system remained in service because the isolation was defeated in accordance with plant procedures. "This event resulted in partial Group 2A, 3, 7A, 8A, and 8B isolations. The systems successfully functioned per the plant design and plant configuration." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-05-24
54082 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-05-21 | 2019-05-23 16:55 | 2019-05-23 | AGREEMENT STATE REPORT - ACTUAL DOSE GREATER THAN PRESCRIBED DOSE BY 87.6% The following information was obtained from the state of Florida via email: "On May 22, 2019, [the licensee Radiation Safety Officer] notified the BRC [Florida Bureau of Radiation Control] of an overdose of radiation treatment to a female 60 year-old Caucasian patient. Patient was prescribed ten 340 cGy planning target volume (ptv) fractionated treatments: 2 per day for 5 days. Minimum dose of 340 cGy per fraction, mean dose value 625 cGy per fraction, actual dose administered 1167.3 cGy in single fraction. Source S/N: 24-01-7403-001-032119-13092-68. Licensee has notified the patient that an overdose did occur, and expects no harm to the patient due to this fraction of treatment. Patient has five more treatments." The machine used was a Varying GammaMed+, SN 641053, using a 7.385 Ci Iridium-192 GammaMed 232 source. Florida Incident number: FL19-071 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-05-31
54081 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2019-05-22 23:48 | 2019-05-23 01:19 | 2019-05-23 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability occurred which could allow access to a protected area for which compensatory measures were not employed. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/23/2019 AT 0256 EDT FROM JONATHAN LAUF TO JOANNA BRIDGE * * * Security measures have since been re-established. Notified R4DO (Gepford) and 73.71Safeguards Group (e-mail). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-05-23
54080 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2019-05-22 11:15 | 2019-05-22 17:49 | 2019-05-22 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the state of Oregon via email: "[The licensee] was asked to perform density testing of the roadway at the intersection of US Hwy. 26 and SE Firwood in Sandy, Oregon. [The licensee's client], Fall Line Construction, is working for DEPCOM Power. "At approximately 1115 [PDT], [the gauge user] was asked to move [his] vehicle by the construction workers onsite. [The user] moved the Nuclear Densometer to a place where [he] believed would be safe from equipment onsite. "While [the user] was parking (approximately 400 feet away), [he] saw some construction workers waving down the bulldozer operator who had backed into [the] Nuclear Densometer. "[The user] checked to see if the gauge had been damaged. The lead shield had not been damaged. The handle for the gauge had been bent. Due to this deformation, the [source] was stuck in the safe position. "[The user] tested the gauge with [a] Geiger counter and there appeared to be no excessive radiation coming from the gauge. "The gauge was loaded back into the transport box and returned to the permanent storage place. The gauge will be sent out for repair either today or tomorrow." The gauge is a Troxler model 3440, SN 26146, containing 9 mCi of Cs-137 and 44 mCi of Am-241:Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2019-05-30
54079 | 0 | SSM INDUSTRIES |  |  |  |  | 2019-05-10 | 2019-05-22 15:43 | 2019-05-22 | PART 21 NOTIFICATION FOR HYTORK MODEL XL1126 ACTUATORS Excerpts from the SSM Industries fax notification: "On May 10, 2019, SSM Industries, Inc. discovered, during electronic research of literature for Hytork actuators, that an Important Product Safety Notice (safety notice) was issued by Emerson Valve Automation/Hytork concerning Hytork models XL 1126 and XL 1371 pneumatic rack and pinion actuators, manufactured after 2005 and before June 2015. Emerson stated that a model XL 1371 actuator developed a crack in the side wall just underneath the dual stroke adjustment (DSA) pad. "SSM immediately reviewed all projects supplied with Hytork actuators. SSM Industries, Inc. supplied a total of three (3) Hytork model XL 1126 actuators as part of the specialty ventilation dampers manufactured for the nuclear industry. These damper actuators were dedicated by SSM Industries, Inc. at that time and were provided as Safety Related. One (1) of the damper actuators was supplied to Dominion Millstone Nuclear Plant and two (2) were supplied to Dominion North Anna Nuclear Plant. Both utilities have been notified. SSM Industries, Inc. was informed by both utilities that all three actuators were visually inspected and no cracks were discovered. On May 22, 2019 SSM Industries, Inc. made the determination that the defect was reportable under 10 CFR 21. "SSM Industries, lnc. will send Hytork Brace Mechanisms to the aforementioned customers in accordance with the Emerson safety actions. This ensures the safety and integrity of the existing actuators. "SSM Industries, Inc. has ordered Hytork XL 1127 replacement actuators for immediate replacement of installed XL 1126 Hytork actuators. Expected delivery of these actuators is anticipated to be less than 4 weeks. "For additional information please contact the following SSM Industries, Inc. personnel. "Matt Gorman, SSM Power Division Manager: (412)777-5100 Ext 320 (Office); mgorman@ssmi.biz (e-mail), Lou Reda, SSM QA Manager; (412)777-5100 Ext 382 (Office); lreda@ssmi.biz (e-mail)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-05-22
54078 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2019-05-22 02:56 | 2019-05-22 06:01 | 2019-05-22 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On 5/22/2019, the 'A' Control Structure Chiller (Div I) tripped due to a loss of [motor control center] MCC 0B136. The 'B' Control Structure Chiller was already inoperable due to Div II [Emergency Service Water] ESW being out of service for planned maintenance. With the loss of Control Structure HVAC System the ability to maintain temperatures in various spaces including relay rooms, Control Room Floor Cooling and Emergency Switchgear rooms was lost. The 'B' Control Structure Chiller was restarted at 0251 EDT and cooling was reestablished to the required areas, however the 'B' chiller is not considered operable at this time. "Units 1 and 2 entered [Technical Specification] TS 3.0.3 at 0256 EDT and a controlled shutdown of both units commenced, Unit 2 at 0340 EDT and Unit 1 0350 EDT. "This constitutes a TS required shutdown and requires a 4 hour [Emergency Notification System] ENS notification in accordance with 10 CFR 50.72(b)(2)(i). The failure also requires an 8 hour ENS notification in accordance with 10 CFR 50.72(b)(3)(v) due to the loss of a safety function." The licensee needs to restore the 'B' loop of ESW to exit the Limiting Condition of Operation (LCO). The licensee is currently performing a flow surveillance, once complete and assuming the data is acceptable, the licensee will be able to exit the LCO. The units are in a normal electrical lineup. The licensee will be notifying the state of Pennsylvania FEMA Operations Center. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 05/22/2019 AT 1302 FROM SCOTT MYRTHEL TO THOMAS KENDZIA * * * "On 5/22/2019 at 0601 EDT Susquehanna Steam Electric Station reported a shutdown had been commenced at 0340 EDT for Unit 2 and 0350 EDT for Unit 1 due to inoperability of both control structure chillers. Power has been restored to MCC 0B136, and at 0901 EDT the 'A' control structure chiller was declared operable and LCO 3.0.3 was exited. Power reduction for both units was halted at 0901 EDT and preparations for power restoration initiated. As of 1255 EDT on 5/22/2019, Unit 1 power is 94% and Unit 2 power is 92%." Notified the R1DO (Arner). | 80 | 80 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2019-05-22
54077 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-05-22 02:33 | 2019-05-22 05:45 | 2019-05-22 | MANUAL REACTOR TRIP DUE TO FAILURE OF MAIN FEEDWATER REGULATING VALVE "On May 22, 2019, at 0233 EDT, Watts Bar Nuclear Plant (WBN) Unit 2 reactor was manually tripped due to a failure of the #2 Main Feedwater Regulating Valve during power ascension following a refueling outage. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and Steam Dumps. Unit 2 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B). "There was no impact to WBN Unit 1. "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-05-22
54076 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2019-05-21 16:55 | 2019-05-21 18:45 | 2019-05-21 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability occurred which could have allowed access to a protected area for which compensatory measures were not employed. Security measures have since been re-established. The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-05-21
54075 | -1 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2019-05-20 18:33 | 2019-05-21 17:14 | 2019-06-06 | POTENTIAL MISSED SURVEILLANCE FOR ISFSI "At approximately 1833 EDT on 5/20/2019, VC Summer Nuclear Station identified a potential missed surveillance of the Spent Fuel Storage Canister Heat Removal System Surveillance Requirement (SR) 3.1.2. This is a surveillance requirement in the Holtec CoC No. 1032 Amendment 0, Revision 1 for the HI-STORM FW. It was identified that the station suspended verifying all overpack inlets and outlets were free of blockage from solid debris or floodwater every 24 hours and began utilizing the alternate surveillance method of installed temperature monitoring equipment. However, this monitoring equipment had not been declared operable from the completion of the Dry Cask Storage Campaign on April 11, 2019. This surveillance was last performed satisfactorily on May 15, 2019. "The station has documented this missed surveillance in the Corrective Action Program under CR-19-01866. "The NRC Senior Resident has been notified." The licensee stated that the temperature monitoring equipment while not operable, was functional. The licensee successfully performed the surveillance requirement on 5/21/2019. * * * RETRACTION FROM BETH DALICK TO RODNEY CLAGG AT 0828 EDT ON 6/6/19 * * * "ENS Event Number 54075, made on May 21, 2019, is being retracted. "NRC Notification 54075 was made to ensure the 24-Hour Non-Emergency reporting requirement of 10 CFR 72.75(d)(1)(i) was met for a potential missed surveillance of the Spent Fuel Storage Canister Heat Removal System Surveillance Requirement (SR) 3.1.2. "On June 4, 2019, a Past Operability Evaluation determined the temperature monitoring equipment, utilized to complete the Technical Specification Surveillance 3.1.2, was operable during the time period of 5/16/2019-5/21/2019. The station performed satisfactory calibration checks on the temperature monitoring equipment and had not experienced any significant weather events capable of producing vent blockage (i.e. flood, tornado, snow storm, etc.). Therefore, utilizing the installed temperature monitoring equipment is not considered a missed surveillance of SR 3.1.2 and renders this event not reportable under 10 CFR 72.75(d)(1)(i). "VCSNS's evaluation of this event is documented in the Corrective Action Program in Condition Report (CR-19-01866). "The licensee has notified the NRC Resident Inspector." Notified R2DO (Rose) and NMSS Events Notification (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 72.75(d)(1) |  |  |  | 0 | 2019-05-21
54074 | 0 | WIGHTMAN AND ASSOCIATES |  |  |  |  | 2019-04-25 15:30 | 2019-05-21 14:05 | 2019-05-22 | SOURCE LOST FROM TROXLER DENSITY GAUGE DURING USE The following is a summary of a phone call with the licensee: On April 25, 2019, the licensee was using a Troxler Model 3440 density gauge, serial number 24233, with (per Troxler literature) an 8 mCi Cs-137 and a 40 mCi Am-241/Be source, on a project. The technician using the gauge noted the gauge was giving different than expected readings and stopped using the gauge. The gauge was taken to a repair facility to be checked out. On May 21, 2019, the repair facility notified the licensee that the source was found to be missing on May 20, 2019, at approximately 1700 EDT. The licensee has notified NRC Region 3 Inspector (Gattone), the State of Michigan, and the Berrin County Police. The licensee and Berrin County HazMat are trying to locate the source. Region 3 Inspector (Sulaiman) is headed to the site. * * * UPDATE ON 05/22/2019 AT 1135 FROM BOB GATTONE (NRC) TO JEFFREY WHITED * * * The NRC Region 3 Inspector (Gattone) requested that the licensee provide a certificate for the Cs-137 source that was lost. After receiving the certificate, it was determined that the current source activity is 4.5 mCi. Notified R3DO (Cameron), ILTAB, NMSS Event Notification, CNSC, and NRC Region 3 Inspectors Gattone and Sulaiman via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-05-29
54073 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2019-05-19 18:09 | 2019-05-20 00:02 | 2019-05-20 | LOSS OF THE SAFETY PARAMETER DISPLAY SYSTEM DUE TO INVERTER FAILURE "On May 19, 2019, at 1809 CDT, the Safety Parameter Display System (SPDS) was lost to both Arkansas Nuclear One Units 1 and 2 due to the SPDS Inverter (2Y-26) failure. The SPDS Inverter is the power supply to both units' SPDS. The Unit 2 Control Room dispatched operators in response to a smoke alarm received from the 2Y-26 Inverter room. Upon arrival, smoke was reported emanating from 2Y-26. There was no report of fire at any time. Field operators de-energized 2Y-26 and the smoke ceased. The loss of SPDS also caused the Power Operating Limits (POL) function of the Unit 2 Core Operating Limits Supervisory System (COLSS) to be lost, so Unit 2 reduced power to 91 [percent] in accordance with Technical Specifications. Both units are at power and stable. "The NRC Resident has been notified. "This is reportable per 10 CFR 50.72(b)(3)(xiii)." | 100 | 91 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-05-20
54072 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2019-05-18 11:08 | 2019-05-18 14:00 | 2019-05-18 | MANUAL REACTOR TRIP DUE GRID DISTURBANCE "This is a non-emergency notification to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a valid actuation of the Reactor Protection System (RPS) (four hour notification) and 10 CFR 50.72(b)(3)(iv)(A) for a valid Engineered Safeguards (ESF) actuation (eight hour notification) due to Auxiliary Feedwater (AFW) initiation. "Unit 3 manual reactor trip following grid disturbance." Following the grid disturbance, a manual reactor trip was initiated due to lowering steam generator water levels. All control rods fully inserted. AFW started as expected. All other systems responded as expected. Current reactor temperature is 547 degrees F. Current reactor pressure is 2235 psig. Decay heat is being removed through the Atmospheric Steam Dumps (no known primary to secondary Reactor Coolant System leakage exists). The unit is in a normal post-trip electrical lineup. There was no affect on Unit 4. The cause of the grid disturbance is under investigation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-05-18
54071 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2019-05-17 23:03 | 2019-05-18 02:09 | 2019-05-18 | MANUAL REACTOR SCRAM DUE TO DEGRADING CONDENSER VACUUM "On Friday, May 17, 2019 at 2303 [EDT], with the reactor at 70 [percent] core thermal power, Pilgrim Nuclear Power Station initiated a manual reactor scram due to degrading condenser vacuum as a result of the trip of Seawater Pump B. All control rods inserted as designed. The plant is in hot shutdown. "Plant safety systems responded as designed. Pressure is being controlled using the Mechanical Hydraulic Control System and Main Condenser. Reactor water level is being maintained with the feedwater and condensate system. During the manual reactor scram, the plant experienced the following isolation signals as designed: "Group 2 Isolation: Miscellaneous containment isolation valves Group 6 Isolation: Reactor Water Clean-up Reactor Building Isolation Actuation "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'any event that results in actuation of the reactor protection system (RPS) when the reactor is critical...' This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section...' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs).' "This event has no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified. The licensee will notify the Massachusetts Emergency Management Agency." | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-05-18
54070 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-05-14 16:20 | 2019-05-17 08:06 | 2019-05-17 | AGREEMENT STATE - UNATTENDED GAUGE DAMAGED BY BULLDOZER The following was received via e-mail: "On May 14, 2019, at approximately 1620 [EDT] Kentucky Transportation Cabinet, (KY RML# 201-086-51) reported that a Humboldt 5001 EZ, serial number 3133 moisture density gauge had been severely damaged and partially buried by a bulldozer, at a road construction project in Madison County located near Richmond KY. The gauge contained 0.37 GigaBq (10 milliCi) Cesium-137 (serial number 8273GQ) and 1.48 GigaBq (40 milliCi) Americium-24:Beryllium (serial number NJ03357). The technician had been taking some readings, while waiting for more rock to be put in place and put the device in safety mode and set it on top of pile of Dense Graded Aggregate. He then walked over about 80 feet to talk to an operator when it was run over by a bulldozer. KY Radiation Health Branch personnel were on the scene at approximately 1800 [EDT] and determined that the top of the source rod had been broken off and the outer case of the gauge was cracked. There was no leakage detected and the survey of the broken case showed readings = 10mR/hr on contact indicating that the shielding had not been compromised. The area was taped off in a 30 foot circle surrounding the damaged device till it was recovered by the Fayette County HAZMAT Team and placed into a 55 gallon drum, sealed and removed to a storage facility. The Radiation Safety Office indicated that a final decision on the disposition of the gauge will be forthcoming, and that retraining of the employee would be a priority, to include emphasis on surveillance and situational awareness at jobsites." KY Event No.: KY190005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-05-27
54069 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2019-05-16 23:03 | 2019-05-17 03:35 | 2019-06-05 | REACTOR TRIP DUE TO SOURCE RANGE HI FLUX SIGNAL "This is an 8-hour, non-emergency notification for a valid reactor trip signal with the reactor not critical, and a valid auxiliary feedwater system actuation in accordance with 10 CFR 50.72(b)(3)(iv)(A) - Valid System Actuation. "At 2303 [CDT] on May 16, 2019, the plant was administratively in mode 2 due to withdrawing control rods for startup following refuel. The reactor had not been declared critical. The P-6 permissive at 10E-10 Amps was met for one of two Intermediate Range detectors allowing for block of the Source Range high flux trip (1E5CPS). Prior to performing the block, the Source Range high flux trip setpoint was exceeded and a reactor trip received. All systems responded as expected. A feedwater isolation signal was received due to the reactor trip with feedwater temperature less than 564 degrees Fahrenheit. Auxiliary feedwater was started to maintain steam generator levels. The plant is being maintained stable in mode 3 with no complications. The NRC Resident Inspector was present during the startup and was notified of the reactor trip." * * * UPDATE FROM JONATHAN LAUF TO HOWIE CROUCH AT 1454 EDT ON 6/5/19 * * * "A correction is being made for the sixth sentence in the second paragraph above, which states, 'A Feedwater Isolation signal was received due to the reactor trip with feedwater temperature less than 564 degrees Fahrenheit.' Within this sentence, 'feedwater temperature' is to be replaced with 'reactor coolant system temperature.'" The licensee has notified the NRC Senior Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-05-17
54068 | 0 | WATERFORD | 3 |  |  | [3] CE | 2019-05-16 13:48 | 2019-05-16 18:07 | 2019-05-16 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "This is a non-emergency notification from Waterford 3. "On May 16, 2019, at 1348 CDT, Waterford 3 experienced an automatic reactor trip due to Steam Generator number 1 high level, which was the result of a Main Turbine trip and subsequent reactor power cutback which had occurred at 1345 CDT. The cause of the Main Turbine trip is currently under investigation. "Subsequent to the Reactor trip, Main Feedwater Isolation Valves number 1 and number 2 closed on high Steam Generator levels. Emergency Feedwater automatically actuated for Steam Generator number 2 at 1419 CDT and Steam Generator number 1 at 1425 CDT. Main Feedwater was restored to both Steam Generators by 1629 CDT. "The plant entered the Emergency Operating Procedure for an uncomplicated reactor trip and is in the process of transitioning to the normal operating shutdown procedure. The plant is currently in Mode 3 and stable with Main Feedwater feeding and maintaining both Steam Generators. "The NRC Senior Resident Inspector has been notified." All control rods fully inserted. Decay heat is being removed through the main condenser. The plant is in a normal shutdown electrical lineup. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-05-16
54067 | 0 | ALL WEST TESTING & ENGINEERING |  |  |  |  | 2019-05-15 10:30 | 2019-05-16 10:29 | 2019-05-16 | NUCLEAR DENSITY GAUGE DAMAGED BY VEHICLE At 1030 MDT, on 5/15/2019, a Troxler gauge was damaged by a vehicle driving at a high rate of speed through a job site in Middleton, ID. The gauge was damaged and the source and rod disconnected from the gauge base. The on site technician contacted the radiation safety officer who arrived on-site to investigate the incident. The gauge area was quarantined, the area surveyed and the damaged equipment was placed into a container and shipped back to the office while it awaits leak testing prior to returning the gauge to the vendor. The area surveyed after the gauge was removed indicated that there was no surface contamination. The licensee filed a police report and documented the issue. The gauge was a Troxler model 3444 Serial Number: 35061 Isotopes: Cs-137, 8 milliCuries; Am-241, 40 milliCuries The licensee contacted the Region IV office (VonEhr). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-05-24
54066 | 0 | FL DIVISION OF EMERGENCY MANAGEMENT |  |  |  |  | 2019-05-16 | 2019-05-16 00:54 | 2019-06-06 | AGREEMENT STATE REPORT - TRANSPORTATION ACCIDENT The following is a summary of an e-mail received from the State of Florida: On May 15, 2019 at 2327 EDT, the Florida Division of Emergency Management, Radiation Control Duty Officer, contacted the NRC via e-mail to report that all westbound lanes of East Colonial Drive, in Orlando FL, were closed and the entrance and exit ramps to/from State Route 417 were closed. The State Trooper on scene reported that there was a potential release of an unknown quantity of medical grade radioactive material, Molybdenum-99. This material is used in the treatment of cancer. Orange County HAZMAT was dispatched to the scene and requested a call back for assistance. A state inspector was dispatched to the scene. The inspector found no damage to the radioactive material and no contamination. The material was housed in a lead lined box, surrounded by styrofoam, in a cardboard shipping container. There was one person reported with minor injuries due to the crash. Florida Report No.: 2019-2728 Notified DOT Crisis Management Center, DOE and DHS SWO. * * * UPDATE ON 6/6/2019 AT 1718 FROM STATE OF FLORIDA TO RODNEY CLAGG * * * "Vehicle accident occurred around 2215 EDT on the west bound side of East Colonial Drive at the south bound exit ramp of the 417 involving medical radioisotopes. Tradewind Enterprises Inc (Hillsboro, OR; 503-648-2823) courier vehicle was a small SUV with radioactive placards carrying three packages of Mo-99 in the back of the SUV. Contact cell phone numbers for Orange County Fire are 407-402-8532 and 407-383-9806. State of Florida inspector responded. The boxes did not leave the vehicle nor sustain any damage nor was there any leakage of radioactive material. Surveys of packages showed all within Tl [transportation index], swipes indicated no removable contamination. Custody of packages was taken by driver's supervisor. This incident is closed." Notified R1DO (Carfang) and the NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-05-30
54065 | 0 | JAN XRAY SERVICES |  |  |  |  | 2019-05-14 13:24 | 2019-05-15 11:11 | 2019-05-15 | RADIOGRAPHY SOURCE STUCK IN EXPOSED POSITION On May 14, 2019, at 1324 EDT the Radiation Safety Officer (RSO) was contacted by the Operation Manager and informed that a source located at a site in Muskegon MI could not be returned to the shielded position by the normal means. The technicians verified the boundary to ensure no unplanned exposure. The RSO called the site technician and went through the source retrieval procedure. The source was a SPEC model 150 camera with 89 Ci Ir-192 source. The RSO went to the site and was able to determine the location of the source and put temporary shielding on it. The RSO determined the source tubing was crimped and was able to straighten the tube. The source was retracted into the camera and locked by 1550 EDT. The crimped tubing was replaced with new tubing. The device was tested satisfactorily. There were no over exposures. The doses received during the radiography and retrieval process were: RSO 28 mR, Radiography 23 mR, and Assistant Radiography3 mR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-05-23
54064 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-05-14 21:51 | 2019-05-15 02:21 | 2019-05-15 | VOLTAGE TRANSIENT DUE TO LOSS OF OFFSITE SWITCHYARD "At 2151 CDT, on 14 May 2019, Comanche Peak Nuclear Power Plant (CPNPP) experienced a voltage transient within the onsite 138kV switchyard due to the loss of one of the offsite switchyards supplying power to the CPNPP 138kV switchyard. The reduction in safeguards bus voltage due to the transient caused the Unit 2 safeguard busses to load shed and perform a slow transfer to power supplied from 345kV transformer XST2A. Unit 2 was subjected to actuation of both blackout sequencers causing an automatic start of both motor driven Auxiliary Feedwater (AFW) pumps as well as the turbine-driven AFW pump. "No emergency diesel generators started by design. All AFW pumps have been returned to standby status. All other safety systems functioned as designed. Unit 1 is currently defueled, and was unaffected by this event. "The licensee has notified the NRC resident inspector." | 0 | 92 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-05-15
54063 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2019-05-10 16:00 | 2019-05-13 13:40 | 2019-05-13 | AGREEMENT STATE REPORT - SHUTTER STUCK IN OPEN POSITION The following was received via e-mail: "On May 13, 2019, the Wisconsin Department of Health Services (DHS) was notified by the licensee TC Transcontinental that at around 1600 CDT on Friday, May 10, 2019, a shutter got stuck in the open position. A ThermoFisher technician was on site doing regular maintenance checks on a Kr-85 Thermo EGS Gauging Model TFC-185 when the shutter got stuck in the open position. The licensee cordoned off the area to prevent unauthorized access to the vicinity. "ThermoFisher was on site Saturday, May 11, 2019 and repaired the stuck shutter. The shutter now opens and closes as expected. "The Wisconsin DHS will perform a reactive inspection with the licensee." Event Report ID No.: WI 190004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2019-05-21
54062 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-05-12 10:39 | 2019-05-12 15:28 | 2019-05-12 | REACTOR SCRAM DUE TO PARTIAL LOSS OF SERVICE WATER "At 1039 CDT the reactor was manually [scrammed] due to a partial loss of plant service water. The loss of plant service water was caused by a loss of [balance of plant] BOP transformer 23. Reactor power was reduced in an attempt to restore pressure to plant service water. Reactor level is being maintained with condensate and feedwater. Reactor pressure is being maintained with bypass control valves. Standby Service Water A and B were manually initiated to supply cooling to Control Room A/C and [Engineered Safety Feature] ESF switchgear room coolers. The cause is under investigation. "The NRC Resident Inspector has been notified. "This event is being reported under 10 CFR 50.72(b)(2)(iv)(B) as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical and also reported under 10 CFR 50.72(b)(3)(iv)(A), as any event or condition that results in actuation of RPS and Standby Service Water." The plant is currently in a normal electrical lineup. * * * UPDATE ON 5/12/19 AT 1846 EDT FROM GERRY ELLIS TO JEFFREY WHITED * * * "This is an update to the original notification. "The Drywell and Containment exceeded the technical specification (TS) temperature limits of 135 degrees F [TS Limiting Condition of Operation (LCO) 3.6.5.5] and 95 degrees F [TS LCO 3.6.1.5], respectively. "An 8-hour notification is being added for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material per 10 CFR 50.72(b)(3)(v)(C)." Notified R4DO (Alexander). | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | POT UNCNTRL RAD REL |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(C) |  | 0 | 2019-05-12
54061 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2019-05-11 23:05 | 2019-05-12 04:51 | 2019-05-12 | DISCOVERY OF A CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "On 5/11/19, Callaway Energy Center entered Mode 4 at 1217 [CDT]. At 2305, the door from the Auxiliary Building to the RAM Storage building was found blocked open. This door is an Auxiliary Building pressure boundary for the Emergency Exhaust system. The Emergency Exhaust system is required in Modes 1,2,3,4, and during movement of irradiated fuel assemblies in the Fuel Building. The door was being blocked open with a large ramp. This rendered the Emergency Exhaust system not capable of performing its design safety function. LCO [Limiting Conditions for Operation] 3.7.13.B was entered, and preparations to move the ramp commenced. LCO 3.7.13.B is for two Emergency Exhaust trains being inoperable due to an inoperable auxiliary building boundary. The allowed outage time is 24 hrs. to restore the boundary to Operable. The door was closed and LCO 3.7.13.B was exited at 0111 on 5/12/19. "This event is reportable per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (C) control the release of radioactive material, or (D) mitigate the consequences of an accident. "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-05-12
54060 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2019-05-10 07:20 | 2019-05-10 15:30 | 2019-05-10 | PROHIBITED SUBSTANCE INSIDE THE PROTECTED AREA "At 0720 CDT [on 5/10/19], security was notified of a prohibited item (un-opened alcohol container) reported in the protected area. Security assumed escort of the non-supervisory [contract] individual and took custody of the prohibited item." The employee's access to the plant has been suspended. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2019-05-10
54059 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-05-07 | 2019-05-10 14:55 | 2019-05-10 | AGREEMENT STATE REPORT - UNDER ADMINISTRATION OF PRESCRIBED DOSE DURING MEDICAL PROCEDURE The following was received via a telephone report from the Kentucky Department of Radiation Control: The Kentucky Department of Radiation Control was notified by the University of Kentucky Medical Center in Lexington, Kentucky, that on 05-07-2019 they had a medical event. During a Sirtex Therapy procedure, which uses Y-90 microspheres, less than 20 percent of the prescribed dose was delivered. Investigation continues. Kentucky Event Report ID No.: KY190004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-05-20
54058 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2013-09-26 | 2019-05-10 14:44 | 2019-05-10 | AGREEMENT STATE REPORT - IMPROPER DISPOSAL OF RADIOACTIVE MATERIAL The following information was excerpted from an email received from the State of Louisiana: On 8/15/2018, the radiation safety officer (RSO) at NASA's Michoud Assembly Facility (NASA-M) discovered a dew point device containing a radioactive source was sent to a recycling center for disposal. The recycler was UNICOR Recycling Factory (UCF) in Marinna, FL. UCF was not licensed to receive radioactive material. The dew point device with the source was sent to UCF for disposal on 9/26/2013. The RSO reported the disposal to the Louisiana Department of Environmental Quality, as a lost source and unreported release of radioactive material, on 5/9/2019. UCF was contacted my NASA-M for records and documentation, but UCF stated they did not have any records/documentation for that device disposal. The device was an Alnor Instrument Co.; Type 7000U Dew Point Determination device with a 35 microCi Am-241 source (serial number 25829). Louisiana Event Report ID No.: LA-190007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-05-20
54057 | 0 | QUEENS MEDICAL CENTER |  |  |  |  | 2019-05-08 13:17 | 2019-05-09 18:08 | 2019-05-09 | ADMINISTRATION OF LESS THAN PRESCRIBED DOSE "This was a Y-90 TheraSphere administration [120 Gy to the right lobe of the liver]. The catheter was guided to the right hepatic artery and the position was verified by fluoroscopy. No issues with catheter flow while administering contrast and normal saline. The catheter was connected to the primed infusion system and the dose delivery was initiated. The IR (Interventional Radiology) physician, under the supervision of the Authorized User, was delivering the dose. The IR physician saw several small air bubbles in the delivery line and then experienced high resistance. Some of the Y-90 activity (approximately 13.2 mCi or 0.49 GBq) was delivered to the patient. Approximately 60% of the activity was in the administration set and catheter. No contamination of the IR suite or of any of the personnel occurred. All of the dose was either in the delivery system/catheter or the patient. "No harm was done to the patient since the activity was delivered to the target organ and the dose did not exceed the prescribed dose. "The referring physician and the patient were notified within 24 hours." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 35.3045(a)(2) |  |  |  | 0 | 2019-05-17
54056 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2019-04-24 16:30 | 2019-05-09 15:19 | 2019-05-09 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER FAILED CLOSED The following was received via e-mail: "On April 24, 2019 at about 4:30 PM [MDT], the RSO [Radiation Safety Officer] for Kennecott Copper Corporation called and notified a DWMRC [Utah Department of Environmental Quality, Division of Waste Management and Radiation Control] staff member that one of their gauges was not working properly. The licensee reported that the shutter on a fixed gauge, an Ohmart Vega, model number SH-F2, serial number 68852, containing 800 mCi of Cs-137 in a sealed source did not open when a shutter test was conducted. The licensee stated that the gauge would be left in place for now and removed and cleaned the next week, to see if that resolved the problem. The RSO reported that he would engage a licensed provider if disassembly is required to fix the problem. "Another [DWMRC] staff member spoke to the licensee's RSO at about 5:00 PM that evening. The licensee's RSO indicated that they did not have the information regarding the gauge with them at the time but that they believed the gauge just needed to be cleaned. The licensee indicated that the gauge had not been in use for a while and that they were testing the device prior to putting the device back into operation when the issue was discovered. The gauge is located in an area difficult to access. The licensee would need to use certain equipment to safely reach and remove the gauge. The RSO had tried to contact their regular gauge service licensee and determined that the service licensee would not be available until after May 1, 2019. The RSO indicated that they would remove and clean the gauge the following week. "Specific individuals on the licensee's radioactive materials license are authorized to install and remove gauges and the extra time would allow the RSO to ensure that the appropriate individuals were available. On April 30, 2019, the licensee's authorized personnel removed the gauge from its location at the pebble crusher. After a thorough cleaning of the exterior of the source housing, the shutter was still showing no movement. "The RSO realized the gauge needed to be taken apart and cleaned in order to allow the shutter to work properly. The service licensee was contacted and arrangements were made for the service licensee to work with the gauge on May 2, 2019. The device was stored in a properly secured area at any time it was not under the licensee's constant surveillance until the service licensee took possession of the device. The licensee informed the DWMRC that they would provide a report regarding the outcome." Event Report No.: UT190002 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2019-05-17
54055 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2019-05-09 09:16 | 2019-05-09 13:51 | 2019-05-09 | EMPLOYEE SUPERVISOR TESTED POSITIVE ON A RANDOM FITNESS-FOR-DUTY TEST A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the site has been terminated. The NRC Resident Inspector has been informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2019-05-09
54054 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2019-05-09 03:48 | 2019-05-09 07:01 | 2019-05-09 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "On May 9, 2019 at 0348 CDT, an automatic scram was received on Unit 2 following a turbine trip. "All rods inserted to their full-in positions. "All Group 2 and Group 3 automatic isolations actuated as expected. Systems operated as expected. "Reactor vessel inventory and pressure are being maintained in normal control bands. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical. "The NRC Resident Inspector has been notified." Decay heat is being removed using the steam bypass valves to the condenser and the safety relief valves did not lift as a result of the trip. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-05-09
54053 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2019-04-26 15:00 | 2019-05-07 13:57 | 2019-05-07 | AGREEMENT STATE REPORT - LOST CALIBRATION SOURCES The following was received via e-mail: "During a routine [Utah Division of Radiation Control] inspection on April 26, 2019, the licensee discovered that two planchet sources containing radioactive materials were missing from its secured laboratory. The sources were used to calibrate a wipe counting system that the licensee rarely used. One source contained 9.9 nanoCuries of strontium-90 (Sr-90) and the other source contained 17.81 nanoCuries of plutonium-239 (Pu-239). The activity of the Sr-90 source was well below the exempt quantity threshold. The inspector gave the licensee until May 3, 2019, to search for the sources and to let the inspector know the results of the search. On May 2, 2019, the licensee informed the Division that, after an exhaustive search, the licensee had failed to locate the sources. Following a review of the applicable rules by Division staff on May 6, 2019, the inspector verified with the licensee that the sources were still missing and informed the licensee of the incident notification requirements and the anticipated enforcement activities to be taken by the Division." Event Report No.: UT190001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2019-05-15
54052 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-05-06 22:04 | 2019-05-06 22:49 | 2019-05-07 | NOUE DUE TO FIRE LASTING LONGER THAN 15 MINUTES IN TURBINE BUILDING At 2204 EDT on 5/6/19, a Notification of Unusual Event (NOUE) was declared due to a fire lasting greater than 15 minutes. The fire occurred in the '2B' Heater Drain Pump motor located in the turbine building. The fire was extinguished following initial Emergency Declaration. There were no releases to the environment. Unit 1 was unaffected by the event and remains in Mode 1 at 100 percent power. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 5/7/19 AT 0002 EDT FROM MICHAEL BRADEN TO BETHANY CECERE * * * The NOUE was terminated as of 2359 EDT on 5/6/19. No off-site resources were required to extinguish the fire. The turbine building is now free of smoke. The licensee will notify the NRC Resident Inspector, State of North Carolina, Brunswick County, New Hanover County, and the Coast Guard. Notified R2DO (Heisserer), NRR EO (Miller), and IRD (Gott). Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2019-05-06
54051 | 0 | UNIVERSITY OF MICHIGAN |  |  |  |  | 2018-11-30 | 2019-05-06 14:00 | 2019-05-06 | LOST TRITIUM EXIT SIGNS The following is a summary of a phone call with the licensee: After performing an inventory of Tritium exit signs in April of this year, a Senior Health Physicist inquired about the location of two specific missing signs. The Senior Health Physicist found that the building had been under renovation in 2018 and a contractor likely removed the two exit signs in November, 2018. The licensee is currently waiting on information from the contractor regarding the exit signs. The licensee will be notifying NRC Region III. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-05-14
54050 | 0 | KAKIVIK ASSET MANAGEMENT |  |  |  |  | 2019-05-05 00:18 | 2019-05-05 21:53 | 2019-05-05 | STUCK RADIOGRAPHY CAMERA SOURCE The following information was received via E-mail: "At approximately 0018 YDT on 5/5/2019, a Kakivik radiographic crew working in Alpine, Alaska on drill site CD-4, could not retract a source under normal conditions. Once this was identified the crew initiated emergency procedures by establishing 2mR boundaries and making notifications per O&E procedures. The crew was using a QSA Global 880D device with a model A424-9, 44.6, Ci Ir-192 source along with a 10HVL collimator. The crew had made 15 exposures. The last exposure is when the Radiographer noticed a sudden stop from the drive cable during his retraction and that is what initiated the emergency procedures. At approximately 0308 YDT the source was locked and secured in the 880D device. It was determined that the guide tube was draped low in a 'W' shape at the guide tube extension point which was preventing the source from coming in under normal conditions. The cranks were straightened and a pole was used to raise the guide tube at the extension connection point and the source was retracted in normal conditions. No one was over-exposed and the boundaries were placed at such a distance that the crew and public were safe. It was a four man crew, two of whom received 0mR and the Radiographer and Assistant received 11mR and 8mR, respectively. The emergency response team members received 1mR (two of them) and 3mR (two of them)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-05-13
54049 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2019-05-05 14:05 | 2019-05-05 20:41 | 2019-05-30 | SECONDARY CONTAINMENT DECLARED INOPERABLE DUE TO POTENTIAL EQUIPMENT FAILURE "At 1405 CDT, Secondary Containment differential pressure exceeded the Technical Specification limit due to a potential equipment failure. This required entry into [Limiting Condition of Operation] LCO 3.6.4.1 Condition A for Secondary Containment inoperability. An event or condition that could have prevented the fulfillment of a safety function requires an 8 hour report per 10 CFR 50.72(b)(3)(v)(C) for Control of Rad Release. Secondary Containment differential pressure was restored to greater than or equal to 0.25 inches vacuum, water gauge in accordance with plant procedures. Secondary Containment was declared operable at 1600 CDT. The issue has been entered in the Corrective Action Program and investigation of the cause is in progress. "The NRC Senior Resident Inspector has been informed of this condition." * * * RETRACTION AT 1759 EDT ON 5/30/2019 FROM ROY GILES TO JEFF HERRERA * * * "CNS [Cooper Nuclear Station] is retracting the 8-hour notification made for event 54049 which occurred on May 5, 2019 at 1405 CDT. Subsequent evaluation determined that no equipment failure occurred. In addition, there were no procedure inadequacies or human performance issues identified. The indications observed were expected and part of a pre-planned evolution which included entry into a planned LCO for the Secondary Containment." The NRC Resident Inspector has been notified. Notified the R4DO (Kozal). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-05-05
54048 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-05-03 | 2019-05-03 18:37 | 2019-05-03 | AGREEMENT STATE REPORT - Y-90 UNDERDOSAGE REPORT The following was received via e-mail: "At 1138 PDT on 05/03/2019, the [California Radiation Control Program] received a phone call from the licensee's [Radiation Safety Officer] RSO providing the initial report on a Y-90 radioembolization underdose. Only 76 percent of the planned dose was provided to the organ of interest with the rest having leaked out because of a faulty stopcock assembly. The leak area was contained and cleaned up. All decontamination is complete and the only effect is the underdose to the patient." CA 5010 Number: 050319 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-05-13
54047 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-05-03 15:54 | 2019-05-03 19:00 | 2019-05-03 | AUTOMATIC REACTOR TRIP ON OVER TEMPERATURE DELTA TEMPERATURE "At 1554 EDT on 5/3/19, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped on Over Temperature Delta Temperature following a pressure transient in the Reactor Coolant System. The trip was uncomplicated with all systems responding normally post trip. Operations manually started the motor driven auxiliary feedwater pumps and has stabilized the plant. Decay heat is being removed by the condenser. Unit 2 is not affected. "Due to Reactor Protection System actuation while critical and actuation of the motor driven auxiliary feedwater pumps, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." Unit 1 is in a normal electrical lineup. Prior to the automatic trip, the backup pressurizer heaters were in service as is normal during power ascension. The pressure transient started when the backup heaters were in the process of being removed from service. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-05-03
54046 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2019-05-03 08:52 | 2019-05-03 16:43 | 2019-05-03 | FITNESS-FOR-DUTY REPORT A non-licensed contract supervisor had a confirmed positive during a for-cause fitness-for-duty test. The individual's authorization for site access has been terminated. The NRC Resident has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2019-05-03
54045 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-05-02 | 2019-05-03 15:30 | 2019-05-03 | AGREEMENT STATE REPORT - I-125 SEED LOST The following information was received via e-mail: "On 5/1/19 a patient had two [radioactive seed localization] RSL seeds [200 microCuries; I-125] implanted. The same patient returned the following day for an explant procedure. At that time, it was discovered that one seed was missing from the patient. The licensee confirmed through recorded imaging, consultation with the surgeon, patient surveys, and detailed surveys of the implant site and the explant site that the most likely area where the seed was lost was somewhere in between when the patient left the implant site and returned to the explant site the following day. North Carolina Radioactive Materials Branch has started an investigation that is ongoing at this time. "This event is reportable per 20.2201(a)(1)(ii) - Lost, stolen, or missing licensed material in a quantity greater than 10 times the Appendix C quantities." North Carolina Tracking ID: NC 190016 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-05-13
54044 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-05-02 14:41 | 2019-05-03 11:10 | 2019-05-03 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was received via fax: "On May 2, 2019, at approximately 1441 CDT, [an employee] of Alabama general licensee FMC in Axis, AL notified the Alabama Office of Radiation Control [the Agency] that the leak test results from an [electron capture detector] ECD/gas chromatograph source indicated that the source was leaking (results of 1 microCurie). [The employee] stated that the source was not in use, had been in storage for years, that FMC was preparing the source for transfer/disposal, and that FMC is working with Agilent to prepare the source for shipping. "The Agency did not collect identifying source information before submission of this event. However, the Agency's records indicate that FMC possesses 15 mCi nickel-63 sources only." Alabama Event 19-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2019-05-13
54043 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2019-05-03 06:00 | 2019-05-03 10:55 | 2019-05-03 | AGREEMENT STATE REPORT - BROKEN SHUTTER The following was received via e-mail: "On May 3, 2019, the Department [South Carolina Department of Health and Environmental Control] was notified by the licensee that a shutter had broken on one of its gauges while attempting to close the shutter because of a sprinkler failure that was soaking the area where the gauge was mounted. The gauge is a Kay-Ray Model 70628 containing 10 mCi of Cesium 137. The licensee has contacted Systems Services who is specifically licensed to repair the damaged shutter. The [Radiation Safety Officer] RSO stated that he has performed a radiation survey around the gauge where individuals normally work and the radiation readings are background. Access to the gauge has been restricted and the area has been roped off by the RSO until the service provider comes to fix the shutter. The service provider is scheduled to come May 7, 2019." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2019-05-13
54042 | 0 | INTERNATIONAL ISOTOPES, INC. |  |  |  |  | 2019-05-02 21:30 | 2019-05-03 01:02 | 2019-11-19 | UNPLANNED CONTAMINATION EVENT DUE TO BREACHED CS-137 SOURCE The Radiation Safety Officer (RSO) at International Isotopes, Inc. reported that at 2130 PDT on 5/2/19, while changing out the Cs-137 source on a research irradiator, they breached the source which resulted in widespread contamination and a possible uptake event. The irradiator is a JL Shepard Mark 168A and is located at the Harborview Research and Training Facility at the University of Washington in Seattle, WA. International Isotopes, Inc. is an NRC licensee working under reciprocity in the State of Washington (an agreement state). After discovery of the breach, the immediate area was isolated, the building was ordered evacuated, and the ventilation was secured. Indications are that the seven members of the source retrieval team were externally and potentially internally contaminated. The State of Washington was notified. The University of Washington RSO was sending response teams to the area. A local hazardous material team is on site. The source was reported to be 2800 Ci. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 05/03/2019 AT 1545 EDT FROM TRISTAN HAY TO JEFFREY WHITED * * * The following update was received via E-mail from the Washington State Department of Health: "University of Washington (UW) was having their research irradiator (Mark-1 SERIES / Cs-137) disposed of by International Isotopes (NRC License 11-27680-01MD). The Agreement state regulators were present to verify dose measurements and observe ALARA practices. During the source removal and transfer into the transport shielded cask, there was a breach of the sealed source and a small portion of the source was released into the working area. The working area was comprised of the irradiator unit, the shielded containment rig, the loading dock, a 100 feet radius around the loading dock, and the Harborview Research and Technology Center floors 1-3 and stair well. The source was encapsulated with International Isotopes' source housing capsule. A breach was identified during the precursor wipe survey performed prior to putting it into the source housing unit. Once contamination was identified, all personnel performed area contamination surveys and secured and taped off the work space area. All personnel who were present at some point during the transfer were notified of the potential contamination and were given special instructions to return to the Harborview Medical Center area for decontamination. "Simultaneously the NRC, Washington Radiation Emergency Hotline, and the [National Materials Event Database] NMED were notified of the situation by International Isotopes immediately after the incident occurred. Seattle Fire and Seattle Hazmat units were dispatched to the scene to assess the situation and begin decontamination protocols. The International Isotope workers, UW RSO, FBI agent, and other present workers were decontaminated and placed in a contained area of the Harborview Medical Center Emergency Room. Bioassay samples were collected from urine and blood from the contaminated individuals." Additionally, employees from the State of Washington who responded to the event were surveyed, with the highest level of contamination being 300 cpm on the individual's shoes. Washington State Licensee: University of Washington Washington Agreement State License No. C001 Event Report ID No.: WA-19-015 Notified R4DO (Werner), IRD MOC (Gott), NMSS (Rivera-Capella), and NMSS Events Notification via e-mail, DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 05/04/2019 AT 2136 EDT FROM JOHN MILLER TO JEFFREY WHITED * * * The following update is a synopsis of information received via E-mail from International Isotopes: In its E-mail, the licensee provided an initial incident report regarding the breached Cs-137 source incident that occurred during the removal of the source from the Research Irradiator at the Harborview Training and Research Building. The licensee provided a summary of planned work, a summary of the incident, a summary of the whole-body exposures received by International Isotopes and contractor employees, a summary of initial personnel skin contamination results, a summary of post-decontamination personnel skin contamination results, and a summary of recovery actions taken to date. According to its assessment, the licensee indicated that the highest whole-body exposure to any one individual was 55 mrem. The majority of surveys taken at the loading dock level indicated that surfaces were contaminated in the 50,000 - 300,000 cpm range. The summary of recovery actions taken to date are as follows: International Isotopes hired a contractor to perform decontamination and remediation of the affected areas. The Department of Energy, Region 8, Radiological Assistance Program team surveyed the building floors. International Isotopes employees surveyed the parking lot area where emergency response operations took place reducing the size of the controlled area, marking spots with identified levels. The loading dock area was further isolated from the building by covering outdoor louvers and double door between corridor and loading dock with heavy plastic. International Isotopes remains on-site to support the contractor and the University of Washington by performing assessment surveys and development of the decontamination and recovery plan. Notified R4DO (Werner), IRD MOC (Gott), NMSS (Kock), and NMSS Events Notification via e-mail, DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE AT 1648 EDT ON 05/16/2019 FROM JOHN MILLER TO JEFF HERRERA * * * "This report provides an update to the May 2, 2019 incident involving the breached Cs-137 source. "International Isotopes Inc. (INIS) performed dose estimates based on 24 hour urine samples collected from the INIS employees that were involved in the incident. "There were seven INIS individuals involved, the INIS estimates are provided in the table below. Note that individuals 6 and 7 are not included in the LANL Report as their urine sample results were released later. These sample results have since been provided to LANL. "Name; Time Between intake and sample (days); Concentration (pCi/L); Modeled Intake (uCi); Percent ALI; CED (mRem) "Individual 1: 1.625; 15,700; 2.284; 1.142 Percent; 57.1 Individual 2: 1.396; 6,100; 1.235; 0.618 Percent; 30.9 Individual 3: 1.698; 1,280; 0.186; 0.093 Percent; 4.7 Individual 4: 1.665; 8,540; 1.242; 0.621 Percent; 31.1 Individual 5: 1.697; 19,800; 2.880; 1.440 Percent; 72.0 "Individual 6: 1.687; 5,540; 0.806; 0.403 Percent; 20.1 Individual 7: 1.437; 4,110; 0.624; 0.312 Percent; 15.6" Notified R4DO (Proulx), IRD MOC (Kennedy), NMSS (Rivera Capella), and NMSS Events Notification via e-mail, DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 05/20/2019 AT 1050 EDT FROM STEVE LAFLIN TO THOMAS KENDZIA * * * The following update is a synopsis of information received via email from International Isotopes: International Isotopes provided a detailed update on internal and whole body doses, skin contamination and decontaminated results for the affected seven individuals. The highest internal dose was 57.1 mrem for individual 1, the highest whole body dose was 55 mrem for individual 7, and the highest dose to the skin from skin contamination was 36 mrem to individuals 3 and 4. Blood sampling of the individuals showed no changes due to radiation. Facility decontamination continues. International Isotope management is in the process of conducting a detailed investigation in order to determine the direct, contributing, and root causes of this event. Notified R4DO (Gepford), IR MOC (Kennedy), and NMSS Events Notification via e-mail. * * * UPDATE ON 7/25/2019 AT 1228 EDT FROM TRISTAN HAY TO ANDREW WAUGH * * * The following update is a synopsis of an email from the Washington State Department of Health: In this update the state of Washington provided detailed corrective actions taken and planned for this event and gave the status of current decontamination efforts. The update also states that one of the impacted employees was a University of Washington employee and not a contractor as previously stated. Notified R4DO (Taylor), IR MOC (Gott), and NMSS Events Notification (email). * * * UPDATE ON 11/19/2019 AT 1809 EST FROM STEVE LAFLIN TO THOMAS KENDZIA * * * The following update is a synopsis of information received via email from International Isotopes: International Isotopes (INIS) has completed their portions of the facility decontamination, which is now being run by the Department of Energy (DOE) and Los Alamos National Laboratory. INIS continues to support the DOE accident investigation. INIS investigation report will be delayed until after the DOE Accident Investigation Board report. Notified R4DO (O'Keefe), IR MOC (Kennedy), and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | AGREEMENT STATE | [8 empty] | NON EMERGENCY | 4 | ID | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2019-05-10
54041 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2016-12-06 | 2019-05-02 14:47 | 2019-05-10 | AGREEMENT STATE REPORT - I-125 APPLICATOR LEAK TEST FAILURE The following was received via e-mail: During a Wisconsin Department of Health Services inspection a previously unreported event was discovered. The date of the event is still being determined. "While performing a manual brachytherapy procedure, the Mick applicator became jammed and the licensee switched to a different applicator to finish the procedure. Following the procedure, the [Radiation Safety Officer] RSO wiped the jammed device and found contamination so several I-125 seeds were isolated and held for decay in storage." This indicates that the device failed a leak test, which is a reportable event. * * * UPDATE ON 05/10/2019 AT 1108 EDT FROM JOSEPH ROSS TO JEFFERY HERRERA * * * "On December 6, 2016, while performing a manual brachytherapy procedure, a Mick applicator became jammed when the oncologist was attempting to insert a seed. The radiation oncologist removed the Mick applicator and switched to an extra Mick applicator with a different cartridge of seeds. A surgeon continued implanting seeds with the physicist to finish the procedure. Meanwhile, the radiation oncologist forcefully extracted the cartridge from the jammed Mick applicator. This was when the physicist/RSO believed that a seed was ruptured. Following the procedure, the RSO took the Mick applicator to the nuclear medicine hot lab and wiped the device and cartridge. The RSO found contamination on the seeds/cartridge so thirteen I-125 seeds (.333mCi each) were isolated and held for decay in storage in the hot lab. "There is no indication of contamination in the operating room surveys or any expected uptake by the patient." Notified R3DO (Stoedter) and NMSS Events (via email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2019-05-10
54040 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-05-01 16:43 | 2019-05-01 21:03 | 2019-05-08 | MANUAL REACTOR TRIP DUE TO MISALIGNED CONTROL ROD "At 1643 [CDT], with Unit 2 in Mode 2 during low power physics testing, the reactor was manually tripped per procedure due to a misaligned control rod. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Decay heat is being removed by discharging steam to the atmosphere using the atmospheric relief valves. Unit 1 is not affected. "Due to the Reactor Protection System actuation, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." * * * UPDATE ON 05/08/2019 AT 1212 EDT FROM MIKE CONNER TO JEFFREY WHITED * * * "This Event Notification is being updated to clarify that the reactor was not critical when this event occurred. Therefore, the reporting requirement is changed from 10 CFR 50.72(b)(2)(iv)(B) to 10 CFR 50.72 (b)(3)(iv)(A). "The reactor was tripped during low power physics testing. The misaligned rod was encountered during rod group insertion and the affected bank had been inserted to the extent that the reactor was subcritical when the operators tripped the reactor. "The licensee notified the NRC Resident Inspector." Notified R2DO (Lopez) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-05-01
54039 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-04-30 11:15 | 2019-04-30 15:16 | 2019-04-30 | AGREEMENT STATE REPORT - STOLEN NUCLEAR DENSITY GAUGE The following report was received from the State of California via email: "The RSO [Radiation Safety Officer] of Geolabs reported to the RHB [Radiation Health Branch] that his gauge technician had reported a CPN MC-3 (serial number M37067701) was stolen. The CPN gauge contains 10 milliCuries of Cs-137 and 50 milliCuries of Americium-241, and was inside its Type A transportation container. The technician was transporting the CPN gauge to a temporary job site. The RSO will be contacting the Ventura County Sheriff's Dept. to report the theft and take a statement from the technician. This is an ongoing investigation." California 5010 number: 043019 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-05-08
54038 | 0 | NATIONAL INST OF STANDARDS & TECH |  |  |  | 20000 KW TEST | 2019-04-30 09:00 | 2019-04-30 14:17 | 2019-04-30 | TECHNICAL SPECIFICATION VIOLATION DUE TO USING THE WRONG PROCEDURE "On April 30, 2019 at approximately 0900 EDT at the National Bureau of Standards Test Reactor (NBSR) a Senior Reactor Operator (SRO) was discussing proposed changes to the area radiation monitor system with NBSR Instrumentation and Control personnel. During this discussion, the SRO realized that the surveillance standard for the radiation monitors had changed in September 2018. The Technical Specification 3.7.1(4) states 'The reactor shall not be operated unless: Two area radiation monitors are operable on floors C-100 and C-200'. To verify operability Technical Specification 4.7.1(4)(b) states 'The Area Radiation Monitors shall be channel tested monthly and channel calibrated annually'. The SRO informed the Chief of Reactor Operations (CRO) that they had incorrectly performed the required monthly channel test in December 2018 and January 2019. The channel test was properly performed in November 2018 and February 2019. The Reactor operated between 12/05/2018 and 12/21/2018 and again between 02/05/2019 and 02/15/2019." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | DEVIATION FROM T SPEC | [9 empty] | NON EMERGENCY | 0 | MD | NPR |  | 50.72(b)(1) |  |  |  | 0 | 2019-04-30
54037 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2019-04-29 12:30 | 2019-04-30 07:37 | 2019-04-30 | NON-LICENSED SUPERVISOR FAILED FOLLOW-UP TESTING "A non-licensed employee supervisor had a confirmed positive test for a prohibited substance during a follow-up fitness-for-duty test. The individual's unescorted access to the plant has been terminated. "The NRC Senior Resident Inspector was notified by the licensee." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2019-04-30
54036 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-04-29 20:29 | 2019-04-29 22:50 | 2019-04-29 | OFFSITE NOTIFICATION DUE TO A SPURIOUS ACTUATION OF AN EMERGENCY SIREN "On 4/29/19, at approximately 2029 EDT, the Operations Shift Manager was made aware that the Berrien County Sheriff's Department (BCSD) had been notified of an Emergency Siren that had spuriously actuated. BCSD was notified by local residents. The affected siren has been disabled and it has been verified that all associated local areas still have coverage from other functional emergency sirens. "The cause of the actuation is under investigation at this time. "This notification is being made under 10 CFR 50.72(b)(2)(xi), Offsite Notification, as a four (4) hour report." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-04-29
54035 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2019-04-29 16:33 | 2019-04-29 20:01 | 2019-04-29 | MANUAL REACTOR SCRAM DUE TO POWER OSCILLATIONS AND HIGH PRESSURE COOLANT INJECTION SYSTEM INITIATION "During power ascension on April 29, 2019, at 1630 [EDT], Nine Mile Point Unit 1 power and pressure oscillations were observed with reactor power at approximately 82 [percent]. At time 1633 [EDT], the reactor was manually scrammed when the scram criteria of greater than 4 [percent] APRM power oscillations were observed in accordance with special operating procedures. All control rods fully inserted and all plant systems responded per design following the scram. "Following the manual scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI system actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 1633 [50 seconds after the reactor scram], RPV level was restored above the HPCI System low level actuation setpoint and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. The offsite grid is stable with no grid restrictions or warnings in effect. The cause of the power oscillations is currently under investigation." The NRC Resident Inspector was notified. The New York State public service commission was notified. | 0 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-04-29
54034 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-04-28 06:33 | 2019-04-29 12:19 | 2019-04-29 | CONTROL BLADE INOPERABLE "On April 28, 2019, at 0633 CDT, with the University of Missouri-Columbia Research Reactor (MURR) operating at 10 MW in the automatic control mode, the Lead Senior Reactor Operator (LSRO) was conducting surveillance Technical Specification (TS) 4.2.a, which states, 'All control blades, including the regulating blade, shall be verified operable within a shift.' During this verification of control blade operability, shim control blades 'A,' 'B,' 'C,' and the regulating blade were verified operable. However, shim control blade 'D' would not move in the inward direction. The LSRO then immediately shut down the reactor by initiating a manual scram by placing Master Control Switch 1S1 to the 'TEST' position. The LSRO completed all immediate and applicable subsequent actions of reactor emergency procedure REP-8, 'Control Rod Drive Mechanism Failure or Stuck Rod,' and verified all shim control blades were fully inserted. "This email is a required notification per TS 6.6.c(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by TS 1.1.b, has occurred. MURR was not in compliance with all of the Limiting Conditions for Operations (LCOs) as established in TS Section 3.0. The failure of the control rod drive mechanism to insert shim control blade 'D' is a deviation from TS 3.2.a, which states, 'All control blades, including the regulating blade, shall be operable during reactor operation.' In addition, shim control blade 'D' would not have inserted during the activation of any rod run-in function listed in TS 3.2.f - shim control blades 'A,' 'B,' and 'C' would have inserted. All reactor safety system scram functions were unaffected and remained operable during this event. "Troubleshooting revealed a broken wire to the inward motor winding of shim blade 'D' control rod drive mechanism. The wire was repaired, and the shim control blade 'D's operability was tested satisfactorily. Permission from the Reactor Facility Director was obtained prior to reactor startup per TS 6.6.c(4), and the reactor returned to 10 MW operation at 1319 CDT on April 28. A detailed event report will follow within 14 days as required by TS 6.6.c(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2019-04-29
54033 | 0 | ARIZONA DEPT OF HEALTH SERVICES |  |  |  |  | 2019-04-28 | 2019-04-28 14:57 | 2019-04-28 | AGREEMENT STATE REPORT - THEFT OF CAT 2 MATERIAL The following was received from the state of Arizona via e-mail: "The [Arizona Department of Health Services] received notification that an individual stole [three] industrial radiography cameras and threatened to use them. It is believed that the individual is a current or former worker at the licensee. The isotope is Iridium-192 for all three cameras and the approximate activity amounts are 30 Curies, 49 Curies, and 80 Curies. As of approximately 1120 [MDT], the individual was located, the material was secured, and the [Radiation Safety Office] is waiting to bring the material back to the storage location. The Department has requested additional information and continues to investigate the event. Arizona Incident No.: 19-009 Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and Domestic Nuclear Detection Office Joint Analysis Center (email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf * * * UPDATE ON 4/28/19 AT 1920 EDT FROM BRIAN GORETZKI TO JOANNA BRIDGE * * * The following is a summary of a telephone call: The sources were safely recovered. They were found in the radiography cameras. It is widely believed that the suspect never removed the sources from the shielded cameras. The cameras have been returned to the storage facility. Notified R4RDO (Young), NMSS Events Notification (email), NMSS (Moore), ILTAB (e-mail), CNSNS Mexico (email), IR MOC (Kennedy), ILTAB (Smith), NMSS INES Coordinator (email), INES National Officer (email). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and Domestic Nuclear Detection Office Joint Analysis Center (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-05-06
54032 | 0 | IRISNDT, LLC |  |  |  |  | 2019-04-28 05:45 | 2019-04-28 15:04 | 2019-04-28 | SAFETY EQUIPMENT FAILURE - RADIOGRAPHY SOURCE FAILED TO RETRACT "This report is intended to serve the requirements of written notification of an inability to retract a radionuclide source assembly to its fully shielded position, per 10 CFR 34.101(a)(2). The incident occurred at NIPSCO Michigan City Generating Station [in] Michigan City, IN at 0545 CDT, on 28 April, 2019. The event consisted of a temporary inability of the radiography crew to immediately return a radionuclide source assembly of Cobalt-60 (76 Ci) to its fully shielded position. "The cause of the incident is presumed to be a source guide [tube] positioned with too tight of a radius, through which the sealed source could not be fully retracted. The equipment involved was manufactured by Source Production and Equipment Co., and was a model SPEC-300 projector (SN: 0080) and model G-70 source assembly (SN: C60-100). "The actions taken to return the source assembly to the projector consisted retracting the source as far as possible, the RSO [Radiation Safety Officer] approaching from behind the projector, using the intrinsic shielding of the exposure device as shielding, straightening the guide tube with the use of 7 ft. remote-handling tongs, allowing the source to clear the bend in the source guide tube, then retracting the source, as normal, using the control cables. "The incident occurred at approximately 0545 CDT, and upon discovering that the inability to fully retract the source, radiographer called [the] RSO at 0552 [CDT], while [the] assistant radiographer extended barricades to emergency distance. [The] RSO left his home promptly to gather the retrieval kit from IRISNDT's Hammond, IN office. RSO arrived on site at approximately 0715 [CDT]. After performing an assessment, the source retrieval took approximately fifteen (15) minutes to complete, and the source was returned to the shielded position by 0745 [CDT]. "All retrieval operations were conducted by individuals who have been trained to perform such tasks. All associated remote-handling equipment was subsequently removed from service for inspection. No involved equipment was found to be damaged or defective. "No members of the public received any dose. The lead radiographer, received a dose of 8.8 mrem from the start of his shift until the retrieval was complete, the assistant radiographer, received a dose of 0.2 mrem from the start of his shift until the retrieval was complete, and the RSO performing the retrieval, received a total dose of 4.3 mrem. "Radiographic personnel responded appropriately in identifying that the source had not returned to the shielded position, reposting and monitoring emergency barricades, contacting the Radiation Safety Officer, maintaining the restricted area while awaiting the RSO's arrival to site, and assisting with the retrieval as instructed, and following all procedures and O&E instructions." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-05-06
54031 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2019-04-26 11:47 | 2019-04-26 20:19 | 2019-04-26 | THROUGH WALL LEAK ON STANDBY LIQUID CONTROL SYSTEM PIPING "At 1147 [CDT] on 4/26/19, a through wall leak (reported as 1 drop every 1 to 2 minutes) was identified and confirmed by operation and NDE [Non-Destructive Examination] personnel on the Standby Liquid Control injection line during pressure testing activities. The line is 1.5 inch in diameter and classified as an ASME Section Ill, Class 1 line. The leak is currently isolated from the reactor vessel by a danger tagged manual valve." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2019-04-26
54030 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2019-04-22 | 2019-04-26 17:22 | 2019-04-26 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following was received from the state of Wisconsin via e-mail: "On April 26, 2019, Wisconsin Department of Health Services (DHS) was notified that at the licensee's Kaukauna facility, a fixed gauge mounted to a coal chute had been damaged and failed with the shutter closed. The incident occurred on April 22, 2019. Maintenance staffs were repairing a valve located above an Ohmart/Vega Corporation Model SHLG-1 fixed gauge containing 5 mCi of Cs-137. The valve failed, rotated downward, and made contact with the shutter actuator handle which severed the handle from the device. The gauge was not in operation at the time of the incident and the shutter remained in the closed position, the licensee's [Radiation Safety Officer] (RSO) stated on the initial phone call that the shutter is now inoperable. "The maintenance staff called the RSO on the day of the incident and he instructed them to cordon off the area and perform surveys of the device. The surveys indicated that the source was not impacted and the RSO later performed confirmatory surveys that yielded similar results. "Wisconsin DHS intends to perform a reactive inspection when the licensee's service provider replaces the gauge; the date is still to be determined." Event Report No.: WI 190001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2019-05-06
54029 | 0 | AZ DEPARTMENT OF HEALTH SERVIC |  |  |  |  | 2019-04-25 | 2019-04-25 17:42 | 2019-04-26 | AGREEMENT STATE REPORT - POTENTIAL OVER EXPOSURE The following was received from the state of Arizona via e-mail: "The [Arizona Department of Health Services] received notification from the licensee that an individual received a whole body exposure of approximately 290 Rem for the month of March. The individual is believed to be an x-ray technologist that works in the operating room. It is unknown at this time if the individual may also work with radioactive materials. The Department has requested additional information and continues to investigate the event. "Additional information will be provided as it is received in accordance with SA-300. "Arizona incident Number 19-008." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE ON 4/26/19 AT 1134 EDT, FROM BRIAN GORETZKI TO JOANNA BRIDGE * * * The following was received from the state of Arizona via e-mail: "This correspondence is a follow-up to the notification sent [on 4/25/19] regarding an approximate 290 Rem whole body exposure. It was determined through inspector interviews and procedure logs that the individual is an x-ray technologist and does not work with radioactive materials. The individual is the lead [certified radiation technologist] in an [operating room] department of a hospital performing 6-7 fluoroscopic procedures per day." It is believed that the actual exposure was just to the badge and not to the person. Notified R4 RDO (Young), NMSS Events (email), NMSS Director (Kock), and INES (Milligan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2019-05-03
54028 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-04-23 16:11 | 2019-04-25 12:09 | 2019-04-25 | AGREEMENT STATE REPORT - DOSE GREATER THAN PRESCRIBED DOSE The following was sent by email from the Commonwealth of Massachusetts: "The licensee reported on April 24, 2019 that it discovered on April 23, 2019 two High Dose-rate Remote Afterloader (HDR) medical events where tissue other than the treatment site received a dose exceeding the reporting requirements 105 CMR 120.594(A)(1)(c). One of the medical events occurred in March of 2019 and the other occurred in October of 2018. "The licensee reported that a 5 cm offset from the target location resulted in dose to unintended tissue during each treatment. "The licensee used a Varian Medical Systems, Inc. Model VariSource iX HDR containing iridium-192 to deliver the doses for both treatments. Each prescribed dose to each patient was 10 gray (1,000 rad) to the vaginal cavity across two fractions. "Both events occurred as a result of an unintended area of each patient's vaginal cavity receiving a portion of the prescribed dose. The licensee reported that the cause of the events is a combination of a change in applicator size and incorrect parameters input into the device console. Some two years ago, the size of the vaginal applicator changed from 120 cm in length to 125 cm in length, but there were no issues until the two aforementioned events. From the administration documentation, the licensee determined that the technician erroneously entered 120 cm into the device console rather than 125 cm, effectively causing a 5 cm offset. As a result the lower 5 cm of each patient's vaginal cavity received more dose than intended. The exact number is yet unknown. The licensee will provide additional information in a written report. "The licensee reported that the referring physician, who is the same for each patient, has been notified and that the referring physician intends to notify each patient. "The Agency [Massachusetts Radiation Control Program] plans to perform a special inspection and considers this event to be open." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-05-03
54027 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2019-04-25 09:18 | 2019-04-25 12:04 | 2019-04-25 | AUTOMATIC REACTOR TRIP DUE TO TURBINE GENERATOR TRIP "At 0918 [EDT] on 4/25/19, with [Saint Lucie] Unit 1 in Mode 1 at 100% power, the reactor automatically tripped due to a Turbine Trip. The reactor trip was uncomplicated with all systems responding normally. "Operations is maintaining the plant stable in Mode 3. Decay heat removal is being accomplished by main feed water and the main condenser using the turbine steam bypass valves. "Unit 2 is not affected and remains at 100% power. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-04-25
54026 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-04-24 | 2019-04-25 11:04 | 2019-04-26 | AGREEMENT STATE REPORT - GAUGE STUCK SHUTTER The following was received via email from the State of Louisiana: "On 04/24/2019, Weeks Marine, Inc. was performing their routine operations with their licensed device. During their dredging operations, work ceased and the gauge shutter would not close when not in operation. The gauge shutter would not close due to dirt and grime residue in the shutter mechanism. Weeks Marine, Inc. called a service contractor, Applied Health Physics, to evaluate the situation and determine the best course of action to correct the problem (clean and lubricate). "The sources and device with the stuck open shutter will remain installed on the process until the repairs are made. This is not a radiation exposure hazard and does not pose a health and safety situation for the Weeks Marine, Inc. employees or the general public. "The density/level gauge is a Berthold Model 7400D series device/source holder, loaded with an approximately 1500 mCi Cs-137 source, s/n 372-1-85. Initial activity was 3000 mCi in 1985 [manufacture] date. "This event is being reported to the NRC Operations Center as required by Regulatory Requirement 10 CFR Part 30.50(b)(2) and LAC 33:XV 340.B." Louisiana Event Report ID No.: LA-190006 * * * UPDATE AT 0933 EDT ON 4/26/2019 FROM JOSEPH NOBLE TO JEFF HERRERA * * * The following update was received from the Louisiana Department of Environmental Quality via email: "[On] 04/25/2019, at [1440 CDT] Weeks Marine reported that Applied Technical Services had completed the maintenance on this fixed density gauge and that Hopper Dredge # 456 is back in operation. This event is considered completed and closed." Notified the R4DO (Young) and NMSS (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-05-03
54025 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-04-23 09:00 | 2019-04-24 13:55 | 2019-04-24 | NEW YORK AGREEMENT STATE REPORT - PANORAMIC IRRADIATOR SOURCE FAILED TO RETRACT The following information was received from the state of New York via facsimile: "The New York State Department of Health (NYSDOH) was notified by [the radiation safety officer] (RSO) of Pall Hauppauge (C1935) that they had an incident where the source did not retract completely leaving the source partially exposed for a period of time. "According to the RSO, he was notified on April 23, 2019, at approx. [0900 hrs. EDT] of a fault at Vault 4, and arrived approximately 15 minutes later and found that the source had gotten stuck very slightly above the down (safe) position when the cycle ended. All of the safety and alarm systems worked as designed, and the operator did not attempt to enter the irradiator or take any action. "The RSO contacted Nordion to discuss the situation and he was able to free the source and get it into the safe position without any issue. The RSO then checked the radiation levels in the irradiator and found that they were normal. There was no risk of personnel or public exposure at any time during this incident, nor was there any risk of contamination. "The root cause for the source getting stuck has not been yet determined. The RSO will be working with Nordion to assess the equipment and decide the course of action. "DOH will continue to monitor this incident. "Pall Hauppauge is licensed to possess Cobalt 60 in sealed source use in a Nordion International dry panoramic storage irradiator." NY Event Report ID No.: NY-19-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-05-02
54024 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-04-23 12:56 | 2019-04-24 10:40 | 2019-04-24 | FITNESS FOR DUTY REPORT - ALGORITHM USED FOR RANDOM TESTING EXCLUDED A POPULATION OF INDIVIDUALS "On April 23, 2019, at 12:56 Central Time, South Texas Project Nuclear Operating Company (STPNOC) identified a programmatic failure, degradation, or discovered vulnerability of the fitness for duty (FFD) program that may permit undetected drug or alcohol use or abuse by individuals within a protected area, or by individuals who are assigned to perform duties that require them to be subject to the FFD program." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.719 |  |  |  | 0 | 2019-04-24
54023 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-04-22 | 2019-04-23 20:32 | 2019-04-23 | CALIFORNIA AGREEMENT STATE REPORT - POTENTIAL MEDICAL EVENT The following information was excerpted from a report received from the state of California via email: "[A] potential medical event occurred during an HDR [high dose rate] brachytherapy procedure in which the Tandem Ovoid [was] inserted into the patient. The patient was there to receive the 3rd dose of 8 Gy (for a total of 24 Gy) to the uterus. Instead, because all of the guide tubes were 132 cm instead of 120 cm in length, the entire 8 Gy of this last fraction was delivered to the vagina. They do not believe that the uterus received any of the prescribed 8 Gy, and all of it was delivered to non-target organ. The patient and her treating physician were informed, and she is going to return to the hospital for monitoring. Since this was the last of 3 fractions, the uterus has only received 16 Gy, not 24, while the unplanned dose to non-target organ was 8 Gy. "A site visit will be conducted Monday, 4/29/2019, [by the California Department of Public Health, Radiologic Health Branch]." CA 5010 Number: 042319 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-05-01
54022 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2019-04-23 | 2019-04-23 19:33 | 2019-04-23 | WASHINGTON AGREEMENT STATE REPORT - LOST AND FOUND RADIOACTIVE MATERIAL The following information was received from the state of Washington via email: "Swedish Medical Center notified the state of Washington that a lead pig, containing 50 mCi (1.86 GBq) of Y-90 Sir-Spheres, was picked up for lead recycling. When the recycling company (Stericycle) came to collect all the lead pigs, a tech let the company into the waste room to collect the pigs not knowing that one of the pigs contained the Y-90 material left over from a treatment on Friday the 19th of April 2019. On April 23rd, the RSO [radiation safety officer] was reviewing the lead disposal paperwork and realized the material was sent out with the other lead pigs and notified the State. The RSO called the recycling company and was told the pigs were still in a drum and had not been processed. They will be returning the drum to the medical center on April 24th, 2019 and the RSO will notify the State when it arrives." WA Event Report ID No.: WA-19-014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2019-05-01
54021 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-04-23 02:32 | 2019-04-23 09:44 | 2019-04-23 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 0232 EDT on April 23, 2019, a Main Control Room (MCR) alarm was received for low control room positive pressure. "At 0233 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10 Control Room Emergency Ventilation System (CREVS) was declared not met for both trains. Watts Bar Unit 1 entered Condition B. Watts Bar Unit 2 was not performing movement of irradiated fuel assemblies and did not meet the APPLICABILITY for CREVS per LCO 3.7.10. "At 0233 EDT on April 23, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10 Condition B was exited. "The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of Design Basis Accident (DBA) consequences to CRE occupants. From 0232 EDT to 0233 EDT, [Watts Bar Nuclear] WBN was unable to validate that CREVS could fulfill its required Safety Function. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-04-23
54020 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-04-22 13:24 | 2019-04-22 20:41 | 2019-04-22 | MANUAL INITIATION OF THE AUXILIARY FEEDWATER SYSTEM IN RESPONSE TO A LOSS OF FEEDWATER "At 1324 CDT, on 4/22/2019, with unit 2 in Mode 3 at 0 percent power, an intentional manual initiation of the Auxiliary Feedwater System occurred in response to a loss of feedwater condition. The loss of feedwater condition occurred after the non-safety related Startup Feedwater Pump was secured due to high bearing temperatures. The A Train Auxiliary Feedwater Pump was started per procedure. The Auxiliary Feedwater System started and operated as designed following intentional manual initiation. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feedwater System. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-04-22
54019 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-04-19 | 2019-04-22 17:38 | 2019-04-22 | AGREEMENT STATE REPORT - LOST AND RECOVERED I-125 SOURCE The following information was obtained from the state of Illinois via email: "The RSO [radiation safety officer] at the University of Chicago [Hospital], called to report that the University received one lsoAid, Model IAl-125A, I-125 source for a seed localization procedure. It had an activity of 271 microCuries when implanted in the patient on Thursday, April 18, 2019. On Friday, the patient's tissue [containing the I-125 seed was excised] and sent to pathology for evaluation. During all steps, the individuals involved reported that they measured appropriate dose rates from the seed. The Pathology technician was using scissors on the patient's tissue and the seed popped out of the specimen and fell into the sink. The seed was recovered before it went down the drain. Surveys of the sink show no contamination or dose rate measurements. The radiation safety staff measured the recovered source with both a survey instrument and a gamma counter, and the source has no measureable dose rate. The patient was surveyed and it was determined that the source [was] not in the patient. "A review of the SSDR [sealed source and device registry] sheet has determined that this source contains I-125 adsorbed on a silver rod which is further encased in the outer capsule. The outer capsule measures 3.0 mm x 0.5 mm and there are no visible signs that the source was cut. They plan to take the seed for an x-ray today to determine if the inner rod is missing and to see if there are obvious signs that the outer capsule was breached. "UPDATE: The I-125 seed was found intact in the sink trap. The source that was initially believed to be the subject seed was from another patient and was a three-year-old prostate seed that had decayed to background." NMED Item Number: IL190012 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-04-30
54018 | -1 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2019-04-22 11:30 | 2019-04-22 16:16 | 2019-04-30 | CONTRACT SUPERVISOR TESTED POSITIVE ON A RANDOM FITNESS-FOR-DUTY TEST A contract supervisor tested positive for drugs on a random fitness-for-duty test. The contractor's access to the facility has been revoked and his badge was confiscated. Additionally, the supervisor failed a follow-up test administered the previous day (see EN #54017). * * * RETRACTION ON 4/30/2019 AT 1642 EDT FROM KELLI ROBERTS TO BRIAN LIN * * * "On April 16, 2019, an individual was selected for a follow-up drug test. The same individual was selected again on April 17, 2019 for a random drug test. The results for both tests were ruled by the Medical Review Officer (MRO) on the same day and ruled positive for the same drug on April 22, 2019. These FFD violations were reported to the NRC on April 22, 2019, as EN #54017 and EN #54018, respectively. As allowed by 10 CFR 26.185(o), the MRO further reviewed the quantitation of the drug in both tests and determined that no further drug use had occurred since the first positive test. Therefore, the MRO concluded that this should be considered one FFD violation, and EN #54018 is being retracted. No changes are needed to EN #54017." The NRC Resident Inspector has been notified of this retraction. Notified R2DO (Heisserer) and FFD Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2019-04-22
54017 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2019-04-22 11:30 | 2019-04-22 16:16 | 2019-04-22 | CONTRACT SUPERVISOR TEST POSITIVE FOR DRUGS ON A FOLLOW-UP TEST A contract supervisor tested positive for drugs on a follow-up fitness-for-duty test. The contractor's access to the facility has been revoked and his badge was confiscated. Additionally, the supervisor failed a random test administered the next day (see EN #54018). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2019-04-22
54016 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2019-04-21 23:07 | 2019-04-22 01:51 | 2019-04-22 | AUTOMATIC REACTOR TRIP AND SPECIFIED SYSTEM ACTUATION "At 2307 EDT on April 21, 2019, in Mode 1 at approximately 100 percent reactor power, Unit 1 automatically tripped due to a Main Turbine Trip. The Main Turbine Trip was a result of two out of three level instruments sensing a false high reactor water level. All control rods inserted as expected during the scram. Safety Relief Valves G and K lifted per design. The same level instruments that failed also tripped both Reactor Feed Pumps. As a result, reactor water level dropped below the Low Level 1 and 2 actuation setpoints. Per design, the Low Level 1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The Low Level 2 signals resulted in Group 3 (i.e. Reactor Water Cleanup) isolation, a secondary containment isolation signal, and an auto start of Standby Gas Treatment and Control Room Emergency Ventilation. Also, the Low Level 2 resulted in [high pressure coolant injection] HPCI and [reactor core isolation cooling system] RCIC automatically starting and injecting into the vessel. "All systems responded as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) for RPS actuation and 10 CFR 50.72(b)(3)(iv)(A) as an event that results in valid actuations of the Primary Containment Isolation System. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." Decay heat is currently being removed via the turbine bypass valves. Condensate and feed water are maintaining water level. The reactor is still at saturation temperature and 475 psi, lowering slowly. The reactor is still in a normal electrical lineup. There was no impact to Unit 2 as a result of this event. * * * UPDATE ON 04/22/19 AT 0220 EDT FROM ALAN SCHULTZ TO JEFFREY WHITED * * * The licensee updated the event report to include a 4-Hr Non-Emergency Notification in accordance with 10 CFR 50.72(b)(2)(iv)(A) for Emergency Core Cooling System, HPCI, Discharge to the Reactor Coolant System. Notified R2DO (Dickson), NRR EO (Miller) and IR MOC (Gott). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2019-04-22
54015 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-04-21 09:20 | 2019-04-21 12:43 | 2019-04-21 | LIMERICK ONSITE NON-WORK RELATED FATALITY "Event of Public Interest performed to notify State and Local agencies for emergency vehicle response required due to an on-site non-work related illness. The individual was unresponsive and was unable to be resuscitated due to the medical issue. The individual was outside the Radiological Controlled Area (RCA) and no radioactive material or contamination was involved." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-04-21
54014 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2019-02-22 10:30 | 2019-04-21 08:46 | 2019-04-21 | INVALID ACTUATION OF A UNIT 1 CONTAINMENT ISOLATION LOGIC DUE TO A BLOWN FUSE "This 60-Day telephone notification is being made per the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of Limerick Generating Station Unit 1 containment isolation logic. "On February 22, 2019, while performing work on the 1C Main Seam Line Rad Monitor a partial containment isolation occurred due to a blown fuse. The blown fuse caused a single channel 'C' isolation signal for the Refueling Area Ventilation Exhaust High Radiation and the Reactor Enclosure Ventilation Exhaust-High Radiation logic. "The following systems had components that actuated due to the partial isolation: - Plant Process Radiation Monitoring System - Nuclear Boiler System - Control Rod Drive Hydraulic System - Containment Atmospheric Control System - Primary Containment Instrument Gas System "This event resulted in partial Group VIC and partial Group VIIIB isolations. All the components that would actuate on a single 'C' isolation signal responded as designed." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-04-21
54013 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2019-04-15 | 2019-04-19 15:08 | 2019-04-20 | AGREEMENT STATE REPORT - LEAKING INTRAVASCULAR BRACHYTHERAPY DEVICE IDENTIFIED The following report was received from the Washington State Department of Health via email: "UW [University of Washington] Radiation Safety (RS) conducts semi-annual sealed source leak test during the months of April and October. After analyzing a leak test for a Sr-90 Intravascular Brachytherapy (IVB) device it was found to be leaking. Details provided by the University of Washington radiation safety office are as follows: "'The results of the sample's analysis were reviewed and it was discovered that a sample for one of the IVB source trains indicated contamination at 3737 cpm. A second sample of both IVB source trains was obtained. The sample for the 40 mm source train indicated 177 cpm and the sample for the 60 mm source train indicated 7998 cpm. The RS staff member discussed the contamination with the Radioactive Materials Compliance Manager (RMCM) and the Radiation Safety Officer (RSO). It was then discovered that the leak test procedure specified in the Novoste Beta-Cath User's Manual was not performed correctly. A swab of the water sample obtained during the leak test was analyzed rather than the whole 5 ml of water. The RS staff member performed another leak test of both IVB source trains, and analyzed the 5 ml water samples (The results are provided below). The IVB device was placed out of service and removed from Radiation Oncology. The RS staff member contacted the RSO at Best Vascular who requested the sources and items used for the leak testing be returned to Best Vascular for investigation. "'Radiation Safety counted the 5 ml water samples using one of their liquid scintillation counters (LSC) [Packard Tricarb 2900TR - S/N 426395]. Using an efficiency of 100 percent for Sr-90 (Beckman Coulter's Isotope Booklet for Liquid Scintillation Counters - 2002) the activity calculated was: "'40 mm source train: 396 counts / min (decays / 1 counts)(min / 60 sec)(Bq*sec / decays) = 6.6 Bq "'60 mm source train: 17429 counts / min (decays / 1 counts)(min / 60 sec)(Bq*sec / decays) = 290 Bq "'The activity level of the 60 mm source train leak test sample exceeded the limit of 185 Bq. The contamination in the leak test for the 40 mm source train is believed to be a result of cross contamination from the 60 mm source train leak test.'" WA Event Report ID No.: WA-19-013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2019-04-29
54012 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2019-04-20 05:07 | 2019-04-20 09:54 | 2019-04-20 | BOTH REACTOR FEED PUMPS TRIP CAUSING MANUAL REACTOR SCRAM AND ECCS INJECTION "At 0507 [CDT on April 20, 2019], the DAEC [Duane Arnold Energy Center] experienced a trip of both reactor feed pumps. Operators inserted a manual scram. All control rods inserted, as required. As a result of the feed pump trips and scram, HPCI and RCIC automatically injected. Also, containment isolations occurred, as expected for this event. All systems responded as designed. "Operators are currently taking the unit to cold shutdown conditions. Vessel level is being controlled by RCIC with Condensate System available. Pressure is being controlled using Main Steam Line drains and the Main Condenser is available." Normal electrical lineup remains. The cause of the reactor feed pumps tripping is believed to be an instrument air leak to flow control valves, causing loss of suction to both feed pumps. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2019-04-20
54011 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-04-12 06:45 | 2019-04-19 11:42 | 2019-04-19 | AGREEMENT STATE REPORT - FAILURE TO RETRACT RADIOGRAPHY CAMERA SOURCE The following report was received from the Alabama Department of Public Health Radiation Control via facsimile: "On 4/12/19, at 0645 CDT, a radiographer was shooting in the vault at ATL [American Testing Labs], when the source became un-retractable. [The radiographer] closed the vault door and called the RSO [Radiation Safety Officer]. "The RSO arrived 45 minutes later and checked the status of the crank and the positioning of the camera in the vault. The RSO then took apart the handle of the crank and manually pulled the source through the cable into a safe position within the camera. "The crank was serviced and the RSO found some debris within the crank. The crank was cleaned and placed back into service. After several shots, the crank was operational. "The RSO received 24 mR on his dosimeter and the radiographer received 0 mR." Alabama Incident #19-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2019-04-29
54010 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-04-11 | 2019-04-18 18:00 | 2019-04-18 | AGREEMENT STATE REPORT - PATIENT UNDERDOSAGE OF YTTRIUM 90 THERASPHERES The following report was received from the Georgia radioactive materials program environmental protection division via email: "GA 292-1 reported on Friday 4/11/19 that a misadministration of Y-90 Theraspheres occurred on 4/3/19. It was discovered that the male patient only received 65 percent of the prescribed dose. The total dose consisted of 2 vials; the first vial was administered without any issues, but the second vial was observed as still being relatively full after being returned to nuclear medicine department for disposal. A radiation survey was completed on the vials after they were returned to the nuclear medicine department and it was noted by the department personnel that vial 2 had a higher activity then what was expected. It was later determined that vial 2 contained more dose [than expected] after performing the procedure as prescribed. The remainder of the prescribed dose was delivered to the patient on 4/5/19. Preliminary results indicate there may have been an issue with the delivery equipment (perhaps with the tubing). The radioactive materials were fully accounted for and results were confirmed by performing contamination survey, following the procedure. The RSO will submit a detailed report to the radioactive materials program within 5 days of this notification. "[On 4/18/2019] the licensee provided a written report pertaining to the event. Based on the report, no root cause has been determined at this time. The licensee suggests that the equipment can possibly be examined or sent back to the manufacturer after the radioactivity in the waste container has decreased to background levels, to determine whether any equipment defects can be found." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-04-26
54009 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-04-18 | 2019-04-18 17:44 | 2019-04-18 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email: "On 4/18/2019, [California Department of Public Health-Radiologic Health Branch (CDPH-RHB)] received a notification from [the California Governor's Office of Emergency Services] regarding a stolen moisture density gauge. The gauge involved is a Troxler Model 3430, S/N 31163, containing 9 mCi of cesium-137 and 44 mCi of americium-241. The gauge was stolen from an authorized user's truck parked near his residence at 1830 PDT on 4/17/2019. At the time of the incident, the device was secured in a Type A package, chained to the bed of the truck. On 4/18/2019, around 1000 PDT, the user discovered that the gauge was stolen from his vehicle. Immediately after the incident a report was filed with the Sacramento County Sherriff Office. RHB will be following up on this investigation." CA 5010 Number: 041819 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-04-26
54008 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2019-04-17 08:12 | 2019-04-17 15:21 | 2019-04-17 | TURBINE TRIP SOLENOIDS FAILURE TO ACTUATE "At 0812 EDT on 4/17/2019, it was discovered that both sets of turbine trip solenoids were previously unable to actuate within the allowable time frames; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D). At the time of discovery, one set of turbine trip solenoids had been restored. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-04-17
54007 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2019-04-17 | 2019-04-17 12:52 | 2019-04-17 | AGREEMENT STATE REPORT - TRITIUM EXIT SIGNS DISMANTLED The following report was received via e-mail: "The Department [Arizona Department of Health Services] received notification from the licensee that they dismantled 24 tritium exit signs by removing the outer glass and aluminum housing, and then releasing the glue that held the glass ampules onto the inner plastic. The licensee said they were attempting to reduce the cost of shipping the signs for disposal. The Department has requested additional information and continues to investigate the event. "The Licensee is: Arizona License Number- 07-138 Banner Boswell Medical Center 10401 Thunderbird Blvd Sun City, Arizona 85351" Arizona Incident: 19-005 None of the vials were damaged and the wipe tests were all negative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-04-25
54006 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-04-16 | 2019-04-17 12:22 | 2019-04-17 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "On April 16, 2019, the licensee notified the Agency that one of its Humboldt model 5001-C moisture/density gauges (SN: 2076), containing 40 milliCuries americium-241/beryllium (SN: 47-6041) and 10 milliCuries of cesium-137 (SN: 40-6862), had been run over and damaged by a dump truck at a temporary job site in Danbury, Texas. While a density test was being performed and the cesium source was extended into the ground, a dump truck backed up into the test area. The technician had to jump out of the way. The truck tire ran over and shattered the housing on one side of the gauge. The source was retracted, with some difficulty, into its shielded position. Radiation surveys indicated the shielding was intact. However, the technician reported that the source rod could be pulled completely out of the top of the housing. With the source in the normal shielded position, the gauge was placed inside its transport case and returned to the licensee's facility. The licensee is making arrangements for repair/disposal. There were no exposures as a result of this event. More information will be provided as it is obtained in accordance with SA-300." Texas Incident: 9675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-04-25
54005 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2019-04-17 01:37 | 2019-04-17 06:25 | 2019-04-17 | UNDERVOLTAGE TO A SAFETY RELATED BUS RESULTING IN VALID SYSTEM ACTUATION "At approximately 0137 CDT, with the Plant [Callaway] in No Mode (Defueled) the "B" Switchyard Bus cleared resulting in a loss of normal power to "A" Train Safety Related Transformer XNB01. This resulted in an under voltage condition on Safety Related Bus NB01. The "A" Emergency Diesel started per design and re-energized Bus NB01. This actuated the shutdown sequencer which first sheds loads including the "A" Spent Fuel Pool Cooling Pump and started "A" Essential Service Water Pump, "A" Component Cooling Water Pump, "A" Control Room A/C and other design loads. No complications were identified. The "A" Switchyard Bus remained energized at all times. The "A" Spent Fuel Pool Cooling Pump was restarted per off normal procedure response at 0149 CDT. Spent Fuel Pool water temperature started at 102 F and rose to 103 F prior to restart. There was no movement of irradiated fuel in progress in the Fuel Building during this time. The plant remains stable in No Mode (Defueled). "At the time of the loss of "B" Switchyard Bus, the plant was closing Generator Output breaker MDV53 to establish a backfeed alignment. Further investigation is in progress. "This event is reportable per 10 CFR 50.72(b)(3)(iv)(A). "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-04-17
54004 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2019-04-16 | 2019-04-16 23:34 | 2019-04-17 | AGREEMENT STATE REPORT - UNABLE TO INJECT FULL PRESCRIBED DOSE DURING MEDICAL TREATMENT The following was received via e-mail: "On April 16, 2019, the Department [Arizona Department of Radiation Control] received notification from the licensee [Banner University Medical Center - Tucson] of a possible medical event involving yttrium-90 radiolabeled glass microspheres (Therasphere). The pre-treatment calibration measured an activity of 2.91 GBq and the post-treatment calibration measured 2.65 GBq. The patient was being treated for a hepatocellular carcinoma in the left hepatic lobe, segment II. The Department has requested additional information and continues to investigate the event." Additional information from call to licensee Radiation Safety Officer: During injection of the prescribed dose to the patient, backpressure during the injection prevented injecting the full dose, with 2.65 GBq of a prescribed dose of 2.91 GBq not delivered (24 percent was delivered). Arizona Incident 19-006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2019-05-01
54003 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-05-10 | 2019-04-16 15:27 | 2019-04-16 | AGREEMENT STATE REPORT - LOST GENERALLY LICENSED TESTING DEVICE The following report was received via e-mail: "On January 11, 2018, FHL Industries, LLC, acquired Replogle Hardwood Flooring out of bankruptcy. The new owners were unaware of a generally licensed hazardous testing device from previous ownership. During a search of the facility during April 2018, FHL concluded the device was missing. FHL has no intentions of acquiring another radioactive testing device. "Isotope and activity: Am-241, 0.03 mCi; Cm-244, 13.0 mCi Manufacturer: Asoma Instruments Model: 100 SN: 1537" Tennessee Event: TN-18-089 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2019-04-24
54002 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-04-15 23:55 | 2019-04-16 02:59 | 2019-04-16 | OFFSITE NOTIFICATION - ON SITE FATAILITY "At 2355 CDT on 4/15/19, life-saving activities by offsite medical personnel for a Farley employee were terminated. The coroner declared the individual deceased at the plant site at 0130 CDT. "The fatality is not believed to be work-related and the individual was inside of the Radiological Controlled Area. "This is a four-hour notification, non-emergency for a notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). The NRC Resident Inspector has been notified." The licensee will be notifying the Occupational Safety and Health Administration due to the on-site fatality. The licensee will perform a radiological survey of the individual prior to transportation offsite. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-04-16
54001 | 0 | CURTISS-WRIGHT |  |  |  |  | 2019-04-15 | 2019-04-15 20:12 | 2019-04-15 | PART-21 NOTIFICATION - SNUBBER HYDRAULIC FLUID BATCH CONTAINS PARTICULATES The following report was received via fax: "Pacific Gas and Electric notified Curtiss Wright [CW] Enertech that they observed white particulate in SF-1154 fluid in three containers. The white particulate was found settled at the bottom of the containers. The fluid was dedicated and supplied by CW Enertech in November 2016 The fluid was traced back to Momentive Batch 14ELVS145. "The momentive batch 14ELVS145 was previously reported by Lake Engineering Company (Ref NRC ML17212A628 and ML17128A465). The white particulates/semisolid material was identified as phenyl cyclic precipitate. The safety hazard that could be created by this defect is the blockage of snubber bleed port as reported by Duane Arnold (Ref ML070300154). This blockage could prevent the snubber from unlocking after a seismic event, thus preventing the snubber to allow for system movement during normal operations. "In addition, evaluation performed by Lake Engineering Company has found that all of the solids are dissolved back into the fluid when heated to 110 [degrees] fahrenheit. With all solids dissolved, there is no potential safety hazard with this fluid." Affected sites: Fermi, Shearon Harris, Beaver Valley, Diablo Canyon, Watts Bar, Perry, and Almaraz (Spain). Curtiss-Wright point of contact: Rosalie Nava, 714-528-2301 ext 1872 See also EN 43071 dated 1/3/2007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-04-15
54000 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2019-04-15 05:11 | 2019-04-15 11:36 | 2019-04-15 | TRANSPORT OFFSITE TO MEDICAL FACILITY OF POTENTIALLY CONTAMINATED INDIVIDUAL "At 0511 CDT on 4/15/2019, transport of a potentially radiologically contaminated person from the Monticello Nuclear Plant to a local hospital was performed prior to conducting a radiological survey as a prudent measure to ensure timely medical support. At 0658 CDT a radiological survey determined that the individual and their clothing were not contaminated. "This is reportable under 10 CFR 50.72(b)(3)(xii). The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2019-04-15
53999 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-04-14 03:20 | 2019-04-14 06:44 | 2019-08-06 | AUTOMATIC REACTOR TRIP DUE TO MAIN FEEDWATER PUMP TRIP "At 0320 EDT, April 14, 2019, Sequoyah Unit 1 experienced an automatic reactor trip. The event was initiated by the trip of the 1A main feedwater pump. During the automatic unit runback, an automatic reactor trip was initiated due to low-low level in Steam Generator number 3. "The Auxiliary Feedwater System (AFWS) automatically actuated as required when the expected post-trip feedwater isolation actuated. Reactor Coolant System temperature is being maintained by the AFWS and the steam dump system. During this operational cycle, one control Rod Position Indicator (RPI) for core position E-5 in shutdown bank 'A' has been inoperable, and the appropriate Condition and Required Actions of [Technical Specification Limiting Condition of Operation] 3.1.7 were complied with. Due to this inoperable RPI, the associated shutdown rod is conservatively assumed to be full out and untrippable. Consequently, boration was required to establish adequate shutdown margin. All other Control and Shutdown rods fully inserted. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the reactor trip. The unit is currently stable in Mode 3. Unit 1 is in a normal shutdown electrical alignment. "There was no impact on Unit 2. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the AFW system. "There was no impact on the health and safety of the public or plant personnel. "The NRC Senior Resident Inspector has been notified." * * * UPDATE ON 8/6/19 AT 12:20 EDT FROM KEVIN MICHAEL TO KERBY SCALES * * * The licensee provided an update to paragraph 2. "The Auxiliary Feedwater System (AFWS) automatically actuated as required when the expected post-trip feedwater isolation actuated. Reactor Coolant System temperature is being maintained by the AFWS and the steam dump system. All Control and Shutdown rods fully inserted, except E-5 which was previously identified and conservatively assumed to be in a full out position. Applicable TS actions were performed to maintain shutdown margin. All safety systems responded as designed. No primary or secondary safety valves actuated during or after the reactor trip. The unit is currently stable in Mode 3. Unit 1 is in a normal shutdown electrical alignment." Notified the R2DO (Gerald McCoy) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-04-14
53998 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2019-04-14 00:03 | 2019-04-14 03:21 | 2019-04-14 | AUTOMATIC REACTOR SCRAM AND SPECIFIED SYSTEM ACTUATION "On April 14, 2019 at 0003 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram during reactor startup. The cause of the automatic scram was due to high [Reactor Pressure Vessel] pressure following closure of the turbine stop valves. All control rods fully inserted and all plant systems responded per design following the scram. "Following the automatic scram, the High Pressure Coolant Injection (HPCI) System automatically initiated as expected. At Nine Mile Point Unit 1, a HPCI System actuation signal on low Reactor Pressure Vessel (RPV) level is normally received following a reactor scram, due to level shrink. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. At 0004, RPV level was restored above the HPCI System low level actuation set point and the HPCI System initiation signal was reset. Pressure control was established on the Turbine Bypass Valves, the preferred system. No Electromatic Relief Valves actuated due to this scram. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor water level and pressure maintained within normal bands. The offsite grid is stable with no grid restrictions or warnings in effect. "The unit is currently implementing post scram recovery procedures." The NRC Resident Inspector has been notified. The Licensee will notify the State of New York. | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-04-14
53997 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2019-04-12 18:15 | 2019-04-13 02:04 | 2019-05-24 | HIGH ENERGY LINE BREAK DOOR FOUND IN INCORRECT POSITION RESULTING IN LPCI AND CORE SPRAY BEING INOPERABLE "At approximately 1815 CDT on April 12, 2019, High Energy Line Break (HELB) Door-410A in the Reactor Building was discovered in the closed position. HELB Door-410B was previously closed for maintenance. Either Door-410A or Door-410B must be open to support the current HELB analyses. With both doors closed, this is considered an unanalyzed condition resulting in the loss of a post-HELB safe shutdown path. "With Door-410A and Door-410B closed, LPCI [Low Pressure Coolant Injection] and Core Spray injection valves in both divisions are no longer considered available. "This condition is being reported under 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented the fulfillment of a safety function. "The condition was resolved at approximately 1845 CDT on April 12, 2019 when Door-410A was blocked open. The health and safety of the public was not affected by this condition. "The NRC Resident has been notified." * * * RETRACTION FROM JESSE TYGUM TO HOWIE CROUCH AT 1330 EDT ON 5/24/19 * * * "Event Notification (EN) #53997, made on 4/13/2019, is being retracted. An engineering evaluation completed subsequent to this event analyzed the discovered condition with both Door-410A and Door-410B being closed. The engineering evaluation determined that the environmental conditions present with both Door-410A and Door-410B closed would not have impacted the availability of both divisions of the LPCI (Low Pressure Coolant Injection) and Core Spray injection valves nor would it have resulted in the loss of a post-HELB safe shutdown path. Therefore, this condition did not meet the criteria for an 8-hour notification per 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition that significantly degrades plant safety or per 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." The licensee also notified the Minnesota State Duty Officer. Notified R3DO (Cameron). | 25 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-04-13
53996 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-04-03 | 2019-04-12 13:21 | 2020-04-30 | AGREEMENT STATE REPORT - UNDERDOSE ADMINISTRATION OF Y-90 THERASPHERES The following is a synopsis of the information received from the Radioactive Materials Program of Georgia received via email: On April 3, 2019, an underdose of Y-90 TheraSpheres was administered to a patient. Only 65% of the prescribed dose was administered. On April 5, 2019, the remainder of the prescribed dose was delivered to the patient. There is no definitive cause identified at this time but the licensee has concluded that it was probably a delivery equipment problem (perhaps with the tubing). The licensee will follow-up with a formal report. * * * UPDATE FROM IRENE BENNETT TO HOWIE CROUCH (VIA EMAIL) ON 4/29/20 AT 1553 EDT * * * The state of Georgia amended the original report to state that the deliver apparatus is awaiting decay to background and will be examined locally or will be sent to the manufacturer for a root cause analysis. The prescribed dose was 127 Gy. The delivered dose was 59.8 Gy which is 47% of prescribed dose. As stated above, the patient was informed and returned two days later to complete the treatment. NMED Item: 190182 Notified R1DO (Schroeder) and NMSS Events Notification (email). * * * UPDATE FROM IRENE BENNETT TO HOWIE CROUCH (VIA EMAIL) ON 4/30/20 AT 1323 EDT * * * The state of Georgia has amended the original report and the update from 4/29/20 as follows: -the prescribed dose was 122 Gy -the delivered dose was 78.8 Gy -the difference is 64.5 percent. This same event was also reported under NRC Event Notification #54010 which has been deleted from the report database. Notified R1DO (Schroeder) and NMSS Events Notification (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | Agreement State | [9 empty] | Non Emergency | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-04-22
53995 | 0 | TILDEN MINING CO |  |  |  |  | 2019-04-12 08:00 | 2019-04-12 11:24 | 2019-04-12 | PROCESS GAUGE STUCK SHUTTER The following is a synopsis of an event received via email: On April 11, 2019, a trained technician was in the process of performing the biannual inventory/shutter check when the individual reported that Kay Ray Model #7050, Serial #1399, 250 mCi, Cs-137 gauge located on 5B DTU (Deslime Thickener U/Flow) in the Deslime basement had a frozen shutter mechanism and cannot be closed, rendering the shutter non-operable. The gauge won't be replaced until the first time the slurry pipeline goes down for repair. If the line goes down prior to that, the gauge will be replaced at that time. Similar events in the past have never had an exposure to any individuals. In the event of an emergency, the gauge will be removed and placed on a piece of lead and brought to storage. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-04-22
53994 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-04-11 12:23 | 2019-04-12 09:37 | 2019-04-15 | AGREEMENT STATE REPORT - POTENTIAL PERSONNEL OVEREXPOSURE The following was received via e-mail: "On April 11, 2019, at 1223 (CDT), the Radiation Safety Officer (RSO) for Vital Inspection Professionals, Inc. advised the [Alabama Department of Public Health] Office of Radiation Control (ORC) of an incident that occurred on that day in the permanent shooting room at their facility in Alabaster, AL. Vital Inspection Professionals, Inc. has an Alabama Radioactive Material License No. 1118 for conducting industrial radiography. Preliminary information indicates that the radiographer, working alone, cranked out a 67 Curie Ir-192 source for an exposure and failed to crank the source back in before setting up for the next exposure. The radiographer's personal dosimeter badge has been sent in for emergency processing. Results are pending. "Personnel from ORC are currently at the licensee's facility performing an incident investigation to include interviewing personnel and conducting re-enactments of the event." Alabama Incident: 19-08 * * * UPDATE AT 1118 EDT ON 4/15/19 FROM DAVID TURBERVILLE TO JOANNA BRIDGE * * * The following was received via fax: "This is an update to Alabama incident 19-08 that was reported the morning of April 12, 2019. As background, the Radiation Safety Officer (RSO) for Vital Inspection Professionals, Inc. (Alabama License No. 1118) advised the Office of Radiation Control (ORC) of an incident that occurred on April 11, 2019 in the permanent shooting room at their facility in Alabaster, AL. The radiographer, working alone, cranked out a 67 Curie Ir-192 source for an exposure and failed to crank the source back in before setting up for the next exposure. "The radiographer's personal dosimeter badge was been sent for emergency processing and the results determined the badge received an exposure of 8.149 Rem. The licensee's preliminary investigation calculated extremity exposure to the left hand of 39.684 Rem and exposure to the right hand of 9.338 Rem. The radiographer is being monitored by a medical physician. Personnel from ORC performed an initial investigation of the incident on the morning of April 12, 2019. The primary cause of the incident appears to be human error. Specifically, the radiographer failed to crank in the source at the conclusion of the exposure; failed to observe the radiation actuated visible alarm; bypassed the audible alarm feature of the shooting room; and failed to observe his survey meter upon entry into the shooting room. The investigation concluded that all safety features were operating properly at the time of the incident. Additional contributing factors are being evaluated at this time. The licensee's written report is pending. "The information in this report is current as of 1000 CDT, April 15, 2019." Notified R1DO (Bicket), NMSS (Rivera-Capella), INES Coordinator (Milligan), and NMSS_Events_Notification email group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2019-04-22
53993 | 0 | AMETEK |  |  |  |  | 2019-04-12 | 2019-04-12 09:31 | 2019-04-12 | PART 21 REPORT - OVERHEATING AND FAILURE OF TRANSFORMERS The following was received via e-mail: "COMPONENT DESCRIPTION: AMETEK part number 80-315382-90, T801 main transformer. "PROBLEM YOU COULD SEE: Overheating and failure of transformers installed in equipment with 0.7 power factor load requirements "CAUSE: The inverters on AMETEK job number C72143 were required to support a 0.7 power factor load. To meet this requirement, CVT capacitors were added which led to overcurrent on the capacitor current windings and overheating. The overheating led to a breakdown in insulation between windings, causing a premature failure of the transformer set and inverter relative to its 40-year qualification life. "EFFECT ON SYSTEM PERFORMANCE: The overheating accelerates the degradation of the insulation between windings and eventually leads to shorting. This will cause an inverter failure and require the load to be transferred to bypass. "ACTION REQUIRED: This is the only instance AMETEK has experienced for this issue. Therefore, action is only required for the equipment on AMETEK job number C72143, located at TVA Sequoyah. New transformers have been provided as replacements that require fewer capacitors, contain additional venting to improve cooling, and include larger winding material to reduce current density. The main transformers (T801) installed in the serial numbers associated with this job (C72143-0111 through 0911) should be replaced to prevent any similar occurrences. "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: AMETEK has enhanced this particular transformer design to improve cooling and reduce capacitor current. Additionally, corrective action #175 has been issued in AMETEK's system. "If you have any questions, please contact Mr. Mark Shreve of the Client Services group at 1- 800-222-9079 or 1-614-846-7500 ext. 6332. mark.shreve@ametek.com." Sequoyah is the only site affected by this Part 21 Report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2019-04-12
53992 | 0 | BROOKE ARMY MEDICAL CENTER |  |  |  |  | 2019-03-13 | 2019-04-11 18:19 | 2019-04-11 | LOST I-125 SEEDS The following is a synopsis from a phone call: At Brooke Army Medical Center, two I-125 seeds were lost on October 16, 2018. One source was 156 microCuries and the second source was 158 microCuries, totaling approximately 314 microCuries at the time. The sources were not realized missing until March 13, 2019, when the activity would have been approximately 28 microCuries each, totaling 56 microCuries. Investigation is ongoing and actions to prevent recurrence are being implemented. There was no significant exposure above dose limits. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-04-19
53991 | -1 | WATERFORD | 3 |  |  | [3] CE | 2019-04-11 02:00 | 2019-04-11 10:28 | 2019-05-17 | CONTROL ROOM ENVELOPE INOPERABLE DUE TO DOOR HANDLE DETACHING "On April 11, 2019, at 0200 CDT the shift operating crew declared the control room envelope inoperable in accordance with Technical Specification (TS) 3.7.6.1 due to the door handle for Door 86 (H&V Airlock Access Door) being detached. Operations entered TS 3.7.6.1 action b, which requires that with one or more control room emergency air filtration trains inoperable due to inoperable control room envelope boundary in MODES 1, 2, 3, or 4, then: 1. Immediately initiate action to implement mitigating actions; 2. Within 24 hours, verify mitigating actions ensure control room envelope occupant exposures to radiological, chemical, and smoke hazards will not exceed limits; and 3. Within 90 days, restore the control room envelope boundary to OPERABLE status. Action b.1 was completed by sealing the hole in Door 86 at 0232 CDT. This event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(D), 'event or condition that could have prevented fulfilment of a safety function of structures or systems that are needed to (D) mitigate the consequences of an accident,' due to the control room envelope being inoperable. "The licensee notified the NRC Resident." * * * RETRACTION ON 5/17/19 AT 1620 EDT FROM MARIA ZAMBER TO BETHANY CECERE * * * "This is a Non-Emergency Notification from Waterford 3. This is a retraction of EN 53991. This event was evaluated in accordance with the corrective action process. The original operability determination of inoperable was made based on a conservative evaluation that with the door handle for Door 86 (Heating and Ventilation Airlock Access Door) being detached, the control room envelope boundary could not perform its safety function. A more detailed engineering evaluation was subsequently performed. This shows that the condition of the door handle being detached is bounded by the most recently performed non-pressurized radiological tracer gas test, as the control room envelope differential pressure was maintained more positive with the detached door handle as compared to that observed during the test. Additionally, the control room envelope differential pressure trends showed no discernable change between the two conditions of the door handle detached or with the opening taped over (resulting in an air tight seal). This information supports the conclusion that with the door handle for Door 86 being detached, the control room envelope boundary remained operable and did not constitute a condition that could have prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident; therefore, this event is not reportable per 10 CFR 50.72(b)(3)(v)(D). "The licensee notified the NRC Resident Inspector." Notified R4DO (Proulx). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-04-11
53990 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-04-08 | 2019-04-10 14:57 | 2019-04-10 | AGREEMENT STATE REPORT - LOST DENSITY GAUGE The following report was received from the Commonwealth of Pennsylvania via fax: "On April 8, 2019, the [Department of Environmental Protection] DEP was notified of a Cs-137 source that was discovered at a metal recycler, reportable per 10 CFR 20.2201(a)(1)(i). "On April 8, 2019, a radiation portal monitor alarmed at a metal recycling facility in Slippery Rock, PA. The load was reading approximately 4 mR/hr at a distance of 4 ft through scrap metal. The load was transferred back to its origin at Mercer Lime and Stone where it could be off-loaded and sorted. DEP representatives oversaw the emptying of the load at Mercer Lime and Stone. An intact gauge was found bolted to a plate. A representative noted bolts for another gauge, but no gauge was found. The found gauge, Nuclear Chicago, series: PNA, model: 5193, serial number: 219, manufactured: 2/8/74, containing 200 mCi of Cs-137, was secured in a building on site. The current activity is 70.7 mCi. The remaining site has been cleared except for a few remaining buildings. "Mercer Lime and Stone has a general license with DEP but did not notify the DEP of intent to terminate their license nor to vacate their licensed location. Upon later review of their license, it was noted they possessed two of the same model gauges, serial numbers 219 and 220. The whereabouts of serial number 220 are unknown at this time. The DEP is currently working to locate the owner of the site, and location of the (still) missing gauge. The DEP will update this event as soon as more information is provided." Event Report ID No.: PA190012 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-04-18
53989 | 0 | ARCELORMITTAL |  |  |  |  | 2019-04-09 11:01 | 2019-04-10 11:34 | 2019-04-10 | SAFETY EQUIPMENT FAILURE - SHUTTER POTENTIALLY STUCK OPEN The licensee reported that there is a potential for a shutter to be stuck open on a bin level gauge. The licensee specifically noted that the shutter arm moves more freely than normal. The following was received via e-mail: "Indiana Harbor's [Radiation Safety Officer] RSO was notified of a problem with a gauge at the IH7 Blast Furnace operations at 1101 CDT on April 9, 2019. This issue has the potential to be a shutter failure. [Source details] Kay Ray model 7064P, serial number 8318, Cs-137, originally 5000 mCi (1978) estimated 2000 mCi remaining. There is no exposure potential. It is installed on the North Lockhopper at the # 7 blast furnace on elevation 13. Upon attempting to unlock the 'North Lockhopper empty' gauge, the shutter arm was moving freely. The position of the shutter is not know, however, the source beam is directed into the hopper if the shutter is open and there are no personnel that can access the beam while the furnace is in operation. The next opportunity to access the gauge will be during the next scheduled outage on June 4 or 5, 2019." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-04-18
53988 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-04-09 | 2019-04-09 15:20 | 2019-04-15 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received from the State of California via e-mail: "On April 9, 2019, the [Radiation Safety Officer] RSO for GeoSolutions in San Luis Obispo, CA notified the RHB [Radiologic Health Branch] Brea office that a moisture density gauge had been reported stolen from his employee's vehicle that was parked overnight at a residence in Orcutt, Santa Barbara County, CA. Reporting person states that a Humboldt Scientific Instrument 5001C nuclear moisture density testing device, serial number 1749, was stolen. The device contained 0.37 GBq (10 mCi) Cs-137 and 1.48 GBq (40 mCi) Am-241. The theft has been reported to local law enforcement, Santa Maria Police report number 2019R03937, and to the local service provider Pacific Nuclear Technology. "The device was in a locked protective case at the time it was stolen; its transport index is 0.2; DOT class 7 type A package. The owner found the chain securing the device to the truck bed was also cut. The operator reported that the Cs-137 source rod was locked in the safe position on the gauge. The device was stolen on 4/9/2019 at an unknown time during the night. RHB will continue to investigate." California 5010 number: 040919. * * * UPDATE AT 2003 EDT ON 4/15/19 FROM L. ROBERT GREGER TO MARK ABRAMOVITZ * * * The following was received via e-mail: "The moisture density gauge that was reported stolen was reported by the licensee to have been recovered on 4/11/19. The gauge, inside its transportation container (the transportation container lock was missing, but the gauge was locked in the shielded position), was found in a trash dumpster at a local convenience store. Police are currently reviewing security camera tapes in an attempt to determine who placed the gauge in the convenience store trash dumpster." Notified the R4DO (Pick) and NMSS (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-04-17
53987 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-04-09 | 2019-04-09 14:39 | 2019-04-09 | AGREEMENT STATE REPORT - LOST THEN FOUND Am-241 FILL LEVEL GAUGE SOURCES The following report was received from the State of Illinois via e-mail: "The Agency [Illinois Emergency Management Agency] was contacted at approximately 1213 CDT on 4/9/19 by the radiation safety officer (RSO) for Heuft USA to advise that a 0.88 Ci shipment of Am-241 sealed sources enroute to their facility did not arrive as expected by April 8, 2019. The shipment was found as of 1330 CDT by the carrier at their terminal in Illinois. "The shipment was not a Cat 1 or Cat 2 quantity. The shipment was labeled White-I and packaged in a 28 pound, 5 gallon, Type A drum. [Prior to being found], the package's last known (physically confirmed) location was the [common carrier's] facility in Columbus, OH on 4/5/19. A manifest was present at [the common carrier's] Chicago Heights facility, indicating it may have arrived there. The RSO for the licensee was the individual who personally packaged the sources and offered them for consignment to [the common carrier]. There was no indication of intentional theft or diversion. "Heuft USA is a licensee of the Agency (IL-01354-22) authorized for the possession, installation and maintenance of Am-241 fill level gauges. This shipment contained (2) QSA Global AMC.17 fill level gauges containing 300 mCi each, (1) XN.240 fill level gauge containing 100 mCi, and (4) AMC.25 fill level gauges containing 45 mCi each. State of Ohio radiation control program staff were notified. "While writing the report, the carrier located the package on their dock and began to finalize the shipment to the licensee. Pending confirmation of receipt by the licensee, this matter is considered closed." Illinois item number: IL190011. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-04-17
53986 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-03-08 | 2019-04-09 08:46 | 2019-04-10 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the Ohio Department of Health (the bureau) via email: "On April 8, 2019, Romanoff Electric informed the bureau that three H-3 exits signs [Manufacturer: SRB TECHNOLOGIES INC; Model: BX-10-WH-S-RD] that were in storage at a project site in Johnstown, Ohio were missing. The signs were acquired in December 2018, and were in storage prior to installation at the job site. The signs were not found during a search of the job site and the licensee's warehouse." Item Number: OH190006 * * * UPDATE ON 4/10/2019 AT 0829 EDT FROM MICHAEL SNEE TO JEFFREY WHITED * * * The state of Ohio provided the following update to the event via e-mail: Source 1: H3 Exit Sign (9.83 Ci; Model Number BX-10WH-S-RD; s/n C157764) Source 2: H3 Exit Sign (9.83 Ci; Model Number BX-10WH-S-RD; s/n C157765) Source 3: H3 Exit Sign (9.83 Ci; Model Number BX-10WH-S-RD; s/n C160439) The state also noted that the licensee is creating new procedures as a corrective action to prevent recurrence. Notified the R3DO (Orth) and NMSS Events Notification, ILTAB, and CNSC (Canada) via e-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-04-17
53985 | -1 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-04-08 13:46 | 2019-04-08 15:17 | 2019-04-10 | AGREEMENT STATE REPORT - SHUTTER STUCK IN OPEN POSITION The following was received by e-mail from the state of Louisiana: On 4/8/19, Georgia Pacific Consumer Products (GA-PAC) reported that an additional level density gauge malfunction was discovered during process unit decommissioning. The first gauge was reported on 3/11/19 via a phone call to Louisiana Department of Environmental Quality (LDEQ) - see EN 53927. This second gauge was reported via e-mail on 4/8/19 to LDEQ as part of the written follow-up to the first gauge. "A level density gauge on a process [unit] had a shutter malfunction. GA-PAC was attempting to inventory and package [the gauge] for disposal. In the lock-out/tag-out process, they discovered the shutter handle would not turn to completely close the shutter. The gauge is a RONAN SA8-C5 device/source holder, S/N 9775GG with a 50 mCi Cs-137 source. "GA-PAC called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. The sources and gauges were packaged by BBP Sales and sent to QSA Global for disposal on 4/2/19. GA-PAC is decommissioning this unit. This is not a radiation exposure hazard and does not pose a health and safety situation for the GA-PAC employees or the general public. "This event is considered closed by LDEQ. This event is being reported to the NRC as required by 10 CFR 30.50(b)(2) and LAC 33:XV341.B." LA Event Report ID No.: LA-190005. * * * RETRACTION AT 1155 EDT ON 4/10/19 FROM JOSEPH NOBLE TO JEFF HERRERA * * * The following information was reported by the Louisiana Department of Environmental Quality via email: "The reported information was not a new event. This was follow up information for two previously reported events." Notified the R4DO (Werner) and NMSS_Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-04-16
53984 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-04-06 09:30 | 2019-04-08 14:25 | 2019-04-08 | AGREEMENT STATE REPORT - DRY SOURCE STORAGE IRRADIATOR SOURCE RACK DID NOT RETRACT COMPLETELY The following was received from the state of New York via fax: "The New York State Department of Health (NYSDOH) was notified that on Saturday, April 6, 2019, at approximately 0930 [EDT], a bearing in the pulley that is part of the 'slack cable' switch/mechanism failed to function as intended. The failure caused the source cable to bind where it passes through the slack cable switch, which prevented the source from reaching its full down/safe position. When the licensee freed the cable from the slack cable switch, the source easily returned to its down/safe position. The radiation levels in the irradiator confirmed that the source was in its shielded position. The licensee repaired the slack cable switch (in a way that will prevent re-occurrence) and cycled the source up and down many times with no further incident. Pall Hauppauge is licensed to possess cobalt 60 for use in a Nordion International panoramic dry [source] storage irradiator. "The licensee sent an email and left a voice mail to the NYSDOH mail log, which was not read or listened to until 0830 [EDT] on Monday morning. The licensee failed to contact the NYS Warning Point who would have then immediately notified responsible individuals within NYSDOH. NYSDOH will conduct a site visit since this is the second time in less than a year that they have had issues with source retraction." The earlier event was on 11/9/18 reported in EN53729. Incident Report#: NY-19-05. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-04-16
53983 | 0 | GENERAL ELECTRIC OF PLEASANTON |  |  |  | 100 KW NTR (TANK) | 2019-04-04 12:50 | 2019-04-05 14:00 | 2019-04-05 | NON POWER REACTOR - REACTOR NOT PROPERLY SECURED "On 4/4/19 at approximately 1250 PDT, it was discovered that the Nuclear Test Reactor (NTR) facility control room console had not been properly secured at the Vallecitos Nuclear Center (VNC) in accordance with license technical specifications and internal procedures. The console key remained in the console and no licensed operator was present. The reactor is considered secured when the console key lock switch is off and the console key is in proper custody. "The reactor was shut down at the time and the key lock was in the off position. The licensed operator exited and locked the control room at 1250 PDT but left the console key at the console failing to secure it in the designated storage safe as required. "No personnel entered the control room until 1345 PDT when an authorized Radiation Monitoring Technician entered, discovered the key and immediately notified a licensed operator. Additional actions are being evaluated as a part of the corrective action program. "No unsafe condition existed, however, the event is being reported pursuant to an inadequacy of an administrative or procedural control in NTR Technical Specification 6.2.2(a)(2) because it could have caused the existence or development of an unsafe condition with regard to reactor operations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | CA | NPR | [5 empty] | 0 | 2019-04-05
53982 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2019-04-05 11:25 | 2019-04-05 12:19 | 2019-05-21 | FITNESS-FOR-DUTY: FALSIFIED PRE-EMPLOYMENT INFORMATION A non-licensed employee falsified pre-employment information. The employee's access to the plant has been terminated. * * * RETRACTION FROM ETHAN HAUSER TO DONALD NORWOOD AT 1456 EDT ON 5/21/2019 * * * "The following event notifications are retracted: EN 53822 reported on 1/11/2019 and EN 53982 reported on 4/5/2019. "Subsequent to the initial notification, further investigation revealed that no new information was discovered that would meet the criteria for reporting under RG 5.62 or NUREG-1304. Further the events were also determined to be limited to an act of personal deception by those applying for unescorted access, without intent to commit or cause events identified in paragraphs I (a) and (d) of Appendix G to Part 73, and is not a programmatic breakdown. Based on this information, and consistent with the NRC memorandum dated May 19, 1995, 'Access Authorization Reportability and Enforcement Issues,' this event does not meet the threshold for reporting. "The NRC Resident Inspector has been notified." Notified R3DO (Cameron) and via E-mail the FFD E-mail group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2019-04-05
53981 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2019-04-04 15:15 | 2019-04-05 07:16 | 2019-04-05 | AGREEMENT STATE REPORT - GAUGE RUN OVER BY BULL DOZER The following was received via e-mail: "On April 4, 2019, the Department [South Carolina Department of Health and Environmental Control] was notified by the licensee at approximately 1515 EDT that one of its gauges had been run over by a bull dozer at a jobsite. The gauge was a Humboldt Model 5001 s/n 941 containing 10 mCi of Cs-137 and 40 mCi of Am-241:Be. The sealed source serial number for the Cs-137 source is 2467GH and the sealed source serial number for the Am-241:Be source is NJ00918. A radiation surveys and wipe tests of the gauge were performed at the scene. There was no removable contamination detected. The gauge was safely transported back to the licensee's facility and placed in storage awaiting disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2019-04-15
53980 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-03-12 10:00 | 2019-04-04 17:36 | 2019-04-04 | AGREEMENT STATE REPORT - POTENTIAL EXCESSIVE EXPOSURE AND SAFETY EQUIPMENT FAILURE The following information was received via e-mail: "Louisiana Department of Environmental Quality (LDEQ) was notified of this event on Monday, April 1, 2019. This event occurred in a manufacturing fabrication shop in a fixed shooting bay. "On Tuesday, March 12, 2019, the Radiation Safety Officer (RSO) and a radiography trainee were shooting welds at the Steel Forgigs, Inc. (SF) site. The RSO stated the QC/QA [Quality Control/Quality Assurance] safety checks had been performed before the 'radiography work' began. During radiography work of shooting welds and exchanging out pipe to be x-rayed, the trainee proceeded to change out the film on the pipe while the RSO went to retrieve a new piece of pipe. The safety alarm/lights were not flashing and the trainee assumed the source had been retracted into the shielded position. However, the trainee's survey meter saturated and his pocket dosimeter went off scale. The lights and alarm were still not responding. The RSO stated 'I knew the trainee did not exceed the 5 REM exposure limit due to my work experience.' "The survey meter was functioning properly when removed from the 'high radiation' field and his pocket dosimeter appeared to function properly when re-zeroed after the off-scale reading. The trainee's personnel monitor was sent to be processed for his personal exposure. The exposure results were 2.488 REM exposure. "The equipment involved in the incident was a QSA 880 Delta, s/n D5843, exposure device with a QSA source model A424-9, Ir-192 source, s/n 71973G with an activity of 19 Ci. "The internal investigation documented there was no excessive exposure to the trainee. However, the late reporting of the incident, not reporting of the incident by regulatory requirement and no commitment to corrective actions to prevent these events from reoccurring in the future are still outstanding. "LDEQ is seeking escalated enforcement actions pertaining to this licensee and NMED incident." Louisiana Event Report ID No.: LA-190005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-04-12
53979 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-04-03 | 2019-04-04 16:50 | 2019-04-05 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following report was received via e-mail: "On April 4, 2019, the Agency was notified by the licensee that one of their radiography crews was unable to retract a source on April 3, 2019, when a jig on a ladder fell on the source tube. The crew contacted the RSO [Radiation Safety Officer]. The RSO, an authorized source retriever, reported to the temporary job site in approximately 20 minutes and retrieved the source. "No member of the general public received an exposure from this event. No additional information has been provided. The radiographers were to be interviewed on April 4, 2019. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: 9670 * * * UPDATE ON 4/5/2019 AT 1222 EDT FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "On April 5, 2019, the licensee provided the following information. The device was a QSA 880D exposure device containing a 62 curie iridium-192 source. The highest exposure received from this event to any of the individuals involved was to the individual who retrieved the source. [The RSO] received 370 millirem whole body dose and his right hand received 350 millirem. No individual exceeded any exposure limits due to this event. The exposure device has been returned to the manufacturer for service and the guide tube has been taken out of service. Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (Kozal) and NMSS Events Notification (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-04-12
53978 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-04-03 | 2019-04-04 15:19 | 2019-04-04 | AGREEMENT STATE REPORT - FIXED GAUGE MISSING SHUTTER The following report was received via e-mail: "On 4/3/19, during preparation to conduct maintenance on a coal chute, workers prepared to isolate a gauge from service to prevent worker exposure to the beam. It was discovered that the gauge was missing its isolation shutter. The RSO [Radiation Safety Officer] and plant personnel conducted an extensive search and investigation of the missing shutter, but it could not be located. A six-month physical inventory of the facilities devices was conducted on 3/26/19 and 3/27/19 and there was no notation of any problems with this gauge on the inventory sheets. The gauge involved is a Texas Nuclear Model 5189 with a 20 mCi Cesium-137 source. "The RSO and job supervisor held a discussion and decided that they could use the shutter from another Model 5189 gauge in the vicinity. The second gauge is used in a continuously operating process line and would have the shutter open for operations. The area around the second gauge will have signage and barricades installed to safely mark the area if future work activities will take place in that location. The shutter from the second gauge was placed on the first gauge and it was tagged out for maintenance of the coal chute. The second gauge remains in the open position during operation of the second process line. "The RSO contacted ThermoFisher Scientific and discovered that because of the age of the gauge, replacement parts could not be obtained. They were provided with a list of third-party service providers to assist with proper repair or removal and disposal of the gauge. The licensee will explore options and inform ODH [Ohio Department of Health] of the actions to be taken." Ohio Item Number: OH190005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-04-12
53977 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2019-04-04 11:55 | 2019-04-04 15:16 | 2019-04-04 | TECHNICAL SUPPORT CENTER VENTILATION NON-FUNCTIONAL "Oyster Creek NGS [Nuclear Generating Station] Tech Support Center [TSC] ventilation is not functional due to a broken belt on exhaust fan FN-843-14. The TSC ventilation system will remain non-functional until fan belt replacement can be completed. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to partial loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-04-04
53976 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-04-04 08:55 | 2019-04-04 10:53 | 2019-04-09 | SAFEGUARDS REPORT Actual entry of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BLAKE MITCHELL TO DONALD NORWOOD AT 1538 ON 4/9/2019 * * * "Farley Nuclear Plant is retracting the one-hour notification made at 1053 EDT, April 4, 2019 under EN 53976. Upon further review, this event was determined to be a program administration human performance error and has been documented in the station's Security Incident Report. The NRC Resident Inspector has been notified." Notified R2DO (Coovert) and by E-mail the 73.71 Safeguards E-mail Group. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-04-04
53975 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-01-08 | 2019-04-04 09:19 | 2019-04-15 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION The following was received via e-mail: "On January 8, 2019, the Agency [Texas Department of State Health Services] was contacted by the license and notified they have some conflicting data that suggest they may have up to three (3) leaking Nickel (Ni) - 63 ten milliCurie sources that may be slightly above the 0.005 microCuries reporting limit. The licensee stated they need to investigate further as a second set of leak tests showed no detectable activity on the same three sources. The three sealed sources in question have been bagged and are slotted for disposal. The licensee will provide additional information as it is received. "On January 25, 2019, the licensee contacted the Agency and stated they had leak tested all similar sources in their possession. The licensee found a total of four sources exceeded the limit. The sources are all Ni-63 containing 10 milliCuries. The licensee stated they will dispose of all leaking sources. The licensee stated it believed the sources were manufactured in Singapore. The sources are used in gas chromatographs. The Agency conducted an on site investigation at the facility on March 11, 2019. During the investigation the licensee stated none of their customers who had been provided a device had reported a source that failed a leak test. "On April 3, 2019, the Agency was notified by the licensee that they were going to restrict access to a room for more than 24 hours due to fixed and removable radioactive contamination levels. The contamination was found while performing surveys in the area in response to leak test results of four Ni-63 sources exceeding the limit (NMED report number 190032). The licensee will perform bioassay sampling of all individuals who had been in the room. The licensee stated they have begun decontamination of the room. Additional information will be provided as it is received in accordance with SA-300." Texas Incident number: 9648 * * * UPDATE AT 1645 EDT ON 4/15/2019 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On April 15, 2019, the Agency [Texas Department of State Health Services] was notified by the licensee that they had found additional contamination in the facility and had closed the facility until a full survey can be completed and any areas found to be contaminated released. The licensee is working on a bioassay plan for the employees." Notified the R4DO (Pick) and NMSS (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-04-12
53974 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-04-01 | 2019-04-03 17:09 | 2019-04-04 | AGREEMENT STATE REPORT - POSSIBLE INTERNAL OVEREXPOSURE The following was received from the State of New York via fax: "The Radiation Safety Officer [RSO] of NRD, LLC, called to report an incident in which three individuals may have been exposed to Americium-241. NRD, LLC has a specific radioactive material license with the NYS [New York State] Department of Health to Manufacture Radioactive Products. Below is a brief description of the information reported so far. "On Monday [4/1/19] evening an individual (Person1) was trying to clean up a 'small rusty contamination' in the change area using a HEPA vac. The vacuum was previously used in a different area (Silver Recovery) area to clean up Americium-241 metal. He turned on the vacuum and noticed it was blowing stuff out. He turned it off and told a second individual (Person 2) to shut the doors. After doing so, Person 2 went into another room. During this time the RSO (Person 3) was notified. Person 3 'stuck his head in the room for a minute.' Person 1 and person 2 were in the area for about a minute. Person 1 was in the area for approximately 20 minutes. "The reading on a nose swab done on Person 1 read 6600 dpm [see update below]. After his clothing was removed and he took a shower and blew his nose, a second swab was done. The reading on the those swabs were 4884 dpm (right nostril), 1729 dpm (left nostril). On day 2 a third set of swab were done with the following reading: 67 dpm (right nostril), 36 dpm (left nostril). "The lab remains closed and there is no work being done. They are trying to set up an access control point to enter the lab. "The RSO indicated he was in communication with REACTS [Radiation Emergency Assistance Center/Training Site]. They suggested the Person 1 and Person 2 see their medical doctors. The bioassays collected were going out today, Wednesday, April 3, 2019. "Based on the results reported for the initial nose swab, this incident is reportable under 10 CFR 20.2202(a)(1). NYSDOH [New York State Department of Health] Incident No. 1278 has been assigned to track this event." New York Event Report ID No.: NY-19-04 Exposure to person 1 may have resulted in an intake five times the occupational Annual Limit on Intake (ALI). * * * UPDATE ON 4/4/19 AT 1055 EDT FROM DESMOND GORDON TO BETHANY CECERE * * * The initial report was incorrect for the nose swab done on person 1 - it read 66,000 dpm, not 6,600 dpm. Notified R1DO (Young), and NMSS_Events_Notification email group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-04-11
53973 | 0 | WEIR VAVLES AND CONTROLS |  |  |  |  | 2018-11-06 | 2019-04-03 17:32 | 2019-04-03 | PART 21 REPORT - RESIDUAL HEAT REMOVAL SYSTEM MOTOR OPERATED GLOBE VALVE EXPERIENCED STEM FAILURES The following was received via e-mail: "This notification is being submitted pursuant to the guidelines of 10 CFR Part 21 to report that a 24in Class 150 Globe valve for RHRSW HX [Residual Heat Removal Service Water Heat Exchanger] Isolation MOV [motor operated valves], E1150F068B at Detroit Edison - Fermi 2, experienced two stem failures. "The site notified WVC USA [Weir Valves and Controls, USA] on November 6 of this issue involving two stems. WVC USA had supplied these stems on orders 20000262-10 and 20012001-10, Detroit Edison PO's [part orders] 4700505700 and 4701149217. A new stem failed after approximately 1 month in service in valve F068B. A replacement stem was installed and failed soon after being placed in service. This second stem failure had previously been in service for approximately three years while installed in sister valve F068A. Both stem breakages occurred at the transition area of the stem backseat and were visually identical. See pictures of failure in Attachment A. In the as found condition, the disc to stem connection appears to have lacked design clearances. The cause of this clearance issue was cleaning of the disc surface where the disc nut is tack welded. The material supplied is A276 410 heat treated and tempered to obtain (269-311 BHN). This material was approved by Powell as an acceptable alternate to the original material A182 F6 (269-311 BHN). During original Part 21 evaluation, testing of the stem material revealed low impact values and reflected effects of temper embrittlement. Other possible contributors to the failure were transition region at stem backseat and the valve service conditions where vibration due to throttling has been experienced. It was determined that although temper embrittlement and other factors may have contributed to the failures, that the lack of design clearance led to the failure of the stems and was not reportable by WVC USA. However, after discussions with Detroit Edison, WVC USA was requested to evaluate the failure considering the effects of temper embrittlement that might lead to future failures. "WVC USA engineering is unable to determine the effects of temper embrittlement for the A276 410 material. Powell engineering was also consulted and there are no known methods to evaluate the potential for failure on the stem in this condition. As noted in NRC Information Notice No. 85-59, tempering in the 700 degrees F to 1050 degrees F range is not recommended because it results in low and erratic impact properties and poor resistance to corrosion and stress corrosion for 410 stainless steel. "The stem failures in this case reflected these low and erratic impact properties based on material testing that was performed by DTE [Detroit Edison] Fermi and WVC USA. The A276 410 materials supplied in this event were tempered at 1025 degrees F and 1050 degrees F. "The best solution is to eliminate the potential for temper embrittlement by using a higher required tempering temperature. The recommendation is to use A276 410 tempered at a minimum of 1100 degrees F. This is also in alignment with Code Case N-62-7. We are in the process of updating our item records to reflect this minimum tempering requirement and expect this action to be completed within one month. "WVC USA is notifying the following sites of this potential issue so that they can evaluate the impact on the safe operation of the plant. "74347-10 Entergy PO 10118969 Site Grand Gulf Item Number P 26126666ASSEMAO_QLA Stem & Disc Assy 14" Qy (1) Shipped 7/28/06 "0020005433-10 Georgia Power Company PO SNG10081312 REV. 2 Site Hatch Item Number P0000419C Stem/Disc Assy 24-300 Globe Valve Qty (1) Shipped 10/29/15 "0020006979-10 Detroit Edison Company PO 4700846295 Site Fermi 2 Item Number P0000455C Stem Bin Gate Valve Qty (1) Shipped 6/29/15 "0020011676-10 Detroit Edison Company PO 4701123403 Site Fermi 2 Item Number P0000455C Stem Bin Gate Valve Qty (1) Shipped 2/14/18 "0020013251-10 Detroit Edison Company PO 4701230062 Site Fermi 2 Item Number P0000283 Stem Globe 24in 150# Qty (1) Shipped 9/19/18 "0020013586-10 Detroit Edison Company PO 4701259926 C0#6 Site Fermi 2 Item Number P0000283 Stem Globe 24in 150# Qty (1) Shipped 11/13/18 "Stem supplied under order 0020013251-10 is currently installed in F068A and order 0020013586-10 was delivered but not installed. F068B valve has been restored by Detroit Edison with a stem which has acceptable properties for the service." The above Part 21 notification affects Grand Gulf, Fermi 2, and Hatch. Point of Contact: Allen Fisher Director of Engineering 978-825-8451 allen.fisher@mail.weir | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-04-03
53972 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-03-21 | 2019-04-03 13:40 | 2019-04-03 | AGREEMENT STATE REPORT - MEDICAL EVENT- ELUATE EXCEEDED BREAKTHROUGH LIMITS ON RUBIDIUM - 82 GENERATOR The following was received from the State of Kentucky via fax. "On Thursday, March 21, 2019, a technologist inadvertently used Ringer's saline as the eluate on a Bracco Rb-82 generator. On March 21, 2019, four (4) patients were imaged using the Rb-82 generator at 0852/0902, 1037/1049, 1143/1156, and 1335/1347 EDT (two infusions per patient). On March 21, 2019, a technologist notified Bracco that their eluate volumes for each patient were decreasing slightly, while the overall activity of each infusion remained the same, this was the inverse of what they normally saw. On the morning of March 22, 2019, routine quality control was performed at 0730 EDT and it was found that the Sr-82 breakthrough measured 18.6 microCuries and the generator expiry limit was exceeded. The technologist inspected the unit's tubing and settings, but found nothing out of the ordinary. The Bracco representative returned the previous day's call and said to check the saline attached to the machine. It was discovered that Ringer's saline had been used. The RSO [Radiation Safety Officer] was notified and the hospital was instructed to discontinue use." Kentucky Event Report ID No.: KY190003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-04-11
53971 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2019-04-02 10:42 | 2019-04-03 12:25 | 2019-04-03 | AGREEMENT STATE REPORT - MEDICAL EVENT - UNDERDOSE ADMINISTRATION OF Y-90 MICROSPHERES The following was received from the Commonwealth of Massachusetts via e-mail: "On 4/2/19, 1430 EDT, the licensee reported a medical event involving Nordion TheraSpheres (SS&D NR-0220-D-131-S) emerging technology for total administered activity that differed from prescribed treatment activity as documented in the written directive by 20 percent or more. A portion of a two-vial Y-90 62 mCi (13 mCi and 49 mCi vials) microsphere therapy treatment delivered to the patient's liver on 4/2/19 was stuck in the catheter causing delivery of approximately 37 mCi Y-90. This was discovered immediately after treatment. The administered dose to the treatment area differed from the prescribed dose by approximately 40 percent. The licensee stated that the primary cause was an equipment malfunction. The first vial of 13 mCi was delivered fully, but only 24 mCi of the second vial containing 49 mCi was actually administered to the patient. The prescribing physician, referring physician and patient have been notified. The licensee stated that there were no negative health effects to the patient due to the situation. No additional Y-90 therapy treatment will be required. Corrective actions will include removal of the suspect equipment (catheter) and return of said equipment to the manufacturer for evaluation. A larger diameter catheter will be used during future therapy treatments. The licensee will submit a written report within 15 days of the discovery date. Agency on-site investigation is pending. This is a next day reportable medical event per regulations. "Investigation ongoing. Agency considers this event docket to still be OPEN." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2019-04-11
53970 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-04-01 | 2019-04-02 18:39 | 2019-04-02 | LOST THEN FOUND CATEGORY 2 RADIOGRAPHY EXPOSURE DEVICE The following information was received via E-mail: "The licensee RSO [Radiation Safety Officer] reported that a Mistras technician lost an INC IR-100 radiography camera, serial number 6744, on April 1, 2019, between approximately 0000 and 0100 PDT. The camera contained an Ir-192 sealed source, number 159E, with 85.3 curies. "The radiography camera was left unsecured on the tailgate of a company darkroom vehicle upon departing the licensee's Long Beach office. The camera was being transported to the Chevron refinery in El Segundo for radiographic operations during the night. The lost camera was reported to the Long Beach office (at approximately 0110 PDT) by the technician upon arrival at the El Segundo refinery, and a radiography crew was sent from the Long Beach office to search the route taken by the first individual. The camera was found and recovered by the radiography crew approximately 0130 PDT on the breakdown lane of limited-access CA Hwy 91 westbound, approximately 4 miles from the Long Beach facility (near Wilmington Ave). "The recovered radiography camera was returned to the Long Beach facility, where a leak test was performed, showing no leakage. The radiography camera was sent to a repair facility for further inspection. RHB [Radiation Health Branch] will investigate the cause of the incident, take appropriate enforcement action, and ensure appropriate corrective actions by the licensee." California 5010 Number: 040119 Notified External: DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, and EPA EOC. Notified External via E-mail and/or FAX: Mexico, FDA EOC, NuclearSSA, FEMA National Watch Center, DNDO-JAC. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-04-10
53969 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-03-15 16:00 | 2019-04-02 13:47 | 2019-04-02 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGES The following was received via fax: "The Radiation Safety Officer [RSO] for Parsons called to report that four (4) generally licensed fixed slurry moisture gauges were missing. Each gauge contained 90 microCuries of cesium-137. All devices were of Ronan Engineering RLL-1 1619 5L2A3 make and model, and sources were of Ronan SRC-PT-CS-90UCL make/model. The device serial nos. are: DX-520 with source s/n DE-520; DX-814 with source s/n DE-814; DX-816 with source s/n DE-816; and DX-818 with source s/n DE-818. These sources were inadvertently left at 522 Gerelock Road, Camillus, New York 13031 following completion of extensive contract work for Honeywell International. The sources were identified as lost by the RSO on March 15, 2019, at 1600 EDT. These sources were not found upon the RSO's return to the Camillus facility, and the RSO reported the lost sources to NYSDOH [New York State Department of Health] on March 18, 2019, at 0830 EDT. Parsons will be contacting Honeywell International and other contractors at this facility to locate the missing sources. NYSDOH Incident number 1272 assigned to track this event." New York Event Report ID No.: NY-19-01 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-04-10
53968 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2019-03-31 20:06 | 2019-04-01 06:40 | 2019-05-15 | UNANALYZED CONDITION DUE TO ECCS LEAKAGE "At 2006 [MST], on 3/31/2019, the Palo Verde Nuclear Generating Station Unit 1 Shift Manager was informed that leakage was measured from the Train A Emergency Core Cooling System (ECCS) piping at approximately 100 ml/minute through a High Pressure Safety Injection (HPSI) A drain valve. This value exceeds the assumed 3000 ml/hour ECCS leakage for a large break loss of coolant accident analysis. At 0230 [MST] on April 1, 2019, the valve was flushed and the leakage reduced to 10 ml/minute (600 ml/hour) and was no longer above the limit of the safety analysis. This condition is being reported as an unanalyzed condition per 10 CFR 50.72(b)3)(ii)(B) and a condition that could have prevented the fulfillment of a safety function to the control the release of radioactive material per 10 CFR 50.72(b)(3)(v)(C). This event did not result in an abnormal release of radioactive material. "Notification received by Caty Nolan and emailed to HOO.HOC@NRC.GOV The NRC asked a followup question: Why was the criterion for Control of Radioactive Material selected? per the PVNGS Unit 1 Shift Manager, this criterion was selected due to the potential of exceeding offsite dose projections, post recirculation, following a Design Basis Accident." The resident inspector has been notified. * * * UPDATE ON 05/15/19 AT 1417 EDT FROM SEAN DORNSEIF TO BETHANY CECERE * * * "An engineering evaluation concluded that the as-found ECCS leakage would not have degraded the performance of the Pump Room Exhaust Air Cleanup system; therefore, it remained operable. "The evaluation also concluded that the as-found leakage was within the analysis margins for HPSI pump hydraulic performance and containment flood level following a Large Break Loss of Coolant Accident; therefore, the ECCS also remained operable. "Based on the above information, the condition identified on March 31, 2019, was an unanalyzed condition per 10 CFR 50.72(b)(3)(ii)(B), but did not prevent the fulfillment of the safety function of the structures or systems that are needed to control the release of radioactive material per 10 CFR 50.72(b)(3)(v)(C). "The NRC resident inspectors have been informed." Notified R4DO (Proulx). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) |  |  | 0 | 2019-04-01
53967 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-03-30 21:30 | 2019-03-31 00:17 | 2019-03-31 | MANUAL REACTOR TRIP DUE TO MSIV FAILING CLOSED "At 2130 [EDT] on March 30, 2019, with Unit 2 in Mode 1 at 30 percent reactor power, the reactor was manually tripped due to a main steam isolation valve failing closed. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam lines through the steam dumps and into the condenser. "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "Unit 1 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified." | 0 | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2019-03-31
53966 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-03-30 17:47 | 2019-03-30 21:06 | 2019-03-30 | MANUAL REACTOR SCRAM AND SPECIFIED SYSTEM ACTUATION "At 17:47 Eastern Daylight Time (EDT) on March 30, 2019, with Unit 2 in Mode 1 at approximately 23 percent reactor power and main turbine startup in progress coming out of a refuel outage, a high temperature was sensed at main turbine bearing #9. As a result of and to arrest the high temperature condition, the main control room inserted a manual reactor scram. "All control rods inserted as expected during the scram. When the scram was inserted, reactor water level dropped below the Low Level 1 actuation setpoint. Per design, the Low Level 1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. "The main control room manually closed all Main Steam Isolation Valves (MSIVs), in anticipation of a low vacuum prior to the Group 1 automatic closure signal being received. High Pressure Coolant Injection (HPCI) was aligned for pressure control and Reactor Coolant Isolation System (RCIC) was aligned for level control. The Reactor Coolant Sample Line Isolation valves closed as expected on low main condenser vacuum. "All systems responded as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) for RPS actuation and 10 CFR 50.72(b)(3)(iv)(A) as an event that results in valid actuations of the Primary Containment Isolation System. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." At the time of notification, decay heat was being removed by the condenser through one open MSIV and a feedwater pump running. | 0 | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-03-30
53965 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-03-29 | 2019-03-29 16:23 | 2019-04-06 | AGREEMENT STATE REPORT - LOSS OF AN I-125 SEED The following was received from the State of Florida via email: "Received a call from Adventist Health to report the loss of an I-129 seed that was removed from a patient. According to [Adventist Health], the seed was removed on 2/19/2019 and discovered missing on 2/20/2019, all attempts to locate the seed have been unsuccessful. It is believed that the seed was discarded with the medical waste and sent to the incinerator. A preliminary report will be sent to [the Florida Bureau of Radiation Control] as soon as possible, and followed up with the official report from the hospital when their investigation is complete." Florida Incident Number: FL19-047 * * * UPDATE ON 4/5/2019 AT 1602 EDT FROM TIM DUNN TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "Adventist Health reported the loss of an I-125 seed that was removed from a patient. The seed was removed [from the patient] on Feb. 19th and discovered missing on Feb. 20th, all attempts to locate the seed have been unsuccessful. It is believed that the seed was discarded with the medical waste and sent to the incinerator. "There was no adverse outcome in patient care from this incident. The seed was either disposed of in biohazard or normal trash. In either case, the portal monitors would not have measured the radiation emitted from the seed due to the low activity. No personnel or general public exposure would have been significant based upon the low exposure rate and the nature of controlled biohazard waste. The waste was incinerated. No environmental impact is expected. "Corrective actions taken as a result of the loss of this source: 1) Surgery will survey the specimen when placed in the bag before sending to imaging. Education on this process has occurred to ensure compliance. 2) X-ray will scan the specimen placed in the bag with a survey meter when obtaining the specimen x-ray, prior to going to pathology. Education on this process has occurred to ensure compliance. 3) Pathology will survey the specimen upon receipt to confirm the seed is present. Reeducation on this process has occurred to ensure compliance." This event was previously reported as a loss of an I-129 seed, which was incorrect. Seed activity: 241 microCuries Notified R1DO (Young) and NMSS Events and ILTAB (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-04-08
53964 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-03-29 11:00 | 2019-03-29 15:44 | 2019-03-29 | AGREEMENT STATE REPORT - LOST TROXLER DENSITY GAUGE "At around 1:50 p.m. EDT, [the radiation safety officer] of Meskel Associates called to notify the BRC [Bureau of Radiation Control] of the loss of a Troxler Soil Moisture Density Gauge Model 3440 S/N 17405, source numbers 507-6784 & 47-12827. The gauge fell off of the back of a pickup truck because the tailgate was down and the gauge was not secured. No injuries were reported, the licensee checked with FHP for collision reports. Five people from the licensee looked for it, none found it." Florida Incident Number FL19-046 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-04-08
53963 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-03-05 | 2019-03-29 11:01 | 2019-03-29 | AGREEMENT STATE REPORT - INCORRECT SOURCE STRENGTH ENTERED RESULTING IN OVERDOSE OF 20 PERCENT The following report was received from the North Carolina Division of Health Service Regulation via email: "A prostate patient returned for a 30 day post treatment review and CT scan. Licensee Physics Group reviewed the Post Op Plan with the Intended Plan. It was found that when the Intended Plan was entered into the planning software, a dosimetrist entered an incorrect source strength into the planning system, causing the planning system to appear to be implanting weaker seeds than were being implanted resulting in an over dose of 20 percent. "Event Date: 3/5/19 Discovered Date: 3/28/1 Prescribed dose: 164.85 mCi Administered dose: 213.15 mCi Isotope: PD-103. Target organ: Prostate Referring Physician notified on: 3/28/19 Patient notified on: 3/28/19 Effects/Outcome to the Patient: None anticipated. Physician will monitor patient for side effects. Notifications & Generic Implications: None. Corrective Action: Procedure revision. "A reactive inspection was conducted today [by the North Carolina Division of Health Service Regulation]. Following this entry into NMED we [the North Carolina Division of Health Service Regulation] would like to request the event be closed and complete. We [the North Carolina Division of Health Service Regulation] have concluded our investigation. "NC Tracking Number: 190011" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-04-08
53962 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2019-03-28 16:54 | 2019-03-28 20:55 | 2019-03-28 | AUTOMATIC ACTUATION OF THE PRIMARY CONTAINMENT ISOLATION SYSTEM AND THE REACTOR PROTECTON SYSTEM "At 1654 EDT on March 28, 2019, with Unit 1 in Mode 3 at 0 percent power, an actuation of the Primary Containment Isolation System occurred, closing the outboard Main Steam Isolation Valves (MSIVs) due to a low condenser vacuum signal. The MSIVs had been manually closed, per procedure, during the shutdown evolution to address drywell leakage. The inboard MSIVs had not been reopened when the isolation occurred. "Subsequently, at 1658 EDT a Reactor Protection System (RPS) actuation occurred due to reactor water level dropping below the actuation setpoint. All control rods were inserted at the time of the actuation. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in valid actuations of the Primary Containment Isolation System and the Reactor Protection System. "There was no impact on the health and safety of the public or plant personnel. The safety function of both the MSIVs and the RPS had already been completed at the time of the event. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-03-28
53961 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2019-03-28 14:50 | 2019-03-28 15:07 | 2019-03-29 | UNUSUAL EVENT DECLARED DUE TO RCS UNIDENTIFIED LEAKAGE At 1450 EDT on March 28, 2019, the licensee observed that the Unit 1 unidentified Reactor Coolant System (RCS) leakage was greater than 10 gallons per minute (gpm) for greater than or equal to 15 minutes. The licensee declared an Unusual Event in accordance with their EAL SU 5.1. The licensee initiated a unit shutdown in accordance with their procedures and the unit was approximately 58 percent reactor power at 1507 EDT, with unit shutdown in progress. The licensee also received an alarm due to increasing Drywell Pressure at 1.7 pounds drywell pressure. At 1600 EDT the licensee called with an update. Unit 1 was still in an Unusual Event with the unit at 37 percent power with the shutdown continuing. Drywell Pressure had decreased to 0.8 pounds. At 1603 the licensee scrammed Unit 1. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 3/28/2019 AT 1808 EDT FROM MARK TURKAL TO THOMAS KENDZIA * * * "At 1437 EDT on March 28, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, a Technical Specification-required shutdown was initiated due to indication of a leak in the drywell. Technical Specification Action 3.4.4.A, Unidentified Reactor Coolant System (RCS) leakage increase not within limit, requires RCS leakage to be reduced to within limits within 8 hours. "It is expected that the leakage would not have been reduced to within limits within the required Technical Specification completion time; therefore, this event is being reported in accordance with 10 CFR 50.72(b)(2)(i). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." * * * UPDATE ON 03/29/19 AT 0302 EDT FROM TOM FIENO TO BETHANY CECERE * * * At 0259 EDT on March 29, 2019, the Unusual Event was terminated because RCS leakage was reduced to less than 10 gallons per minute. The most recent leakage rate measured at 0225 EDT was 3.9 gpm. The source of the leak will be identified when plant conditions allow containment entry. No elevated radiation levels were observed during this event. Drywell pressure is currently 0.0 psig. Unit 1 is in Mode 4. The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser), NRR EO (Miller), IRD MOC (Grant), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 58 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) |  |  | 0 | 2019-03-28
53960 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2019-03-25 | 2019-03-26 16:28 | 2019-03-26 | AGREEMENT STATE - LOST TRITIUM EXIT SIGNS The following is a summary of information received from the State of Nebraska: On March 26, 2019, the Nebraska Department of Radioactive Materials received a letter dated March 25, 2019, from the licensee (Flint Hills Resources) concerning the loss of two tritium exit signs, each with an activity of 17.51 Curies. Two H-3 exit signs were lost during recent construction of additional warehouse space on an existing building. One sign was over a personnel door on the wall demolished for the new space and one was on a personnel door proximal to the construction area. NE Item Number: NE190002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-04-03
53959 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-03-26 10:30 | 2019-03-26 16:08 | 2019-03-26 | REPORT OF DEGRADED CONDITION DUE TO LEAKING VALVE "On 3/26/2019 at 1030 CDT Engineering evaluation determined that Traversing lncore Probe (TIP) System test results related to Leak Rate Testing of 2-CKV-76-653, TIP Purge Header Check Valve, during the Unit 2 Refueling Outage resulted in a reportable condition. On 3/24/2019 at 1558 CDT, Leak Rate Testing identified a [local leak rate test] LLRT failure of 2-CKV-76-653. The gross leakage Leak Rate value exceeded the Technical Specification allowable value for Type C valves of less than 0.6 [allowable leakage] La. "This constitutes an 8-hour NRC notification in accordance with 10 CFR 50.72(b)(3)(ii)(A) - Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The short-term corrective actions include repairing the valve such that it passes the test. The valve needs to be repaired before the unit can change modes. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2019-03-26
53958 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-03-22 | 2019-03-25 18:05 | 2019-03-25 | AGREEMENT STATE REPORT - LOST AND FOUND RA-223 PACKAGE The following was received via e-mail: "The Department [Colorado Department of Public Health and Environment] received an e-mail notification on March 25, 2019, from Cardinal Health reporting a lost and found package of Ra-223. On March 22, 2019, the package was suspected to have fallen out of a [common carrier] truck and onto a member of the public's lawn located a few blocks away from the Cardinal Health Facility. The member of the public returned the package to the doorstep of Cardinal Health later that day (3/22/19). No signs of damage to the package were identified. Cardinal Health performed wipes for removable contamination and exposure rate surveys and determined there was no outer or inner contamination and all of the safety seals remained intact. More details are forthcoming." The activity of the shipment is unknown at this time, however, it is assumed to be less than CAT 3. The State of Colorado will update the event when the activity has been determined. Colorado Event Report No: CO190005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-04-02
53957 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-03-21 | 2019-03-25 17:53 | 2019-03-25 | AGREEMENT STATE - STUCK OPEN GAUGE SHUTTER The following was received via e-mail: "On March 25, 2019, the agency [Texas Department of State Health Services] reviewed a voicemail left on an investigator's office phone line in which a licensee reported a stuck shutter on a gauge. The gauge is a Thermo Fisher Scientific model 7062BP, with serial number S99G0101, containing a 100 millicurie Cesium-137 source with serial number 6551GQ. The shutter is stuck in the open position. Open is the normal operating position. The gauge is located on a 6" line and no exposures are anticipated as a result of this malfunction. The manufacturer has been contacted and service will be scheduled. Updates will be sent in accordance with SA-300." Texas Incident: I-9668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-04-02
53956 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-03-04 | 2019-03-25 16:37 | 2019-03-25 | AGREEMENT STATE - LEAKING ELECTRON CAPTURE DEVICES The following was received via e-mail: "The department [Colorado Department of Public Health and Environment] received an e-mail notification on March 7th, 2019 reporting two leaking Electron Capture Devices (ECD's). The [ECD's] are associated with Agilent model G239765505 with serial numbers: U1186 and U6642. The semi-annual leak test results show 35300 picocurie/sample for serial number U1186 and 17100 picocurie/sample for serial number U6642. The wipe test results were received by Test America on March 4, 2019. "Test America reported that the ECD's were removed from use and the instruments on March 4, 2019 and sent to Detector Service Center, LLC for cleaning and repair. "Test America performed surveys for the affected machines and cleaned with a radiacwash solution. A wipe test was done on the instruments and counted by Gas Flow Proportional Counter low background instrument which indicated no removable contamination present. A direct survey with a Ludlum Model 3 Giger Muller detector indicated no fixed contamination. The completion date was reported to be March 5, 2019. "Test American has removed the leaking ECD's and will continue 6-month wipe tests as required." Colorado Event Report ID No.: CO190004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-04-02
53955 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2019-03-25 04:02 | 2019-03-25 11:14 | 2019-03-25 | AUTOMATIC START OF FOUR EMERGENCY DIESEL GENERATORS "At 0402 Eastern Daylight Time (EDT) on March 25, 2019, an actuation of the four Emergency Diesel Generators (EDGs) occurred. At the time of the event, Unit 1 was in Mode 1 at approximately 100% power and Unit 2 was in Mode 4 at 0% power. Unit 2 was in the process of aligning the electrical distribution system to power the emergency buses via the Unit Auxiliary Transformer (UAT) in accordance with plant procedures. It was determined that a fault occurred on the power path between the 230 KV switchyard and the UAT. This caused a main generator differential lockout relay to actuate; thereby starting the EDGs. All emergency buses remained energized from offsite power via the Startup Auxiliary Transformer and, therefore, the EDGs did not tie to their respective buses. The EDGs responded per design to this event. This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in valid actuation of the EDGs. Due to the shared configuration of the Brunswick electrical system, both Unit 1 and Unit 2 are affected. "The Unit 2 main generator lockout was reset and the EDGs have been restored to standby condition. Troubleshooting activities to determine the cause of the fault are in progress. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-03-25
53954 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2019-03-24 14:45 | 2019-03-24 17:40 | 2019-03-24 | REACTOR AUTOMATIC TRIP ON TURBINE TRIP "On March 24, 2019, at 1445 EDT, Indian Point Unit 2 automatically tripped on a turbine trip due to a loss of excitation. All control rods fully inserted and plant equipment responded normally to the unit trip. This RPS [reactor protection system] actuation is reportable under 10 CFR 50.72(b)(2)(iv)(B). "The auxiliary feedwater system actuated following the automatic trip as expected. This specified system actuation is reportable under 10 CFR 50.72(b)(3)(iv)(A). During the event offsite power remained available and stable. No primary or secondary reliefs lifted. Unit 2 is in Mode 3 at normal operating temperature and pressure. Decay heat removal is via the steam generators to the atmospheric steam dumps. No radiation was released. "Indian Point Unit 3 was unaffected by this event and remains defueled in a scheduled refueling outage. "A post trip investigation is in progress. "The licensee has notified the NRC Resident Inspector" The New York State Public Service Commission, Consolidated Edison System Operator, and New York State Independent System Operator were also notified. | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-03-24
53953 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-03-24 01:59 | 2019-03-24 05:23 | 2019-03-24 | MANUAL REACTOR SCRAM DUE TO DEGRADING CONDENSER VACUUM "At 0159 [EDT], with Unit 2 in Mode 1 at 25 percent power, the reactor was manually tripped due to degrading condenser vacuum. After the turbine was tripped, the station service electrical buses did not transfer to alternate supply resulting in loss of the condensate feedwater system and level being controlled by the RCIC system. "Operators responded and stabilized the plant. Reactor water level is being maintained via the RCIC system. "Pressure is being controlled and decay heat is being removed by the HPCI system in pressure control mode. Unit 1 is not affected. "Additionally, an actuation of the primary containment isolation system occurred during the reactor scram. The reason for the actuation was a group II isolation signal was received on reactor water level and a group I isolation was received on decreasing vacuum. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non- emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Additionally, this event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the primary containment isolation system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-03-24
53952 | -1 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-03-21 | 2019-03-22 14:22 | 2019-04-24 | AGREEMENT STATE REPORT - FAILED MOISTURE GAUGE SHUTTER The following was received from the Commonwealth of Pennsylvania via e-mail: "The licensee reported that on March 21, 2019, the Berthold Technologies Model LB-7 410 moisture gauge containing 300 milliCuries of americium-241 was not able to operate as designed; the shutter locking mechanism cylinder was able to be pulled out of the gauge. The gauge was being removed from the east side of #3 Blast Furnace to the storage area at the Blast Furnace spares building. A service provider was already scheduled on site to observe removal and transport of the gauge. A contract employee working with the service provider stated that the cylinder was able to be pulled out of the gauge. The cylinder was never fully removed, but if it was, this would allow the shutter to be manually opened or closed. The cylinder locking device was depressed by the service provider employee and it is currently in that condition. The shutter can't be moved with the cylinder depressed. The gauge is currently locked in the storage area at the Blast Furnace spares building. All work was performed using ALARA principles and at no point were employees exposed to excess levels of radiation. Survey results indicated no abnormal amounts of radiation in the area before, during, or after the removal of the device. Berthold has been contact for repair or replacement." PA Event Report ID No: PA19001 * * * RETRACTION FROM THE JOHN CHIPPO TO CATY NOLAN ON 4/24/19 AT 1059 EDT * * * The following was received via fax: "A follow-up interview and review of the operation of the locking mechanism was conducted with the contract employee. It was determined that the contract employee was unfamiliar with the operation of the locking mechanism at the time of the removal and that the cylinder never was able to be pulled out of the gauge. Based on this investigation, it has been determined that there was not a failure of the locking mechanism or shutter during the removal of the gauge on March 21, 2019. Therefore, this event should be retracted from NMED." Notified R1DO (Lilliendahl) and NMSS Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-04-01
53951 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2019-03-18 | 2019-03-21 15:44 | 2019-03-21 | AGREEMENT STATE REPORT - GENERATOR LOST IN TRANSIT The following was received from the state of George via e-mail: "On January 17, 2019, GE Healthcare in Atlanta (GA 1166-1) consigned a Mo-99/Tc-99m generator (5.14 mCi at the time of shipment) to [common carrier] for delivery to Medi-Ray in Tuckahoe, NY for recycling (the trip included a transit stop in Charlotte, NC). As of March 20, 2019, the device has not arrived at its final destination. On March 18, 2019, [the common carrier] formally notified GE Healthcare that the device was lost in transit. "This information was received on March 20, 2019." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2019-03-29
53950 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2019-03-19 20:00 | 2019-03-21 16:04 | 2019-03-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received from the state of Alabama via fax: "On March 20, 2019 at approximately 0800 [CDT], [an individual] of Alabama licensee TTL, lnc. notified the Alabama Office of Radiation Control [Agency] that gauge make and model Troxler 3440P was stolen from a technician's vehicle between approximately 2000 [CDT] March 19, and 0500 [CDT] March 20, 2019. The technician was working at a temporary job site in Auburn, AL, and the truck parked in the hotel parking lot. [The individual] reported that the technician stored the gauge in a gauge box; the gauge box was appropriately secured to the truck bed. The technician reported the theft to the local police department before contacting the Agency. The Agency has no further information regarding the whereabouts of this gauge as of today, March 21, 2019. "TTL, Inc. is authorized to possess gauges under Alabama license 512. The stolen gauge is identified as Troxler model 3440P [serial number] 72314, with maximum source activities of 10 mCi Cs-137 and 50 mCi Am/Be-241." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2019-03-29
53949 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-03-20 | 2019-03-21 11:14 | 2019-10-14 | AGREEMENT STATE REPORT - FIXED GAUGE STUCK SHUTTER The following report was received from the state of Texas via e-mail: "On March 21, 2019, the licensee notified the Agency [Texas Department of State Health Services] that during routine shutter checks on March 20, 2019, it had discovered that the shutter on one of the Ronan Model SA-1 gauges (SN: M-3824) was stuck in the open position. Open is the normal operating position for this gauge. The gauge contains a cesium-137 source with a calculated current activity of 10 milliCuries. Due to the location of the gauge, there is no increased risk of exposure. The licensee plans to replace the gauge." Texas Incident #9667 * * * UPDATE AT 1518 EDT ON 10/14/19 FROM MATTHEW KENNINGTON TO JEFF HERRERA * * * The following update was received from the Texas Department of State Health Services via email: "Licensee contacted the Agency on October 9, 2019, to report that the vendor was successfully able to close the stuck shutter and the old source is being packaged and prepared for disposal. The gauge was replaced with a Vega SHLD-1. File is closed." Notified the R4DO (Kellar) and NMSS Events (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-29
53948 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2019-03-20 | 2019-03-20 14:14 | 2019-03-20 | AGREEMENT STATE REPORT - CONTAMINATED RADIATION WORKER The following was received from the Oklahoma Department of Environmental Quality via email: "A person administering a dose of I-131 to a cat at Oklahoma State University (OK-00237-03) was found to have contamination on the palm of one hand after the injection. According to the licensee, the contaminated individual is a radiation worker. The amount of material on the individual is estimated at 0.17 microCuries and it is believed to have been on the person for 15 to 30 minutes. After the discovery, the person was decontaminated, which reduced the radiation level to background. The [contaminated individual] will be bio-assayed tomorrow." Inspection number 19-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2019-03-28
53947 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2019-03-19 15:10 | 2019-03-19 16:02 | 2019-05-07 | SAFEGUARDS REPORT Safeguards material was discovered in an unapproved container. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 05/07/19 AT 1336 EDT FROM BRAIN MCWILLIAMS TO JOANNA BRIDGE * * * "On completion of the initial investigation, it was determined that a number of factors existed regarding the storage of the material labeled as Safeguards Information. With these factors in mind, this incident has been determined to be a 24 hour loggable entry and not one hour reportable. Therefore, Event Number 53947, made on 03/19/2019, is being retracted. "The NRC Senior Resident Inspector has been notified." Notified: R1DO (Gray) and Safeguard Group (e-mail). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-03-19
53946 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-02-24 | 2019-03-19 12:13 | 2019-03-19 | AGREEMENT STATE REPORT - SOURCE NOT CONTROLLED WHILE VEHICLE IMPOUNDED The following was received from the state of Texas by email: "On February 25th, 2019, the Agency [Texas Department of State Health Services] was notified by a licensee that control was lost of a Spec 150 (SN: 2472) radiography camera containing a 49 Curie iridium-192 source (Source SN: ZL1103, model G-60 manufactured by SPEC) as the result of an employee arrested for driving while intoxicated [in Odessa, TX]. The vehicle containing the source was impounded. The keys to the vehicle were left with the impound yard. The vehicle was locked, alarm armed, in a fenced lot, behind a locked gate, and under video surveillance. Keys to the darkroom, where the source was stored, were located in the center console of the vehicle. No individuals accessed the vehicle while in the impound lot. The vehicle was retrieved by the licensee shortly after being notified of the arrest and impounding. The source was out of the licensee's control for approximately eleven hours. No exposures occurred as a result of this event." TX Incident #: 9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-27
53945 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-03-18 | 2019-03-19 10:54 | 2019-03-19 | AGREEMENT STATE - EQUIPMENT DISABLED AND FAILED TO FUNCTION AS DESIGNED The following was received from the Commonwealth of Pennsylvania via fax: "On March 19, 2019, the licensee informed the Department [PA Department, Bureau of Radiation Protection] of a fixed gauge becoming disabled during routine source movement. It is reportable per 10 CFR 30.50(b)(2). Event location is Koppel, PA. "During the process of installing a Co-60 source rod and moving it from a transfer shield to a gauge and industrial process mold, the licensee observed difficulty in getting the source rod to insert into the mold. It is suspected that the rod is slightly bent. The rod was retracted into the fully shielded position in a spare transfer shield. The transfer shield containing the Co-60 rod was then taken to a designated storage area where it is secured from unauthorized access. A service provider has been contacted for possible repair or replacement. No exposures over regulatory limits occurred. "Radionuclide: Co-60 Manufacturer: Berthold Technologies Source Model: P 2608-100 Gauge Model: LB 300 ML Source Serial Number: unknown at this time Activity: approximately 12 milliCuries "The rod has been securely stored and placed out of service until repairs or return can be accomplished by a licensed service provider. The Department has scheduled a reactive inspection. More information will be provided when available. "PA Event Report ID No: PA190009" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-03-27
53944 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-03-19 01:40 | 2019-03-19 07:41 | 2019-03-19 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "At 0140 [EDT] on 03/19/2019, while the unit was at approximately 1% power and 154 psig pressure in MODE 2, it was discovered that Unit 2 High Pressure Coolant Injection (HPCI) was INOPERABLE. HPCI does not have a redundant system, therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." Unit 2 entered LCO 3.5.1.c for the HPCI being inoperable. There is no effect on Unit 1. | 0 | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-03-19
53943 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2019-03-05 | 2019-03-18 14:09 | 2019-03-18 | AGREEMENT STATE REPORT - SCRAP METAL WITH RADIUM DISCOVERED The following was received from the state of New Jersey by email: "The Pennsylvania Department of Environmental Protection informed the New Jersey Department of Environmental Protection that a load of scrap metal from the John Blewett company in Howell, New Jersey set off the radiation alarm at Sims Metal Management in Morrisville, Pennsylvania. Sims rejected the load and it was returned to Blewett in Howell via a U.S. DOT special permit. Once returned to Blewitt, the load was dumped and what appeared to be the instrument panel from a World War II era plane was found to be the cause of the elevated readings. Based on readings taken at the site, it is estimated that the panel contains 61 microCi of Ra-226. The highest reading seen was 12.5 mR/hr on contact. Some of the glass covering over a gauge was broken. A gross wipe test indicated removable contamination was present. Those individuals who had touched the panel were checked for contamination or advised to check. The area where the panel had been originally placed was also checked, with slightly elevated readings discovered. All surfaces were cleaned to background levels, as well as the area where the panel had been originally secured. The panel and all items involved in the clean-up were placed in a five-gallon bucket and will be secured pending proper disposition through a waste broker." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2019-03-26
53942 | -1 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-03-17 07:35 | 2019-03-17 14:10 | 2019-04-23 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "At 0735 CDT on March 17, 2019, the High Pressure Coolant Injection (HPCI) system was isolated due to a water-side leak from the HPCI Gland Seal Condenser. Unit 3 declared the HPCI system Inoperable and entered Technical Specification LCO 3.5.1 Condition C with required actions to verify the Reactor Core Isolation Cooling system is Operable, and to restore the HPCI system to Operable status within 14 days. All other Unit 3 Emergency Core Cooling Systems (ECCS) remain Operable. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(V)(D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' This is also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(V)(D). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified of this event." * * * RETRACTION FROM WESLEY CONKLE TO HOWIE CROUCH ON 4/23/19 AT 1549 EDT * * * "ENS Event Number 53942, made on March 17, 2019, is being retracted. "NRC Notification 53942 was made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 (b)(3)(v)(D) were met when the licensee discovered an event, that at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "At 0735 CDT, on March 17, 2019, during the performance of a routine surveillance, a momentary pressure transient of 844 psig from the Feedwater system was introduced into the High Pressure Coolant Injection (HPCI) system discharge and suction piping that ruptured the seal on the gland seal condenser and flooded the U3 HPCI Room. Unit 3 HPCI was declared inoperable due to isolation of the waterside of the HPCl system. "On April 11, 2019, a Past Operability Evaluation was completed which determined that the HPCI System remained operable. The evaluation of the potential pressure transient and room flooding concluded that the HPCI System could have performed its specified safety function of vessel injection throughout the time that the gland seal was ruptured. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(D). "TVA's evaluation of this event is documented in the Corrective Action Program in Condition Report 149973. "The licensee has notified the NRC Resident Inspector." Notified R2DO (Ehrhardt). | 0 | 0 | 47 | 0 | 0 | 47 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-03-17
53941 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2019-03-16 11:00 | 2019-03-16 13:42 | 2019-03-16 | LOSS OF TONE ALERT RADIO TRANSMISSION TOWER "At approximately 1100 CDT on March 15, 2019, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning due to evacuating their office in Omaha as a result of local flooding. This affects the tone alert radios used to notify the public in event of an emergency condition. Loss of function of this tower is reportable at 1100 CDT on March 16, 2019, when the tower could not be restored within 24 hours of the loss. This condition is reportable under 10 CFR 50.72(b)(3)(xiii). A backup notification method is available and will be utilized for notifications if needed. "A return to service time for the Shubert tower is not currently available. "The NRC Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-03-16
53940 | 0 | CA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2019-03-14 | 2019-03-15 17:37 | 2019-03-15 | AGREEMENT STATE - UNDER-DOSAGE TO PATIENT The following was received via e-mail: "On March 15, 2019, the University of California Los Angeles (UCLA) notified the Radiologic Health Branch that a medical event involving Y-90 TheraSphere had occurred on March 14, 2019. A patient was prescribed 120 Gy to the left lobe of their liver with Y-90 TheraSpheres. However, the authorized user (physician) was only able to deliver 80.9 Gy (67.4 percent of the prescribed dose) due to suspected complications with the delivery system. UCLA's Office of Environment, Health and Safety (EH&S) team will continue to investigate and notify the BTG Radiation Safety Officer (RSO) group to examine the delivery system. "The patient was notified of the under-dosage and potential continuation of their treatment. The patient was discharged in a stable condition." CA 5010 No.: 031419 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-03-25
53939 | 0 | LA DEPT OF ENVIRONMENTAL QUALITY |  |  |  |  | 2019-03-15 10:30 | 2019-03-15 14:37 | 2019-03-15 | AGREEMENT STATE - THREATENED OVER-EXPOSURE The following was received via e-mail: "On March 14, 2019 around 1430 CDT, Turner Industries Group, LLC was performing work in a permanent shooting cell. Two industrial radiographers got into a verbal altercation, which lead to one industrial radiographer cranking out a source onto the other industrial radiographer. Dose reconstruction indicated less than 2 millirem/hr whole body to the one radiographer. The first radiographer was twelve feet from the four Half-Value Layer (HVL) collimator and ran to a shielded condition within seconds after realizing the source had been cranked out. The second radiographer was behind a shooting cell wall performing the crankout. "The radiographer performing the crankout has been terminated and led off the property. All access that he had has been revoked and access codes changed." Louisiana Event Report ID No.: LA20190004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-03-25
53938 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-03-14 | 2019-03-15 14:05 | 2019-03-15 | AGREEMENT STATE - STUCK OPEN GAUGE SHUTTER The following was received via e-mail: "On March 14, 2019, the licensee informed the Department [Pennsylvania Department of Environmental Protection (DEP)] of a moisture/density nuclear gauge with a stuck open shutter. It is reportable per 10 CFR 30.50(b)(2). "While at a temporary job site, a DEP inspector found a Troxler gauge with a stuck open shutter. The technician did not know how long the shutter had been open and was only able to get the Tungsten sliding block closed by tapping on the gauge. After it was closed the technician was unable to get the sliding block open again. The DEP will update this event as soon as more information is provided. "The Department will perform a reactive inspection. More information will be provided upon receipt." Pennsylvania Event Report ID No: PA190008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-03-25
53937 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2019-03-15 13:00 | 2019-03-15 13:39 | 2019-03-15 | AUTOMATIC REACTOR TRIP DUE TO TURBINE GENERATOR TRIP "On March 15, 2019 at 1300 EDT, Indian Point Unit 2 automatically tripped offline from mode 1 - 100% power operations. Reactor Operators verified the reactor trip and the plant is currently stable in mode 3. All automatic systems functioned as required. The auxiliary feedwater system actuated following the trip, as expected. All control rods fully inserted upon the trip, as expected. "This event is reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B). The unit remains on offsite power in hot standby at normal operating temperature and pressure. Decay heat is being removed from the steam generators via the auxiliary feedwater system and the condensate steam dump valves. "Unit 3 remains in mode 6 for a scheduled refueling outage. "The licensee notified the NRC Resident Inspector, the local transmission company, and New York State Independent System Operator." The Indian Point Unit 2 automatic trip was caused by the trip of the main generator. The cause of the generator trip is unknown at this time. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-03-15
53936 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-03-14 | 2019-03-15 11:03 | 2019-03-15 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE DAMAGED BY BACKHOE The following report was received from the California Department of Public Health via email: "A moisture density gauge was being used at a construction site when it was struck by a backhoe. The gauge operator had visual contact with the gauge, and had been assured by the backhoe operator that the gauge would not be impacted by the backhoe operation. However, that was not the case. The backhoe bucket struck the gauge source rod extension, bending it, and damaging the gauge casing. Due to the damage, the source rod could not be fully shielded and locked in the storage position." CA 5010 Number: 031419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-03-25
53935 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-03-14 | 2019-03-15 10:03 | 2019-03-15 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER STUCK IN CLOSED POSITION The following report was received via e-mail: "On 3/14/2019, NC Radioactive Materials Branch (RMB) was notified that a fixed nuclear gauge was stuck in the closed position (found that day). The reporting licensee had the vendor arrive on site, the same day, and repaired the gauge." Source Sr-90, 100 milliCuries North Carolina State Tracking ID: 190009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-03-25
53934 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2019-03-15 05:46 | 2019-03-15 07:08 | 2019-03-24 | UNUSUAL EVENT DECLARED DUE TO HIGH RIVER LEVEL At 0546 CDT, Cooper Nuclear Station declared an Unusual Event due to the Missouri River level reaching 899.05 feet above mean sea level (MSL), which is above the Emergency Action Level (EAL) HU 1.5 elevation of 899 feet above MSL. The river is expected to crest above 901 feet above MSL within the next day, and remain above 899 feet above MSL for the next several days. Declaration of an Unusual Event is a 1 hour report, and is reportable under 10 CFR 50.72.a.1.1. Actions are in progress in accordance with site flooding procedure, including strategic placement of barriers at building entrances and important facilities. There is no major plant equipment out of service at this time. Personnel access to the site is not presently impeded and emergency evacuation routes remain available. A press release is planned for this event, which is a four hour report, reportable under 10 CFR 50.72.b.2.11. If the Missouri River were to reach 901.5 feet above MSL, Cooper would initiate a unit shutdown in accordance with their procedures. If the Missouri River were to rise greater than 902 feet above MSL, Cooper will declare an Alert. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE AT 1742 EDT ON 3/24/2019 FROM KLINTON BEHRENDS AND CURTIS MARTIN TO JEFFREY WHITED * * * The licensee terminated the Unusual Event at 1601 CDT due to lowering Missouri River water levels. River water level is currently at 896.0 feet MSL and lowering. "A press release will be issued to inform the public of Cooper Nuclear Station's exit from the Notification of Unusual Event regarding high Missouri River level. The initial entry into the Notification of Unusual Event occurred on 03/15/2019 and was exited on 03/24/2019 at 1601 CDT. The press release is reportable per 10 CFR 50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. Notified R4DO (O'Keefe), NRR EO (Miller), IRD MOC (Gott), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2019-03-15
53933 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2019-03-14 09:34 | 2019-03-14 17:08 | 2019-03-14 | FITNESS FOR DUTY REPORT - LICENSED EMPLOYEE FAILED A RANDOM SCREENING A licensed employee was determined to be under the influence of alcohol during a random test. The employee's access to the plant has been suspended pending an investigation. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2019-03-14
53932 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-03-07 | 2019-03-14 16:05 | 2019-03-14 | AGREEMENT STATE REPORT - MISADMINISTRATION OF DOSE TO PATIENT The following was received via e-mail: "On March 14, 2019, the Texas Department of Health Services was notified by the licensee's radiation safety officer (RSO) that a therapy event had occurred. A patient was scheduled for three fractions using a high dose rate after loader containing a 6.8 curie iridium-192 source. Multiple catheters were to be used. On March 14, 2019, prior to the third fraction, the licensee determined that one of the catheters was shorter than the length required and the patient received 350 centigrays (50 percent) of the prescribed dose to the thigh resulting in the target tissue receiving 50 percent of the prescribed dose (350 centigrays). The third fraction was not administered. The RSO stated they intended to create a new treatment plan to correct the error and insure the intended area receives the correct dose. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9665 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-22
53931 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-02-26 | 2019-03-13 08:46 | 2019-03-13 | AGREEMENT STATE REPORT - Mo-99/Tc-99 BREAKTHROUGH LIMIT EXCEEDED. The following report was received via e-mail: "On March 7, 2019, the Ohio Department of Health received a phone notification from Cardinal Health stating the first elution on 2/26/2019 from the NorthStar RadioGenix Mo-99/Tc-99m generator exceeded breakthrough limits in Ohio Administrative Code 3701:1-58-35 (10 CFR 35.204). The measured breakthrough was 0.252 microCuries Mo-99 per milliCurie Tc-99m. Cardinal Health stated this was an isolated event and all other elutions have been within the limits. The licensee is using the elution for research only; it is not for human use. Cardinal Health has contacted the manufacture to determine the cause." Ohio Event: 190004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2019-03-21
53930 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-03-13 03:21 | 2019-03-13 08:18 | 2019-03-28 | SAFEGUARDS REPORT - SECURITY SUSPENDED SAFEGUARDS REQUIREMENTS DUE TO SUDDEN SEVERE WEATHER Security suspended safeguards requirements due to severe weather. Compensatory actions were taken. The licensee will notify the NRC Resident Inspector. * * * RETRACTION ON 3/28/2019 AT 1553 EDT FROM ROBERT DANIELS TO ANDREW WAUGH * * * The licensee determined that this event was not reportable since compensatory measures had been taken. The licensee has notified the NRC Resident Inspector of the event retraction. Notified R4DO (Kozal) and 73.71 Safeguards Group (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-03-13
53929 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2019-03-11 12:35 | 2019-03-12 11:21 | 2019-03-12 | FITNESS FOR DUTY REPORT - EMPLOYEE FAILED TO REPORT FOR TESTING A contract employee failed to report for a random fitness for duty test. The contractor's access to the plant has been terminated. The licensee notified the NRC Resident Inspector and the NY Public Service Commission. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2019-03-12
53928 | 0 | WEIR VALVES & CONTROLS |  |  |  |  | 2019-01-18 | 2019-03-11 15:38 | 2019-03-11 | PART 21 REPORT - IMPROPER ANTI-ROTATION KEY DIMENSION ON GLOVE VALVE "This notification is being submitted pursuant to the guidelines of 10 CFR Part 21 to report that a 24" Class 150 Globe valve for RHRSW HX Isolation MOV, E1150F068A at Detroit Edison - Fermi 2, failed to fully open due to the failure of the anti-rotation key. "The site notified WVC [Weir Valves and Controls] USA on January 18th of this issue involving a new bonnet that was installed which included a key bushing/key assembly. The new bonnet used was from an originally supplied valve assembly on WVC USA order 0010001147-10 with a quantity of one, Detroit Edison Company PO 4700732583. The key is welded on top and bottom in the key bushing keyway to hold the key in place. After a month in service, during operation, the welds failed which caused the key to drop out or be driven out from the key bushing by friction/vibration. Upon review of the design it was found that the key and key slot were not dimensioned properly for a tight fit allowing a larger than recommended gap between key and keyway. This gap allowed the operational torque loads to put the welds in bending which caused the welds to fail. Loss of the key renders the valve inoperable to open or close. "The site has currently restored the key bushing/key assembly with new keys with proper fit and welds to ensure the key is retained. "[WVC USA] has performed an extent condition review and has concluded that one other operating site, Georgia Power - SNC, Hatch Unit 1 1WVC USA order 0010000081-10 (55544A), Southern Nuclear Operating Co PO SNG10025571 has a similar key/key bushing assembly. There was a quantity of six valve assemblies shipped for this purchase order. The site has been contacted to evaluate the fit of the key bushing/key assembly. "Engineering has determined that improper design clearance was the cause of failure. [WVC USA is] performing corrective actions to ensure future re-occurrences cannot occur in design engineering." Affected sites include: Fermi Unit 2 and Hatch Unit 1. For additional information, contact: Allen Fisher Director of Engineering allen.fisher@mail.weir 978-825-845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-03-11
53927 | 0 | LOUISIANA DEPT OF ENV QUALITY |  |  |  |  | 2019-03-11 13:30 | 2019-03-11 15:17 | 2019-03-11 | AGREEMENT STATE REPORT - SHUTTER STUCK IN OPEN POSITION The following was received by email from the state of Louisiana: "On 03/11/2019, Georgia Pacific Consumer Products [GA-PAC] Port Hudson Operations was shutting down a process to perform a disposal decommission maintenance. In the process of securing the radiation sources for shipping and disposal, it was then discovered the shutter [on a level density gauge] would not close. "GA-PAC has called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. GA-PAC will have BBP Sales determine the proper disposal for this device. The device was manufactured in 1967. "The sources and device with shutter failure will be sent for disposal and not replaced. GA-PAC is decommissioning this unit. This is not a radiation exposure hazard and does not pose a health and safety situation for the GA-PAC employees or the general public. "THIS EVENT IS CONSIDERED CLOSED BY LDEQ. This event is being reported to the NRC as required by Regulatory Requirement 10 CFR Part 30.50 (b) (2) & LAC 33:XV341.B." The Gauge is an OHMART HM8 device/source holder, S/N 6563 with a 100 mCi Cs-137 source. LA Event Report ID No.: LA-190003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-03-19
53926 | 0 | OREGON HEALTH AUTHORITY |  |  |  |  | 2019-03-05 | 2019-03-11 13:55 | 2019-03-13 | AGREEMENT STATE REPORT - LOST IR-192 SOURCE The following is a summary of the phone call with the state of Oregon: On March 5, 2019, the licensee realized that a 9.4 Curie Ir-192 industrial radiography source was missing when the scheduled shipment was not received on March 4, 2019. Last known location was Memphis, TN on March 1, 2019. * * * UPDATE AT 1110 EDT ON 3/13/2019 FROM DARYL LEON TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On March 11 at 11:38 AM (PDT), the licensee (OWL) emailed and stated that the lost package and source have been found after an extended telecon (1 hour) with the carrier. No location given in email but a statement that [the common carrier] had held the shipment because they needed a copy of the shipping papers to send it on to its destination (QSA in Baton Rouge, LA). OWL emailed a copy of the shipping papers to [the common carrier] and the package was released to continue on to QSA. "On March 12 at 9:15 AM (PDT), [the state of Oregon] contacted the licensee (OWL) by phone. The package and source were found by [the common carrier] in their Memphis, TN shipping center. [The common carrier] did not have shipping papers for the package when received in Memphis and placed it into their 'Overgoods' department where 'lost dangerous goods' are taken and held if there is a paperwork issue preventing a shipment from continuing on its way. The package in this case was released on March 11th as previously indicated and arrived at QSA in Baton Rouge at 10:02 AM (CDT)." Notified the R4DO (Groom), and NMSS Events Resource and ILTAB (via e-mail). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2019-03-19
53925 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-02-13 | 2019-03-11 10:17 | 2019-03-11 | AGREEMENT STATE REPORT - UNDERDOSAGE TO PATIENT DURING I-131 TREATMENT The following was received from the state of Pennsylvania: "On 2/13/19, a patient was administered 171 milliCuries (mCi) of liquid iodine 131 (I-131) through a feeding tube inserted into the patient's gastric tube as he was unable to swallow I-131 in pill form. While flushing the feeding tube with saline, a technologist noticed a pool of liquid next to the patient on a disposable drape, on the patient, and on the imaging table, that was determined to be radioactive. The feeding tube was removed from the gastric tube, and flushed, without any further leaking. All non-essential personnel were cleared from the room and the nuclear medicine staff contained the spill, decontaminated the patient and the site. All radioactive trash was contained in a lead-lined storage drum and secured. No hospital personnel were contaminated during this event. The licensee reported that given the I-131 dose was diluted with saline, the total amount of I-131 that was spilled could not be determined at the time of the event. In an effort to determine the activity and dose the licensee surveyed all contaminated items in their storage drum. Using this data and conservative decay calculations the licensee estimates 97.2 mCi was spilled. This resulted in an under-dose of 56.8 percent. The patient is scheduled for another administration to complete the therapy. The DEP [Pennsylvania Department of Environmental Protection, Bureau of Radiation Protection] will update this event as soon as more information is provided." Pennsylvania Event Report Number: PA190007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-03-19
53924 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-03-11 08:51 | 2019-03-11 10:00 | 2019-03-11 | PLANNED COMMUNICATION SYSTEM MAINTENANCE "On 03/11/2019 planned maintenance activities will be performed on the Beaver Valley Power Station (BVPS) Unit 2 Digital Radiation Monitoring System's (DRMS) Communications System. "The work includes upgrades to the DRMS hardware, software and computer peripherals. Components to be upgraded under this planned maintenance include: Redundant Servers, Operator Console, Health Physics Office Console/Workstation, Printers and Portable Mass Storage/Backup and Computer peripherals necessary to interface with the computer system. This planned upgrade on the Unit 2 DRMS Communications System will result in the loss of Unit 2 radiological monitoring capability in the Control Room and on the Plant Computer System (PCS). Neither the Emergency Response Facilities nor the Emergency Response Data System (ERDS) will receive radiological data. No actual radiation monitors are affected. The scheduled work duration is approximately three weeks. "When the DRMS is out of service for the upgrade, compensatory actions will be in place. Radiation monitors will be continuously monitored for any increases in radiation levels. The Unit 2 Shift Manager will be notified of any increase in radiation monitor readings, including exceeding Emergency Action Levels (EAL). "This is an eight-hour, non-emergency notification for a Loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the upgrade to the DRMS Communications System will result in the loss of the Unit 2 radiological monitoring capability in the Control Room and to the Unit 2 Plant Computer System that affects the functionality of an Emergency Response Facility. "There is no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The licensee is currently in a Technical Specification Action Statement, Limiting Condition for Operation for spent fuel pool radiation monitor and leakage rate monitor. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-03-11
53923 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-03-09 22:59 | 2019-03-10 04:38 | 2019-03-10 | AUTOMATIC SCRAM RESULTING IN RPS AND ECCS ACTUATION "At 2259 CST on 3/9/2019, Browns Ferry Unit-3 received an automatic SCRAM on Main Generator Breaker Failure and Turbine Load Reject. Unit-3 declared a Notification of Unusual Event SU1 for loss of offsite AC power to Unit-3 specific 4kV Shutdown Boards for greater than 15 minutes. "Primary Containment Isolation Systems (PCIS) Groups 1, 2, 3, 6, and 8 isolation signals were received. Upon receipt of these signals, all required components actuated as required. Main steam relief valves lifted on the initial transient. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) initiated on low reactor water level. HPCI remains in service for reactor level and pressure control. RCIC is not in service at this time, the station is investigating low flow from the pump. All four Unit-3 Diesel Generators started and loaded as expected. Residual Heat Removal System is in service for suppression pool cooling. "4kV Station Unit Boards have been restored from the 161kV system. Actions are in progress to restore 4kV Shutdown Boards to offsite power. "This event is reportable within 1 hour in accordance with 10 CFR 50.72(a)(1)(i) for declaration of the Licensees Emergency Plan. Complete as documented on EN 53922. "This event requires a 4 hour report per 10 CFR 50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "This event also requires an 8 hour report per 10 CFR 50.72(b)(3)(iv)(A). 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B), (1) Reactor protection system (RPS) including: reactor scram or reactor trip, (2) General containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs), (4) ECCS [Emergency Core Cooling System] for boiling water reactors (BWRs) including: core spray systems; high-pressure coolant injection system; low pressure injection function of the residual heat removal system, (5) BWR reactor core isolation cooling system; isolation condenser system; and feedwater coolant injection system, and (8) Emergency AC electrical power systems, including: Emergency diesel generators (EDGs).' "The NRC resident inspector has been notified." As of the event report, the MSIVs were opened and decay heat was being removed via the bypass valves to the condenser. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-03-10
53922 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-03-09 23:12 | 2019-03-10 00:48 | 2019-03-10 | NOTICE OF UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER At 0012 EST on 3/10/2019, Browns Ferry Unit-3 declared an Unusual Event due to a spurious trip of the generator breaker, resulting in a loss of AC power to the 4 kV shutdown boards greater than 15 minutes. All diesel generators started and loaded to supply onsite power. The reactor auto-scrammed, with all rods fully inserting. The Main Steam Isolation Valves opened and shutdown cooling was being conducted via the condenser. The licensee will exit the emergency declaration once offsite power is restored. There is no estimated restart date. Browns Ferry Unit 1 remains in Mode-1 (100%), Unit 2 remains in Mode-5 for a refueling outage. The NRC Resident Inspector has been notified. This event is related to EN 53923. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 3/10/19 AT 1419 EDT FROM JOHN HOLLIDAY TO BETHANY CECERE * * * At 1310 CDT, Browns Ferry Unit-3 exited the Unusual Event when 161 kV lines were made available. The licensee is executing procedures for securing the diesel generators while alternate offsite power methods are utilized. Switchyard damage evaluation is in progress. The licensee will notify the NRC Resident Inspector. Notified R2DO (Desai), R2RA (Haney), DNRR (Nieh), NRR EO (Miller), and IRD (Grant). Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2019-03-10
53921 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2019-03-09 12:00 | 2019-03-09 13:59 | 2019-03-09 | SEWAGE LINE BACKUP CAUSING WASTEWATER DISCHARGE TO CHESAPEAKE BAY "A sewage line on the south end of the plant backed up causing sanitary wastewater to flow into storm drains and out to the Chesapeake Bay. This is a required notification of the Maryland Department of the Environment under COMAR [Code of Maryland Regulations] 26.08 for discharge of a pollutant into navigable waters or the adjoining shoreline. The amount has been estimated at less than 1000 gallons and the source has been isolated and storm drains have been covered to stop any flow into them and subsequently to the Chesapeake Bay. This notification is made in accordance with 10CFR50.72(b)(2)(xi) due to notification of a state agency." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-03-09
53920 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-03-08 | 2019-03-08 17:50 | 2019-03-08 | AGREEMENT STATE REPORT - MOISTURE DENSITY GAUGE RECOVERED BY FIRE DEPARTMENT The following report was provided by the Texas Department of State Health Services via email: "On March 8, 2019, the Agency [Texas Department of State Health Services] was notified by the Houston Fire Department that they had recovered a moisture density gauge belonging to a Texas licensee. The gauge contained 10 milliCuries of cesium-137 and 40 milliCuries of americium-241. The Agency has not yet been notified by the licensee about this loss. Investigation is ongoing. Updates will be provided in accordance with SA-300." Texas Incident #: 9663 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-18
53919 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-03-08 | 2019-03-08 16:59 | 2019-03-08 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER FAILED TO OPEN COMPLETELY The following report was received from the Texas Department of State Health Services via email: "On March 8, 2019, a licensee reported to the Agency [Texas Department of State Health Services] that a shutter on a fixed nuclear gauge failed to open completely. The gauge is a Thermo Fisher Scientific model SCL-1C, serial number UM900, containing 100 milliCuries of strontium-90. No individuals received any exposure due to this equipment failure. The manufacturer has repaired the gauge and the shutter now functions as intended." Texas Incident #: 9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-18
53918 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2019-03-08 11:13 | 2019-03-08 15:51 | 2019-03-08 | OFFSITE NOTIFICATION FOR OIL SPILL INTO U.S. WATERS "Browns Ferry Nuclear Plant (BFN) is notifying state and local agencies of the presence of an oil sheen in the cold water channel. Water from the cold water channel was running into a tunnel that connects to the waters of the US. "BFN Procedure RWI-007, Spill Prevention Control and Countermeasure Plan requires the National Response Center as well as other state and local agencies be notified of any oil sheen on the water. This oil spill is reportable to the EPA (National Response Center) under 40 CFR 112. The notification was made to the National Response Center at 1113 CST under notification number 1239580. The Alabama Emergency Management Agency (AEMA) and Alabama Department of Environmental Management (ADEM) were notified at 1120 CST. "This event is reportable as a 4-hour Non-Emergency Notification report in accordance with 10 CFR 50.72(b)(2)(xi) 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made.'" The licensee has notified the NRC Resident Inspector. The oil is believed to come from the number one cooling tower basin due to heavy rainfall. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling | Power Operation | Power Operation | Refueling | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-03-08
53917 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2019-03-08 11:30 | 2019-03-08 15:15 | 2019-03-08 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following is a synopsis of an email from the state of Florida: A nuclear density gauge (CPN Model: MC-1 Elite, Serial number: 30803) was not secured properly on the licensee's transport truck and released during a traffic accident with a passenger vehicle at the intersection of Knotty Pine Road and US-192 in West Melbourne, FL. The truck was on its way to a job site for further testing. Brevard County Fire and Rescue HazMat teams and the Brevard County Emergency Management radiological coordinator responded to the scene. The 10 mCi Cs-137 source separated from the gauge housing, but the 50 mCi Am/Be source was intact. No injuries or fatalities were reported. No evacuations were reported, however a 15 ft. perimeter was established around the material until surveys were completed. Surveys were 592 mR/hour at 1 inch, 23 mR/hour at 1 foot, and there was no removable contamination detected. There was no release of radioactive material during this event, and the personnel who picked up the item were surveyed and cleared. The sources were secured by the licensee, placed in a transport case (with added shielding), and taken to their permanent storage location in Sebastian. The licensee will return the gauge to CPN for repair or replacement. Florida Incident Number: FL19-033. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2019-03-18
53916 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2019-03-05 | 2019-03-08 09:50 | 2019-05-31 | AGREEMENT STATE REPORT - TROXLER GAUGE DESTROYED WHEN RUN OVER The following was received from the Arkansas Department of Health via e-mail: "The Department [Arkansas Department of Health Radioactive Materials Program] received notification on March 5, 2019, from licensee GTS, Inc. that a Troxler gauge model 3440 [serial number: 73390, 40 mCi Am-241, 8 mCi Cs-137] had been struck by a skid steer while performing routine measurements at a road construction site. As a result of the incident, the source had been pulled from its testing position and become partially exposed. "Upon review of the event, it was noted that the technician quickly created a thirty (30) foot containment barrier and notified his company's Radiation Safety Officer [RSO]. The [RSO] for GTS mobilized to the event location and contacted the [Department]. "Upon receiving an exemption from the Department, the RSO was able to manipulate the source into the shielded position and place the remnants into the transportation container for transport to the permanent storage location. The gauge was returned to the permanent storage location at approximately 1330 [CST] on March 5, 2019. The licensee performed leak tests of the sources, surveys of the gauge transport container, and surveys of the storage location. "[Department] inspectors visited the licensee on March 6, 2019, to investigate the event. Surveys at the exterior of the transport container were determined to be 3-5 mR/hr. Surveys performed inside of the transport container were measured to be a maximum of 15 mR/hr at a location close to the surface of the shielded source. "The [Department] considers this investigation open pending receipt and review of the licensee's 30 day report" State of Arkansas Event Report No. : AR-2019-002 * * * UPDATE AT 1437 EDT ON 4/10/19 FROM CHRISTOPHER TALLEY TO KARL DIEDERICH * * * The following was received via e-mail: "Upon review of the licensee's 30 day report, received April 5, 2019, it was noted that the dosimetry badge worn by the RSO during the retraction and transportation of the source showed no measurable dose. The dosimetry badge was new for the month of March. "The report also contained leak test results for the sources both prior to the event, January 19, 2019, and after the event, March 6, 2019. The results for the leak tests in both instances were measured to be below 185 Bq (0.005 microCuries), considering the sources to be non-leaking sources. "The company conducted mandatory safety meetings with all staff who work with the portable gauges and also sent a companywide e-mail to all employees as a result of the event. Topics discussed during the meetings and e-mail included radiation safety, worksite safety, portable gauge specific safety and use, emergency response procedures, and gauge security. The contractor responsible for the skid steer also conducted an on-site safety meeting immediately following the event on March 5, 2019. "The Department now considers this event to be closed providing that no new information is received by the Department." Notified R4DO (Werner) and NMSS Events (via e-mail). * * * UPDATE ON 5/31/19 AT 1037 EDT FROM CHRISTOPHER TALLEY TO THOMAS KENDZIA * * * The following was received via e-mail: "The Licensee has transferred the radioactive sources and associated nuclear gauge remnants to the manufacturer for disposal/repair. The sources are now listed under North Carolina Radioactive Materials License #032-0182-1." The Department now considers this event to be closed. Notified R4DO (Kozal) and NMSS Events (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2019-03-18
53915 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2019-02-18 | 2019-03-07 13:56 | 2019-03-07 | AGREEMENT STATE REPORT - LOST IODINE-125 LOCALIZATION SEED The following report was received from the New York State Department of Health via email: "On February 20, 2019 the Department [New York State Department of Health] was notified of a missing I-125 localization seed (Activity:[approximately] 215 microCuries) at Roswell Park Cancer Institute in Buffalo, New York. "An lodine-125 localization seed was removed from a patient, along with a specimen, in a procedure that took place on February 18, 2019 (to be confirmed in the written report). Images confirm that the seed was removed from the patient. The seed and specimen are believed to have been delivered to the facility's Pathology Department. The RSO [Radiation Safety Officer] was informed of the missing seed on February 19, 2019. Currently, the facility is trying to locate the missing seed. Updates will be provided as they become available." Event Report ID No.: NYDOH-19-03 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-03-15
53914 | 0 | ELI LILLY AND COMPANY |  |  |  |  | 2019-03-07 | 2019-03-07 12:30 | 2019-03-07 | LOST TRITIUM EXIT SIGN The following is a summary of a phone call with the licensee: During a routine inventory Eli Lilly and Company discovered that one of their tritium exit signs was missing. The company believes the sign went missing during a remodeling project. The company is still actively looking for the sign, but believes that it is out of their possession at this time. The tritium exit sign, serial number A11223, was manufactured by Isolite in January of 2001. The activity at the time of manufacturing was 7.5 Ci, which would be approximately 2.5 Ci today. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-03-15
53913 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-03-06 | 2019-03-06 14:54 | 2019-03-06 | AGREEMENT STATE REPORT - STOLEN I-131 TRACER AND RADIOACTIVE WASTE The following report was received via e-mail from the state of Texas: "On March 6, 2019, the licensee notified the Agency [Texas Department of State Health Services] that someone had broken into one of their vehicles at an oil well drilling site northeast of Odessa, Texas, and stole a shipping/transport container with a bottle of approximately 7 milliCuries of iodine-131 tracer material (liquid form) and a box containing radioactive waste (i.e. gloves, rags). A number of other items (computer and other equipment) were also taken. The licensee has reviewed the initial information and is of the opinion, at this time, that it appears the material was not the target of the break-in but was grabbed along with other items of value. The licensee notified local law enforcement. The tracer material was scheduled to be used late in the day on March 5, 2019, but the schedule was changed at the last minute for it to be injected the next morning. The licensee's employee left the company truck containing the material at the site overnight, the vehicle was locked. There were no workers at the site overnight. The licensee has employees searching around the well site, along the road, and other nearby areas it may have been discarded." Event Location: Approximately six miles South of Odessa, Texas. Texas Incident #9661 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-14
53912 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2019-03-06 | 2019-03-06 09:24 | 2019-03-06 | PART 21 REPORT - TARGET ROCK SOLENOID VALVE 810000-X POSITIONER CIRCUIT FAILURE MAY CAUSE UNDESIRED POSITION The following was received via email: "Target Rock Modulating Solenoid Operated valves which utilize model 810000-X positioner manufactured and supplied by Target Rock. Target Rock Modulating Solenoid Operated valves are equipped with a separate, remote mounted, positioner unit, which is a closed loop valve position control system. The valve positioner is electronically connected to the valve assembly via a wiring harness. This defect only applies to the current production 810000-X positioner model. All previous versions of the Target Rock Modulating Solenoid Operated valve positioners do not exhibit this defect. "Three (3) 810000-X model positioners were returned to Target Rock by Duke Energy Carolinas, LLC, Oconee Nuclear Station for defective operation. Target Rock evaluated these units and found two defective circuits in the positioner PC board at unrelated locations: the 80 V Regulator Circuit and the Close Indication Relay Driver Circuit. "Description: 1.) 80 V Regulator Circuit Failure - In the event of a failure of the positioners 80 V Regulator Circuit, the positioner, and therefore its associated modulating solenoid operated valve, will no longer receive voltage from the positioner, resulting in the return spring moving the valve disc to its fail position (fully open or fully closed depending on the design specification requirement). Based on the positioners returned by Duke Oconee, and additional testing performed by Target Rock, this 80 V Regulator Circuit Failure will only occur during initial powering of the device. Positioner units currently in operation, and constantly energized, will not have this failure occur. In the instance where the positioner is powered down and then powered back up during maintenance activity or other event, this failure has the potential to occur upon re-energization of the device. Having said that, should the positioner continue to be operational through power-up, it would be expected to perform its intended function throughout operations. 2.) Close Indication Relay Driver Circuit Failure - In the event of a failure of the positioners Close Indication Relay Driver Circuit, the positioner will be unable to send a signal to indicate the valve has reached its fully closed position. Typically, this circuit is enabled for plant monitoring purposes. This failure has no effect on the ability of the Modulating Solenoid Operated valve or positioner to control fluid flow as intended. "Root Cause: 1.) 80 V Regulator Circuit Failure - The defect observed on the 80 V Regulator Circuit is a failure of a Zener reference diode. The Zener reference diode reduces the normal (90 - 140 V) supply voltage to approximately 80 V for this portion of the circuit. In the event of a failure of the Zener reference diode, full input voltage (90 -140 V) is passed to the downstream components in the circuit. The downstream components from the Zener reference diode are not rated for 90 - 140 V operation and fail, rendering the positioner inoperable. 2.) Close Indication Relay Driver Circuit Failure - The defect observed on the Close Indication Relay Driver Circuit was a trace wire in the PCB which had opened (broke) at multiple locations." "Corrective Action: Two corrective actions have been put in place. All new 810000-X positioner units manufactured by Target Rock will have these revisions incorporated: "1.) The Zener reference diode for the 80 V Regulator Circuit has been replaced with a different component. The rating for the Zener reference diode has been increased from 30 mA to 73 mA. This upgrade will ensure current ratings are not exceeded during initial powering of the device. 2.) The PCB trace which failed has been upgraded. The trace width has been changed from 12 mil to 70 mil. The wider trace width will be less susceptible to variations in width during the manufacturing process, and in the event of any minor variations in width, will still be sufficient to pass the required current. "Should you have any questions regarding this matter, please contact Michael Cinque, General Manager at (631) 293-3800 Very Truly Yours, Michael Cinque General Manager Target Rock, Business Unit of Curtiss-Wright Flow Control Corporation" Affected sites are Oconee, Vogtle, South Texas Project, and Millstone. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-03-06
53911 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-03-05 05:35 | 2019-03-05 12:46 | 2019-03-05 | AUTOMATIC ACTUATION OF THE PRIMARY CONTAINMENT ISOLATION SYSTEM "At 05:35 Eastern Standard Time (EST) on March 5, 2019, with Unit 2 in Mode 5 at 0% power, an actuation of the Primary Containment Isolation System occurred during hydrolazing of the reactor water level variable leg instrumentation line nozzle N011B in the reactor cavity. The hydrolazing activity caused low reactor water level to be sensed on Division II of the shutdown range level instrumentation. Per design, the low level 1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Primary Containment Isolation System. "There was no impact on the health and safety of the public or plant personnel. The Group 8 was reset and shutdown cooling was restored at approximately 05:45 EST. "The safety significance of this event was minimal. Although there was a brief interruption of the shutdown cooling, the Residual Heat Removal (RHR) shutdown cooling system operation was restored in approximately 10 minutes without extensive troubleshooting or maintenance, and remained operable. The RHR shutdown cooling system is not credited in any Updated Final Safety Analysis Report Chapter 6 or 15 accidents or transients. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-03-05
53910 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-10-17 | 2019-03-04 14:01 | 2019-03-04 | AGREEMENT STATE REPORT - SUSPECTED CYBER ATTACK The following report was received via email: "[Oklahoma Dept. of Environmental Quality] was informed this morning that Fisher Wireline Services (OK-27453-02) has been the victim of an email hack which resulted in email sent to the licensee being diverted to an unauthorized account. This included emails from NSTS [National Source Tracking System] to the licensee regarding their annual source reconciliation. It appears that the licensee's email has been compromised since Oct. 17, 2018." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2019-03-12
53909 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2019-03-03 09:16 | 2019-03-03 09:54 | 2019-03-03 | NOTICE OF UNUSUAL EVENT DUE TO UNCONFIRMED FIRE ALARM At 0916 EST on March 3, 2019, North Anna Unit 2 declared a Notice of Unusual Event under Emergency Action Level HU 2.1 (fire in/or restricting access to any table H-1 area not extinguished within 15 minutes of control room notification or verification of a control room alarm). At 0906 the control room received a heat sensor alarm for the Unit 2, Reactor Coolant Pump motor cube. The fire brigade was dispatched to the scene where they found no indication of fire, no smoke and no fire damage. There were no actuations associated with the alarm and no redundant indications of fire. There was no effect on plant equipment and no indications of RCS leaks. The site determined that the alarm was invalid and terminated the NOUE. Unit 2 is in a stable condition and in a normal electrical lineup. Offsite support was not requested. The NRC Resident Inspector, State, and local authorities have been notified by the licensee. Notified R2RA (Haney), DNRR (Evans), IRD MOC (Grant), R4RDO (Rose), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2019-03-03
53908 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2019-03-02 22:37 | 2019-03-03 00:13 | 2019-03-03 | MANUAL REACTOR TRIP DUE TO DEGRADING MAIN CONDENSER VACUUM "On March 2, 2019 at 2237 EST, North Anna Unit 2 reactor was manually tripped, while operating at approximately 12 percent power, due to degrading vacuum in the main condenser. The unit was in the process of a planned shutdown for refueling when condenser vacuum degraded to greater than 3.5 inches of mercury absolute. The operations crew entered the reactor trip procedure and stabilized the unit in Mode 3 at normal operating pressure and temperature. All control rods fully inserted into the core following the reactor trip. The reactor protection system actuation is reportable per 10 CFR 50.72(b)(2)(iv)(B). There were no ESF system actuations. Decay heat is being removed by the Steam Generator Pressure Operated Relief valves. Unit 2 is in a normal shutdown electrical lineup. "The NRC Resident Inspectors have been notified. The Louisa County Administrator will be notified." | 0 | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-03-03
53907 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-03-02 | 2019-03-02 21:02 | 2019-03-02 | AGREEMENT STATE REPORT - RADIOGRAPHY DEVICE LEFT UNSECURED The following report was received from the North Carolina Division of Health Service Regulation, Radioactive Materials Branch via email: "Licensee reports that an Industrial Radiography [IR] exposure device was unaccounted for during the 15 hours following work site activities on March 1st. The IR device was left unsecured the entire time until discovered the morning of March 2nd by the radiography crew that left it. The device [Spec 150; S/N: 1251] and source [72 Ci Ir-192; Model: G-60; S/N: AA0805] are secured and in possession of the corporate RSO [Radiation Safety Officer] at the time of this report. North Carolina Radioactive Materials Branch has initiated an investigation and will update this report for completion." NC Event Tracking ID: 190008 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-03-11
53906 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-03-02 03:17 | 2019-03-02 06:12 | 2019-03-02 | REACTOR TRIP DUE TO FEEDWATER ISOLATION VALVE CLOSURE "At 0317 CST, the Unit 2 Reactor tripped due to Feedwater Isolation Valve (FWIV) 2-04 going closed. All Auxiliary Feedwater Pumps started due to steam generator Lo-Lo levels. "Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IPO-007B. The Emergency Response Guideline Procedure Network has been exited. Decay heat is being rejected to the Main Condenser via the Steam Dump Valves. "The cause of the FWIV going closed is currently under investigation." All control rods fully inserted and the reactor trip was uncomplicated. Unit 2 is in a normal post-trip electrical line-up. There was no impact on Unit 1 due to the Unit 2 reactor trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-03-02
53905 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-02-28 | 2019-03-01 13:56 | 2019-03-01 | AGREEMENT STATE REPORT - MISSING ANALYZER SOURCE The following was received via fax from the Pennsylvania Department of Environmental Protection: "On March 1, 2019, a manufacturer's technician from Sabia Inc. (PA-R0124) notified the Department [Pennsylvania Department of Environmental Protection] of a missing 0.9 microgram (0.5 mCi) Californium-252 source from a Sabia XL5000 analyzer at the Holcim (US), Inc. Whitehall Cement Plant (PA-1336). The manufacturer was performing replenishment of two of seven sources [on February 28, 2019]. It was discovered that the analyzer only contained six sources. The analyzer was removed and disassembled, destroying the unit, in efforts to locate the missing source but it was not located. The manufacturer technician surveyed the unit and the area multiple times and did not find the source. The remaining sources have been packaged in a drum for safe storage until shipping can be arranged. "The Department will perform a reactive inspection. More information will be provided upon receipt." Pennsylvania Event Report ID No: PA190006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-03-11
53904 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-02-28 | 2019-03-01 13:53 | 2019-03-01 | AGREEMENT STATE REPORT - UNDERDOSE OF THERASPHERE Y-90 TREATMENT The following report was received from the Kentucky Department of Public Health via email: "The University of Kentucky RSO [Radiation Safety Officer] reports a patent delivery system failed to deliver part of a TheraSphere Y-90 treatment on February 28, 2019. A patient written directive indicated a prescribed dose of 208 Gy. The patient only received 145 Gy. "The RSO indicated the first vial of Y-90 was administered without difficulty. The second vial failed to empty into the administration catheter. Calls were placed to the drug representative and unsuccessful attempts made to administer the remainder of the dose. Patient treatment was stopped with only partial dose delivery. At the time of the report, March 1, 2019, the University is establishing the reason for the administration failure. The patient had been notified and the physician and referring physician are being notified. The university plans an update in 15 days." Kentucky Event Report ID No.: Ky190002. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-03-11
53903 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2019-02-28 22:17 | 2019-03-01 04:03 | 2019-03-01 | SPECIFIED SYSTEM ACTUATION - TRIP OF SAFETY RELATED BUS "On February 28, 2019, at 2217 CST, LaSalle Unit 2 experienced a trip of the 241Y Safety Related Bus during surveillance testing resulting in a valid undervoltage actuation signal to the Common Emergency Diesel Generator ('O' EDG), causing it to start and load to Bus 241Y. The purpose of the surveillance testing was to demonstrate the operability of the breakers necessary to provide the second off site source to Unit 2. This event is reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A), as an event that results in a valid actuation of the emergency AC electrical power system. In addition to the 241Y bus trip and 'O' EDG actuation signal, the following plant responses occurred as designed due to the momentary loss of this AC Bus: "A" RPS de-energized due to the loss of the 2A Reactor Protection System Motor-Generator Set, and the running Unit 2 Fuel Pool Cooling pump tripped. The Non-Safety Related Bus 241X de-energized resulting in a trip of the Unit 2 Station Air Compressor. All systems have been restored and troubleshooting is currently in progress. Unit 1 remained in MODE 1 during this event. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-03-01
53902 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-02-25 | 2019-02-28 20:51 | 2019-03-27 | AGREEMENT STATE REPORT - UNINTENDED DOSE TO NON-TARGET TISSUE The following was received from the state of California: "The licensee reported an unintended dose to non-target tissue of a patient from an HDR [High Dose Rate] treatment, apparently due to mispositioning of the uterus-ovary applicator. The unintended dose occurred on the final of four fractions. The target tissue received the intended dose in each of the four fractions, but non-target tissue of the bowel received in excess of 50 rem and 150 percent of the expected dose to the non-target bowel tissue from the four fractions combined, with the excess non-target bowel dose occurring in the final fraction due to the mispositioned applicator. "The licensee will submit a 15-day written report to the California Department of Public Health-Radiologic Health Branch (CDPH-RHB) in accordance with 10 CFR 35.3045(d), and will include the calculated dose to the non-target tissue of concern. That report will be forwarded to NRC by CDPH-RHB. "The referring physician was informed of the unintended dose to the non-target bowel tissue." CA 5010 Number: 022719 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION AT 1644 EDT ON 03/27/2019 FROM ROBERT GREGER TO JOANNA BRIDGE * * * The following was received via e-mail: "The licensee determined that a dose volume of 5 cc was appropriate for the unintended tissue exposure (instead of 2 cc). Based on the 5 cc tissue volume, the dose was less than the Medical Event reporting criteria contained in 10 CFR 35.3045(a)(3). Please note that the original event submittal by California erroneously referenced the applicable regulatory reporting requirement as 10 CFR 35.3045(a)(1)(iii)." Notified R4DO (Kozal) and NMSS Events. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-03-08
53901 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2019-02-28 13:00 | 2019-02-28 17:15 | 2019-02-28 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following was received via email from the state of Colorado: "At approximately 1438 MST on February 28, 2019 the RSO [Radiation Safety Officer] for CO 152-01, St. Anthony Hospital - Centura Health, notified the Department [Colorado Department of Public Health and Environment] of a Y-90 SIR-Sphere misadministration. The procedure occurred at approximately 1300 MST and it was determined that 65 percent of the prescribed dose was delivered to the patient. The RSO noted that during the procedure there were issues with the delivering catheter. During the procedure, the catheter was replaced. "A department investigation will occur in the near future. A written report per section 7.21.4 is expected within 15 days." Colorado Event Report ID No.: CO190003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-03-08
53900 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-02-14 | 2019-02-28 11:34 | 2019-02-28 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION FROM OIL FIELD EQUIPMENT The following was received via email from the state of Texas: "On February 27, 2019, the Agency [Texas Department of State Health Services] confirmed that access to an oil field equipment wash building had been restricted since February 14, 2019, due to radioactive material contamination. "On February 11, 2019, a load of waste from the licensee's facility had set off the radiation alarm at the landfill. The isotope was identified as antimony-124. The load was returned to the licensee's facility later that afternoon. On February 12, 2019, the licensee began surveying and investigating, starting with the dumpster and expanding to other areas. The contamination was found to be on piece/part of a fracking pump. On February 13, 2019, contamination was identified on a fracking pump trailer. On February 14, 2019, surveys identified contamination in the trench of one of the bays in the equipment wash building. "Access to the building was restricted that day and is still restricted. The licensee's initial sampling from the trench identified antimony-124 and scandium-46. They are waiting on analyses of a second sampling of the trench sludge after water was removed/collected, and they will be sampling the traps/separators between the trench and the sanitary sewer system. "The licensee is not licensed for, nor did it use, these tracer materials. Their equipment was being used on a well site at which another licensee had performed a tracer study while the equipment was in use. The tracer study licensee has been involved in some of the surveying and with the collection of contaminated equipment items they took possession of to be held or disposed in accordance with their license. "An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-08
53899 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-02-22 | 2019-02-28 11:11 | 2019-02-28 | AGREEMENT STATE REPORT - LOSS OF LICENSED MATERIAL The following was received via email from the state of North Carolina: "North Carolina Radiation Protection Branch (RMB) was notified on February 22, 2019, that a General Licensee could not account for two Microderm hand-held probes containing two sources each [25 micro Ci of Sr-90 and 100 micro Ci of Tl-204]. RMB has been in communications with the General Licensee to ascertain whether or not the devices containing the sources have been returned to the vendor or are indeed lost. At this time, this cannot be verified and the RMB anticipates more information to follow on March 4, 2019. Additional details to follow to complete this event report." NC Event Tracking ID: 190007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-03-08
53898 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-02-25 | 2019-02-25 15:43 | 2019-02-25 | AGREEMENT STATE REPORT - GAUGE SHUTTER FAILURE The following information was received via e-mail: "On February 25, 2019, the Agency [Texas Department of State Health Services] received a report from the licensee's technical representative stating that the shutter on an Ohmart Vega model SH-F1 gauge, containing a 50 millicurie cesium-137 source, failed to shut during maintenance when the handle broke off. Open is the normal operation position of the gauge shutter. No licensee employee received any exposure as a result of this event. The gauge will be repaired in September 2019 during an outage. Additional information will be sent in accordance with SA-300." Texas Incident #: 9659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-03-05
53897 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2019-02-25 07:04 | 2019-02-25 11:59 | 2019-02-25 | FITNESS-FOR-DUTY - LICENSEE SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL A non-licensed, licensee supervisory employee failed a for-cause FFD test for alcohol. The individual's authorization for site access has been denied. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.719 |  |  |  | 0 | 2019-02-25
53896 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2019-02-25 00:24 | 2019-02-25 03:44 | 2019-02-25 | AUTOMATIC REACTOR SCRAM DUE TO GENERATOR TRIP "At 0024 EST on 2/25/19, with Unit 1 in Mode 1 at 74 percent power, the reactor automatically tripped due to a generator trip. The trip was not complex, with all systems responding normally post-trip. "Operations responded and stabilized the plant. Reactor water level is being maintained via the feed system. Decay heat is being removed by discharging steam to the main condenser using the turbine bypass valves. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The generator trip is under investigation, but is believed to be due to grid perturbations. | 0 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2019-02-25
53895 | -1 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2019-02-23 | 2019-02-23 21:41 | 2019-03-01 | SAFEGUARDS REPORT - INTRODUCTION OF CONTRABAND INTO THE CONTROLLED ACCESS AREA Actual introduction of contraband into the controlled access area. The licensee notified the NRC Senior Fuel Facility Projects Inspector (Adkins). * * * RETRACTION AT 1243 EST ON 03/01/2019 FROM RICARDO MEDINA TO CATY NOLAN * * * The licensee determined that this was not a reportable event. Notified R2DO (Rose), NMSS Events, NRC Senior Fuel Facility Inspector (Adkins), and 73.71 Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2019-02-23
53894 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-02-23 14:58 | 2019-02-23 19:05 | 2019-02-23 | AUTOMATIC REACTOR SCRAM AFTER TURBINE CONTROL VALVE FAST CLOSURE "Actuation of RPS [Reactor Protection System] with the reactor critical. Reactor scram occurred at 1458 [CST] on 2/23/2019 from 100% power. The cause of the scram was due to Turbine Control Valve Fast Closure. "All control rods are fully inserted. Currently reactor water level is being maintained by the Condensate Feedwater System in normal band and reactor pressure is being controlled via Main Turbine Bypass valves to the main condenser. No ECCS [Emergency Core Cooling System] initiation signals were reached and no ECCS or Diesel Generator initiation occurred. "The Low-Low Set function of the Safety Relief Valves actuated upon turbine trip. This was reset when pressure was established on main turbine bypass valves. "The cause of the turbine trip is still under investigation. "There were no complications with scram response." The licensee notified the NRC Resident Inspector. There was no maintenance occurring on the main turbine at the time of the scram. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-02-23
53893 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2019-02-23 02:12 | 2019-02-23 09:13 | 2019-02-23 | AUTOMATIC ACTUATION OF 2C EMERGENCY DIESEL GENERATOR "At 0212 EST on February 23, 2019, with Unit 2 in Mode 5, an actuation signal for the 2C Emergency Diesel Generator (EDG) was received during the Loss of Coolant Accident / Loss of Offsite Power logic system functional test. The 2C EDG was running and tied onto the 2G 4160 emergency bus when the alternate supply breaker was closed as required per the test procedure. Immediately upon closing the alternate supply breaker, both the alternate supply breaker and 2C EDG output breaker tripped open. The 2C EDG output breaker reclosed once the 2G 4160 bus undervoltage relays sensed a deenergized bus. When the 2C EDG tied to the 2G 4160 bus, the bus voltage was noted as being high, and the 2C EDG was secured. Investigation is ongoing to determine the cause of the initial bus undervoltage and the subsequent bus excessive voltage. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the emergency AC power system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." This event puts Unit 1 in a 72 hour Limiting Condition for Operation for the 1C Startup Transformer being out of service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2019-02-23
53892 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2019-02-21 18:45 | 2019-02-22 17:40 | 2019-02-22 | IROFS SURVEILLANCE PERIODICITY ERROR "It was discovered that the calculation which determines the periodicity for performing the IROFSC22 [Item Relied On For Safety] surveillance contains an error. IROFSC22 is a mass balance enrichment control. "It is unclear if the calculation error causes the surveillance periodicity to fall outside of the minimum time to achieve a safe mass. UUSA [Urenco USA] has since changed the IROFS surveillance to a more frequent periodicity which has been determined to be sufficient. "Although no event has occurred and the IROFS remain sufficient to meet the performance requirements of 10CFR70.61, as a conservative measure, UUSA is reporting this condition due to the facility being in a state that is different from that analyzed in the Integrated Safety Analysis and in accordance with 10 CFR 70 Appendix A(b)(1) "The plant is in a safe condition." The licensee will notify NRC Region 2 (Lopez). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2019-02-22
53891 | 0 | FLOWSERVE |  |  |  |  | 2019-02-20 | 2019-02-22 14:35 | 2019-02-22 | PART 21 REPORT - FLOWSERVE VALVE ASSIST SPRINGS MAY PREVENT FULL CLOSURE The following report was received via fax: "Description: GE BWXT, acting on behalf of Ontario Power sent five valves back to the Flowserve facility for evaluation of the spring which could spread apart when the flapper rotates open and wedge between the valve body and flapper, creating the potential for the valve flapper to stick open. "Evaluation: Shop inspections of the returned valves confirmed the potential for the spring legs to rotate outwards and potentially wedge between the flapper and seat retainer. Of the five valves evaluated, two of the valves had the spring legs rotate outward and after repeated cycles got caught between the flapper and disc; on one of the instances the spring legs prevented full closure of the flapper. "If the valves have a safety-related function to isolate flow and must transfer closed, then the springs could prevent the valve from performing its safety related function. "The evaluation determined the cause is an inadequate spring design which allows the spring to deflect and permit the legs to move outward. "Extent of Condition: In discussion with the customer, it is believed the problem did not exist with valves originally supplied from the Worcester, Scarborough Canada facility; although this cannot be confirmed by Flowserve. It is believed the extent of condition resides with valves and replacement springs supplied from the Flowserve Raleigh, NC facility when the product line was transferred and the spring vendors changed; even though it has been confirmed that the springs supplied out of the Raleigh, NC facility comply with the product drawing requirements. The springs were first sold in valve assemblies or as replacement parts from the Raleigh facility starting in 2008. "Valve Scope: The scope of impacted valves is the Worcester series 44 swing check valves. (Please note Worcester also has a series 44 three piece ball valve, which is not in the scope.} The Raleigh facility has supplied parts or valves for four Worcester series 44 swing check valves assemblies which use these springs. The drawings numbers for these valve assemblies are listed below: Drawing Valve Size Customer KN44-0590 1.5 X 1 X 1.5 Bruce Power, GE BWXT & Ontario Power KN44-0630 2 Comanche Peak 14-107362-001 1.5 X 1 X 1.5 GE BWXT 16-118733-001 1.5 X 1 X 1.5 GE BWXT "Corrective Actions: 1) Owner's may remove the springs. The valves will check-off and seal under low pressure conditions without the assistance of the spring; this was demonstrated in shop tests using tap water pressure (approximately 60 psig) and will initiate closure when full open without the assistance of the spring. 2) Flowserve is evaluating alternate spring designs along with the possibility of adding guides to prevent the undesired spring movement. Any new design will be proof tested. "Respectfully submitted, Mark Rain, PE Product/Design Engineering Specialist Flowserve Corporation Flow Control Division 1900 S. Saunders St. Raleigh, NC 27603" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-02-22
53890 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2019-02-21 | 2019-02-22 13:30 | 2019-02-22 | AGREEMENT STATE REPORT - POTENTIAL RADIOGRAPHER OVEREXPOSURE "The Chief RSO for TechCorr USA, LLC contacted the Radiation Control Bureau of the State of New Mexico after he received a report from Landauer IAC that showed an employee had received in excess of 1000 Rads. "TechCorr is an industrial radiography company licensed in New Mexico. Based on the activity of the camera, the badge would have had to be exposed for 4 hours to get a dose reading of greater than 1000 Rads. After an interview with the employee, TechCorr has decided to send the employee to the hospital and have a blood sample drawn. "The film badge of the crew member who worked with the individual with the high film badge reading only showed around 200 mrem dose on his badge. A more complete investigation will follow" State Item Number: NM190001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2019-03-04
53889 | 0 | GLACIER NATIONAL PARK |  |  |  |  | 2018-08-31 | 2019-02-22 10:17 | 2019-02-22 | TRITIUM EXIT SIGNS DESTROYED IN A FIRE On August 31, 2018, an intense fire in Glacier National Park destroyed a building and with it six (6) exit signs containing Tritium (H-3). The intensity of the fire was such that the building has been reduced to ash. The remains of the building are still on site. After a discussion with Region IV, the licensee determined that the loss of the exit signs was reportable in accordance with 10 CFR 31.5. The licensee notified the Department of the Interior, National Park Service, Intermountain Regional Office in Denver CO, of the event. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | MT | MAT | [5 empty] | 0 | 2019-03-04
53888 | 0 | ABERDEEN PROVING GROUNDS |  |  |  |  | 2019-02-21 11:20 | 2019-02-21 13:27 | 2019-02-21 | NI-63 SOURCE LOST DURING SHIPMENT The following was received from the licensee via e-mail: "On 21 February 2019 the Aberdeen Proving Ground Garrison Radiation Safety Officer (RSO) notified [the Combat Capabilities Development Command Chemical Biological Center RSO] of a lost [commercial carrier shipment] containing multiple Chemical Agent Monitor (CAM) detectors. Shipment, dated November 26, 2018. "On November 26, 2018, the Garrison RSO shipped a package containing multiple chemical detectors with radioactive sources. One CAM, serial # 11769, containing 10 mCi of Ni-63 which is owned by the Chemical Biological Center under NRC license 19-10306-01, was included in the package. "The shipment was going to Pine Bluff, Arkansas for final waste disposal. "The Garrison RSO stated that a search for the packaged had been conducted at two [commercial carrier] locations, one in Maryland and one at the Pine Bluff final destination location with no package being found." This event is related to NRC Event Number 53884. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-03-01
53887 | 0 | AVERA MCKENNAN HOSPITAL |  |  |  |  | 2019-02-21 07:00 | 2019-02-21 11:28 | 2019-02-21 | MOBILE DIAGNOSTIC TRUCK INVOLVED IN FATAL TRANSPORTATION ACCIDENT The Avera McKennan Hospital mobile diagnostic truck was in an accident where the truck went off the road, the cab and box detached, and the driver was killed. The truck contained various used sources and medical materials used in nuclear diagnostic medicine. The sources, although ejected from the truck, were found nearby in their respective transport boxes with the exception of the Tc-99 used syringes (sharps). Surveys and wipe tests show no contamination. The sealed sources will be leak checked. The transport box for the Co-60 source was damaged with a small hole. Radiation readings are slightly higher in the proximity of the hole. All the recovered sources are in storage at the hospital. The sharps container was empty with the sharps strewn along the snow bank alongside the road. Residual materials may be within the sharps. Cleanup of the material is underway but may be delayed until the snow melts. The accident occurred on I-29, north of Sioux Falls, between the Baltic and Dell Rapids exits. The truck was headed north. The South Dakota Highway Patrol responded to the scene. Notified South Dakota Health Agency, DOT Crisis Management Center, DOE Ops Center, and DHS SWO. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | SD | MAT | [5 empty] | 0 | 2019-03-01
53886 | 0 | COLORADO DEPT OF PUBLIC HEALTH |  |  |  |  | 2019-02-11 | 2019-02-20 17:21 | 2019-02-20 | AGREEMENT STATE REPORT - LOST PACKAGE CONTAINING RA-223 The following report was received from the State of Colorado via email: "On February 14th, 2019, a written report was received from Cardinal Health detailing the events of a lost package containing 180.3 microCi (shipped activity) Ra-223. The package was lost in transit on February 11th, the intended recipient was in Savannah, GA. The courier for the package was a [Common Carrier]. A search by the [Common Carrier] located the package on the side of the road on February 12th in the Savannah, GA area. Regional Cardinal Health technicians were dispatched to the found package and determined that the transport index was as expected and the package indicated no removable contamination. Cardinal Health took possession of the package for decay-in-storage." CO Event Report ID No.: CO190002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2019-02-28
53885 | 0 | CA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2019-02-20 09:03 | 2019-02-20 15:15 | 2019-02-20 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received from the State of California via email: "On February 20, 2019, the RSO [Radiation Safety Officer] of G3SoilWorks, Inc. contacted the California Office of Emergency Services about a moisture density gauge that was stolen from the operators vehicle at an apartment complex [in] Newport Beach, CA. The gauge was a CPN MC-3, Serial Number M390705215 (10 mCi Cs-137, 50 mCi Am:Be-241). The incident was reported to the Newport Beach Police Department. The gauge has not been found at this time." California 5010 number: 022019 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-02-28
53884 | 0 | US ARMY TACOM |  |  |  |  | 2019-02-20 09:30 | 2019-02-20 13:25 | 2019-02-20 | REPORT OF LOSS OF NI-63 SOURCES USED IN IMPROVED CHEMICAL AGENT MONITORS The following was received from the licensee via e-mail: "The concerned radioactive material is part of an Army Chemical Detection Equipment (CDE) and is called an Improved Chemical Agent Monitor (ICAM) NSN [National Stock Number] 6665-01-357-8502 and Chemical Agent Monitor (CAM), NSN 6665-01-199-4153. Each ICAM and CAM contains 10 mCi of Ni-63. The items with the radioactive material are under US Army NRC License 21-32838-01 issued to the Tank-Automotive and Armaments Command (TACOM). TACOM is located in Warren, MI. "The reporting was based on 10 CFR 20.2201(a)(ii) (Reports of Theft or Loss of Licensed Material). Licensed material in a quantity greater than 10 times the quantity specified in Appendix C. The quantity specified in Appendix C is 100 microCi. One ICAM/CAM containing 10 mCi is 10,000 microCi. [The Radiation Safety Officer (RSO)] had reported nine CDE, but after confirming the serial numbers, we determined that one of the CDE (serial number 11769) was under another NRC license 19-10306-01 issued to the US Army Edgewood Chemical Biological Center (ECBC) located in Aberdeen Proving Ground (APG), Maryland. This report is for eight CDE under TACOM's NRC license. We have six ICAMs and two CAMs that are lost for a total of 80,000 microCi. The serial numbers for the ICAMs are Z47-M-13972, Z47-M-13526, Z47-M-01859, Z47-M-15832, Z47-M-21980 and Z47-M-18759. The serial numbers for the CAMs are Z16-M-01075 and Z16-M-01025. "The ICAMs/CAMs are not known to leak and do not have a leak test requirement. The Ni-63 is inside the ICAM/CAM. "[The RSO] was notified via e-mail on February 19, 2019, at 1545 EST, by the Army Rad waste agency (Joint Munitions Command [JMC] located in Rock Island, IL) of the following: "'A package containing nine each CDE was in route from APG, Maryland to Pine Bluff Arsenal (PBA), Alabama via [a Common Carrier] and was lost in the possession of [the Common Carrier]. The CDE were being sent for demilitarization and eventual disposal of the Ni-63. The subject package was dropped off at [the Common Carrier] in Baltimore, MD on 26 Nov 2018. The tracking system showing the package as 'In [Common Carrier] Possession'.' "Prior to the notification on February 19, 2019, JMC called PBA shipping and receiving. PBA personnel indicated that subject package was not received at their location. Also, APG personnel traveled to the [Common Carrier] facility where the items were dropped off. Personnel confirmed that the package was not at that facility. "As of February 19, 2019, JMC indicated that [the Common Carrier] has not formally issued the a statement of loss, but that JMC will continue to track this for APG. It was a Local Project for JMC with ID number of APG 2018-001. "On February 20, 2019, at 0847 EST, the [RSO] called [the Common Carrier] with the tracking number. [The RSO] spoke to [an individual] who indicated that a case was assigned to the shipment and a claim was put in. [The RSO] was put in contact with the Trace Department, and was then told that the shipment was considered lost. Shipments after 14 days are considered lost." This event is related to NRC Event Number 53888. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2019-02-28
53883 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-02-19 12:53 | 2019-02-19 15:19 | 2019-02-19 | SECONDARY CONTAINMENT INOPERABLE "On February 19, 2019, at 1307 EST, with the reactor at 100 percent Core Thermal Power and steady state conditions, plant personnel notified the Main Control Room that both doors in the Secondary Containment Airlock on the Reactor Building Fifth Floor were opened simultaneously for a period of approximately five minutes (i.e., from 1253 to 1258 EST). The failure of this interlock, which is intended to prevent both doors from being opened simultaneously, resulted in the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. The maximum Secondary Containment pressure observed during that time remained within TS limits. There were no radiological releases associated with this event. "Declaring Secondary Containment inoperable as a result of not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." The repair to the failed interlock is in progress. As a compensatory measure signs are posted on the doors to notify personnel to not access the Reactor Building via those doors. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-02-19
53882 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-02-18 | 2019-02-19 11:32 | 2019-02-19 | AGREEMENT STATE REPORT - LEVEL DENSITY GAUGE SHUTTER MALFUNCTION "On 02/18/2019, BCS [Blue Cube Solutions] was performing their routine operational checks of their RAM LICENSED devices. During their routine maintenance checks, the shutter malfunction was discovered. The gauge shutter would not close. BCS called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. "The sources and device with the shutter stuck open will remain installed on the process until the repairs are made. This is not a radiation exposure hazard and does not pose a health and safety situation for the BCS employees or the general public. "The Level Gauge is a KAY RAY Model 7062B device/source holder, S/N KR23306B, loaded with an approximately 100 mCi Cs-137 source. "LDEQ [Louisiana Department of Environmental Quality] was notified when BCS called the LDEQ Radiation Emergency Hot Line at 0800 CST. The notice was forwarded to the LDEQ/ERSD/Radiation Section. The notification was to get the preliminary information report and meet the 24 hour reporting requirement. Additional information will be provided when available. BCS will provide LDEQ a corrective action and a final report no later than 30 days of the corrective action. "This event is being reported to the NRC OPERATIONS CENTER as required by Regulatory Requirements 10 CFR Part 30.50(b)(2) & LAC 33:XV 340.B." Louisiana report LA-190002. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-02-27
53881 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2019-02-16 | 2019-02-18 15:01 | 2019-02-18 | AGREEMENT STATE REPORT - IRIDIUM 192 SEEDS LOST DURING MEDICAL TREATMENT The following was received from the state of North Carolina via email. "A patient underwent an Interstitial OBGYN Implantation on 2/14/19, consisting of 45 seeds of Iridium 192 (5 seeds per strand; total of 9 strands) with an activity of 34.1 mCi. The morning of 2/16/19, the patient, still located at the licensee's facility, removed the strands containing the sources, placing some in the room's trash and some in the toilet and flushed the sources. Four strands containing 20 seeds were flushed and the remainder in the room were recovered by radiation safety. The licensee confirmed surveys of the patient and room. No other sources were found. The patient room had been isolated when licensee personnel found the patient with the removed sources. The licensee's maintenance crew determined that waste pipes from the room were accessible through confined space entry via manholes to sewer system only. The NC RPS [North Carolina Radiation Protection Section] dispatched an investigator as soon as it was notified, same day. The licensee will not be pursuing the collection of these sources due to the added hazards of attempting searches in a sewer system." North Carolina Event Tracking ID 190003 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2019-02-26
53880 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2019-02-14 | 2019-02-17 08:25 | 2019-02-17 | AGREEMENT STATE REPORT - LOST MO-99/TC-99 GENERATOR The following is a synopsis from information received from the state of California via email. The California radiation protection program was notified by the licensee of a partially depleted, missing Mo-99/Tc-99m generator. The generator was shipped using a commercial carrier on October 31, 2018, from the licensee's California facility to their facility in Arlington Heights, Illinois. Near the beginning of February 2019, the licensee became aware that the generator did not arrive at its destination. The commercial carrier spent the last couple of weeks searching their facilities for the missing generator with no success and has suspended the search and considering the package lost. At the time of shipment, the generator contained 10.35 GBq (280 mCi), greater than 1000 times the 10 CFR 20 Appendix C activity for Mo-99, making it reportable under 10 CFR 20.2201(a)(1)(i). It is housed in a 12.7 kg depleted uranium shield. The package was shipped as a label category Yellow II, with a TI [transportation index] of 0.2. By November 5, 2018, the activity of Mo-99 would have decayed below the 10 CFR 20.2201(a)(1)(i) reporting criteria. By November 23, 2018, the activity of Mo-99 would have decayed below the 10 CFR 20.2201(a)(1)(ii) reporting criteria. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2019-02-25
53879 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2019-02-13 07:24 | 2019-02-15 17:07 | 2019-06-04 | AGREEMENT STATE REPORT - DOSE DELIVERED WAS LESS THAN PRESCRIBED The following was received from the Arkansas Department of Health, Radiation Control Program (the Department) via email: "The treatment prescribed activity was for 0.54 GBq (14.5 mCi) on February 13, 2019. The calibrated activity at projected treatment time was 0.53 GBq (14.3 mCi). The patient received a dose of 0.204 GBq (5.51 mCi) due to 61.5 percent of the dose remaining in the connector of the manufacturer tubing and the catheter Terumo-Progreat Microcatheter (2.0 French Catheter). The Department performed an on-site review and investigation on February 15, 2019 at approximately 1215 [CST]. "The Department performed exposure surveys of the connector confirming activity stuck at the connector site. The connector site read the highest and in that concentrated area, reading 430 mR/hr, on February 15, 2019, at approximately 1415 [CST]. "There were no spills and/or contamination during this event. "The licensee notified the manufacturer and the manufacturer will be performing an investigation on the tubing and radiopharmaceutical/sealed sources. The licensee is continuing to investigate the root cause and is preparing an initial fifteen day written report. "The Department is waiting on information from the manufacturer(s) and licensee for further investigation. The Department will update this report when the licensee provides additional information." Arkansas Event AR-2019-001 * * * UPDATE AT 1516 EST ON 3/7/19 FROM ANGIE HALL TO JEFF HERRERA * * * The following update was received from the Arkansas Department of Health, Radioactive Materials Program via email: "The Department [Arkansas Department of Health] received a Y-90 TheraSphere Glass Microsphere patient therapy misadministration notification on February 14, 2019 from a medical licensee. The Department performed an on-site review and investigation on February 15, 2019 at approximately 1215 [CST]. The Department has received the required initial fifteen day report from the Licensee. "The Y-90 TheraSphere therapy prescribed activity was for 0.54 GBq (14.6 mCi) on February 13, 2019. The Y-90 TheraSphere calibrated activity at projected treatment time was 0.53 GBq (14.3 mCi). The patient received a dose of 0.204 GBq (5.51 mCi) due to 61.5 percent of the dose remaining in the connector of the manufacturer tubing and the catheter. The catheter used was a Terumo-Progreat Microcatheter (2.0 French Catheter). This dose resulted in a 54.34 Gy exposure instead of the intended 143 Gy exposure. "The Licensee performs Y-90 TheraSphere therapies on a regular basis. The Licensee's physician/Authorized User and colleagues state that they have never had this issue before. The Authorized User states that 54.34 Gy is still a therapeutic dose. A patient CT follow-up scan will be performed to evaluate the therapy dose effectiveness. "The Department verified activity stuck at the connector site via exposure surveys with a Fluke ion chamber survey meter (reading 430 mR/hr) on February 15, 2019 at approximately 1415 [CST]. "The Licensee notified the Manufacturer and the Manufacturer will be performing an investigation on the tubing and on the radioactive sealed sources. "There were no spills and/or contamination during this event. "The Department is waiting on information from the Licensee regarding the Manufacturer's investigation. The Department will update this report when the Licensee provides additional information. "Corrective Actions: In Process by Licensee and Manufacturer." Notified the R4DO (Werner), NMSS Events (via email). * * * UPDATE FROM ANGIE HILL TO HOWIE CROUCH VIA EMAIL ON 4/24/19 AT 1708 EDT * * * "The Department received a report on April 24, 2019 (dated April 4, 2019) from the Licensee regarding the Y-90 TheraSphere misadministration. "The Department requested additional information on April 24, 2019, regarding the information provided by the Licensee. The request includes clarification from the manufacturer's report and the Licensee's corrective actions. "The Department will update this report when the Licensee provides additional information." Notified R4DO (Young) and NMSS Events (via email). * * * UPDATE FROM ANGIE MORGAN HILL TO HOWIE CROUCH VIA EMAIL ON 6/4/19 AT 1150 EDT * * * The following information was obtained from the state of Arkansas via email: "The Licensee has submitted to the Department the Manufacturer's Report, possible Root Cause and Corrective Actions. "According to the Manufacturer's Report, it states 'the most likely cause of this event is insufficient flow rate due to high backpressure associated with the microcatheter.' 'BTG [the manufacturer] recommends following the TheraSphere package insert guidance for the selection of a microcatheter with an inner diameter that is equal or larger than 0.020 inch.' The Manufacturer's Report also states, in part, 'A review of the manufacturing records confirmed there were no device defects.' "It is noted by the Licensee that the Authorized User prescribed a different size microcatheter from the Manufacturer Recommendations and Manufacturer's package insert. "The Licensee states regarding the root cause, 'After testing the tubing and catheter, it was determined that the event was caused by insufficient flow through the microcatheter possibly caused by overall length and inner diameter of the microcatheter, septum fragments from the dose vial, and possible changes in the condition of materials during the time from treatment to inspection (e.g. dried saline, coiled in tight bends for extended time.' 'Having several potential causes and contributing factors, the root cause is still not known.' The Licensee states that their corrective actions to prevent reoccurrence are '(1) continue to abide by our standard operating procedure of performing three flushes, ensuring the electronic dosimeter, or rados, is reading zero, and surveying the patient; (2) Flush an additional time with 20 mL of saline after the rados reads zero; (3) Will use a catheter with a diameter greater than or equal to 0.02 inches. A smaller catheter will only be used if the patient would otherwise be unable to receive the treatment due to small vessels.' The Department did not issue any Items of Noncompliance for this medical event. The Department considers this event closed. Notified R4DO (Kellar) and NMSS Events Notification (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2019-02-25
53878 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2019-02-15 | 2019-02-15 13:33 | 2019-02-15 | AGREEMENT STATE REPORT - THEFT OF A MOISTURE DENSITY GAUGE The following was received from the state of Mississippi via email: "Mississippi Department of Transportation (MS-261-01) reported that a Troxler Model 3440 (serial number: 19297) portable gauge containing 10 milliCuries of cesium-137 and 44 milliCuries of americium-241/beryllium was stolen from the licensee's job site trailer closet in Red Creek, Mississippi. The gauge was padlocked in its original carrying case. Local law enforcement and the FBI have been notified. Follow-up information will be provided to the NRC on the recovery of the stolen gauge and entered into the Nuclear Material Events Database." Mississippi Report Number: MS-190001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2019-02-25
53877 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-02-13 | 2019-02-15 11:47 | 2019-02-15 | AGREEMENT STATE REPORT - ADMINISTERED DOSE TO UNINTENDED ORGANS RESULTS OR WILL RESULT IN UNINTENDED PERMANENT DAMAGE The following was received from the Pennsylvania Department of Environmental Protection (DEP) Bureau of Radiation Protection via email: "On February 13, 2019, the patient was prescribed 31.3 milliCuries (mCi) Yttrium-90 (Y-90) Sirsphere for metastatic colorectal cancer and 31.69 mCi was delivered at time of treatment. From the post Y-90 Bremsstrahlung scan, performed on the day of treatment, it was discovered by the nuclear medicine physician, that some of the Y-90 microspheres also traveled to the stomach and left lobe of liver. The doctor has informed the patient and the patient is being monitored for potential complications. The doctor is working to determine the percentage of the Y-90 that went to stomach and left lobe of liver. No more information is available at this time from the licensee. The DEP will update this event as soon as more information is provided. "The DEP will perform a reactive inspection." The licensee reported this to the state per 10 CFR 35.3045 (b). Pennsylvania Report: PA190004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-02-25
53876 | 0 | KINGSFORD MANUFACTURING COMPANY |  |  |  |  | 2018-10-09 | 2019-02-15 09:40 | 2019-02-15 | NUCLEAR GAUGE SHUTTER STUCK OPEN The following is a summary from a phone call with the licensee: The licensee decided to remove seven nuclear gauges from service. Ronan Engineering performed the removal. During the device removal on October 9, 2018, one device was found to have a stuck shutter in the open position. The gauge was removed and repaired. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-02-25
53875 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2019-02-12 16:45 | 2019-02-13 14:35 | 2019-02-13 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following information was received via email from the state of North Dakota: "Desert NDT, LLC dba Shawcor reported a 3.256 TBq (88 Ci) Iridium-192 sealed source (Industrial Nuclear Model 32, serial #022E) had disconnected from a drive cable connected to an Industrial Nuclear Model IR-100 radiography exposure device (serial #4321) at a temporary job site in Williston, ND on 2/12/2019. The event occurred at 1645 [MST] while the radiography crew, consisting of a radiographer and assistant radiographer, was performing industrial radiography under extreme cold weather conditions on a pipe section. Upon retracting the source after the third exposure, the crew noticed the radiography device's safety latch did not pop up indicating the source in the safe/locked position. Upon performing a radiation survey while approaching the device, the crew noticed an increased exposure rate indicating a source disconnect. The crew immediately retreated from the device and reset an actual 2 mR/hr public dose boundary and contacted their radiation safety officer who made arrangements for authorized retrieval personnel to dispatch to the site. The crew maintained constant surveillance of the site while awaiting the source retrieval personnel. The source was successfully retrieved at 2020 [MST]. At the time of the event, the radiographer had received 50 mR and the assistant radiographer 55 mR on their direct reading dosimeters. The retrieval individual received a total of 357 mR to the direct reading dosimeter located on his arm and 243 mR to the direct reading dosimeter located on his chest. Shawcor will provide a detailed report to the North Dakota Department of Health upon establishing the root cause and corrective actions." NMED Item #ND190001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-02-21
53874 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2019-02-12 | 2019-02-13 13:29 | 2019-02-13 | AGREEMENT STATE REPORT - POTENTIAL GAMMA KNIFE TREATMENT UNDERDOSE RECEIVED The following was received from the state of New Jersey via e-mail: "While receiving treatment with an Elekta Leksell Gamma Knife Perfexion unit, serial number 6016, the patient's head may have slipped forward in the stereotactic frame by two millimeters. This was not noticed until after the treatment was completed. The licensee is not sure when the slippage occurred. If the movement occurred during treatment, the dose received would have been 50 percent of the prescribed dose. The authorized user and authorized medical physicist are in discussions with the Radiation Safety Officer concerning the matter. The licensee will follow-up with a full report." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2019-02-21
53873 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-02-13 | 2019-02-13 13:20 | 2019-02-13 | AGREEMENT STATE REPORT - REPORT OF LOSS OF BRACHYTHERAPY SEEDS The following was received from the State of Illinois via e-mail: "The agency [Illinois Emergency Management Agency] was notified the morning of 2/13/19 by Bard Brachytherapy, IL-02062-01, in Carol Stream to advise that a package of (34) I-125 brachytherapy seeds arrived with no obvious damage, but (5) of the (34) seeds were unaccounted for. Facility staff were immediately alerted of the issue when [the common carrier] opened the dock door and meters alerted to elevated radiation readings. (2) seeds were identified by the licensee staff outside of the package on the floor. Package wipes were taken and there is no indication of removable contamination. Each of the seeds has a current activity of 0.346 mCi and would have an exposure rate of approximately 0.6 mR/h at one foot. There is currently no reason to suspect any malicious intent or deliberate diversion of package contents. The five unaccounted for seeds contain an aggregate activity of 1.73 microCuries as of 2/13/19. "The [common carrier] driver's vehicle was surveyed by licensee staff. Additionally, it was determined that the driver picked the package up at O'Hare airport, went to the [common carrier's] hub and then directly to Bard. Licensee staff are coordinating with [the common carrier] and are currently en route to the hub to perform surveys. Additional details will be provided as they become available. This matter remains open." Illinois Item Number: IL190008 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-02-21
53872 | 0 | US ARMY AVIATION MISSILE COMMAND |  |  |  |  | 2019-01-31 | 2019-02-13 12:12 | 2019-02-13 | REPORT OF LOSS OF AM-241 SOURCES CONTAINED IN HELICOPTER LASERS The following is a summary of a call with the US Army Aviation Missile Command. While taking inventory of sources located in decommissioned helicopter lasers, the US Army Aviation Missile Command identified that they were missing 88 Am-241 sources located in 44 helicopter lasers. It can not be determined exactly where the sources were lost, though the licensee is going to provide possible options, including that the lasers could have been lost during combat. It is assumed that the sources are not in public areas. It can not be determined when the sources were lost. The licensee noted that it is unlikely anyone would receive a dose as a result of this loss of material because it is difficult to retrieve the sources. The US Army continues to attempt to find the sources during routine house keeping activities. They have a similar license for a new aircraft and will perform inventory checks more frequently to ensure that any losses are more promptly reported. The licensee has notified the NRC Regional Office. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | AL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-02-21
53871 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2019-02-10 | 2019-02-13 12:00 | 2019-02-13 | AGREEMENT STATE REPORT - GAUGE DEVICE DAMAGED BY MOLTEN STEEL The following report was received from the Commonwealth of Kentucky via fax: "KY RHB [Kentucky Radiation Health Branch] was notified by telephone on 2/12/2019 at 1315 EST by a representative from a specifically licensed facility, North American Stainless, that on Sunday, 2/10/2019, North American Stainless encountered a 'breakout' when molten steel escaped and poured onto billet caster molds located below a 'tundish' filled with molten steel. One of the molds attached to a Berthold Model No. LB300ML Mold Level Control fixed gauging device, serial number 9415, containing 1 mCi (37 MBq) Co-60 (source serial number 1819-11-15) was covered with the liquid steel encapsulating the source holder. After the steel and mold had cooled, it was freed on 2/12/2019 and segregated. The encapsulating steel rendered the device on-off mechanism (shutter) inoperable. Initial readings taken with a Ludlum 2241-3 survey instrument measured 6.25 mR/hr measured 12 inches directly in front of the window, and 1.25 mR/hr measured 90 degrees from the line of the window measured at a distance of 12 inches. Readings at the back of the source holder were 132 microR/hr measured at a distance of 12 inches. No overexposures have been reported. On 2/12/2019, Radiametric Technologies, a service provider located in Lorain, Ohio, requested reciprocal approval and was granted reciprocity on 2/13/2019 in order to assess and remediate the situation. "The fixed gauging device involved in the incident was recently leak tested (test conducted on 7/31/2018) by Suntrac Services, League City TX. Radiametric Technologies, Lorain OH, recently tested the source holder on-off mechanism (1/31/2019) and it was found to be in good working order. North American Stainless is reviewing the incident to avoid future incidents involving 'tundish' failures. A full report will be provided once the remediation is complete. "Reporting criteria in 10 CFR 30.50(b)(2)." KY Report #KY190001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2019-02-21
53870 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2019-02-12 09:00 | 2019-02-13 09:42 | 2019-02-13 | FITNESS FOR DUTY - ENTERGY NON LICENSED SUPERVISOR FAILED TO REPORT FOR FITNESS FOR DUTY TEST On 1/17/2019 at 0619 CST, a non-licensed employee supervisor failed to report to perform a fitness for duty test. The individual's access to the site was terminated. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.719 |  |  |  | 0 | 2019-02-13
53869 | -1 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2019-02-11 15:19 | 2019-02-12 13:55 | 2019-03-07 | LOSS OR DEGRADATION OF SAFETY ITEMS "[On February 11, 2019 at 1519 MST,] it was discovered that the calibration certificates for Measuring and Testing Equipment (M&TE) used to perform temperature trip IROFS [Items Relied On For Safety] surveillances, only had 1 set of calibration data. The instruments have an internal temperature sensor and an external input for temperature. Previously, the IROFS surveillances for IROFS 1, 2, 4, 5, 11, 43, C15, and C16 were performed using the external input. "An external vendor, that performs the calibration for this M&TE, confirmed that the calibration had only been performed on the internal temperature sensor. This issue of how ATC-1 and ATC-2 (Jofra brand dry-block temperature calibrators) were calibrated is not currently an issue, as UUSA [URENCO USA] now only uses the Jofras as a heat source and uses a separately calibrated resistance temperature detector (RTD) and display for IROFS surveillances. "Further investigation findings showed that a number of UF6 stations had not had their scheduled surveillance with the new method using a separately calibrated RTD. In total, 25 stations had their required annual IROFS surveillances performed with M&TE equipment which used an input that was not properly calibrated. "The plant is in a safe condition." The licensee will be contacting Region II. * * * RETRACTION ON 3/7/2019 AT 1518 EST FROM BLAKE BIXENMAN TO ANDREW WAUGH * * * "Event Notification (EN) 53869, made February 11, 2019, reported a condition in accordance with Appendix A to 10 CFR 70 (b)(2). The notification described degradation of items relied on for safety (IROFS) that could potentially result in failure to meet the performance requirements of 10 CFR 70.61. "This notification was prompted by improperly calibrated Measuring and Testing Equipment (M&TE) which was used to perform surveillance activities for IROFS 1, 2, 4, 5, 11, 43, C15, and C16. At the time of the report, functionality of the IROFS' Active Engineered Controls within the acceptable parameters could not be verified. Therefore, URENCO USA (UUSA) conservatively assumed a degradation of IROFS resulting in failure to meet the performance requirements of 10 CFR 70.61. "Since the time of the initial report, UUSA has re-performed surveillance activities using approved methods and obtained as found tolerances of the Active Engineered Controls for all of the affected stations. With this supporting data, UUSA has concluded that the affected IROFS were, at all times, operating below the maximum IROFS trip set point. "The operating events using improperly calibrated M&TE can be categorized as events with low safety significance since they would not have resulted in breached/ruptured UF6 cylinders. Cylinder integrity would not have been compromised, as the temperature sensors were found to be available and reliable to perform their safety function. This correlates with a low consequence event. "Based on engineering determinations and as found trip set points, the condition reported in EN 53869 did not result in failure to meet the performance requirements of 10 CFR 70.61. Therefore, the reported condition did not exceed the criteria which would necessitate an event be reported to the NRC. URENCO USA hereby retracts EN 53869." The licensee has notified Region II. Notified R2DO (Desai) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2019-02-20
53868 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2019-02-08 | 2019-02-11 14:15 | 2019-02-14 | AGREEMENT STATE REPORT - DELIVERED DOSE TO PATIENT LESS THAN PRESCRIBED DOSE The following report was received from the Pennsylvania Department of Environmental Protection Bureau of Radiation Protection via email: "The licensee reported that on February 8, 2019, while reviewing a patient treatment plan, it was discovered that the patient had received a dose from a high dose rate remote afterloader containing iridium-192 that was less than the prescribed dose in the written directive. The original treatment plan was prescribed for 7.0 Gy per fraction, however at the beginning of the 3rd fraction it was noticed that the total dose delivered was 4.67 Gy instead of the prescribed 14 Gy they should have received for the same 2 fractions. The physician has informed the patient and will amend the written directive to add additional fractions at different doses to achieve the original prescribed dose to the treatment area. No more information is available at this time from the licensee. We will update this event as soon as more information is provided. "Cause of the Event: Unknown / Human error. "ACTIONS: The Department [Pennsylvania Department of Environmental Protection] will perform a reactive inspection. More information will be provided upon receipt." * * * UPDATE AT 1227 EST ON 02/14/2019 FROM JOHN CHIPPO TO TOM KENDZIA * * * The following update was received from the Pennsylvania Department of Environmental Protection via email: "The patient received treatment on January 29, 2019, and February 5, 2019. The patient had not finished her initially scheduled 3rd fraction. The Medical Event was identified on Friday, February 8, 2019. The equipment manufacturer is Varian, model VariSource iX(t), Serial Number 00400. The source activity as of February 11, 2019 was 6.819 Ci. The licensee is still in the process of identifying root cause and corrective action." Pennsylvania Report: PA190003 Notified the R1DO (Ferdas) and NMSS Events (via email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-02-19
53867 | 0 | AZZ NUCLEAR |  |  |  |  | 2015-10-01 | 2019-02-08 18:31 | 2019-02-11 | PART 21 - EATON A200 STARTERS DID NOT OPEN WHEN POWER WAS REMOVED The following is a synopsis of the Part 21 received: "Pursuant to 10 CFR 21.21(d)(3)(ii), AZZ Nuclear is providing initial written notification of the identification of a deviation. "PDMS material has been identified in the Eaton A200 series starters/contactors with date code T4115 (41st week of 2015) which is outside the range of May 2008 to December 2012 that were originally identified in NRC Event Number 51611 from 2015. This resulted in a few instances where the starter did not immediately open when the power was removed." Point of contact for additional information: Tracy Bolt, Director of Quality Assurance AZZ Nuclear 7410 Pebble Drive Ft. Worth, TX 76118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [10 empty] | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-02-11
53866 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-08-01 | 2019-02-08 15:58 | 2019-02-08 | AGREEMENT STATE REPORT - LOSS OF TRITIUM EXIT SIGNS The following was received via email from the Nebraska Department of Health and Human Services: "Nebraska Department of Health and Human Services, Office of Radiological Health followed up with a phone call to Nebraska General Licensee GL0762 concerning their Annual Radioactive Materials License Renewal and Inventory Sheet on 2/7/2019. The licensee indicated over the phone that 2 tritium exit signs have not been seen or on the property since at least August 2018. The licensee was instructed to search the entire facility and report their findings. "On 2/8/2019, the licensee conducted a complete search of the property grounds and could not locate the exit signs. Records were searched and no indication was made to the disposal of the signs. The property manager believes that they may have been disposed of in the regular trash and moved to the local landfill. "The exit signs were from the Isolite Corporation, model SLX60, containing 6 Curies of H-3 each." State Event Report ID No.: NE-19-0001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2019-02-18
53865 | 0 | MRIGLOBAL |  |  |  |  | 2019-01-29 | 2019-02-08 09:46 | 2019-02-08 | LOSS OF ELECTRON CAPTURE DETECTOR WITH NICKEL-63 SOURCE The following is a summary of a discussion with the licensee: On approximately January 29, 2019, MRIGlobal in Kansas City, Missouri determined that they had lost a 15 milliCurie Nickel-63 source contained in an Electron Capture Detector (ECD - SN Agilent Technologies - U-2802). The detector was taken out of service in 2015, though an employee continued to note that leak testing had been done on the detector since then. During the performance of an inventory in December 2018, they noticed that the Serial Number did not match and attempted to locate the detector. The facility was closed over the holiday season, but the licensee searched after returning from the break. It was previously believed that the detector had been given to staff to be placed in a storage area. During their search, the licensee found e-mails stating the detector had been taken out of service. Based on the e-mails, the licensee believes the detector has been missing since 2015. The licensee is not certain of the current location of the ECD. During an attempt to locate the source, the licensee checked in the safety storage room, the old radiation storage shed, and other file cabinets and drawers in the facility. There is no risk from exposure due to the loss of the source. The licensee notified the Region 3 materials inspector (Tran). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2019-02-18
53864 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2019-02-07 10:50 | 2019-02-07 17:05 | 2019-02-07 | FITNESS-FOR-DUTY - ALCOHOL CONSUMED IN PROTECTED AREA "A non-licensed and non-supervisory employee inadvertently possessed and consumed alcohol within the protected area. The employee's access to the plant has been suspended." The Senior Resident Inspector has been notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 26.719 |  |  |  | 0 | 2019-02-07
53863 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2019-02-05 18:00 | 2019-02-06 12:46 | 2019-02-06 | FITNESS-FOR-DUTY - CONTRABAND DISCOVERED IN PROTECTED AREA On February 05, 2019 at approximately 1800 EST, candy that contained alcohol was discovered in the plant protected area. The candy was removed from the protected area by station security management. The licensee notified the NRC Resident Inspector and the State of New York Public Service Commission. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2019-02-06
53862 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-04-20 | 2019-02-06 11:40 | 2019-02-06 | AGREEMENT STATE REPORT - UNDERDOSE EXCEEDING 20 PERCENT OF THE PRESCRIBED DOSE The following was received via email from the state of Illinois: "During a routine inspection [by the State of Illinois] of Riverside Medical Center, IL-01242-01, conducted on January 29, and continued document review conducted February 5, 2019, inspectors identified an apparent under dose to a patient receiving I-125 seed prostate therapy. The event occurred in April of 2016. Of the six patient records reviewed (all 2016), one post operational dosimetry report indicated a D90 of 120.7 Gy, resulting in a 24.5 percent variance from the prescribed dose of 160 Gy. Two of the patient records did not have a post operational dosimetry report and inspection findings indicate the licensee does not have written procedures for prostate seed therapies which ensure the administrations are in accordance with the written directive. As a result of the lack of procedures, the determination of a 20 percent variation from the prescribed dose is being compared against the D90 value following prior recorded NMED [Nuclear Materials Events Database] events and NRC guidance. The licensee has been notified and will submit a written report within 15 days. "The licensee is not actively engaged in brachytherapy and the authorized user is no longer with the licensee. Agency enforcement action will ensure either procedures are established or modality authorization is removed. Pending appropriate address of the patient's treatment and root cause by the licensee, a reactive inspection is not being conducted in accordance with Management Directive 8.10, Section III(A)(3). This report will be updated as additional details become available." Item Number: IL190007 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-02-14
53861 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2019-02-05 18:04 | 2019-02-06 02:22 | 2019-02-06 | UNIT ONE HPCI SYSTEM INOPERABLE DUE TO BLOWN FUSE "On February 5, 2019, at 1804 [CST], during a Unit 1 High Pressure Coolant Injection (HPCI) operability surveillance, a fuse blew in the logic for the motor speed changer for the turbine. The Unit 1 HPCI system was taken out of service for planned maintenance earlier in the day. The fuse issue was not related to any maintenance activities. Had HPCI been demanded, this fuse failure would not have allowed HPCI to reach its required speed. HPCI remains inoperable pending resolution of the issue. The Reactor Core Isolation Cooling (RCIC) system was confirmed operable. There were no other systems inoperable at the time of the event. HPCI had been last successfully tested on November 6, 2018. "This event is being reported as a condition that could have prevented fulfillment of a safety function in accordance with 10 CFR 50.72(b)(3)(v)(D). The HPCI system is a single train system and the loss of HPCI could impact the plant's ability to mitigate the consequences of an accident. "The NRC Senior Resident Inspector has been notified." Inoperable HPCI places the unit in a 14 day Technical Specification Limiting Condition of Operability. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-02-06
53860 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2019-02-04 14:03 | 2019-02-04 18:40 | 2019-02-04 | FITNESS FOR DUTY - LICENSED OPERATOR CONFIRMED POSITIVE FOR DRUG TEST A licensed reactor operator had a confirmed positive random fitness-for-duty drug test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2019-02-04
53859 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-02-04 | 2019-02-04 17:32 | 2019-02-04 | AGREEMENT STATE REPORT - UNDERDOSE EXCEEDING 20 PERCENT OF THE PRESCRIBED DOSE The following was received via email from the state of Illinois: "Alexian Brothers Medical Center has advised that an attempted intravascular brachytherapy procedure utilizing a Novoste BetaCath System [containing a sealed source of Sr-90] appears to have resulted in a medical event with an underdose exceeding 20 percent of the prescribed dose. The source train was unable to reach the target location after three attempts, stopping approximately 60mm proximal. The source train was retracted without complication after a 'few seconds' during each attempt. The prescribed exposure was 18.4 Gy. The licensee estimates the unintended area receiving dose (aorta) received 0.006 Sv, less than the 0.5 Sv reporting requirement. This matter is being reported due to the fact the intended tissue received less than 20 percent of the intended dose. This event is ongoing and the report will be amended as details become available. This will be reported to NMED today. "There is no adverse medical consequence expected for the patient." Item Number: IL 190006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-02-12
53858 | -1 | SAN ONOFRE |  |  |  | ISFSI | 2019-02-01 14:05 | 2019-02-02 13:44 | 2019-04-02 | NO SEISMIC ANALYSIS FOR CANISTER TRANSPORT PROCESS "During follow-up reviews resulting from the Aug. 3, 2018 canister downloading event (EN#53605), Southern California Edison [SCE] became aware of a condition where, during short periods of the canister transport process, the Vertical Cask Transporter (VCT) could have been operated without a supporting seismic analysis while transporting loaded canisters for storage. SCE has decided to conservatively report this issue. "The VCT is a mobile gantry crane that is used to transport and download fuel canisters into an Independent Spent Fuel Storage Installation (ISFSI) enclosure. Twenty-nine canisters have been downloaded into the San Onofre nuclear plant ISFSI in this manner since January, 2018. The Holtec UMAX Certificate of Compliance requires that lifting of a loaded spent fuel canister must be performed with redundant (i.e., single-failure-proof) load drop protection features. Inherent in the definition is the ability to withstand seismic loading. SCE identified that although applicable rigging and downloading procedures were followed, a supporting seismic analysis should be developed for the short duration periods in the process where the canisters are transitioned to rigging. "Southern California Edison has directed its vendor, Holtec, to perform this further seismic analysis. While the additional analysis may conclude that the VCT is stable and functional during these transitioning periods, SCE will work with the vendor should modifications to the canister transport process become necessary. "SCE is making this notification in accordance with the requirements of 10 CFR 72.75(d)(1). There was no seismic event that resulted in damage to the VCT or a spent fuel canister during the fuel transfer campaign. All 29 spent fuel canisters are currently in safe storage within the ISFSI." * * * RETRACTION FROM TIM CUSICK TO DONALD NORWOOD AT 1930 EDT ON 4/2/2019 * * * "On 4/2/19, Southern California Edison (SCE) is retracting San Onofre Nuclear Generating Station (SONGS) Event Report 53858 dated February 2, 2019 for the Independent Spent Fuel Storage Installation (ISFSI). SCE conservatively submitted the event report under 72.75(d)(1) after it was initially determined the Vertical Cask Transporter (VCT) may have been operated for short periods of time during the canister transport process without a supporting seismic evaluation, contrary to the requirements of the Certification of Compliance (COC). A revision to the calculation by the vendor has subsequently confirmed the transport process and VCT operation met the seismic requirements of the Holtec COC. Therefore, Event Report No. 53858 is retracted." Notified R4DO (Gaddy) and via E-mail IRD MOC (Kennedy) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 72.75(d)(1) |  |  |  | 0 | 2019-02-02
53857 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2019-02-01 12:00 | 2019-02-01 17:22 | 2019-02-01 | AGREEMENT STATE REPORT - UNDER DOSE ADMINISTRATION OF Y-90 SIR-SPHERES The following was received via email from the state of Illinois: "Midwestern Regional Medical Center, Inc. (Zion, IL) administered an under dose of Y-90 SIR-Spheres to a patient. The intended dose was 21.06 mCi but only 10.10 mCi was administered. The imaging supervisor called on 02/01/19 to report a possible medical event. The event occurred today at 1200 CST. During the administration the licensee began to feel pressure in the syringe. A smaller gauge syringe was used but made no difference so the treatment was aborted. Clumping of the microspheres in the catheter is suspected as the cause. Only about 52 percent of the dose was delivered. The licensee is still working on the dosimetry, but it appears that a medical event has occurred in any case. "They intend to treat the patient again after an investigation." Illinois Item Number: IL 190005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-02-11
53856 | 0 | SOR |  |  |  |  | 2018-12-08 | 2019-02-01 13:53 | 2019-02-01 | PART 21 - NOTIFICATION OF DEVIATION OF SWITCHES WITH TERMINAL BLOCKS The following was received via fax and email from SOR: "Exelon Limerick generating station notified SOR on December 8, 2018 via email regarding corrective action needed for the R-series housing on two of their emergency diesel engines. Limerick reported that the field wire lugs were in close contact with the switch cover gasket and had degraded the EPR (Ethylene Propylene Rubber) housing cover material enough to short to the cover which, in turn, tripped the 1A control fuse. Limerick reported that the uninsulated terminals and wiring were already available at the switch location during installation and used without modification. Limerick's immediate corrective action was to land the field wiring on the bottom tier of the terminal block and insulate the lugs. "EPR is known to be an effective electrical insulator, and is used as insulation for many electrical cables. For this reason, the EPR cover gasket was used on the SOR R-series nuclear housing to offer sufficient electrical insulation. Due to the failure at the Limerick generating station and subsequent evaluation at SOR, the EPR gasket alone does not provide sufficient electrical insulation between the terminal block connections and the metallic housing cover when uninsulated terminals are installed. This direct connection will cause heating of the gasket and eventual direct short through the EPR material. "SOR does not have the capability to perform further evaluations to determine if a safety hazard exists as the specific customer installation practices is unknown. The end user must confirm for each application the wire installation applied with this specific model string." The plants who are potentially affected by this deviation are in the process of being notified by email and/or postal letter and are: - Callaway - Braidwood - Byron - Limerick - Quad Cities - Davis Besse - St. Lucie - H.B. Robinson "SOR has completed or is implementing the following corrective actions: - Completed the identification of the customers potentially affected by this deviation within this notification - Initiated customer complaint 21 and corrective action (CAR) 1003 - Released ECO 5443 to add 3.5" wide Nomex insulation paper to the terminal block units - Created a modified cover gasket with a Kapton insulation piece for field units - Revision to SOR General Instruction to require customers to use insulated terminal connections targeting completion by February 28, 2019 - Investigate modification to SOR insulation resistance and dielectric tests targeting completion by February 28, 2019" Should you have any additional questions regarding this matter, please contact: For general inquiries: Linda Coutts Inside Sales Representative Email: lcoutts@sorinc.com Tel 913-956-3071 For technical inquiries: Mike Bequette Vice President of Engineering Email: mbeguette@sorinc.com Tel 913-956-3040 Sara Roos Senior Engineer Email: sroos@sorinc.com Tel 913-956-3049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-02-01
53855 | -1 | LACROSSE | 1 |  |  | [1] AC (ALLIS CHAMBERS) | 2019-02-01 | 2019-02-01 11:03 | 2019-02-13 | SAFEGUARDS REPORT - ADMINISTRATIVE LAPSE OF ACCESS CONTROL FOR A SAFEGUARDS LOCATION A security officer, whose qualifications were temporarily suspended, was performing access control to a safeguards area. No actual breech of safeguards occurred. The licensee notified the NRC R3 Security Inspector (Bonano). * * * RETRACTION AT 1328 EST ON 02/13/19 FROM CHERYL OLSON TO BRIAN P. SMITH* * * The purpose of the notification is to retract ENS Notification 53855 made on 02/01/19. Generic Letter 91-03, NRC Reporting of Safeguards Events, dated March 6, 1991, specifically enclosure 1 page 2, provides guidance on access control situations similar to the event on 02/01/19 which would not need to be reported to the NRC. Notified R3DO (Duncan), Region 3 Security Inspector (Bonano), and 73.71 Safeguards Group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 1 | 2019-02-01
53854 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2019-01-31 10:30 | 2019-01-31 17:06 | 2019-01-31 | FALSE NEGATIVE INDICATED ON A FITNESS FOR DUTY BLIND QUALITY ASSURANCE TEST "On 1/31/2019, the Medical Review Officer for Seabrook was notified of an error made by the HHS [Health and Human Services] certified lab resulting in a false negative Fitness for Duty quality assurance test result. The test lab, Quest Diagnostics-Norristown, was provided an adulterated sample specimen that was part of a blind performance test, which tested negative. This false negative test result will be investigated and the results reported as required. "This event is being reported in accordance with 10 CFR 26.719(c)(3). "NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.719 |  |  |  | 0 | 2019-01-31
53853 | -1 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2019-01-31 07:43 | 2019-01-31 10:48 | 2019-03-22 | BOTH EMERGENCY DIESEL GENERATORS INOPERABLE DUE TO LOW AIR TEMPERATURE "At 0743 [CST] on 1/31/2019, both trains of Unit 2 Diesel Generators were declared INOPERABLE due to outside air temperature exceeding the low temperature design limit for the diesel engines; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v) for an event or condition that could have prevented the fulfillment of a safety function. The Unit 2 Diesel Generators are still able to start if necessary to provide power. Additionally, multiple layers of defense in depth measures are in place to ensure safety. Prairie Island has five sources of offsite power; all of which are currently available. The Unit 1 Diesel Generators are OPERABLE and capable of being cross-connected to Unit 2. Additional equipment capable of responding to beyond design basis events is available on site providing another layer of defense in depth. "Both Unit 2 Diesel Generators were returned to an OPERABLE status at 0810 on 1/31/2019 based on outside air temperature rising above the low temperature design limit with forecasted temperatures to remain above the low temperature design limit. "There is no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The air temperature limit was -30 degrees Fahrenheit. Unit 1 was not affected. The EDGs were supplied by a different manufacturer with different air temperature limits. * * * RETRACTION AT 1340 EDT ON 03/22/2019 FROM BRIAN JOHNSON TO JEFFREY WHITED * * * "Engineering analysis performed subsequent to the event notification has determined that both Unit 2 Diesel Generators would have been able to fulfill their safety function during the period of time when the outside air temperature had exceeded the low temperature design limit. Therefore, EN# 53853 is being retracted. "The NRC Resident Inspector has been notified of the event notification retraction." Notified R3DO (McCraw). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-01-31
53852 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2019-01-31 03:01 | 2019-01-31 04:23 | 2019-01-31 | MANUAL REACTOR TRIP - CIRCULATING WATER ICING CONDITIONS "At 0301 [EST] on 1/31/19, with Unit 2 in Mode 1 at 100% power, the reactor was manually tripped due to icing conditions requiring the removal of 4 Circulating Water Pumps from service. The trip was not complex, with all systems responding normally post-trip. 21 CFCU [Containment Fan Cooler Unit] was inoperable prior to the event for a planned maintenance window and did not contribute to the cause of the event and did not adversely impact the plant response to the trip. An actuation of the Auxiliary Feedwater System occurred following the manual reactor trip. The reason for the Auxiliary Feed Water System auto-start was due to low level in a steam generator. Operations responded and stabilized the plant. Decay heat is being removed by the Main Steam Dumps and Auxiliary Feedwater System. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is also being reported as an eight hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feed Water System. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The icing condition was described as frazil ice. Unit-1 reduced power to 88% because one circulating water pump was shutdown. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-01-31
53851 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2019-01-30 09:10 | 2019-01-30 17:41 | 2019-01-30 | SECONDARY CONTAINMENT INOPERABLE "At 0910 [CST] on January 30, 2019, the Dresden Station Heater Boiler 'B' tripped while placing the station Heater Boiler 'A' in service. With colder temperatures, the density of the supply air increased and contributed to a greater quantity of air entering the Reactor Building than what was previously being supplied with heating steam in service. The Reactor Building differential pressure (DP) degraded and dropped below 0.25 inches water column vacuum. This condition represents a failure to meet Technical Specification (TS) Surveillance Requirement 3.6.4.1.1. Entry into TS 3.6.4.1 Condition A was made due to Secondary Containment becoming inoperable. "Standby Gas Treatment System was initiated to assist with Reactor Building DP control. Reactor Building DP was restored to greater than 0.25 inches water column vacuum. TS 3.6.4.1 Condition A was exited. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to ... control the release of radioactive material.' "The NRC Resident Inspector has been notified." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-01-30
53850 | 0 | INTERTEK ASSET INTEGRITY MANAGEMENT |  |  |  |  | 2019-01-29 | 2019-01-29 10:44 | 2019-01-29 | RADIOGRAPHY CAMERA SOURCE DISCONNECTED The following incident occurred in federal waters on Chevron's St. Malo platform. On January 26, 2019, while retracting the source after a radiography shot, the radiographer determined that the source had become disconnected. The radiographer and assistant radiographer established a 2 mR boundary and contacted their radiation safety officer (RSO). The RSO dispatched a licensed source retriever to the platform. After arriving at the platform on January 27, 2019, the source retriever was able to place the source into a shielded container. The source and camera were transported back to the licensee facility located in Houma, LA. The camera and source will be inspected/repaired by the manufacturer prior to placing them back into service. The camera is a SPEC-150 camera, serial number 1717, containing a 33 Ci Ir-192 source, serial number ZI0603. The licensed retriever received 275 mR during the retrieval. The radiography and assistant radiography technicians received 24 mR and 41 mR exposure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-02-06
53849 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-01-27 19:13 | 2019-01-28 15:01 | 2019-01-28 | CONTROL BLADE INOPERABLE "On January 27, 2019, at 1913 CST, with the University of Missouri-Columbia Research Reactor (MURR) operating at 10 MW in the automatic control mode, the Lead Senior Reactor Operator (LSRO) was conducting surveillance Technical Specification (TS) 4.2.a, which states, 'All control blades, including the regulating blade, shall be verified operable within a shift.' During this shiftily verification of control blade operability, all blades were initially verified operable. However, when banking the control blades to their final position after all blades were satisfactorily tested a few seconds earlier, shim control blade 'A' would not move in the inward direction. The LSRO then immediately shut down the reactor by initiating a manual scram by placing the Master Control Switch 1S1 to the 'TEST' position. The LSRO completed all immediate and subsequent actions of reactor emergency procedure REP-2, 'Reactor Scram,' and verified all shim control blades were fully inserted. "The inability to manually insert shim control blade 'A' with Control Rod Operate Switch 1S4, which inserts and withdraws the control blade, is a deviation from TS 3.2.a, which states, 'All control blades, including the regulating blade, shall be operable during reactor operation.' "Troubleshooting revealed a problem with an electrical contact on Control Rod Operate Switch 1S4, and it has since been replaced. The reactor has not returned to operation at the time of this email. However, permission from the Reactor Facility Director has been obtained to restart the reactor once scheduled maintenance activities have been completed. A detailed event report will follow within 14 days as required by MURR TS 6.6.c(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2019-01-28
53848 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2019-01-25 14:30 | 2019-01-25 16:27 | 2019-01-25 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following information was received via email from the State of Oklahoma: "On January 25, 2019, at approximately 1430 CST, [Oklahoma Department of Environmental Quality (DEQ)] received a call from Sagebrush Pipeline Equipment Company, Inc., Oklahoma License No. OK-32109-01. [The licensee] experienced a guide tube disconnect, while the source was cranked out. They were using a SPEC 150 with 48 Ci of Ir-192. The carded radiographer explained that when cranking out the source, there was a small catch, so he attempted to crank the source back into the camera. That was when they realized the guide tube was disconnected from the camera, and the source while still connected to the guidewire, was still in the guide tube. They were able to return the source back to its shielded position. [Oklahoma DEQ] will provide updates when they receive the licensee's report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2019-02-04
53847 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2019-01-24 | 2019-01-25 10:37 | 2019-01-25 | AGREEMENT STATE REPORT - PATIENT UNDERDOSED BY GREATER THAN 20 PERCENT The following was received from the State of New Jersey via email: "While a dosage of samarium-153 Quadramet was being administered to a patient, no one noticed that there was a crack in the locking assembly of the IV tubing connection. As a result, when the material was being administered, most of it leaked out of the assembly, rather than being administered to the patient. This resulted in the patient receiving only 2.35 mCi of the prescribed dosage of 58 mCi. This caused a reportable underdosage. The physician has been informed and all the necessary involved persons involved have been supplied with this information. The licensee will follow-up with a full report." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2019-02-04
53846 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2018-12-06 | 2019-01-24 17:15 | 2019-03-21 | PART 21 - POTENTIAL DEFECT IN VICKERS VOLTAGE REGULATOR SYSTEM The following summary was provided in the Part 21 report: "ESI [Engine Systems Inc.] was notified on December 6, 2018 of a potential issue with saturable reactors (also referred to as magnetic amplifiers) supplied to Monticello Nuclear Generating Plant. ESI provided the reactors as like-for-like replacements for the existing magnetics of the original Vickers voltage regulator and static exciter. During system testing performed by Monticello at another vendor facility, issues with the static excitation system were identified which prevented proper control of the generator field current. Troubleshooting identified several potential causes and ESI believes there may be a potential deficiency in the saturable reactor, P/N 8408218-ESI. "This component is integral to operability of the Vickers style voltage regulator and static exciter systems used on many emergency diesel generator sets in the nuclear industry. A deficiency in the reactor would adversely affect the ability to control generator output voltage and therefore adversely affect emergency diesel generator set performance. "ESI is in the process of performing additional testing and analysis at the transformer manufacturer's facility to determine if a deficiency exists in this component. ESI is unable to complete an evaluation within the 60-day requirement." ESI has supplied the part to NRC licensees but, to ESI's knowledge, none of the components have been installed. ESI is notifying each customer and advising not to install the reactors until the evaluation is complete. This Part 21 Report affects the following licensees: Surry Power Station Turkey Point Nuclear Generating Station Monticello Nuclear Generating Station Point of Contact: Dan Roberts Telephone: 525-977-2720 Fax: 252-446-1134 175 Freight Road, Rocky Mount, NC 27804 * * * UPDATE ON 3/21/19 AT 1448 EST FROM DAN ROBERTS TO JEFFREY WHITED * * * The following is a summary of the information provided by the vendor via fax: On January 24, 2019, Engine Systems Inc. (ESI) issued interim report 10 CFR 21-0124-INT, rev.0 regarding an identified deviation for which ESI was unable to complete an evaluation within the 60-day requirement. Per the interim report, ESI committed to complete the evaluation by March 22, 2019. The evaluation is now complete and the deviation is determined to be reportable in accordance with 10 CFR Part 21. Identification of the basic component supplied within the United States which fails to comply or contains a defect and nature of the defect: Part Number (P/N) 8408213-ESI: Power Current Transformer - Insufficient core gap. P/N 8408218-ESI: Saturable Reactor - Differences in coil winding and core lamination from original design. P/N 8411387-ESI: Excitation Power Transformer - Incorrect polarity Each of the devices listed above provide a specific function within the static exciter of a Vickers voltage regulator system. The exciter supplies DC excitation current to the generator field based on input from the voltage regulator. Failure of any one of the components to perform correctly will negatively impact excitation current supplied to the generator field which in turn directly affects generator output. Therefore, failure of any one of the components may prevent the emergency diesel generator from carrying its associated safety-related loads. The corrective action which has been, is being, or will be taken: P/N 8408213: Return to ESI for rework. The part required additional insulating material to increase the core gap. P/N 8408218: Return to ESI for replacement. P/N 8411387: Return to ESI for rework to have primary terminal markings re-labeled. Contacts: John Kriesel Engineering Manager Engine Systems Inc. 175 Freight Rd. Rocky Mount, NC 27804 Dan Roberts Quality Manager Engine Systems Inc. 175 Freight Rd. Rocky Mount, NC 27804 Affected facilities still include Monticello, Turkey Point, and Surry. Notified R2DO (Montgomery) and R3DO (McCraw), Part 21/50.55 Reactors group via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2019-01-24
53845 | 0 | NUCOR STEEL |  |  |  |  | 2019-01-24 07:00 | 2019-01-24 15:36 | 2019-01-24 | GAUGE NOT OPERATING DUE TO POWER LOSS TO UNIT The following was received via e-mail: "[The Nucor Steel] Electrician received a call this morning at approximately 0700 EST by the slitter line operator notifying him that the slitter line gauge was not operating and had no power to the entire unit. The electrician did a survey to ensure the shutter was closed on the device. He measured 12 microR/hr on contact, at 1 foot and at 3 feet. At that time he trouble shot the electrical and determined that it was something that was not going to be resolved quickly so he locked out the device and did another survey to confirm that the shutter was closed. He used a Fluke 451 meter serial# 2194 Calibration date 5/30/2018. "[The Nucor Engineer] went over this afternoon to confirm the survey with another meter and got 18 microR/hr on contact, 8 microR/hr at 1 foot with a background of 5 microR/hr, [using] a fluke 451P serial #6064 meter with calibration date 5/30/2018. "[Nucor] maintenance personnel are planning on continuing to troubleshoot the electrical issue and determine whether they can fix it or they will need to call in an outside vendor tomorrow. Only electrical work on power to the system will be performed by Nucor personnel. "[The Nucor] radioactive materials registration is XF7000385, expires 12/9/19. The gauge is a DMC AM-5A Serial# BS957911 with a Am-241 source 1 Curie activity Serial# 5135LV." No personnel radiation exposure occurred due to this event. No additional notifications were performed by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-02-01
53844 | -1 | TILDEN MINING COMPANY L.C. |  |  |  |  | 2019-01-24 | 2019-01-24 11:14 | 2019-02-18 | FAILURE TO CLOSE AND LOCK NUCLEAR GAUGE SHUTTER The following was received via e-mail: "Between 2200 EST on January 23, 2019 and 0000 EST on January 24, 2019 a Ronan RLL1 [Density Scale Source] was unbolted from the frame on which it was mounted and placed on the floor. (Source was a Cs-137 0.54 milliCurie decayed to 0.45 milliCurie, Serial #212785A) "No permit was pulled to remove the scale source, and the shutter wasn't closed and locked out. "After it was unbolted, and was placed on the floor with the beam pointed towards a conveyor belt and the ceiling. "Balling line 10, Conveyor 21 was approximately 6 feet above the placed source, and the ceiling is at 60 feet. "No employees worked in front of the beam once placed on the floor. "No one noticed the scale sitting on the floor unlocked until January 24, 2019 around 1500 EST. "Once the source was found, trained personnel put the shutter block in place and locked out the source. "The RSO then authorized a permit. "Once the source was secured, and permit posted, the RSO did a full investigation. "Basic cause - The maintenance employee that unbolted the source entered the area from a direction that could only be accessed during a maintenance down. There was a radiation label on the scale itself, but no sign from his access point." * * * RETRACTION ON 2/18/19 AT 1311 EST FROM LAWRENCE GRAY TO THOMAS KENDZIA * * * Based on the findings of an NRC inspector, this event was determined to not be reportable since the shutter was fully functional and no exposure to personal occurred. Notified R3DO (Duncan), NMSS Events Notification Group by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-02-01
53843 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2018-10-05 | 2019-01-23 13:49 | 2019-01-23 | AGREEMENT STATE REPORT - MISSING I-125 SEED The following report was received via fax: "On 11/28/2018 the Department [New York State Department of Health] was notified of a missing I-125 localization seed (Best Medical International, Inc., Model 2301, Activity: 186 microCuries) at Roswell Park Cancer Institute in Buffalo, New York. "Two lodine-125 breast localization seeds were placed into a patient on September 20, 2018 and removed on September 28, 2018. One seed was placed in a specimen container with the specimen, and the other seed was placed into a separate specimen container. Surgery has documentation that both seeds were sent to Pathology in separate containers; however, only one was returned to the Nuclear Medicine Department on October 4, 2018. The RSO was informed on October 5, 2018. The facility conducted searches and surveys of the Surgery, Pathology, Nuclear Medicine and Environmental Services areas, but could not locate the missing seed. Trash and regulated medical waste were also surveyed and inspected. Searches and surveys were repeated, but the seed was not found. It is believed that the seed was disposed of as regulated medical waste or in regular trash." New York State ID: NYSDOH - 18-04 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2019-01-31
53842 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2019-01-22 07:23 | 2019-01-22 14:40 | 2019-01-22 | FITNESS FOR DUTY POLICY VIOLATIONS - PRESENCE OF ALCOHOL IN THE PROTECTED AREA "On January 22, 2019, 0723 CST, the Contracts group called and reported to FFD [fitness for duty], that a box of candy was received from a supplier vendor that may contain alcohol. Upon investigation of the candy with the manufacturer, pieces of the candy contain 20-30mg of Alcohol after the chocolate is cooked. The Contract offices are located in the Protected Area and this incident is being reported under 10 CFR 26.719." No for-cause testing was performed based on the consumption of the candy. No safety related work was performed by the individuals who may have consumed the candy. The box of candy was removed from the site. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 26.719 |  |  |  | 0 | 2019-01-22
53841 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2019-01-21 12:35 | 2019-01-22 12:15 | 2019-01-22 | DEVIATION OF TS 3.3.a(1) for ANTI-SIPHON DEVICE FOUND INOPERABLE "On January 21, 2019 at approximately 1235 CST, with all four (4) shim control rods fully inserted into the reactor core during performance of a pre-startup checklist, the University of Missouri-Columbia Research Reactor (MURR) deviated from Technical Specification (TS) 3.3.a(1) due to test jumpers being installed while electrical power was available to the shim rod drive mechanism electromagnets. Prior to this event, the reactor was shut down for a regularly-scheduled maintenance period. A required notification per TS 6.6.c(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1, had occurred. Specifically, MURR was not in compliance with all TS Limiting Conditions for Operations, specifically TS 3.3.a(1). "For about ten (10) seconds at approximately 1235 CST, power was available to the shim rod drive mechanism electromagnets while electrical test jumpers, which hold anti-siphon system isolation valves V543A and V543B closed, were inserted. In effect, the anti-siphon system was not operable while the reactor was technically operating for ten (10) seconds per the following definitions: 1. TS 1.23 Reactor in Operation - The reactor shall be considered in operation unless it is either shutdown or secured. 2. TS 1.27 Reactor Shutdown - The reactor is shutdown when: All four (4) of the shim blades (rods) are fully inserted and power is unavailable to the shim rod drive mechanism electromagnets. 3. TS 1.26 Reactor Secured - MURR did not meet the definition of Reactor Secured during the event. "Though all four shim rods were fully inserted and a reactor startup had not commenced, electrical power being available to the shim rod drive mechanism electromagnets caused the reactor to technically be in Operation for a very brief period. Though this event happened at approximately 1235 CST, it was not fully identified as an abnormal occurrence per TS 1.1.b until approximately 1625 CST, after a reactor startup was performed to 10 MW operation. Once the abnormal occurrence was realized, the Reactor Facility Director was immediately notified at 1715 CST, and he gave permission to continue reactor operation. A detailed event report will follow within 14 days as required by MURR TS 6.6.c(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2019-01-22
53840 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-12-02 00:28 | 2019-01-22 09:41 | 2019-01-22 | INVALID CONTAINMENT VENTILATION ISOLATION ACTUATION "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report an invalid Containment Ventilation Isolation (CVI) actuation at Watts Bar Nuclear Plant (WBN) Unit 1. "On December 2, 2018 at 0028 Eastern Standard Time (EST), the Train A CVI actuated due to an invalid High Radiation signal from 1-RM-90-130, Containment Purge Exhaust Radiation Monitor. In addition to the Train A CVI, instrument malfunction alarms were received for 1-RM-90-106, Lower Containment Radiation Monitor and 1-RM-90-112, Upper Containment Radiation Monitor as the associated valves isolated for the CVI. A common instrument malfunction alarm was also received for 1-RM-90-130 and 1-RM-90-131, Containment Purge Exhaust Radiation Monitors. Prior to and following the invalid High Radiation alarm, all radiation monitors except 1-RM-90-130 were stable at their normal values. All required automatic actuations occurred as designed. Upon investigation, the cause of the invalid High Radiation alarm was due to a failed ratemeter for 1-RM-90-130. "Control room operators performed appropriate checks and confirmed that the subject indication was an invalid high radiation signal. The ratemeter for 1-RM-90-130 was replaced and the monitor returned to service. At the time of the event, plant conditions for a High Radiation alarm did not exist; therefore, the CVI was invalid. "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-01-22
53839 | 0 | BAXTER |  |  |  |  | 2019-01-21 09:00 | 2019-01-22 08:36 | 2019-01-22 | IRRADIATOR POOL WATER CONDUCTIVITY EXCEEDS LIMIT During a routine surveillance, oil was seen in the pool with the underwater irradiator. Testing found that the pool's conductivity was 180 micro Siemens per centimeter (æS/cm), exceeding the 20 æS/cm regulatory limit and the 100 æS/cm reportability limit. The licensee is currently filtering the water to clean up the pool and at the time of the notification had lowered the conductivity to 160 æS/cm. Additional filters are being purchased and the licensee estimates a few more days before the conductivity will be below the regulatory limit. A leaking chiller was identified as the source of the oil. An assessment is being conducted to either repair or replace the chiller. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | POOL COND HIGH | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 36.83(a)(10) |  |  |  | 0 | 2019-01-30
53838 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2019-01-21 09:30 | 2019-01-22 07:27 | 2019-01-22 | SIGNIFICANT FITNESS FOR DUTY POLICY VIOLATIONS - PRESENCE OF ALCOHOL IN THE PROTECTED AREA "On January 21, 2019 at approximately 0930 [EST], BWXT NOG-L Security management determined alcohol had been introduced into the Protected Area. The item in question was a single empty container of rum (50mL) which was identified in a break area trashcan. "An engineer in the area observed the bottle in the trash when filling a coffee mug. The engineer immediately took control of the bottle and contacted BWXT Security Management who contacted the Fitness for Duty Coordinator (FFDC). The bottle was turned over to the FFDC, who maintained control of the bottle while it remained in the Protected Area. The area where the bottle was located is a limited access common area, and area management was briefed on the discovery. "Area management interviewed personnel with access to the common area in an attempt to determine if any individuals exhibited indicators of substance abuse or had information pertaining to the item or its introduction into the area. Management interviews resulted in no individuals who exhibited substance abuse indicators and no additional information in reference to the item. "At approximately 1030, the Fitness for Duty Coordinator escorted the bottle out of the Protected Area. "BWXT NOG-L Management will provide incident information to all site personnel, conduct an evaluation of the incident, and enter a corrective action into the P/CA System to capture lessons learned and mitigate future events." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 26.719 |  |  |  | 1 | 2019-01-22
53837 | 0 | WATERFORD | 3 |  |  | [3] CE | 2019-01-18 13:33 | 2019-01-18 17:03 | 2019-01-18 | REACTOR COOLANT SYSTEM WELD DOES NOT MEET ACCEPTANCE CRITERIA "This is a non-emergency notification from Waterford 3. "On January 18, 2019, a relevant indication was detected in the performance of Phased Array Ultrasonic Examinations of A600 Dissimilar Metal Piping Welds during planned inspections. The indication was observed during the analysis of data recorded of the Reactor Coolant System (RCS) Loop 2A Reactor Coolant Pump Suction Drain Nozzle to Safe-End Butt Weld (11-007). This indication does not meet applicable acceptance criteria under American Society of Mechanical Engineers (ASME) Section XI. The plant was in Mode 6 (Refueling) at 0 percent power for a planned refueling outage at the time of discovery. The condition will be resolved prior to plant startup. This condition has no impact to the health and safety of the public. This report is being made in accordance with 10 CFR 50 .72(b)(3)(ii)(A), 'Any event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded,' because an indication was found that did not meet acceptance criteria referenced in ASME Section XI , IWB-3514-2 and Code Case N-770-2, 3132. "The NRC Resident Inspector has been notified. "Reference: CR-WF3-2019-01041" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2019-01-18
53836 | -1 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-01-18 | 2019-01-18 16:49 | 2019-02-21 | AGREEMENT STATE REPORT - MISADMINISTRATION OF RADIUM-223 TO PATIENT The following was received via e-mail: "On January 18, 2019, the Texas Department of State Health Services was contacted by the licensee's radiation safety officer (RSO) and notified that they had a treatment error occur at their facility. The error occurred to a patient who was to be treated with multiple fractions of radium-223. The treatment was to relieve bone pain in the patient. The dose from each fraction was based on the weight of the patient. The fraction activity was determined to be 75 microCuries based on the weight in pounds of the patient involved. The technician involved with administering the dose mistook the weight units and ordered the fraction dose based on the patients weight measured in kilograms. As a result the patient was administered 165 microCuries of radium-223 instead of the 75 microCuries. The error was discovered as they were preparing to administer the second dose (The date of the first dose was not provided). The RSO stated the patient and prescribing physician have been contacted and notified of the error. The RSO stated the patient would not experience any adverse effects from the dose received. The RSO stated the patient's treatment going forward is being reviewed. The RSO stated they would provide a written report next week. "At 1530 hours the Agency contacted the RSO and confirmed the dose to the patient. The RSO stated the dose to the bones from the activity given would be 693 rad instead of 315 rad. "Additional information will be provided as it is received in accordance with SA-300." Texas Department of State Health Services Incident Number 9651 * * * RETRACTION AT 1558 EST ON 2/21/2019 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "This event was determined not to be a reportable event. It does not meet the reportability criteria. Dosage on the written directive, signed by the prescribing physician/authorized user, was the dosage administered to the patient." Notified the R4DO (Deese) and NMSS (via e-mail). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-01-28
53835 | 0 | NUCOR STEEL CORPORATION |  |  |  |  | 2019-01-18 | 2019-01-18 14:00 | 2019-01-18 | PROCESS GAUGE CLOSED SHUTTER INDICATION NOT FUNCTIONAL A process gauge shutter indication did not properly indicate that the shutter was in the closed position. A survey was performed and verified that the shutter was indeed in the closed position. The system has been locked out to prevent access and the licensee stated that repairs to the gauge shutter are in progress. Gauge Model No.: DMC-AM-5A Source: Am-241 Activity: 1.0 Curies Serial Number: 1979LQ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2019-01-28
53834 | 0 | WATERFORD | 3 |  |  | [3] CE | 2019-01-17 18:58 | 2019-01-17 23:07 | 2019-01-17 | RELEVANT INDICATION OF DEGRADED CONDITION "This is a non-emergency notification from Waterford 3. "On January 17, 2019, a relevant indication was detected in the performance of Phased Array Ultrasonic Examinations of A600 Dissimilar Metal Piping Welds during planned inspections. The indication was observed during the analysis of data recorded of the Reactor Coolant System (RCS) Loop 1A Reactor Coolant Pump Suction Drain Nozzle to Safe-End Butt Weld (07-009). This indication does not meet applicable acceptance criteria under American Society of Mechanical Engineers (ASME) Section Xl. "The plant was in Mode 6 (Refueling) at 0 percent power for a planned refueling outage at the time of discovery. The condition will be resolved prior to plant startup. This condition has no impact to the health and safety of the public. This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A), 'Any event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded,' because an indication was found that did not meet acceptance criteria referenced in ASME Section Xl. IWB-3514-2 and Code Case N-770-2, 3132. "The NRC Resident Inspector has been notified. "Reference: CR-WF3-2019-0967" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2019-01-17
53833 | 0 | WESCHLER INSTRUMENTS |  |  |  |  | 2019-01-11 | 2019-01-17 14:50 | 2019-01-17 | PART 21 - POTENTIAL DEFECT IN WESCHLER KX-241AXIAL, VX-252, AND VC-252 INSTRUMENT MODELS The following is a summary of the Part 21 report: There is a potential defect identified in Weschler KX-241 axial, VX-252, and VC-252 instrument models. The condition could result in the instrument's inability to perform its safety-related function, which is accurate indication of a measured process. The symptom of this inability to perform its safety-related function is changing indication, which is not accurately reflective of the monitored process. This symptom may exhibit as a wandering indication or difficulty in maintaining a stable zero scale setting. The condition is due to a dimension of a component of the assembly being beyond lower tolerance limits. The part, known as the insulating bushing, is part number 186N051H01. It is used as one of the two anchor and centering points for the part of the instrument that the pointer is attached to. The subject instrument models are and have been sold as commercial, nuclear designated and nuclear safety-related. The affected production period is from August 15, 2018, when the non-compliant bushings were received from the supplier, through January 11, 2019, when the condition was discovered by production personnel. The initial analysis of the movement of bushings through inventory suggests that non-conforming bushings may not have been used on safety-related instruments, or were used in a quantity of less than 10 units. If you have any questions related to this information please contact: Nancy Hughes Quality Assurance Manager Weschler Instruments Division of Hughes Corporation 4000 N.W. 121" Ave. Coral Springs, Florida 33065 Email: nancy.hughes@weschler.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-01-17
53832 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2019-01-17 08:45 | 2019-01-17 16:00 | 2019-01-17 | FITNESS-FOR-DUTY - CONTRACTOR SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL A non-licensed contractor supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The contractor's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2019-01-17
53831 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2019-01-16 19:08 | 2019-01-16 23:51 | 2019-01-16 | OFFSITE NOTIFICATION DUE TO FIRE REQUIRING LOCAL FIRE DEPARTMENT RESPONSE "At 1908 CST, a fire was reported in an unoccupied exclusion area opening (EAO) enclosure outside of the Fort Calhoun Station protected area. Offsite fire departments responded at 1923 CST and the fire was extinguished by 1930 CST. There were no injuries reported. "The State Fire Marshal of Nebraska was notified by the Blair (Nebraska) Fire Department at approximately 1913 CST. His investigation determined the cause to be a malfunctioning heating element in a climate control unit. There was no release of radioactivity or hazardous materials." The climate control unit was clarified to be a ceiling mounted heater in the enclosure. The licensee notified the NRC Decommissioning Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2019-01-16
53830 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-01-16 09:00 | 2019-01-16 18:38 | 2019-01-16 | SIGNIFICANT FITNESS-FOR-DUTY POLICY VIOLATION "At 0900 EST on 01/16/2019, it was discovered that a licensee manager intentionally failed to re-approve the list of individuals granted unescorted access to verify each individual was subject to a behavioral observation program. Compensatory actions have been taken in response to this event. Personnel affected have had their access authorization suspended. "This is reportable under the provisions of 10 CFR 26.719(b)(3) as an intentional act that casts doubt on the integrity of the Fitness-For-Duty program. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2019-01-16
53829 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2019-01-15 15:09 | 2019-01-16 15:10 | 2019-01-16 | FITNESS-FOR-DUTY REPORT REGARDING A NON-LICENSED SUPERVISOR "A non-licensed supervisor failed to disclose information as required by the fitness-for-duty program. The employee's access to the plant has been terminated. "The NRC Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2019-01-16
53828 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2019-01-16 01:37 | 2019-01-16 08:12 | 2019-01-16 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE EXCEEDED TECHNICAL SPECIFICATION ALLOWED VALUE "On January 16, 2019, with James A. Fitzpatrick Nuclear Power Plant operating at 100 percent power, the Emergency and Plant Information Computer (EPIC) indicated that Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement of greater than or equal to 0.25 inches of vacuum water gauge while isolating Reactor Building Ventilation. The Secondary Containment differential pressure was less than 0.25 inches of vacuum water gauge for approximately ten (10) seconds, and then immediately returned to greater than or equal to 0.25 inches of vacuum water gauge. "This condition did not impact the leak tightness of Secondary Containment or the ability of the Standby Gas Treatment system to establish and maintain the required differential pressure. When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was inoperable. This event is being reported under 10 CFR 50.72(b)(3)(v)(C)." "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2019-01-16
53827 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2019-01-15 08:00 | 2019-01-15 12:25 | 2019-01-15 | FITNESS-FOR-DUTY VIOLATION At 0800 CST on January 15, 2019, a non-licensed employee supervisor had a confirmed positive for alcohol during a for-cause fitness-for-duty test. The employee's access to the plant has been placed on hold. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 26.719 |  |  |  | 0 | 2019-01-15
53826 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2006-09-21 | 2019-01-14 18:12 | 2019-01-15 | UTAH AGREEMENT STATE REPORT - RECOVERY OF A LOST RADIOACTIVE SOURCE The following information was received from the state of Utah via email: "The NMED Item Number: 140349 describes that a fixed gauge source (Serial Number: 207822A) from Idahoan Food, LLC was lost/stolen/missing [last seen in 2006; entered in NMED on 3/31/14]. The source was found in Utah on November 28, 2018. On January 10, 2019 it was recovered and properly disposed of by Qal-Tek. "For details on the identification, retrieval, and disposal of the source please see the following below: "On November 28, 2018 the Utah Division of Waste Management was notified by the Ogden, Utah Police Department that an unknown radioactive source had been found at the Swift Building located at 390 West Exchange Road in Ogden, Utah. It was found during the EPA cleanup of the site. "On December 2, 2018 [an Ogden Police Officer] visited the Swift Building and determined the following about the source: Ronan Engineering Company RLL1 (Radiation Low Level Source) Serial Number: 207822A Date: 08/06 Activity level: 0.81 mCi Cs-137 "Doing a search of the serial number in the NRC ADAMS system it was determined that the source was a lost/stolen/missing source from Idahoan Food, LLC, a NRC General Licensee in the State of Idaho (See ML4170B170 for details). "On December 6, 2018 the State of Utah notified Idahoan Foods, LLC that the source had been found and gave them the contact information for the Ogden Police Department. On December 11, 2018 the State of Utah notified the NRC by e-mail that the source (207822A) had been found in Utah. On January 14, 2019 the State of Utah let the NRC know that the source had been properly disposed of on January 10, 2019 by Qal-Tek." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2019-01-23
53825 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-01-14 09:58 | 2019-01-14 13:12 | 2019-01-14 | ACTIVE SEISMIC MONITORING SYSTEM INOPERABLE "On 01/11/2019 at 0958 EST, the Fermi 2 Active Seismic Monitoring system was taken out of service for planned maintenance. During the maintenance activity, the Active Seismic Monitoring System failed a planned surveillance test and was not restored to operability within 72 hours. Compensatory measures to provide alternative methods for event classification of a seismic event were implemented in accordance with the Fermi 2 Emergency Plan procedures prior to the start of the planned maintenance outage. The planned outage time to restore operability exceeded 72 hours on January 14th, 2019, at 0958 EST. Repairs have been completed, the Active Seismic Monitoring System has been declared Functional at 1037 EST, January 14th, 2019, and declared Operable at 1109 EST, January 14th, 2019. "The loss of the Active Seismic Monitoring System is reportable to the NRC within 8 hours of discovery in accordance with 10 CFR 50.72(b)(3)(xiii). "No seismic activity has been felt onsite and the United States Geological Survey (USGS) recorded no seismic activity in the area. "The NRC Resident Inspector has been notified." Femi 2 has two seismic monitors, one on the Reactor Pressure Vessel Pedestal and one in the High Pressure Core Injection (HPCI) room. Only the HPCI room monitor was inoperable. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2019-01-14
53824 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2019-01-13 08:30 | 2019-01-13 17:49 | 2019-03-07 | HIGH PRESSURE CORE SPRAY SELF TEST FAILURE "On January 13, 2019, the Self Test System reported a fault associated with the logic system for the High Pressure Core Spray (HPCS) high reactor water level closure function that could prevent the system from performing its safety function. The HPCS system was subsequently declared inoperable with actions taken per LCO [Limiting Condition for Operation] 3.6.1.3 to close and deactivate the 1E12-F004 valve, a primary containment isolation valve. "Since HPCS is an emergency core cooling system and is a single train safety system, this condition is reportable under 10 CFR 50.72(b)(3)(v)(D) 'Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "The NRC Resident Inspector has been notified." HPCS is in a 14-day technical specification LCO action statement. * * * RETRACTION AT 1908 EST ON 3/7/19 FROM JAMES FORMAN TO JEFF HERRERA * * * "Testing of the logic system load driver card for the High Pressure Core Spray (HPCS) high reactor water level closure function was completed both on site and at General Electric Hitachi (GEH). This testing determined the cause of the self-test system fault report was limited to the self-test portion of the load driver card and did not impact the ability of HPCS system to perform its specified safety function. "Based on the testing results, this event is not reportable under 10 CFR 50.72(b)(3)(v)(D), 'Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' Therefore, EN 53824 is being retracted. "The NRC Resident Inspector has been notified." Notified the R3DO (Hills). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-01-13
53823 | 0 | MINNESOTA DEPARTMENT OF HEALTH |  |  |  |  | 2018-12-24 | 2019-01-11 10:08 | 2019-01-11 | AGREEMENT STATE REPORT - LOST THEN FOUND STATIC ELIMINATOR The following report was received from the State of Minnesota by email: "The licensee uses a static eliminator on the end of an air line. Typically the static eliminator is kept on the line and not removed. The licensee recently moved locations and not all of their stations were set up, so they were moving the static eliminator around. The static eliminator was removed from a line and placed on top of a box. It slid off the box and ended up under a nearby pallet. They noticed the static eliminator was missing on 12/24/2018. The pallet was moved and the static eliminator was found on 1/11/2019. All of the stations are now set up and the static eliminator will stay connected to a dedicated line. "Material: Po-210, NRD model P-2021, 1.9 mCi on 1/10/19 "State event report: MN190001" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | AGR |  |  |  |  | 0 | 2019-01-21
53822 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2019-01-11 09:11 | 2019-01-11 10:07 | 2019-05-21 | FITNESS FOR DUTY A non-licensed employee disclosed that he had previously used illegal drugs. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ETHAN HAUSER TO DONALD NORWOOD AT 1456 EDT ON 5/21/2019 * * * "The following event notifications are retracted: EN 53822 reported on 1/11/2019 and EN 53982 reported on 4/5/2019. "Subsequent to the initial notification, further investigation revealed that no new information was discovered that would meet the criteria for reporting under RG 5.62 or NUREG-1304. Further the events were also determined to be limited to an act of personal deception by those applying for unescorted access, without intent to commit or cause events identified in paragraphs I (a) and (d) of Appendix G to Part 73, and is not a programmatic breakdown. Based on this information, and consistent with the NRC memorandum dated May 19, 1995, 'Access Authorization Reportability and Enforcement Issues,' this event does not meet the threshold for reporting. "The NRC Resident Inspector has been notified." Notified R3DO (Cameron) and via E-mail the FFD E-mail group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2019-01-11
53821 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2019-01-10 | 2019-01-10 17:25 | 2019-01-10 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was received from the State of Texas via email: "On January 10, 2019, during a routine gauge inspection/shutter check, the handle broke off the rod that turns the shutter on an Ohmart Model HM-10 source holder which contained 5,000 milliCuries of cesium-137 (original activity) (SN: 6967). The shutter is in the closed position and there is no risk of exposure. External corrosion was observed. The licensee plans, at this time, to replace the gauge and further evaluation will be performed at the time of replacement. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: I-9649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2019-01-18
53820 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2019-01-08 00:30 | 2019-01-10 13:32 | 2019-01-10 | AGREEMENT STATE REPORT - UNABLE TO RETRACT RADIOGRAPHY SOURCE The following information was received from the State of Louisiana via email: "On 01/08/2019, 1535 CST, [the licensee] called the Louisiana Department of Environmental Quality (LDEQ) to report a source would not retrieve back into the shielded position. The event happened at approximately 0030 CST at a temporary jobsite in Loggy Bayou, LA Red River Parish. "The camera was being used at this temporary jobsite. The exposure was made and the source would not retract into the shielded position. The reportable event was the 'drive cable' in the crankout handle broke in the associated equipment being used with this QSA Global, Model 880 Delta gamma camera/exposure device. The SN for the 880D is #14342. The device was loaded with 72.7 Ci of Ir-192 with the SN# 73586G. "The Industrial Radiography Crew followed the H & H Safety Procedures and contacted the radiation safety officer. A three-man crew performed the source retrieval and equipment evaluation after the repair/fix. The exposure device was put back into service after the repair. Two personnel involved in this retrieval received exposures of 40 mrem and the other individual's exposure was 50 mrem. The Industrial Radiography Crew's pocket dosimeter readings were 13 mrem and 11 mrem for the shift when the incident occurred. There were no excessive exposures associated with this event." Event Report ID No.: LA-190001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2019-01-18
53819 | 0 | PALISADES | 1 |  |  | [1] CE | 2019-01-09 10:34 | 2019-01-09 13:23 | 2019-01-09 | REACTOR TRIP FROM FULL POWER DUE TO RPS TESTING "At 1034 EST on January 9, 2019, with the reactor at 100% power, an automatic reactor trip was initiated. The trip occurred while Reactor Protection System testing was in progress. The trip was uncomplicated with all systems responding normally following the rip. Troubleshooting and investigation of the cause is ongoing. "All full-length control rods inserted fully. Auxiliary Feedwater System actuated as designed in response to low steam generator water levels. Operations stabilized the plant in Mode 3 (hot standby). Decay heat is being removed by the turbine bypass valve. "This condition has no impact to the health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-01-09
53818 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2019-01-08 09:45 | 2019-01-08 15:45 | 2019-01-08 | REACTOR CORE ISOLATION COOLING DECLARED INOPERABLE "On January 8, 2019, at 0945 EST Pilgrim Nuclear Power Station discovered that the Reactor Core Isolation Cooling (RCIC) system failed to meet its surveillance test requirements and was declared inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v), 'event or condition that could have prevented the fulfillment of a safety function: (D), mitigate the consequences of an accident.' "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2019-01-08
53817 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-11-12 13:31 | 2019-01-08 08:12 | 2019-01-08 | INVALID SPECIFIED SYSTEM ACTUATION "On November 12, 2018, at 1331 EST, Unit 1 secondary containment isolated and Standby Gas Treatment (SBGT) systems started on Unit 1 and Unit 2 due to a blown fuse. The blown fuse was caused by a degraded refuel floor radiation monitoring relay, causing the radiation monitor to trip and resulted in an invalid actuation of the Unit 1 Group 10 and Group 11 primary containment isolation valves, all Unit 1 secondary containment isolation valves, and auto start of the Unit 1 and Unit 2 SBGT system. The Unit 1 Fission Product Monitor isolated and tripped and both Unit 1 H202 Analyzers isolated. "This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) since the containment isolation and auto-start of SBGT on both units was not part of a pre-planned sequence and the event resulted in the invalid actuation of general containment isolation valves in more than one system. "All primary and secondary containment isolation valves, with the exception of the 2T41F003A, Refueling Floor Inboard Vent Supply Isolation valve, functioned successfully. The refuel floor inboard vent supply isolation valve failed to travel fully closed on the secondary containment isolation signal and was therefore declared inoperable. The 2T41F003B refuel floor outboard vent supply isolation valve was verified to go fully closed and therefore isolation of that associated penetration line was successful. After assistance from maintenance, the valve was verified to be fully closed. "All SBGT systems functioned successfully. The associated fuse and relay were replaced, and secondary containment was returned to normal service. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2019-01-08
53816 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2019-01-07 | 2019-01-07 12:48 | 2019-01-31 | PART 21 - COMPONENTS PROVIDED AS SAFETY-RELATED SPARE PARTS WITHOUT BEING DEDICATED "AMETEK Solidstate Controls (SCI) is providing this report in accordance with 10CFR Part 21 as notice of a process defect that resulted in components being provided as safety-related spare parts without being dedicated. "PROBLEM DESCRIPTION: Lack of evidence of dedication testing for AMETEK Solidstate Controls Safety-Related Operational Spare Parts Kits provided with SCI equipment "CAUSE: In October 2018, NextEra Seabrook notified SCI of a part number discrepancy with a safety-related fuse that was provided with an operational spare parts kit with an equipment order. After further investigation, it was determined that dedication testing was not performed on the operational spare parts kits provided with the equipment on various jobs in recent years. "Generally, spare parts are ordered separately from equipment and a process is in place to direct the parts to quality for commercial grade dedication testing. In this instance, the parts were ordered as a line item on the sale and the parts in question were selected from inventory without being routed through quality for commercial grade dedication. "PROBLEM YOU COULD SEE: Evidence of dedication testing is not available for operational spare parts kits which were provided with equipment orders, however, there are no functional concerns with the components provided on these orders. The parts would have been selected at the same time as the parts that were installed in the systems. Additionally, for the commercial grade items provided, there is no history of failure during dedication testing performed by AMETEK either in equipment or during bench testing. "ACTION REQUIRED: Aside from printed circuit boards, the parts supplied as operational spare parts will need to be dedicated. AMETEK SCI recommends returning the untested items and will work with [the customer] to arrange returns and retesting. Please contact Mr. Mark Shreve of AMETEK SCI's Client Services group at 1-800-222-9079, 1-614-846-7500 ext. 6332, or mark.shreve@ametek.com." The non-dedicated parts were supplied to Brunswick Steam Electric Plant, Seabrook Station, and North Anna Power Station. In addition, non-dedicated parts were also supplied to the Krsko Nuclear Power Plant in Slovenia and the Maanshan Nuclear Power Plant in Taiwan. * * * UPDATE ON 1/31/19 AT 1304 EST FROM ETHAN SALSBURY TO OSSY FONT * * * The following was received via email from Ametek: "After further evaluation, [Ametek] has determined that additional kits are impacted by this issue, but the same customer list and POs apply. No additional customers are impacted and a corrected notification will be provided to customers that have been previously identified." R1DO (Bickett) and R2DO (Lopez) were notified. Part 21 Reactors Group was notified via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2019-01-07
53815 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2019-01-05 10:40 | 2019-01-05 17:30 | 2019-02-11 | POTENTIAL LOSS OF MSIV SCRAM FUNCTION DURING MAIN STEAM LINE ISOLATION VALVE TESTING "At approximately 1040 EST on January 5, 2019, during evaluation of test results for the 'C' Main Steam Isolation Valve (MSIV), it was determined that closure of three of four Main Steam Lines would not necessarily have resulted in a full scram during testing due to failure of a limit switch (LS-6) associated with MSIV-1C while in the test configuration. This condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v), 'Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition.' "The system was restored from the testing configuration at 1057 EST and the failed trip channel was placed in the tripped condition at 1326 EST thus restoring the design function. There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." * * * RETRACTION AT 1529 EST ON 02/11/19 FROM JOSEPH FRATTASIO TO JEFF HERRERA * * * "The purpose of the notification is to retract ENS Notification 53815 made on 01/05/19 for Pilgrim Nuclear Power Station. The previous notification reported that there was a potential loss of Main Steam Isolation Valve (MSIV) scram function during main steam line isolation valve testing, at the time of discovery, due to failure of a limit switch (LS-6) associated with MSIV-1C while in the test configuration. Subsequent evaluation has demonstrated that the scram function credited in the design basis was not lost. "Specifically, after an Engineering Evaluation, it has been determined that the MSIV position RPS logic was not lost for those functions within the design basis and, as such, was capable of performing its intended safety function." The NRC Resident Inspector has been notified. Notified the R1DO (Cahill). | 31 | 0 | 0 | 31 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2019-01-05
53814 | -1 | WASHINGTON UNIVERSITY IN ST. LOUIS |  |  |  |  | 2019-01-03 16:00 | 2019-01-04 12:15 | 2019-01-14 | MEDICAL EVENT - Y-90 THERASPHERES ADMINISTERED TO THE WRONG LIVER SEGMENT A medical event occurred on 1/3/2019 at Washington University in St. Louis. The patient treatment plan called for 1.06 GBq of Y-90 TheraSpheres to be administered to Segments 6 and 7 of the patient's liver. However, 1.02 GBq of Y-90 TheraSpheres were administered to Segments 5 and 8 of the patient's liver instead. The patient and the referring physician were notified of the event. Washington University in St. Louis has initiated an investigation of the event. * * * RETRACTION ON 1/14/19 AT 1256 EST FROM MAXWELL AMURAO TO THOMAS KENDZIA * * * The following was received via email from the licensee: "As a follow up to the phone call placed today (1/14/19) at 12:56 pm EST, [the licensee radiation safety officer] is writing to retract the report of a event number 53814. The initial report of a suspected medical event with the administration of Y-90 microspheres to a patient was made on 1/4/19 at 12:15 pm EST. After taking the limitations of the imaging software into account, the reviewing team of clinicians have evaluated that the Y-90 microspheres were administered to the correct patient, with the correct dosage and correct route of administration, and in agreement with the Written Directive." Notified R3DO (PELKE) and NMSS vis email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2019-01-14
53813 | 0 | PALISADES | 1 |  |  | [1] CE | 2019-01-03 20:28 | 2019-01-03 23:57 | 2019-01-04 | REACTOR TRIP DUE TO CYCLING OF TURBINE GOVERNOR VALVE "At 2028 [EST] on January 3, 2019, with the reactor at 85% power, the reactor was manually tripped due to cycling of Turbine Governor Valve #4. The trip was uncomplicated with all systems responding normally following the trip. Investigation of the cause of the valve cycling is ongoing. "All full-length control rods inserted fully. Auxiliary Feedwater System actuated as designed in response to low steam generator water levels. Operations stabilized the plant in Mode 3 (hot standby). Decay heat is being removed by atmospheric dump valves. "This condition has no impact to the health and safety of the public. "The licensee notified the NRC Senior Resident Inspector. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2019-01-04
53812 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-11-30 | 2019-01-03 14:05 | 2019-01-03 | AGREEMENT STATE REPORT - INABILITY TO RETRACT RADIOGRAPHY SOURCE The following report was received from the Commonwealth of Pennsylvania via fax: "The licensee reported that on November 30, 2018, while using a Sentinel Model 880 Delta, Serial Number D-11934, containing a 39.2 Curie source of iridium-192, the guide tube had come unbound from the strapping used to hold the collimator and guide tube to the weld being inspected and fell approximately the full length of the guide tube. This left the guide tube hanging at a 90-degree angle from the exposure camera which proved too great to let the source be retracted into a shielded position inside the exposure device and left the source inside the collimator. "The technicians secured the area by adjusting their 2 mR/hr boundaries to an unshielded source distance and immediately contacted their Operations Manager. Once on scene, the Operations Manager utilized various tools to straighten the guide tube enough for the source to be fully retracted into a shielded position. "The device was taken back to the licensee's storage vault in Sugar Grove, PA for inspection and possible repair or disposal by the manufacturer. Direct read dosimetry showed exposures of 18 mR for the Operations Manager, 18 mR for the radiographer and 5 mR for the radiography assistant, thus no overexposures have occurred because of this event. Corrective actions include retraining on suspended exposure procedures and future discussion of this event at monthly staff meetings. The Department will perform a reactive inspection. More information will be provided upon receipt." Pennsylvania Report ID: PA190001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2019-01-11
53811 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2019-01-01 04:54 | 2019-01-01 11:02 | 2019-01-01 | GLAND SEAL EXHAUSTER - AUTOMATIC TRIP FUNCTION INOPERABLE "On January 1, 2019 at approximately 0454 EST, while performing planned maintenance activities on the Feedwater Distributed Control System (FW DCS), it was discovered that the automatic trip instrumentation of the Gland Seal Exhauster (GSE) was inoperable. The automatic GSE trip is assumed in the safety analysis for the Control Rod Drop Accident (CRDA) and is required when Thermal Power is less than or equal to 10%. "The automatic trip function of the GSE was inoperable for 1 minute, 19 seconds. No Control Rod movement occurred while the automatic trip of the GSE was inoperable. There was no adverse impact to public health and safety or to plant employees and there was no radiological release. "This report is being made pursuant to 10CFR50.72(b)(3)(v)(C) and 10CFR50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." | 5 | 0 | 0 | 5 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2019-01-01
53810 | -1 | NATIONAL INST OF STANDARDS & TECH |  |  |  | 20000 KW TEST | 2018-12-29 09:00 | 2018-12-31 14:56 | 2019-01-03 | SECURITY VULNERABILITY - DEVIATION TO SITE SECURITY PLAN Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures were not employed. * * * RETRACTION ON 1/3/19 AT 1128 EST FROM THOMAS NEWTON TO BETHANY CECERE * * * Subsequent investigation has shown that the vulnerability did not exist. This event is being retracted. Notified NPR PM (Yin), NPR SS (Reed), and 73.71 Safeguards Reports E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | SAFEGUARDS REPORTS | [8 empty] | NON EMERGENCY | 0 | MD | NPR |  |  | 73.71(b)(1) |  |  | 1 | 2018-12-31
53809 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-12-29 09:04 | 2018-12-29 10:27 | 2018-12-29 | NOTICE OF UNUSUAL EVENT DUE TO TOXIC GAS AND FIRE At 0904 CST, on December 29, 2018, Cooper declared a Notice of Unusual Event under emergency action level HU 3.1. The emergency declaration was due to a toxic gas asphyxiant as a result of a fire. The fire is contained and the fire brigade continues to extinguishing the fire. Offsite support has not been requested. The licensee notified the NRC Resident Inspector. Additionally, State and Local government agencies were also notified. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 12/29/2018 AT 1655 EST FROM JIM FLORENCE TO JEFFREY WHITED * * * At 1544 CST, on December 29, 2018, Cooper terminated the Notice of Unusual Event under emergency action level HU 3.1. The fire was verified to be extinguished and the flammable material was removed. The plant remained at 100% power for the duration of the event. The licensee issued a press release regarding the event at 1202 CST, on December 29, 2018. The license notified the NRC Resident Inspector. Notified R4DO (Taylor), NRR EO (Groom), IRD MOC (Gott), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-12-29
53808 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-12-26 | 2018-12-26 17:01 | 2018-12-26 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER MECHANISM FAILED CLOSED The following was received from the State of Illinois by email: "The radiation safety officer for Combined Metals of Chicago reported that the shutter on their Data Measurement Corporation Sr-90/100 mCi gauge had failed in the closed position due to a screw that had dislodged from the shutter mechanism. The manufacturer has been called for repair services." IL Item Number: IL180044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2019-01-03
53807 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2018-12-26 | 2018-12-26 14:32 | 2018-12-27 | AGREEMENT STATE REPORT - PORTABLE MOISTURE DENSITY GAUGE STOLEN The following report was received from the Commonwealth of Virginia Department of Health via email: "On December 26, 2018, the licensee reported a stolen Troxler portable moisture/density gauge. The gauge had been stored at a temporary jobsite (the Lorton Construction Landfill in Lorton, Virginia). It was stolen between December 21, and the start of work on December 26 when it was discovered missing. The Radiation Safety Officer (RSO) contacted the Virginia State Police and the Fairfax County Police Department, the local law enforcement agency. Initial searches near the landfill by the licensee were unsuccessful. The gauge contained a cesium-137 source and an americium-241 source. This report will be updated when the RSO provides additional information, including serial numbers of the gauge and sources and the source activities." * * * UPDATE ON 12/27/2018 AT 1052 EST FROM CHARLES COLEMAN TO ANDREW WAUGH * * * The following update was received from the Commonwealth of Virginia Department of Health via email: "The licensee identified the stolen gauge as a Troxler Model 3430, serial number 33748. It contained a cesium-137 source, serial number 750-9405, with a nominal activity of 8 milliCuries (4/19/2002) and an americium-241:beryllium source, serial number 47-29401, with a nominal activity of 40 milliCuries (8/12/1999). "There has been no media attention. The licensee may issue a press release regarding the theft." Notified R1DO (Arner), NMSS Events Notification, and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2019-01-03
53806 | 0 | MOBRIDGE REGIONAL HOSPITAL |  |  |  |  | 2018-12-24 09:30 | 2018-12-26 11:38 | 2018-12-26 | SPILL OF TC-99M VIAL IN HOT LAB "[At 0930 MST on 12/24/18, a] Technologist went to screw the bottom of the pig on and had difficulty getting the bottom screwed on. The vial [containing approximately 272 mCi of Tc-99m] then slipped from the pig and the technologist's hands and dropped to the floor and broke. The technologist was wearing [Personal Protective Equipment] PPE in the form of gloves. Her shoes, clothing were removed and placed in a sealed bag to decay in the hot waste area. Initial reading from the sealed bag was 0.8 mR/hr. PPE was worn and the spill was covered with absorbent material. To prevent the spread of contamination movement of staff was limited. A witness was not contaminated during the incident as she was more than 10 feet from the hot lab and her personal survey results were 0.05 mR/hr which is equivalent to the background of the room. The contaminated personnel's skin readings post decon were 0.1 mR/hr at skin level on her leg. "The spill was sprayed with Radiacwash and the contaminated absorbent material was placed in a sealed bag, labeled with date and radioactivity and placed in the hot waste storage area to decay. The spill was contained within the nuclear medicine hot lab, a sign was posted to close the room and secure the area to prevent entry. Final survey and wipe tests were completed on 12/26/2018 at 1100 [MST]. "The [Radiation Safety Officer] RSO was notified on 12/24/2018 at 0952 [MST]. The RSO talked to the Avera St. Luke's Director of Nuclear Medicine to ensure we are following the correct protocol. The RSO was notified on 12/26/2018 of the final survey and final wipe tests performed, and permission was given to return to work in the area." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2019-01-03
53805 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2018-12-22 | 2018-12-23 20:22 | 2018-12-23 | SURVEILLANCE NOT DONE DUE TO INADEQUATE PROCEDURE The following was received via email: "[The licensee notified] the NRC of a reportable occurrence identified on December 22, 2018 due to violation of an LCO [limiting condition for operation]. While performing testing and surveillance following control rod maintenance, the Reactor Supervisor identified an interlock check was not being completed due to an inadequate procedure. The inadequacy was identified as part of additional documentation checks that are being implemented at the facility. "Per Technical Specification 3.4.3 - Table 2, the CONTROL ROD (STANDARD) position interlock must be operable in PULSE MODE. The interlock prevents withdrawal of the standard control rods while in PULSE MODE. The surveillance to ensure the interlock is operable is required on a SEMIANNUAL frequency as specified in Technical Specifications 4.4.2. As currently written, the procedure used to satisfy this surveillance does not direct the operator to enter PULSE MODE to check the interlock. Instead, the procedure activated a similarly named interlock (Pulse Power) that indirectly prevents withdrawal of the standard control rods by engaging the source interlock; however it is not specified to enter PULSE MODE in the procedure steps. The CONTROL ROD (STANDARD) position interlock was subsequently tested to be operable in that it functioned properly during the test and no operational history would suggest it was non-functioning otherwise. "Based on the surveillance not being performed in PULSE MODE, the interlock was technically not operable during pulsing operations. The reactor is and will remain shutdown until a review by the Reactor Safeguards Committee of corrective actions in accordance with Technical Specifications. "A written report will be submitted within ten days summarizing the reportable occurrence." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | KS | NPR | [5 empty] | 0 | 2018-12-23
53804 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-12-19 | 2018-12-21 15:55 | 2019-01-17 | AGREEMENT STATE REPORT - RADIOACTIVE SOURCE FAILS LEAK TEST The following report was received via e-mail: "A routine leak test at the Swedish Cancer Institute found a leaking Cs-137 e-vial source in the Physics Lab. The initial leak test was taken 12/19/2018 and analyzed on 12/20/2018. It revealed an activity of approximately 10 nanoCuries, and additional confirmation tests found contamination above the regulatory threshold for a leaking source. "The source was immediately removed from service, contained within multiple non-permeable barriers, and placed into a larger pig while it is being held for disposal. Surveys of the original storage pig and the hot lab where the source was utilized found no removable contamination and there was no personnel contamination detected. "The RSO [Radiation Safety Officer] was notified of the positive results the morning of 12/21/2018 and provided notification to DOH [Washington State Department of Health] at 1114 PST on 12/21/2018." * * * UPDATE ON 01/17/2019 AT 1201 EST FROM ANDREW HALLORAN TO JEFFREY WHITED * * * The following report was received via e-mail: "A leaking sealed source was discovered at The Swedish Cancer Institute during periodic leak tests performed by the health physics staff. The source (MED3550 Gamma Reference Standard, SN 11345, Cs-137, initial activity 209.6 micro-Ci, reference date 8/1/2001) was used in the A Level Physics Lab as part of routine radiation oncology operations. The source was initially received by Swedish 12/6/2007. "The sample was collected on 12/19/2018 using an alcohol wipe, and analyzed on 12/20/2018 using a Ludlum 261 single channel analyzer coupled with a NaI well detector. The system was set to detect the 662 keV photon energy for Cs-137, with a calculated efficiency of 11.71 percent. The result of the wipe test analysis was a removable activity of 9.92 Nano-Ci, above the 5 Nano-Ci threshold for a leaking source. "After the RSO was notified of the positive result on 12/21/2018, the source was immediately removed from service, contained within multiple non-permeable barriers, and placed into a lead pig. The pig is currently being stored in the Radiation Safety Office Lab awaiting disposal. Wipes of the A Level Physics Lab source storage cabinet and all surfaces of the pig used to house the source when it was in service yielded no detectable removable contamination. "After reviewing the final report of the licensee, this event is now closed as of 1/3/2018. DOH will verify that the source has been disposed of during the next routine inspection of the licensee." Washington Event Report ID: WA-18-031 Notified R4DO (Drake) and NMSS Event Notification (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-12-31
53803 | 0 | IRIS NDT |  |  |  |  | 2018-02-24 | 2018-12-21 14:46 | 2018-12-21 | RADIOGRAPHY CAMERA GUIDE TUBE DISCONNECTED DURING USE The following is a synopsis of the report received via email: The quick connect fitting on the guide tube came apart when the source was being cranked out. When the source was cranked out beyond where the end of the guide tube was supposed to be the technicians stopped and tried to crank the source back into the camera. The source rod became stuck because the control cable had become entangled. The RSO (Radiation Safety Officer) was later able to disconnect the source's pigtail, unkink the control cable, reconnect the guide tube, and reconnect the control cable to retrieve the source. The maximum doses received were 114 mRem whole body and 260 mRem to the right hand. Camera: model SPEC-300 with model G-70 source assembly Source: 88 Ci Co-60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-12-31
53802 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-12-13 | 2018-12-21 10:05 | 2019-02-07 | AGREEMENT STATE REPORT - REPORT OF LOST I-125 SEED DURING MEDICAL PROCEDURE "Nebraska Department of Health and Human Services, Office of Radiological Health was notified on December 21, 2018 at 8:50 am CST by the Radiation Safety Officer (RSO) from Regional West Medical Center (Nebraska license 21-01-03) that one I-125 seed is lost and still missing at this time. The I-125 seed was part of a manual brachytherapy procedure that involved one hundred permanently implanted I-125 seeds in the patient's prostate. The procedure occurred in a surgery suite at approximately 9 am MST, the patient was then transported to a recovery room and then to a CT suite to confirm the placement of the seeds at approximately 12:19 pm MST. During the review of the CT, the licensee observed that only ninety nine seeds were implanted. The licensee then conducted a search for the missing I-125 seed. "During the search of the missing I-125 seed on December 13, 2018, licensee staff surveyed the surgical suite and recovery room of the patient. The licensee staff were not able to find the missing seed. During the survey, licensee staff also questioned the nursing staff and it was noted that a nurse emptied a catheter bag into a toilet shortly following the completion of surgery. Licensee staff believe that the missing I-125 seed may have been flushed and disposed in the sanitary sewage system. "The missing I-125 seed was a Bard Medical product, serial number 7815544SO, containing 283 uCi and was one of many seeds preloaded into a needle to be injected into the patient. On December 13, 2018 at 9:30 am CST, the RSO was contacted to report the search results in the adjacent hallways, the CT suite, and if possible, any sewage holding areas. The RSO has dispatched staff to conduct a new search of all areas and transport beds that the patient was in and in contact areas. The RSO expects this to be completed later in the day of 12/21/2018. "The State is awaiting the results of this new survey and will be following up with the licensee and US NRC." Nebraska Report: NE-18-0009 * * * UPDATE AT 1721 EST ON 02/07/2019 FROM LARRY HARISIS TO JEFF HERRERA * * * The following update was received from the Nebraska Department of Health and Human Services (DHHS) via email: "On 01/16/2019, Nebraska DHHS Office of Radiological Health staff arrived at the licensee's facility. Discussions, reenactments, radiological surveys, and presentations were performed and given to assess if the I-125 seed was disposed of in the sanitary system. A review of the licensee's training of oncology staff and nursing personnel, policies and procedures for specific seed implantation for oncology and nursing staff, and interviews of all involved personnel were completed. "It was determined that all 100 I-125 seeds were implanted into the patient as ordered and the bladder was verified as emptied by a cystoscope after removing an inflated balloon to prevent seeds from entering the bladder. After the inflatable balloon device was removed from the patient, a seed near the urethra was dislodged and entered the urethra then into a urinary catheter bag. When the oncology personnel arrived at the patient's recovery room, they noticed that the urinary catheter bag was abnormally low. Oncology personnel found that a nurse in the recovery room emptied the urinary catheter bag without approval from Oncology personnel, inadvertently disposing of the seed in a sink in the recovery room. Oncology personnel surveyed the surgical suite, recovery room, and sink with no results above background. A review of the policies and procedures of radioactive seed implantation with the nursing staff was also completed. "The licensee's implementation of corrective measures to prevent a reoccurrence will be reviewed on the next inspection." Notified the R4DO (Werner) and NMSS Events (via email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-12-31
53801 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-12-20 | 2018-12-21 00:02 | 2018-12-21 | CONTAINMENT AIR RETURN FAN SYSTEM INOPERABLE "At 1642 Eastern Standard Time (EST) on December 20, 2018, it was determined that both trains of Containment Air Return Fan (CARF) were simultaneously INOPERABLE from 0817 (EST) to 1129 (EST) on November 20, 2018. This condition is not bounded by existing design and licensing documents; however, it poses no impact to the health and safety of the public or plant personnel. Therefore, this event is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(ii)(B). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-12-21
53800 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2018-12-18 | 2018-12-20 16:32 | 2018-12-20 | AGREEMENT STATE REPORT - REPORT OF LOST METAL DISC CONTAINING RA-226 FOUND WITHIN SCRAP LOAD The following was received from the State of Massachusetts via e-mail: "On December 18, 2018, the Massachusetts Radiation Control Program (MARCP) was informed by Schnitzer Steel Metal Recycling Facility that a scrap metal load shipment from Minichiello Brothers Scrap It (431 Second Street, Everett, MA 02149) set off the radiation monitor alarms. The vehicle returned back to Minichiello Brothers Scrap It for radiation consultant follow-up survey via MARCP Department of Transportation Special Scrap Permit MA-MA-18-4. On December 20, 2018, this material was identified, removed and segregated from this scrap load by the radiation consultant. The radioactive material found is an abandoned metal disc (three inch in diameter) containing Radium-226. The radiation consultant's direct radiation dose rate reading was 1.2 mR/hour at 30 cm from the metal disc. The Radium-226 activity was estimated to be approximately 5.55 MBq (150 uCi) based on the dose rate taken. This material is being held in a secured location at the Minichiello Brothers Scrap It Facility awaiting appropriate disposal. "This activity meets the immediate event report requirements where report of lost or abandoned RAM [Radioactive Material] is found to be greater than 1,000 times the quantities specified in 10 CFR 20 Appendix C or MA equivalent 105 CMR 120.297 Appendix C. (The 1000 times reportable quantity for Radium-226 is 100 uCi.) "The MARCP considers this event to be open until proper disposal of this metal disc is confirmed." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2018-12-28
53799 | 0 | FROEHLING AND ROBERTSON |  |  |  |  | 2017-02-27 | 2018-12-20 14:12 | 2018-12-20 | DAMAGED MOISTURE DENSITY GAUGE A technician did not secure the Troxler Moisture Density Gauge in his truck before moving from one job site to the next. The tailgate was open and the gauge fell from the truck onto the dirt road. Someone subsequently found the gauge and returned it to the technician approximately 20 minutes after losing the gauge. The sources remained in the stored position. Subsequent surveys and wipe tests determined that no damage had occurred to the sources however the case itself was cracked. The gauge was sent back to the manufacturer and the case was replaced. Troxler model 3430 (S/N 23714) Sources: Cs-137 at 8 mCi and Am-241 at 40 mCi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-12-28
53798 | 0 | SAN ONOFRE |  |  |  | ISFSI | 2018-12-19 | 2018-12-20 13:56 | 2018-12-20 | SPENT FUEL TRANSFER VEHICLE OUTSIDE SEISMIC ANALYSIS LIMITS "As part of the reviews following the August 3rd 2018 canister downloading event (EN#53605), SCE has identified events where the HI-PORT may have been operated outside the analytical assumptions of the seismic analysis while transporting a loaded canister in the HI-TRAC. SCE has decided to conservatively report this issue. "The HI-PORT is subject to requirements in the Certificate of Compliance that result in seismic restrictions on center of gravity and proximity to structures that could adversely affect the function of the HI-PORT along the haul route. SCE has concluded that during previous movements of loaded spent fuel canisters during 2018, the HI-PORT likely exceeded these procedural and analytical limits in some cases. "Additional analysis is underway that may conclude that damage to the HI-PORT would not occur under these conditions. Nevertheless, this situation is being reported in accordance with 10CFR72.75(d)(1) for an important to safety component that was disabled or failed to function. There was no seismic event that resulted in damage to the HI-PORT during the fuel transfer campaign. All 29 spent fuel canisters are currently in safe storage within the ISFSI. "NRC Region IV will be notified as SONGS does not have a NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 72.75(d)(1) |  |  |  | 0 | 2018-12-20
53797 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-12-19 10:49 | 2018-12-20 10:24 | 2019-01-30 | AGREEMENT STATE REPORT - FIXED GAUGE STUCK SHUTTER The following was received from the State of Texas via email: "On December 19, 2018 at 10:49 am, the licensee's radiation safety officer reported a stuck shutter on a fixed gauge, found during routine maintenance. Gauge is in the open operating position; no employee or public exposures are anticipated. Gauge is attached to a vessel located several feet off the ground. Device information: source SN 8423CN, model SH-F1B, Cs-137, 100 mCi. A service company has been called to repair the gauge. Update will be sent in accordance with SA300 guidelines." Texas Incident #: I-9646 * * * UPDATE ON 01/30/2019 AT 1135 EST FROM MATTHEW KENNINGTON TO JEFFREY WHITED * * * The following update was received from the State of Texas via email: "On January 29, 2019, the licensee's Radiation Safety Officer (RSO) reported to the [Texas Department of State Health Services] that after further investigation two additional gauges were found on December 19, 2018, with shutters stuck in the open position. Open is the normal operating position. The gauges are Ohmart Vega model SH-F1B serial number 8431CN and 8443CN, both containing 100 mCi of cesium (Cs)-137. The RSO stated he discovered the additional shutter failures after reviewing reports received on January 21, 2019. The gauges are located on towers, not easily accessible, and are unlikely to cause unintended exposure. The RSO has contacted a service company and is anticipating the repairs completed to all three gauges in the next week. The RSO intends to apply grease to O-rings to prevent moisture from entering and fouling the shutter mechanism." Notified R4DO (Werner) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-12-28
53796 | 0 | WATERFORD | 3 |  |  | [3] CE | 2018-12-19 | 2018-12-20 05:32 | 2018-12-20 | CONTROL ROOM ENVELOPE INOPERABLE "On December 19, 2018, at 2322 CST, the shift operating crew declared the control room envelope inoperable in accordance with Technical Specification (TS) 3.7.6.1 due to valve HVC-102 exceeding its maximum allowed closed stroke time of 2.0 seconds during performing of surveillance procedure OP-903-119. Actual closed stroke time was 2.1 seconds. Valve HVC-102 is part of the control room envelope. TS 3.7.6.1 requires that two control room emergency air filtration trains shall be OPERABLE. Operations entered TS 3.7.6.1 action b, which requires that with one or more control room emergency air filtration trains inoperable due to inoperable control room envelope boundary in MODES 1, 2, 3, or 4, then: 1. immediately initiate action to implement mitigating actions; 2. within 24 hours, verify mitigating actions ensure control room envelope occupant exposures to radiological, chemical, and smoke hazards will not exceed limits; and 3. within 90 days, restore the control room envelope boundary to OPERABLE status. Actions b.1 and b.2 were completed by placing the control room ventilation system in isolate mode at 2355. This event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(D), 'event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to (D) mitigate the consequences of an accident,' due to the control room envelope being inoperable. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-12-20
53795 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-12-19 | 2018-12-19 17:28 | 2018-12-20 | AGREEMENT STATE REPORT- CONTAMINATED PACKAGE The following was received from the State of Colorado via email: "Event description: Thermo MF Physics, LLC received 2 packages of radioactive materials, both containing approximately 700 Ci of H-3. When performing contamination surveys as part of the package receipt, wipe tests indicated approximately 600 dpm/cm2 of removable H-3. A third package that was received at the same time, which did not contain any radioactive materials, also exhibited removable contamination. Thermo MF Physics, LLC has contacted the final delivery carrier and made them aware of the situation. Thermo MF Physics, LLC is continuing to count removable contamination samples to determine the extent of the contamination event." Colorado Event Report ID No.: CO180033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-12-27
53794 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-12-15 | 2018-12-19 11:10 | 2018-12-19 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following was received from the State of Colorado via email: "[Colorado Department of Public Health and Environment] CDPHE became aware of a misadministration on the evening of December 18th, 2018; the event was discovered by the licensee on the morning of December 18th, 2018. The event occurred over three consecutive days, December 15th, 16th, and 17th, 2018. "Description of the events: The licensee reported that strontium break through occurred on a Braco (Rb-82) generator resulting in levels of Sr-82/Sr-85 exceeding manufacture specified limits. The licensee failed to identify the strontium breakthrough and the doses were subsequently used in patient procedures, eight (8) patients were affected. "The licensee has no more information at this time and has been instructed to notify the department as soon as patient dose information becomes available. CDPHE is awaiting a full report by the licensee." Colorado Event Report ID No.: CO180032 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-12-27
53793 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2018-12-18 | 2018-12-18 15:40 | 2018-12-18 | AUTOMATIC REACTOR TRIP - LOSS OF NON-VITAL BUS "On December 18, 2018 at 1126 CST, Arkansas Nuclear One, Unit 1 (ANO-1) reactor automatically tripped due to a loss of the A-1, non-vital 4160V bus. All control rods fully inserted. Loss of the A-1 bus resulted in de-energizing A-3 vital 4160V bus. Emergency Diesel Generator #1, K-4A, started automatically and is currently powering A-3 vital bus. Non-vital buses A-2, H-1, and H-2 and vital bus A-4 transferred power automatically to the Startup Transformer #1. Off-site power remains energized and available for ANO-1. The reason for loss of A-1 bus is unknown at this time. Currently, ANO-1 has stabilized in Mode 3, Hot Standby." Decay heat is being removed by the main condenser using the turbine bypass valves. The loss of the A-1, non-vital bus, is under investigation. The licensee has notified the NRC Resident Inspector and the state. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-12-18
53792 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2018-12-17 | 2018-12-18 11:51 | 2018-12-18 | AGREEMENT STATE REPORT - DAMAGED TROXLER The following was received from the state of Kansas via email: "Yesterday the Kansas Radiation Control Program was notified by a licensee, Kruger Technology Inc (dba KTI) 22-B659-01, of a Troxler gauge which was hit and damaged at a construction site in Edgerton ,KS. No one was injured. The source was in the shielded position. Initial surveys indicate [that] the shielding is intact. The rod was slightly bent, fortunately the device still fit in the transport case. The licensee reported by phone that the device was hit [at] approximately 1530 CST. The initial report was made to the State at 1615 CST. The RSO was on scene within an hour of the incident. The incident occurred on a new road construction site. It was the end of the day and few workers were present, no public traffic is permitted on the road. The site is an industrial complex in a rural area and there is no public access to the site. "Currently the device is secured in the licensee's storage room. An inspector was dispatched this morning to conduct a reactive inspection and verify survey results. More information will be provided to the NRC as it is available, including the device make and model, serial number, survey meter information, verified survey results, more information on how the incident occurred, enforcement actions taken if applicable, and more precise location information." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2018-12-26
53791 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2018-12-12 | 2018-12-13 16:12 | 2018-12-13 | AGREEMENT STATE REPORT - RADIOGRAPHY GUIDE TUBE KINKED WITH SOURCE EXPOSED "Braun Intertec Corporation reported an event of the inability to retract a 1.44 TBq (39 Ci) Ir-192 sealed source (QSA Global, Inc. Model A424-9, SN 67476) which occurred at a temporary job site near Belfield, ND at approximately 4:02 pm CST on December 12, 2018. While performing radiography using a QSA Global, Inc. Model 880 Delta (SN D9541) exposure device on a pipe section resting on a stand, the pipe fell from the stand and kinked the guide tube. The radiography crew was unable to retract the source and immediately expanded the public dose boundary to an actual 2 mR/hr distance and maintained continuous surveillance and contacted their RSO for guidance. The RSO arrived on site the same day at approximately 8:45 pm CST and completed the source retrieval at approximately 9:45 pm CST. The sealed source was successfully retrieved into the exposure device. The maximum exposure readings from the direct reading exposure devices of the radiography crew and retrieval personnel was 3 mR. The crank assembly and guide tube were taken out of service. Visual inspection noted no defects to the pigtail assembly." North Dakota Event: 180003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2018-12-21
53790 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-12-13 | 2018-12-13 15:03 | 2018-12-22 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA LOST BY COMMERCIAL CARRIER The following report was received from the state of Florida via e-mail: "Received a call from Versa Integrity Group to report a missing Ir-192 radiography camera. The device was shipped from Sanford, Florida via [commercial carrier] on 11-29-18 in route to Corpus Christi, Texas, but never arrived. The last location that [the commercial carrier] can confirm the location of the package was Memphis, Tennessee. (Source information - model: A424-9, S/N: 62109G)." The camera had a 330 GBq Ir-192 source. The licensee contacted the commercial carrier on 12-10-18, to inquiry about the shipment and was told it was delayed. The licensee recontacted the commercial carrier on 12-13-18 and was told the package could not be located. Florida Incident: FL18-153 * * * UPDATE FROM ART TUCKER TO HOWIE CROUCH AT 1556 EST ON 12/13/18 * * * The state of Texas also reported the same event since their licensee was the intended recipient. The Texas Department of State Health Services will be contacting the state of Florida about this event. Texas Incident: 9645 Notified R4DO (Taylor) and NMSS Events Notification group (email). * * * UPDATE AT 1345 EST ON 12/21/2018 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received via fax: "At 12:39 PM [CST] on December 21, 2018, the licensee contacted the Agency [Texas Department of State Health Services] and stated they had received an email from [the commercial carrier] stating the exposure device would be delivered to the facility in Corpus Christi by 1645 [CST] hours today." Texas Incident: I-9645 Notified the R1DO (Jackson), R4DO (Alexander) and NMSS (via e-mail). * * * UPDATE AT 1703 EST ON 12/21/2018 FROM ART TUCKER TO TOM KENDZIA * * * The following information was received via fax: "The licensee contacted the Agency [Texas Department of State Health Services] at 1550 hours and reported they had received the exposure device. The licensee stated they would provide additional information after they completed their investigation. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: I-9645 Notified the R1DO (Jackson), R4DO (Alexander) and NMSS (via e-mail). THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-12-21
53789 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-12-12 | 2018-12-13 14:37 | 2018-12-13 | CONTRACTOR SUPERVISOR SUBVERTS A FOLLOW-UP FITNESS FOR DUTY TEST "At 1700 EST on December 12, 2018, a contractor supervisor violated the licensee's Fitness-for-Duty (FFD) program by subverting a follow-up Fitness for Duty Test. The contractor's site access has been terminated. The NRC Resident Inspector was notified." No work was performed on safety related equipment. The licensee has made a PADs entry. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-12-13
53788 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-12-12 | 2018-12-12 17:29 | 2018-12-14 | MANUAL REACTOR SCRAM DUE TO FAILED OPEN TURBINE BYPASS VALVE "At 1351 CST, the reactor was manually shutdown due to 'A' Turbine Bypass Valve opening. The Main Steam Line Isolation Valves were manually closed to facilitate reactor pressure control. Reactor level is being maintained through the use of Reactor Core Isolation Cooling System, Control Rod Drive System, and High Pressure Core Spray System. High Pressure Core Spray System was manually started to initially support reactor water level control. Reactor Pressure is being controlled through the use of the Safety Relief Valves and the Reactor Core Isolation Cooling System. The plant is stable in MODE 3. "The cause of the 'A' Turbine Bypass Valve opening is under investigation at this time. "The NRC Resident Inspector has been notified." * * * UPDATE ON 12/14/18 AT 1140 EST FROM GERRY ELLIS TO TOM KENDZIA * * * "This is an update to EN # 53788 to correct an error on the event classification block of the form. The original notification did not have the block for 8 hour notification for Specified System Actuation checked. The actuation of Reactor Core Isolation Cooling System was discussed in original notification." The licensee notified the NRC Resident Inspector. Notified R4DO (Taylor). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2018-12-12
53787 | 0 | NH DEPT OF HEALTH & HUMAN SERVICES |  |  |  |  | 2018-12-11 | 2018-12-11 16:18 | 2018-12-11 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the State of New Hampshire via email: "On December 11, 2018, the NH Radiological Health Section (Agency) was notified by the Radiation Safety Officer at Lakes Region General Hospital of the administration of an incorrect radiopharmaceutical. On this date a patient received an injection of 7.7 milliCuries (mCi) of technicium-99m Sestamibi rather than 7.7 mCi technicium-99m Choletec. The consequence is a dose to an unintended organ. "The patient, radiologist, and authorized providers were informed. No health effects are anticipated. "The RSO will conduct a root cause analysis and present a written report of the findings and corrective actions to the Agency within 15 days." New Hampshire Event Report ID No.: NH 18-005 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NH | OTH | AGR |  |  |  |  | 0 | 2018-12-19
53786 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-10-15 | 2018-12-11 15:09 | 2018-12-11 | INVALID AUXILIARY FEEDWATER PUMP ACTUATION "This 60-day telephone notification is being made in accordance with the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A). "The successful, complete train actuation of the 22 Auxiliary Feedwater Pump was initiated by an invalid signal during testing. "The Auxiliary Feedwater System was not impacted in its ability to perform its function. "There were no safety consequences or impacts to the health and safety of the public as a result of this event. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-12-11
53785 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-12-07 | 2018-12-10 18:12 | 2018-12-10 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following information was received from the State of Louisiana via email: "[On 12/7/2018, the licensee's RSO reported to the Louisiana Department of Environmental Quality (LDEQ)] that his personnel monitoring provider had informed him of excessive exposures to a Nuclear Medicine Technologist's (NMT) monitors. The monitors had received a whole-body exposure of 6,358 mRem and an extremity exposure 29,245 mRem. The monitoring period was 9/20/20018 to 10/19/2018. "[The RSO's] in-house investigation revealed he had a 'Reportable NMED Event'. The event occurred under the Ochsner Clinic Foundation Broad Scope Medical License (OCFBS), LA-0002-L01. The event involves two monitors, a whole-body and an extremity monitor. The monitoring company could not determine the type of exposure using their normal exposure filters. "The RSO for this licensee did his own investigation after he was notified of the exposures on 12/5/2018. The RSO interviewed the NMT, reviewed area survey records, and did a bioassay of the NMT. The isotopes in use at the facility are Tc-99, Lu-177, and a Ga-68 generator. The NMT attaches both monitors together for storage after their use. The NMT did admit to not being in gloves at all times when handling radioactive isotopes. The RSO called in the possible NMED event [to the LDEQ] when he finished his investigation on 12/7/2018. "This incident is being reported as a (potential) real or threatened excessive exposure NMED Event on 12/10/2018. The actual exposure determination will be up-dated when LDEQ concludes its investigation. "LDEQ considers this incident still open and subject to investigation and corrective action implementation." Event Report ID No.: LA-180020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-12-18
53784 | -1 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-12-07 | 2018-12-08 06:12 | 2018-12-20 | INOPERABLE CONTROL ROOM ENVELOPE "Braidwood Station was performing Control Room Envelope Testing. During testing the Station identified a failed acceptance criteria. The Control Room Envelope is a single train system and could constitute a Loss of Safety Function. If a single train system is inoperable per Technical Specifications (TS), it is Reportable as a Loss of Safety Function per 10 CFR 50.72(b)(3)(v) regardless of the system's continued ability to meet the accident analysis requirements. "Both Units remain Mode 1, 100% power." The licensee will be notifying the NRC Resident Inspector. The acceptance criteria that failed was to maintain the control room pressure above the miscellaneous electrical equipment room pressure. The station has realigned ventilation to normal, and has entered TS Limited Condition for Operation (LCO) 3.7.10 condition B, which requires the station to restore to operable the control room envelope within 90 days or shutdown the plant. The station has also initiated contingency actions to verify SCBA (self contained breathing apparatus) are available and control room personnel are qualified to use SCBA. * * * RETRACTION ON 12/20/18 AT 1714 EST FROM ANTHONY SIEBERT TO JEFFREY WHITED * * * "On Wednesday, December 19, 2018, Braidwood Station concluded that the ENS notification 53784 could be retracted. It has been determined that the issue was not with the Control Room Envelope structure. Troubleshooting identified that the Unit 1 Upper Cable Spreading Room Area Supply Flow Control (OVC035Y) damper which supplies the Train A control room ventilation equipment room with air flow was not opening enough to supply the required flow. The subject duct work is shared by both A-train and B-train, and the flow through OVC035Y is controlled by a two-position actuator. The damper is less open when A-train is in operation (actuator energized) and more open when B-train is in operation (actuator de-energized). The only adjustments performed were to the actuator energized stroke limits which only affect the A train and thus a single train failure which could affect the safety function of both trains did not exist. "Further calculations of unfiltered air inleakage into the Control Room Envelope (CRE) under a slightly negative differential pressure condition resulted in a calculated in leakage to the CRE of less than the maximum allowable unfiltered air inleakage for a radiological event of 436 scfm. The unfiltered air inleakage into the CRE assumed in the licensing basis analyses of Design Basis Accident consequences was never exceeded. Thus, TS Surveillance Requirement 3.7.10.4 continued to be met and entry into TS 3.7.10 Condition B was not required. "The licensee has notified the NRC Resident Inspector." Notified the R3DO (Stone). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2018-12-08
53783 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-12-03 | 2018-12-07 16:35 | 2018-12-07 | AGREEMENT STATE REPORT - SOURCE ABANDONMENT THROUGH BANKRUPTCY The following was received from the Louisiana Radiation Protection Department (LDEQ/ERSD/Radiation Section) via e-mail: "On or about December 3, 2018, [an individual] contacted KLS Physics to inform them he had acquired some sealed sources (check sources) in a bankruptcy liquidation of assets. KLS Physics had provided physics support to HVA [Heart & Vascular Associates, PC] for their Radioactive Materials Program. KLS Physics instructed [the individual] to contact LDEQ/ERSD/Radiation Section to determine how to proceed correcting/solving the situation. "LDEQ staff received [the individual's] notification on December 3, 2018. The inventory performed by KLS Physics on December 4, 2018, indicated the five (5) sources are check sources of Cs-137 and Co-57. The activities range from 0.02 microCuries Co-57 to 176 microCuries of Co-57. At this time, the Department has taken possession of three of the sources. "LDEQ has assigned this NMED Incident to an investigator. This is a preliminary investigation report. Information will be updated when available. "The five sources were abandoned by [the licensee], who is the registered owner of Heart and Vascular Associates, PC. [The licensee's] equipment was sold during a bankruptcy liquidation to pay expenses. The licensed source possession and Regulatory Reporting requirements are [the licensee's] responsibility. "LDEQ staff received [the individual's] notification on December 3,2018. He reported the acquisition of the sources to KLS Physics Services. The name was on documents included in the box of equipment. KLS in turn had him contact the LDEQ's Radiation Section. "The Department dispatched an inspector to [the individual's] residence to assess the situation. [The individual] only had three of the five sources in question. All three were is their lead pigs and surface readings were minimal. Staff personnel is still attempting to contact [the licensee] about the remaining two sources." The LDEQ reported that the sources that were found had the following activities: 69.35 microCuries of Cs-137, 57.98 microCuries of Cs-137, and 0.01 microCuries of Co-57. The sources that are still missing had the following activities: 176 microCuries of Co-57 and 0.62 microCuries of Cs-137. Louisiana Event Report ID No.: LA-180019 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-12-17
53782 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2018-11-16 | 2018-12-07 12:34 | 2018-12-07 | LOSS OF SEALED SOURCE AT VA MEDICAL CENTER The following is a summary of information provided by the Department of Veterans Affairs via e-mail: "The source is believed to have been mistakenly discarded with non-radioactive trash on Friday, November 16, 2018. The loss was discovered on Monday November 19, 2018. It is believed that the source is buried deep in a commercial landfill in Johnson City, TN. A radiation survey performed at the landfill did not locate the source. "The source contains approximately 15 millicuries of cobalt-57. "The US Department of Veterans Affairs hold NRC Master Materials License No. 03-23853-01VA. The source was lost at the VA Medical Center [located in] Johnson City, TN 37604. This facility holds VA radioactive materials permit number 41-19792-01. "We expect that doses to personnel from the lost source are and will be much less than the NRC's dose limit for members of the public. "The State of Tennessee has been notified of the lost source. Also, the VA's NRC Liaison (Parker) of NRC Region III, has also been notified." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-12-17
53781 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-11-01 | 2018-12-07 12:29 | 2018-12-07 | AGREEMENT STATE REPORT - LOSS OF 2 GENERALLY LICENSED STATIC ELIMINATORS The following was received from the Illinois Emergency Management Agency via e-mail: "A graduate student affiliated with the University of Illinois reported the loss of two generally licensed NRD Model P-2042 static eliminators (5 mCi/Po-210, Serial Numbers A2KX694 and A2KX695). They were shipped on March 3, 2017, whereupon he proceeded to perform small neutron experiments. The devices were then put into a storage building and subsequently lost during a move to a new location sometime in November 2017. He believes the devices went to a landfill. At the time of loss they would have decayed to around 1.5 mCi each. By today's date, they would have decayed to approximately 200 uCi each. "In August of 2018, the general licensee reported it to NRD, Inc., and they referred him to the Illinois Emergency Management Agency. A report was received on the matter on November 19, 2018. The investigation is ongoing." State of Illinois Item Number IL180043 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-12-17
53780 | 0 | FRAMATOME INC |  |  |  |  | 2018-10-09 | 2018-12-06 16:00 | 2018-12-06 | PART-21 - RHR SHAFT SEAL O-RING SHEARED DUE TO MANUFACTURER DEFECT The following is a synopsis from the Part 21 report received via e-mail: During an outage at Prairie Island Nuclear Generating Plant, the licensee replaced the mechanical shaft seal on the 11 Residual Heat Removal (RHR) pump. During subsequent post maintenance testing, it was found that there was significant seal leakage on the pump. An evaluation was completed on December 4, 2018, which determined that it was a substantial safety hazard. The licensee has shipped back six seals to Framatome to be tested. It was determined that the cause of the failure was improper O-ring installation by the manufacturer. Discussions with Framatome indicate that only Prairie Island Nuclear Generating Plant is effected by this defect, but investigations are still ongoing. Affected Plant: Region 3: Prairie Island Nuclear Generating Plant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-12-06
53779 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2018-12-05 | 2018-12-05 20:07 | 2018-12-05 | MANUAL REACTOR TRIP ON LOSS OF MAIN CONDENSER VACUUM "At 1539 [CST] December 5, 2018, with Unit 1 at 100 percent power, the reactor was manually tripped due to degrading condenser vacuum. The trip was uncomplicated with all systems responding normally, post-trip. An actuation of the auxiliary feedwater system occurred during the manual trip. The auxiliary feedwater system automatically started as designed when the valid actuation signal was received. Operations stabilized the plant in mode 3 [hot standby]. Decay heat is being removed by atmospheric dump valves. "Unit 2 is not affected. "This event is being reported pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." The loss of condenser vacuum resulted because one of two circulating water pumps was running and its discharge valve shut. The cause for the valve shutting is under investigation. There is no primary to secondary leakage. The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-12-05
53778 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2018-12-05 | 2018-12-05 17:06 | 2018-12-05 | THREE MINUTE LOSS OF SECONDARY CONTAINMENT VACUUM "At 1010 [EST] on December 5, 2018, Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement of greater than or equal to 0.25 inches of vacuum water gauge. This condition existed for approximately 3 minutes before the differential pressure was restored to normal when the Standby Gas Treatment system was manually initiated. "This event was caused by a trip of the service air compressor 39AC-2A. The loss of instrument air pressure caused Reactor Building ventilation to isolate and raise Secondary Containment differential pressure. The instrument air pressure was restored when 39AC-2A was isolated and the two backup air compressors started. "This condition did not impact the leak tightness of Secondary Containment or the ability of the Standby Gas Treatment system to establish and maintain the required differential pressure. When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was inoperable. This event is being reported under 10 CFR 50.72(b)(3)(v)(C)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-12-05
53777 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2018-10-09 | 2018-12-05 14:54 | 2018-12-05 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made in accordance with 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A) to provide information pertaining to an invalid Engineered Safety Feature actuation signal. "On October 9, 2018, Arkansas Nuclear One, Unit 2 was in refueling Mode 6, when a vital inverter failed while aligned from its alternate power source causing a loss of one of four vital instrument buses. The loss of the instrument bus resulted in one of the four engineered safety feature protection channels to enter a tripped state. Because one of the other four channels was already in a tripped state in support of a channel power supply replacement activity, two out of four protection channels were now in the tripped state resulting in a Safety Injection Actuation Signal, Containment Spray Actuation Signal, Containment Cooling Actuation Signal, Recirculation Actuation Signal, Emergency Feed Actuation Signal, and Containment Isolation Actuation Signal. "In general, only one train of equipment is protected and assumed to be available during Mode 6 operations. Due to the defense-in-depth plant configuration in Mode 6, which is intended to avoid inadvertent start of emergency systems, the resulting actuations caused no adverse impact to Shutdown Cooling or Spent Fuel Pool cooling operations. At least one train of the following systems was aligned for automatic actuation: "Service Water Emergency Diesel Generator Containment Penetration Room Exhaust Fan Other non-essential components which are shed or realigned upon safeguards actuation "The few systems and components that were aligned for automatic operation responded as designed, including containment isolation valves and valves associated with the above systems (if aligned for automatic operation). The Service Water system was already in operation and, therefore, no Service Water pumps actuated. All systems and components which were capable of automatic operation performed as designed. "The Emergency Diesel Generator started but did not synchronize to the bus. No safety injection occurred to the core. "This actuation was caused by equipment failure and was not an actual signal resulting from parameter inputs. The affected actuation signals do not perform a safety function in Mode 6 and are not required to be available or operable. Therefore, this actuation is considered invalid. "This event was entered into ANO's corrective action program for resolution. This event did not result in any adverse impact to the health and safety of the public. "In accordance with 10 CFR 50.73(a)(i) a telephone notification is being made in lieu of submitting a written Licensee Event Report. The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-12-05
53776 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-10-13 | 2018-12-05 11:24 | 2018-12-05 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a Primary Containment Isolation System (PCIS) Group 1 for Main Steam Isolation Valves (MSIVs), Group 3 for Reactor Water Cleanup (RWCU), Group 6 for Secondary Containment isolation, Group 7 for Reactor Water Sampling, Diesel Generator, Reactor Core Isolation Cooling (RCIC) System logic, and Residual Heat Removal (RHR) logic. "Group 1, Group 6, Diesel Generator actuation, RCIC actuation and RHR actuation are within scope of 10 CFR 50.73(a)(2)(iv). Group 3 and Group 7 are not within scope as they affect only one system. "Cooper Nuclear Station [CNS] was shut down in Mode 5 at the time of the event with the reactor cavity flooded. On October 13, 2018, at 0028 Central Daylight Time, CNS received full PCIS Groups 1, 3, and 6, and a half Group 7 on the Division 1 side. The MSIVs and RWCU isolation valves were already closed for maintenance. The Secondary Containment isolated. Control Room Emergency Filter and the Standby Gas Treatment Systems initiated. The inboard Reactor Water Sample valve isolated. Diesel Generator #1 started but was not required to connect to the critical bus. Reactor Core Isolation Cooling System logic actuated with no expected response due to being isolated for shutdown conditions. "Division 1 RHR pump logic actuated. Division 1 RHR system was operating in shutdown cooling mode. The actuation caused the Division 1 RHR outboard injection and heat exchanger bypass valves to open. Shutdown cooling was unaffected and remained in service throughout the event. "The plant systems responded as expected with no Emergency Core Cooling System injection. "At the time of the event, an in-service inspection of welds inside the reactor vessel was taking place using a robot scanner that uses two vortex thrusters to hold the robot to the vessel wall. The robot inadvertently passed over an instrument penetration, drawing suction on the process leg, resulting in low reactor water level indications and the subsequent invalid Level 1 and 2 system actuations. Actual reactor vessel water level remained steady at cavity flooded conditions. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-12-05
53775 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2018-12-04 | 2018-12-04 17:12 | 2018-12-04 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "On 12/4/2018 at 1340 [PST], Columbia entered a planned evolution to replace the seismic monitoring system. Use of the Modified Mercalli Intensity Scale has been implemented as a compensatory measure per station procedures. The expected duration of the replacement activity will exceed 72 hours, therefore, this is being reported as a major loss of emergency assessment capability in accordance with regulation 10 CFR 50.72(b)(3)(xiii). "Compensatory measures will remain in place until the seismic system replacement has been completed. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-12-04
53774 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-12-04 | 2018-12-04 16:06 | 2018-12-04 | AGREEMENT STATE REPORT - OCCUPATIONAL EXPOSURE EXCEEDING REGULATORY LIMITS The following information was received from the State of Georgia via email: "In accordance with Georgia Rule Chapter 391-3-17-.03-15(b)(3)(ii) [the licensee is notifying the Georgia Radioactive Material Program] of a potential extremity exposure exceeding regulatory limits to an occupational worker at Northside Hospital Atlanta. The timeline and circumstances are as follows: "Northside Hospital received notification from Landauer ([the licensee's] personnel dosimetry vendor) on November 2, 2018, concerning an excessive reading of 58,748 millirem to an extremity dosimeter issued to [an employee] in Nuclear Medicine. "[The licensee's] RSO immediately initiated an investigation which included a personal interview with the employee which resulted in the employee remembering the potential contamination of their ring dosimeter with a radiopharmaceutical as they were handling and injecting a patient dose during the period of use for that dosimeter; however, he was unsure as to the actual presence of contamination on the ring itself. "The RSO assured the employee of the lack of any untoward effects but asked him for a follow-up for any skin effects that may have presented. Also it was noted that the whole body dosimeter during the same period showed only 25-30 millirem exposure. "Based on this incident, there will be a renewed emphasis for all Nuclear Medicine Technologists that in the event of potential contamination to themselves and particularly to any personnel dosimeter, an immediate investigation by [the licensee's] RSO will be initiated and a report filed with [the licensee's] Radiation Safety Committee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2018-12-12
53773 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2018-11-29 | 2018-12-04 15:53 | 2018-12-06 | AGREEMENT STATE REPORT - THEFT AND RECOVERY OF MOISTURE DENSITY GAUGE The following was received from the Maryland Department of the Environment via phone: "On November 29, 2018, at approximately 2230 EST, an unidentified citizen contacted the Prince William, VA police department stating they observed a suspicious person throw a yellow box out of their vehicle and then exit the commuter parking lot at 12745 Minnieville Road, Woodbridge, VA 22192. The response was coordinated by the Virginia Emergency Response Center and Hazardous Materials Office. The responding officer located the yellow case having a radiation warning label affixed and his PRD [Personal Radiation Detector] [indicated that] a radiation source [was] present. The Virginia Department of Fire and Rescue, Virginia Department of Transportation, Virginia Department of Emergency Management, Virginia State Police, and the FBI responded. "Spectral analysis identified Cs-137 with readings of approximately 1.5 mR/hr on contact with the case; typical for a Troxler gauge. The outside lock on the case was cut; a Troxler 3430 gauge with shipping papers were present. The trigger lock was in place. The Virginia Department of Health (VDH) did not have the facilities or capability to take possession of the gauge. The gauge was secured in the Hazardous Materials officer's (HMO) vehicle until other arrangements could be made. "On November 30, 2018, at approximately 0930 EST, VDH contacted the lead Prince William County HMO and was told that there was information contained in the shipping container with the gauge that identified the owner. VDH received that information at approximately 1000 EST and determined the owner of the gauge to be a Maryland licensee [Kim Engineering]. At approximately 1020 EST, the Director of the Virginia Radioactive Materials Program contacted the Maryland Radiological Health Program (RHP) concerning a recovery of a Troxler gauge at a Virginia Department of Transportation park-and-ride. The device was identified as a model 3430, S/N 67880 having an 8 mCi Cs-137 source (5/14/2013), S/N 77-12674, and a [40mCi] Am-241/Be source, S/N 78-8664. The device was last leak tested on 6/22/2018. An official of the Maryland RHP volunteered to drive to Prince William County, VA to retrieve the gauge. Arrangements were [made with] the Maryland official to meet with the Prince William County HMO. At approximately 1315 EST, the State of Maryland official contacted the VDH to confirm transfer of possession of the Troxler gauge to transport it back to Maryland. The Maryland official informed VDH that the licensee notified RHP that someone had stolen a Troxler gauge from the licensee. Maryland agreed to notify the US NRC Operations Center of this incident. "Maryland has scheduled a reactive inspection of the licensee to determine the root cause of the loss or theft." * * * UPDATE AT 1337 ON 12/06/2018 FROM ALAN GOLDEY TO JEFF HERRERA * * * The following is a summary of the additional information was provided by the Maryland Department of the Environment via email: The activity for the Am/Be source, Serial Number: 78-8664, was tested on 6/22/2018 and was less than 185 Bq (0.005 microCuries). Notified R1DO (Lally), ILTAB (Allston - via email), NMSS_events (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2018-12-12
53772 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2018-12-04 09:35 | 2018-12-04 13:35 | 2019-01-30 | HPCI INOPERABLE DUE TO MECHANICAL DRAFT COOLING TOWER FAN BRAKE INVERTER FAILURE "At 0935 EST on December 4, 2018, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to failure of the over speed fan brake inverter. The brakes prevent fan over speed from a design basis tornado. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. Investigation into why the Division 2 MDCT fan over speed brake inverter failed is in progress. This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) based on an unplanned HPCI inoperability. "The NRC Resident Inspector has been notified." Fermi 2 is in a 14-day LCO for inoperability of HPCI and a 72-hour LCO for UHS inoperability. * * * RETRACTION ON 1/30/19 AT 1605 EST FROM CHRIS ROBINSON TO BETHANY CECERE * * * "The purpose of this notification is to retract EN 53772 made on December 4, 2018. Subsequent to the initial notification, the event and site Technical Specifications (TS) were reviewed further. An evaluation determined that TS Limiting Condition for Operation (LCO) 3.0.9 for barriers could be applied to the MDCT fan brakes. As a result of applying TS LCO 3.0.9 to the MDCT fan brakes, it was not necessary to declare the UHS inoperable. With the Division 2 UHS operable on December 4, 2018, the HPCI system was also operable. With HPCI operable, there was no event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident under 10 CFR 50.72(b)(3)(v)(D). Therefore, EN 53772 is retracted and no Licensee Event Report (LER) under 10 CFR 50.73(a)(2)(v)(D) is required to be submitted. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Cameron). | 82 | 0 | 0 | 82 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-12-04
53771 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2018-12-01 | 2018-12-03 19:56 | 2018-12-03 | TECHNICAL SPECIFICATION VIOLATION Violation of Technical Specification 6.1.3, which requires the minimum staffing when the reactor is not secured to be a licensed reactor operator, and another individual. The key was inserted at 1316 PST and removed at 1325 PST and reinserted at 1327 PST and removed at 1331 PST on December 1, 2018. The reactor operator was trying to complete the reactor startup checklist, but was alone. No rods were withdrawn during this period. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | OR | NPR | [5 empty] | 0 | 2018-12-03
53770 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-12-03 | 2018-12-03 16:28 | 2018-12-03 | AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE The following was received from the State of California by email: "On 12/03/18, the RSO [Radiation Safety Officer] contacted CA Office of Emergency Services (OES) to report a stolen density gauge. The gauge involved is a Troxler Model 4640-B, S/N 1292, containing 9 mCi of Cs-137 (thin lift asphalt density gauge). The parked vehicle [in San Francisco, CA] was broken into and the gauge was stolen during overnight hours. According to the RSO, at the time of the theft, the gauge was locked inside a Type A container with additional locks securing the gauge to the vehicle. The gauge user was enroute to a field job in the area near Quality Inn where the theft occurred. "The RSO has immediately notified South San Francisco Police Department of the theft (Report # 18-7086). Licensee will be posting a reward for safe return of the gauge. RHB [CA Department of Public Health - Radiologic Health Branch] will be following up on this investigation." 5010 Number: 120318 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-12-11
53769 | 0 | TRACERCO |  |  |  |  | 2018-12-02 | 2018-12-03 16:06 | 2018-12-03 | LOST SOURCE A pipeline pig was being used to clean out a pipeline in the Gulf of Mexico. The pipeline pig was lost out of the receiver as it was being brought up from the depth. The pig had an attached source so it could be tracked while in the pipeline. The pig and the source are believed to have dropped to the sea floor, a depth of 7,000 feet. Efforts to recover the source have been abandoned. The source is Ta-182 with an activity of 6.24 mCi. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-12-11
53768 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-12-01 | 2018-12-03 14:20 | 2018-12-03 | LOST THEN FOUND TROXLER MOISTURE DENSITY GAUGE The following was received from the State of Illinois by email: "The licensee contacted the agency on 12/1/18 at approximately 1800 [CST] to report that a tornado had struck their portable gauge storage location at 1615 [CST]. Licensee was unable to locate the gauge at the time of the call. Agency inspectors arrived at the location at 1945 [CST] and began surveys. The Troxler gauge was located in its transport case beneath the rubble of the destroyed building. The following morning, an excavator was utilized to remove the debris and gain access to the gauge. Both the gauge and the transport case were undamaged. The gauge was secured by two physical barriers in another building on site. Leak tests will be taken the week of 12/3/18 and the gauge is removed from service until leak test results are received. The licensee will be submitting an amendment request for a new storage location. Pending no further developments, this matter is considered closed." IL Event Item Number: IL180040 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-12-11
53767 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-12-03 | 2018-12-03 11:15 | 2018-12-03 | ACTUATION OF BLACKOUT SEQUENCERS DUE TO LOSS OF ONE OFFSITE POWER SOURCE "At 0315 [CST] on 12/3/18, the Comanche Peak Nuclear Power Plant experienced a loss of 138 KV transformer XST1. Unit 1 is currently at 100% power. Unit 2 was subjected to actuation of both blackout sequencers causing an automatic start of both motor driven Auxiliary Feedwater (AFW) pumps as well as the turbine driven AFW pump. "No emergency diesel generators started as per design. Train A and B motor driven and the turbine driven AFW pumps have been returned to automatic. All other safety systems functioned per design. "The loss of power to 138 KV transformer XST1 resulted in loss of power to both safeguards busses on Unit 2. The busses performed a load-shed and slow transfer to power supplied from 345 KV transformer XST2A as designed and were re-energized and loads sequenced back onto the busses. The emergency diesel generators are not required to start unless the busses are not re-energized by the alternate offsite transformer. All electrical power related actuations functioned as designed. There was no impact on Unit 1. "The licensee has notified the NRC Resident Inspector." | 0 | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-12-03
53766 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-12-02 | 2018-12-02 17:52 | 2018-12-03 | AGREEMENT STATE REPORT - PATIENT CONTAMINATION OF HOSPITAL ROOM The following information was received via e-mail: "On December 2, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that they had admitted a patient at 2210 hours [CST] on December 1, 2018, complaining about a sickness. At 0000 hours on December 2, 2018, the patient gave the treatment nurse a piece of paper from a hospital in Houston, Texas, stating this individual had received a thyroid treatment with iodine-131 on November 29, 2018. At this time the patient was moved to an appropriate room. At this point the patient had been in four different rooms. The four rooms were surveyed for contamination. No contamination was found in the first room surveyed. In the second room, only paperwork was found to be contaminated and the paperwork was disposed of. The third room was a bathroom. Seven tiles in the bathroom were found to be contaminated and were removed. The fourth room was also a bathroom. In this room, the toilet was found to be contaminated. The RSO stated the first survey performed with a 14C rate meter with a pancake GM probe read greater than 20 millirem per hour (mR/hr) (maximum reading on the instrument, i.e. pegged high). A second survey performed with a second instrument indicated a dose rate of 60 mR/hr (on scale reading). The RSO was asked if the reading was in mR/hr or microrem per hour. The RSO confirmed the reading was 60 mR/hr at one foot from the top of the bowl. The RSO stated the room has been isolated and posted. The RSO stated all contaminated laundry had been removed from the areas and placed in the appropriate storage location. The RSO stated the second bathroom would be isolated for an extended period of time. The RSO had been at the facility since 0000 hours so he was headed home for rest. The RSO stated he would provide additional information on Monday December 3, 2018. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: 9641 * * * UPDATE ON 12/03/18 AT 1843 EST FROM KAREN BLANCHARD TO BETHANY CECERE * * * The following update was received from the State of Texas via e-mail: "The licensee's RSO informed the Agency that during its follow-up survey of the bathroom in which they had removed contaminated floor tiles, a single spot was found with readings of 5 mR/hr on the toilet near its water supply line. Therefore, access to this bathroom will also remain restricted. The patient was released from the emergency room late in the day on 12/02/2018. More information will be provided as it is received in accordance with SA-300." Notified R4DO (Gaddy) and NMSS Event Notification Group (by email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-12-10
53765 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2018-12-02 | 2018-12-02 06:17 | 2018-12-02 | ALERT DECLARED DUE TO EMERGENCY DIESEL GENERATOR DAMAGE "During the post-maintenance testing run of the Division III Emergency Diesel Generator [EDG], [a field operator] reported smoke coming from the diesel and an emergency shutdown was required. After the EDG was shutdown, significant damage [thrown rod] to the EDG was observed. "Emergency Action Level HA 2.1 [an Alert] was declared at 0530 [EST]." Currently, the plant is stable and operating at 100 percent power. All safety systems are available. The damage occurred approximately 20 minutes into the required 1 hour run. The licensee's emergency response organization has been activated. No offsite assistance was required or requested. There is a 14-day shutdown limiting condition for operation (LCO) in effect under technical specification 3.5.1 for the high pressure core spray system. Notified DHS Senior Watch Officer, FEMA Operations Center, DHS NICC Watch Officer, HHS Operations Center, DOE Operations Center, EPA Emergency Operations Center, FDA EOC (email), FEMA NWC (email) and DHS Nuclear SSA (email). The licensee has notified state and local authorities and the NRC Resident Inspector. * * * UPDATE ON 12/2/18 AT 0737 EST FROM TODD DAVIS TO HOWIE CROUCH * * * The licensee terminated the Alert at 0731 EST on 12/2/18. The basis for termination was that the licensee has met all procedural requirements to terminate the emergency and on-shift personnel can operate the unit without further assistance. Notified R1DO (Burritt), NRR EO (Miller), IRD MOC (Gott), HQPAO (Couret), ERDS Activation Group, DHS Senior Watch Officer, FEMA Operations Center, DHS NICC Watch Officer, HHS Operations Center, DOE Operations Center, EPA Emergency Operations Center, FDA EOC (email), FEMA NWC (email) and DHS Nuclear SSA (email). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-12-02
53764 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-12-01 | 2018-12-01 16:56 | 2018-12-01 | AUTOMATIC REACTOR TRIP OF UNIT 2 DUE TO A LOAD REJECTION "At 1006 [PST], on December 1, 2018, with Unit 2 at 100 percent power, the reactor automatically tripped due to a load rejection from the 500 kV offsite electrical system. "Operations responded and stabilized the plant. Decay heat is being removed by the Main Steam system to the main condenser using the steam dump valves. The cause of the load rejection is currently under investigation. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). Additionally, due to the actuation of the Auxiliary Feedwater System, as expected, this event is being reported per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Senior Resident Inspector was notified. A press release is planned for this event." All control rods fully inserted and the trip was uncomplicated. There was no effect on Unit 1. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2018-12-01
53763 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2018-11-30 | 2018-11-30 16:08 | 2018-12-21 | PART-21 - EMERGENCY DIESEL GENERATOR EMD FUEL AND SOAKBACK PUMPS LOOSE BOLTS The following report was received via fax: "ESI [Engine Systems, Inc.] was notified by a nuclear customer of two instances where a bolt was found loose or backed out of the cover of an EMD [Electro-Motive Diesel] engine driven fuel pump P/N 8410219. Following notification, ESI inspected remaining pumps in inventory and found instances where one or more of the pump cover bolts were loose or lightly torqued. "EMD fuel pump, P/N 8410219, is commonly used on all 12, 16, and 20-cylinder EMD model 645E4 and E4B engines. The pump is either mechanically driven from the engine (via the scavenging tube oil pump) or motor driven (as in the case of a backup/redundant fuel pump). The pump transfers fuel oil from the day tank to the fuel injectors to support fuel combustion. Without the supply of fuel oil, the diesel engine is unable to produce power which adversely affects the safety-related operation of the emergency diesel generator set. "ESI recommends inspecting the bolts of all pumps for proper bolt tightness. Use a torque wrench and ensure all bolts are tightened to 108 to 120 in-lbs (12 to 13 Nm). "This activity should be performed at the earliest opportunity; however, it is more important for the inspection to be performed on newly installed pumps. It is expected that for pumps supplied with low bolt torque, if a problem were to develop it would be in the form of a fuel leak soon after installation. For pumps that have been successfully installed for several months or years with no detectable leakage, it is less likely that bolt(s) are loose and therefore the urgency of this inspection is reduced." Points of Contact: (252) 977-2720 Dan Roberts, Quality Manager John Kriesel, Engineering Manager Affected Plants: Region 1: Nine Mile Point, Fitzpatrick Region 2: Brown's Ferry, Savannah River, Oconee, St Lucie, Surry Power Station, Turkey Point, Watts Bar Region 3: La Salle, Point Beach, Dresden, Clinton Region 4: Grand Gulf, River Bend, Energy Northwest,, Entergy Operations Inc - Arkansas, Omaha Public Power - Fort Calhoun * * * UPDATE FROM DAN ROBERTS TO JEFFREY WHITED AT 1202 EST ON 12/21/18 * * * The following was received via fax: Revision 1 involves updates on page 2 of the 10 CFR Part 21 Report which include: "In item (iv), added reference to F4B engine application. Revised Item (vii): "For all affected customers: "ESI recommends inspecting the bolt tightness for all pumps. The recommended bolt torque is 108 to 120 in-lbs (12 to 13 Nm). After verifying bolt torque, a shaft freeness check is recommended. The pump shaft should be capable of being rotated by hand in either direction. Due to the small shaft size, this check is commonly performed with a small crescent wrench or with the coupling half installed on the shaft. Inability to rotate by hand indicates loss of end clearance and the pump should be returned to ESI for rework or replacement. "Note: For installed pumps where it is not possible to check shaft freeness, ESI recommends using a reduced bolt torque of 60 to 70 in-lbs (7 to 8 Nm). This is sufficient to ensure the bolts are snug while safeguarding against loss of end clearance that would otherwise go undetected. "This activity should be performed at the earliest opportunity; however, it is more important for the inspection to be performed on newly installed pumps. It is expected that for pumps supplied with low bolt torque, if a problem were to develop it would be in the form of a fuel leak soon after installation. For pumps that have been successfully installed for several months or years with no detectable leakage, it is less likely that bolt(s) are loose and therefore the urgency of this inspection is reduced. "For ESI: The dedication procedures for these pumps have been revised or are being revised to add a step to verify proper bolt torque. This will be completed prior to any future shipments. In addition, ESI is in correspondence with the pump manufacturer to implement corrective actions to prevent reoccurrence." Notified R1DO (Jackson), R2DO (Bonser), R3DO (Stone), R4DO (Alexander), and Part 21/50.55 Reactors (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-11-30
53762 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-11-30 | 2018-11-30 04:22 | 2018-11-30 | OFFSITE NOTIFICATION DUE TO CONTRACTOR FATALITY "At 2300 EST on November 29, 2018 Catawba Nuclear Station (CNS) requested offsite transport for treatment of a contractor to an offsite medical facility. Upon arrival of the offsite medical personnel, the individual was declared deceased at 2354 EST on November 29, 2018. "The fatality was not work-related and the individual was outside of the Radiological Controlled Area. "No news release by CNS is planned. Notifications are planned to the South Carolina Division of Occupational Safety and Health. "This is a four hour notification, non-emergency for a notification of other government agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Defueled | Power Operation |  | Defueled | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-11-30
53761 | 0 | US STEEL CORPORATION GARY WORKS |  |  |  |  | 2018-11-29 | 2018-11-29 17:18 | 2018-11-29 | GAUGE STUCK SHUTTER Maintenance technicians performing a lockout for maintenance manipulated a moisture gauge and the handle broke, rendering the shutter stuck in the open position. The normal position for the shutter is open. The maintenance was canceled and the area around the gauge was roped off. The vendor has been contacted to help the licensee repair the gauge. No exposure to personnel resulted from this event. The gauge measures the moisture content in a bin containing metallurgical coke. The gauge is a Berthold containing a 300 mCi Am-241/Be source (serial number 048/10). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-12-07
53760 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2018-10-01 | 2018-11-29 12:56 | 2018-11-29 | INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of the Reactor Protection System (RPS). "At 0147 [EST] on October 1, 2018, Seabrook Unit 1 was in Mode 3 shutdown, when an invalid Reactor Protection System actuation occurred due to a high Source Range detector. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into Seabrook's corrective action program for resolution. "The NRC Resident Inspector has been notified." The Source Range detector which gave the invalid input has been replaced. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-11-29
53759 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-11-28 | 2018-11-28 17:25 | 2018-11-28 | DISCOVERY OF A CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "On November 28, 2018, while performing an engineering review of the bases for environmental qualification (EQ) requirements for the Atmospheric Steam Dumps (ASDs), it was determined that applicable EQ requirements had not been applied to a key component of each of the ASDs. The result of this issue is that it the availability of the ASDs for a controlled plant cooldown following a postulated steam line break outside containment cannot be assured. "Callaway is developing a compensatory action temporary plant modification to install insulation that will protect the affected ASD components from the post Main Steam Line Break temperature. "This condition is reportable 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (B) remove residual heat, or (D) mitigate the consequences of an accident." The issue places the plant in a 24-hour Technical Specification (TS) Limiting Condition for Operations (LCO), 3.7.4. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-11-28
53758 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-28 | 2018-11-28 17:10 | 2018-11-28 | AGREEMENT STATE - FIXED GAUGE STUCK SHUTTER The following information was received from the State of Texas via email: "On November 28, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that while performing a shutter test on an Ohmart-Vega Model SH-F1 gauge containing a 20 milliCurie (original activity) Cs-137 source, the shutter would not close. Open is the normal operating position for the gauge. The gauge is in a location that does not present an exposure risk to any individual. The licensee has contacted a service provider to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9640. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-12-06
53757 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-11-28 | 2018-11-28 12:30 | 2018-11-28 | OFFSITE NOTIFICATION DUE TO INADVERTENT SIREN ACTIVATION "At 0752 CST, on November 28, 2018, Dakota County inadvertently actuated their sirens while performing a scheduled weekly [Emergency Planning Fixed Siren Test]. All seven (7) Dakota County sirens actuated for approximately 9 seconds before Dakota County Dispatch canceled the activation. This 4-hour non-emergency report is being made per 10 CFR 50.72(b)(2)(xi), Offsite Notification [which was made to Dakota County Dispatch]. Capability to notify the public was never degraded during this time. All Emergency Notification sirens remain in service. No press release is planned at this time." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-11-28
53756 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-11-27 | 2018-11-28 05:40 | 2018-12-03 | INOPERABILITY OF EQUIPMENT FOR CONTROL OF RADIOLOGICAL RELEASE "At 2130 CST on 11/27/2018, Division 1 Main Steam Positive Leakage Control System (MS-PLCS) was declared inoperable because of a leaking check valve that caused excessive cycling of the associated air compressor. "Division 2 MS-PLCS had been declared inoperable on 11/27/2018 at 1400 CST when a pressure control valve in the system exceeded the maximum allowable stroke time. "Because MS-PLCS supplements the isolation function of the main steam isolation valves (MSIVs) by processing fission products that could leak through the closed MSIVs, both divisions of MS-PLCS inoperable at the same time represents a condition that could prevent the fulfillment of a safety function of an SSC [Structures, Systems and Components] that is needed to control the release of radioactive material. "The station diesel air compressor is available to supply backup air to the safety relief valves as required by the Technical Requirements Manual." [This is associated with operability of the safety relief valves, due to the inoperable MS-PLCS air compressor.] The unit is in a 7 day shutdown Limiting Condition for Operation (LCO), 1-TS1-18-Div 1 & 2 MSPLCS-685, for the two divisions of MS-PLCS being inoperable. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 12/03/18 AT 1551 EST FROM TIM GATES TO BETHANY CECERE * * * "This event was initially reported under 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented the Main Steam Positive Leakage Control System (MS-PLCS) from fulfilling its safety function to control the release of radioactive material. Division I was declared inoperable due to a failed component. Division II was declared inoperable due to a pressure control valve in the system exceeding the maximum allowable time to close by 0.50 seconds. An engineering evaluation has since been performed and concluded that the 2 second maximum allowable time to close was based on the pressure control valve being classified as a rapid closure valve and was established from the original baseline data of 0.50 seconds. This baseline data is an administrative target value per the In-Service Testing Program. There are no technical specification requirements associated with the 2 second closure time. "The engineering evaluation also determined that the volume of air supplied through the pressure control valve during the extra 0.50 seconds of valve closure would have an inconsequential effect on the pressure within the volume of leakage barrier between the Main Steam Isolation Valves associated with the MS-PLCS pressure control valve or have any effect on containment over-pressurization. "Based on the information provided by the engineering evaluation, the Division II MS-PLCS has been declared operable-degraded non-conforming since time of initial discovery. Consequently, this event is not reportable as a condition that could have prevented the Main Steam Positive Leakage Control System (MS-PLCS) from fulfilling its safety function. "The [NRC] Resident Inspector has been notified via e-mail." Notified the R4DO (Gaddy). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-11-28
53755 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-11-26 | 2018-11-26 15:51 | 2018-11-26 | AGREEMENT STATE REPORT - LOSS OR THEFT OF MOISTURE DENSITY GAUGE The following report was received from the State of California via email: "On November 26, 2018, at approximately 1015 [PST] .., [the] RSO [Radiation Safety Officer] of RMA Group, Radioactive Materials License #8054-37, contacted RHB [Radiologic Health Branch] Brea concerning the moisture/density gauge, Troxler 3430, Cs-137 serial #750-4104, Am-241 serial #47-26740 (Cs-137, 0.333 GBq, Am-241, 1.6 GBq) that had been found missing during a semi-annual inventory of the radioactive gauges possessed at the permanent storage facility at 6976 Convoy Court, San Diego, CA 92111. [The RSO] will contact local law enforcement in San Diego and will fill out a police report with them. A copy of the theft report will be forwarded to the RHB Brea office to be included as part of this report. [The RSO] will contact local newspapers to attempt to retrieve the stolen radioactive gauge as well as notifying local servicing vendors of radioactive gauges to be alert for the serial number of the stolen gauge in case it turns up for service. The investigation will continue to determine if the radioactive gauge can be found and determination can be made on how it was lost at the permanent storage location. This is being reported to the NRC Operations Center as a 24-hour report under 10 CFR 30.50(b)(2) since the radioactive gauge has been lost and it can not be determined what condition the sources are currently in." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-12-04
53754 | -1 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-11-26 | 2018-11-26 08:31 | 2018-11-29 | UNUSUAL EVENT DECLARED FOR EXCESSIVE SMOKE IN CONTAINMENT At 0816 EST, a Notification of Unusual Event was declared for Unit 2 under Emergency Action Level H.U.4 for excessive smoke in the lower level of containment with a heat signal. Onsite fire brigade is responding to the event. A command post is established. Offsite support is requested by the fire brigade. No flames have been observed as of this report. The NRC Resident Inspector and State and Local government agencies will be notified. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 11/26/18 AT 1036 EST FROM BILL HARRIS TO JEFFREY WHITED * * * At 1036 EST, Sequoyah Nuclear Station Unit 2 terminated the Notice of Unusual Event. The licensee determined that the source of the smoke in containment was oil on the pressurizer beneath the insulation, that heated up during plant heatup. The licensee did not see visible flame during the event. The licensee is still working to determine if there was any damage to the pressurizer. The licensee will notify the NRC Resident Inspector. Notified R2DO (Rose), R2RA (Haney), NRR (Nieh), IRD MOC (Gott), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 11/26/18 AT 1337 EST FROM STEPHEN FRIESE TO KARL DIEDERICH * * * Following declaration of the Notification of Unusual Event, TVA media relations communicated with the local media regarding the event. The licensee has notified the NRC Resident Inspector. Notified R2DO (Rose). * * * UPDATE ON 11/26/18 AT 1551 EST FROM STEPHEN FRIESE TO DONG PARK * * * "At 1036 EDT, Sequoyah Nuclear Plant (SQN) terminated the Notification Of Unusual Event (NOUE) due to initial report of heat and smoke in Unit 2 Lower Containment. "At 1000 EDT, it was determined that no fire had occurred. Due to difficulty of access to some of the areas being searched, the source could not be identified prior to 1000 EDT. No visible flame (heat or light) was observed. "The source of the smoke was determined to be residual oil from a hydraulic tool oil in contact with pressurizer piping. The pressurizer piping was being heated up to support Unit 2 start-up following U2R22 refueling outage. Once the residual oil dissipated, the smoke stopped. It has been concluded that no fire or emergency condition existed. "Unit 2 is currently in Mode 5, maintaining reactor coolant temperature 160F-170F and pressure 325psig-350psig with 2A Residual Heat Removal (RHR) system in service in accordance with U2R22 refueling outage plan." The licensee has notified the NRC Resident Inspector. Notified R2DO (Rose). * * * RETRACTION ON 11/29/2018 AT 1358 EST FROM FRANCIS DECAMBRA TO ANDREW WAUGH * * * "Sequoyah Nuclear Plant (SQN) is retracting this notification based on the following additional information not available at the time of the notification: "Following a full Reactor Building inspection, it was concluded that a fire did not exist. The source of the smoke originally reported was later determined to be residual oil from a hydraulic tool in contact with pressurizer piping. Once the residual oil dissipated, the smoke stopped. The source of heat originally reported was normal heated conditions associated with the pressurizer commensurate with plant conditions. SQN reported initially based on the available information at the time and to ensure timeliness with emergency declaration and reporting notification requirements." The licensee has notified the NRC Resident Inspector. Notified R2DO (Shaeffer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2018-11-26
53753 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-11-25 | 2018-11-25 15:10 | 2018-11-25 | SAFEGUARDS REPORT - SECURITY MEASURES SUSPENDED DUE TO WEATHER CONDITIONS Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 11/25/2018 AT 2110 EST FROM ROY GILES TO DONG PARK * * * All security measures have been returned to normal at 1955 CST. The licensee will notify the NRC Resident Inspector. Notified R4DO (Werner) and 73.71 Group via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 |  | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-11-25
53752 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2018-11-24 20:15 | 2018-11-25 02:47 | 2019-01-18 | LOSS OF CONTROL ROOM ENVELOPE DUE TO DOOR FAILURE "On 11/24/18 at 2015 EST, a loss of Control Room Envelope (CRE) was declared due to failure of the control room boundary door, 204-36-008. [Abnormal Operating Procedure 8588A Mitigating Actions for Control Boundary Breach was implemented]. The door was repaired at 2030 EST, restoring CRE to operable [status]." A mechanical failure of the control room door latch prevented the door from closing. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 01/18/19 AT 1457 EST FROM GARY CLOSIUS TO JEFFREY WHITED * * * "The purpose of this call is to retract a report made on November 25, 2018, NRC Event Number EN53752. "NRC Event Report number EN53752 describes a condition at Millstone Power Station Unit 2 (MPS2) in which a control room envelope boundary door was discovered to not be able to fully close due to the latching mechanism being stuck in the extended position. "The condition was reported to the NRC pursuant to 10 CFR 50.72(b)(3)(v)(D) via an 8-hour prompt report as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "Upon further review, MPS2 determined that there was no loss of safety function. An engineering evaluation determined that even with the control room boundary door unable to be fully closed due to the latching mechanism being stuck in the extended position, control room air in-leakage would not have been sufficient to prevent the control room emergency ventilation system from performing its safety function. "Therefore, this condition is not reportable and NRC Event Number EN53752 is being retracted. "The basis for this conclusion has been provided to the NRC Resident Inspector." Notified the R1DO (Carfang). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-11-25
53751 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-11-24 | 2018-11-24 21:27 | 2018-11-24 | AUXILIARY BUILDING DOOR BLOCKED OPEN "At 1420 [EST] on November 24, 2018, operators discovered that a door was blocked open creating a breach of the auxiliary building secondary containment enclosure (ABSCE) boundary that exceeded the allowed ABSCE breach margin [of three minutes]. As a result, Unit 1 entered Technical Specification Limiting Condition of Operation (LCO) 3.7.12 Condition B for two trains of Auxiliary Building Gas Treatment System (ABGTS) inoperable due to an inoperable ABSCE boundary in MODE 1, 2, 3, or 4, and both Units entered Condition E for one required ABGTS train inoperable with fuel stored in the spent fuel pool. "In MODES 1, 2, 3, and 4, the analysis of the loss of coolant accident (LOCA) assumes that radioactive materials leaked from the Emergency Core Cooling System are filtered and absorbed by the ABGTS. For the fuel handling accident, the analysis assumes that the ABSCE boundary is capable of being established to ensure releases from the auxiliary and containment buildings are consistent with the dose consequence analysis. "The event is reportable in accordance with 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to: (C) control the release of radioactive material and (D) mitigate the consequences of an accident. "No actual LOCA or fuel handling accident occurred while both trains of ABGTS were inoperable. The condition had no impact on the health and safety of the public. "The NRC Resident Inspector has been notified." This situation occurred because of maintenance activities. A breeching permit had been initiated however, the required personnel to ensure the door could be closed within the required three minutes were not assigned. The door was closed approximately 15 minutes after the situation was noticed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-11-24
53750 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-11-21 21:25 | 2018-11-22 03:56 | 2018-12-28 | HPCI UNEXPECTEDLY TRANSFERRED TO ALTERNATE SUCTION SOURCE DURING TESTING "At 2125 [CST] on 11/21/2018, it was discovered that U1 High Pressure Coolant Injection System (HPCI) was inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v), as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "During performance of a routine surveillance, HPCI automatically transferred from its normal suction source to the alternate suction source. The control room operator then manually tripped the HPCI turbine. HPCI was already inoperable in accordance with Technical Specifications (TS) Limiting Condition for Operability (LCO) 3.5.1, ECCS Operating, Condition C during performance of the surveillance. However, this condition was not expected nor induced by the testing. "There was no impact to the safety of the public or plant personnel. The NRC Resident Inspector has been notified. "CR 1469109 documents this condition in the Corrective Action Program." * * * RETRACTION ON 12/28/18 AT 1300 EST FROM MARK MOEBES TO JEFFREY WHITED * * * "ENS Event Number 53750, made on November 22, 2018, is being retracted. "NRC notification 53750 was made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72(b)(3)(v)(D) were met when the licensee discovered an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "During performance of a routine surveillance, the High Pressure Coolant Injection (HPCI) System automatically transferred from its normal suction source to the alternate suction source. As a result, Unit 1 HPCI was declared inoperable. "On December 20, 2018, a Past Operability Evaluation was completed which determined that the HPCI System remained operable. The evaluation determined that the HPCI System could have performed its specified safety function of vessel injection throughout the time that the suction path was aligned to the torus. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(D). "TVA's evaluation of this event is documented in the Corrective Action Program in Condition Report 1469109. "The licensee has notified the NRC Resident Inspector." Notified R2DO (Desai). | 13 | 0 | 0 | 13 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-11-22
53749 | 0 | PALISADES | 1 |  |  | [1] CE | 2018-11-21 | 2018-11-21 17:27 | 2018-11-21 | DEGRADED CONDITION IDENTIFIED DURING SURFACE INSPECTION OF REACTOR HEAD NOZZLE PENETRATION "On November 21, 2018, during an extent of condition review, after completion of ultrasonic testing, further interrogation of reactor vessel closure head (RVCH) penetration 36 was performed using eddy current testing. The testing detected three repairable indications. No indication of boric acid leakage was identified at this location during the bare metal visual inspection. Extent of condition review is complete on all RVCH penetrations. "The plant was in cold shutdown at 0 percent power and in Mode 6 for a refueling outage at the time of discovery. Repair actions will be completed prior to plant startup from the outage. "This condition has no impact to the health and safety of the public. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A) for degradation of a principal safety barrier. "The licensee notified the NRC Senior Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-11-21
53748 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-11-16 | 2018-11-20 16:04 | 2018-11-20 | AGREEMENT STATE REPORT - MISADMINISTRATION OF SODIUM PERTECHNETATE The following information was received via e-mail from the State of Florida: "On Friday, November 16, 2018, [the licensee] called to report a medical event involving licensee 4000-1. A patient was administered 150 milliCi of Sodium Pertechnetate that was originally intended to be used to calibrate a machine. The critical organ dose was less than 50 rem; the effective dose was 7 rem." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-11-28
53747 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-08 | 2018-11-20 15:26 | 2018-11-20 | AGREEMENT STATE REPORT - LIQUID SCINTILLATION COUNTER SENT TO RECYCLING CENTER The following information was received via e-mail from the State of Texas: "On November 20, 2018, the licensee reported that a Liquid Scintillation Counter (LSC) (LKB -WALLAC 1410), potentially containing an internal source and also H-3/C-14 standards, was surplused on November 8, 2018. Surplus staff informed that the unit had gone to metal recycling. On November 19, 2018, radiation safety retrieved broken glass standards (approx. 100,000 dpm each vial, November 1987) from metal recycling [Madison Metals in Bryan TX]. This particular model WALLAC 1410 was known to contain approximately 12 microCi Eu-152. The activity currently could be as low as 2.45 microCi. Neither the source nor shielding was found. A contamination survey was completed with probes and the wipes were counted in an LSC, and nothing was found over background. The metal recycling center is closed for the holidays and no one is expected to receive an exposure. More information will be forwarded once it is received. The investigation is ongoing." Texas Incident Number: I-9639 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-11-28
53746 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2018-11-19 | 2018-11-20 11:15 | 2018-11-20 | CONTAMINATED WORKER REQUIRING MEDICAL TREATMENT "On November 19, 2018, at approximately 1130 [EST], a conversion area worker was cleaning up a spill of liquid uranyl fluoride (UO2F2) that can contain hydrofluoric acid (HF). During the cleanup effort, some amount of this solution was able to come in contact with the worker's clothing potentially impacting their skin on the legs above the ankle. Appropriate treatment for exposure to HF was provided by onsite medical response staff. When the operator attempted to exit the chemical side of the plant, radioactive material contamination was detected on both hands. The contamination on both hands was above free release criteria and was unable to be removed by normal decontamination methods. The worker was transported to an offsite medical facility accompanied by plant health physics personnel. The worker was sent to the hospital for observation due to the potential chemical exposure. "The Columbia plant is a licensed Part 70 facility subject to 10 CFR 70 Subpart H. Spills within the conversion area of the plant are evaluated in the Integrated Safety Analysis and Summary. This issue does not challenge the performance requirements of 10 CFR 70.61. "Operations staff finished cleaning up the spill. At the time of this notification, the employee reported to management that they are awaiting discharge from the hospital. This issue has been entered into the facility's corrective action program. "24-Hour Event Notification based on 10 CFR 70.50(b)(3), 'An event that requires unplanned medical treatment at a medical facility of an individual with spreadable radioactive contamination on the individual's clothing or body.' Also applicable to this issue is a 24-Hour Event Notification based on 10 CFR 70 Appendix A(c), 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made, shall be reported to the NRC Operations Center concurrent to the news release or other notification.' This issue requires notification to the South Carolina (SC) Department of labor, Division of Occupational Safety and Health." The licensee has notified NRC Region 2. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | MED TREAT INVOLVING CONTAM | OFFSITE NOTIFICATION/NEWS REL | [8 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.50(b)(3) | PART 70 APP A (c) |  |  | 0 | 2018-11-28
53745 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2018-11-19 | 2018-11-19 23:04 | 2018-11-19 | EMERGENCY DIESEL GENERATOR ACTUATION DUE TO LOW VOLTAGE SIGNAL "On 11/19/2018, at 1916 EST, with unit 2 in Mode 5 at 0 percent power, an actuation of the 'B' [Emergency Diesel Generator] EDG occurred during troubleshooting activities with the opposite train protected. The reason for the 'B' EDG auto-start was low voltage on the E-2 bus due to its supply breaker opening. The 'B' EDG automatically started as designed when the low voltage signal was received. Following the EDG start, required loads sequenced on as designed including the 'B' [Motor Driven Auxiliary Feedwater Pump] MDAFW Pump. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Emergency AC Electrical Power System (Emergency Diesel Generator) and Auxiliary Feedwater System (Motor Driven Auxiliary Feedwater Pump). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-11-19
53744 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2018-11-17 | 2018-11-19 13:59 | 2018-11-19 | UNPLANNED CONTAMINATION DUE TO KILN SEAL LEAK "On 11/17/2018, at approximately 1445 EST, it was discovered that the Fuel Manufacturing Operation (FMO) Dry Conversion Line 1 kiln seal began to leak and caused an alarm on the Hydrogen Fluoride (HF) room detection system. This manufacturing process equipment is within an established FMO contamination-controlled area which is designed to contain and control this type of release. The area was not occupied at the time, there were no personnel exposures or releases from the area and the affected process was shut-down. "As a precautionary measure consistent with current NRC radiation protection requirements, an appropriate, additional radiological control was imposed by requiring respiratory protection for entry into the room to keep personnel exposures as low as reasonably achievable until the area could be decontaminated in a safe and timely manner. Although the affected equipment remains shutdown, this additional radiological control remained in place for more than 24 hours. "NRC Fuel Cycle Safety and Safeguards staff recently clarified its position for this type of reportability determination in a letter sent to the Nuclear Energy Institute dated October 5, 2018. Because of this letter, this event is conservatively being reported pursuant to the requirements of 10 CFR 70.50 (b)(1)." The NRC region will be notified. Additionally, the North Carolina Radiation Protection Commission and New Hanover County Emergency Management will also be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2018-11-27
53743 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-16 | 2018-11-16 18:13 | 2018-11-16 | AGREEMENT STATE REPORT - MISADMINISTRATION OF THERASPHERE MICROSPHERES The following information was received via E-mail: "On November 16, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that a medical event had occurred earlier that day. "The event occurred when the licensee attempted to treat a patient with 220 grays of Yttrium-90 (TheraSphere) microspheres. After the treatment the injection catheter was removed from the device and placed in a storage container. A survey of the container indicated the dose rate was half of the dose rate prior to injection. The licensee stated they believe only 107.1 Grays of the spheres had been injected into the patient. "The licensee did not provide the target organ, but will provide it in the written report. The licensee stated the patient would not experience any adverse effects from the event. The licensee stated no individual performing the treatment received any significant exposure. The licensee stated the area was not contaminated. The licensee did not have a cause for the event, but will provide it once determined. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I - 9636 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-11-26
53742 | -1 | EPA OFFICE OF RESEARCH AND DEVELOPM |  |  |  |  | 2018-11-16 | 2018-11-16 16:08 | 2018-11-21 | TROXLER GAUGE LOST IN TRANSIT On 11/16/2018, a Troxler gauge was declared lost by the EPA while in transit from Ada, OK to the Troxler Corporation in Research Triangle Park, NC. The Troxler gauge departed from the EPA Office of Research and Development to the Troxler corporation for disposal on 11/8/2018. On 11/16/2018, the EPA Radiation Safety Officer contacted Troxler and determined that they had not yet received the gauge. The transportation company was then contacted and the transportation company records indicated that the gauge was still in transit to Memphis, TN, but could not be located. The EPA is still investigating to determine the location of the gauge. The gauge is a Troxler Model 4302, Serial Number 382, containing 10 milliCuries of Am-241/Be. * * * RETRACTION ON 11/21/18 AT 0959 EST FROM CHERRI ADAIR TO BETHANY CECERE * * * The intact gauge was located in Richmond, VA. The transportation company plans to deliver the gauge to Troxler, as originally intended. Notified R4DO (Werner), NMSS Events Notification Group, and ILTAB by email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | OK | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-11-26
53741 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-11-16 | 2018-11-16 05:16 | 2018-11-16 | TRANSPORT OF POTENTIALLY CONTAMINATED WORKER AND SUBSEQUENT FATALITY "On November 16, 2018 at 0202 EST, a potentially contaminated Dominion worker was transported offsite for medical attention. The individual was initially found unresponsive in a contaminated area. A partial survey was performed prior to the individual being transported offsite, and no contamination was found. The individual passed away in transit to the hospital. Follow-up surveys to verify no contamination are ongoing. A notification to OSHA (Occupational Safety and Health Administration) is planned. "This event is being reported pursuant to 10CFR50.72(b)(2)(xi) due to notification of an offsite organization and 10CFR50.72(b)(3)(xii) due to a potentially contaminated worker transported offsite. "The NRC Resident Inspector was notified." * * * UPDATE FROM ALAN BIALOWAS TO DONALD NORWOOD AT 1640 EST ON 11/16/2018 * * * "Follow-up radiological surveys were performed and determined that there was no contamination on the worker, response personnel, or ambulance. The Occupation Safety and Health Administration was notified on 11/16/18. No media release is planned." The NRC Resident Inspector was notified. Notified the R2DO (Sandal) and via E-mail the NRR EO (Miller) and IRD MOC (Gott). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2018-11-16
53740 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-11-14 | 2018-11-15 13:13 | 2018-11-15 | AGREEMENT STATE REPORT - MEDICAL EXPOSURE READ AS OCCUPATIONAL EXPOSURE The following report was received via e-mail: "On Wednesday, November 14, [the University of Miami Radiation Safety Officer (RSO)] received an Occupational Exposure Report from Mirion Technologies indicating that for wear dates July 1 through July 31, 2018, x-ray technologist [redacted] received the following doses: Deep: 8328 mR, Eye: 8328 mR, and Shallow: 8328 mR. "Upon interviewing Mr. [redacted], in the presence of his supervisor, Mr. [redacted] indicated that he had a therapeutic Nuclear Medicine procedure for hyperthyroidism during the month of July in one of our facilities. Upon review of his medical records it was confirmed that Mr. [redacted] received 24 microCuries of iodine-131 for an uptake scan on July 10, 2018, and a therapeutic dose of 28.9 mCi of iodine-131 on July 17, 2018. It was noted that Mr. [redacted] wears his dosimeter high on the collar of his scrubs, very close to the area overlying his thyroid and continued to wear it throughout the period in question. Based on this information it is [the RSO's] professional judgement that this dose does not constitute an Occupational Dose but is rather a medical dose, and he will be requesting that his dosimetry provider remove it from Mr. [redacted] Occupational [dose]." Florida Incident: FL18-139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-11-23
53739 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2018-11-14 | 2018-11-15 12:02 | 2018-12-14 | AGREEMENT STATE REPORT - RADIATION WORKER RECEIVES HIGH DOSIMETRY READING The following report was received from the Arkansas Department of Health via email: "The RSO reported at 1100 [CST], on November 14, 2018, that the dosimetry provider had reported to the licensee one radiation worker badge had received a possible exposure of 9,000 mR for the month of October. The dosimetry provider has stated the exposure was a dynamic exposure with atypical exposure to the badge. "The licensee began to investigate the cause of the high reading. The worker had worked with other employees and had not worked independently during the month. Other workers had routine exposures for the month. "The licensee requires workers to wear SRD's [Self Reading Dosimeter] while working in the restricted area. The worker's cumulative reading for the time period was 200 mR. The worker's ring badge had routine exposure readings. "During investigation by the licensee, there was no recollection of the badge being separated from the worker during the month. During off hours, all dosimetry is stored with the worker's lab coats outside the restricted area. "The licensee develops PET [Positron Emission Tomography] radionuclides for radiopharmaceutical research and development. "Since the time period of the exposure cannot be determined, the Arkansas Program is reporting this event under RH-1502.b. of the Arkansas Regulations equivalent to 10 CFR 20.2202(b)(1) of the NRC Regulations. "The licensee and the State continue to investigate. "The State of Arkansas will update when additional information is known. "Arkansas event number AR-2018-006." * * * UPDATE ON 12/14/18 AT 1535 EST FROM STEVE MACK TO BETHANY CECERE * * * The following update was received from the Arkansas Department of Health (Department) via email: "The licensee provided a written report dated November 15, 2018, outlining the investigation performed to verify the overexposure reported. "This report restated the requirements of additional dosimetry worn by the worker with no significant indication exposure above routine doses. The report also indicated that at no time during the month was contamination detected when conducting personnel surveys leaving the restricted area. The licensee continues to believe that the dose was only received by the badge and not to the whole body of the radiation worker. "The licensee submitted its own dose estimate on December 3, 2018, in which the licensee calculated a possible contamination event of the badge that would provide the dose yet exclude dose to other measuring devices and could evade detection when exiting the restricted area. "The Department has taken this dose estimate into consideration and is requesting that the October, 2018 dose for the radiation worker be reduced to 250 mrem. "The Department considers this event closed." Notified R4DO (Taylor), NMSS Events Notification group, and INES (Milligan) by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2018-11-23
53738 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-10-18 | 2018-11-15 11:13 | 2018-11-15 | AGREEMENT STATE REPORT- FAILED SHUTTER The following was received from the state of Pennsylvania via email: "Notifications: On November 14, 2018, the licensee informed the Department [Pennsylvania Department of Environmental Protection] of a failed shutter. It is reportable per 10 CFR 30.50(b)(2). "Event Description: The licensee reported that on October 18, 2018, a IRMS Model TG-2 gauge, serial number 00MO397-15, containing 3000 milliCuries of americium 241 did not properly perform following scheduled maintenance. Specifically, the shutter failed to open completely and then would not open at all. The gauge was taken out of service and a service provider was contacted, responded and corrected the problem. The licensee has since contacted the same service provider and, on November 2, 2018, transferred the device for proper disposal. Licensee and service provider survey results indicated no abnormal amounts of radiation in the area before, during or after the event or removal of the device. There were no overexposures related to this event. "Cause of the Event: Equipment failure. "Actions: The Department will perform a reactive inspection. More information will be provided upon receipt." PA Event Report ID No: PA180020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-11-23
53737 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-11-13 | 2018-11-14 07:47 | 2018-11-14 | AGREEMENT STATE REPORT- IRRADIATOR ACCESS CONTROL SYSTEM INOPERABLE The following was received from the state of Pennsylvania via email: "On November 13, 2018, the Department [Pennsylvania Department of Environmental Protection] was notified by the licensee that part of the access control system to their J. L. Shepherd Model 81-14 beam irradiator containing approximately 9900 Curies of cesium 137 is currently inoperable. Specifically, the 'activation of the visual and audible alarm' and 'notification of another individual who is onsite of the entry' parts of 10 CFR 36.23(b). Non-compliance with this regulation also renders them in non-compliance with 10 CFR 36.23(c). The licensee is currently complaint with all other parts of the regulation. They have taken the alarm system off-line since it currently is alarming every time the facility door is opened, even though the source is in the shielded position. A security system vendor is on site as of today and is working on both issues. The licensee is currently also performing a root cause analysis alongside this security system vendor, and the state will perform a reactive inspection." PA Event Report ID No: PA180019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-11-22
53736 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-11-12 | 2018-11-12 20:52 | 2018-11-12 | SPECIFIED SYSTEM ACTUATION "On November 12, 2018, at 1636 EST, with Surry Unit 1 at 100 percent power and Surry Unit 2 defueled, the 'C' Reserve Station Service Transformer (RSST) pilot wire lockout actuated during restoration of the 'C' RSST following transformer replacement. This resulted in electrical isolation of the 'C' RSST, the 'F' Transfer Bus, the Unit 1 'H' Emergency Bus, and the Unit 2 'J' Emergency Bus. The #1 and #3 Emergency Diesel Generators automatically started and loaded onto the 1H and 2J emergency buses, respectively, as designed. Operations entered the appropriate abnormal procedures and stabilized both units. This equipment operated as expected during the event. "The Surry electrical distribution system was in an off-normal alignment to support 'C' RSST replacement with the dependable alternate power supply from Unit 2 station service backfeed supplying the 1H and 2J emergency buses. The 'C' RSST pilot wire lockout tripped and locked out the station service supply tie breaker to the 'F' Transfer Bus. "The organization is reviewing the 'C' RSST pilot wire lockout and the required actions for recovery. Surry Unit 1 entered a 6-hour action statement to place the unit in Hot Shutdown due to this partial loss of offsite power. This clock was exited upon reset of the pilot wire lockout, restoring backfeed as a dependable offsite power source. Unit 1 remained at 100 percent power throughout the event. "No radiological consequences resulted from this event. This event is being reported pursuant to 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the #1 and #3 Emergency Diesel Generators. "The NRC Resident was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-11-12
53735 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2018-11-12 | 2018-11-12 14:06 | 2018-11-14 | OFFSITE NOTIFICATION TO FIRE MARSHALL FOR FIRE SUPPRESSION SYSTEM INSPECTION "At 0930 (EST) on November 12th, 2018, the New Hanover County Deputy Fire Marshall was notified per State code requirements that the fire suppression system (Fire Riser 617) for the FMO [Fuel Manufacturing Operations] oil storage warehouse will be taken offline to replace sprinkler heads and conduct the required 5 year inspection. This impairment will begin Tuesday, November 13th. This building is normally unoccupied. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70 Appendix A(c)." The system will be offline for approximately 8 hours and the NRC will be notified once work is complete. The licensee will notify the NRC Region and the State of North Carolina * * * UPDATE ON 11/14/18 AT 1547 FROM PHILLIP OLLIS TO BETHANY CECERE * * * "Fire Riser 617 and the supporting system was restored to service at approximately 1300 EST, 11/14/18. The NHC Deputy Fire Marshall was notified via telephone of the return to service." Notified R2DO (Sandal) and NMSS Events Notification (by email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-11-20
53734 | 0 | PALISADES | 1 |  |  | [1] CE | 2018-11-11 | 2018-11-11 21:59 | 2018-11-11 | DEGRADED CONDITION DUE TO INDICATION DURING ULTRASONIC INSPECTION OF REACTOR HEAD NOZZLE PENETRATION "On November 11, 2018, during ultrasonic data analysis from reactor vessel closure head in-service inspections, signals that display characteristics consistent with primary water stress corrosion cracking in head penetration 33 were identified. No indications of boric acid leakage and no surface indications were detected at this location during bare metal visual inspection. "The plant was in cold shutdown at 0% power and in Mode 6 for a refueling outage at the time of discovery. Repair actions will be completed prior to plant startup from the outage. "This condition has no impact to the health and safety of the public. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A) for degradation of a principal safety barrier. "The licensee notified the NRC Senior Resident Inspector. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-11-11
53733 | 0 | PALISADES | 1 |  |  | [1] CE | 2018-11-10 | 2018-11-10 17:48 | 2018-11-10 | BORIC ACID IDENTIFIED ON REACTOR VESSEL HEAD PENETRATION "On November 10, 2018, during a planned bare metal visual inspection of the reactor head, boric acid was discovered at a CRDM [Control Rod Drive Mechanism] nozzle to reactor head penetration. Investigation of the source of the boric acid is ongoing. The plant was in cold shutdown at 0% power and Mode 6 for a refueling outage at the time of discovery. Repair actions will be completed prior to plant startup from the outage. All other reactor vessel head penetrations have had a bare metal visual inspection completed with no other indications identified. "This condition has no impact to the health and safety of the public. "This report is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A) for degradation of a principal safety barrier. "The licensee notified the NRC Senior Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-11-10
53732 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-11-10 | 2018-11-10 04:35 | 2018-11-10 | AUTOMATIC REACTOR SCRAM ON HIGH REACTOR PRESSURE "At 0046 CST, River Bend Station experienced an automatic reactor scram on high reactor pressure. Initial indications are that the cause of the scram was an uncommanded closure of the #3 turbine control valve. "The plant is stable with reactor water level in the normal level band of 10-51 inches being maintained with feedwater and condensate. Reactor pressure is in the prescribed band of 500-1090 psig, being maintained with turbine bypass valves and steam line drains. "No injection systems were actuated either manually or automatically as a result of the event. "The reactor scrammed on a Reactor Pressure High scram signal. A Reactor Level 3 signal resulted from the normal post-scram water level response. All systems responded as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an automatic RPS actuation with the reactor critical." All control rods fully inserted. The Unit is in a normal shutdown electrical alignment. All control rods inserted properly and all systems functioned as designed. The licensee is investigating the cause of the event. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-11-10
53731 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-11-09 | 2018-11-09 18:51 | 2018-11-15 | AGREEMENT STATE REPORT - LOSS OF NUCLEAR MEDICINE MATERIALS DUE TO WILDFIRE The following was received via fax from the State of California: "A wild fire is burning in Butte County where the Feather River Hospital is located. This facility has a small Nuclear Medicine operation with radioactive materials permitted by 10 CFR 35.100, 200, and 300 (Ra-223 only). RHB [California Radiation Health Branch] has not received any notifications from this licensee (nor can the hospital be reached by telephone). Based on news reports, the extent of fire damage to the hospital may be severe. According to the previous inspection reports, the Nuclear Medicine Department should currently possess the following radioactive materials: two Co-57 flood sources (2.6 milliCuries and 2.1 milliCuries as of 11/9/18), and two Cs-137 check sources (96.9 microCuries and 16.7 microCuries as of 11/9/18). The California Department of Health-Radiologic Health Branch (CDPH-RHB) will be following up with the licensee once the area becomes accessible for inspection. This event report is being filed based on the general information that is known currently about the extent of the fire and damage in the town of Paradise, and will be updated as appropriate when more complete information becomes available." CA 5010 Number: 110918 * * * RETRACTION ON 11/15/2018 AT 1658 EST BY ROBERT GREGER TO MARK ABRAMOVITZ * * * The following retraction was received via e-mail: "A CA Department of Public Health-Radiologic Health Branch individual has accessed the fire devastated town of Paradise in northern CA, and has determined that the portion of the Feather River Hospital containing licensed radioactive material was undamaged in the recent wildfire. The radioactive sources were accounted for." Notified the R4DO (Haire) and NMSS (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-11-19
53730 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-11-09 | 2018-11-09 18:20 | 2018-11-15 | AGREEMENT STATE REPORT - LOSS OF PET RADIOACTIVE MATERIALS DUE TO WILDFIRE The following report was received from the State of California via email: "On 11/09/18, RSO [Radiation Safety Officer] at Alliance Healthcare Services contacted the California OES [Office of Emergency Services] to report possible loss of control of radioactive materials that are located in one of their mobile PET [Positron Emission Tomography] Coaches stationed at the Feather River Hospital in Paradise, CA, due to a wildfire. A huge wildfire is still burning and spreading in the area and the extent of the damage is unknown, although the town of Paradise is reported to have been evacuated and heavily damaged in the fire. The PET Coach is believed to have contained Cs-137 (210 microCuries), Ba-133 (260 microCuries), and Ge-68 (3 milliCuries). RHB [California Radiation Health Branch] will be following up with the licensee once the area becomes accessible for inspection. This event report is being filed on the information that is known now about the extent of the fire and damage, and will be updated as appropriate when more complete information becomes available." CA 5010 Number: 110918 * * * EVENT RETRACTED ON 11/15/2018 AT 1700 EST BY ROBERT GREGER TO MARK ABRAMOVITZ * * * The event is retracted via e-mail: "The CA licensee and Radiologic Health Branch personnel have accessed the fire devastated town of Paradise in northern CA, and have determined that the PET coach and its radioactive material contents were undamaged in the recent wildfire. The radioactive sources were accounted for." Notified the R4DO (Haire) and NMSS (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-11-19
53729 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2018-11-09 | 2018-11-09 17:10 | 2018-11-09 | AGREEMENT STATE REPORT - IRRADIATOR SOURCE RACK FAILS TO RETRACT The following was received via fax from the State of New York: "The New York State Department of Health (NYSDOH) was notified by the radiation safety officer (RSO) of Pall Hauppauge (C1935) that they had a source rack which did not retract completely leaving the source partially exposed for a period of time. Pall Hauppauge is licensed to possess Cobalt 60 in sealed source use in a Nordian International dry panoramic storage irradiator. "The RSO activated the radiation monitor remotely and confirmed elevated radiation readings. He indicated that he was able to raise the rack up and then lowered it down. This time it went completely down, resulting in the source being completely shielded. "According to [the RSO], at no time were any workers exposed or potentially exposed, since there was no access to the vault. All other systems worked properly. "[The RSO] indicated that they are conducting a root cause investigation. A written report will be forwarded to the Department." Incident Report#: NY-18-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2018-11-19
53728 | 0 | KARMANOS CANCER CENTER |  |  |  |  | 2018-11-09 | 2018-11-09 16:21 | 2018-11-09 | PATIENT UNDERDOSAGE DUE TO LOSS OF AIR SEAL INTEGRITY "Today, Nov 9, 2018 a medical event occurred at our facility in which 145.7 mCi of Lutathera Lutetium-177 was delivered out of the prescribed 200 mCi. The full dose could not be delivered as there was loss of integrity of the air seal on the Lutathera vial." The licensee indicated the cause of the event was still under investigation and the Doctor and patient were informed of the issue. The licensee has not notified the Region III office. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-11-19
53727 | 0 | TILDEN MINING CO |  |  |  |  | 2018-11-09 | 2018-11-09 12:38 | 2018-11-09 | STUCK OPEN SHUTTER ON PROCESS GAUGE "In the process of performing the inventory/shutter check it was reported on November 09, 2018 at 1030 [EST] that our [Tilden Mining Co.] Kay Ray Model #7050, Serial #1412, 200mCi, Cs-137 gauge located on 6B DTU (Deslime Thickener U/Flow) in the deslime basement had a broken handle on the shutter mechanism, rendering the shutter non-operable. Work order (1836130) was entered into Ellipse. It was determined that the area in which the gauge is located does not create an exposure hazard. "The plant process requires the shutter to remain in the open position during normal operation and does not create a hazard to individuals, the course of action will be to remove and replace the gauge at the first opportunity. Once the gauge is removed, it will be placed and locked in [a] cage. The gauge will be placed on top of the required amount of lead to remove any potential exposure hazard; surveys will be performed to confirm personal safety." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-11-19
53726 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-11-09 | 2018-11-09 12:21 | 2018-11-09 | AGREEMENT STATE REPORT - RADIOGRAPHERS EXPOSED TO UNSHIELDED SOURCE The following was received via email from the State of Colorado: "After changing film between exposures, the radiography crew went to expose the source and realized the source was still in the unshielded, collimated position. The crew retracted the source and checked their pocket dosimeters and found them to be off-scale. The survey meter was found to be in the 'off' position. Dosimeters were sent in for emergency processing. The camera was a 96 Ci, Ir-192, model QSA 880D." Incident Report #: CO 997-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-11-19
53725 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2018-11-08 | 2018-11-08 16:51 | 2018-11-08 | TECHNICAL SPECIFICATION VIOLATION - UNSECURED REACTOR LEFT UNATTENDED The following is a synopsis of a notification received from Reed College: The licensee made an official notification of a violation of technical specification (TS) 6.1.3 a 1 as well as TS 1, which defines the reactor as operating when it is not shutdown or secured. The Reactor Operator (RO) left the control room for approximately 30 seconds while the reactor was subcritical but not secured. Per the TS definition, the reactor is not secured if the reactor console key is in the console. The RO immediately returned to the control room and removed the key and ensured the reactor scrammed. The Senior Reactor Operator (SRO) was in the next room and was informed. Another SRO was in the control room but was not requalified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | OR | NPR | [5 empty] | 0 | 2018-11-08
53724 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-11-07 | 2018-11-08 16:19 | 2018-11-08 | AGREEMENT STATE REPORT - RESIDUAL CONTAMINATION FOUND DURING SOURCE EXCHANGE This report was received by the State of Illinois via e-mail: "Varian Medical Systems reported that during a routine [high dose rate] HDR source exchange on 11/7/18, at Hinsdale Hospital, IL, they found residual contamination on a wipe sample of the wire from the source being removed from the device. The wipe activity measured less than leak test limits of 0.005 microCurie and measured 7.87 cps (40 Bq) with background measuring 0.45 cps. The source and wire were removed from the device. The wire was wiped prior to shipment to return the source to Alpha Omega. The area was immediately cordoned off by the engineer. Varian assumes this is a contaminated particle on the wire and that the source itself is not leaking. The wire is wiped prior to shipment from Alpha Omega and if contaminated it should not have been installed in the field. The source activity is now approximately 4.0 Ci of lr-192. The investigation is ongoing by the licensee and Varian." Illinois Item Number: IL180039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-11-16
53723 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-08 | 2018-11-08 14:19 | 2018-11-08 | AGREEMENT STATE REPORT - STUCK SHUTTER This report was received by the State of Texas via e-mail: "On November 8, 2018, the Agency [Texas Department of State Health Services] received notification from a licensee's radiation safety officer that a gauge was found in the stuck open position on a blender truck at a well site. The gauge was checked and the shutter arm was broken off. The shutter was adjusted into the closed position and removed from the truck. The gauge is in storage until repaired. Another gauge was mounted to the truck. The gauge was manufactured by Berthold, model 8010, serial 12097, with source serial number 0108/12, isotope Cs-137, activity 20 mCi. The gauge will be sent to the manufacture for repair. No exposures were reported or expected from the position the gauge was mounted and used during the frac operation. Update will be sent in accordance with SA-300." Texas Incident #: I-9633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-11-16
53722 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-08 | 2018-11-08 13:07 | 2018-11-08 | AGREEMENT STATE REPORT - STUCK SHUTTER This report was received by the State of Texas via e-mail: "On November 8, 2018, the Agency [Texas Department of State Health Services] was notified by the radiation safety officer that a gauge used to calibrate Agency equipment had a stuck shutter. The Agency owns the gauge and it is not listed under a license. The port was stuck in the closed position. It did not and does not pose a health risk or exposure to individuals/public. The gauge is manufactured by JL Shepherd, Calibrator Model 28-6A SN:10239, 120 mCi Cs-[137] source. A service company has been contacted to schedule repairs. Additional information will provided in accordance with SA 300." Texas Incident #: I-9632. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-11-16
53721 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-06 | 2018-11-08 12:19 | 2018-11-08 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received via email from the State of Texas: "On November 6, 2018, the licensee notified the Agency [Texas Department of State Health Services] that one of its Troxler model 3411 moisture/density gauges had been damaged at a temporary work site. The gauge contains an 8 milliCurie Cesium - 137 source and a 40 milliCurie Americium source. The initial report stated the casing and electronics were damaged but the shielding and insertion rod were not damaged. "The licensee's Radiation Safety Officer (RSO) stated that at approximately 1430 [CST] on November 6, 2018, one of their technicians was working at a temporary job site. He had left the Troxler model 3411 moisture/density gauge on the ground about 10 feet behind him while he was preparing the test hole. A front end loader came into the area and struck the gauge with its back tire. The outer casing/shell of the device was broken as were the electronics. The source had been inside the gauge at the time. The insertion rod did not appear to be bent (didn't push it out to make sure), the shielding was not damaged, and survey did not detect any radiation above the same levels when sources are known to be fully shielded. The gauge was placed inside its transport case and transported to the licensee's facility for storage. The RSO stated the gauge would be taken to the service company for repair or disposal. "On November 7, 2018, the Agency contacted the RSO and requested a picture of the device. The Agency received the pictures later that day. The Agency reviewed the pictures and the insertion rod for the cesium source appeared to have a slight bend in it. The Agency sent an e-mail request to the RSO and asked if the rod was operable. "On November 8, 2018, the RSO responded to the Agency and stated they had not operated the source rod and he believed it would not be operable because of a slight curving bend in the operating rod. The gauge is still in storage at the licensee's location. The Agency will not ask the licensee to try and operate the rod as there is the risk that the source could get stuck in an unshielded position. "Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-11-16
53720 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-11-01 | 2018-11-07 15:44 | 2018-11-07 | AGREEMENT STATE REPORT - MISADMINISTRATION DUE TO BATCH ERROR The following information was received by the State of Florida: "At noon [on 11/7/18], [Akumin] called [the State of FL Bureau of Radiation Control] to report that both Akumin Hollywood and Akumin Aventura View ordered F-18 Fluciclovine, and received packages that were labeled as F-18 Fluciclovine, but were subsequently notified by their radiopharmaceutical vendor PET NET Solutions-Ft Lauderdale, on Thursday, November 1, 2018 that due to a 'batch error,' the packages actually contained F-18 FDG [Fludeoxyglucose]." Three patients were reported as receiving the incorrect radiopharmaceutical. Activity reported as approximately 10 mCi. Florida Incident: FL18-137 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-11-15
53719 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2018-11-06 | 2018-11-07 17:28 | 2018-11-07 | AGREEMENT STATE REPORT - GAUGE LOST AND THEN FOUND The following information was received from the Commonwealth of Kentucky by email: "On 11/6/2018, a former licensee [formerly licensed as Wickliffe Paper Co.] reported discovery of a nuclear gauging device (TN [Texas Nuclear] model 5036 originally containing 200 mCi assayed 12/94) that it was unaware it possessed. The license was terminated on August 9, 2016 and at that time, the former licensee provided information related to the disposition of all devices the licensee was aware it possessed. License termination was due to plant closure. During engineering surveys to assess plant conditions for restart, personnel discovered the device still mounted on plant equipment. The former licensee is taking steps to have the device transferred to a licensed manufacturer for disposal. There is no reason to believe any individuals received any exposure at levels which would exceed the regulatory limits." Kentucky Event: KY180004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2018-11-15
53718 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-11-07 | 2018-11-07 14:49 | 2018-11-07 | AGREEMENT STATE REPORT - DAMAGED DENSITY GAUGE The following was received via email from Texas Department of State Health Services: "On November 7th, 2018, the Agency [Texas Department Of State Health Services] was notified by the licensee's radiation safety officer that a moisture density gauge was damaged by heavy equipment [at a construction site in San Antonio, TX]. The gauge was manufactured by Troxler, serial number 38348, with Cs-137 (S/N:77-5682) and Am-241:Be (S/N:47-8792) sources of 8 mCi and 40 mCi respectively. The technician was operating the gauge at a construction site and a heavy equipment operator failed to notice the technicians attempts to stop him, and subsequently ran the gauge over. The source rod remained intact, however it could not be retracted into the shielded position. The licensee contacted the manufacturer and received shielding instructions. The gauge and the soil surrounding it were removed and transported to the licensee's office. The gauge will be sent back to Troxler for repair in an approved type package. No overexposures to the technician or to the public were reported." Texas Incident #: I-9631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-11-15
53717 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-11-05 | 2018-11-05 15:38 | 2018-11-05 | OFFSITE NOTIFICATION DUE TO CHEMICAL SPILL OFFSITE "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) which requires notification to the NRC of notifications made to other government agencies. "On November 3, 2018, a Fyrquel hydraulic fluid leak was discovered at the plant's intake structure (on the Missouri River). The leakage was initially believed to have only flowed into the sump located at the lower level of the intake structure. On November 5, 2018, during subsequent investigation, plant staff recovered approximately 40 gallons from the sump. Approximately 200 gallons of hydraulic fluid could not be accounted for, so it was assumed to be released to the Missouri River. The leak was either caused by the hydraulic fluid being pumped to the stilling chamber, which drained to the river before operators were able to secure the intake pumps, or by leakage from hydraulic lines located near the free discharge valve, which would have then been carried by water leaking from piping associated with the free discharge valve into the stilling chamber (and then to the river). "The Environmental Protection Agency (EPA), Unites States Coast Guard National Response Center (NRC), and Missouri Department of Natural Resources (DNR) were notified on November 5, 2018. "The NRC Senior Resident Inspector has been notified by the licensee." The licensee confirmed that this leakage was above the reportable quantity. Notified EPA, USDA, and FEMA. Notified DOE and HHS via e-mail. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-11-05
53716 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-11-02 | 2018-11-05 11:26 | 2018-11-05 | AGREEMENT STATE REPORT - LOST STATIC ELIMINATORS The following information was received via email: "When conducting the annual reconciliation, Karcher North America, INC. reported eleven lost static eliminators. "Static Eliminators: Model: P-2021 8101. Isotope/units: PO-210, 10 mCi ea. Serial Numbers: A2JZ217, A2KH719, A2CP799, A2DM543, A2DT589, A2DU443, A2DU444, A2EZ668, A2GS233, A2JD061, A2JD062." Colorado Event Report ID No.: CO180027 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-11-13
53715 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-11-04 | 2018-11-05 11:30 | 2018-11-06 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE-DENSITY GAUGE The following information was received from the State of Florida via e-mail: "[The Licensee Operations Manager ] called [the Florida Bureau of Radiation Control] to report a Troxler gauge theft from the truck of [an operator]. The gauge was noted missing from the back of [the operator's] truck on Sunday, November 4, 2018. The Incident was reported to this office [Florida Bureau of Radiation Control] on November 5, 2018 at 1030 EST. [The Licensee Operations Manager] plans to call local law enforcement to report the theft. At the time of this report, [the Licensee Operations Manager] could not furnish [the operator's] residential address." The gauge contained an 8 mCi Cs-137 source and a 40 mCi Am-241/Be source. Florida Incident Number: FL18-136 * * * UPDATE FROM MARK SEIDENSTICKER TO TOM KENDZIA AT 1050 EST ON 11/6/2018 * * * The following information was reported via phone: The Florida Bureau of Radiation Control was informed that the Troxler gauge has been found. They have no other information at this time. Notified R1DO (WERKHEISER), ILTAB (via E-mail), and NMSS Events Notifications E-mail group. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-11-13
53714 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-11-03 | 2018-11-04 21:35 | 2018-12-06 | AGREEMENT STATE REPORT - DAMAGED DENSITY GAUGE The following report was received from the Washington State Department of Health via email: "On 11/3/2018, a gauge user was working at a jobsite located in Kirkland, Washington. He sat the gauge down and moved approximately 30 feet away to speak to a contractor. While the gauge was out of his direct control, it was hit by a piece of heavy equipment and damaged. The contractor took the gauge back to the Redmond office, secured it in the gauge storage room, and notified the office ARSO [Assistant Radiation Safety Officer] and corporate RSO [Radiation Safety Officer]. The ARSO, notified DOH [Washington State Department of Health] that evening. [The Washington State Department of Health Laboratory Program Manager] spoke with [the ARSO] to get an overview of the incident. "[The DOH Laboratory Program Manager] met with the ARSO and the corporate RSO, at the Redmond office at 0930 PST on 11/4/2018 to examine the gauge (CPN MC1DRP S/N MD00805859) to determine whether the Cs-137 and Am-241 sources had been compromised. After performing swab tests of the interior and exterior of the gauge and measuring the exposure rates around the gauge, [The DOH Laboratory Program Manager] made the assumption that the sealed sources were not compromised (the licensee couldn't do this because they don't have a survey instrument). [The DOH Laboratory Program Manager] also surveyed the vehicle used to transport the damaged gauge to verify that there was no detectable contamination in the vehicle. "DOH will conduct an investigation into the incident, and the licensee is submitting an incident report. More information to follow." Event Report ID: WA-18-027 * * * UPDATE AT 1229 EST ON 12/5/2018 FROM ANDREW HALLORAN TO MARK ABRAMOVITZ * * * The following update was received via e-mail: "DOH [Washington State Department of Health] conducted an investigation and a review of the licensee's internal incident report and root cause analysis. The gauge user did not maintain direct control of the gauge, resulting in the gauge being left unattended when it was damaged by an excavator. Additionally, the licensee failed to follow both the emergency procedures and radiation safety program guidance included in their radioactive materials license application renewal, further compounding the health and safety issues. Instead of securing the area and remaining onsite and alerting DOH as required by procedure, the gauge user and project manager decided to remove the damaged gauge and return it to the Redmond storage location. Both the failure to maintain control of the gauge and the failure to follow the emergency procedures were cited as violations in a compliance letter sent to GeoEngineers. In addition to the corrective actions required by the compliance letter, DOH will also perform a follow-up inspection of the Redmond office and field site." This event was closed on 12/5/2018. Notified the R4DO (Gaddy) and NMSS (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-11-12
53713 | 0 | TILDEN MINING CO |  |  |  |  | 2015-03-19 | 2018-11-02 13:20 | 2018-11-02 | PROCESS GAUGE SHUTTER STUCK OPEN "In the process of performing the inventory/shutter check it was reported on March 19, 2015 that our Kay Ray Model Number: 7050, Serial Number: 1405, 200 mCi, Cs-137 gauge located on 4B DTU (Deslime Thickener U/Flow) in the deslime basement had a broken handle on the shutter mechanism, rendering the shutter non-operable. Work order (1545064) was entered into Ellipse. It was determined that the area in which the gauge is located does not create an exposure hazard. "The plant process requires the shutter to remain in the open position during normal operation and does not create a hazard to individuals, the course of action will be to remove and replace the gauge at the first opportunity. Once the gauge is removed, it will be placed and locked in the cage located in the warehouse. The gauge will be placed on top of the required amount of lead to remove any potential exposure hazard; surveys will be performed to confirm personnel safety." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-11-12
53712 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2018-11-01 13:00 | 2018-11-01 20:10 | 2018-12-28 | UNANALYZED CONDITION DUE TO MODIFICATION NOT ADDED TO PROCEDURE "On November 1, 2018, at approximately 1300 EDT, Fermi 2 identified that a Station Blackout (SBO) procedure was deficient as a result of a modification installed during a recent refueling outage. A review identified that the performance of the SBO procedure could have resulted in a challenge to having an alternate AC source available within one hour as outlined in the Updated Final Safety Analysis Report (UFSAR) 8.4.2. The alternate AC source was always available to be manually aligned in accordance with other standard operating procedures. The modification did not affect the function for Appendix R alternative shutdown. "Immediate actions are underway to revise the impacted procedure. The health and safety of the public was not affected as offsite power has remained available since the modification was installed. Investigation into the cause and corrective actions is ongoing. "Fermi 2 is reporting this event as an unanalyzed condition pursuant to the requirements of 10 CFR 50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 12/28/18 AT 1228 EST FROM JEFFREY MYERS TO JEFFREY WHITED * * * "The purpose of this notification is to retract a previous report made on November 1, 2018 (EN 53712) under 10 CFR 50.72(b)(3)(ii)(B). Subsequent to the initial notification, the event, site procedures, and the NRC guidance in NUREG-1022 pertaining to 10 CFR 50.72(b)(3)(ii)(B) were reviewed further. The evaluation determined that at the time of the event, there were multiple methods defined in existing station procedures to establish an available alternate AC source within one hour as outlined in the Updated Final Safety Analysis Report (UFSAR) 8.4.2. "Under these circumstances, the event does not represent an unanalyzed condition under 10 CFR 50.72(b)(3)(ii)(B). Therefore, EN 53712 can be retracted and no Licensee Event Report (LER) under 10 CFR 50.73(a)(2)(ii)(B) is required to be submitted. "The licensee has notified the NRC Resident Inspector." Notified R3DO (Riemer). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-11-01
53711 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-11-01 | 2018-11-01 15:38 | 2018-11-01 | DISCOVERY OF INDICATIONS THAT DID NOT MEET ACCEPTANCE CRITERIA ON ONE REACTOR VESSEL HEAD PENETRATION "On 11/01/2018, during the Beaver Valley Power Station Unit No. 2 (BVPS-2) refueling outage, while performing examinations of the 66 reactor vessel head penetrations, it was determined that one penetration could not be dispositioned as acceptable per ASME Code Section XI. Penetration 27 will require repair prior to returning the vessel head to service. The indication was not through wall and there was no evidence of leakage based on inspections performed on the top of the reactor vessel head. The examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) and ASME Code Case N-729-4 to find potential flaws/indications before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. The other 65 penetrations will be examined during the 2R20 [current] refueling outage. "The plant is currently shutdown and in Undefined Mode. The reactor vessel head is not currently installed. Repairs are currently being planned and will be completed prior to startup. "This is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A) since the as-found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-4 to remain in-service without repair. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-11-01
53710 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-10-31 | 2018-11-01 15:33 | 2018-11-01 | AGREEMENT STATE REPORT - LEVEL GAUGE SHUTTER MALFUNCTION The following was reported by the Louisiana Department of Environmental Quality via email: "On 10/31/2018, Eagle US 2 was performing their semiannual inventory and operational checks of their RAM [radioactive material] licensed devices. During their routine semiannual maintenance checks, the shutter malfunction was discovered. The gauge shutter would not close due to a shutter pin sheer. "Eagle US 2 called a service contractor, BBP Sales, [to] perform the semiannual checks. BBP Sales is evaluating the situation to determine the best course of action to correct the problem. [The contractor] was unable to close the shutter and will determine the course of corrective action. It appears the corrective action will be to replace the device. The cause appears to be the conditions of a corrosive environment where the gauge is installed and used. "The sources and device with a broken shutter pin and shutter stuck open will remain installed and utilized on the process until the repairs are made. This is not a radiation exposure hazard and does not pose a health and safety situation for the Eagle US 2 employees or the general public. "The Gauge is a RONAN SA1-C-10 device/source holder, S/N 5977-GK, loaded with a 5 mCi Cs-137 source." Event Report ID No.: LA-180018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-11-09
53709 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-10-31 | 2018-11-01 10:26 | 2018-11-01 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following information was obtained from the State of Tennessee via email: "On 10/31/18, while performing radiography work in Nashville, TN, a radiographer working for World Testing noticed that his survey meter still had elevated readings and that the source had not successfully returned back to the camera. He attempted again to return the source but was unsuccessful. The [Radiation Safety Officer] RSO was notified. After responding and investigating, the RSO was able to retract the source back into the camera. The device information includes the following: "Manufacturer: USA Global Model #: A424-9 Serial #: 9269 Source Serial #: 65744G Isotope: Ir-192 (20.1 Ci) "A follow-up report will be submitted within 30 days." Tennessee State Event Report ID No.: TN-18-197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-11-09
53708 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2018-10-05 | 2018-10-31 17:05 | 2018-10-31 | PART 21 NOTIFICATION - FISHER DIGITAL VALVE CONTROLLERS 6000/6200 SERIES NOT ENVIRONMENTALLY QUALIFIED The following information is summarized from information received from Fisher Valves via email: A customer ordered a replacement digital valve controller. When the original controller was purchased, documentation indicated that it was qualified under IEEE 323-1974. The DVC6000 series and the DVC6200 series are not qualified in accordance with IEEE 323, nor was there any intent to qualify these devices to this standard. The only customer that has requested Environmentally Qualified controllers is Seabrook Station. Fisher requests that the recipient of this FIN review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questions, please contact: Jacob Clos Quality Manager Emerson Automation Solutions Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Phone: (641) 754-2108 Jacob.Clos@Emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-10-31
53707 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-08-13 | 2018-10-31 15:57 | 2018-10-31 | AGREEMENT STATE REPORT - LOST AMERICIUM-241 SOURCE The following information was obtained from the State of Tennessee via email: "On 10/31/18, the Tennessee Division of Radiological Health was contacted via phone by Ludlum Measurements RSO regarding the loss of a licensed source. It appears the source was last seen on 8/10/18. The licensee realized the source was missing on 8/13/18. The licensee has been searching for the source from 8/13/18 to date. The whereabouts of the source are still unknown at this time. "Isotope and activity: Am-241, 1.057911 microCi Manufacturer: Eckert and Ziegler Model and Source Serial #: 1637-72-2 "A follow-up report will be submitted within 30 days." Tennessee State Event Report ID No.: TN-18-195 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-11-08
53706 | 0 | PACE ANALYTICAL SERVICES |  |  |  |  | 2018-10-01 | 2018-10-31 10:18 | 2018-10-31 | MISSING ELECTRON CAPTURE DEVICES The following was received via email: "Specific Location Information Where Incident Occurred: Pace Analytical Services, Beaver-WV Environmental Laboratory "Incident, Amount: In [Pace's] inventory, [Pace] had six spare Agilent ECDs [Electron Capture Devices]. [Pace] believes they were accidentally placed in the trash for disposal and were subsequently placed in the local landfill. The ECDs have a sealed source with approximately 15 milliCuries of Nickel 63 each. These were the ECDs only and not the entire instrument, Gas Chromatograph (GC). "ECDs / Models: F6470 / 19233 F6526 / 19233 L2643 / 19233 L7189 / 19233 F4602 / 19233 F6242 / 19233 "Date of Lost/Misplaced ECDs, Last Time Seen: Identified as missing October 1, 2018. Confirmed to be missing October 3, 2018 Last seen September 26, 2018. Believed to be placed in the laboratory trash September 26th-29th, 2018. "Root Cause: During a clean-up/lean event employees were going through the lab and reorganizing/disposing of unneeded materials. The six ECDs were used as reserves for GC instrumentation and placed in a bag in efforts to not dispose of them. At some point later in the week, it is believed that either an employee or cleaning person mistook the bag as garbage and threw them away. "Measures to Recover: Upon discovering the lost ECDs, Pace contacted the trash hauler - Raleigh County Solid Waste Authority. They stated that, due to the length of time that has passed since disposal, the likelihood of recovery is essentially zero. Due to the process of filling hollow-like areas, anything disposed has approximately 20 feet of additional material over it, and they have no way of knowing where the truck would have dumped the materials." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2018-11-08
53705 | -1 | SSM HEALTH ST. MARY'S HOSPITAL |  |  |  |  | 2018-10-30 | 2018-10-30 16:33 | 2018-10-31 | MISSING LICENSED MATERIAL Replacement camera sources were properly delivered by the common carrier to St. Mary's Hospital located in Jefferson City, Missouri. The sources were received by the Biomed Hospital Imaging Specialist and placed in the biomed office. Currently, the package containing the sources is missing. The licensee investigation continues. Sources are two Gd-153 (10 mCi each) and two Co-57 (0.5 microCi each). * * * RETRACTION ON 10/31/2018 AT 1425 EDT FROM KEN WOHLT TO ANDREW WAUGH * * * This event is being retracted. The sources were discovered to be delivered to SSM Hospital's biomed office instead of nuclear medicine. The sources were secured and in control of the SSM Hospital at all times. There were no exposures to personnel. The licensee notified NRC Region 3 (Warren). Notified R3DO (Stoedter) and NMSS Events Notification and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2018-11-07
53704 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2018-10-29 | 2018-10-29 18:53 | 2018-10-29 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was excerpted from an email received from the State of Nevada: On October 29, 2018 Round Mountain Gold Corporation reported a high wall failure that led to the collapse of an entire section of a mine. No one was hurt in the incident. The wall was being monitored for failure and the Mine Safety and Health Administration was at the mine two weeks ago. A Cs-137 fixed gauge of approximately 26.7 mCi was damaged in the incident. The gauge is in the unshielded position and cannot be recovered at this time due to industrial safety concerns. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2018-11-06
53703 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2018-10-29 | 2018-10-29 16:47 | 2018-10-29 | MANUAL REACTOR TRIP DUE TO INADEQUATE FEEDWATER FLOW "On October 29, 2018 at 1317 EDT, with St. Lucie Unit 1 in Mode 1 at 100% power, the reactor was manually tripped due to inadequate feedwater flow to both 1A and 1B Steam Generators (S/Gs). The trip was uncomplicated with all systems responding normally post-trip. [All control rods fully inserted and there were no specified system actuations.] Operators responded and stabilized the plant in Mode 3. The cause of the inadequate feed flow to the 1A and 1B Steam Generators is currently under investigation. "Decay Heat removal is being accomplished through forced circulation with stable conditions from Main Feedwater and the Steam Bypass Control System to the Main Condenser. Currently maintaining Pressurizer pressure at 2250 psia and Reactor Coolant System temperature at 532 degrees F. "St. Lucie Unit 2 was unaffected and remains in Mode 1 at 100% power. "This report is submitted in accordance with 10CFR50.72(b)(2)(iv)(B) for the reactor trip. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-10-29
53702 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2018-10-29 | 2018-10-29 12:56 | 2018-10-29 | OFFSITE NOTIFICATION OF NON- WORK RELATED FATALITY "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "At approximately 03:30 MST on October 29, 2018, an Arizona Public Service Company (APS) employee developed a personal medical condition in the Owner Controlled Area outside of the Secured Owner Controlled Area at Palo Verde Generation Station (PVGS). PVGS Emergency Medical Technicians responded and transported the individual to an offsite emergency trauma center. Upon arrival at the trauma center, medical personnel declared the individual deceased at approximately 05:35 MST. "The fatality was not work related and the individual was outside of the Radiological Controlled Area and no radioactive material or contamination was involved. "No news release by APS is planned. Notifications were made to the Arizona Division of Occupational Safety and Health at 08:15 MST. "The NRC Resident Inspectors have been notified." | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Defueled | Power Operation | Power Operation | Defueled | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-10-29
53701 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2018-10-28 | 2018-10-29 10:48 | 2018-11-01 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following was received via email from the Commonwealth of Massachusetts: "Massachusetts Radiation Control Program was notified this morning by S.W. Cole Engineering (MA Radioactive Materials License 48-0689) of Taunton, MA, that InstroTek Model 3500 Xplorer Series portable moisture density gauge, containing 11 mCi Cs-137 and 44 mCi Am-241, was stolen yesterday (Sunday, 28 October 2018) from a temporary job site in Fall River, MA. "Local Police, State Police and FBI have been notified." * * * UPDATE FROM JACK PRIEST TO HOWIE CROUCH AT 2248 EDT ON 11/1/18 * * * Notified by the Commonwealth of Massachusetts that at 2130 EDT on 11/1/18, the Commonwealth was notified by the FBI that the subject gauge was recovered during the course of a criminal investigation. The gauge is currently in the possession of the Swansea, MA Police Department. The Commonwealth will coordinate with the licensee to take possession of the gauge on 11/2/18. The gauge appears to be undamaged and there is no evidence of tampering. The licensee will be conducting a leak check and inspection of the gauge once they regain possession. Notified R1DO (Schroeder), ILTAB (Davis), and NMSS Events Notification (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2018-11-06
53700 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-10-28 | 2018-10-28 21:44 | 2018-10-28 | SEISMIC MONITORING PANEL SYSTEM INOPERABLE "This event is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for a major loss of emergency assessment capability at the Prairie Island Nuclear Generating Plant. "At 1435 CDT on October 28, 2018, troubleshooting of the Seismic Monitoring Panel resulting from the receipt of Control Room annunciator 47023-0603 (Seismic Monitor Panel) determined that the '[Operational Basis Earthquake] OBE Exceedance' alarm on the Seismic Monitoring Panel will not alarm and determined the panel is non-functional. "The Seismic Monitoring Panel system functions to provide indication that the OBE threshold has been exceeded following a seismic event and is used in the Prairie Island Nuclear Generating Plant Emergency Plan to perform classification of Initiating Condition 'Seismic event greater than OBE levels' and Emergency Action Level HU2.1. "Station personnel are monitoring the seismic recorders for event alarms on a 15 minute frequency due to alarm function failure. The station is developing repair plans for restoration of the alarm function. "This event does not adversely affect the safe operation of the plant or health and safety of the public. "The licensee has notified the NRC Resident Inspector." | 29 | 100 | 0 | 29 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-10-28
53699 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2018-10-28 | 2018-10-28 15:10 | 2018-10-28 | NON ESSENTIAL SERVICE WATER INOPERABLE "During the performance of Service Water Essential header swap, SWN-6 (Supply to Turbine Building Oil Coolers) valve stem became disconnected from its gear box at 85% open and could not be operated. Therefore, the non-essential service water system was inoperable. LCO 3.0.3 was entered at 0930 [EDT] with required actions to be in Mode 3 in 7 hours, Mode 4 in 13 hours and Mode 5 in 37 hours. Repair efforts were successful at shutting SWN-6, and LCO 3.0.3 was exited at 1305 [EDT] before adding any negative reactivity in support of shutdown. ('TS Required S/D' box not checked.) "This condition constituted a loss of safety function which requires an 8 hour report [in accordance with] IAW 50.72(b)(3)(v)(B): Without the ability to close SWN-6, the non-seismic portion of the conventional Service Water System could not be isolated as required in the event of either a seismic event or as required in the EOPs. The nonessential service water system is required to support the recirculation phase post [Design Basis Accident] DBA for accident mitigation." The licensee notified the NRC Resident Inspector and the State of New York. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | POT RHR INOP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(3)(v)(B) |  |  | 0 | 2018-10-28
53698 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2018-10-28 | 2018-10-28 08:57 | 2018-10-28 | AUTOMATIC REACTOR SCRAM DURING A REACTOR SHUTDOWN "At 0445 [CDT], with reactor power less than 1% rated thermal power on Instrument Range Monitor (IRM) ranges 6 and 7, Clinton Power Station received an automatic Reactor Protection System (RPS) actuation. The Reactor Scram Off Normal procedure was entered and all control rods were verified to be fully inserted. The apparent cause of the scram is cold water injection causing an upscale trip of the IRMs due to Motor Driven Reactor Feedwater Pump (MDRFP) Feedwater Regulating valve 1FW004 valve coming off the full shut seat momentarily. All systems responded appropriately following the scram and the plant is currently stable. Clinton Power Station will be proceeding to Mode 4 to support the planned Maintenance Outage. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-10-28
53697 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-10-27 | 2018-10-27 16:52 | 2018-10-27 | MANUAL REACTOR TRIP FOLLOWING STARTUP "On October 27, 2018, at 1533 EDT, Watts Bar Nuclear (WBN) Plant Unit 1 reactor was manually tripped due to a failure of the #3 Reactor Coolant Pump normal feeder breaker to close during the planned power transfer to unit power following startup. Concurrent with the reactor trip, the Auxiliary Feedwater system actuated as designed. "All Control and Shutdown rods fully inserted. [Main Steam Isolation Valves] MSIVs were required to be isolated due to cooldown. All safety systems responded as designed. The unit is currently stable in Mode 3, with decay heat removal via Auxiliary Feedwater and Steam Generator Atmospheric Dump Valves. Unit 1 is in a normal shutdown electrical alignment. "This reactor trip and system actuation is being reported under 10CFR 50.72(b)(3)(iv)(A) and 10CFR 50.72 (b)(2)(iv)(B). "There was no effect on WBN Unit 2. "The NRC Senior Resident has been notified." | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-10-27
53696 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2018-10-26 | 2018-10-27 01:50 | 2018-10-27 | AUTOMATIC START OF THE EMERGENCY DIESEL GENERATOR AND LOSS OF RADIATION MONITOR "RCS [Reactor Coolant System] Pressure: vented to containment, refueling cavity greater than 23ft. [above reactor vessel]. RCS temperature: 96 degrees Fahrenheit. "The 12A bus de-energized, 'A' EDG [Emergency Diesel Generator] automatically started and loaded on [emergency] buses 14 and 18. The RCS configuration is refueling cavity level greater than 23ft. above the reactor flange with no impact to shutdown cooling. "Radiation monitor R-1, Control Room radiation monitor, lost power for 2 hrs 10 min. This placed Ginna in a major loss of emergency preparedness capabilities. A temporary radiation monitor has been installed in the Control Room." Prior to the notification, the licensee had restored the 12A bus from offsite power and the R-1 monitor was re-energized. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(xiii) |  |  | 0 | 2018-10-27
53695 | 0 | UNIVERSITY OF MICHIGAN HOSPITAL |  |  |  |  | 2018-10-25 | 2018-10-26 12:11 | 2018-10-26 | MEDICAL EVENT - UNDERDOSE A patient was prescribed 200 mCi of Lutetium-177. Due to dose administration issues, a delivered dose of 135 mCi was received by the patient. The licensee notified the NRC Region 3 contact (Gattone). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-11-05
53694 | 0 | WAYNE STATE UNIVERSITY |  |  |  |  | 2017-06-08 | 2018-10-26 09:59 | 2018-10-26 | LOST DEVICE On 10/18/18, the licensee identified a Liquid Scintillation Counter missing during an inventory. The Radiation Safety Officer believes the device was disposed of as electronic waste on 6/8/2017. A Wallac Liquid Scintillation Counter contains a 10 microCurie Ra-226 source. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-11-05
53693 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2018-10-24 | 2018-10-24 17:45 | 2018-10-24 | 1/2 EDG AUTO STARTED AND LPCI/CORE SPRAY INOPERABLE DUE TO LOSS OF SAFETY BUS "On October 24, 2018 at 0901 CDT, during performance of the 'Functional Test of Unit 1 Second Level Undervoltage,' a loss of Bus 13-1 and Bus 18 occurred. The 1/2 Emergency Diesel Generator (EDG) automatically started due to a valid actuation on loss of power to Bus 13-1, but did not load due to required testing alignment. "The loss of Bus 13-1 caused the loss of the 1A loop of Core Spray, both loops of Low Pressure Coolant Injection (LPCI), and Bus 18. All equipment responded as expected. "Bus 13-1 and Bus 18 were restored at 0911[CDT] on 10/24/18. Other affected systems are in the process of being restored. An investigation as to the cause of the event has been initiated. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(iv), 'Event or Condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B),' because the 1/2 EDG auto started due to the loss of power condition. "This notification is also being made in accordance with 10 CFR 50.72(b)(3)(v)(B), 'Event or Condition that Could Have Prevented Fulfillment of a Safety Function,' because both loops of LPCI were inoperable for a short time period." During the ten minutes where LPCI was unavailable, Unit 1 was in Technical Specification LCO 3.0.3. Unit 1 is currently in LCO 3.8.1(b) until the EDG is restored. Unit 2 was not affected by this event. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | POT RHR INOP |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2018-10-24
53692 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2018-10-23 | 2018-10-24 10:45 | 2018-10-24 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following was received from the State of New Jersey via email: "A reciprocity licensee informed [New Jersey Department of Environmental Protection Radioactive Materials Program] that during a routine preventive maintenance and source exchange of a [high dose rate] HDR unit at a hospital, the sealed Ir-192 source was found to be leaking. Upon discovery of the leakage, the source exchange was halted. The sealed source is a model 105.002 Ir-192 source manufactured by Alpha Omega Services, Inc. for use in an Elekta HDR microSelectron model 106.990, serial number 10362. "The wipe test revealed the presence of 190 Bq on the check cable and 183 Bq on the source cable. Checks of the transfer tubes were within regulatory limits. Checks on the applicators used and the indexer cap are being conducted. The source is secured in its shielded position within the HDR unit. Exposure levels are normal for a shielded source. The unit itself is secured in its routine storage location. There are no HDR patient treatments scheduled for the next two weeks. This should be sufficient time for the levels of contamination to decay to below regulatory limits. At that time, the source exchange will proceed. "A phone call and follow-up e-mail was made to the State of New Jersey Department of Environmental Protection's Bureau of Environmental Radiation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2018-11-01
53691 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-10-23 | 2018-10-23 19:24 | 2018-10-23 | NOTIFICATION OF ENVIRONMENTAL REPORT TO ANOTHER GOVERNMENT AGENCY "At 1616 EDT on 10/23/18, Salem reported to the New Jersey Department of Environmental Protection a sheen on ground water discovered during excavation in the Salem Switchyard. This discovery did not violate any NRC regulations or reporting criteria. This notification is being made solely as a four-hour, non-emergency notification for a Notification of Other Government Agency. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel." The licensee notified the NRC Resident Inspector and will notify Lower Alloway Creek Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-10-23
53690 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-10-23 | 2018-10-23 15:43 | 2018-10-23 | OFFSITE NOTIFICATION TO OSHA DUE TO SUPPLEMENTAL EMPLOYEE FATALITY "On October 23, 2018 at 1510 EDT, a notification to OSHA (Occupational Safety and Health Administration) was initiated due to a supplemental employee experiencing a non-work related medical event that resulted in the supplemental employee passing. When the issue was identified, the station first aid team responded to administer first aid. The supplemental employee was transported to a local hospital for additional medical support. Subsequent to the employee passing, a report was made to OSHA in accordance with federal requirements. This event is reportable to the NRC per 10 CFR 50.72(b)(2)(xi) since another governmental agency was notified of this employer medical event. "The supplemental employee was in a building within the owner controlled area and was not contaminated. "The licensee notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-10-23
53689 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-10-22 | 2018-10-23 12:39 | 2018-10-23 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received from the State of Texas by email: "On October 23, 2018, [a report was received by the Texas Department of State Health Services that] a consulting company servicing the equipment for a licensee found during a maintenance operation that a gauge had a stuck shutter on October 22, 2018. The device is labeled Vega, SH-F1A, 20 mCi, Cesium-137, Source Serial number 5786CN. The gauge measures vessel material levels and is mounted about 10 feet above ground level. No risk of radiation exposure to members of the public or radiation workers at the location. The gauge shutter is stuck in the open operating position. A repair company was called to contract an inspection to repair or replace the gauge. An update will be provided as information is obtained." Texas Incident #: 9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-10-31
53688 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2018-10-22 | 2018-10-23 04:17 | 2018-10-23 | INOPERABLE CONTROL ROOM ENVELOPE DUE TO FAILED SURVEILLANCE "On October 22, 2018 at 2241 hrs. EDT, a loss of Control Room Envelope (CRE) was declared due to failing to meet the requirements of (surveillance requirement) SR 4.7.6.1h during 72-month surveillance testing. Measured in-leakage exceeded the SR acceptance value. "Abnormal Operating Procedure 2588A, 'Mitigating Actions for Control Room Envelope Boundary Breach', have been implemented." The licensee has notified Connecticut Department of Environmental Protection, Connecticut dispatch, Waterford dispatch, and the NRC Resident Inspector of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-10-23
53687 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2018-10-22 | 2018-10-22 16:24 | 2018-10-22 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the Commonwealth of Virginia by email: "On October 22, 2018, the RSO [Radiation Safety Officer] for the licensee reported an accident that morning at a construction site near Sterling, Virginia. A roller hit a portable moisture/density gauge with its rear wheels while backing up. The gauge user established an exclusionary area until the RSO arrived to perform an onsite investigation and radiation survey. The RSO reported the plastic housing of the gauge was cracked but the source rod and shielding were intact. Surveys indicated no unusual radiation levels. The licensee contacted a vendor to analyze leak test samples and to determine potential repairs to the gauge. "The gauge was a Troxler 3430, serial [number] 30198, with an 8 milliCurie Cs-137 source, serial [number] 750-2497, and a 40 milliCurie Am-241:Be source, serial [number] 47-27175." VA Event Report ID No.: VA-18-007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2018-10-30
53686 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-10-22 | 2018-10-22 15:27 | 2018-10-22 | AGREEMENT STATE REPORT - OVEREXPOSURE EVENT The following was received from the State of Louisiana via email: "On October 22, 2018 around 1000 CDT, Capitol Ultrasonics, L.L.C. was working at Exxon Refinery. Two industrial radiographers' pocket ion chambers went off scale while moving the source guide tube. Dose reconstruction indicated 743 mR whole body to one radiographer. The second radiographer received 294 mR whole body and 51 Rem extremity dose to the hands. "The industrial radiography camera being used was an 880D Amersham, serial number: D15404, with a source strength of 34.3 Ci of Ir-192, serial number: 66839G. "Body badges are being sent in for immediate processing at this time." Louisiana Event Report ID No.: LA20180017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-10-30
53685 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2018-10-22 | 2018-10-22 14:42 | 2018-11-09 | CONTROL ROOM ENVELOPE DECLARED INOPERABLE DUE TO DOOR LATCH FAILURE "At 0856 EDT on October 22, 2018, it was discovered that the Control Room Envelope, a single-train system, was inoperable due to failure of a boundary door to latch; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D) as a loss of safety function. The door latch was repaired, and the Control Room Envelope declared operable at 0910 EDT. "There was no impact on the health and safety of the public or plant personnel, as the door was capable of being closed at all times and the door was manned the entire time it could not latch. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 1510 EST ON 11/09/18 FROM NICK DOWNING TO OSSY FONT * * * "Retraction of Event #53685, Control Room Envelope Declared Inoperable due to Door Latch Failure "Based on subsequent field measurements taken for the boundary door, the force needed to open the unlatched door is sufficient to maintain the Control Room Envelope positive pressure. Therefore, the Control Room Envelope remained Operable with the boundary door unlatched, and this issue did not prevent the system from fulfilling its safety function to mitigate the consequences of an accident. "The NRC Resident Inspector has been notified." Notified the R3DO (Hanna). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-10-22
53684 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-10-20 | 2018-10-22 14:22 | 2018-10-22 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following was received from the State of North Carolina by email: "On 10/20/18, at 1757 EDT, the office RSO [Radiation Safety Officer] received a call from a crew working a project at Kings Mountain Compressor Station in Kings Mt., NC. The qualified radiographer assigned is Technician 1, with assistant Technician 2. Upon exposure of a 3 inch weld, the source did not retract when attempting to secure the RAM to end exposure. The crew immediately verified and re-verified and secured boundaries and called the RSO as required by operating and emergency procedures. "The local RSO notified the CRSO [corporate RSO] of the event at 1803 EDT and proceeded to the site. [While] in route to the project site, Technician 4 was notified to go to the Charlotte office to get spare control cables for possible use in recovery operations. Upon arrival at approximately 1830 EDT, the RSO evaluated the site and boundaries and took action to move the source and collimator assembly to a better position to allow stacking of available sand bags in order to minimize boundary area for a more condensed and controllable area. During the movement of the exposure device, positive pressure was applied to the control to prevent the source from moving out of the collimator. Once the exposure device was positioned correctly, sand bags were placed over the source assembly to reduce exposure limits. During this operation, survey meters were used to verify radiation exposures. The radiation area was reduced to 30-35 feet. "A conversation with the CRSO and calls with additional Applus groups were made in order to identify the closest source recovery tools and equipment in order to attempt recovery of the source. "[Personnel] added another layer of area markings for control purposes. Contractor site personnel stayed clear of the area without issue during event. No exposure to the general public occurred. "The recovery kit arrived on site at approximately 1030 EDT, 10/21/18. After review of available equipment, a recovery plan was discussed. Dosimetry, equipment operation, and proper calibrations were verified. All dosimeter pencils were verified at zero at the beginning of the event and monitored at stages during recovery. Actions were broken down in order to balance and reduce exposure to each individual and modified as necessary during event. "The plan of action was to create a shielded dam with available lead shot and sand bags at the open end of the guide tube, with one bag directly in front of the tube to stop the source assembly at the most shielded position, with the others providing a shielded position for the capsule of the source assembly. The last sand bag on the collimator was left in position up until the last step. Two individuals were directed to quickly remove the last shielding bag while the other utilized an extended tong device to lift the collimator assembly directly upward to propel the source to the established dam of shielding. Survey meters were used to monitor this action to verify the source moved from the previous position to the created shielding dam. All dosimeter pencils were reviewed in order to determine who would be chosen to disconnect damaged connector and then another to make the connection to the functioning control cable. The first person pulled the connection out only far enough to disconnect the damaged connector. The second person performed the re-connection. The survey meter reading at the connection area was approximately 200 mR/hr during these steps. The time of exposure to perform these two events was estimated to be less than 30 seconds, which would have equaled approximately 1.6 mR of exposure to the hands of each individual. From the safe distance of the control cable, the source was retracted to the shielded position of the device and surveyed and secured. At this time, the exposure device and control cable have been returned to the office and tagged with damage tags so no one will use it." NC tracking number: 180043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-10-30
53683 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2018-10-20 | 2018-10-22 12:44 | 2018-10-22 | AGREEMENT STATE REPOT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the Commonwealth of Virginia by email: "On October 20, 2018, the representative of the Virginia Radioactive Materials Program (VRMP) received a telephone call from the licensee that the guide tube of a portable nuclear moisture/density gauge (CPN Model MC-1DRP, Serial number MD50507856) was damaged (bent) by a truck while performing testing at a temporary jobsite in Sterling, Virginia. The gauge contained 10 milliCuries of Cesium-137 and 50 milliCuries of Americium-241/Beryllium. The sources were in the shielded position and the shielding integrity was not damaged. The licensee performed a survey of the gauge and readings observed were between 0.2 and 0.3 mR/hr at three (3) feet distance from the gauge. "The gauge was put in its transport box and returned to the office. Wipe test samples were taken. Samples were sent to the North East Technical Services for analysis. Results are pending. The VRMP is currently working with the licensee to obtain additional information. This report will be updated when VRMP receives more information." VA Event Report ID No.: VA-18-006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2018-10-30
53682 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2018-09-11 | 2018-10-22 12:24 | 2018-10-22 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following was received from the State of New York by fax: "Terracon Consultants reported that a moisture/density gauge [Troxler model 3430P, serial #70428, containing 0.30 GBq (8 mCi) Cs137 and 1.48 GBq (40 mCi) Am-Be source] was damaged at a mass fill project in Rochester, NY. The source manufacturer and serial number are not yet available. "While at a mass fill project in Rochester, NY, a technician had completed a round of density testing and placed the gauge within a roped off area at the end of the fill area. He then walked to his truck approximately 100 feet away to get water. During that time, a 10-ton single drum roller moving in reverse headed towards the roped off area and gauge. The technician noticed the operator approaching the gauge as he walked back towards it and yelled and tried to gain the attention of the roller operator. The rear rubber tire of the roller impacted the side of the gauge and damaged the plastic covering. The technician cordoned off the area 15 feet around the gauge and surveyed the operator and roller. "The technician called their office manager and a regional manager (who happened to be in their office) and went to the site and surveyed the gauge and all parties/equipment involved and it did not appear that the gauge was leaking. The gauge was visually inspected for damage and it appeared that only the top case was damaged, the gauge was still operational, and the source rod was fully enclosed in the gauge. The gauge was returned to its transport case and returned to its permanent storage location in Rochester, NY. The gauge will be transported for repair and leak testing. "An internal root cause analysis and follow up training with the technician will be set in place with their corporate RSO [Radiation Safety Officer] in the next few days." NY EVENT REPORT ID NO. NY-18-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2018-10-30
53681 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-10-22 | 2018-10-22 10:39 | 2018-10-22 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2018-10-22
53680 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-10-21 | 2018-10-21 19:58 | 2018-10-21 | OFFSITE NOTIFICATION DUE TO DEATH OF EMPLOYEE ON SITE "This notification is being made due to the death of an employee on-site. A Security Officer was found unresponsive on the Turbine Building Moisture Separator Re-heater deck on the Unit 1 side. Upon arrival of Fire Operations and on-site medical the individual had suffered an apparent heart attack. Hamilton County Emergency Medical Services will be transferring the individual to the medical examiner's office. The on-site NRC Senior Resident Inspector has been notified." The licensee believes this event may receive media attention and a press release could be issued. | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-10-21
53679 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-10-20 | 2018-10-21 16:19 | 2018-10-21 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILURE TO RETRACT The following information was received via E-mail: "On October 20, 2018, the agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that one of its radiography crews was unable to return an 80 curie iridium-192 source to the fully shielded position in an INC IR 100 exposure device. The RSO stated that the event occurred near Pecos, Texas. The RSO stated that the radiographers had established a 2 millirem boundary. "An individual listed on their license responded to perform the source retrieval. The location where the event occurred was remote and the event did not present an exposure risk to any individual. The RSO stated that there are very few people at the site. "Once the individual who was sent to retrieve the source arrived, they inspected the exposure device and guide tube. The inspection discovered the radiographers had bent the guide tube to get it through some pipes and the angle of the bend was what had prevented the source from being retracted. The guide tube was straightened and the source was retracted to the fully shielded position at 2100 hours. The guide tube was inspected and did not have any damage. The RSO stated that no overexposures had occurred." Texas Incident Number: 9622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-10-29
53678 | -1 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-10-21 | 2018-10-21 06:19 | 2018-12-13 | TECHNICAL SPECIFICATION SHUT DOWN DUE TO CHEMISTRY LIMIT EXCEEDED "At 0200 Central Daylight Time on 10/21/2018, Browns Ferry Nuclear Plant Unit 3 commenced a reactor shutdown as required by the Technical Requirements Manual Limiting Condition for Operation 3.4.1 Coolant Chemistry Condition D due to conductivity greater than 10 micro mho/cm at 25 degrees Celsius. The required action for this condition is to immediately initiate an orderly shutdown and be in Mode 4 as rapidly as cooldown rate permits. This event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(i). "There was no impact on the health and safety of the public or plant personnel. The NRC Senior Resident Inspector has been notified." * * * RETRACTION AT 1719 EST ON 12/13/2018 FROM NEEL SHUKLA TO MARK ABRAMOVITZ * * * "ENS Event Number 53678, made on 10/21/18, is being retracted. "NRC notification 53678 was made to ensure that the four-hour non-emergency reporting requirements of 10 CFR 50.72 were met when the licensee discovered a condition requiring shut down of a reactor. "10 CFR 50.72 requires a report in accordance with 50.72(b)(2)(i) for any Technical Specifications (TS) required reactor shutdown. NUREG-1022 only specifies TS applicability and makes no mention of a Technical Requirements Manual (TRM) required shutdown. Because the shutdown comes from the TRM and not the TS as discussed in 10 CFR 50.72 and NUREG-1022, an EN was not required. "TVA's evaluation of this event notification is documented in the corrective action program. "The licensee notified the NRC Resident Inspector." Notified the R2DO (Ehrhardt). | 0 | 0 | 67 | 0 | 0 | 67 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2018-10-21
53677 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2018-10-19 | 2018-10-20 01:13 | 2018-10-20 | TURBINE STEAM SEAL HEADER PRESSURE MALFUNCTION "On 10/19/18 at 2202 EDT, at 19 [percent] Reactor power, a malfunction of [the] Turbine Steam Seal Header pressure control caused a loss of Condenser vacuum, resulting in an automatic trip of the Main Turbine and a manual reactor trip (RPS Actuation). Just prior to the reactor trip, Emergency Feedwater was manually initiated to mitigate the potential loss of Main Feedwater. Condenser vacuum was recovered after the reactor trip and Main Feedwater remained in operation. Due to the RPS actuation while critical, this event is being reported as a 4-hour non-emergency per 10CFR50.72(b)(2). Also, due to the manual initiation of Emergency Feedwater, this event is also being reported as an 8-hour non-emergency per 10CFR50.72(b)(3). "Following the reactor trip, all systems responded as expected with no complications. Emergency feedwater was secured at 2300. Unit 1 is in Mode 3 and stable, continuing to cooldown for a refueling outage." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-10-20
53676 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2018-10-19 | 2018-10-19 21:44 | 2018-10-19 | AUTOMATIC REACTOR TRIP DUE TO FEEDWATER REGULATING VALVE FAILING CLOSED "At 1725 CDT, a Feedwater Regulating valve failed closed, resulting in a reactor level transient, which initiated a reactor trip, Primary Containment Isolation System signals to valves in Groups 2, 3, and 4 and initiation of High Pressure Coolant Injection and Reactor Core Isolation Cooling. All control rods inserted and level has been restored to normal. The cause of the feedwater valve failure is under investigation. All other systems responded as expected. "This report is being made under 10 CFR 50.72 (b)(2)(iv)(B), (b)(3)(iv)(A) and (b)(2)(iv)(A). "The Senior Resident Inspector has been informed." Decay heat is being removed via the main condenser and reactor vessel water level is being maintained by the condensate and feedwater systems. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2018-10-19
53675 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2018-10-19 | 2018-10-19 12:04 | 2018-10-19 | POSTULATED HOT-SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "During extent of condition review of a previously identified fire induced hot-short (Ref. EN#53644) an unfused circuit associated with the 0M23C0002A, Miscellaneous Switchgear Recirculation Fan was discovered. This condition is not bounded by existing design and licensing documents. "This results in an unanalyzed condition due to the possibility for a postulated fire induced hot-short to cause a secondary fire in a different fire area, which would be outside the boundaries analyzed for safe shutdown in the Appendix R Evaluation, Safe Shutdown Capabilities Report, due to an unfused circuit. "Without overcurrent protection for this circuit, the potential exists that an initial fire event affecting this circuit could cause a short circuit that would cause excessive current through the circuit beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where this circuit is routed, challenging the ability to achieve and maintain safe shutdown. "The postulated event would affect multiple fire zones in the control complex. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Resident Inspector." * * * UPDATE ON 10/19/2018 AT 1454 EDT FROM EDWARD CONDO TO ANDREW WAUGH * * * "Further extent of condition reviews have discovered another unfused circuit. The circuitry is related to 0M24C001A, Battery Room Exhaust Fan. This condition is not bounded by existing design and licensing documents. "This results in an unanalyzed condition due to the possibility for a postulated fire induced hot-short to cause a secondary fire in a different fire area, which would be outside the boundaries analyzed for safe shutdown in the Appendix R Evaluation, Safe Shutdown Capabilities Report, due to an unfused circuit. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Senior Resident Inspector." Notified R3DO (Hills). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-10-19
53674 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-10-19 | 2018-10-19 10:00 | 2018-10-19 | LOW PRESSURE CORE INJECTION PUMPS INCAPABLE OF AUTOMATIC STARTUP "On 10/19/2018, at approximately 0400 EDT, during an investigation into a failed surveillance test for a Loss of Offsite Power (LOP) coincident with a Loss of Coolant Accident (LOCA), it was identified that the Engineered Safety System Bus degraded voltage relay scheme contained a time delay setting that could inhibit all Low Pressure Core Injection (LPCI) pumps from automatically starting and operating during a LOP/LOCA, thus making LPCI incapable of meeting its functional requirement of automatic startup and operation regardless of the availability of offsite power supply (UFSAR Section 6.3.1.4 and Tech. Spec. Surveillance Requirement 3.8.1.17). "The condition was identified during the first-time performance of a revised surveillance procedure for a LOP coincident with a LOCA signal. Fermi is currently in Mode 4 (Cold Shutdown) and LPCI auto start on a LOP/LOCA signal is not required. However, the initial investigation identified the condition likely existed in the past during modes of operation where LPCI auto start on LOP/LOCA was required. Investigation into the cause and corrective actions is ongoing. "Since LPCI auto start is not required at the time of discovery (Mode 4), this event is being reported pursuant to 50.72(b)(3)(ii)(b). "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-10-19
53673 | 0 | ITT ENIDINE |  |  |  |  | 2018-08-23 | 2018-10-19 08:40 | 2018-10-19 | PART 21 REPORT - ENVIRONMENTAL QUALIFICATION TEST DISCREPANCY The following report synopsis was received via fax from ITT Enidine: On August 23, 2018, ITT Enidine discovered a discrepancy between the published specifications in sales literature, internal test acceptance procedures and the environmental qualification (EQ) test report for the ITT Conoflow model GT25 series. The current to pressure transducer EQ report 3419 lists the temperature range as -40 to 150 degrees Fahrenheit, and the linearity as 0.75 percent of span. The current temperature range specification is 0 to 150 degrees Fahrenheit, and the linearity is 1.5 percent of span. Units manufactured after October 2010 may not conform to the specifications of the EQ test report for linearity and temperature range. Customers who procured safety related GT25 series I/P transducers and the specific part numbers since 2010 will be notified of this potential product defect by October 23, 2018. ITT GT25 Series customer list (2010 to present): - ALMARAZ: GT25CD1826 - ARIZONA PUBLIC SERVICE - GT25CA1826 - CALVERT CLIFFS NUCLEAR - GT25CD1826 - DUKE ENERGY (CATAWBA NUCLEAR STATION) - GT25CA1826; GT25CD1826 - CONTROL COMPONENTS INC - GT25CD1826 - ENERTECH - GT25CD1826 - ENRICO FERMI POWER - GT25CD1826 - FLOWSERVE - GT25CA1826 - TRACTABEL (VIA GEFRAN BENELUX) - GT25CA1826; GT25CD1826 - KHNP - GT25CA1826 - KOREA HYDRO - GT25CA1826 - KRSKO NUCLEAR PLANT - GT25CA1826 - NEBRASKA PUBLIC POWER - GT25CA1826 - ONTARIO POWER GENERATION - GT25CA1826 - SPX FLOW TECHNOLOGY (SPX MCKEAN) - GT25CA1826 - WEIR VALVES - GT25CA1826 - ERGYTECH - GT25CD1826 - OPPG FORT CALHOUN STATION - GT65FA1826 - BECHTEL POWER CORPORATION (TVA) - GT25CD1826; GT65CD1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2018-10-19
53672 | -1 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-10-16 | 2018-10-18 13:08 | 2019-07-23 | AGREEMENT STATE REPORT - ADMINISTERED DOSE LOWER THAN PRESCRIBED DOSE The following information was obtained from the State of Ohio via email: "On October 16, 2018, a suspected medical event occurred. A patient was prescribed a dose of 120 Gy for segment 4 of the left lobe of the liver involving Y-90 TheraSpheres. All the pre-procedural safety checks were made and appropriate imaging (cone beam CT) was performed to check the catheter position and lesion location. During the first set of infusions, there was high resistance felt on the syringe which continued for the next few infusions. It was decided to stop the treatment as there was risk of inadequate delivery of the microspheres due to possibility of stasis and concern for non-target embolization to other sites. The residual was calculated and it was noted that estimated dose delivered was 6.4 Gy to the target lesion. Post-procedure, the patient had a PET CT to check the Y-90 microspheres distribution and it did not demonstrate any non-targeted deposition. "The administered dose was 6.4 Gy to segment 4 of the left lobe of the liver. The dose was therefore 5% of the prescribed dose, a 95% difference. "The microspheres not delivered to the target were contained in the catheter. No contamination occurred as a result of this event. "The referring physician has been notified as well as the patient. "A follow-up inspection will be conducted during the week of Oct. 22, 2018." Ohio NMED Report No.: OH180010 * * * RETRACTION ON 7/23/2019 AT 1526 EDT FROM MICHAEL RUBADUE TO ANDREW WAUGH * * * The following retraction was obtained from the State of Ohio via email: "A follow-up inspection was conducted on October 24, 2018 to determine the circumstances leading up to this event. "It was determined the difference in administered dose was due to emergent patient conditions and resistance of the patient's complex hepatic arterial system; stasis. There was no evidence of catheter misplacement, non-target disposition or mechanical failure of the Y-90 microsphere delivery system. There was also no evidence of any non-compliance with NRC guidelines or Ohio Administrative Code regulations." Notified R3DO (Norton) and NMSS Events Notification (email). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-10-26
53671 | -1 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-10-16 | 2018-10-17 18:34 | 2018-10-18 | AGREEMENT STATE REPORT - EQUIPMENT FAILURE The following was received from the State of Nebraska: "Event type: Equipment Failure as reportable under 10 CFR 30.50, item b.2. and Inoperability of Access Control System under 10 CFR 36.83, item 5. "Event description: Nebraska Department of Health and Human Services, Office of Radiological Health was conducting a performance-based inspection of the Becton Dickinson and Company licensee (10-08-01) during the late afternoon (between 2:30 and 3:30 pm) on October 16, 2018. During the inspection, an inspector was able to open an outer door leading from the production floor area to the control room, which is a part of the licensee's controlled access area. The control room also contains an access door which leads to a panoramic, wet source storage irradiator licensed for millions of curies of Co-60. The access door in the control room did not fail and was functioning as intended. The outer door leading to the control room was able to be opened by the inspector only after a routine entry was made. During the initial inspection by the licensee, it was determined that the locking mechanism was loose and did not latch as intended. The licensee was able to repair the locking mechanism within 2 hours and could not open the outer door after a routine entry was made. "The State inquired with the Region IV Regional State Agreement Officer (RSAO) in the early afternoon (between 1:30 and 2:30pm) of October 17, 2018 to ask if this incident was a reportable event under 10 CFR 37. The RSAO indicated and agreed that this incident was not a report event under the reporting requirements of 10 CFR 37. Later that afternoon (between 3:30 and 4:00 pm), the RSAO stated that this incident may be a reportable event under 10 CFR 30.50, item b.2. and 10 CFR 36.83, item 5. "The State and Region IV staff are scheduled to discuss this further on October 18, 2018, and this incident may need to be retracted. "State Event Report ID No.: NE-18-0008" * * * RETRACTION ON 10/18/2018 AT 1129 EDT FROM LARRY HARISIS TO ANDREW WAUGH * * * The following retraction was received from the State of Nebraska via email: "Please retract this event. This does not meet the reporting requirements of either 10 CFR 30.50 or 10 CFR 36.83 since this outer door is not a part of the access control system. This was reviewed and discussed by State staff and NRC Region IV staff this morning." Notified R4DO (Pick) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-10-25
53670 | 0 | EXXON MOBIL REFINING & SUPPLY CO. |  |  |  |  | 2018-10-16 | 2018-10-16 18:41 | 2018-10-16 | INABILITY TO RETRACT A SOURCE TO ITS SHIELDED POSITION The following information was received via email: "On October 16th 2018, The ExxonMobil RSO at the Billings Montana Refinery (License # 25-03375-01) notified USNRC of one (1) device (insertion type nuclear gauge) that failed to function as designed (10 CFR 30.50.Section B.2). "Device Information: Ohmart device, model MT-93-439-001 with 10 mCi. of Cs-137; S/N: 0692GK; Source capsule model: A-2102 (X38/2); Manufacture date: Nov 7th, 1994 "Upon locking out the nuclear gauge at approximately 11:00am, the nuclear gauge user identified that the cable connecting the source capsule housing (torpedo) to the source holder retrieval mechanism had become detached. The source capsule housing appears to be in its normal operating location at the bottom of the equipment guide tube in the boot of the vessel, however, due to the disconnected cable it cannot be retrieved. The following precautionary measures were taken to ensure minimal potential for exposure (1) no vessel entry permits will be issued for the vessel (2) the area around the boot was barricaded to restrict entry. "There is no additional risk of radiation exposure to members of the general public or radiation workers due to the failure of the equipment function. "The source capsule housing is scheduled to be retrieved, shielded, and shipped for transfer to QSA Global by VEGA Americas, Inc. on 10/18/18." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-10-24
53669 | 0 | CLOROX |  |  |  |  | 2018-09-19 | 2018-10-16 10:12 | 2018-10-16 | MISSING FIXED GAUGE The Clorox Company discovered a missing fixed gauge containing radioactive material. The gauge was a Filtec, model FT-2 containing 100 microCuries of Americium-241. Gauge S/N: 105382; Source S/N: 1786. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2018-10-24
53668 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-10-15 | 2018-10-16 00:21 | 2018-10-16 | FITNESS-FOR-DUTY TEST POSITIVE FOR LICENSED EMPLOYEE "In accordance with 10 CFR 26.719(b)(2)(ii), this notification reports a licensed Reactor Operator tested positive for alcohol during a random fitness for duty test. The employee's access to the plant has been suspended. "The NRC Senior Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 26.719 |  |  |  | 0 | 2018-10-16
53667 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-10-14 | 2018-10-15 13:45 | 2018-10-15 | AGREEMENT STATE REPORT - STUCK IRRADIATOR SOURCE RACK The following was received from the State of Nebraska via email: "This morning at approximately 1030 [CDT], the State of Nebraska was contacted by the RSO of Becton, Dickinson and Company located in Holdrege, NE (NE license # 37-03-01) concerning a 24 hour reportable event. I believe the reporting requirement could be 10 CFR 36.83(a)(1), source stuck in the unshielded position or 10 CFR 36.83(a)(4), failure of the cable or drive mechanism used to move the source rack. "Event: Approximately 1930 [CDT] on the night of October 14, 2018, there was an alarm of the source positioning indicators alerting the operators of a moving source. When the source rack failed to reach the rack down position in the allotted time period, a fault was recorded at the control panel. It appeared that the rack was stuck in the up position. The RSO called in at approximately 1940 [CDT] to help investigate the situation. Soon after arriving at the facility, [the RSO] placed a call into MDS Nordion for help with the situation. During the 2 hour time period for MDS Nordion to call back, [the RSO] successfully returned source rack #2 to the shielded position and tried to lower the source rack #1 to its shielded position but was unable to lower source rack #1. They also did some preliminary investigations and assumed that one of the guide cables for source rack #1 had busted. Once MDS Nordion returned their call, it was verified that the guide cable for source rack #1 had busted. MDS Nordion had the operators raise source rack #2 and with source rack #2 in its up position, lower source rack #1. After a couple attempts, they were successful in lowering the source rack #1 to its shielded position. Once source rack #1 was in its shielded position, the operators lowered the source rack #2 to its shielded position. Both were verified by the source down positioning switch. "Note: After about 3.5 hours of the sources being stuck in the up position, the rack deluge system (rack sprinkler system) was deployed as a precautionary step to cool the sources and the product close to the sources. The overall time the sources were in the up position was approximately 5 hours. This was Nordion Model JS-8900 commercial irradiator. "It was reported that nobody entered the vault while the sources were in the up position and that there is no reason to believe that any addition exposure to the workers was involved in this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-10-23
53666 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2018-10-14 | 2018-10-14 07:35 | 2018-10-14 | OFFSITE NOTIFICATION DUE TO A SODIUM HYPOCHLORITE LEAK "Notified New York State Department of Environmental Conservation for draining of sodium hypochlorite (12-15% by weight) from the storage tank into it's engineered secondary containment of approximately 1300 gallons. Reportable per regulation 6 NYCRR Part 597." The NRC Resident Inspector will be notified by the licensee. Licensee investigation into the cause of the leak is ongoing. | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-10-14
53665 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2018-10-12 | 2018-10-12 16:54 | 2018-10-12 | AUTOMATIC REACTOR TRIP "On October 12, 2018 at 1353 EDT, St. Lucie Unit 2 experienced an automatic RPS actuation and Reactor Trip due to a fault on the 2A1 6.9kv bus during a transfer of the bus power supply from the 2A Auxiliary Transformer to the 2A Startup Transformer. The bus fault caused a fire in the 2A1 6.9kv switchgear that has been extinguished. Offsite support was not required to extinguish the fire. The specific cause of the fault is currently under investigation. "Following the reactor trip, both Steam Generators are being supplied by main feedwater. All [Control Element Assemblies] (CEAs) fully inserted into the core. Decay Heat removal is being accomplished through forced circulation. Main Feedwater and Steam Bypass Control Systems are maintaining stable conditions in Mode 3. "St. Lucie Unit 1 was unaffected and remains in Mode 1 at 100 percent power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the Reactor Trip." The fire was extinguished within 28 minutes. Plant loads are being supplied by the 2B Auxiliary Transformer. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-10-12
53664 | 0 | ABB MOTORS AND MECHANICAL |  |  |  |  | 2018-08-02 | 2018-10-12 15:04 | 2019-03-04 | INTERIM PART 21 REPORT - EVALUATION OF MOTORS The following information was received by from ABB Motors and Mechanical INC by facsimile: "Pursuant to 10 CFR 21.21(a)(2) this letter provides an interim report concerning an evaluation being performed by ABB Motors and Mechanical Inc. (formerly Baldor Electric Company) on three 40 ft-lb, 56 frame, 2-pole AC electric motors. The issue being evaluated pertains to the abnormal appearance of cracked paint and minor deformation around the stator pin which is located in the motor housing shell. "The three motors were supplied to Flowserve - Limitorque on a single purchase order in April 2013. The issue being evaluated was identified after MOV production set-up and testing at the valve manufacturing facility. The equipment had not been supplied to a nuclear power plant and thus had not been placed into service. "The discovery date of the condition being evaluated is August 2, 2018. Evaluation of reportability cannot be completed within the initial evaluation period due to the need to perform additional inspections of motors manufactured in the same period. ABB is working with Flowserve - Limitorque to expedite the additional inspections and testing. It is anticipated that this will be completed by 01/11/2019. "An initial review of ABB's records indicate that since 1998 ABB has supplied approximately 670, 56-frame AC electric motors of 40 and 60 ft-lb. to Flowserve - Limitorque. Flowserve - Limitorque communicated to ABB that there have been no previously reported occurrences of this issue nor any reported motor failures related to this issue. "(i) Name and address of the individual or individuals informing the Commission. "Sheldon Thomas QA Manager ABB Motors and Mechanical Inc. Flowery Branch, GA 30542 (678) 947 7350 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility which fails to comply or contains a defect. "The basic components being evaluated are Class 1E 40 ft-lb, 56 frame, 2-pole motors supplied to Flowserve - Limitorque for installation on valve actuators to be supplied into nuclear plant applications, to date, no basic components have been determined to contain a defect. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect. "The basic components being evaluated were supplied by ABB Motors and Mechanical Inc. (formerly Baldor Electric Company) ("ABB"), No basic components have been determined to contain a defect. This is an interim report. "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such defect or failure to comply "ABB was contacted by our customer Flowserve - Limitorque regarding three 40 ft-lb, 56 frame, 2-pole AC electric motors which were reported to have an abnormal visual appearance of cracked paint and minor deformation of the motor housing material around the stator pin. The motor stator pin is installed through the motor housing shell into the stator assembly. ABB's initial inspection of the three motors suggested that the deformation around the pin may have occurred when the motor was operated during actuator and/or MOV production testing. ABB is evaluating whether this abnormal condition of the stator pin interface with the motor frame constitutes a defect that could potentially affect the safety related function of the motor. To date, no basic components have been determined to contain a defect. This is an interim report. "(v) The date on which the information of such defect or failure to comply was obtained. "The discovery date of the condition being evaluated is August 2, 2018, "(vi) In the case of a basic component which contains a defect or fails to comply, the number and location of these components in use at, supplied for, being supplied for, or may be supplied for, manufactured, or being manufactured for one or more facilities or activities subject to the regulations in this part. "At this time, no basic components have been determined to contain a defect. "(vii) The corrective action, which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action. "None at this time, "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees. "None at this time." * * * UPDATE AT 0815 EST ON 1/11/2019 FROM SHELDON THOMAS TO MARK ABRAMOVITZ * * * The following information was received via fax: "This letter is a follow-up to the initial Interim Notification dated October 12, 2018 (Ref. ML18302A229). ABB continues to work with Flowserve-Limitorque to expedite the additional inspections of motors in the field and testing of motors pulled from inventory. The testing is necessary to assist in determination if the abnormal appearance and deformation constitutes a defect which would cause a substantial safety hazard. "It is anticipated that this will be completed by February 28, 2019. At that time, motor testing should be complete and analysis of results conducted. ABB will then be able to determine if the nature of the condition is a substantial safety hazard and reportable. If further time is necessary for evaluation, a follow-up to this report will be filed. "Since discovery of the condition, and to the date of this report, ABB and Flowserve-Limitorque are not aware of any confirmed field inspections by Flowserve-Limitorque's customer or the results of such inspections." Notified the R1DO (Bower) and Part 21 Reactors Group (via e-mail). * * * CLOSEOUT RECEIVED AT 1642 EST ON 3/4/20119 FROM SHELDON THOMAS TO MARK ABRAMOVITZ * * * The following closeout was received by fax: "ABB has completed the evaluation of the abnormal appearance of the three motors identified in this notification with the determination that this condition does not constitute a defect that would affect the safety related function of the motor." Notified the R1DO (Werkheiser) and Part 21 Reactors Group (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2018-10-12
53663 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2018-10-11 | 2018-10-12 03:58 | 2018-10-12 | AIR START SOLENOID CLOSURE FAILURE "During a post maintenance start of the 1B diesel generator, the air start solenoid valves did not close as expected. This resulted in lowering air pressure in the common air start headers causing inoperability of the 2A and 2B diesel generators at time 23:03. The 1B diesel generator was isolated from the common air start header, which restored the air start header pressure to the 2A and 2B diesel generators. The 2A and 2B diesel generators were declared operable at 23:34." The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-10-12
53662 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2018-10-11 | 2018-10-12 01:14 | 2018-10-12 | ACTUATION OF EMERGENCY DIESEL GENERATOR DUE TO TRANSFORMER TRIP "On 10/11/18 at 2304, with both Surry Units at 100% power, the 'A' Reserve Station Service Transformer (RSST) tripped on a pilot wire lockout. This resulted in electrical isolation of the 'A' RSST, the 'D' Transfer Bus and the Unit 1 'J' Emergency Bus. The #3 Emergency Diesel Generator (EDG) started and loaded on the Emergency Bus, as designed. Operations entered the appropriate Abnormal Procedures and stabilized the unit. All equipment operated as expected during the event. "A report of a flash at the 'A' RSST was received (at approximately the time of the initiating event) but there were no reports of visible damage, smoke or fire from the RSST or any associated breakers on subsequent investigation. The #3 EDG is running with normal parameters. "There was heavy wind/rain in the area associated with Tropical Storm Michael. "All other electrical distribution systems are in a normal alignment. "The organization is staffing to evaluate the lockout and required actions for recovery. "No radiological consequences resulted from this event. "This event is being reported IAW [in accordance with] 10 CFR 50.52(b)(3)(iv)(A) due to the actuation of the #3 EDG. "The NRC Resident [Inspector] was notified" | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-10-12
53661 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-08-16 | 2018-10-11 15:37 | 2018-10-11 | INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On August 16, 2018, at approximately 1736 CDT, Browns Ferry Nuclear Plant (BFN), Unit 2 experienced an unexpected loss of the 2B Reactor Protection System (RPS). This resulted in Primary Containment Isolation System (PCIS) groups 2, 3, 6, and 8 isolations, and initiation of Standby Gas Treatment Trains A, B, and C and Control Room Emergency Ventilation System Train A. All affected safety systems responded as expected with the exception of the Unit 1 Refuel Zone Supply Fan Outboard Isolation Damper, 1-FCO-64-5, that failed to indicate closed position. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywell Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywell Pressure. At the time of the event, these conditions did not exist; therefore, the actuation of the PCIS was invalid. "The cause of the RPS MG [Motor Generator] Set trip was a failed (shorted) operating coil associated with the 480 VAC motor starter inside the control box. "There were no safety consequences or impact to the health and safety of the public as a result of this event. "This event was entered into the Corrective Action Program as Condition Reports 1440047 and 1440050. "The NRC Resident Inspector has been notified of this event." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-10-11
53660 | 0 | ABB INC |  |  |  |  | 2018-09-10 | 2018-10-11 09:39 | 2018-10-11 | PART 21 REPORT - DEFECT ASSOCIATED WITH DRY TYPE TRANSFORMER The following information was received by from ABB INC by facsimile: "1. This letter provides a notification of a defect associated with dry type transformer serial # 24-26458. The failure was caused by the breakdown of layer to layer insulation within the 4160 volt winding due to dielectric stress. Deterioration of the insulation resulted in an internal fault within the bravo phase 4160 volt winding, triggering a ground fault trip shutdown of equipment. This failure was reported by Exelon's Clinton Nuclear Station and it is the only known reported occurrence of safety related transformer failure caused by the breakdown of layer to layer insulation. Information is provided as specified in 10 CFR 21 paragraph 21.21(d)(4). "2. Notifying individual: Joey Chandler, Plant Manager, ABB ([PGTR] Power Grids Transformer Division, US), 171 Industry Drive, Bland, VA 24315. "3. Identification of the Subject component: ABB P/N 24-26458 dry type transformer. This transformer is used for stepping down voltage and was intended for providing power to safety related electrical equipment. "4. Nature of the deviation: The Exelon Clinton Nuclear Generating Station shut down due to a ground fault alarm on the 4160 volt side of the stepdown transformer that provides power to numerous safety-related components at the plant. Subsequent troubleshooting of the problem revealed that the dry-type transformer supplying 480 volt power had dielectrically failed due to apparent internal fault within the Bravo phase. Further investigation of this failure revealed an operational voltage design stress on the Nomex 410 insulation between the 4160 volt winding's layers of conductor of greater than recommended by the manufacturer (DuPont) for a 40 year design life. At the time of failure, the subject transformer had been in operation for approximately 33.5 years and had progressed 37 years and two months into its intended 40 year life given the 10/1980 ship date. ABB has no knowledge of any adverse operational variances over the course of the approximate 33.5 year life of operation to be able to assess or comment on this potential impact in terms of life. "5. The function of this dry type transformer is to step voltage down from 4160 volts to 480 volts while providing transfer of power to safety related components. Exelon's Clinton Nuclear Power Station has identified this transformer's power transfer to feed safety related equipment. An interruption of this transfer in power would result in a loss of power to the safety related equipment downstream and could potentially result in a compromise in safety. "6. ABB was notified of this transformer failure on 12/9/2017. This notification was delayed while the failure was being investigated. This investigation is documented in report: Exelon Clinton Failure Analysis_26458_011218 rev5.doc.pdf dated 09/10/2018. "7. Corrective actions include: a. Reviewed and verified current electrical engineering safety related design standard for allowable design stress on insulation per DuPont's recommendation for 40 year life. (Complete.) b. Reviewed the material used for transformer 24-26458. Found only affected safety related product to be isolated to Clinton Nuclear Station, though records may be incomplete as these records have been archived for over 35 years. (Complete.) c. Re-trained all involved personnel of the 10 CFR 21 reporting requirements, and the need to provide an interim report within 60 days of discovery. d. ABB worked directly with Clinton Nuclear to ensure all transformers of respective design was replaced with new transformers following ABB's Technical Evaluation for Nuclear 1E Transformer, Rev. 18 which documents operational design stresses be less than or equal to 30 volts / mil of Nomex 410 insulation between layer to layer of conductor for 40 year life. "8. Recommendation: Because of the possible existence of additional affected transformers, ABB (PGTR) cannot determine the potential for a substantial safety hazard exists at any other licensee's facility. Licensees are requested to evaluate any Gould-Brown Boveri/ITE dry type transformer with the following nameplate identification below. Transformers associated with this identification are recommended to be replaced. "kVA: 750AA/ 1000 FA HV: 4160 Delta Connected LV: 480 Wye Connected Class: AA/ FA Type: Vent Frequency: 60 Hz Temp Rise: 80 degrees C Date of Manufacture: 10/1988 and older models "Questions concerning this notification should be directed to the Quality Manager (Rick Kinder) at the ABB transformer plant in Bland, VA at (276) 688 -3325." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-10-11
53659 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-10-10 | 2018-10-11 08:24 | 2018-10-11 | AGREEMENT STATE REPORT- FIXED GAUGE SHUTTER BROKE The following information was received from the State of Texas by email: "On October 10, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that while performing a leak test of a Vega SH-F1 nuclear gauge the operating handle broke preventing manipulation of the shutter. The gauge contains a 100 milliCurie (original activity) cesium - 137 source. The gauge is located 160 ft. above ground level and does not present an exposure threat to workers. The manufacturer and a service contractor have been contacted to perform the repair of the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident: 9620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-10-19
53658 | 0 | TEAM INDUSTRIAL SERVICES |  |  |  |  | 2018-10-10 | 2018-10-10 17:40 | 2018-10-10 | RADIOGRAPHY SOURCE FAILED TO RETRACT "During retraction of the source following an exposure inside a storage tank [at the BP Refinery, Whiting, IN], the radiographer noted the source did not retract with the drive cable as survey readings indicated the source was still exposed. An immediate call was made to the local RSO [Radiation Safety Officer], who is source retrieval trained, to report the issue. Barricades were continuously monitored while waiting for his arrival. Upon arrival and evaluation of the situation, the local RSO determined a source disconnect had occurred due to a possible broken drive cable. Source retrieval procedures were then enacted with the source safely returned to the shielded position in the exposure device at approximately 1400 CDT. The exact cause of the event is not clear at this time and the drive cable and connector are being sent to the manufacturer for evaluation. "Equipment involved: QSA Ir192 model A424-9 source assembly with approximate activity 84 Curies; QSA model 880 Delta exposure device and associated equipment (drive assembly and guide tube). "Approximately 4-5 individuals were involved in the retrieval process with the RSO (Authorized Source Retriever) indicating he received the highest exposure, as recorded on pocket dosimeters, of 25 mrem." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-10-18
53657 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2018-10-09 | 2018-10-10 03:26 | 2018-11-14 | CONTROL ROOM EMERGENCY VENTILATION AC SYSTEM INOPERABLE "On October 9, 2018 at 2002 CDT the Control Room Emergency Ventilation Air Condition (CREV AC) system was in the process of being returned to service following maintenance. During the return to service, the end bell on the CREV AC Condenser developed a significant leak requiring isolation. No work was performed on the CREV AC Condenser during the work window. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10CFR50.72(b)(3)(v)(D), "Event or Condition That Could Have Prevented Fulfillment of a Safety Function " because the CREV system is a single train system required to mitigate the consequences of an accident." The NRC Resident Inspector has been notified. * * * RETRACTION AT 1714 EST ON 11/14/2018 FROM JASON SWAIN TO JEFF HERRERA * * * "The purpose of this notification today (November 14, 2018) is to retract the ENS Report made on October 10, 2018 at 0326 EDT (ENS Report #53657). "Upon further investigation, it was determined that while the CREV AC system was out of service for planned maintenance and inoperable, the return to service valve sequencing caused an in-rush of residual heat removal service water (RHRSW) at 300 psig dead-heading into the refrigeration condensing unit (RCU). Previous normal sequencing had refilled the RCU with service water which is supplied at 100 psig. This unexpected higher than normal pressure on the RCU end bell gasket (rated at 150 psig) caused the gasket to be pushed from its normally seated position to allow a leak path. The gasket was not previously leaking; upon removal was inspected and no evidence of premature cracks or tears were found. "The CREV AC system leak was induced by an improper coordination of return to service activities at the time of discovery, and the leak path was not previously present. This was not a latent failure. As such, a pre-exiting condition that could have prevented the fulfillment of a safety function did not exist, and based on this information, ENS Report# 53657 is being retracted. "Note: On October 11, 2018 at 1330 hours CDT, the CREV RCU System gaskets were replaced and the system was returned to service under the properly sequenced tagout and was returned to Operable status. "The NRC Resident Inspector has been notified. " Notified the R3DO (Peterson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-10-10
53656 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-10-09 | 2018-10-10 01:29 | 2018-10-10 | UNPLANNED LOSS OF EMERGENCY RESPONSE EQUIPMENT "At 2115 CST on October 9, 2018, South Texas Project Electric Generating Station (STPEGS) experienced an unplanned loss of the Integrated Computer System (ICS) to the Emergency Operations Facility (EOF). The loss of ICS resulted in a major loss of emergency assessment capability to the STPEGS Emergency Operations Facility (EOF) for greater than 75 minutes. Assessment capability has been verified to be available in the Unit 1 and Unit 2 Technical Support Centers (TSC) and the Unit 1 and Unit 2 Control Rooms. "This report is being made pursuant to 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability, off site response capability, or off site communications ability. "The NRC Resident Inspector has been informed." The cause of the unplanned loss is currently being investigated and compensatory measures are in place. * * * UPDATE ON 10/10/18 AT 0951 EDT FROM RICK NANCE TO PHIL NATIVIDAD * * * Integrated Computer System was returned to service as of 0810 CDT on October 10, 2018. Notified R4DO (Gepford) and CAT via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-10-10
53655 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-10-07 | 2018-10-09 14:51 | 2018-10-09 | AGREEMENT STATE REPORT - STOLEN PORTABLE X-RAY FLUORESCENCE DEVICE The following was received via email from Washington State: "Over the weekend of October 6-7 2018, Wood Environment & Infrastructure Solutions, INC at 420 Lake Washington Blvd. NE, STE 200, in Kirkland, Washington 98033, was broken into and a portable XRF [x-ray fluorescence] device was stolen. Police report with case number 18-37870 was filed with the Kirkland police department. "'The lock to the main door of the storage unit was cut, and the lock to the large steel nuclear gauge/XRF device storage cabinet, located inside the storage unit, was cut. [The licensee] verified all four (4) nuclear gauges [they] have in [their] inventory are accounted for and in [their] possession. The steel cable running through the nuclear gauge cases and locked to the steel cabinet was not cut. However, the portable XRF device (information below) stored on the upper shelf of the steel cabinet was stolen, and has been recorded as stolen by the Kirkland Police Department.' "The stolen XRF device: -Manufacturer: Niton - Thermo Fisher Scientific -Model: XLp-306A -Serial Number: 24923 -Source: Cd109 - 40 mCi (resourced 02/2018 - current approx. 27 mCi) -Transport/carrying case was locked." Incident Report No: WA 18-025 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-10-17
53654 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2018-10-08 | 2018-10-09 12:20 | 2018-10-09 | AGREEMENT STATE REPORT - I-125 SEEDS LOST IN TRANSIT The following was received via email from the State of Virginia: "On Monday, October 9, 2018, the Virginia Radioactive Materials Program (RMP) received a phone call from the licensee (Best Medical International) that a radioactive material package, Type A Package, containing 4.9 GBq (132.4 mCi) of I-125 seeds was lost in transit. The package was intended to be shipped to Centre d oncologies Dr. Leon-Richard, Moncton, Canada. [The Common Carrier] picked up the package on September 28, 2018 at the licensee's facility in Springfield, Virginia. The licensee tracked the shipment until it passed the [Common Carrier's] facility located in Alexandria, Virginia. After that, the licensee was unable to track the package. "On October 8, 2018, the licensee called the recipient to check if the package was delivered and found that the package was not delivered. The licensee contacted [the Common Carrier] immediately to get the whereabouts of the package. [The Common Carrier] searched for the package and was unable to locate the package after it left the Alexandria [Common Carrier] facility until this report was prepared (10/09/2018). "The licensee determined the package is lost but they stated that the search will continue with [the Common Carrier] to locate the package. This report will be updated when RMP receives the 30 day written report." Incident Report No: VA-18-005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2018-10-17
53653 | 0 | CURTISS WRIGHT |  |  |  |  | 2018-08-07 | 2018-10-08 14:54 | 2019-05-31 | PART 21 NOTIFICATION - NAMCO LIMIT SWITCH FAILED TEST DUE TO INSUFFICIENT LUBRICATION The following information was received via email from Curtiss Wright: "Curtiss-Wright was notified on August 7, 2018 by Exelon's Dresden Plant that a Curtiss-Wright Supplied Namco Limit Switch, P/N: EA700-90964 had failed during a planned maintenance test. "The switch contacts were found to be sluggish in returning to the normal shelf state after actuation, or would not return at all. The switch was identified as Curtiss-Wright Tag Number 5T34603 and was provided as a safety related component to Exelon in September 2005. According to Exelon, the item was stored for 8 years, then failure occurred approximately 5 years into service. The part has a manufacturer date coded as August 2005. "The switch was subsequently sent to Exelon Powerlabs where a detailed failure evaluation was performed. Exelon Powerlabs confirmed the failure mode and determined that there was insufficient lubrication in place to support normal switch function. The switch was then sent to Namco for further evaluation and Namco confirmed the lack of lubricant was the likely cause of the failure. "Curtiss-Wright is currently investigating this issue and will provide a follow up report by November 15, 2018." * * * UPDATE FROM TIM FRANCHUK TO DONALD NORWOOD AT 1335 EST ON 11/16/2018 * * * The following information was received via E-mail: "In reference to the Curtiss-Wright Interim Notification Report dated 10/8/2018 for an EA700-90964 limit switch failure, the following clarifications and updates are provided. "The subject switch was originally supplied by Curtiss-Wright to Exelon's Dresden plant. Subsequently Dresden transferred the switch to Quad Cities where it was installed and found degraded and inoperable during a planned maintenance test. The initial notification of failure to Curtiss-Wright was by Quad Cities personnel, and not Dresden personnel. The switch was previously identified as Curtiss-Wright Tag Number 5T34603, which was incorrect. The actual Tag Number of the failed unit is 5T36403. "The failure is still under investigation and Curtiss-Wright has been in communication with the manufacturer, Quad Cities personnel and Exelon Powerlabs personnel concerning the failure and application. A key factor in the failure appears to be heat related, specifically the switches operating temperature. As such, additional operating temperature data is being taken by Exelon personnel which will conclude in late February or early March 2019. Once this data is made available, a final conclusion as to the root cause of the failure can be determined. "We therefore request additional time to complete our evaluation and should have our final report issued by March 8th, 2019." Notified R3DO (Peterson) and Part 21/50.55 Reactors E-mail group. * * * UPDATE ON 3/8/2019 AT 1320 EST FROM MARGIE HOOVER TO ANDREW WAUGH * * * The following information was received via email: "In reference to the Curtiss-Wright Interim Notification Report dated 10/8/2018 for an EA700-90964 limit switch failure, the following updates are provided. "Curtiss-Wright's investigation is ongoing, with the current focus being the evaluation of in-service switch operating temperatures and results from a recent disassembly/inspection of similar switches (same model but different date codes). Additional inspection of other switches currently in-service at the plant is needed to finish the investigation. Evaluation of these switches is expected to be completed by mid-May. Once this data is made available, a final conclusion as to the root cause of the failure can be determined. "We therefore request additional time to complete our evaluation and should have our final report issued by May 31, 2019." Notified R3DO (Hills) and Part 21/50.55 Reactors group (email). * * * UPDATE AT 1106 EDT ON 5/31/19 FROM MARGIE HOVER TO JEFF HERRERA * * * The following information was received via e-mail: "ln reference to the Curtiss-Wright Interim Notification Report dated 10/8/2018 (Event No. ML18289A457lLoC No. 2018-24-00) for an EA700-90954 limit switch failure, the following updates are provided. "Curtiss-Wright was notified on August 7th, 2018 by Exelon's Quad Cities Plant that a Curtiss-Wright Supplied Namco Limit Switch, PIN: EA 700-90954 had failed during a planned maintenance test. "CW Conclusion: "Based upon similar wear patterns, the presence of 'significant grease' does not resolve wear pattern issue caused in a shorter period of time, thus the lack of grease can be considered to 'not be a significant credible failure mechanism' (same or no grease between shuttle and housing). Based upon the NAMCO report, the presence or lack of grease has no impact on wear or operability and thus does not affect the safety function. "In addition, the CQ14100801 S/N 03 installed for 9 months, the O-Ring measured an 81 durometer hardness (showing aging) but not brittle. The other 3 installed for 6 years were brittle but did not affect operability. Thus the hardness of the O-Rings can be considered to 'not be a significant credible failure mechanism'. "All four switches in Report QDC-62770 had paint scrapings caused by wear which was present and operated properly after being in service for an extended period of time. Thus the presence of paint residue due to wear can be considered to 'not be a significant credible failure mechanism'. "There have been no other reported failures of this type. The root cause failure mechanism has not been identified, thus this switch failure does not appear to represent a common mode failure." Notified the R3DO (Daley) and Part 21/50.55 Reactors group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2018-10-08
53652 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-10-08 | 2018-10-08 04:13 | 2018-10-08 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE "On Monday, October 8, 2018 at 0111 CDT, during the initial containment entry for unit 2 refueling outage (A2R20), reactor coolant system pressure boundary leakage was discovered at the 2D Steam Generator bowl drain line. Unit cooldown to mode 5 is in progress. "This event is reportable under 10CFR50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' "The licensee has notified the NRC resident inspector." Approximately 0.1 gpm was leaking from the drain line. LCO 3.4.13 was entered and the licensee anticipates being in mode 5 within a couple of hours. The leak will be repaired prior to exiting the refueling outage. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-10-08
53651 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-10-07 | 2018-10-07 16:52 | 2018-10-07 | SAFEGUARDS REPORT - SECURITY MEASURES SUSPENDED DUE TO WEATHER CONDITIONS Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-10-07
53650 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2018-10-05 | 2018-10-06 05:56 | 2018-11-15 | CONTROL ROOM EMERGENCY FILTER SYSTEM INOPERABLE "On 10/5/2018, at 2219 CDT, the Control Room Emergency Filter (CREF) System was determined to be inoperable during a required condition of applicability due to being aligned to a Division 2 power source with its associated emergency power supply (Diesel Generator #2) removed from service earlier in the day. The power supply alignment was not identified at the time Diesel Generator #2 was removed from service (Diesel Generator #2 was rendered inoperable on 10/5/2018 at 1728 CDT). Movement of lately irradiated fuel assemblies in the Secondary Containment was in progress at the time of discovery of this condition. This condition represents an unplanned loss of safety function for a single train system during its specified condition of applicability. Movement of irradiated fuel was suspended until the power supplies to CREFs could be realigned to Division 1 which was completed at 0004 CDT on 10/6/2018. "This represents a condition that could have prevented the fulfillment of the safety function of CREFs needed to mitigate the consequences of a fuel handling accident." The NRC Resident Inspector has been notified. * * * RETRACTION AT 1533 EST ON 11/15/18 FROM THOMAS FORLAND TO JEFFREY WHITED * * * "CNS [Cooper Nuclear Station] is retracting the 8-hour non-emergency notification made on October 5, 2018 at 2219 CDT (EN# 53650). A subsequent evaluation concluded that the Control Room Emergency Filter (CREF) system remained operable in accordance with the applicable Cooper Nuclear Station Technical Specification Requirements 3.7.4 CREF System, 3.8.2 AC Sources - Shutdown, and 3.8.8 Distribution Systems - Shutdown. As a result of CREFs remaining operable throughout this period, no loss of safety function occurred. The NRC Senior Resident Inspector has been notified." Notified R4DO (Haire) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-10-06
53649 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2018-10-05 | 2018-10-05 17:33 | 2018-10-05 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following was received via email from the State of Nevada: "This is an email to report a possible medical event. The licensee is Renown Regional Medical Center, the license number is 16-12-0016-01. Occurrence was 10/5/2018 and reported the same day by Renown's RSO. The administration of Y-90 was given, prescribed dose was 15.66mCi and the delivered dose was 9.86mCi. The reason for this was due to patient intervention, apparently the patient moved and pulled the IV [Intravenous therapy] out. A full report from Renown's RSO has not been received, just the initial report." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2018-10-15
53648 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2018-10-05 | 2018-10-05 15:39 | 2018-10-05 | AUTOMATIC REACTOR SCRAM DUE TO LOW REACTOR WATER LEVEL "On Friday, October 5, 2018 at 1209 hours, with the reactor at 100 percent core thermal power, Pilgrim Nuclear Power Station (PNPS) automatically tripped due to reactor water level perturbation and receipt of a low reactor water level Reactor Protection System (RPS) signal. The cause of the low reactor water level is under investigation. The plant is in hot shutdown. "All other plant systems responded as designed. Pressure is being controlled using the Mechanical Hydraulic Control System and Main Condenser. Reactor water level is being maintained with the feedwater and condensate system. "During the automatic reactor scram the plant experienced the following isolation signals as designed: Group 2 Isolation: Miscellaneous containment isolation valves Group 6 Isolation: Reactor Water Clean-up Reactor Building Isolation System Actuation "Due to the RPS actuation while critical, this event is being reported as a four-hour, non-emergency notification in accordance with 10 CFR 50.72(b)(2)(iv)(B), 'any event that results in actuation of the reactor protection system (RPS) when the reactor is critical.' This notification is also being made in accordance with 10 CFR 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section ... ' (B)(2) 'General containment isolation signals affecting containment isolation valves in more than one system.' "This event has no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The licensee will notify the Massachusetts Emergency Management Agency. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-10-05
53647 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2018-10-05 | 2018-10-05 09:59 | 2018-10-18 | UNPLANNED LOSS OF THE ASSESSMENT CAPABILITY DUE TO TECHNICAL SUPPORT DIESEL "At 05:52 CDT on 10/5/2018, the [Wolf Creek Nuclear Operating Corporation] (WCNOC) Technical Support Center (TSC) Diesel fuel oil transfer pump would not run. There was ongoing modification to the facility Halon system at the time. The modification process had included a jumper to the fuel oil transfer pump to allow it to continue to be available. This issue was discovered during testing as the modification was progressing. The pump was verified to function on 10/4/2018 by normal operations rounds. "If an emergency is declared requiring the TSC activation during the time the TSC diesel is non-functional, the TSC will be staffed and activated using existing emergency planning procedure. If offsite power is lost, the TSC will relocate to the Alternate TSC using existing emergency planning procedures. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 10/18/2018 AT 1306 EDT FROM MARCY BLOW TO ANDREW WAUGH * * * "Event Notification (EN) 53647, made on October 8, 2018, is being retracted because during the time that the TSC Diesel fuel oil transfer pump was not available, normal power was continuously available. The Alternative TSC was also available. "Consequently, the condition did not meet the criteria for a 8-hour notification per 10 CFR 50.72(b)(3)(xiii) for any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (e.g., significant portion of control room indication, Emergency Notification System, or offsite notification system). "The NRC Resident Inspector has been notified of the Event Notification retraction." Notified R4DO (Pick). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-10-05
53646 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2018-10-05 | 2018-10-05 09:52 | 2018-10-24 | MAIN STEAM ISOLATION VALVES EXCEEDED PRIMARY CONTAINMENT LOCAL LEAK RATE ACCEPTANCE CRITERIA "At 0520 (CDT), on October 05, 2018, it was discovered that a Primary Containment local leak rate test performed on Main Steam Isolation Valves (MSIV) exceeded its acceptance criteria. "During Mode 1, 2, and 3, Surveillance Requirement 3.6.1.3.10 requires MSIV leakage for a single MSIV line to be less than or equal to 106 standard cubic feet per hour (scfh) when tested at 29 psig and Surveillance Requirement 3.6.1.3.12 requires the combined leakage rate for all MSIV leakage paths to be less than or equal to 212 scfh when tested at 29 psig. "As-found for the 'C' MSIV line leakage results were unquantifiable and gave a [minimum] path value greeter than 160 scfh. This leakage rate lead to Surveillance Requirement 3.6.1.3.10 and 3.6.1.3.12 limits to be exceeded. This event is being reported as a condition of the nuclear power plant, including its principal safety barriers, being seriously degraded per 10 CFR 50.72(b)(3)(ii)(A) since the Primary Containment Isolation Valves leakage limits for MSIVs were exceeded. "The NRC Resident Inspector has been notified." * * * RETRACTION AT 2320 EDT ON 10/24/2018 FROM THOMAS FORLAND TO MARK ABRAMOVITZ * * * "CNS [Cooper Nuclear Station] is retracting the 8-hour non-emergency notification made on October 5, 2018 at 0520 CDT (EN# 53646). Subsequent evaluation concluded that overall as-found 'C' MSIV leakage rate was not at a level that exceeded the surveillance requirement 3.6.1.3.10 and 3.6.1.3.12 limits and thus the Primary Containment Isolation Valve leakage rate limits for the MSIVs were not exceeded. "The NRC Senior Resident Inspector has been notified." Notified the R4DO (Drake). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-10-05
53645 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-10-04 | 2018-10-04 16:49 | 2018-10-04 | SAFEGUARDS EVENT An actual entry of unauthorized persons into Material Access Areas. The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2018-10-04
53644 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2018-10-04 | 2018-10-04 12:29 | 2018-10-04 | POSTULATED HOT SHORT FIRE EVENT THAT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "Degraded or unanalyzed condition due to the possibility for a postulated fire induced hot short to cause a secondary fire in a different fire area, which would be outside the boundaries analyzed for safe shutdown in calculation SSC-001 due to an unfused circuit associated with the 1M43C0001A, Diesel Generator Building Ventilation Fan. This condition is not bounded by existing design and licensing documents. "Without overcurrent protection for this circuit, the potential exists that an initial fire event affecting this circuit could cause a short circuit without protection that would cause excessive current through the circuit beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where this circuit is routed challenging the ability to achieve and maintain safe shutdown. "The postulated event would affect the following fire zones: 1CC-3c (Unit 1, Division 1 4160V and 480V Switchgear Room, 620 feet 6 inch elevation), 1CC-3e (Unit 1 West Corridor North of Elevator, 620 feet 6 inch elevation), DG-1d (Hallway Diesel Generator Building 620 feet 6 inch elevation), and 1DG-1c (Unit 1, Division 1 Diesel Generator Building 620 feet 6 inch elevation). "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B). Interim compensatory measures (i.e., fire watches) have been implemented for affected areas of the plant. "The licensee has notified the NRC Senior Resident Inspector." | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-10-04
53643 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-10-04 | 2018-10-04 07:57 | 2018-10-19 | MANUAL REACTOR TRIP DURING LOW POWER PHYSICS TESTING "At 0544 EDT on October 4, 2018, with Unit 1 in Mode 2 with reactor power in the intermediate range performing low power physics testing, the reactor was manually tripped due to a rod control urgent failure alarm. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam system. "Unit 2 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified. "All control rods inserted as expected. The cause of the rod control urgent failure is being investigated." * * * UPDATE FROM KEVIN LOWE TO DONALD NORWOOD AT 1408 EDT ON 10/19/2018 * * * "This Event Notification is being updated to clarify that the reactor was not critical when this event occurred. Therefore, the reporting requirement is changed from 10 CFR 50.72(b)(2)(iv)(B) to 10 CFR 50.72 (b)(3)(iv)(A). "During Dynamic Rod Worth Measurement testing, Control Bank Charlie was inserted approximately 153 steps when the urgent failure occurred (CBC positioned at 75 steps out). Following the scram, additional analysis concluded that the reactor was subcritical when the Reactor Protection System was actuated." The licensee notified the NRC Resident Inspector. Notified the R2DO (McCoy). | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-10-04
53642 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2018-10-03 | 2018-10-03 19:39 | 2018-10-03 | FITNESS FOR DUTY - SUPERVISOR TESTS POSITIVE "At 1135 PDT on October 3, 2018, Southern California Edison (SCE) determined a SCE supervisor failed a random breathalyzer test for alcohol during a random Fitness-for-Duty (FFD) test. The employee's unescorted access to San Onofre Nuclear Power Plant has been suspended." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2018-10-03
53641 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-10-02 | 2018-10-03 15:11 | 2018-10-03 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY SOURCE The following was received via email from the State of Texas: "On October 3, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that one of their radiography crews had reported they could not retract a 22 Curie Iridium-192 source into a SPEC 150 exposure device. The crew was working at a remote job site [in Carrizo Springs, TX]. The exposure device was sitting on a pipe rack. During an exposure (not the first one) the device fell off the pipe rack, hitting the guide tube, and crimping the tube to a point where the source could not be retracted back into the device. "The crew contacted the RSO and a retrieval team was sent to the location. The source was positioned in the collimator and covered with bags of lead shot. The retrieval team was able to cut the protective coating off of the guide tube and, using a pair of pliers, reshape the guide tube until the source could be retracted to the fully locked position. "No member of the general public received an exposure from this event. The highest dose received by an individual responding to this event was 40 millirem." Texas Incident: I-9616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-10-11
53640 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-10-03 | 2018-10-03 15:16 | 2018-10-09 | AGREEMENT STATE - LOSS OF CONTROL AND POSSIBLE DAMAGE OF MOISTURE DENSITY GAUGE At 1355 CDT on 10/3/18, the Nebraska Office of Radiological Health was notified by the Corporate Radiation Safety Officer (RSO) that a licensed moisture density gauge was run over by a large piece of construction equipment on a construction site in Omaha, NE. At the time of the notification to the State, the Corporate RSO did not know which of the licensee's gauges was involved in the incident, nor the device model number, isotope, or quantity. Staff from the Nebraska Office of Radiological Health were dispatched and are enroute to the event site to meet the licensee's Assistant RSO to assess the possible damage to the gauge and obtain further information. No injuries related to the event were reported to the State and no offsite emergency services support were requested. * * * UPDATE ON 10/5/2018 AT 0945 EDT FROM HOWARD SHUMAN TO ANDREW WAUGH * * * Contamination swipes verified the source of the gauge to be intact. The gauge's source rod was broken during the event and the source had to be manually retracted into the shielded position. The gauge is currently at Terraco. The moisture density gauge is a Troxler Model 3440 (serial number: 30122). Notified R4DO (Farnholtz) and NMSS Event Notifications (email). * * * UPDATE ON 10/5/2018 AT 1725 EDT FROM LARRY HARISIS TO DONG PARK * * * The following was received via email from the State of Nebraska: "Nebraska Department of Health and Human Services, Office of Radiological Health was notified on October 3, 2018, by the Radiation Safety Officer (RSO) from Terracon, Inc (Nebraska license 01-58-01) that a portable nuclear moisture density gauge was damaged at a temporary job site. [The licensee authorized user] said that he arrived on the jobsite in Omaha, NE to perform moisture density measurements for Peter Kiewit Construction (general contractor) that was going to be pouring concrete later that afternoon by JR Barger & Sons Concrete Contractors (subcontractor). When [the licensee authorized user] arrived, he parked his vehicle near the work area and assessed the work area. He noticed that there were trucks and other heavy machinery working in the area. [The licensee authorized user] proceeded to take the Troxler portable nuclear moisture density gauge (model 3440, serial number 30122 containing 9 mCi of Cs-137 and 44 mCi of Am-241:Be) out of his vehicle and placed it on the ground where moisture density measurements were to be made. While performing a moisture density measurement with the Cs-137 source deployed from the protective housing, a skid loader backed up and hit the portable gauge. Fortunately, [the licensee authorized user] was able to dive out of the way with the back of the skid loader hitting the back of [the licensee authorized user's] arm. The extent of [the licensee authorized user's] injury is unknown. "[The licensee authorized user] indicated he then proceeded to inform the skid loader to stop but said he continued without acknowledgement. [The licensee authorized user] was then able to get the attention of [the construction project supervisor] to inform him what just transpired. [The licensee authorized user] said that [the construction project supervisor] was not interested in stopping work for the damaged gauge and proceeded to tell [the licensee authorized user] [profanity] or we will call your boss . At this time, [the licensee authorized user] indicated that [an employee] picked up the damaged gauge and threw it to an area outside the work location. An assumption was made of the [the employee's] whole body dose of 571.1 millirem, assuming that he carried the gauge at one centimeter from the trunk of the body and that it took him one minute to move the gauge. "[The licensee authorized user] said he then called [the Omaha RSO] and informed him of what just happened. [The Omaha RSO] then called the Corporate RSO. [The Omaha RSO] was then dispatched to the area with a survey meter and to assist [the licensee authorized user]. [The Corporate RSO] informed [the Nebraska Department of Health and Human Services (DHHS), Office of Radiological Health Manager]. [The Nebraska DHHS, Office of Radiological Health Manager] dispatched [personnel] to the scene. "Meanwhile at the jobsite, [the licensee authorized user] maintained surveillance of the gauge and informed personnel to stay away from where the gauge was located. [The Omaha RSO] said that when he arrived, a radiation survey of the surveillance area and gauge was made. Radiation levels at the surveillance area was about 0.5 mR/hr and the gauge was 10 mR/hr, nearest to the extended Cs-137 source and the source was stuck into the ground to provide additional shielding. Calculations indicated that the exposure rate at the 15 foot exclusion boundary would have been 0.04 mR/hr. "When Nebraska DHHS, Office of Radiological Health staff arrived, another confirmatory radiation survey of the gauge was completed with a result of 10.5 mR/hr. The gauge was also observed to have the source rod extended into the ground and part of the trigger mechanism was broken and sheared off. A wipe test was performed on the source rod with nip tongs and was reading the same as background. The portable gauge was then manipulated to place the Cs-137 source rod assembly back into the shielded position. After an unsuccessful attempt was made, the sliding spring lock was still open and was emitting 385 mR/hr on contact of the port hole. [The Omaha RSO] was able to clear off the excess mud and dirt on the port hole using the nip tongs and the sliding spring lock was shut. Another wipe test was completed and read at background. A radiation survey of the portable gauge confirmed that the Cs-137 source was in the shielded position and measured 20.8 mR/hr. "[The Omaha RSO] placed the portable gauge back in the shipping container and duct tape was applied to prevent any movement of the source rod from the shielded position. A radiation survey of the transport case was performed with the portable gauge inside and the highest was 8.9 mR/hr on contact and 0.4 mR/hr at 3 feet. The listed TI [Transportation Index] of the package was labeled as 0.6 mR/hr. [The Omaha RSO] stated that he will contact InstroTek to either repair or dispose of the gauge upon their return to the Omaha office. "An investigation is currently underway and the event is not closed." Notified R4DO (Farnholtz) and NMSS Event Notifications (email). * * * UPDATE ON 10/9/2018 AT 1624 EDT FROM HOWARD SHUMAN TO OSSY FONT * * * The State of Nebraska submitted the full report. The detailed information was previously provided via email. The item is still open pending a reconstruction of the dose received by the employee who picked up the damaged gauge. Incident Report No: NE180006 Notified R4DO (Gepford) and NMSS Event Notifications (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-10-11
53639 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-09-28 | 2018-10-03 12:06 | 2018-10-03 | AGREEMENT STATE - UNDERDOSAGE OF YTTRIUM 90 THERASPHERES The following was received via email from the State of California: "On 09/28/18, [the Radiation Safety Officer] RSO initially contacted [Radiologic Health Branch] RHB to report a problem related to patient therapy treatment with Yttrium 90 TheraSpheres performed on 09/28/18. The intended activity of the dosage was 11.9 milliCurie, but only approximately 36 percent was delivered to the target tissue based on the measurement of activity remaining in the delivery system after the procedure. The desired dose for the target volume was 135 Gy and the dose delivered was 49 Gy. At the time of the RSO contact, the licensee was uncertain whether the problem was due to patient stasis or an issue with the delivery system (e.g., a kink in the catheter). "On 10/02/18, RHB received an email from the RSO stating that the physician (Authorized User) had used a micro catheter on the thinner end and it was very tortuous and made the resistance in the circuit higher than the administration box can tolerate such that the delivery system was not able to work properly in this situation. Licensee stated that the problem was not due to patient stasis. "The licensee will submit a written report in accordance with 10 CFR 35.3945(d)." California Report No. 5010-092818 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-10-11
53638 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-09-28 | 2018-10-03 10:57 | 2018-10-03 | AGREEMENT STATE - STOLEN DENSITY GAUGE The following was received via email from the State of California: "On October 2, 2018, at approximately 0830 [PDT] the, Radiation Safety Officer (RSO) for Geocon, Inc. contacted [California Radiologic Health Branch] RHB Brea concerning the moisture/density gauge, Troxler, model 3440, serial #33877 (Cs-137, 0.333 gigaBecquerel; Am-241, 1.6 gigaBecquerel) that had been stolen along with a transport vehicle parked in San Ysidro, CA, at approximately 0600 to 0700 [PDT], on Friday morning, September 28, 2018. "The authorized user whose truck was stolen did not inform the RSO until 1000 to 1030 [PDT] on Monday, October 1, 2018, of the stolen radioactive gauge. The RSO has contacted local law enforcement in San Diego and is awaiting the completed police report, a copy of which he will send to RHB Brea to be included as part of this report. The RSO will contact local newspapers to attempt to retrieve the stolen radioactive gauge as well as notifying local servicing vendors of radioactive gauges to be alert for the serial number of the stolen gauge in case it turns up for service. The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame. California Notices of Violation will be issued to the licensee for failure to report the loss in a timely manner, and loss of control of the radioactive material." California Report No. 5010-100218 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-10-11
53637 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2018-10-01 | 2018-10-02 14:38 | 2018-10-04 | CONCURRENT NOTIFICATION "At approximately 1525 [EDT] on October 1st, 2018, Fire Riser 318 which serves both non-contaminated and contaminated areas in [Fuel Manufacturing Operations] (FMO), was taken out of service due to a pin hole leak in the pipe. Water was contained and surveys were completed to ensure no contamination was released into non-contaminated areas. The New Hanover County Deputy Fire Marshall was notified at 1655 [EDT] on October 1st, 2018, per State code requirements. An hourly fire watch was implemented for surveillance of the affected areas. Because the New Hanover County Deputy Fire Marshall was notified, a concurrent notification to the NRC Operations Center is being made per 10 CFR 70, Appendix A(c)." The licensee will notify NRC Region 2 and the State of North Carolina Radiation Protection Section. * * * UPDATE ON 10/4/18 AT 1335 EDT FROM PHILLIP TO OLLIS * * * "The leaking sprinkler pipe fitting was replaced this morning and the system was restored to service at approximately 11 AM, 10/4/18. The NHC [New Hanover County] Deputy Fire Marshal was notified via telephone of the return to service at 11:50 AM, 10/4/18." Notified the R2DO (Lopez), NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-10-02
53636 | 0 | RANCHO SECO |  |  |  | ISFSI | 2015-09-05 | 2018-10-01 19:54 | 2018-10-01 | UNAUTHORIZED ENTRY INTO PROTECTED AREA An actual entry of an unauthorized person into a protected area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2018-10-01
53635 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-07-27 | 2018-10-01 10:33 | 2018-10-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the Colorado Department of Public Health and Environment via email: "United Parcel Service reported one tritium exit sign was lost when the building was renovated." CO Event Report ID No.: CO180024 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-10-09
53634 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-06-28 | 2018-10-01 10:33 | 2018-10-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the Colorado Department of Pubic Heath and Environment via email: "Keystone Resort-Property Management reported one tritium exit sign was unable to be located during the annual reconciliation." CO Event Report ID No.: CO180025 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-10-09
53633 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-22 | 2018-10-01 10:30 | 2018-10-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the Colorado Department of Public Health and Environment via email: "Canyon Bakehouse reported that three tritium exit signs were not in the building when the ownership of the building was transferred." CO Event Report ID No.: CO180023 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-10-09
53632 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-29 | 2018-10-01 10:27 | 2018-10-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the Colorado Department of Public Health and Environment via email: "Olinger Hampden Funeral Home & Cemetery reported three lost tritium exit signs when conducting the annual reconciliation." CO Event Report ID No.: CO180021 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-10-09
53631 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-12-19 | 2018-10-01 10:23 | 2018-10-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the Colorado Department of Public Health and Environment via email: "Marriott Denver Tech Center reported three lost tritium exit signs when conducting the annual reconciliation." Event Report ID No.: CO180020 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-10-09
53630 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2018-09-30 | 2018-09-30 15:29 | 2018-09-30 | AUTOMATIC SCRAM DUE TO A LOSS OF TWO CONDENSATE PUMPS "On Sunday, September 30, 2018, at 1130 EDT, an automatic scram was received on U3 following a loss of two condensate pumps. Following the reactor scram, water level lowered from normal level of 23" to below 1" which resulted in automatic Group II and Group III isolations. Reactor water level lowered to -48" which resulted in initiation of the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems. Reactor water level and reactor pressure have been restored to their normal bands. All systems responded properly to the event. Unit 3 remains in Mode 3 with reactor pressure being controlled on the turbine bypass valves. The cause and details of the event are under investigation. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A). "All control rods inserted. Decay heat is being removed via the main condenser. "The NRC Resident Inspector has been notified." A notification to the media and a press release were made. Unit 2 was unaffected and continues coastdown to refueling. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2018-09-30
53629 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2018-09-24 | 2018-09-28 10:21 | 2018-09-28 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The following information was received via E-mail: "On 09/24/2018 the licensee discovered unusual dose rate survey readings on the floor in the treatment area. The licensee notified the Department [South Carolina Department of Health and Environmental Control] on 09/27/2018 via telephone that a potential contamination event had occurred. "The licensee is authorized to administer liquid Iodine 131 for the treatment of hyperthyroidism in cats. The last administration occurred on 09/04/2018, with approximately 5 mCi of I-131 administered via syringe to a cat. "A BRH [Bureau Radiological Health] Inspector was dispatched to the facility on 09/27/2018 and confirmed contamination of an area of floor in the treatment area. Access to the contaminated area has been restricted and boundaries have been put in place to ensure the dose rate does not exceed .002 rem in any one hour. The Department is conducting an investigation into the incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2018-10-08
53628 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-09-27 | 2018-09-27 14:42 | 2018-09-27 | FITNESS FOR DUTY - CONTRACTOR SUPERVISOR TESTS POSITIVE "At 1000 EDT on September 27, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for drugs during a random Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-09-27
53627 | 0 | MAINE YANKEE |  |  |  | ISFSI | 2018-09-27 | 2018-09-27 13:31 | 2018-09-27 | UNAUTHORIZED ENTRY INTO AN ADMINISTRATIVELY CONTROLLED AREA "A vendor followed a member of onsite staff into the Administratively Controlled Area. This vendor was not authorized to enter this area. The vendor was immediately removed from the area and was informed of his access boundaries. The area entered was not the Protected Area. " The vendor was onsite to perform scheduled maintenance on the emergency diesel generators. The vendor entered the unauthorized area for approximately 3 seconds prior to being removed from the area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | ME | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2018-09-27
53626 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2018-09-26 | 2018-09-26 23:25 | 2018-09-26 | AUTOMATIC SCRAM DUE TO GENERATOR OUTPUT BREAKER TRIP "On September 26, 2018 at 1908 CDT. an automatic scram was received on U1 following main generator 345 kV output breaker 7-8 trip with 345 kV output breaker 6-7 already opened for maintenance on line 0401. Following the reactor scram, reactor water level decreased to approximately minus 15 inches, which resulted in automatic Group II and Group Ill isolations (expected response). Reactor pressure rose to approximately 1083 psig, and the 3B and 3C low set relief valves opened briefly to control reactor pressure. Reactor water level and reactor pressure have been restored to their normal bands. All systems responded properly to the event. Unit 1 remains in Mode 3, with reactor pressure being controlled on the turbine bypass valves. The cause and details of the event are under investigation. "Unit 2 was unaffected by the event and remains at 100% power. "This report is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." All control rods inserted. Decay heat is being removed via the main condenser. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-09-26
53625 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2018-09-26 | 2018-09-26 21:43 | 2018-09-26 | HIGH PRESSURE CORE INJECTION (HPCI) SYSTEM INOPERABLE "On 9/26/2018 at 1530 EDT, it was discovered that the HPCI system was inoperable due to a blown fuse in the 10C617 Panel, E21-F15A. Therefore, this condition Is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v)(D). The blown fuse also impacts 'A' channel Residual Heat Removal (RHR) subsystem and 'A' Core Spray (CS) subsystem. These Emergency Core Cooling subsystems have been declared inoperable. Remaining Emergency Core Cooling subsystems and the Reactor Core Isolation Cooling (RCIC) system remain OPERABLE. "There was no impact on the health and safety of the public or plant personnel." The licensee notified the NRC Resident Inspector and will notify the local authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-09-26
53624 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-09-26 | 2018-09-26 16:29 | 2018-09-26 | FITNESS FOR DUTY - DISCOVERY OF KOMBUCHA TEA INSIDE THE PROTECTED AREA "An unopened (sealed) container of Herbal Tea (Kombucha) was found in a refrigerator located within a common office break area inside the protected area. Kombucha Tea is a fermented tea, which contains at least 0.5 percent alcohol by volume. Alcohol is a prohibited item per the requirements of 10 CFR Part 26.719(1). "The incident was entered into the NFS corrective action program and an investigation is in progress "The licensee notified the NRC Resident Inspector." NFS Event (PIRCS) Number: 67184. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 26.719 |  |  |  | 0 | 2018-10-04
53623 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2018-09-26 | 2018-09-26 15:10 | 2018-09-26 | UNDERVOLTAGE CONDITION INITIATES AN AUTOMATIC START OF THE DIESEL GENERATOR "At 0946 CDT on 9/26/2018, a disruption in power to the offsite 138 kV line and the subsequent trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) resulted in a degraded voltage signal on the Division 1- 4.16 kV safety bus. The degraded voltage signal resulted in a trip of the ERAT feed to the bus, blocking closure of the 345 kV Reserve Auxiliary Transformer (RAT) feed to the bus and auto start of the Division 1 Emergency Diesel Generator (EDG). The Division 1 EDG successfully started and re-energized the Division 1- 4.16 kV bus as designed. The unit is stable with the Division 1 EDG carrying the Division 1- 4.16 kV bus. "The Ameren Transmission System Operator in St. Louis, MO informed the station that they had received a report that a 138 kV to 13.8 kV transformer at Clinton Route 54 substation was on fire and the South feed to the Tabor substation cycled as a result of this fault. "The NRC Resident Inspector and Illinois Emergency Management Agency Resident Inspector have been notified." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-09-26
53622 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-09-25 | 2018-09-25 20:25 | 2018-09-25 | CONTROL BUILDING CHILLERS IN UNANALYZED CONDITION "At 1200 CDT on September 25, 2018, while the plant was in MODE 1 at 90 percent power, it was identified that an additional condition existed which had not previously been considered in developing the compensatory measures implemented for design flaws and single point vulnerabilities associated with the Control Building Chilled Water System. Specifically, a 20 minute 'quick restart timer' on Control Building Chillers that have analog control systems (HVK-CHL1A & 1B) would prevent the chillers from starting in specific scenarios. "The recommended compensatory actions to address the new condition were implemented at 1235 CDT on September 25, 2018. "Currently the Chilled Water System is otherwise operating as designed. Operator actions are in place to ensure the plant meets all required design safety system functions. Work is currently underway to identify and correct all design vulnerabilities. "The [NRC] Senior Resident Inspector has been notified." This was identified by engineering during an extended condition search. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-09-25
53621 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-09-25 | 2018-09-25 15:47 | 2018-09-25 | AGREEMENT STATE REPORT - STUCK GAUGE SHUTTER The following was received via email from the state of Texas: "On September 25, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee [Graphic Packaging] that the shutter on a Berthold model P2602-100 gauge containing 100 milliCuries of Cobalt-60 failed to close during the required maintenance check. The gauge shutter is stuck in the open position, which is the normal operating position for the gauge and does not pose an increased exposure risk to any individual. The gauge is attached to a second floor crystallizer ash tank recirc line and is not accessed during system operation. "The licensee stated that they were in the process of contacting the manufacturer for repairs or replacement of the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Report #: I-9614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-10-03
53620 | 0 | ACCUREN INSPECTION INC |  |  |  |  | 2018-09-23 | 2018-09-25 11:10 | 2018-09-26 | RADIOGRAPHY SOURCE STUCK OUT DUE TO BENT GUIDE TUBE "On 9/23/18, a worker reported an equipment failure while conducting radiographic operations at a refinery in Wyoming. A magnetic stand was used to support a 2.28TBq (61.8 Ci) Ir-192 source while performing internal tank radiography. The magnetic stand disconnected from the wall of the tank during crank out, falling and striking the 7ft guide tube and preventing the source from being retracted. The workers immediately backed up, expanded the boundary, and called the RSO [radiation safety officer]. The RSO advised the crew to return the source to the collimator, backup, and monitor the area while he contacted management since he was out of state. The RSO received a second call from the workers where they stated they successfully retracted the source into the exposure device after pulling the crank to relieve the kink caused by the magnetic stand. "The crew surveyed the scene, verified the source was secure in the device, and ended their shift at the refinery. The crew arrived back in Colorado at 2100 MDT on 9/23/18, and management performed an initial assessment of the guide tube and cranks at 0715 MDT on 9/24/18. "The RSO returned from vacation on 9/25/18 and inspected the guide tube, guide tube extension, cranks, and exposure device. The RSO concluded the exposure device and cranks were operational but removed the guide tube from service because it was involved in the strike incident. "The RSO reviewed the statements from the workers and contacted the State of Colorado and the NRC. The workers statements revealed that one of the workers performed a source retrieval by dropping lead shot bags on the collimator and pulling the guide tube and extension (not the crank) to relieve the kink in guide tube. As a result, one of the employee's dosimeters went off scale. Both film badges were overnighted for processing on 9/25/18. "The root cause was determined to be the equipment failure of the magnetic stand. Employees and management discussed the incident and reminded the individuals that source retrievals should be performed by the RSO or trained management as stated in Acuren Inspection Inc. procedures, and to always properly secure magnetic stands with a safe line while performing radiography at any elevation." * * * BRETT PAYTON TO VINCE KLCO ON 9/26/18 AT 1445 EDT * * * The licensee received the dosimetry report. Dose to the workers was 103 mRem and 76 mRem. Notified R4DO (Alexander) and NMSS Events Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-10-03
53619 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2018-09-24 | 2018-09-24 14:06 | 2018-09-24 | CONTROLLED SUBSTANCE DISCOVERED WITHIN THE PROTECTED AREA "On September 22, 2018, at approximately 0050 [CDT], Duane Arnold Energy Center (DAEC) Security was contacted by a site assigned contractor that they had located what appeared to be drug paraphernalia inside the Protected Area. Local Law Enforcement was contacted and responded to DAEC. The Linn County Sheriff's office took the items into evidence for testing to determine if there was any presence of a controlled substance. On September 24, 2018, at 1013, the Linn County Sheriff's office notified DAEC that the items tested positive for the presence of a controlled substance. Therefore, this is being reported in accordance with 10 CFR 26.719. DAEC Site security is working with NextEra Corporate security regarding the investigation into this incident. "The Resident Inspector has been notified." | 73 | 0 | 0 | 73 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 26.719 |  |  |  | 0 | 2018-09-24
53618 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-09-21 | 2018-09-24 11:29 | 2018-09-24 | AGREEMENT STATE REPORT - POTENTIAL LOSS OF I-125 SEED The following was received by the State of Florida by email: "[Boca Raton Regional Hospital Women's Imaging Center] Radiation Safety Officer, contacted [the State of Florida Bureau of Radiation Control] by phone on Friday, September 21, 2018 at approximately 1500 EDT to report the potential loss of a 170 microCurie Iodine-125 seed, from Boca Raton Regional Hospital Women's Imaging Center. ISOAID Seed Company has been contacted to assure the seed was not received in an earlier shipment. Seed can be tracked to the Nuc Med Hot lab. Staff has confirmed it is not in the patient or in the Pathology lab. Sealed source certificate will be sent later. Full investigation report will be submitted within 30 days." Florida Incident Number: FL18-124 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-10-02
53617 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2018-09-21 | 2018-09-21 22:04 | 2018-09-22 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "On 9/21/18, at 1755 EDT, Peach Bottom Atomic Power Station Unit 3 declared the High Pressure Coolant Injection system [HPCI] inoperable due to an inoperable differential pressure indicating switch [DPIS]. The DPIS is used to isolate the HPCI system when there is a high steam line flow condition. Operations declared the HPCI system inoperable and entered Technical Specification 3.5.1 Condition C for HPCI being inoperable. Technical Specification 3.3.6.1 was also entered for HPCI instrumentation being inoperable. Other standby systems (Reactor Core Isolation Cooling and Low Pressure Emergency Core Cooling Systems) are OPERABLE. "HPCI is a single train system. Therefore, per NUREG-1022, this condition is being reported pursuant to 10CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system required to mitigate the consequences of a design event. "This condition has been entered into the corrective action program (IR 4175355). Investigation of the exact cause of the indication issue is in progress. "The NRC Resident has been informed of this notification." * * * UPDATE AT 1317 EDT ON 09/22/2018 FROM CRAIG TAULMAN TO JEFF HERRERA * * * "On 09/22/18 at 0955 EDT, RCS [Reactor Coolant System] pressure boundary leakage was identified as the cause of the HPCI high steam flow indication issue. Technical Specification 3.4.4 was entered which will require the initiation of a nuclear plant shutdown. This indicates a degradation of a principal safety barrier. Current Unit 3 reactor power is 35%. This condition is being reported pursuant to 10 CFR 50.72(b)(2)(i) and 50.72(b)(3)(ii). This condition is being tracked in the corrective action program (IR 4175355). The NRC Resident has been informed". Peach Bottom will be notifying State and local agencies regarding the event. Notified the R1DO (Greives). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION | PLANT S/D REQD BY TS | DEGRADED CONDITION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  | 0 | 2018-09-21
53616 | -1 | MISSOURI BAPTIST MEDICAL CENTER |  |  |  |  | 2018-09-21 | 2018-09-21 17:40 | 2018-10-03 | POSSIBLE EXTRAVASATION OF RA-223 "The patient's first dose of 110.3 microCuries, 4.3 mL, of Ra-223 (Xofigo) was administered today, 9/21/18 at 1040 CDT. An IV was placed by RN [Registered Nurse] in the patient's left wrist. The IV was flushed with saline and blood return was checked and present prior to administration of Ra-223 by [the] MD [medical doctor]. The Ra-223 was delivered by MD. After delivery, the MD began [a] saline flush and after approximately 5cc of saline, noted resistance and a cold bulge near the infusion site. He was not able to get blood return. The RN was called in to check the IV and was not able to get blood return. It was noted an infiltration/extravasation had occurred. The IV was removed with catheter noted to be intact. Prior to the infusion the patient was told that the infusion should not be painful and he did not acknowledge any pain or discomfort during or after infusion. At this time it is not known if there was an extravasation of Ra-223 because the infiltration/extravasation was not noted until during the second saline flush. The patient and patient's family were notified at the time of the incident." * * * RETRACTION ON 10/03/18 AT 1525 EDT FROM TOM MOENSTER TO RICHARD SMITH * * * The licensee does not believe there was more than 10 percent of therapy dose that was not infiltrated. Based on the fact that the swelling went down in less than 45 minutes post imaging of the wrist, compared to the body, leads the Radiation Safety Officer (RSO) to believe most of the therapy dose went throughout the body. Notified R3DO (Orth) and NMSS vis email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2018-10-01
53615 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-09-20 | 2018-09-20 20:22 | 2018-09-20 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The licensee will notify the NRC Resident Inspector. * * * UPDATE AT 2101 EDT ON 9/20/2018 FROM JOSEPH BRAUNREITER TO JEFF HERRERA * * * At 1954 CDT the inclement weather conditions were lifted and security measures were restored. The licensee has notified the NRC Resident Inspector. Notified the R3DO (Orlikowski) and 73.71 Safeguards group (via email). | 79 | 100 | 0 | 79 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-09-20
53614 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-09-19 | 2018-09-20 15:24 | 2018-09-20 | AGREEMENT STATE REPORT - DAMAGED GAUGE AT CONSTRUCTION SITE The following information was received from the State of California via email: "On September 19, 2018, the [Radiation Safety Officer] RSO notified the [California Radiological Health Branch] that a CPN soils gauge, model MC-1DR # MD00605736 containing 10 mCi of Cs-137 and 50 mCi of Am-241/Be had been run over by construction equipment at a temporary job site in Camarillo, CA. The gauge operator had placed the gauge near his test area, but was 15 feet away when the accident occurred. After the accident, he immediately stopped all work in the area and cordoned off an area 30 feet around the damaged gauge before calling his RSO. "A radiation survey meter was available from a local radiography company who met the RSO and the gauge operator at accident site. The shaft housing the rod above the cesium source was snapped off from the gauge. The source was in the 'safe mode' during the accident and remained in the shielded area of the gauge. The gauge was able to be loaded into the shipping container for return to the permanent storage location. Radiation surveys were performed with a Bicron GM detector and no contamination was found in the area. The root cause is operator error by the gauge operator. The gauge will be disposed thru the manufacturer (CPN)." California Report No.: 5010-091918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-09-28
53613 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-09-19 | 2018-09-19 14:40 | 2018-09-19 | AGREEMENT STATE REPORT - PACKAGE ARRIVED WITH SURFACE CONTAMINATION The following information was obtained from the Ohio Department of Health via email: "At approximately 0730 EDT on 9/19/18, a package containing Tc-99m was received by the Cleveland Clinic Foundation from Cardinal Health in Oakwood, OH that exceeded the DOT surface contamination limits. The contact dose rates were incompliance. An initial wipe for removable contamination showed 1258 cpm over 300 cm2 of the package surface. Wipes of the handle (10759 cpm), the zipper (11290 cpm) and the top address label cover (24342 cpm) identified additional removable contamination on the package. Conversion to dpm with appropriate area correction resulted in 2946 dpm/cm2. "No other contamination was found in the lab or package receipt area. "A follow-up inspection at Cardinal Health in Oakwood will be conducted to determine the cause of the event." Ohio NMED Report No.: OH180008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-09-27
53612 | -1 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-09-17 | 2018-09-18 14:15 | 2018-09-20 | UNANALYZED CONDITION "On September 17, 2018, a notification was made by [Specialty Fuel Facility] (SFF) Operations that during dissolution of depleted uranium in the Conversion Area, the Recovery scrubber system was shut down for maintenance. During the shutdown, a reduction in vacuum to the box ventilation was experienced and a small amount of NOx [Nitrous Oxide] was released into the room. As the result of BWXT's review of this event, it cannot be determined within the 24 hour notification period that documentation is available to demonstrate that the condition has been analyzed in the [Integrated Safety Analysis] (ISA). BWXT is making this report per 10 CFR 70.61, Appendix A(b)(1), 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the ISA, and which results in a failure to meet the performance requirements of 10 CFR 70.61 (i.e. high consequence events are highly unlikely and intermediate consequences are unlikely)'. "The area is currently shutdown and in preparation for inventory. No material has been processed within the system since the event. BWXT is continuing to review the ISA documentation and will provide further updates as appropriate." The licensee notified the NRC Resident Inspector. * * * RETRACTION AT 1315 EDT ON 9/20/18 FROM CHRIS TERRY TO JEFF HERRERA * * * "BWXT is retracting Event Notification #53612 that was reported on September 18, 2018. The notification was made due to the fact that it could not be determined within the 24 hour notification period that documentation was available to demonstrate that a NOx release from the Conversion Area dissolver had been analyzed in the ISA. Subsequently, BWXT located the documentation that the condition was analyzed and meets the performance requirements of 10 CFR 70.61. Additionally, new calculations of the current process were run and the results confirmed the original analysis." The licensee notified the NRC Resident Inspector. Notified the R2DO (Guthrie), NMSS Events and Fuels group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2018-09-26
53611 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2018-09-18 | 2018-09-18 09:06 | 2018-09-18 | MANUAL REACTOR TRIP DUE TO A STEAM LEAK ON A HIGH PRESSURE FEEDWATER HEATER "Due to a steam leak on the reheater line to 36C Feedwater Heater, operators initiated a manual trip of the reactor, verified the reactor trip, and closed all Main Steam Isolation Valves. The plant is currently stable in Mode 3 with the steam leak isolated. "The Auxiliary Feedwater System actuated following the trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.72(b)(2)(iv)(B). The unit remains on offsite power in Hot Standby at normal operating temperature and pressure. "Decay heat is being removed from the steam generators via the Auxiliary Feedwater System and atmospheric steam dumps. "Unit 2 was unaffected and remains at 100 percent power." The licensee notified the NRC Resident Inspector, the State of New York, and the local transmission company. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-09-18
53610 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-09-17 | 2018-09-18 08:28 | 2018-09-18 | CONTRACT SUPERVISOR TESTED POSITIVE ON RANDOM FITNESS FOR DUTY TEST "At 1610 [EDT] on September 17, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for drugs during a Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-09-18
53609 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-09-15 | 2018-09-15 15:45 | 2018-09-18 | UNUSUAL EVENT DUE TO SITE CONDITIONS PREVENTING PLANT ACCESS "A hazardous event has resulted in on site conditions sufficient to prohibit the plant staff from accessing the site via personal vehicles due to flooding of local roads by Tropical Storm Florence." Notified DHS SWO, FEMA OPS, and DHS NICC. Notified FEMA NWC, NuclearSSA, and FEMA NRCC via email. * * * UPDATE FROM BRUCE HARTSCOK TO VINCE KLCO ON 9/28/2018 AT 1414 EDT * * * On 9/18/2018 at 1400 EDT, the Unusual Event at Brunswick was terminated due to the ability to transport personnel to the site. The licensee will notify the NRC Resident Inspectors. Notified the R2DO (Guthrie), NRR EO (Miller) and the IRD MOC (Grant). Notified DHS SWO, FEMA OPS, and DHS NICC. Notified FEMA NWC, NuclearSSA, and FEMA NRCC via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Hot Shutdown | Hot Shutdown |  | Hot Shutdown | Hot Shutdown |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-09-15
53608 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-09-14 | 2018-09-14 21:09 | 2018-09-14 | MANUAL REACTOR SCRAM "At 1644 [CDT] a manual reactor scram was inserted by placing the Reactor Mode Switch to Shutdown. At 1643 [CDT] the Condensate Booster Pump A tripped on low suction pressure. At 1644 [CDT] the Reactor Feed Pump A tripped on low suction pressure. A Recirculation Flow Control Valve runback occurred as designed. Reactor Water level was approaching the Automatic Low Water Level 3 (11.4 inches) scram set point and manual actions were taken by placing the Mode Switch to Shutdown before the low level set point was reached. All systems responded as expected following the manual scram. The plant is stable in mode 3. This event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "The NRC Senior Resident Inspector has been notified." All control rods fully inserted, and decay heat is being removed through the turbine bypass valves to the main condenser. The licensee is investigating the cause of the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-09-14
53607 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2018-09-14 | 2018-09-14 18:25 | 2018-09-14 | AGREEMENT STATE REPORT - STOLEN MOSITURE DENSITY GAUGE The following information was received from the State of Nevada via email: "Around 0900 PDT on September 14, 2018 the State of Nevada Radiation Control Program was informed by Aztech Inspection & Testing, LLC, RML 00-11-0482-01, that a Humboldt, Model 5001EZ, Serial Number 1142, containing 10 millicuries (mCi) of cesium-137 and 40 mCi americium-241: beryllium, was stolen from the licensee's vehicle parked in the parking lot of the gauge user's residence. The gauge was secured to the steering wheel using a chain and lock inside of the cab of a locked pickup truck. The State is following the incident and working with local authorities to develop a press release. Local Law enforcement and the FBI have been notified. Follow-up information will be provided to NRC on the recovery of the stolen gauge and entered into NMED [Nuclear Material Event Database]." Nevada NMED report number NV180004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2018-09-24
53606 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-09-14 | 2018-09-14 16:28 | 2018-09-14 | AUTOMATIC REACTOR TRIP DUE TO A FAILURE OF THE STEAM GENERATOR FEED REGULATING VALVE "At 1323 [EDT] on 9/14/18, with Unit 2 in Mode 1 at 90% power, the reactor automatically tripped due to a failure of 23BF19, 23 Steam Generator (SG) Feed Regulating Valve. The trip was not complex, with all systems responding normally post-trip. No equipment was inoperable prior to the event. An actuation of the auxiliary feedwater system occurred following the automatic reactor trip. The reason for the auxiliary feed water system auto-start was due to low level in the steam generator. Operations responded and stabilized the plant. Decay heat is being removed by the main steam dumps and auxiliary feedwater system. Unit 1 is not affected. "Due to the Reactor Protection System actuation while critical, this event is being reported as a four-hour, non- emergency notification per 10 CFR 50.72(b)(2)(iv)(B). This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the auxiliary feed water system. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified. The Lower Alloways Creek Township will be notified." | 0 | 0 | 0 | 90 | 90 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-09-14
53605 | 0 | SAN ONOFRE |  |  |  | ISFSI | 2018-08-03 | 2018-09-14 16:00 | 2018-09-14 | SPENT FUEL CANISTER BECAME BOUND DURING DOWNLOAD INTO DRY STORAGE "On Friday, August 3, [2018,] at approximately 1245 PST, Holtec International (a contractor for Southern California Edison (SCE)) was lowering a Multi-Purpose Canister (MPC) loaded with spent fuel into the Cavity Enclosure Container (CEC) of the SONGS Holtec UMAX Independent Spent Fuel Storage Installation (ISFSI) for purposes of dry storage. The canister was suspended from a Holtec Vertical Cask Transporter (VCT). During the download, the canister encountered an interference with the CEC divider shell and became bound in place. As a result, the downloader slings of the VCT became slack while the MPC was resting partially inside the CEC. "Once Holtec became aware of the situation, the VCT towers were raised in order to restore tension in the rigging and to raise the MPC. The VCT was then adjusted, and the MPC was then safely lowered into the CEC and the rigging was disengaged. "There was no effect on the integrity of the canister or release of radioactive material as a result of this event. "This event meets the reporting criteria of 10CFR72.75(d)(1) in that the VCT, which is an important-to-safety component, was placed in a configuration which defeated its ability to perform its safety function. The VCT and associated rigging are described in Certificate of Compliance 1040, Technical Specification 5.2.c.3, which requires that lifting equipment shall have redundant drop protection features which prevent uncontrolled lowering of the load. By placing the VCT in the configuration of this event, the single-failure proof nature of the lifting devices was defeated. The VCT was no longer capable of mitigating the consequence of an accident, and there was no redundant equipment available and operable to perform the required safety function. "SCE made an original determination that the event did not require a report. However, SCE contacted the NRC [Region IV] on Monday August 6th and again on Tuesday August 7th to provide details of the event. "It has now been determined that the event is reportable under 10CFR72.75(d)(1) and this late report is being made." Licensee notified RIV (Simpson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SFTY EQUIP. DISABLED OR FAILS TO FUNCTION | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 72.75(d)(1) |  |  |  | 0 | 2018-09-14
53604 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2018-09-15 | 2018-09-14 11:29 | 2018-09-15 | PREPLANNED OUTAGE OF A REQUIRED SAFETY MONITORING SYSTEM "The UUSA [URENCO USA] facility CAAS [Criticality Accident and Alarm System] exists to detect and alarm in the unlikely event of a criticality accident, as required by 10 CFR 70.24, Criticality accident requirements. This monitoring system will be temporarily disabled during planned corrective maintenance activities for approximately thirty minutes, commencing at approximately 0730 MDT, on Saturday, September 15th, 2018. This activity will affect the CAAS in the Separations Building Module (SBM) 1001/1002 and the Cylinder Receipt and Dispatch Building (CRDB). The CAAS in the remaining portions of the facility will be unaffected. "Essential personnel will remain inside the controlled access area during the maintenance activities. The populated areas of the facility will be limited to the Security Alarm Station, Operations Control Room, and the Maintenance Area housing the CAAS control cabinets in the Technical Services Building (TSB) where technicians will be needed for this work evolution. CAAS coverage of these populated areas will be provided during the maintenance activity by temporary criticality detection equipment. "Compensatory measures will be implemented in accordance with section 3.1.5 of the UUSA Integrated Safety Analysis (ISA) Summary. These measures including evacuation of non-essential personnel from the areas of concern and the Immediate Evacuation Zone (IEZ) before removing the equipment from service, limiting access into facility, and restricting Special Nuclear Material (SNM) movement will be implemented until CAAS coverage is verified operational. "UUSA will notify the NRC when CAAS coverage is returned to normal operation. Radiation surveys will be conducted prior to re-entry to confirm acceptable conditions in the area." The licensee has notified the NRC Project Manager. * * * UPDATE FROM WYATT PADGETT TO HOWIE CROUCH AT 1139 EDT ON 9/15/18 * * * The Criticality Accident and Alarm System was returned to service at 0930 MDT after the completion of the scheduled maintenance. During the maintenance period, no abnormal radiation readings were observed. Notified R2DO (Ernstes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | SAFETY EQUIPMENT FAILURE | [8 empty] | NON EMERGENCY | 2 | NM | FUE |  |  | 70.50(b)(2) |  |  | 0 | 2018-09-14
53603 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-16 | 2018-09-13 14:38 | 2018-09-13 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following information was received by the State of Texas: "On 09/13/2018, the Agency [Texas Department of State Health Services] was notified by a licensee that an employee received a personnel dosimetry report of 16.0 rem for the second quarter of 2018. The employee had received a report of a 3.3 rem exposure for the previous quarter. The licensee suspects that someone tampered with the dosimeter. The employee works in the nuclear medicine department and always leaves the badge attached to the lab coat on the door to the hot lab. Other employees performing similar work only received minimal exposures. Due to the amount of the reported exposure, the agency will conduct an investigation on site." Texas Incident: I-9613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-09-21
53602 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-09-10 | 2018-09-13 12:11 | 2018-09-13 | AGREEMENT STATE REPORT - REPORT OF LEAKING MEDICAL SOURCE The following excerpted information was obtained from the State of Washington via email: "On 8/31/2018, two [70 microCurie] I-125 seeds were implanted into a patient's breast associated with an RSL [radioactive seed localization] procedure; they were explanted on 9/4/2018. On 9/5/2018, [the State of Washington] was notified by a Nuclear Medicine Technician from Polyclinic-Madison Center (904 Seventh Avenue, Seattle) that I-125 seeds had been returned to them following a pathologic exam at the Polyclinic Histology Laboratory." "The leaking seeds and surgical clips were placed in a shielded container that housed multiple seeds undergoing decay-in-storage prior to disposal. The three plastic containers that were used (specimen cup, sentinel node container, and breast tissue container) have sealed lids and are presently located in the shielded Biodex storage locker located in Polyclinic's nuclear cardiology Hot Lab at Madison Center. All three containers have internal I-125 contamination from the leaking seed. In an attempt to establish a mechanism of action for the leaking source, the surgeon was interviewed and nothing in the way of an apparent cause was identified. Additionally, the surgical notes did not identify any anomalies." "Although a breach of source containment occurred for an unknown cause, the radiation exposures received by personnel involved with handling of the leaking seed and the patient that had the seed implanted in breast tissue for four days were assessed as not representing a safety issue for any individual." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-09-21
53601 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2018-09-13 | 2018-09-13 08:24 | 2018-09-13 | HURRICANE NOTIFICATION PER TECHNICAL REQUIREMENT FOR HURRICANE FLORENCE "A hurricane is within 500 nautical miles from Indian Point Energy Center with wind speed in excess of 87 knots. The National Weather Service has issued a hurricane warning for a hurricane with wind in excess of 87 knots (approximately 100 mph) within 500 nautical miles of the facility. Per the Technical Requirement Manual a prompt report shall be made to the NRC Incident Response Center within 1 hour of receipt of that hurricane warning. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Hot Shutdown |  | Power Operation | Hot Shutdown |  | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2018-09-13
53600 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2018-07-19 | 2018-09-12 16:19 | 2018-09-12 | PART 21 - MOTOR OPERATED POTENTIOMETER DEFECT "A batch of Motor Operated Potentiometers (MOPs) supplied by ESI [Engine Systems Inc.] were found to contain motors that, as they accumulate run time, exhibit increasing current draw and eventually exceed the MOP circuit allowance. Consequently, the motor operation becomes erratic which leads to a sluggish MOP. The MOP is used in a safety-related system to control emergency diesel generator (EDG) output voltage. Failure of the MOP to operate properly can negatively affect the EDG output voltage which affects associated components required to safely shutdown the nuclear reactor. "ESI will revise the test procedure to incorporate an extended run time while trending the motor for any adverse changes. This will be completed within 30 days and will prevent reoccurrence. "For Catawba, any MOPs from this batch are considered suspect and may be returned to ESI for rework or replacement. For units installed, the motor performance should be assessed prior to continued use. The voltage measured across terminals 3(-) and 4(+) while the MOP is operating should remain steady within a range of 22.8 to 25.2 VDC. Any step change or reduction in voltage is an indication of motor deterioration. "The root cause of the excessive current draw was found to be build-up of carbonaceous deposits between the commutator sections of the motor either from the carbon brushes, contamination, or a combination of the two. As the motor accumulated run time, the deposits propagated to the point of a low resistance path between commutator sections which are wired to the armature poles. This affected the magnetic field within the motor which had a direct impact on motor performance. ESI has limited the issue to a single date code of motors supplied within a single batch of MOPs, as listed. "Motor Operated Potentiometer, PIN 72-07900-100-ESI. "Duke Energy Catawba, Customer PO 196046, Qty: 6, ESI Serial Number 3013905-1.1-1 thru 6, MOP Serial Number - H01931980, H01995582, H01995584, H01995585, H01995586, H01995587, C-of-C Date: 5/30/2015." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-09-12
53599 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-09-12 | 2018-09-12 14:14 | 2018-09-12 | CONTRACTOR SUPERVISOR TESTS POSITIVE ON FITNESS-FOR-DUTY TEST "At 1115 EDT on September 12, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for drugs during a Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. The Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-09-12
53598 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2018-09-11 | 2018-09-11 23:23 | 2018-09-11 | WELD DEFECT ON PRESSURIZER INTERFACE "At 2200 EDT on September 11, 2018, during inspections as part of the pressurizer bare metal inspection program, an apparent weld defect was identified on Class 1 pressurizer level piping at the piping to pressurizer interface. The reactor is currently defueled in a refueling outage. Appropriate repairs will be made during the refueling outage." NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | [9 empty] | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-09-11
53597 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2018-09-11 | 2018-09-11 18:42 | 2018-09-11 | UNANALYZED CONDITION "On 9/10/2018, the 11 Core Spray (CSP) loop was placed in service to support quarterly surveillance testing. With the 11 CSP pump in service it was identified that the check valves isolating the 11 CSP system from the keep fill supply were leaking by. At 1129 CDT on 9/11/2018, it was identified that this leakage may have exceeded the leakage rate assumptions made in the dose analysis calculation for emergency core cooling system (ECCS) leakage outside containment following a loss of coolant accident (LOCA). Therefore, this is being reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. "The potential ECCS leak pathway has been isolated. There is no impact to health and safety of the public. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2018-09-11
53596 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-09-07 | 2018-09-11 18:23 | 2018-09-11 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was received from the State of California via email: "HDT&I doing business as American Engineering Laboratories, Inc. had a CPN moisture density gauge (MC39048771 containing nominally 10 mCi of Cs-137 and 50 mCi of Am-241/Be) run over by construction equipment at a temporary job site in Monterey Park on Friday, September 7, 2018 around 1400 PDT. The gauge operator notified his [radiation safety officer] RSO of the accident. He sent photographs of the broken handle and said the source rod was bent. In accordance with the RSO's instructions, the source rod was retracted, secured inside the transport box, and taken to their permanent storage site. Upon return from his travel, the RSO was able to visually inspect the damaged gauge on Sunday, September 9, 2018 and instructed the gauge operator to transport it to the CPN service center on Monday, September 10, 2018. "On Monday, September 10, 2018, the damaged CPN gauge was brought to the CPN service center for evaluation and it was discovered that the tip containing the Cs-137 source had apparently broken off from the source rod in the accident. The Am-241/Be source was secure in place. The gauge operator and the RSO went to the accident site with a Geiger-Muller survey meter to search for the missing source after contacting the job site supervisor that they were returning to search for the lost radioactive source and to ensure personnel/equipment were not working in that area. The gauge operator was able to locate the Cs-137 sealed source at the job site, and used 8-inch long pliers to place it into the gauge's shielding. The gauge was then placed into the transport case and transported back to the service center for evaluation and emergency leak testing of the sealed source." California Report No.: 5010-091018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-09-19
53595 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-09-11 | 2018-09-11 17:53 | 2018-09-11 | CONTRACTOR SUPERVISOR TESTS POSITIVE ON FITNESS-FOR-DUTY TEST "At 1430 EDT on September 11, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for drugs during a Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-09-11
53594 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2018-09-11 | 2018-09-11 17:14 | 2018-09-11 | TECHNICAL SUPPORT CENTER VENTILATION NON-FUNCTIONAL "On September 11, 2018 the Technical Support Center (TSC) ventilation was discovered to be non-functional during system testing. At 1310 EDT, an air leak was identified that prevented the modulating dampers to operate as designed to maintain required pressure. The air leak was not able to be repaired within a 60 minute period. This failure affected the ability of the TSC ventilation system to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities of the TSC are unaffected by this emergent condition. The air leak has been repaired and post maintenance testing was completed satisfactory at 1654 [EDT], restoring the TSC ventilation to a functional condition. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to the potential loss of an emergency response facility because of the unavailability of the ventilation system." The NRC Resident Inspector has been notified. | 97 | 88 | 0 | 97 | 88 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-09-11
53593 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-09-11 | 2018-09-11 05:17 | 2018-09-11 | CONTROL ROOM EMERGENCY VENTILATION SYSTEM INOPERABLE "At 0113 EDT on September 11, 2018, it was discovered both trains of CREVS [control room emergency ventilation system] were simultaneously inoperable; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." The door to the main control room habitability zone from the turbine building was left open and unattended for about a minute, breaking the pressure boundary in the room, resulting in an alarm. The door was closed, clearing the alarm and the CREVS was considered operable. | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-09-11
53592 | 0 | NUCOR STEEL CORPORATION |  |  |  |  | 2018-09-10 | 2018-09-10 16:02 | 2018-09-10 | DAMAGED GAUGE On September 10, 2018 at approximately 0130 EDT a gauge containing a 1 Curie Am-241 source fell and was damaged. The area surrounding the gauge was isolated and the gauge was locked in a secure cabinet. On contact readings were 420 microR/hr and readings at 1 foot were 35 microR/hr. The gauge shutter has been repaired and the gauge has been reinstalled. There were no overexposures as a result of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-09-18
53591 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-09-07 | 2018-09-08 17:44 | 2018-09-08 | AGREEMENT STATE REPORT - ADMINISTERED DOSE LOWER THAN PRESCRIBED DOSE The following information was received from the state of North Carolina via email: "A patient being treated for liver tumors was prescribed to receive 47.6 mCi of Y-90 microspheres, but instead received only 11.9 mCi (about 25 percent of prescribed). The remainder was in the vial as residual. "Because this under-dosing was not due to stasis or emergent patient conditions, and the delivered dose was less than 20 percent of that prescribed, this constitutes a reportable medical event according to the 2016 version (9) of the NRC guidance for Y-90 microspheres. "Source: Microspheres Radionuclide: Y-90 Manufacturer: Sirtex Medical Model: Sir-Spheres S/N: Aggregate "Investigation is pending for the Medical Event." North Carolina Tracking Number: 180039 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-09-17
53590 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2018-09-07 | 2018-09-08 01:38 | 2018-09-08 | NOTIFICATION OF ENVIRONMENTAL REPORT TO ANOTHER GOVERNMENT AGENCY "At 2210 EDT on September 7, 2018, Duke Energy personnel determined that the following event required notification of a federal agency, North Carolina State agency and a local agency for a chemical spill exceedance. "At 2140 EDT on September 7, 2018, plant personnel identified a sodium hypochlorite spill of more than the reportable quantity of 75.9 gallons. This notification is being made as a four-hour, non-emergency notification for a Notification of Other Government Agencies. This event is reportable in accordance with 10 CFR 50.72(b)(2)(xi). "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-09-08
53589 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2018-09-07 | 2018-09-07 20:56 | 2018-09-07 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "[Indian Point Unit 3] entered Technical Specification 3.0.3 for Safety Injection Boron Injection Tank Header Inoperable due to a thru weld leak at the thermal well rendering two Safety Injection Pumps Inoperable. Plant shutdown was started 1803 hours EDT." The licensee plans to be in Mode 4 at 0600 EDT on 9/8/2018. There is no impact to Unit 2. The licensee notified the NRC Resident Inspector and the State of New York. | 0 | 40 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2018-09-07
53588 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-09-07 | 2018-09-07 17:11 | 2018-09-07 | AGREEMENT STATE REPORT - GAUGE STUCK SHUTTER The following information was received from the State of Texas via email: "On September 7, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that during plant maintenance on a vessel, the handle on a Vega model SH-F2 nuclear gauge containing a 70 millicurie (original activity) Cesium-137 source was broken and the shutter was stuck in the half closed (half open) position. The license stated because of the location of the gauge on the vessel it does not create an exposure risk to any individual. The licensee has contacted a service provider to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: 9611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-09-17
53587 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2018-09-07 | 2018-09-07 16:00 | 2018-09-07 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following was received from the State of Utah via fax: "On September 5, 2018, a portable gauge user from Kleinfelder, Inc. (Radioactive Materials License UT 1800085) was performing compaction measurements at a field location in West Jordan, Utah. After performing a test, the operator placed the Troxler 3440 (s/n 19966) gauge on the tailgate of the licensee's vehicle to move to another location. The gauge fell off the tailgate of the truck, struck the pavement, and cracked the gauge case. The licensee performed exposure rate measurements of the gauge and incident site, and determined that the sealed sources were intact and that no contamination was present at the site. The licensee secured the damaged gauge in the transportation package, transported the gauge to the licensee's facility, and secured the gauge in the licensee's gauge storage cabinet. The licensee is conducting an investigation into the incident, and will submit a written report to the Division of Waste Management and Radiation Control (Division) within 30 days." Utah Event Report ID No.: UT180007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2018-09-17
53586 | -1 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2018-09-07 | 2018-09-07 15:13 | 2018-10-03 | SAFEGUARDS REPORT Actual intrusion of an unauthorized person into the controlled access area. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 10/03/2018 AT 1449 EDT FROM BRITAIN FOSTER TO RYAN ALEXANDER * * * After subsequent review of the events, the licensee determined that an actual intrusion of an unauthorized person into the controlled access area did not occur. Therefore the licensee is retracting this event. The licensee notified the NRC Resident Inspector and Regional-based Inspectors. Notified R1DO (Lilliendahl) and 73.71 Safeguards Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-09-07
53585 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2018-09-07 | 2018-09-07 13:14 | 2018-09-07 | AGREEMENT STATE REPORT - ADMINISTERED DOSE LOWER THAN PRESCRIBED DOSE The following information was received from the Commonwealth of Kentucky via fax: "At approximately 1045 [EDT] on September 7, 2018 an Authorized User at Hardin Memorial Hospital (HMH) called the RHB [Radiation Health Branch] supervisor to report a medical event. A HMH medical physicist determined a patient received 70 percent of an intended brachytherapy dose; the same Authorized User is adding seeds to bring the dose up to acceptable range. RHB staff have contacted the HMH Radiation Safety Officer and are awaiting further information on the possible medical event." Kentucky Event Report ID No.: KY180003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2018-09-17
53584 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2018-03-19 | 2018-09-06 17:18 | 2018-09-06 | INVALID SPECIFIED SYSTEM ACTUATION "Pursuant to 50.73(a)(1) the following information is provided as a sixty (60) day telephone notification to the NRC. This notification, reported under 50.73(a)(2)(iv), is being provided in lieu of the submittal of a written LER [Licensee Event Report] to report a condition that resulted in an invalid actuation of the high pressure coolant injection (HPCI). At Nine Mile Point Unit 1, HPCI is a flow control mode of the normal feedwater system and is not an emergency core cooling system. "On March 19, 2018 Nine Mile Point Unit 1 (NMP1) was at 0 percent power and in cold shutdown in support of a planned maintenance outage. At approximately 0118 [EDT], a reactor water level transient initiated by the fill and vent of 12 Reactor Recirculation Pump (12 RRP) occurred. During the fill and vent, Reactor Pressure Vessel (RPV) level lowered quickly from the initial level of 68 inches and a low level alarm was received. Control Room Operators reduced Reactor Water Clean-Up (RWCU) reject flow to turn the level trend and clear the low level alarm generated off of the compensated, GEMAC, level instrumentation. RWCU reject flow was reduced by 50 percent which caused RPV level to start to rise. RPV level was raised to approximately 72 inches at which time the Reactor Operator began to raise reject flow to reestablish the normal level band. During the RPV level transient, with actual water level at 74 inches on the GEMAC, the Yarway level instrumentation, which is not density compensated and therefore invalid, reached 92 inches causing an invalid high RPV water level turbine trip signal and associated invalid HPCI initiation signal. At no point in time did actual RPV water level reach the high RPV water level turbine trip set point of 92 inches. The potential for a turbine trip signal to occur due to shutdown activities was understood and tags were hung to lockout the Feedwater Pumps to prevent the HPCI start signal. Therefore, no HPCI injection occurred. "The Licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-09-06
53583 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-09-06 | 2018-09-06 16:46 | 2018-09-06 | AGREEMENT STATE REPORT - LOST OR STOLEN SOURCES The following was received state of Tennessee via email: "AMETEK conducted an inventory of their sources and found 4 sealed sources that were unaccounted for and possibly lost or stolen. The total amount of all four of the sources was 8.76 microCi. They are as follows: "Mixed gamma, 133 kBq, serial number 1249 Am-241, 2,200 Bq, serial number SS6712 Am-241, 3.873 kBq, serial number 1868 Sr-90, 5 microCuries" State Event Report ID NO.: TN-18-151 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-09-14
53582 | 0 | TILDEN MINING COMPANY L.C. |  |  |  |  | 2017-08-12 | 2018-09-06 12:45 | 2018-09-14 | GAUGE STUCK SHUTTER On August 12, 2017, the Tilden Mining Company experienced a stuck open shutter on a gauge in the Tilden Unit 1 Cooler Chunk Tunnel. The licensee determined that the shutter lever was jammed with debris preventing the shutter from closing. The gauge was repaired on August 15, 2017. The Ronan RLL 1 source contains 0.9 milliCurie of Cesium-137 (serial number 317287A). There were no overexposures as a result of this event. * * * UPDATE FROM LAWRENCE GRAY TO HOWIE CROUCH AT 1151 EDT ON 9/14/18 * * * The licensee reported that the gauge was not repaired on August 15, 2017 as previously reported but was repaired on September 13, 2017. Notified R3DO (Hanna) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-09-14
53581 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2018-08-02 | 2018-09-05 14:39 | 2018-09-05 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION ON A SEALED SOURCE The following information was obtained from the State of New York via fax: "Columbia University notified the New York State Department of Health (NYSDOH) on August 7, 2018 [regarding an August 2, 2018 event] of the detection of 592 Becquerel (0.016 microCurie) of removable radioactive material on a 10 milliCurie Ni-63 sealed source contained in a Shimadzu GC-8A II gas chromatography mass spectroscopy unit. The manufacturer and model number of the source were not available. The licensee immediately suspended the operation of the unit and placed the unit in storage. The source will be disposed of as radioactive waste and the equipment will be decontaminated prior to proper disposal by an authorized waste broker." New York Report Number NYDOH-18-02 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2018-09-13
53580 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2018-09-05 | 2018-09-05 12:53 | 2018-09-05 | NOTIFICATION TO A GOVERNMENT AGENCY FOR ASSISTANCE RELATIVE TO A MEDICAL EMERGENCY "At approximately 0608 Pacific Daylight Time (PDT), the Control Room was notified of a SONGS SCE [San Onofre Nuclear Generating Station Southern California Edison] employee experiencing a non-work related medical emergency outside the protected area, inside the owner controlled area. SONGS fire brigade was dispatched. Camp Pendleton Fire ambulance was requested. At 0644 [PDT] Camp Pendleton Fire department in communication with a doctor determined the victim is deceased. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) for a situation related to the health of on-site personnel for which a notification to other government agencies is planned. California Highway Patrol and Coroner notified and expect the California Occupational Safety and Health Administration (Cal-OSHA) will be notified. "NRC Region IV was notified (approximately 0900 PDT) as SONGS does not have a NRC resident inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-09-05
53579 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2018-09-03 | 2018-09-03 15:20 | 2018-09-03 | AUTOMATIC START OF THE EMERGENCY DIESEL GENERATOR "At 1045 [EDT] on 9/3/18, with Unit 1 and Unit 2 at 100% power, off-site power feed to the 'A' Reserve Station Transformer was lost which resulted in a loss of power to Unit 1'J' Emergency Bus. As a result of the power loss, the 1'J' Emergency Diesel Generator started as designed and restored power to the Emergency Bus. During this event, the Unit 1 'A' Charging Pump, 1-CH-P-1A automatically started as designed due to the loss of power event. "The valid actuation of these ESF [Engineered Safety Features] components due to the loss of power is reportable per 10 CFR 50.72 (b)(3)(iv)(A). "The Unit 1 'J' Emergency bus off-site power source was restored via the Unit 2 'B' Station Service bus and the 1 'J' Emergency Diesel was secured and returned to Automatic. The Unit 1 'A' Charging pump has been stopped and returned to Automatic. "Both Units are in a stable condition. The apparent cause for the loss of power appears to be a bird strike to the 'A' RSST [Reserve Station Service Transformer] Overhead Cable." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-09-03
53578 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2018-09-01 | 2018-09-01 13:52 | 2018-09-01 | FITNESS-FOR-DUTY - CONTRABAND DISCOVERED IN PROTECTED AREA Twelve (12) cans of an alcoholic beverage were discovered inside the protected area. The 12 cans were removed from the protected area and taken to and secured by site station security. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 0 | 2018-09-01
53577 | 0 | PRIME NDT SERVICES |  |  |  |  | 2018-09-01 | 2018-09-01 10:43 | 2018-09-01 | RADIOGRAPHY CAMERA STOLEN AND THEN RECOVERED While filling up a licensee company truck at a gas station located in Ripley, West Virginia, an individual stole the company truck and its associated radiography camera (QSA 880; S/N 677846;108 Ci; Iridium-192 source). The licensee notified LLEA (West Virginia State Police) and the vehicle was recovered. The licensee inspected the properly secured equipment and observed no impact to the radiography camera. The licensee stated there was no radiological impact to the public or employees. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | WV | OTH | AGR | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-09-10
53576 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2018-08-31 21:05 | 2018-08-31 23:26 | 2018-08-31 | MANUAL REACTOR SCRAM DUE TO MAIN CONDENSER DEGRADATION "This notification is being provided in accordance with 10 CFR 50.72(b)(2)(iv)(B). "On August 31, 2018 at 2105 CDT, Unit 2 Reactor Manual Scram signal was inserted due to Main Condenser vacuum degrading. The turbine was tripped following the scram. Main Condenser vacuum is at 6 inches of backpressure slowly improving following the scram and turbine trip. During the scram, one Control Rod (30-31) did not fully insert. Control Rod 30-31 has been manually inserted to position 00 with the first position identified as position 24. Plant is in a stable condition with reactor pressure being maintained by the Turbine Bypass valves. Reactor water level is being controlled with feedwater. Investigation into the cause of the elevated condenser in leakage is in progress. "The Senior NRC Resident has been notified." | 0 | 0 | 0 | 0 | 29 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-08-31
53575 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2018-08-31 05:44 | 2018-08-31 16:04 | 2018-08-31 | UNPLANNED LOSS OF STEAM LINE MONITOR CHANNELS "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) as a Loss of Emergency Preparedness Capabilities at Palo Verde Nuclear Generating Station (PVNGS) Unit 2. On August 31, 2018, at approximately 0544 Mountain Standard Time (MST), the Unit 2 control room experienced an unplanned loss of Steam Generator #1 steam line monitor (RU-139), Channels A and B. "This main steam line monitor is used in the PVNGS Emergency Plan to perform dose assessment in the event of a steam generator tube rupture. "The NRC Resident Inspectors have been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-08-31
53574 | 0 | INDIANA UNIVERSITY IUPUI/IUMC |  |  |  |  | 2018-08-31 09:00 | 2018-08-31 14:28 | 2018-08-31 | DOSE ADMINISTRATION PREVENTED BY KIT MALFUNCTION A patient was prescribed 86.9 milliCuries Yittrium-90 Theraspheres to the liver, but a malfunction in the kit prevented the Theraspheres from travelling to the dose location. There was no contamination detected on the patient or equipment. The patient was notified and rescheduled for this procedure next week. The manufacturer of the kit was notified and the hospital pulled all kits in that lot. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-09-10
53573 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-08-29 | 2018-08-30 09:58 | 2018-10-02 | CONCURRENT REPORT FOR AN OFFSITE NOTIFICATION MADE TO THE STATE OF TENNESSEE "This is a concurrent report of a 24-hour report that was made to the Tennessee Department of Environment and Conservation (TDEC) regarding an unauthorized storm water discharge. As permitted by the State of Tennessee, emulsified vegetable oil was being injected into ground water wells located on the North Site of NFS property. At approximately 11:00 [EDT], Environmental Safety was notified of a cloudy oil substance that was observed in the west storm water ditch. Injections were immediately ceased and immediate corrective actions were implemented. Oil absorbent pads and socks were deployed and samples were collected. Before noon on 8/29/2018, the cloudy substance was observed at the discharge of the storm water ditch into Martins Creek. Because of the discoloration observed at the entrance to Martins Creek, this event required a 24-hour notification to TDEC (made at 16:15 on. 8/29/18) and a five day written report will be submitted. Analysis of the grab samples indicated no radioactive material release. "The licensee notified the NRC Resident Inspector." * * * RETRACTION AT 1039 EDT ON 10/02/18 FROM TIMOTHY KNOWLES TO JEFF HERRERA * * * "On 8/30/2018, NFS made an event report to the NRC Operations Center regarding a concurrent report of a 24-hour report that was made to the Tennessee Department of Environment and Conservation (TDEC) regarding an unauthorized stormwater discharge. Based on the determination that the unauthorized stormwater discharge involved a minor non-radioactive chemical spill that did not affect the safety of NRC licensed material, NFS is retracting the event report. This is consistent with guidance provided in FCSS Interim Staff Guidance - 12, 10 CFR Part 70, Appendix A - Reportable Safety Events, Section 3.5.2 Other Government Notifications." Notified the R2DO (Coovert), NMSS and Fuels Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-09-07
53572 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-08-28 12:40 | 2018-08-29 12:28 | 2018-08-29 | AGREEMENT STATE REPORT - LEVEL GAUGE STUCK SHUTTER The following information was obtained from the State of Illinois via email: "The RSO of Roquette America, Inc. (IL-01033-01) called [The Illinois Emergency Management Agency] and left a message that he had a stuck shutter on a Kay Ray Mode! 70628P/ 5 milliCurie gauge. The shaft of the shutter is simply worn. Local Thermo servicemen arrived and got the shutter working temporarily. The device is still in service on the mill line and able to be manually closed as needed. All employees are aware that the device shutter must be manually closed should there be a problem with other equipment in the area. There are no exposures beyond normal operations associated with this event. The manufacturer will replace the device. " Illinois incident no. IL180035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-09-06
53571 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-08-16 | 2018-08-29 09:30 | 2018-08-29 | AGREEMENT STATE REPORT - LOST I-125 BRACHYTHERAPY SEED The following was received from the State of Florida: "[The State of Florida Bureau of Radiation Control] received a call from [the Medical Physicist] to report the loss of a [190 microCurie] I-125 brachytherapy seed. It is believed that the seed was removed from a patient between July 25 and 26 and placed into the biohazard waste container. The lost seed was discovered missing on Aug. 7th and all attempts to locate the seed have failed. "There was no adverse outcome in patient care from this incident. "No personnel or general public exposure would have been significant based upon the low exposure rate and the nature of controlled biohazard waste. The waste was incinerated. The majority of the radioactivity would have been released through the stack with minimal residual activity. No environmental impact is expected." Corrective actions taken include reeducation of proper documentation methods and reeducation of the proper use and checkoff of the inventory log. Florida Incident Report #: FL18-110 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-09-06
53570 | 0 | CURTISS WRIGHT NUCLEAR DIVISION |  |  |  |  | 2018-06-25 | 2018-08-28 13:41 | 2018-08-28 | PART 21 NOTIFICATION - SELECTOR SWITCH SHORTED DUE TO INCORRECT HARDWARE The following information is summarized and was obtained from Curtiss-Wright via fax: "Curtiss-Wright was notified by Exelon Calvert Cliffs Plant that a Senasys selector switch P/N 910CMC-5240X (previously provided by Curtiss-Wright under Exelon purchase order 00630804), had failed a post-installation test. Calvert Cliffs sent the suspect switch to Exelon Powerlabs where the failure was found to have been caused by an assembly screw that was 1/8 inch too long, allowing it to cut into the coil of the switch, causing an electrical short. Correspondence between Exelon and the manufacturer determined that an inventory error had occurred. "According to [Curtiss-Wright] records, only one customer and one plant received these defective switches. Exelon Generation's Calvert Cliffs received 5 switches on Exelon PO number 00630804 Rev. 2. Exelon Calvert Cliffs has been notified of this issue. "Curtiss Wright's dedication plan will be revised to include a note to ensure no selector switches, for this part number, are manufactured with the November and December 2017 date codes. "If you have any questions pertaining to this information, please contact Timothy Franchuk, Director of Quality Assurance, at 513-201-2176" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-08-28
53569 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-08-26 | 2018-08-27 18:16 | 2018-08-27 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the State of California via email: "On August 27, 2018, [the licensee's radiation safety officer] RSO contacted the Brea Office of the [California] Radiologic Health Branch to report that a moisture density gauge had been stolen from a gauge operator's truck in Santa Rosa, California. The operator stated that the gauge was stolen sometime between the evening of Saturday, August 25, 2018 and the morning of Sunday, August 26, 2018. The gauge was a CPN model MC-3, S/N M320906734 containing nominally 10 mCurie of Cs-137 and 50 mCurie of Am-241:Be. A report was filed with the Santa Rosa Police Department." California Report Number 5010-082718 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-09-04
53568 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-08-24 21:40 | 2018-08-27 13:26 | 2018-08-29 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO A RADIOGRAPHER The following information was obtained from the State of Oklahoma via email: "On August 27, 2018 [Oklahoma Department of Environmental Quality (DEQ)] were informed of an incident which occurred approximately 2140 CDT on August 24, 2018 involving 3 radiographers working for IRISNDT (OK-30246-02). The crew was working at a fabrication shop in Port of Catoosa, OK using a 95 curie Ir-192 source. The crew consisted of one certified radiographer, one radiographer trainer, and one assistant radiographer. The radiographer approached the collimator and knelt down over the guide tube. The assistant and the instructor unlocked the camera and walked back to the crank. Looking back at the camera, they did not see the radiographer and assumed he had already left the area. They began to crank out the source when the radiographer yelled and ran from the area. A re-enactment of the event using a pocket dosimeter recorded a dose of 62.1 mR, the direct reading dosimeter worn by the radiographer recorded a dose of 6 mR, probably due to shielding by the radiographers body. The whole-body badge reported a dose of 211 mR for the current month. A review of the daily exposure records for this monitoring period showed that the individual should have received approximately 155 mR previously, so the dose recorded for this incident is approximately 56 mR. Immediately after the incident the radiographer began complaining of a burning sensation and inflammation of his right shin area. [Oklahoma DEQ] are arranging with a local hospital to have him seen by a radiation oncologist. [Oklahoma DEQ] will conduct a reactive inspection of the licensee." * * * UPDATE FROM KEVIN SAMPSON TO OSSY FONT AT 1046 EDT ON 8/29/18 * * * The following was received via email from the State of Oklahoma via email: "After the reactive inspection yesterday, [Oklahoma Department of Environmental Quality] has determined that the injury reported by the radiographer was due to his hitting his shin on a stand as he ran from the area. It does not appear that this incident resulted in an over-exposure to anyone." Notified R4DO (Hay) and Doug Ballock and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-09-04
53567 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-08-25 | 2018-08-27 13:11 | 2018-08-27 | FLORIDA AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the state of Florida via email: "Ardaman & Associates, Inc., reported to [the Florida Bureau of Radiation Control] a damaged Troxler Gauge at Lake Brantley High School, 991 Sand Lake Rd, Altamonte Springs, FL 32714. Gauge was backed into by heavy equipment. Sources were not extended at the time, and are not damaged. All radiation readings taken after damage were normal expected values. The gauge was immediately retrieved and removed from work site. "Gauge is being transferred to Troxler Orlando Office for evaluation and determination for repair or replacement." The gauge contained an 8 mCi Cs-137 source and a 40 mCi AmBe-241 source. Florida Incident No. FL18-112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-09-04
53566 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-08-27 09:18 | 2018-08-27 13:15 | 2018-08-27 | OFFSITE NOTIFICATION "On 27 August 2018 at 0918 CDT Grand Gulf Control Room was informed that the onsite credit union silent alarm was actuated. The credit union is located outside of the Secure Owner Controlled Area (SOCA), but is located within the Owner Controlled Area. "GGNS [Grand Gulf Nuclear Station] Security entered an elevated security position at 0920 [CDT] and requested assistance from local law enforcement. Claiborne County Sheriff's Department responded to the site. Investigation of the area conducted with the assistance of GGNS Security personnel determined that the cause of the notification was not valid. GGNS Security stood down from the elevated security positon at 0945 [CDT]. "Pursuant to 10 CFR 50.72(b)(2)(xi), this issue is being reported as any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-08-27
53565 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2018-08-27 00:33 | 2018-08-27 03:12 | 2018-08-28 | AUTOMATIC SCRAM DUE TO A GENERATOR TRIP "At 0033 EDT Nine Mile Point Unit 2 experienced an automatic scram on high reactor pressure due to a turbine trip. The cause of the turbine trip was due to a generator trip. All control rods inserted. There were no safety system actuations. The cause of the generator trip is being investigated. "This is a 4-Hour report for 10CFR50.72(b)(2)(iv)(B) RPS Actuation. "The NRC Resident Inspector has been notified." Decay heat is being removed via the main condenser. Reactor vessel water level is being maintained by the condensate and feedwater systems. The licensee will be notifying the state of New York. * * * UPDATE FROM DANIEL CIFONELLI TO HOWIE CROUCH AT 1653 EDT ON 8/28/18 * * * After further review, the licensee has determined that the cause of the automatic scram was due to turbine control valve fast closure as a result of the turbine trip, not high reactor pressure, as originally reported. The licensee has notified the NRC Resident Inspector. Notified R1DO (Lilliendahl). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-08-27
53564 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2018-08-24 | 2018-08-24 16:35 | 2018-09-24 | AGREEMENT STATE REPORT - IMPROPER DISPOSAL OF RADIOACTIVE MATERIAL The following information was received via E-mail: "Oklahoma DEQ [Department of Environmental Quality] notified the Kansas Radiation Control Program of a rejected waste shipment from Kansas. "Preliminary information is the waste was not generated from licensed work. A patient who had received what is believed to be an I-131 dose at an unaffiliated facility came in for labs. Blood was drawn and needle was disposed in sharps without the knowledge of contamination by the lab personnel. The survey data on the waste was reported as 500 microR/hr on surface of the waste package." See EN 53561. * * * UPDATE ON 8/25/2018 AT 1737 EDT FROM DAVID LAWRENZ TO OSSY FONT * * * The following update was provided via E-mail: "The originator of the waste has a radioactive material license, however the package containing the contaminated waste was not from the radiology department where licensed activity occurs. Furthermore the licensee does not use I-131 or any isotope with a half-life nearly as long. [Kansas Radiation Control] will visit the site next week to determine what the dose estimates are for those in the waiting room, lab staff (both blood draw and blood testing), waste transporter and waste handlers. [Kansas Radiation Control] also intend to identify where the blood vial and associated potentially contaminated waste is stored/disposed. "It will likely prove impossible to discover the licensee who administered the I-131 to the patient as the individual did not report they were recently treated, there was no surveys in their unrestricted portion of their facility that is unaffiliated with their RAM [radioactive material] work, and the waste is mixed in with several other patients over the course of several days." * * * UPDATE FROM DAVID LAWRENZ TO VINCE KLCO ON 9/24/2018 AT 1509 EDT * * * The following update was provided via E-mail: "Oklahoma DEQ notified the Kansas Radiation Control Program of a rejected waste shipment from Kansas on 8/24/2018. This was reported to the HOO by David Lawrenz on the same day. "The Cancer Center of Kansas (CCK) was contacted by Stericycle, the company that handles sharps disposal, August 23, 2018. Stericycle stated they had received a radioactive sharps container from CCK. During a phone call with Stericycle, David Lawrenz learned the sharps container had been picked up last week and delivered to the incinerator facility on Monday August 20th. "Preliminary information is the waste was not generated from licensed work. A patient who had received what is believed to be an I-131 dose at an unaffiliated facility came in for labs. Blood was drawn, and needle was disposed in sharps without the knowledge of contamination by the lab personnel. The survey data on the waste was reported as 500 microR/hr. on surface of the waste package on 8/24/18 when [redacted] picked up the container from Stericycle. "After [redacted] picked up the sharps container on 8/24/18, it was determined the sharps container came from the CCK lab. [redacted] took surveys on the exterior of the container and found 500 microR/hr for the highest reading prior to returning to CCK. The CCK lab is separate from the CCK radiology department and the sharps containers are used separately as well. The CCK lab is not a restricted area and no radioactive material is used there. Consequently, the sharps from the lab were not monitored for radioactive contamination. "With the knowledge that the sharps came from a department that does not handle radioactive material and the fact that so much time had passed we determined the radioactive contamination must have originated from outside CCK. CCK only uses Tc99m. CCK is authorized for 35.100 and 35.200 use only. CCK is a cancer specialty clinic so the most likely scenario is that a patient had very recently undergone I-131 therapy at another facility and then came to CCK for lab work. The discarded lab detritus from that patient was then placed in the sharps container that Stericycle collected. "On August 27, 2018 [two individuals from the Kansas Department of Health and Environment] arrived at CCK and met with [the Lab Supervisor]. [redacted] took surveys of the sharps container and lab area. This area is separate from the radiology department. No areas were above background. "[The Lab Supervisor took Kansas personnel] to the hot lab used under the Adams Diagnostics 12-B880. The rejected waste is now stored for decay in the regulated area. [The Lab Supervisor] surveyed the container at 259 microR/hr on contact. "New procedures are being written to include surveys of the labs sharps container to prevent the issue from happening in the future. The licensee was found to not be in violation of any requirements and there will be no enforcement action as a result of this investigation unless new information comes to light. "Root cause analysis is a patient failed to follow instructions after the medical procedure." Notified the R4DO (Alexander) and NMSS Events via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-09-03
53563 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-08-24 10:34 | 2018-08-24 15:14 | 2018-08-24 | CONTRACTOR SUPERVISOR SUBVERTS A FOLLOW-UP FITNESS FOR DUTY TEST "At 1034 [EDT] on August 24, 2018, a contractor supervisor violated the licensee's Fitness-for-Duty (FFD) program by subverting a follow-up Fitness for Duty Test. The contractor's site access has been terminated. "The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-08-24
53562 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2018-08-24 | 2018-08-24 15:01 | 2018-09-13 | INOPERABLE SEISMIC MONITORING SYSTEM "At 0745 EDT on August 24, 2018, the Active Seismic Monitoring System failed a planned surveillance test and was declared inoperable. Compensatory measures to provide alternative methods for event classification of a seismic event have been implemented in accordance with the Fermi 2 Emergency Plan procedures. The compensatory measures include the use of information provided by the United States Geological Survey (USGS) to confirm if an earthquake has occurred within a 100 mile radius. "The loss of the Active Seismic Monitoring System is reportable to the NRC within 8 hours of discovery in accordance with 10CFR50.72(b)(3)(xiii). "No seismic activity has been felt onsite and the USGS recorded no seismic activity in the area. "The NRC Resident Inspector bas been notified." * * * RETRACTION FROM JEFF GROFF TO VINCE KLCO ON SEPTEMBER 13, 2018 AT 1524 EDT * * * "After further review the Active Seismic Monitoring system was removed from service for planned maintenance for a duration less than 72 hours with appropriate compensatory measures established. Therefore, no major loss of emergency assessment capability occurred. In addition, the surveillance tests were re-performed and the Active Seismic Monitoring System was declared Operable. Therefore, no reportable condition existed and EN 53562 reported on August 24, 20I8 is being retracted. "The NRC Resident Inspector has been notified." Notified the R3DO (Hanna). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-08-24
53561 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-08-24 | 2018-08-24 11:29 | 2018-08-24 | AGREEMENT STATE REPORT - IMPROPER DISPOSAL OF RADIOACTIVE MATERIAL The following information was received via E-mail: "This morning Oklahoma DEQ [Department of Environmental Quality] Radiation Management learned of an improper disposal of radioactive material in Oklahoma. Stericycle, an autoclave facility authorized to treat biomedical waste, rejected a load of material from a Kansas facility due to radioactivity. It appears the waste was received by SteriCycle on Wednesday, August 22 (because of an error in the report, this isn't totally clear), and is being picked up today (August 24) for return to the generating facility. SteriCycle did not provide DEQ with any specifics on radiation levels measured, quantity, etc. DEQ has notified the Kansas radiation program, which will investigate. "SteriCycle identified the waste generator as: Cancer Center of KS - Wichita "SteriCycle is located at: Stroud, OK "We are informed that Kansas radiation control regulates the facility under the name Via Christi. "Since the material is being picked up today, Oklahoma DEQ did not attempt a site visit to investigate the material. We have informed the Kansas radiation program and understand they will be following up. There are no known significant exposures to workers or the public, and none are expected at this time. It is not clear that this is reportable, but we are notifying NRC out of an abundance of caution." See EN# 53564. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-09-03
53560 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-08-23 16:00 | 2018-08-23 18:12 | 2018-08-23 | ILLINOIS AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received from the State of Illinois via email: "The RSO [Radiation Safety Officer] for Rush University Medical Center in Chicago (IL-01766-01) notified the Agency [Illinois Emergency Management Agency, Bureau of Radiation Safety] at approximately 1600 [CDT] today that a reportable event transpired while attempting to administer Y-90 TheraSpheres. The licensee attempted to administer Y-90 to a patient this morning and was unable to move the dose through the tubing to the patient. A different administration route was selected and also met with inability to deliver the dose. This treatment was aborted. "A second patient was scheduled for Y-90 administration this afternoon. The licensee encountered resistance in the second delivery system and was unable to deliver the Y-90 dose. This treatment was also aborted. Both patients were imaged and verified to not have been administered any Y-90. The licensee is currently performing a PET [Positron Emission Tomography] scan on the delivery systems to look for occlusions that may have impeded delivery. IEMA [Illinois Emergency Management Agency] staff has requested information on lot numbers for the individual doses. "Details are pending from the licensee on root cause and lot numbers. The licensee will not administer any additional doses from this lot number until root cause is identified. Further details are pending." Illinois Item No.: IL180033 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-08-31
53559 | 0 | WATERFORD | 3 |  |  | [3] CE | 2018-08-14 16:00 | 2018-08-23 12:11 | 2018-08-23 | PART 21 REPORT - DEFECT OF WESTINGHOUSE 7300 PROCESS ANALOG CONTROL SYSTEM CIRCUIT CARDS "This is a non-emergency notification from Waterford 3. "10 CFR Part 21 Notification - Defect of Westinghouse 7300 Process Analog Control System circuit cards "On August 14, 2018, Entergy Operations, Inc. (Entergy) completed an evaluation of a deviation at Waterford Steam Electric Station, Unit 3 (Waterford 3) which concluded the condition constitutes a defect pursuant to 10 CFR Part 21. The Waterford 3 Site Vice President was notified of the result of this evaluation on August 21, 2018. An interim report stating that an evaluation of this deviation was in progress was submitted to the NRC on July 5, 2018 (Entergy letter W3F1-2018-0040, ADAMS Accession Number ML18186A694). "Three Westinghouse 7300 Process Analog Control System (PAC) circuit cards were identified to be failed due to failed hex inverter chips. Some of these cards were installed in applications which support the Ultimate Heat Sink (UHS) at Waterford 3. These PAC cards use Texas Instruments Part Number SN74LS04N, W113 hex inverter chips. The circuit card types of concern are Analog Comparator model number 2838A32G01, Control Board model number 2838A30G011, and Prom Logic model number 2838A33G01. Entergy concluded that this condition could have prevented the UHS from performing its safety function and thus could have created a substantial safety hazard. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2018-08-23
53558 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-08-22 18:03 | 2018-08-22 19:35 | 2018-08-22 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO FIRE "On 08/22/2018 at 1803 hours CDT, Browns Ferry Nuclear Plant declared an Unusual Event per EAL HU4, a fire potentially degrading the level of safety of the plant. "At 1748 CDT Unit 1 received a call reporting smoke coming from the 480V Condensate Demineralizer Panel 3 in the Unit 3 turbine building elevation 557'. At approximately 1803 [CDT], the incident commander on the scene confirmed a fire inside the panel and all three units entered 0-AOI-26-1, Fire Response. The board was subsequently de-energized by operations personnel and the fire was extinguished at 1806 CDT. SM [Shift Manager] exited EAL HU4 and all three units exited 0-AOI-26-1 at 1840 CDT. "Fire operations remain on scene to monitor. A team is being assembled for damage assessment and recovery. "The fire did not affect any safety systems, no plant transients resulted, and no injuries were reported. "This event is reportable within 1 hour IAW 10 CFR 50.72(a)(1)(i). "The NRC Resident inspector has been notified." Notified DHS SWO, FEMA Ops, DHS NICC, FEMA NWC (email) and NuclearSSA (email). | 79 | 100 | 100 | 79 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-08-22
53557 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-08-22 09:43 | 2018-08-22 11:23 | 2018-08-22 | AUTOMATIC REACTOR TRIP "At 0943 EDT on August 22, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 100 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. "The reactor automatically tripped due to a main turbine trip signal. An investigation is in progress. "The automatic actuation of the Reactor Protection System (RPS) is being reported as a four-hour report under 10 CFR 50.72 (b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight-hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-08-22
53556 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-08-21 23:12 | 2018-08-22 02:00 | 2018-08-22 | OFFSITE NOTIFICATION DUE TO HOLDING POND OVERFLOW "At 2322 EDT, Limerick Generating Station notified the Pennsylvania DEP [Department of Environmental Protection] that our plant waste water pond (holding pond) overflowed due to heavy rainfall in the area. Plant alignment changes were made and the holding pond stopped overflowing at 0017 EDT. Limerick Generating Station has not determined this release to contain oil, grease, or pollutants hazardous to the public." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-08-22
53555 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-08-16 19:00 | 2018-08-21 14:24 | 2018-08-21 | AGREEMENT STATE REPORT - SOURCE GUIDE TUBE DAMAGED The following was received via email from the State of Illinois: "On 8/16/18 at approximately 1900 [CDT], the licensee was conducting radiography operations at O'Hare Airport in Chicago, IL. At or around this time, a pipe being analyzed fell off the pipe stand onto the source guide tube, denting it and prohibiting source retraction. Chicago Fire Dept. personnel were contacted at approximately 2030 [CDT] and arrived at the facility. The licensee had established a control boundary at 2 mR/hr and maintained line of sight control over the source. The licensee's recovery team was concurrently deployed and was approximately one hour away. Chicago Fire Dept. contacted and advised IEMA [Illinois Emergency Management Agency] at 2150 [CDT]. Agency staff immediately began coordination with Chicago Fire Dept. and licensee personnel. Agency personnel were deployed at 2335 [CDT] for support operations. Licensee staff (authorized for source retrieval) were able to shield the source and subsequently work out the kink in the guide tube so the source could be cranked back into the device. Based on agency inspector observation, it is believed there were no overexposures as the scene was roped off and constant surveillance maintained. Individual dosimeters worn by the licensee staff indicate a maximum exposure of 25 millirem. Reenactments of the incident conducted after source retrieval support this conclusion. "The licensee contacted IEMA at 0330 [CDT] on 8/17/18 to confirm that the source had been secured at 0204 [CDT]. A written report was received from the licensee on 8/18/18. There was some confusion on the associated reporting requirements with this incident as 350.3048 (10 CFR 34.101) requires a report within 30 days. Additionally, 340.1220 (10 CFR 30.50(b)) requires reporting within 24 hours. Language in 340.1220(a) that is unique to Illinois and differs from its Federal counterpart (30.50(a)), may require reporting immediately. While compliance with this Illinois reporting requirement and the licensee emergency procedures remain under review, this matter is being considered closed." The device involved was a Delta 880, serial number D8400, equipped with a 52.6 Ci Ir-192 source, serial number 66323G. Illinois Item Number: IL 180032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-08-29
53554 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-08-20 18:56 | 2018-08-21 12:25 | 2018-08-21 | FAILED FITNESS FOR DUTY TEST "At 08/20/2018 at 1856 [EDT], it was determined that a contract supervisor failed a test specified by the FFD [fitness for duty] testing program. The individual's authorization for site access has been terminated. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2018-08-21
53553 | 0 | JANX |  |  |  |  | 2018-08-17 10:15 | 2018-08-17 20:30 | 2018-08-17 | INABILITY TO RETRACT RADIOGRAPHY SOURCE TO SHIELDED POSITION While the licensee was performing radiography work in Evansville, Indiana, a radiography camera source (SPEC-150; Ir-192; 46 Ci; Source S/N: ZE0316) became disconnected and did not return to the shielded position. The technician called the corporate radiation safety officer (RSO) at 1015 EDT on 8/17/2018, who then drove to the Indiana site. The RSO verified boundaries at the 2mR/hr level. The source was temporarily shielded while camera maintenance was performed. The source was returned to the camera, secured, and properly shielded within the camera. There was no indication of excessive dose. The RSO who retrieved the source received approximately 100 millirem (as indicated on their self-reading dosimeter). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-08-27
53552 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2018-08-16 15:19 | 2018-08-17 08:17 | 2019-01-08 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED EMPLOYEE At 1519 EDT on August 16, 2018, Exelon determined a non-licensed employee had a confirmed positive for a controlled substance during a random Fitness-for-Duty test. The employee's unescorted access to the plant has been terminated. The NRC Resident Inspector has been notified. * * * UPDATE FROM MICHAEL FITZWATER TO DONALD NORWOOD AT 1310 EST ON 1/8/2019 * * * The following is a correction to the reason for the Fitness-for-Duty test: At 1519 EDT on August 16, 2018, Exelon determined a non-licensed employee had a confirmed positive for a controlled substance during a follow-up Fitness-for-Duty test. The employee's unescorted access to the plant has been terminated. The NRC Resident Inspector has been notified of this correction. Notified R1DO (Bower) and FFD E-mail group. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2018-08-17
53551 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-08-16 08:40 | 2018-08-16 12:08 | 2018-08-16 | FITNESS-FOR-DUTY TEST POSITIVE FOR LICENSED EMPLOYEE "In accordance with 10 CFR 26.719(b)(2)(ii), this notification reports a licensed Operations employee had a confirmed positive for alcohol during a random fitness for duty test. The individual was not in the protected area and not performing licensed duties at the time of discovery. The employee's access to the plant has been suspended. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2018-08-16
53550 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-08-13 22:58 | 2018-08-14 02:18 | 2018-08-14 | AUTOMATIC REACTOR TRIP DUE TO GENERATOR LOCKOUT "At 23:58 (Central Daylight Time) Unit 2 Reactor Tripped [automatic reactor trip] due to a Turbine Trip/ Generator Lock Out. All Auxiliary Feedwater Pumps started due to steam generator Lo Lo levels. "Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IP0-007B. The Emergency Response Guideline Procedure Network has been exited. Decay heat is being rejected to the Main Condenser via Steam Dump Valves. "The cause of the Generator Lockout is currently under investigation." All control rods fully inserted in response to the automatic reactor trip. The licensee notified the NRC resident. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-08-14
53549 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-08-11 12:00 | 2018-08-13 12:05 | 2018-08-13 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE The following information was received from the State of Texas via email: "On August 12, 2018 at approximately 1135 [CDT]., the licensee notified the Agency [Texas Department of State Health Services] that one of its radiography crews had experienced a source disconnect. The event occurred on August 11, 2018, at approximately 1200 [CDT] at a temporary job site near Whitsett, TX. The device involved was an INC IR-100 (SN: 6792) containing a 91 curie iridium-192 source (SN: ZH0109). The crew had set up the device and performed a procedure shot and everything functioned properly. They performed the first shot of the job and the source would not retract into the device--it felt as though it had stuck on something. After a second unsuccessful attempt, the source was cranked back out into the collimator, boundaries set, and an authorized person came to the site and performed the retrieval. The drive cable and source were both new. There was no observable cause for the failure. The device and associated equipment will be sent to the manufacturer for evaluation. Per readings from all three individuals' self-reading pocket dosimeters, there were no overexposures. The source retriever's dosimetry badge is being sent for processing. An investigation into this event is ongoing. More information will be provided as it is obtained in accordance with SA-300." * * * UPDATE FROM KAREN BLANCHARD TO VINCE KLCO ON 8/13/18 AT 1559 EDT * * * The following update information was received from the State of Texas via email: "Clarification: The source assembly [never disconnected] from the drive cable. [The licensee was] unable to retract it back into the exposure device." Notified R4DO (Deese) and NMSS Events Notification Group via email. Texas Incident: I-9606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-08-21
53548 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-08-12 01:58 | 2018-08-12 02:58 | 2018-08-16 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN - LOSS OF 480 VOLTAGE EMERGENCY BUS "On 8-12-18 at 0158 EDT, Beaver Valley Unit 2 experienced a loss of 480 Volt 2P Emergency Bus. This resulted in a Loss of Safety Function due to the 2-2 Emergency Diesel Generator [EDG] being Inoperable coincident with the Residual Heat Release Valve (2SVS-HCV104). A Technical Specification shutdown is required per LCO 3.0.3." The Licensee also stated they were in an unanalyzed condition due to the EDG and Residual Heat Release Valve being inoperable at the same time. The Licensee is shutting down to Mode 5 (Cold Shutdown). The Licensee is notifying the Resident Inspector. The Licensee will be making a Press Release about the unplanned shutdown. * * * UPDATE ON 08/16/2018 AT 1424 EDT FROM BLASE BARTKO TO KEN MOTT * * * "On 8-12-18 at 0158 [EDT] Beaver Valley Unit 2 experienced a loss of 480 Volt 2P Emergency Bus. Per operational guidance, this was determined to be a Loss of Safety Function due to the Unit 2 Emergency Diesel Generator (EDG) being INOPERABLE coincident with the Residual Heat Release Valve (2SVS-HCV104) 10 CFR 50.72(b)(3)(v)(B) and (D). This was also reported as an Unanalyzed Condition 10 CFR 50.72(b)(3)(ii)(b). "No Press Release was performed for this event. "The NRC Resident Inspector was notified. "At 0410 [EDT] a Technical Specification Shutdown was commenced 10 CFR 50.72(b)(2)(i). "At 2011 [EDT] the 480 Volt 2P Emergency Bus was restored and energized. "Further evaluation of the event has determined that this event was not an Unanalyzed Condition and did not result in a Loss of Safety Function. The classifications of Unanalyzed Condition and Loss of Safety Function are being retracted. "The accuracy of the existing guidance relative to Safety Function has been entered in the Corrective Action Program and interim actions have been taken to provide accurate guidance." Notified R1DO (Young) via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2018-08-12
53547 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-06-29 | 2018-08-11 17:34 | 2018-08-11 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was received via email from the State of Ohio: "A process was set up to remove all tritium exit signs (over 100) from [General Motors LLC -] Lordstown Complex, all with replacement dates of 8/1/2014. After reviewing records during an annual self-evaluation audit of self-luminous exit signs located at the Lordstown Complex, 2300 Hallock Young Road, Lordstown, Ohio 44481, it has been determined that up to 34 tritium exit signs are potentially missing. An investigation was launched to try to determine the location of these signs. The Lordstown Complex will continue to periodically search for these exit signs, and employees will be instructed to notify the Environmental Engineering department if any exit signs are discovered. There are no self-luminous tritium exit signs left in operation at the Lordstown Complex. Other than the 34 misplaced exit signs, all others have been transported off site to the recycling facility, Isolite Corporation." Ohio NMED Report: OH180007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf THIS MATERIAL EVENT CONTAINS A "NOT RECORDED" LEVEL OF RADIOACTIVE MATERIAL THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-08-20
53546 | -1 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-08-10 | 2018-08-10 23:13 | 2018-09-29 | EMERGENCY DIESEL GENERATOR COOLING WATER PUMPS DECLARED INOPERABLE "On 8/10/2018 at 1445 [CDT] both trains of Cooling Water [Cooling Water Pumps for Emergency Diesel Generators] were declared INOPERABLE and both units entered [Technical Specification] (TS) 3.0.3 due to corroded jacket cooling water plugs for [the] 12 and 22 cooling water pump motors; therefore this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). At 1543 [CDT], 08/10/2018 the 121 Cooling Water pump was aligned to the "A" Cooling Water train and the TS 3.0.3 condition was exited for both units. [After restoring train A cooling water the site entered a seven day limiting condition for operations, TS 3.7.8 for one inoperable cooling water pump.] "There was no impact on the health and safety of the public or plant personnel." The NRC Resident Inspector has been notified. * * * RETRACTION ON 09/29/2018 AT 2128 EDT FROM BRIAN JOHNSON TO OSSY FONT * * * "Testing and forensic analysis performed subsequent to the notification has determined the as-found condition would not have impacted either diesel-driven pumps' ability to start, run, and meet flow/pressure requirements to perform their required safety function. Therefore, EN# 53546 is being retracted. "The NRC Resident Inspector has been notified of the Event Notification retraction." Notified R3DO (Kozak). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2018-08-10
53545 | 0 | US DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2018-08-09 | 2018-08-10 19:36 | 2018-08-10 | MISADMINISTRATION OF Y-90 MICROSPHERES "This event occurred on August 9, 2018, at the VA Portland Health Care System, Portland, Oregon. "The patient was to receive a prescribed dose of 134 gray to a segment of the liver as a treatment for liver cancer, with Y-90 microspheres. After the procedure, the [actual] dose to the intended segment was estimated as approximately 103 gray, 77 percent of the prescribed dose. "The patient has been notified. No harm to the patient is anticipated." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | OR | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-08-20
53544 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2018-08-09 | 2018-08-10 17:29 | 2018-08-10 | AGREEMENT STATE REPORT - MISADMINISTRATION OF Y-90 MICROSPHERES The following is a summary from a report received via email from the State of Oregon: On 08/09/18, the Oregon Health & Science University (OHSU) Radiation Safety Officer (RSO) reported a misadministered of Y-90 treatment. The activity was 294 Gy, more than twice what was in the written directive (WD), 136 Gy. The prescribed range was 109-163 Gy. The normal pre-procedure process, while still in Nuclear Medicine, includes a dose calibrator reading, which was done, and a decay calculation done based on the manufacturer's calibration data sheet. The two were within 10%. The decayed activity result (or calibrator reading) is supposed to be compared with the WD required activity before taking the dose up to Interventional Radiology (IR) for the preadministration measurements. For this case, the RSO was responsible for the calculation and verification, and should have noticed the incorrect dose before taking it to IR, but the comparison with the WD dose was not done. Another Y-90 dose had been delivered to Nuclear Medicine that morning to decay prior to a case the next week. This was the dose the Nuclear Medicine tech opened and measured, without checking the printed code on the shipping box, which includes the patient's initials. Additionally, another check is done by the nurse manager for these cases, who goes down the day before to verify what was received. The packing slip showed a 5 GBq dose, which was correct and it was the right shipping box. The interventional radiologist was informed as soon as the post-delivery calculations were confirmed. He spoke with the patient, and sent the patient to Nuclear Medicine to be imaged. The scan showed very good containment within the liver. The physician felt the patient actually should tolerate the dose, as he had considered administering a high ablation type of dose (>200 Gy), and because of where the dose was delivered. Corrective actions included a procedure modification; specifically, a dose verification step will be added when the dose is up in IR during the preliminary set-up with the nurse manager. Other steps will be put in place after further discussion. The event is being entered into the hospital notification system, and likely will receive further review at that level. The RSO will submit the full report within the required 20 days. Oregon Item Number: OR180002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2018-08-20
53543 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-08-09 | 2018-08-10 14:29 | 2018-08-10 | AGREEMENT STATE REPORT - FAILED GAUGE SHUTTER The following information was received via email from the State of North Carolina: "NC RMB (North Carolina Radioactive Materials Branch) was notified by an authorized service provider, Systems Service Corporation (License Number: 090-1071-1), that they had repaired a failed shutter on a fixed nuclear gauge located at International Paper located in Riegelwood, NC on 8/9/18. The shutter detent spring was corroded and dissolved due to its corrosive environment. The service provider removed the gauge and rebuilt it on site with another source housing. "No known overexposures occurred during this event and it is unknown at this time whether the shutter was in an open or closed position. However, this investigation is still ongoing at the time of this report. "No other generic implications at this time. No other notifications made. "Source & Device Information: TBD. This report will be updated once RMB completes its investigation." North Carolina Report Number: 180034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-08-20
53542 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-08-08 | 2018-08-09 16:38 | 2018-08-09 | AGREEMENT STATE REPORT - LEVEL GAUGE STUCK SHUTTER The following information was received via E-mail: "On August 9, 2018, the Agency [Texas Department of State Health Services] received a notice from the radiation safety officer that a line level gauge was stuck in the open normal operating position. The gauge was found to be stuck during a blow-down operation yesterday afternoon. The gauge is a Ronan SA1-F37 with a Cesium-137 100 milliCurie source (serial number M5513). The gauge is to be serviced by the manufacturer's technician next week. "The RSO was contacting the licensing section to request an amendment to the permit to operate the gauge in the stuck open position. "The gauge is fixed at least 20 feet above ground level on a vessel and should not cause any effects to personnel. No exposures were reported upon discovery and the gauge does not present an exposure risk to any individual. The RSO will report the repair or disposal once the gauge is serviced/inspected. The investigation into this event is on-going. Updates to be provided in accordance with SA300." Texas Incident #: I-9605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-08-17
53541 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-08-08 | 2018-08-09 16:25 | 2018-08-14 | AGREEMENT STATE REPORT - UNCONTROLLED SOURCE FOUND The following was received via email from the State of Tennessee "Bionomics in Oak Ridge, Tennessee was contracted by a metal recycler in Arkansas to pick up some radioactive material that was rejected by a metals processor. Bionomics made the pickup on August 1st. Upon opening the shipment on August 8th they discovered an orphaned radium source. Current survey information indicates that a contact reading on the device is 22 mRem/hr. The information printed on the device is as follows: "Manufacturer: MINE SAFETY APPLIANCES COMPANY Model: BILLION-AIRE ANALYZER Model #: 706P Serial #: 52328 Isotope: Ra-226 (150 microCi) (JULY 1966) [Calculated 147 microCi (August 2018)] "A follow-up report will be submitted within 30 days." * * * UPDATE FROM ANDREW HOLCOMB TO VINCE KLCO ON 8/14/18 AT 1211 EDT * * * The following information was received from the State of Tennessee via email: "Bionomics in Oak Ridge, TN was contracted by Tenenbaum Recycling Group (TRG) in Harrison, Arkansas, to pick up some radioactive scrap metals. Bionomics made the pick up on August 1st. Prior to leaving the site, the technician discovered a radium source within the pile of scrap metal scheduled for pick-up. On August 8th, Arkansas was notified by Bionomics and in turn notified the State of TN that a radium device had been picked up and was currently in Oak Ridge, TN at the Bionomics facility. Current survey information indicates that a contact reading on the device is 22 mRem/hr. The information printed on the device is as follows: "Manufacturer: MINE SAFETY APPLIANCES COMPANY Model: BILLION-AIRE ANALYZER Model #: 706P Serial #: 52328 Isotope: Ra-226 (150 microCi) "A follow-up report will be submitted within 30 days." Tennessee Event Report ID NO.: TN-18-140 Notified the R1DO (Young) and NMSS Events Notifications via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-08-17
53540 | 0 | RANCHO SECO |  |  |  | ISFSI | 2018-08-08 14:15 | 2018-08-08 17:49 | 2018-08-08 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 4 | CA | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2018-08-16
53539 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-08-02 | 2018-08-08 16:46 | 2018-08-08 | AGREEMENT STATE REPORT - PATIENT OVEREXPOSURE The following information was received via E-mail: "The licensee reported to the [Ohio] Department [of Health] on 8/3/2018 that a potential medical event had occurred due to a delay in a surgical procedure. The delay was caused by the insurance company rescinding approval to remove a breast tumor until three medical opinions were obtained. The licensee implanted a 472 microCi I-125 seed [radioactive seed localization] (RSL) in the tumor on 5/29/2018 after receiving approval from the insurance company. The surgery was scheduled for 6/4/2018. The expected dose to the patient was 12.65 Rem to the tissue and 1.52 Rem EDE [Effective Dose Equivalent]. The surgery was delayed until approval from the insurance company was obtained, and was performed on 8/2/2018. The delay resulted in a tissue dose of 99.45 Rem and EDE of 11.93 Rem. "A follow-up will be conducted with the routine inspection in September." Ohio State Report: OH180006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-08-16
53538 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-08-07 09:09 | 2018-08-07 14:45 | 2018-08-07 | CONTRACTOR SUPERVISOR TESTS POSITIVE FOR ALCOHOL "At 0909 [EDT] on August 7, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for alcohol during a random Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-08-07
53537 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-08-03 09:40 | 2018-08-03 14:10 | 2018-08-03 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "At 0940 EDT on August 3, 2018, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to failure of the over speed fan brake inverter. The brakes prevent fan over speed from a design basis tornado. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. Investigation into why the Division 2 MDCT fan over speed brake inverter failed is in progress. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) based on an unplanned HPCI inoperability. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-08-03
53536 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-08-02 15:30 | 2018-08-02 18:34 | 2018-08-06 | AGREEMENT STATE REPORT - MISSING PORTABLE DENSITY GAUGE The following information was received via E-mail: "At [approximately] 3:30 pm [MDT] on 8/2/2018, Eb Engineering reported that a portable density gauge was missing. A technician first discovered it at about 2:00 pm on 8/2/2018 when he came back from a job site; the gauge along with the transport box, chain, and lock were all missing from the truck. However, nothing else seems to be taken from the truck. He attempted to search along the roads he had been to, but nothing was found. He reported to another staff of this company and, at the time of this report, this staff is currently driving back to the job site to conduct another search. At this point, it has not been determined whether this gauge simply fell off the truck or was stolen. More information will be provided once available. Device Type: Density Manufacture: Troxler Model Number: 3411B Isotope and Activity: Cs-137, 8 mCi and Am-241/Be, 40mCi" * * * UPDATE ON 8/6/2018 AT 1630 EDT FROM SHIYA WANG TO ANDREW WAUGH * * * The following information was received via email: "The licensee attempted a few hours of search in the late afternoon and evening of 8/2/2018 but only found the chain and lock at a street cross section in Longmont, CO. In the morning of 8/3/2018, a public member contacted the licensee that he got the box. This public member found the box from the side of the street, thought it was a cooler, and brought it to his girlfriend's home. Then he saw the RAM label on the box and contacted the licensee in the morning of 8/3/2018. In the morning of 8/3/2018, the box and the gauge were then back to the licensee's possession shortly after the licensee got the call from this public member. When the box was returned from this public member to the licensee, the box was not locked but the gauge handle was locked. It did not appear to have any damage to the box or the gauge or the source. Overall, there were at least two public members involved in this event (the one who found the box and his girlfriend) but their exposures are still to be determined. Additional information will be included in the NMED report once available." NMED Event Report ID No.: CO180016 Notified R4DO (Vasquez), ILTAB, and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-08-10
53535 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-08-02 | 2018-08-02 16:46 | 2018-08-02 | AGREEMENT STATE REPORT - GAUGE FAILURES The following information was received from the State of Louisiana via email: "On 07/26/2018, [the] Radiation Safety Officer (RSO) for ExxonMobil Chemical Co. (ExMCo) reported a multi-source gauge failure to the Department [Louisiana Department of Environmental Quality], LDEQ by e-mail. On 07/25/2018 during routine annual maintenance and pm [preventative maintenance] checks it was discovered the level/density gauge had several shutters stuck in the open position. Three sources would not retract into the shielded position. However, the remaining four sources are functioning properly. "The gauge is a Berthold Technologies USA multi-source device, Model LB 300 IS, utilizing AEA Technologies, Model CKC.P4 sources. There are seven [nominal] 50 mCi Co-60 sources in the device. The sources involved in this malfunction are source #1 s/n 1369-08-02, source #2 s/n 1370-08-02, and source #6 s/n 1374-08-02. All three sources will not retract into the shielded position. The device has a SS&D Registration # TN-1031-D-801-S. "Only one device was manufactured and is no longer being manufactured. The manufacturer is Berthold Technologies GmbH & Co. KG, D-75323 Bad Wildbad Germany. The Berthold Model LB300 IS level density gauge is installed on G-Line High Pressure Reactor Vessel, V5300 and G-Line high pressure separator production line. "ExMCo engineers and Flowmaster/Berthold engineers & service company have been contacted to fix the problem by repairing the source holders or replace the device with other comparable technology. "Event type: The gauge is installed on processes and does not pose a health and safety threat to the general public or the ExMCo employees. The gauge will remain on the operational process until the repair is made to the device. This is considered an equipment failure for reporting requirements. "Event Location: ExxonMobil Chemical Co. Baton Rouge Plastics Plant 11675 Scotland Avenue, (Hwy 19) Baton Rouge, LA 70807, "Event description: Shutters stuck in the open position or difficult to operate shutters were detected on a level/density gauge installed on processes at ExMCo. A service company has been contacted to make the repair or replace the device. The Department will be provided a final report with corrective actions. The Department was notified and the incident was reported to the NRC Operation Center. The report to the NRC as required by 10 CFR Part 30.50 (b) (2) and required by LAC 33:XV.341.B.2.b." Louisiana Event: LA 180015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-08-10
53534 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-08-02 | 2018-08-02 14:23 | 2018-08-02 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received from the State of Texas: "On August 2, 2018, the Incident Investigation Program (IIP) was given a copy of a request for reciprocity to perform work on a nuclear gauge stuck shutter at the licensee's location. IIP searched its database and found that the gauge, a ThermoFisher model SUP-1C gauge containing a 100 millicurie (original activity) strontium - 90 source, had been reported as stuck and repaired on June 20, 2018 (EN 52815). The licensee was contacted and the radiation safety officer (RSO) stated the gauge General Lic - GLA had stuck again this time in the closed position. The gauge does not present an exposure risk to any individual. The RSO stated he did not realize a shutter in the stuck closed position needed to be reported. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: 9603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-08-10
53533 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2018-08-02 09:00 | 2018-08-02 13:09 | 2018-08-02 | OFFSITE NOTIFICATION DUE TO RELEASE OF POSSIBLE TRITIUM BEARING WATER The following was received via telephone and email notification from Millstone Power Station: Millstone Power Station Unit 3, identified that the underground pipe to the Condensate Surge Tank had leaked greater than 100 gallons of water that included trace amounts of tritium to the ground. The effected piping is inside the protected area and has been isolated and drained. No tritium has been detected in any monitoring wells outside of the Protected Area. There is no threat to employees or the public or impact to drinking water. The Connecticut Department of Energy and Environmental Protection, and the towns of Waterford and East Lyme were notified at approximately 1300 [EDT] on August 2, 2018. The licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-08-02
53532 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-07-26 | 2018-08-02 11:48 | 2018-08-30 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION EVENT The following information was received via E-mail: "During the process of shredding filters for cement solidification, the licensee had an unplanned contamination event. Loose surface contamination was spread throughout the building with an estimate of total activity being 2 milliCuries and the primary isotope being Cobalt-60. In addition to building surfaces, several personnel who were working in the area at the time were contaminated. It is unclear at this time the extent of the personnel contamination but inhalation and skin contamination are believed to have occurred. The licensee is currently decontaminating the area using protective clothing and respiratory protection, monitoring the individuals who were working in the area during the time of the event, and has sent a sample of the material to an independent lab for isotopic analysis. The licensee will be performing a root cause analysis and the state will perform a reactive inspection. The cause of the event is unknown at this time." PA Event Report ID No: PA180016 * * * UPDATE ON 8/29/2018 AT 1354 EDT FROM JOHN CHIPPO TO BRIAN LIN * * * The following update was provided via E-mail: "During the process for cement solidification of shredded filter materials the licensee's mixing unit auger became stuck. Technicians eventually, through the use of various manual and air tools, were able to remove the blockage and resume the solidification process. At this time the unit was run again with only a cement mixture with no filter media to create a cap in the disposal container. Upon completion of this procedure a crane operator entered the containment area to remove the filter media hopper from atop the unit. He had forgotten his hard hat and immediately left containment and the H-1 building to retrieve his hat. Upon entering the Personnel Contamination Monitor (PCM) he then set off the alarm. This was the first indication of contamination. The RSO was immediately contacted and all remaining personnel exited the building and were found to be contaminated. Immediately upon discovery of the incident, all doors to the contaminated building (the H-1 building) were locked, all operations equipment was placed in the off position, and the building was secured. Building access was then restricted. The plant manager stopped all work at the site and informed his chain of command. In the days following the event the licensee performed a detailed survey to assess the extent of contamination. The survey showed general distributed contamination of the horizontal surfaces within the building. The maximum contamination level identified with this survey was 800,000 dpm/100cm2. The primary isotope was Co-60 (-90%), with Mn-54 and Sb-125 as other contributors. "Seven personnel exhibited general distributed contamination of varying amounts on their exterior clothing and/or shoes and had indication of inhalation of radioactive material. All showered in the onsite Decontamination Room and then were monitored with an extended count in the PCM and all were released with only gamma related upper torso activity. Nasal swabs from affected personnel were analyzed, however the license has yet to share these or any other personnel dose data. Daily extended PCM counts continue for available personnel who exhibit upper torso gamma activity. Four individuals continue to exhibit this activity. In addition, in-vivo and in-vitro bioassay measurements were initiated and are in progress to complete the internal dose assessment process. It is expected that the offsite laboratory bioassay measurement data will be available in 2-3 weeks and the internal dose assessment will then be completed. "The H-1 Building Containment itself remains restricted. The H-1 Building Containment will remain restricted and the work activities related to the encapsulation of materials inside this containment have been suspended indefinitely. This status will continue until corrective actions have been implemented in order to prevent a reoccurrence of this incident. The licensee contends the initial root cause of the incident was inadequate procedure implementation and training regarding radiological containment inspection and certification. Corrective actions that are planned include: "1. H-1 Building Containment program overhaul. 2. Upgrade procedures to include routine containment inspections to be conducted and implement additional independent verification by Alaron's Radiation Safety staff. 3. Highlight Operational procedures to require signature requirement verifying proper ventilation alignment is functioning prior to commencement of work. 4. Alarming differential pressure gauges will be installed on the HEPA units to provide warning of both HEPA buildup and/or breakthrough. 5. The RSO will review the current application of constant air monitors against problematic conditions such as radon gas buildup to ensure alarm setpoints can adequately protect workers from excessive derived air concentrations in the work zone and retrain all staff. 6. The RSO will review and upgrade shield frisking stations to ensure proper contamination control in areas that have a high dose background. 7. Implement a recurring refresher training program in addition to the recertification training programs. 8. General Manager to conduct an all hands 1-day stand down to communicate priorities (i.e. Safety, Health and environmental stewardship are the top priorities; anyone can stop a job if they feel any of these are being compromised, etc.) "The cause of the event is believed to be inadequate procedure implementation and training." RIDO (Lilliendahl) and NMSS were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-08-10
53531 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2015-05-14 | 2018-07-30 17:10 | 2018-07-30 | AGREEMENT STATE REPORT - BRACHYTHERAPY SOURCE DID NOT FULLY RETRACT The following report was received by e-mail from the state of Illinois: "During a routine inspection [Illinois Emergency Management] Agency inspectors discovered an unreported event that occurred on May 14, 2015. On that date an intravascular brachytherapy procedure was attempted using two BRX-0346 extra-long delivery catheters with a Novoste transfer device and a 40mm Best Vascular, Inc. Sr-90 source train. On the initial treatment attempt, the source would not extend to the treatment location and was promptly returned to the transfer device. A kinked catheter was suspected and a second BRX-0346 XL catheter was put in place. The same train was sent into the second catheter and the same inability to reach the treatment location encountered. At this point, the hydraulic return mechanism failed to return the source train to the transfer device. The licensee's emergency procedure was employed and the entire system was manually removed from the patient. The transfer device, delivery catheter and source train were placed in a temporary storage container and locked in the hot lab. The patient was surveyed and no radioactivity was found to be above background. The treatment was aborted. "The licensee was able to determine that a deformation in the delivery catheter impeded movement of the source train to the treatment location. The source was found to be lodged in the catheter, approximately 11.3 cm from the attachment point to the transfer device. As a result, exposure occurred in the aortic root. Estimates on the exposure to the surrounding tissue is pending from the licensee. Best Vascular representatives were reportedly notified and arrived at the licensee's site the following day for evaluation and return shipping to the manufacturer. "A deformation in the catheter was confirmed as the root cause. The event was not reported to the State. Supporting documentation was reviewed on 7/30/18 and determined to be, at a minimum an equipment-related event. Pending exposure estimates, this is also being entered as a possible medical event and will remain open while the investigation continues. "Radionuclide: Sr-90 Activity: 58.65 mCi (2.17005 GBq) Dose: 18.4 rad (184 mGy)" Illinois Item Number: IL180031 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-08-07
53530 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-07-24 | 2018-07-30 15:42 | 2018-07-30 | AGREEMENT STATE REPORT - LOST PACKAGE OF RADIOACTIVE MATERIAL The following information was received from the State of Colorado via email: "Cardinal Health 414, LLC reported a lost package of Ra-223 in transit via [a common carrier]. The amount shipped was 11.4075 MBq (0.3083 mCi). The intended destination was Valley View Hospital in Glenwood Springs, Colorado. [The common carrier] is currently investigating the location of the package." Colorado Event Report ID No.: CO180014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-08-07
53529 | 0 | AMETEK SOLIDSTATE CONTROLS |  |  |  |  | 2018-05-01 | 2018-07-27 16:14 | 2018-07-27 | PART 21 NOTIFICATION - POTENTIAL DEFECT IN AC VOLTAGE SENSE BOARD "COMPONENT DESCRIPTION: 277VAC Voltage Sense Board. "PROBLEM YOU COULD SEE: In May of 2018, AMETEK Solidstate Controls (SCI) experienced failures during preventative maintenance with the 80-210833-90 AC Voltage Sense board during the startup of a unit. While the failures were experienced on commercial equipment, a version of the AC Voltage Sense printed circuit board is used in safety-related equipment as well. "CAUSE: The failure of the AC Voltage Sense Boards is caused by the opening of the 100 OHM 2W R7 metal oxide resistor, AMETEK SCI part number 03-804103-00, due to insufficient peak power withstand capability for the application. In all instances of failures experienced, the peak inrush power dissipation during startup caused the 2W metal oxide resistor to open. Failures have been limited to the metal oxide resistor. "EFFECT ON SYSTEM PERFORMANCE: If the 100 OHM, 2W metal oxide resistor in the R7 position (PN: 03-804103-00) of the AC Voltage Sense board experiences peak power above its rating and opens, the AC Voltage Sense board may fail. This failure could cause a false low AC voltage alarm and an inoperable high AC voltage alarm condition. During steady state operation, the resistor will not be exposed to power dissipation significant enough to impact the resistor. "This potential defect and 10 CFR 21 notification applies to SCI safety-related 277VAC version of the AC Voltage Sense printed circuit board: 80-9210842-90 - PCB ASSY, VLT SENSE 277VAC, 1PH. "ACTION RECOMMENDED: The R7 metal oxide resistor is being replaced in the 80-9210842-90 version of the AC voltage sense printed circuit board with a wire-wound resistor (PN: 03-804103-10). The AC Voltage Sense Board will be revised to revision level 'I'. AMETEK recommends replacing any prior revisions of the 277VAC AC Voltage Sense boards at the earliest convenience. "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: If you wish to replace the 277 VAC AC Voltage Sense Board with the latest revision, AMETEK Solidstate Controls will work with you to arrange replacements. Please contact Mr. Mark Shreve of our Client Services group at 1-800-222-9079 or 1-614-846-7500 ext. 6332. mark.shreve@AMETEK.com. "AFFECTED CUSTOMERS The list below identifies all AMETEK Solidstate Controls customers who have purchased the printed circuit board 80-9210842-90 since 2008. Any purchases prior to 2008 should have been replaced according to the recommended preventative maintenance schedule and, therefore are not applicable to this 10 CFR 21 notification." China Nuclear, Edison Material Supply, Energy Northwest, Jade Dragon Trading, Korea Hydro & Nuclear Power Company Limited, KRSKO, Exelon Business Services - Braidwood Warehouse, Exelon Business Services - Braidwood/ Byron Generating Station, Georgia Power Company - Vogtle 1 & 2, Shenzhen Chance New Energy Scientific Instrument Co. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-07-27
53528 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-07-27 06:56 | 2018-07-27 13:41 | 2018-07-27 | CONTRACTOR SUPERVISOR TESTS POSITIVE FOR ALCOHOL A non-licensed contractor supervisor had a confirmed positive for alcohol during a random fitness-for-duty (FFD) test. The employee's unescorted access to the plant has been suspended. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-07-27
53527 | -1 | GENERAL ELECTRIC CO. |  |  |  | ADVANCED FUEL R&D AND PILOT PLANTS | 2018-07-26 13:55 | 2018-07-27 13:00 | 2018-08-07 | DISABLED VENTILATION SYSTEM "On 7/26/18 at approximately 1355 PDT, the Building 103 laboratory facility ventilation exhaust system was disabled during a scheduled evacuation drill at the Vallecitos Nuclear Center (VNC). "The system was restored on 7/26/18 at approximately 1407 PDT. There were no active fissile material operations in Building 103, thus no unsafe condition existed, and no release of material occurred. "This event is being reported pursuant to the requirements of 10 CFR 70.50 (b)(2)." The licensee will notify the NRC Region 4 office. * * * RETRACTION FROM SCOTT MURRAY TO HOWIE CROUCH AT 1031 EDT ON 8/7/2018 * * * "EN53527, made July 27, 2018, reported an event in accordance with 10CFR70.50(b)(2) in which the Vallecitos Nuclear Center Building 103 facility ventilation exhaust system was disabled for approximately 12 minutes. "At the time of the report, information regarding the special nuclear material (SNM) in the affected Building 103 areas was not available and a conservative decision was made that the ventilation system was required to prevent releases or exposures to radioactive materials exceeding regulatory limits or to mitigate the consequences of an accident. "Based on a subsequent review of SNM inventory records and additional survey measurements, it has been determined the event report should be retracted due to the minimal amount of SNM that could have been affected. "Notified R4 Fuel Cycle Decommissioning Branch and NMSS Enrichment and Conversion Branch." Notified R4DO (Vasquez) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 4 | CA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2018-07-27
53526 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-07-26 10:40 | 2018-07-26 17:51 | 2018-07-26 | CONTRACTOR SUPERVISOR SUBVERTS A FOR-CAUSE FITNESS FOR DUTY TEST "At 1040 [EDT] on July 26, 2018, a contractor supervisor violated the licensee's Fitness-for-Duty (FFD) program by subverting the Fitness for Duty program. The contractor's site access has been terminated." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-07-26
53525 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-25 | 2018-07-26 14:47 | 2018-07-26 | TEXAS AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was obtained from the state of Texas via email: "On July 26, 2018, the licensee notified the Agency [Texas Department of State Health Services] that on July 25, 2018, while using a crane to perform routine loading of a pipe on which was mounted a Berthold Model LB8010 density gauge, containing a 20 millicurie cesium-137 source, the pipe/gauge fell. The shutter handle was bent and the shutter, which was in the closed position, was not operable due to the damage. The licensee performed surveys to ensure the shutter was in the fully closed position. The licensee is making arrangements for the disposal of the device. There is no risk of exposure to any individual as a result of this event. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #9601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-08-03
53524 | 0 | SC DEPT OF HEALTH & ENV CONTROL |  |  |  |  | 2018-07-25 15:30 | 2018-07-26 07:15 | 2018-07-26 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following was received from the State of South Carolina via email. "On July 25, 2018, the Department [South Carolina Department of Health and Environmental Control] was notified by the licensee at approximately 3:30 PM [EDT] that one of its gauges had been run over by a bull dozer at a jobsite. The gauge was a Troxler Model 3430 (S/N 34618) containing 8 mCi of Cs-137 and 40 mCi of Am-241:Be. The sealed source serial number for the Cs-137 source is 77-1459 and the sealed source serial number for the Am-241:Be source is 47-30042. A radiation survey and wipe test of the gauge were performed at the scene. The gauge was safely transported back to the licensee's facility and placed in storage awaiting disposal." South Carolina Incident #: L548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2018-08-03
53523 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-07-23 20:00 | 2018-07-24 13:40 | 2018-07-24 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following report was received via e-mail: "At approximately [2000 hrs. CDT] last night (July 23) a crew working at the DBI, Inc. facility in Tulsa had a casting they were shooting fall on the guide tube, crushing it, so that the source (28 Ci of Ir-192) could not be retracted. The RSO [Radiation Safety Officer] was notified and responded to the scene. DBI is licensed to perform source recoveries which they successfully did. As far as we [Oklahoma Department of Environmental Quality] know right now, there were no over-exposures as a result of this incident. [The state of Oklahoma] will provide details on the equipment involved when we have them." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-08-01
53522 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2018-07-23 16:31 | 2018-07-24 00:57 | 2018-07-24 | UNPLANNED LOSS OF STEAM LINE MONITOR CHANNELS "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS [Emergency Notification System] or under the reporting requirements of 10CFR50.73. "This event is being reported pursuant to 10CFR50.72(b)(3)(xiii) as a Loss of Emergency Preparedness Capabilities at Palo Verde Nuclear Generating Station (PVNGS) Unit 2. On July 23, 2018, at approximately 1631 Mountain Standard Time (MST), the Unit 2 control room experienced an unplanned loss of Steam Generator #1 steam line monitor (RU-139), channels A and B. "This monitor is used to assess dose projections for Main Steam line exhaust while in Modes 1-4 and is used in the PVNGS Emergency Plan to perform classification of Initiating Conditions 'RS1' and' RG1' and Emergency Action Levels (EALs) 'RS1.2' and 'RG1.2'. The PVNGS Emergency Plan does have two additional EALs that can be assessed for each Initiating Condition. The loss of this monitor constitutes a reportable loss of emergency assessment capability. "The NRC Resident Inspector has been informed of this condition." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-07-24
53521 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-23 | 2018-07-23 18:33 | 2018-07-23 | AGREEMENT STATE REPORT - DAMAGED MOISTURE-DENSITY GAUGE The following was received from the State of Texas via email. "On July 23, 2018, the licensee reported that one of its Troxler model 3430 moisture/density gauges (SN: 68529) had been run over and damaged by a dozer at a temporary job site. The licensee's technician was performing a moisture test when he saw a dozer moving backward into the area and toward the gauge. The technician yelled at the dozer driver but was unable to get his attention and there was not enough time for the technician to move the gauge. The gauge was severely damaged. The 40 milliCurie americium-241/beryllium source (SN: 47-21269) remained secure in its shielding. The source insertion rod was bent and broken and the 8 milliCurie cesium-137 source, which was still attached to the rod, could not be retracted. The licensee wrapped the exposed cesium source in lead blankets and placed the gauge back into its transport case. The area and dozer tracks were surveyed--there were no readings above background. The exterior of the transport case was surveyed and the highest reading was 0.4 mR/hr at the blanketed source. The damaged gauge was transported to the manufacturer's service center where a technician made the determination it was not repairable. The licensee is storing the gauge at its facility until arrangements can be made for disposal. An investigation into this event is ongoing. More information will be provided as it becomes available in accordance with SA-300." Texas Incident #: 9600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-07-31
53520 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2018-07-21 20:00 | 2018-07-21 23:30 | 2018-07-22 | UNUSUAL EVENT DECLARED AT A NON-POWER REACTOR SITE DUE TO A CAMPUS GAS LEAK The licensee declared an Unusual Event on 7/21/2018 at 2000 CDT due to a detected gas leak near a campus dormitory. The reactor was not impacted. Local authorities and the gas company are on location in order to identify and repair the source of the gas leak. The Kansas State University non-power reactor is in a safe shutdown condition. * * * UPDATE FROM ALLEN CEBULA TO OSSY FONT ON 7/22/2018 AT 0051 EDT * * * The Unusual Event was terminated on July 21, 2018 at 2348 CDT. The source of the gas leak was identified and isolated. Notified NRR (Evans), NRR PM (Traiforos), NRR (Reed), IRD (Grant), DHS SWO, DHS NICC, FEMA OPS AND FEMA NATIONAL WATCH CENTER, FEMA NRCC SASC AND NUCLEAR SSA via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 0 | KS | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-07-22
53519 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-07-20 22:35 | 2018-07-20 23:39 | 2018-07-21 | SAFEGUARDS REPORT - PROTECTIVE ACTIONS TAKEN DUE TO WEATHER CONDITIONS Site security measures taken due to severe weather conditions. Compensatory measures were taken. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM JUSTIN GALLAGHER TO VINCE KLCO ON 7/21/18 AT 0135 EDT * * * The tornado warning expired at midnight. Site security was returned to a normal posture. The licensee will notify the NRC Resident Inspector. Notified the R2DO (Nease) and the 73.71 Group via email. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-07-20
53518 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-20 | 2018-07-20 12:32 | 2018-08-14 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following information was obtained from the state of Texas via email: "On July 20, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that he had been contacted by their dosimetry processor and informed that one of his radiographer's dosimeter had read 37.5 rem for the previous month (June, 2018). The RSO stated the report indicated the dose was irregular. The RSO stated the individual had stated they had not lost their badge, but had left it in the radiography truck a few times on their day off. The RSO stated the individual has been removed from all duties that would give them any additional exposure to ionizing radiation. The individual's current dosimeter has been sent to the processor for reading. The RSO stated the exposure to the radiographer this individual had been working with was normal. The RSO stated they would contact Radiation Emergency Assistance Center/Training Site (REAC/TS) and seek assistance. The RSO does not believe the dose is real and is a badge only exposure. The RSO stated the radiographer has not displayed any signs of a high exposure. Additional information will be provided as it is received in accordance with SA-300." * * * UPDATE FROM ARTHUR TUCKER TO VINCE KLCO ON 8/14/18 AT 1727 EDT * * * The following information was received from the State of Texas via email: "On August 14, 2018, the licensee reported they had received sample results for the blood samples sent to Radiation Emergency Assistance Center/Training Site (REAC/TS). The sample indicated a dose of 0.44 gray. The licensee stated the individual exposed has not complained of any unusual feelings in the hands. The licensee's Assistant Corporate Radiation Safety Officer is going to the location where the individual works to interview. The investigation into this event is on going. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #9597 Notified the R4DO (Deese). INES Coordinator (Milligan) and NMSS Events notified via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-07-30
53517 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-07-18 13:00 | 2018-07-19 12:36 | 2018-07-19 | NON-LICENSED CONTRACT SUPERVISOR SUBVERTS FITNESS FOR DUTY TEST "At 1300 [EDT] on July 18, 2018, a contractor supervisor violated the licensee's Fitness-for-Duty (FFD) program by subverting the Fitness for Duty process. The contractor's site access has been terminated. The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-07-19
53516 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-07-17 10:00 | 2018-07-19 02:04 | 2018-07-19 | AGREEMENT STATE REPORT - RECEIVED DOSE GREATER THAN PRESCRIBED DOSE The following information was obtained from the state of California via email: "A cervical patient was receiving her first High Dose Rate (HDR) brachytherapy treatment, using the Varian VariSource iX HDR, on Tuesday, July 17, 2018, starting at 10 am [PDT]. The patient's 3 applicators, for the tandem and right/left ovoids, were attached to the distal ends of the transfer guide tubes specially coded for the GYN treatments (using the Varian Quick Fit connectors), with the tandem as channel 1, ovoid right as channel 2 and ovoid left as channel 3. The guide tubes were attached by the radiation therapist, and checked by two other employees. After the first fraction, the radiation therapist was preparing to disconnect the guide tubes from the applicators and noted that the distal end of the transfer guide tube for channel 1 was hanging approximately vertically along the end of the gurney. The physicist also verified this, and that the Quick Fit connectors for all of the guide tubes were still secured to the applicator and locked in place with their locking rings. However, it appeared that the transfer tube for channel 1 had been severed at its distal end from its Click Fit connector. The patient was re-surveyed to confirm that the source had retracted appropriately, with no radiation detected within the patient. The radiation therapist proceeded to disconnect the guide tubes from the applicators, remove the applicators from the patient, and clean the patient up for discharge home. The licensee is unable to ascertain whether the tube failed before the Ir-192 source deployed to the treatment site or upon return of the source to HDR storage. It is possible that the patient received the planned treatment, with the source in the correct dwell locations. It is also possible that the Ir-192 seed landed on the gurney close to the patient's skin, or that the source extended vertically down from the distal end of the transfer tube, in which case the patient's lower extremities were exposed to a smaller dose of approximately 500 mR. Staff immediately notified Varian of the event, and took the tubing out of service. New tubing is scheduled to arrive on Friday 7/20/2018, and no HDR treatments will occur before then. Staff also immediately notified the patient's physician. RHB will conduct a site visit on Friday 7/20/2018." California report no.: 5010-071718 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-08-02
53515 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-07-18 08:21 | 2018-07-18 19:27 | 2018-07-18 | CONTRACTOR SUPERVISOR TESTED POSITIVE FOR ALCOHOL A contractor supervisor tested positive for alcohol during an access upgrade fitness-for-duty test. The employee's access to the facility has been suspended. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-07-18
53514 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2018-07-17 18:10 | 2018-07-17 22:24 | 2018-07-18 | NOTIFICATION OF OTHER GOVERNMENT AGENCY "At 1810 CDT, Wolf Creek Generating Station initiated contact with the Department of Homeland Security regarding a suspicious occurrence on the Corporate Computer System. The notification was from the Wolf Creek Information Services department to an established point of contact in the Department of Homeland Security. The scope of the occurrence is limited to the business network computer system and does not impact digital systems involved in operation of the plant. "This event is being reported in accordance with 10CFR50.72(b)(2)(xi). "Wolf Creek Unit 1 remains operating at 100% power in Mode 1. No plant actions or compensatory measures have been taken. "The licensee has notified the NRC Senior Resident Inspector." * * * RETRACTION FROM WARREN BRANDT TO HOWIE CROUCH AT 1327 EDT ON 7/18/18 * * * "The licensee is retracting this event based on the following: "Wolf Creek Nuclear Operating Corporation has determined that the condition previously reported in EN #53514 is not a reportable condition. The basis for this determination is described below and is being communicated here in accordance with the guidance of NUREG-1022, rev. 3, section 4.2.3. The event database should be revised to indicate that this is not a reportable condition. "Wolf Creek determined that this was not an event or situation related to the health or safety of the public or onsite personnel. Wolf Creek also determined that this event was not a four-hour cyber security event reportable under 10 CFR 73.77(a)(2)(iii) because the business network computer system is not associated with: safety-related and important-to-safety; security; or emergency preparedness functions. This condition has been documented in the licensee's Corrective Action Program and Wolf Creek Information Services has taken compensatory measures to prevent recurrence." The licensee will be notifying the NRC Resident Inspector. Notified R4DO (Young). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2018-07-17
53513 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-07-16 | 2018-07-17 20:32 | 2018-07-17 | RECOVERY OF A STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was obtained from the state of California via email: "On July 16, 2018, the California Office of Emergency Services (OES) contacted RHB [California Radiation Health Branch] to report the recovery of a stolen moisture density gauge. The gauge recovery was reported to OES by the San Jose Police Department. The service truck containing the moisture density gauge was stolen from a private residence sometime over the weekend, and was found by the San Jose Police Department during patrol early on July 16, with the gauge still chained to the bed of the truck. The San Jose Police Department cut the chain and stored the gauge at the station. The moisture density gauge is a CPN Model MC-1DR-P, S/N MD60508312, containing 10 mCi of Cs-137 and 50 mCi of Am-241. The gauge was collected by RHB and put in RHB storage on July 16. RHB will be following up with the licensee concerning adherence to regulatory and license requirements." California report no.: 5010-071618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-07-25
53512 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2018-07-17 | 2018-07-17 17:54 | 2018-07-17 | AGREEMENT STATE REPORT - TOTAL DOSE DELIVERED DIFFERED FROM PRESCRIBED DOSE BY GREATER THAN 20 PERCENT The following information was received from the state of Wisconsin via email: "On July 17, 2018, the licensee identified a medical event where the total dose delivered differed from the prescribed dose by 20 percent or more. The licensee implanted 83 seeds containing Pd-103 for prostate brachytherapy. The prescribed dose to the prostate was 125 Gy; the dose delivered was 96.25 Gy. The dose received by the prostate (D90) was 77 percent of the intended dose. The patient has been notified. The implant occurred on June 8, 2018, and post-implant dosimetry was completed on July 17, 2018. The department will perform a site investigation to determine the root cause of this medical event." Event Report ID No.: WI180011 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2018-07-25
53511 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-07-17 13:38 | 2018-07-17 17:01 | 2018-07-17 | NON-LICENSED CONTRACT SUPERVISOR TESTS POSITIVE ON FITNESS FOR DUTY TEST "At 1338 [EDT] on July 17, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for a controlled substance during a random Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. The Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-07-17
53510 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2015-05-06 | 2018-07-17 12:34 | 2018-07-17 | POTENTIAL OVER EXPOSURE FROM RADIOGRAPHY OPERATION The following information was summarized from an email received from the state of Kansas: [The licensee RSO] (DBI) reported to the KDEM [Kansas Division of Emergency Management] 24-hour number that they had a potential over exposure during a radiography operation. The radiographer was in the process of setting up the last shot of the day. While returning to the crank, the radiographer was radioed by the refinery's QC person. At the same time, he was adjusting the collimator, which had shifted. The QC person called over the radio 'come on' which the radiographer's assistant (on the same radio channel) took to mean to crank out the source. When the radiographer felt the vibration of the source being cranked out, he dropped the collimator, exited the area immediately, and got the source retracted. Preliminary worst case calculations indicated a possible extremity over exposure. The radiographer's badge was sent in for processing and the report came back with 33 mR for the period since April 9. With this information, the extremity dose will be recalculated to determine the actual exposure to the individual. PQT Services Inc. and REAC/TS consulted on the incident. The worst case scenario is that the radiographer could have received a dose from 50 - 100R to the hands. Pictures of the radiographers were inspected for signs of radiation burns. No signs at this time. The plan is to continue to monitor his hands until June 20, 2015. Both PQT Services and REAC/TS agree that this should be a sufficient time to assure the safety of radiographer. The radiographer's annual dose was DDE 262 mR. Root cause of incident was determined to be weakness in the communication procedures established between personnel during radiographic operations. A visual 'ALL CLEAR' confirmation from the radiographer setting up the exposures must be made with the person operating the exposure device before the source is exposed. All DBI Inc. employees have been notified of this incident and the importance of a visual confirmation prior to exposing the source. This has been implemented in DBI's protocol. This event is considered closed. Item Number: KS150004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2018-07-25
53509 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2015-12-03 | 2018-07-17 12:20 | 2018-07-17 | TWO GAUGES DESTROYED IN A FIRE The following information was received via email. "Tower Plastics Mfg., Inc. reported that their two remaining generally licensed NDC Model 103 gauges (SN's 2160 and 2161 containing 150 mCi/Am-241 each) were destroyed in a fire on December 3, 2015. This was reported during the IEMA [Illinois Emergency Management Agency] 2018 annual source reconciliation. The licensee reported that the site was completely destroyed in the fire and debris was hauled to a landfill. Records of the disposal and an IEMA survey of the site are pending." Item Number: IL180030 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-07-25
53508 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-06-25 | 2018-07-17 08:58 | 2018-07-17 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE UNABLE TO RETRACT The following information was received via email. "North Carolina (NC) Radioactive Materials Branch (RMB) is submitting the following reportable event: Radiography Camera Source Unable to Retract. Reportable per: 10 CFR 30.50(b)(2) & 10 CFR 34.101(a)(2) Event Date & Discovered Date: 6/25/18 Date Reported to RMB: 6/26/18 Location where event took place: Stoneville, NC Reporting Licensee: Applied Technical Services [ATS] NC License Number: 1510-1 Radiography Camera Manufacturer: QSA Global, Inc. Radiography Camera Model #: Delta 880 Radiography Camera S/N: D5059 Source: Ir-192 Source Activity: 71.4 Ci Source Manufacturer: QSA Global, Inc. Source Model #: A424-9 Source S/N: 65909G "While conducting radiography shots at a water tank construction site, ATS radiography crew experienced a source hang up. Radiographers initially believed the cause to be a crimped guide tube due to source not moving in either direction. While maintaining a 2 mR/hr boundary, additional personnel were dispatched to the work site by ATS with additional shielding material and [the] RSO [radiation safety officer] who is responsible for source retrievals. Lead blankets were placed on the guide tube and the RSO determined that the guide tube was not compromised, kinked, crimped or otherwise damaged. Probable cause was determined to be in the control assembly. RSO unthreaded the guide from the outlet adapter and exercised the controls with no effect. Guide tube was reconnected and RSO began to troubleshoot the connection side of the camera by removing the housing from the connection to observe the cable while again exercising the controls. Cable would flex but was observed to be either wedged or pinned at the connector. During this process, it was observed that since the cable would not flex on the outlet side of the camera it was determined that extreme force on the controls side would not result in the cable being disconnected from the pig tail. The housing was reattached, and extreme force was used on the controls to break the cable free and the source was returned to its secured and shielded position. The RSO observed the control assembly crank did have more movement than usual, and root cause was determined to be debris from a damaged bearing that had moved down the control cable housing and locked up the controls. This equipment had quarterly maintenance and weekly inspections conducted on it. [The] controls were shipped to QSA for repair or disposal. All personnel involved in the source retrieval received doses well within annual limits for radiation workers. "RMB has concluded its investigation and consider this event Closed & Complete. No other agencies were informed of this event and no other generic issues identified." NMED Event ID: 180329 NC Tracking ID: 180029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-07-25
53507 | 0 | FLEIS & VANDENBRINK ENGINEERING |  |  |  |  | 2018-07-16 18:00 | 2018-07-16 21:24 | 2018-07-16 | DAMAGED MOISTURE DENSITY GAUGE While performing measurements at a construction site in Big Rapids, MI, a Troxler Model 3430 was struck by a bulldozer while the source rod was extended. While attempting to retract the source, the 9 mCi Cs-137 source disconnected from the source rod. The RSO covered the source and established boundaries around the source. The licensee contacted the NRC Operations Center to get authorization to transport the source back to their storage facility. Notified R3DO (Reimer) and R3DNMS (McCraw) and placed them on a conference call with the licensee. The licensee was authorized to transport the source, in a sand-filled bucket, back to their facility. The Troxler serial number is 23659 and also contained a 44 mCi AmBe source. The AmBe source is in the shield. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-07-24
53506 | -1 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2018-07-13 11:25 | 2018-07-13 16:21 | 2018-08-20 | MEDICAL EVENT The following information is a synopsis of information received via E-mail: A HDR [high dose rate] brachytherapy incident occurred in Brunswick, Georgia, on July 13, 2018. No one, including the patient, was exposed to excessive radiation. SE Georgia Health Systems treated a Gyn [gynecology] patient using the GammaMed Plus HDR unit and a Tandem and Ring applicator set, both supplied by Varian. Upon completion of the treatment, the source wire retracts back into the shielded HDR unit for safe storage. At that time the room was checked with a survey meter and no exposure readings above background were measured. The HDR unit was surveyed to ensure that the source wire had retracted. The exposure reading on the surface demonstrated that the wire had retracted, and the room was safe. Upon scanning the patient's surface, however, a reading of approximately 2.5mR/hr was measured, which was higher than the expected background reading. The applicator was removed from the patient and scanned, the increased exposure reading was in the applicator. The applicator was placed into a large shielded container provided by Varian and immediately placed in safe storage. The patient, the bedding, and all other materials associated with the implant were re-scanned with no readings above background. The patient was removed from the room, deemed safe and released. The time was recorded to be approximately 5 to 6 minutes and will be used for dose estimates. The HDR unit was re-scanned along with the Linac vault. All were deemed clear and safe. The HDR unit was locked and secured. Patient treatments in the Linac continued. The applicator device was then scanned one piece at a time and it was determined that the Ring portion of the Tandem and Ring set was contaminated. It was assumed that the contamination was secure inside the ring which is a rounded hollow metal tube. Exposure readings at the surface of the ring were 96 mR/hr at the surface and approximately 30 mR/hr at 6 inches. SE Georgia Health Systems notified the Georgia Radiation Protection Programs, and Varian Medical Systems of this incident. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * RETRACTION FROM KATHY ARZATE TO HOWIE CROUCH AT 1050 EDT ON 8/7/18 * * * "After investigation and arrival on site to determine the cause of the contamination, it was found there was no contamination on the patient's body. It was not a failure of the device. We [Varian] inspected the device. We attempted to remove the contamination from the applicator, but were unable to. Therefore, the manufacturer of the source took the applicator back to their facility and were able to remove the contamination there. Ultimately, there was no equipment failure per 10 CFR 30.50(b)(2) or (b)(3)." Notified R1DO (Cahill), R2DO (Sykes), R4DO (Vasquez), and NMSS Events (by email). * * * UPDATE FROM KATHY ARZATE TO OSSY FONT AT 1127 EDT ON 8/20/18 * * * The following was received via email from Varian and is part of their retraction on 8/7/18: "The Varian Radiation Safety Officer (VRSO), the Varian Field Service Engineer (VFSE), and the AOS Radiation Safety Officer (ARSO) arrived on the site on July 15, 2018 at 0830 EDT. They were met by the site Radiation Safety Officer and medical physicist. "Utilizing a RADEYE B20-ER Geiger meter, an initial contamination wipe was performed on the afterloader turret. No results above background were found. The VFSE began the process of transferring the potentially contaminated wire from the afterloader to the transport safe. The VRSO then began decontamination steps to remove the particle from the applicator. "The decontamination effort involved running a dummy cable completely through the applicator to the closed end. Once the cable reached the end of the applicator, the wire was moved back-and-forth in the location of the contamination while rotating the applicator. Once the site was agitated for an appropriate amount of time, the cable was slowly pulled from the applicator while holding a wipe on the wire. This action was performed for approximately 45 minutes without success. "Once the old source wire was removed from the afterloader, the afterloader was scanned to determine if any contamination was present in the source wire tubing. No results above background were found. The new wire was installed into the afterloader. The plastic transfer catheter was wiped. No results above background were found. All gloves, wipes, and dummy cable were scanned for potential contamination prior to placement in the biohazard waste stream. No results above background were found. "The ARSO took the contaminated applicator back to the AOS facility. Further efforts at that facility allowed the applicator to be cleaned and returned to the customer site. "The results of all testing indicate that the afterloader was clear of possible radiological contamination. A new source wire was installed and the customer was able to resume treatments as scheduled. There was no indication that the contamination was from a leaking sealed source, but rather external contamination on the wire. There is no indication of patient contamination or equipment failure. Therefore, the NRC Event Report 53506 has been retracted." Notified R1DO (Young) and R2DO (Sandal), R4DO (Taylor) and NMSS Events by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | MED TREAT INVOLVING CONTAM | [8 empty] | NON EMERGENCY | 1 | GA | MAT |  | 30.50(b)(2) | 30.50(b)(3) |  |  | 0 | 2018-07-23
53505 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2018-07-13 | 2018-07-13 11:27 | 2018-07-13 | AGREEMENT STATE REPORT - GAUGE STUCK SHUTTER The following information was received from the state of South Carolina via email: "On July 13, 2018 the Department [South Carolina Division of Health and Environmental Control] was notified by the licensee that it had discovered a stuck shutter on one of its gauges while performing a lockout procedure in order to do maintenance on a rotary valve located near the gauge. The gauge is a Kay-Ray Model 7462BP s/n 22425 containing 50 mCi of Cesium 137. The licensee has contacted Systems Services who is specifically licensed to repair the damaged shutter. The RSO [Radiation Safety Officer] stated that the gauge is located 20 feet above areas where individuals normally work. The RSO also surveyed the gauge and found a reading of less than 2 mR/hr. Access to the gauge is made via a catwalk which will be roped off by the RSO until the service provider comes to fix the shutter. The service provider is scheduled to come July 17, 2018." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2018-07-23
53504 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2018-07-12 | 2018-07-12 16:13 | 2018-07-12 | OFFSITE NOTIFICATION TO SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL "For this event, notification was made to the South Carolina (SC) Department of Health and Environmental Control (DHEC) per R 61-68 E.4.b which requires 24 hour notification upon discovery of an 'unauthorized discharge into waters of the State which may cause or contribute to an excursion of a water quality standard.' While it was not conclusively determined that the leak migrated to the groundwater, Columbia made the notification based on discussions with SCDHEC. SCDHEC was notified by phone on July 12, 2018 at 1530 EDT. "An equipment issue was noted on July 10, 2018 during ongoing maintenance activities to repair the liner associated with Hydrofluoric Acid Spiking Station No. 2 in the conversion process area of the Columbia plant. While the polypropylene liner was removed for repair work, a crack was noticed in the epoxy coating covering the diked area at the spiking station. Upon further investigation, a hole approximately 3 inches in diameter was found penetrating the concrete floor and into the soil beneath. Measurements taken reflect the depth of the hole as approximately 6 feet into the soil. Several samples of soil were obtained from the immediate area the morning of July 11, 2018. These samples were analyzed at the Columbia Plant Chemical Laboratory with results obtained the morning of July 12. The highest measurements reported from the samples are 4,000 ppm Uranium and 24 ppm Fluoride, with a pH of 2.84. "The Hydrofluoric Acid Spiking Station No. 2 remains out of service. This is a localized issue underneath the floor of the existing structure and well within the boundaries of the site, thus there is no impact to public health and safety or facility workers. "The spiking station remains removed from service while the event is being fully evaluated. Maintenance has placed a metal plate over the hole as an interim measure to protect the environment from any potential leaks from associated piping. Monitoring of closest downgradient well will be performed within the next seven days. Appropriate repairs or modifications will be completed to the concrete pad and protective layers before the equipment is returned to service. Issue Report 2018-12123 was entered into the Corrective Action Program." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-07-20
53503 | 0 | TETRA TECH EC, INC. |  |  |  |  | 2018-06-04 | 2018-07-12 13:30 | 2018-07-12 | STOLEN RADIOACTIVE CALIBRATION CHECK SOURCES The following is a synopsis of information received: This event notification is being made in reference to seven radioactive calibration check sources that were stolen from the Tetra Tech EC, Inc. (TtEC) temporary job site at the former Naval Air Station Brunswick (NASB) in Brunswick, Maine. TtEC currently is performing work at NASB for the U.S. Department of the Navy, Naval Facilities Engineering Command On the morning of June 4, 2018, Sites 1 and 3 were inspected as part of the follow-up to a May 25, 2018 break-in of the TtEC field trailer. It was observed and reported to the TtEC Project Manager at approximately 0825 EDT that the Navy-owned, locked bunkers (three total), the abandoned Navy warehouse, and TtEC conex box had been broken into sometime after May 25, 2018. The TtEC Project Manager was informed that they were likely broken into during the weekend of June 2 and 3, 2018. Missing from one bunker was a locked safe that contained seven low-level radioactive check sources (five leased from subcontractor RSRS, and two owned by TtEC). The safe had a label bearing the radiation symbol and the words 'CAUTION, RADIOACTIVE MATERIAL,' as was each of the source holders. At the time of the theft, the sources were locked inside a secure safe, and the safe was, in turn, locked inside a former munitions bunker. The entire safe was stolen from the munitions bunker. The bunker was locked with a heavy-duty keyed padlock issued by the Navy. The following is a listing of the stolen sources: ID No. 109402, Sr-90, 0.00065 microCuries ID No. A2-575, Sr-90, 0.00563 microCuries ID No. 019-456, Cs-137, 2.72463 microCuries ID No. 079-705, Cs-137, 5.80465 microCuries ID No. 129-6119, Cs-137, 2.74557 microCuries ID No. H7-605, Th-230, 0.01060 microCuries ID No. 119-706, Th-230, 0.00957 microCuries. The exposure rate, at 30 centimeters from the safe, is 15 to 16 microroentgens per hour and is not distinguishable from background. If the thieves are successful at opening the safe, they might handle the sources. Of the seven radioactive sources, the cesium-137 source (Identification No. 079-705) would result in the maximum dose to a member of public. An individual would receive a dose of approximately 6 millirem (mrem)/hour if this source was left in a backpack or jacket pocket. The dose rate to an individual 1 foot from this source is 0.041 mrem/hour, and the dose rate to an individual 1 yard from this source is 0.0046 mrem/hour. A thorough search of the TtEC temporary job site at NASB, including all buildings, bins, and grounds, has been performed in an attempt to recover the sources, but none of the sources were found. The local police have been notified of the theft, and a formal police report was filed. As of today, the sources have not been recovered. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | ME | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-07-20
53502 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-07-11 06:45 | 2018-07-12 09:23 | 2018-07-12 | UNPLANNED CONTAMINATION EVENT "On July 11, 2018, at approximately 0645 [EDT] a radiological spill occurred in Building 333 Uranium Metal Dissolution area due to a glass column leak. This area is controlled as a Radiologically controlled Area. Cleanup and evaluation activities were initiated, but later suspended when it was determined the column had failed and additional evaluation for structural stability was necessary prior to safely performing additional recovery and decontamination activities. "There were no radiological or chemical exposures. There were no releases to the environment or public areas. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2018-07-20
53501 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-10 | 2018-07-11 15:58 | 2018-07-13 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the State of Texas via E-mail: "On July 11, 2018, a license notified the Agency [Texas Department of State Health Services] that a medical event had occurred. On July 10, 2018, a patient received the first fraction of a treatment plan delivered by a high dose rate afterloader (HDR) utilizing iridium-192. On July 11, 2018, the medical physicist noticed that the dose per fraction entered in the treatment plan of the 1st fraction was incorrect. Instead of a 350 cGy/fraction for 6 fractions, a value of 2100 cGy was entered for one fraction (which was the total dose for the brachytherapy course). The Radiation Oncologist (RO) was notified and he notified the referring physician and patient that day. RO will follow the patient closely and make all possible interventions to minimize potential adverse effects. The Agency is awaiting answers to multiple questions including identification of target area. More information will be provided as it is obtained and in accordance with SA-300. "Texas Incident #: I-9594" * * * UPDATE FROM CHRIS MOORE TO DONALD NORWOOD AT 1621 EDT ON 7/13/2018 * * * The following was received from the State of Texas via E-mail: "The patient was treated for vaginal cancer using HDR (High Dose Rate) brachytherapy using a 6 Curie Iridium-192 source. A written report was received from the licensee indicating several factors contributed to the medical event including a busy work day, mental fatigue, verbal description of the intended dose instead of written direction, and unavailability of another medical physicist (MP) to independently review the dose/fraction entered in the treatment planning system. The overall brachytherapy plan was modified and the volume treated in the first fraction was considered completed and [the patient] will not receive further treatment. The Radiation Oncologist will follow the patient closely and make all possible interventions to minimize potential adverse effects. Immediate changes implemented at the facility include: no HDR treatment will start without a written prescription in the patient electronic medical record and an independent check of the prescription entry and radiation dosimetry will be conducted by an Authorized User, other than the MP who generated the treatment plan. An Agency team will conduct an onsite investigation in early August 2018 when all parties involved are available. Additional information will be provided as it is obtained and in accordance with SA-300." Notified R4DO (Pick) and NMSS Events Notification E-mail group. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-07-19
53500 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2018-07-11 02:58 | 2018-07-11 03:58 | 2018-07-11 | METEOROLOGICAL DATA UNAVAILABLE "On July 11, 2018, as part of pre-planned maintenance, the site meteorological tower will be removed from service. The tower will be out of service for approximately 11 days. As a result, this is reportable under 10CFR 50.72 (b)(3)(xiii). During the time the data is not available from the meteorological tower; compensatory measures will be in place to obtain the data from the National Weather Service if necessary. "The [NRC] Resident Inspector has been notified." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-07-11
53499 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-07-09 15:15 | 2018-07-09 20:05 | 2018-07-09 | CONTRACTOR SUPERVISOR TESTS POSITIVE ON FITNESS FOR DUTY TEST "At 1515 [EDT] on July 9, 2018, Southern Nuclear Operating Company (SNC) determined a contractor supervisor confirmed positive for a controlled substance during a for cause Fitness-for-Duty (FFD) test. The employee's unescorted access to the plant has been suspended. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-07-09
53498 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-07-09 11:55 | 2018-07-09 18:23 | 2018-07-09 | UNPLANNED LOSS OF TECHNICAL SUPPORT CENTER (TSC) VENTILATION "On July 9, 2018, at 1155 hours [EDT], while testing the TSC Ventilation System, an equipment malfunction occurred that resulted in an unplanned loss of TSC ventilation functionality/habitability for greater than seventy-five minutes. "If an emergency had been declared requiring TSC activation during this period, the TSC would have been staffed and activated using existing emergency planning procedures. If relocation of the TSC had been necessary, the Emergency Coordinator would have relocated the TSC staff to an alternate location in accordance with applicable site procedures. The TSC ventilation system has been placed in an interim configuration that restored functionality and habitability. Additional maintenance is planned to promptly resolve the malfunctioning equipment. "This is an eight-hour, non-emergency notification for a loss of Emergency Assessment Capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the equipment malfunction affected the functionality of an emergency response facility. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." The equipment malfunction (a failed solenoid valve) resulted in the loss of the ability to pressurize and filter the air in the TSC. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-07-09
53497 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-07-09 09:58 | 2018-07-09 17:01 | 2018-07-09 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On 07/09/2018 at 1111 CDT, Browns Ferry Unit 1 Operators identified U1 High Pressure Cooling Injection system steam supply valves were isolated. After reviewing ICS [Integrated Computer System], Operations determined isolation occurred at 0958 CDT during performance of surveillance testing. The Browns Ferry Nuclear Plant Unit 1 High Pressure Coolant Injection (HPCI) system was declared inoperable at 0958 CDT due to an inadvertent isolation that occurred during testing. During performance of surveillance procedure 1-SR-3.3.6.1.2(3B) HPCI System Steam Supply Low Pressure Functional test, an erroneous signal was induced causing actuation of primary containment isolation system group IV (i.e., HPCI Isolation). Technical Specification 3.5.1, ECCS-Operating, Condition C was entered as a result of the inoperable HPCI system. This constitutes an unplanned HPCI system inoperability and requires an 8-hour NRC notification in accordance with 10 CFR 50.72(b)(3)(v)(D). The erroneous signal was cleared and the HPCI isolation was reset. Upon reset of the isolation signal, the HPCI system was returned to available status. The HPCI system was unavailable for 2 hours and 55 minutes, however the HPCI system remains inoperable. "There was no impact to the health and safety of the public or plant personnel as a result of this condition. "The NRC Resident Inspector has been notified. "A condition report has been entered into the Licensee's Corrective Action Program to capture this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-07-09
53496 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2018-07-09 13:34 | 2018-07-09 16:25 | 2018-07-09 | SECONDARY CONTAINMENT INOPERABLE "At approximately 1334 CDT on 7/9/18, both doors of a Secondary Containment Airlock were reported to be open simultaneously for a period of less than 3 seconds. The brief time that the doors were simultaneously open constituted an inoperable condition of Secondary Containment. Secondary Containment was immediately restored to operable by closing the airlock doors. Subsequently, the airlock interlock was verified to operate correctly. "This event is being reported pursuant of 10 CFR 50.72(b)(3)(v)(C). The Senior NRC Resident Inspector has been notified." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-07-09
53495 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2018-07-09 | 2018-07-09 10:29 | 2018-07-13 | AGREEMENT STATE REPORT - STOLEN PORTABLE GAUGE The following information was received from the Commonwealth of Virginia via E-mail: "On Monday July 9, 2018, at approximately 0900 EDT the licensee reported to the Virginia Radioactive Materials Program that a construction trailer, containing a Troxler Model 3440 (serial number 17396) moisture density gauge (portable gauge) was stolen over the weekend from a road construction site in Thornburg, VA. According to the licensee's Radiation Safety Officer (RSO), the gauge was secured inside its case which was secured to the floor of the trailer by lock and chain. The theft of the trailer was discovered on Monday morning (July 9th) when workers reported to the construction site to begin work. The gauge was last seen when secured inside the trailer at approximately 1500 EDT on Friday, July 6, 2018. The gauge contains (nominally) 9 milliCuries of Cs-137 and 44 milliCuries of Am-241. The construction site is located on State Route 606 (Mudd Tavern Road), approximately 1 mile west of I-95. The Virginia State police were notified by the licensee on Monday morning, July 9, 2018. "The Virginia Radioactive Materials Program has encouraged the licensee to issue a press release. The purpose of the press release is to inform the perpetrator(s) that the gauge is of no value to anyone that is not licensed by the U.S. Nuclear Regulatory Commission or an Agreement State, such as Virginia. "Virginia Event Report ID No: VA-18-003" * * * UPDATE ON 7/10/2018 AT 1311 EDT FROM MICHAEL FULLER TO STEVEN VITTO * * * The following update was received from the Commonwealth of Virginia via E-mail: "On Tuesday, July 10, 2018, the licensee's RSO informed the Virginia Radioactive Materials program that the stolen portable gauge had been recovered by the Virginia State Police. As of 10:30 AM, the licensee's technician was in route to the Hampton Roads area to retrieve the stolen trailer and the portable gauge. The police detective informed the licensee that the trailer was broken into but the gauge appeared to be intact. A final update will be provided once the gauge is retrieved and its safe configuration is verified. " Notified R1DO (Bower), ILTAB and NMSS Events Notifications via E-mail. * * * UPDATE ON 7/13/2018 AT 1457 EDT FROM MICHAEL FULLER TO DONALD NORWOOD * * * The following update was received from the Commonwealth of Virginia via E-mail: "On Thursday, July 12, 2018, a Virginia Radioactive Materials Program Inspector conducted a reactive inspection in Thornburg, VA. The inspector verified that the stolen portable nuclear gauge was retrieved by the licensee and that the gauge is intact. "This is the final update to the subject report." Notified R1DO (Bower), ILTAB and NMSS Events Notifications via E-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2018-07-17
53494 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-07-07 14:15 | 2018-07-07 15:11 | 2018-07-07 | SAFEGUARDS REPORT - ATTEMPTED INTRODUCTION OF CONTRABAND INTO THE PROTECTED AREA Attempted introduction of contraband into the protected area. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2018-07-16
53493 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2018-07-07 02:42 | 2018-07-07 08:29 | 2018-07-07 | CONTROL ROOM VENTILATION INOPERABLE "At 0242 EDT, the CCNPP (dual unit, single control room) control room supply damper failed shut. This rendered the Unit 1 and Unit 2 control room ventilation inoperable and the appropriate LCOs were entered. "At 0249, control room ventilation was restored to service and the appropriate LCOs were exited. This is being reported under 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-07-07
53492 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-05-10 | 2018-07-06 16:32 | 2018-07-06 | LOUISIANA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The following is an excerpt from a report received from the state of Louisiana via email: "On June 12, 2018, the Radiation Safety Officer (RSO) for MISTRAS Group, Inc. (MGI), received a Landauer Corporation dosimetry report for an Excessive Exposure to the whole body. The report indicated that an instructor received a whole body exposure of 5168 mR during the month of May, yielding a whole body cumulative exposure to date of 5618 mR. A MGI two-person crew, composed of a radiography instructor and a radiography trainee were making exposures at a temporary jobsite located at the Bechtel Liquid Natural Gas Project at Sabine Pass, Louisiana in Cameron Parish. The exposure device was a QSA GLOBAL Model 880D loaded with a 74 Ci Ir-192 source. "When the RSO informed the instructor of the reported excessive exposure, the instructor claimed that one day during May 2018, he had dropped his badge while he and his trainee were performing panoramic exposures, but did not notice the badge missing until after the exposure was completed. The instructor stated he searched for his badge and recovered it from the platform approximately one foot directly below the area being radiographed for a 90-second exposure. Upon further questioning of the above instructor, the RSO learned the body badge had been dropped and inadvertently exposed on May 10, 2018. The RSO stated the instructor failed to report the incident on the date of occurrence. The instructor claimed his direct-reading pocket dosimeter had not gone off-scale or received a high reading. The instructor stated that he believed his badge had only been missing for a single exposure. Health Physics calculations performed by the RSO using the isotope, activity, distance and exposure time provided to him by the instructor do not adequately account for the above excessive exposure in terms of the claimed single inadvertent exposure to the badge, as described. "Instead of promptly utilizing the Louisiana Department of Environmental Quality [LDEQ] required emergency hotline number, the RSO for the licensee sent an email to an LDEQ radioactive materials inspector on June 25, 2018 at 11:59 am [CDT], approximately 13 days after the RSO for the licensee first discovered the excessive exposure." Event Report ID No.: LA 180013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-07-16
53491 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-07-06 12:01 | 2018-07-06 15:36 | 2018-07-06 | TRANSFORMER FAILURE CAUSES LOSS OF OFFSITE POWER TO UNIT 2 "At 1201 [CDT], Station Auxiliary Transformer 242-2 experienced a bushing failure, resulting in a loss of offsite power to Unit 2. The 2A and 2B Diesel Generators started and sequenced loads onto the Unit 2 ESF buses appropriately. All other buses normally powered from the Station Auxiliary Transformers automatically transferred to the Unit Auxiliary Transformers. ESF Bus 241 and 242 Undervoltage Relays actuated to start the Diesel Generators and the 2A Auxiliary Feedwater Pump started on the 2A Diesel Generator sequencer. ESF Battery Charger 212 tripped at the same time, which was an unexpected condition. DC Bus 212 was cross-tied with DC Bus 112. "This notification is being made under 10 CFR 50.72(b)3(iv)(A) due to the actuation of both Unit 2 Diesel Generators and the 2A Auxiliary Feedwater Pump. "The NRC Senior Resident Inspector has been notified." Currently, offsite power was restored via the Unit 1 Unit Auxiliary Transformer. Both Unit 2 Emergency Diesel Generators have been secured. DC Busses are still cross-tied. The licensee is currently in a 72-hour shutdown action statement for the loss of offsite power and a 7-day action statement for having the Unit 2 DC Bus cross-tied to Unit 1. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-07-06
53490 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-07-06 | 2018-07-06 11:43 | 2018-07-10 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of California via email: "[A Troxler] Moisture Density Gauge (Serial #18330) was stolen from a parked vehicle at a residence. An unknown subject cut a security cable then took the yellow box containing the device and associated equipment. The box was in the rear bed of a pickup truck. The police department has been notified and are enroute to investigate." The Troxler contained an 8 mCi AmBe-241 source and a 48 mCi Cs-137 source. California Report No.: 5010070618 * * * UPDATE ON 7/10/18 AT 1024 EDT FROM KENNETH FUREY TO BETHANY CECERE * * * The following was received by email from the State of California: "The Troxler 3440, serial #18330 reported stolen on July 6, 2018 was recovered by the Rancho Cordova Police Department on July 7, 2018 at 2000 PDT after it was dumped in the Walmart parking lot in Rancho Cordova. [A representative] of Youngdahl Consulting took possession of the gauge." Notified R4DO (Pick), NMSS Events Notification, ILTAB, and CNSNS (Mexico) by email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-07-16
53489 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2018-05-07 | 2018-07-05 20:41 | 2018-07-05 | PART 21 NOTIFICATION - HEX NUTS AND CAP SCREWS ON CERTAIN VEE-BALL VALVES NOT PROPERLY DEDICATED Fisher Controls issued FIN 2018-02 for hex nuts and caps screws for securing the valve body-to-actuator on eight valves (six purchased by D.C. Cook Nuclear and two purchased by Korea Hydro and Nuclear Power) that were not commercial grade dedicated. Fisher became aware of this issue on May 7, 2018. For technical questions, please contact: Jacob Clos Quality Manager Emerson Automation Solutions Fisher Controls International LLC 301 South First Avenue Marshalltown, IA 50158 Phone: (641) 754-2108 Jacob.Clos@Emerson.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-07-05
53488 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-03 | 2018-07-05 18:02 | 2018-07-19 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE EVENT The following information was obtained from the state of Texas via email: "On July 5, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's [Stanley out of Tulsa, OK] consultant that an overexposure event may have occurred involving radiographers working in the state of Texas, under reciprocity, at a field site near Midland, Texas, but offered no actionable information. At 1620 hours [CDT], the consultant called back and stated that a crew was performing radiography in a pit using a 99.6 Curie iridium - 192 source. The individual who received the high exposure had been working in the dark room. He completed the task he was working on and exited the dark room and went straight to the pit. He picked up the collimator and started to move it while the source was still in the collimator. The other radiographers yelled at him and he dropped the source and left the pit. "The consultant stated the calculations for the dose to the individual's hand provided by the licensee is 284 rem. The consultant stated the radiographer held the source for about 3 seconds and the dose calculation was based on no shielding. The consultant stated there is currently no apparent injury to the individual's hand. The consultant stated the licensee is contacting REAC/TS in Oak Ridge, Tennessee, for assistance. The licensee's radiation safety officer is conducting an investigation into the event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #9592 * * * UPDATE FROM THE STATE OF OKLAHOMA TO HOWIE CROUCH ON 7/6/18 AT 1032 EDT * * * The following information is excerpted from an email that was received from the state of Oklahoma: Oklahoma DEQ [Department of Environmental Quality] Radiation Management was contacted by the radiation safety officer (RSO) of Stanley Inspection, License No.: OK-32187-01, after hours on 7/5/2018. Stanley Inspection, a radiography company, was working in Midland, TX under reciprocity, and one of the radiographers potentially overexposed his hand. Stanley Inspection was instructed by Texas to do medical monitoring for the radiographer, including bloodwork and photographs of his overexposed extremity. Notified R4DO (Miller) and NMSS Events Notifications (email). * * * UPDATE FROM IRENE CASARES TO DONG PARK ON 7/19/18 AT 1158 EDT * * * The following information was obtained from the state of Texas via email: "Stanley Inspection Services reported that a radiation overexposure may have occurred involving radiographers working in Texas, under reciprocity, at a field site on 7/3/2018 near Midland, Texas. Reported to NRC as update on July 19, 2018. After complete investigation and reenactment of the incident the following information was obtained and being provided as an update of the incident. "On July 3, 2018, a radiographer working a temporary field site project under reciprocity (OK licensee in TX) with another crew had an incident. The radiographer was working in the dark room and was developing film. He completed this task and exited the darkroom. This was the last shot of the day in which this crew was working. It was the last image for this shot in which four images are taken for this weld of a 36 inch pipe at a time of 6.5 minutes each image. They were about to end the workday. It was at dusk and his assistant went to the front of the vehicle to get a flashlight while a member of the other crew showed up. The time of day was between 9 and 10 pm. When this person showed up, the radiographer was exiting the darkroom. These two radiographers both walked down into the pit to retrieve the film, when they were walking to the film, the assistant arrived at the back of the truck, stating that the source was still out and at that time the survey meter being carried by the other crew member (RDS-30, Mirion technologies) was alarming. The person carrying the survey meter was about 2-3 feet behind the first radiographer. The first radiographer had already put his fingers (index and middle) and thumb on the collimator for estimated 3 seconds as he was checking to ensure it had not moved from the mark/film while imaging. He explained that he heard the alarms from the survey and dosimetry meters and they both ran out of the pit. It was reenacted on 16 July to confirm how he placed his fingers on the collimator and estimated the time. The Delta 880, sn D15456, camera was loaded with, QSA, A424-9, 66225G, Ir-192, at an activity of 101.5 curies. The calculated dose to the hand for 3 seconds with a collimator made of tungsten rated at 4 HVL was 25.54 rem for the extremity dose. The initial whole body dose was estimated to be unshielded at 109 mrem. The radiographer had been wearing an electronic dosimeter (Tracerco) which was acting as an alarming rate meter and dosimeter. The film badge was processed with results of 18 mrem. And the dosimetry was reported to have read 24 mrem by the radiographer for that day's work. The dosimeter was sent for verification/accuracy checks. The radiographer had his blood drawn as instructed by REAC/TS and the RSO photographed his fingers/hands for 3 weeks. The radiographer stated he had no abnormal redness, tingling or sensations in the tissue of the hand. The supporting documents and reenactment support an estimated dose of 25.54 rem to the extremity and approximately 20 mrem to the whole body. "The company is completing its documentation of the incident and will be providing its detailed report with corrective actions, another update will be forthcoming." Notified R4DO (Young), INES (Milligan) and NMSS Events Notifications via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-07-13
53487 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-07-03 | 2018-07-04 23:19 | 2018-07-04 | AGREEMENT STATE REPORT - SOURCE DISCONNECT The following information was received from the State of Texas by email: "On July 4, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that one of their crews has experienced a source disconnect. The crew was using a QSA 880D exposure device containing a 70 Curie Iridium - 192 source. The licensee did not have a lot of details on the event, but stated the source had been recovered and that no over exposures had occurred. The licensee stated the connector ball on the drive cable was tested after the event and failed the test. The RSO stated they would provide additional information on July 5, 2018. Additional information will be provided as it is received in accordance with SA-300." Texas Incident- I-9591 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-07-12
53486 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2018-07-03 17:53 | 2018-07-03 23:27 | 2018-07-03 | TURBINE TRIP SOLENOID FAILED TO ACTUATE DURING TESTING "At 1753 on 7/3/2018 it was discovered that both sets of turbine trip solenoids were previously unable to actuate within allowable time frames; therefore, this condition is being reported as an eight-hour, non-emergency notification per 10 CFR 50.72(b)(3)(v). At the time of discovery, one set of turbine trip solenoids had been restored. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-07-03
53485 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-07-03 15:15 | 2018-07-03 19:07 | 2018-07-31 | DISCOVERY OF AN UNANALYZED CONDITION THAT SIGNIFICANTLY DEGRADES PLANT SAFETY "On July 3, 2018, while performing a review of Emergency Operating Procedures, a concern was identified regarding the potential for excessive loss of ultimate heat sink inventory (UHS) through the auxiliary feedwater (AFW) system mini-flow recirculation pathway. This condition would have the potential to prevent the ultimate heat sink from providing an adequate inventory of water for a 30-day mission time. "The normal water supply for the Callaway AFW system is the condensate storage tank (CST). The CST is a non-safety grade component. The safety-grade supply for AFW is the essential service water (ESW) system. The ESW system is supplied by the UHS. The UHS thermal performance analysis accounts for a loss of UHS inventory to the AFW system up until the point of the accident sequence that the AFW pumps would be secured. The analysis did not include an allowance for loss of UHS inventory through the AFW mini-flow recirculation pathway following the AFW pumps being secured. The EOP guidance that secures the AFW pumps does not isolate the mini-flow recirculation pathway. "Initial estimates indicate that loss of UHS inventory through the mini-flow recirculation pathway, if not isolated, would preclude the UHS from completing its 30-day mission time. This potential for depletion of the UHS placed the plant in an unanalyzed condition that significantly degraded safety. "Callaway has issued interim guidance to the on-shift personnel regarding this concern to ensure that the ultimate heat sink water level is maintained at a level that will be adequate to mitigate the potential loss of inventory. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition that significantly degrades safety. "The NRC Resident Inspectors have been notified of this condition." * * * RETRACTION ON 07/31/2018 AT 1430 EDT FROM LEE YOUNG TO ANDREW WAUGH * * * "Event Notification (EN) 53485, made on July 3, 2018, is being retracted because re-evaluation performed subsequent to the notification has demonstrated, based on actual plant equipment and environmental conditions, that the unanalyzed inventory losses previously reported by EN 53485 would not have depleted the UHS inventory to an unacceptable level during its 30-day mission time. "The re-evaluation has led to the conclusion that the previously unanalyzed losses of UHS inventory would not have prevented the UHS from performing its specified safety functions and meeting its 30-day mission time requirements. With the UHS capable of performing its specified safety functions and meeting its 30-day mission time requirements, the systems supported by the UHS would have remained capable of performing their specified safety functions. Based on these considerations, it has been determined that the condition reported in EN 53485 did not result in the plant being in an unanalyzed condition that significantly degraded safety. Consequently, the condition did not meet the criteria for an 8-hour notification per 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition that significantly degrades safety. "The NRC Resident Inspector has been notified of the Event Notification retraction." Notified R4DO (Gaddy). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-07-03
53484 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-07-03 09:54 | 2018-07-03 12:00 | 2018-07-03 | MANUAL REACTOR TRIP DUE TO HIGH STEAM GENERATOR WATER LEVEL "At 0954 [EDT] on July 3, 2018, with Unit 1 in Mode 1 at 100 percent power, the reactor was manually tripped due to high steam generator water level. The trip was not complex, with all systems responding normally. Operations stabilized the plant in Mode 3. Decay heat is being removed through the main steam lines through the steam dumps and into the condenser. "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "Unit 2 was not affected. "There was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspectors have been notified." All control rods inserted and Unit 1 is in an electrical shutdown lineup. The cause of the high steam generator water level transient is being investigated. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-07-03
53483 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2018-06-28 | 2018-07-02 15:30 | 2018-07-02 | AGREEMENT STATE REPORT - STUCK SHUTTERS The following was received from the Commonwealth of Kentucky via fax: "On 6/28/18 while conducting a 6-month physical inventory and shutter check (on-off mechanism) the licensee, ARKEMA, Inc., discovered the shutters malfunctioned on two separate fixed gauging devices, namely: "1) TN Technologies fixed gauging device model 5208 Serial No. MB 4251 containing 8 Ci Cs-137. The licensee has attempted to contact Thermo Scientific to repair the shutter. The root cause of the failure of the on/off mechanism was due to corrosion and dust due to the gauging device's environment. This licensee produces industrial chemicals and the gauging device is operated in a corrosive environment. This event was reported to the [Kentucky Radiation Health Branch] KY RHB as required by regulation on 6/29/18. "2) Ronan Engineering fixed gauging device model SA-1 Serial Number M8107, containing 5 Ci Cs-137. The licensee has contacted Ronan Engineering and repairs will be conducted during the week starting on 7/16/18. This licensee produces industrial chemicals and the gauging device is operated in a corrosive environment. The event was reported to KY RHB as required by regulation on 6/29/18. "No accidental overexposures have been reported due to the malfunction." Kentucky Event Report ID No.: KY180002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2018-07-10
53482 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2016-01-15 | 2018-07-02 11:27 | 2018-07-02 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION The following information was received from the State of Kansas via email: "The licensee had an incident with an I-131 patient that resulted in the Iodine Patient room being badly contaminated along with the patient's bed and some other room furniture. The room is secured and removed from service. When the licensee has their Weekday management staff meeting on Monday, they develop a plan to complete the room decontamination and return it to service. The room is removed from clinical service at 2100 today (15 Jan 16). "The contamination is contained within the room and there is no risk to Hospital staff or members of the public. No unintended dose to the patient, staff or other personnel. The patient was on a Foley catheter with the urine bag in a roll able pig. She got out of bed and walked around the room and "dragged" the pig. The hose connection inside the pig was damaged and urine spilled inside the pig and some was spilled on the floor. No one was contaminated - skin or clothing ... just the floor. The easily removable contamination / urine is cleaned up and will leave the room to decay for a half-life. That will make clean-up easier and also will reduce dose to those who are involved in the detailed cleanup. "The licensee will notify the department when the room is returned to service. "6/28/2018 - Patient administered 159.8 milliCuries Iodine-131 on 1/13/2016. "The patient placed on a catheter because they were incontinent, had early Alzheimer's, and was not able to comply with instruction. "The patient catheter with urine bag was placed in a 'rollable pig' which was dragged around the room when the patient walked around the room. The hose connection was damaged about the second day and urine spilled in the pig and onto the floor covering, bedding, linens, and absorbent chucks. "The patient was released with an estimated 28 milliCuries Iodine-131 remaining on 1/15/2016. "The initial room survey indicated high contamination levels. The decision was made to allow the contamination to decay over the weekend to allow for lower exposure to personnel performing the decontamination, and determine the contamination levels, location and a plan to decontaminate the room. "The contamination was determined to be confined to the bed (mattress), linens, absorbent chucks and plastic sheeting. Minor contamination was found on the floor under the plastic sheeting. "The contaminated items were removed from the room and held for 10 half-lives decay. "The floor was surveyed and contaminated spots were decontaminated. The room was returned to clinical service Monday morning 1/18/2016. The time out of service was approximately 60 hours. "6/29/2018 - Integrated Material Performance Evaluation Program (IMPEP) review identified the event had not been reported to the NRC as required." Kansas Item Number: KS160001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2018-07-10
53481 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2018-07-01 01:00 | 2018-07-01 08:24 | 2018-07-01 | BLOWN FUSE LEADS TO LOSS OF SAFETY FUNCTION "On July 1st, 2018 at 0100 [EDT], a portion of the Division 1 Emergency Core Cooling System (ECCS) Loss Of Coolant Accident (LOCA) initiation logic was declared inoperable due to the discovery of a blown fuse. The fuse was replaced at 0215 on July 1st, 2018 and the Division 1 ECCS LOCA initiation logic was declared operable at 0230 on July 1st, 2018. "The blown fuse caused the loss of a portion of the Division 1 ECCS LOCA initiation logic which would have prevented the initiation of the Emergency Closed Cooling (ECC) A system. ECC A and supported systems were declared inoperable. Low Pressure Core Spray (LPCS) was one of the supported systems that were declared inoperable. LPCS is considered a single train safety system. Inoperability of LPCS is considered an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The blown fuse also caused the loss of a portion of the Division 1 ECCS LOCA initiation logic which would have prevented the automatic isolation of Nuclear Closed Cooling and Instrument Air to the Containment. The loss of Containment isolation capability is considered an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) "The NRC Senior Resident Inspector has been notified." | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-07-01
53480 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-06-29 | 2018-06-29 22:31 | 2018-07-03 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED RADIATION DEVICE The following report was received from the State of Louisiana via phone: On June 29, 2018 the Louisiana Radiation Protection Division was notified that an employee of Wood Material (a dredging company) stole a radiation device. The radiation device was subsequently sold by the employee to the ERM Southern Recycling center. The recycling center identified and recovered the device. The recycling center then performed a leak test on the device to confirm that the device was not leaking. The device was then isolated and secured in a drum by the recycling center. The device is manufactured by Ronan Engineering and has a serial number of 211023A, but the activity is not known at this time. A police report was filed on the employee who stole the device. Louisiana has notified the NRC regional office. * * * UPDATE ON 7/3/18 AT 0923 EDT FROM JAMES PATE TO BETHANY CECERE * * * The following report was received from the State of Louisiana by email: "The gauge was a Ronan Engineering Flow Meter Gauge Model RLLI, Device S/N: 211023A, Source Model Number: CDC.700, Isotope: Cs-137 with Activity: 0.90 mCi. "The gauge was stolen by an employee from Wood Materials, 6148 River Road, New Orleans 70123. A police report was made & filed. The employee confessed to scraping the gauge for scrap metal. Employee terminated. "The gauge is secure at this time. Enforcement action will be taken on the licensee of the gauge for not securing the gauge. This matter is considered closed out." Notified the R4DO (Miller), NMSS Events, and ILTAB. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-07-09
53479 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-06-28 09:02 | 2018-06-28 13:05 | 2018-06-28 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED SUPERVISOR At 0902 EDT on June 28, 2018, a non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-06-28
53478 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-06-27 | 2018-06-28 10:10 | 2018-06-28 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE DISCONNECT The following information was received from the State of Texas via email: "On June 27, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's corporate radiation safety officer (CRSO) that one of his radiography crew had experienced a source disconnect. The crew was using a QSA 880D exposure device containing a 113.1 Curie iridium - 192 source. After completing the first shot on a new location on the pipeline, the crew could not get the source to return to the exposure device. The crew contacted the CRSO and set up new barriers at 2 millirem. The CRSO and a second individual qualified for source retrieval arrived at the site at 1743 hours. The retrieval team (RT) surveyed the guide tube and determined the source was in the collimator. The RT removed the guide tube from the exposure device and removed the camera from the area. Using a set of long tongs, the guide tube was removed from the pipe and the source slid down the guide tube until the connector was exposed. They could see the drive cable had broken near the connector. The source was shielded with bags of lead shot. The CRSO disconnected the broken drive cable from the source pigtail and connected the pigtail to a new drive cable that had been installed on the camera. The source was retracted to the shielded position in the camera. The camera and crank out device and drive cable will be sent to the manufacturer for inspection. No overexposures occurred as a result of this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # - 9590 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-07-06
53477 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2018-06-27 23:12 | 2018-06-28 05:37 | 2018-06-28 | AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS [Emergency Notification System] or under the reporting requirements of 10 CFR 50.73. "On June 27th, 2018 at approximately 2310 Mountain Standard Time (MST), in Palo Verde Unit 3, the #1 Steam Generator Economizer valve started closing. This caused Steam Generator #1 water level to decrease. Both Feed water pumps speed increased to raise Steam Generator level. At approximately 2311 [MST], the B Main Feed water pump tripped resulting in a Reactor Power Cutback. Steam Generator #1 level continued to decrease resulting in an Automatic Reactor Trip on Low Steam Generator #1 water level. All control rods inserted to shut down the Reactor to Mode 3 using Main Feed water and Steam Bypass. Post trip Steam Generator #1 level then increased and at approximately 2316 [MST] a Main Steam Isolation Signal (MSIS) was received on high Steam Generator level. The 'B' Auxiliary Feed water pump was manually started to maintain Steam Generator water levels and Steam Generator pressure was controlled using the Atmospheric Dump Valves (ADVs). "Following the reactor trip, all CEAs [Control Element Assemblies] inserted fully into the core. All systems operated as expected. No emergency plan classification was required per the Emergency Plan. Safety related busses remained powered during the event from offsite power and the offsite power grid is stable. No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 3 is stable and in Mode 3 feeding Steam Generators with Auxiliary Feed water Pump 'B'. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector was informed of the Unit 3 reactor trip." Unit 1and Unit 2 were unaffected by the Unit 3 trip. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-06-28
53476 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2018-06-26 16:30 | 2018-06-26 23:29 | 2018-08-13 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM DECLARED INOPERABLE "On June 26, 2018, at 1630 CDT, the Control Room Emergency Filtration System (CREFS) was declared inoperable when Main Control Room Supply Fan SF-C-1B was discovered to have elevated vibrations that brought into question the ability to meet its mission time. "CREFS is a single train safety system. Per 10 CFR 50.72(b)(3)(v)(D), an 8 hour report is required due to the fact that at the time of discovery this condition could have prevented the fulfillment of a safety function of an SSC [System Structure or Component] that is required to mitigate the consequences of an accident. "The licensee has notified the NRC Senior Resident Inspector." * * * RETRACTION FROM THOMAS FORLAND TO VINCE KLCO ON 8/13/18 AT 1024 EDT * * * The following retraction was received from Cooper Nuclear Station (CNS) via facsimile and phone call: "CNS is retracting the 8-hour non-emergency notification made on June 26, 2018 at 1630 CDT (EN# 53476). Subsequent evaluation concluded that overall vibration levels were not at a level that would impact the ability of the Main Control Room Supply Fan SF-C-18 to perform its safety function for its required mission time and the CREFS therefore, was operable. "The NRC Senior Resident Inspector has been notified." Notified the R4DO (Deese). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-06-26
53475 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-03-24 | 2018-06-26 18:28 | 2018-06-26 | AGREEMENT STATE REPORT - FAILURE TO PROPERLY LABEL A SHIPMENT The following information was obtained from the State of California via email: "On 03/16/18, the Site Manager at Vallecitos Nuclear Center (VNC) contacted RHB [California Radiologic Health Branch] licensing unit to notify of an incident related to a shipment from their facility. The incident occurred a year ago on 03/24/17, where a shipment of Cf-252 sources with a TI [Transportation Index] of 19 was inadvertently not flagged as exclusive use. This was identified by CHP [California Highway Patrol] at a weigh station approximately 10 miles from VNC [in Livermore, CA] and the shipment was returned to the facility. VNC corrected the paperwork, calling the shipment out as exclusive use. VNC was cited by CHP. VNC has recently received a letter from Alameda County District Attorney's Office referencing a Vehicle Code and a Professional Code. RHB will be following up on this investigation regarding failure to immediately notify RHB and for failure to label the shipment as exclusive use. "Note: Inspection unit at RHB was notified of this incident on 06/18/18." California Report No: 5010-031618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-07-04
53474 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-11-29 | 2018-06-26 17:30 | 2018-06-26 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received from the State of Texas: "During the review of an event, the Agency [Texas Department of State Health Services] found a letter from a licensee reporting the shutter on a Ohmart model SHD-45 containing a 50 millicurie cesium - 137 source had failed in the closed position. The report was dated November 29, 2017. The shutter did not pose an exposure risk to any individual. The licensee has worked with the manufacturer and the gauge was scheduled to be replaced on June 21, 2018. The Agency has not been able to confirm if the gauge was repaired/replaced. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I-9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-07-04
53473 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2018-06-25 | 2018-06-26 08:16 | 2018-06-26 | AGREEMENT STATE REPORT - UNDERDOSE OF Y-90 THERASPHERES The following information was obtained from New York City Department of Health and Mental Hygiene, Office of Radiological Health via email: "On June 25, 2018, a 65-year old male patient was treated with Y90 TheraSphere to the right side of the liver. The intended dose of administration was 64.8 mCi (2.4 GBq). Upon conclusion of the procedure, when the waste materials (delivery line, vial, gauze, etc.) was counted, it was found that 41.87 mCi (1.55 GBq) of Y90 TheraSphere was actually administered to the patient. In other words patient received 64.6% of intended dose. The Radiation Safety Office of Mount Sinai Hospital reported the incident to the New York City Department of Health and Mental Hygiene [NYCDOH] on 6/25/2018 at 1340 hrs. These findings were communicated to the patient and the referring physician within 24 hours. The licensee stated that no serious adverse events occurred and the patient will be followed up with Interventional Radiology as per protocol. The licensee indicated that the root cause analysis of the event is currently being performed and a detailed report of the event with corrective action will be sent to the NYCDOH within 15 days." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2018-07-04
53472 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-06-26 00:03 | 2018-06-26 04:26 | 2018-06-26 | MAIN STEAM LINE RADIATION MONITOR DETERMINED TO BE NON-FUNCTIONAL "At time 0003 [CDT], Main Steamline Radiation Monitor 2-RE-2326 (Main Steam line 2-02) reading spiked and [was] declared non-functional. "With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 2-02 could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant (CPNPP) has assurance of steam generator integrity and fuel cladding integrity and there is negligible safety significance to the current condition [with respect to the] public health and safety perspective. "Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 radiation monitor serves as a backup with alarm function and Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL 2-02. "Corrective actions are being pursued to restore 2-RE-2326 to functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-06-26
53471 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-06-25 10:29 | 2018-06-25 17:58 | 2018-06-25 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED SUPERVISOR At 1029 PDT on June 25, 2018, Pacific Gas and Electric determined a non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2018-06-25
53470 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-06-25 | 2018-06-25 11:11 | 2018-06-25 | OHIO AGREEMENT STATE REPORT - LOST IODINE-125 SEED The following information was obtained from the state of Ohio via email: "An I-125 seed, approximately 127 microCi, was retrieved from a breast seed localization patient on 6/20/18. A gamma probe was used during surgery to verify it was present in the tissue sample. After surgery the sample was x-rayed and surveyed to verify the seed was still present in the sample; the tissue was placed in a formalin tray and locked in a cabinet. Pathology dissected the tissue on 6/21/18 and did not find the seed. The licensee believes the seed was loosely attached to the tissue and was thrown away with the rest of the materials after it was x-rayed. The licensee performed surveys and did not locate the source. Due to the low activity of the source, it is not expected that the public dose limit would be exceeded." Ohio NMED Report No.: OH180005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-07-03
53469 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-06-22 09:00 | 2018-06-22 15:12 | 2018-06-22 | NON-LICENSED SUPERVISORY CONTRACTOR SUBVERTS FITNESS FOR DUTY TEST "At 0900 [EDT] on June 22, 2018, a non-licensed supervisory contractor subverted a random Fitness for Duty test. The contractor's site access has been terminated. The NRC Resident Inspector was notified. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-06-22
53468 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-06-21 | 2018-06-22 14:26 | 2018-07-02 | AGREEMENT STATE REPORT - DOSE MISADMINISTRATION The following information was received from the State of Georgia via email; "RMP [Georgia Radioactive Materials Program] received a call regarding an event that occurred at the main Emory Campus. A 57 year old male was treated on June 21, 2018 with 81.1 mCi of Y-90 Therasphere. The treatment site was the right lobe of the liver. Approximately an hour after the treatment the patient was scanned. The scan indicated that approximately 80% of the administered dose went to the left lobe, 10% went to the right lobe and some went to the stomach and some went to the 1st portion of the duodenum. It was determined there was a vessel spasm during the treatment that caused the theraspheres to shunt to the left lobe of the liver." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. Georgia Incident Report # 3. * * * UPDATE FROM IRENE BENNETT TO VINCE KLCO ON 6/2/2018 AT 1426 EDT * * * The following information was received from the State of Georgia via email: "[The Georgia Radioactive Materials Program] received Emory's report regarding the Y-90 procedure and verified the backflow to the left lobe was due to shunting. Based on this information, [Georgia has] determined that this is not a medical event. All documentation will be filed in the licensee's file and electronically." Notified the R1DO (Powell) and the NMSS Events Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2018-07-02
53467 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-06-22 08:41 | 2018-06-22 12:14 | 2018-06-22 | AUTOMATIC REACTOR TRIP "At 0841 EDT on June 22, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 95% power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. "The reactor automatically tripped due to a main turbine trip. The turbine trip was caused by main generator electrical trip. An investigation is in progress. "The automatic actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." The plant is currently stable at normal operating temperature and pressure. The grid is stable and the plant is in its normal shutdown electrical lineup. Unit 1 was unaffected by the Unit 2 trip. | 0 | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-06-22
53466 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2018-06-21 13:35 | 2018-06-21 18:12 | 2018-06-21 | AGREEMENT STATE REPORT - LOST TRITIUM SIGNS The following was received from the state of Utah via E-mail: On June 21, 2018 at 1335 MDT, Utah Department of Environmental Quality, Division of Waste Management and Radiation Control (DWMRC), received written notification from the Church of Jesus Christ and Latter-Day Saints that on June 21, 2018 four tritium exit signs were discovered to having been sent to the landfill for disposal. The licensee will continue to investigate the incident and will submit a written report to the DWMRC. Utah Event Report ID No: UT180004. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2018-06-29
53465 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-06-20 16:15 | 2018-06-21 12:07 | 2018-06-21 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA CRANK FAILURE The following was received from the state of Oklahoma via phone call and E-mail: On June 20, 2018, at approximately 1615 CDT, Tulsa Gamma Ray, Inc. (License # OK-17178-02) had a failure of the industrial radiography camera leaving the source exposed. The radiography camera is a model QSA 880D, source Spec T5, source strength unknown. The crank was a Sentinel SAN 882 Serial Number 15997. The licensee was authorized to perform a source recoveries, and the Radiation Safety Officer (RSO) successfully recovered the source. The RSO received a dose of 140 mRem as indicated on the RSO's pocket dosimeter. No other exposure information was provide at the time of the report. The state of Oklahoma will provide more information on this event as it becomes available. A State report number will be provided at that time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-06-29
53464 | -1 | AAF FLANDERS |  |  |  |  | 2018-05-02 | 2018-06-20 20:55 | 2019-08-20 | PART 21 - INTERIM REPORT NOTIFICATION The following was received via phone call and email: This report provides notification and interim information concerning an evaluation being performed by AAF Flanders for an unapproved design change in a High Efficiency Particulate Air Filter. "An evaluation is underway for filters that underwent a non-approved design change. AAF Flanders has determined that an evaluation cannot be completed within the 60 day period. Discovery of the potential deviation was May 2, 2018. "The information required for the 60-Day Interim Report Notification 21.21(a)(2) was provided. We anticipate that the evaluation will be completed by Sept 15, 2018. "AAF Flanders is evaluating a potential nonconforming condition associated with filters (model number 0-007-C-42-03-NU-11-13-GG FU5) supplied to Prairie Island Nuclear Generating Plant (PINGP) / Xcel Energy." AAF Flanders notified Prairie Island Nuclear Plant of this potential defect. * * * UPDATE ON 9/14/2108 AT 1129 EDT FROM SHAWN WINDLEY TO ANDREW WAUGH * * * The following information was received via email: "A notification was submitted to the Commission with the subject matter of, 'Unapproved Design Change in a High Efficiency Particulate Air Filter.' At this time, the evaluation is pending third party qualification testing of the product. Information obtained from the qualification will be used in the determination of a defect. AAF Flanders had anticipated this process to have been completed by Sept 15, 2018 but because it is still on-going, we request an extension until October 31, 2018 to submit a final report to the Commission. "The subject filters (model number 0-007-C-42-03-NU-11-13-GG FU5) supplied to Prairie Island Nuclear Generating Plant (PINGP)/ Xcel Energy had not been installed. AAF Flanders has recalled the subject filters and currently have them segregated and stored at our facility. They pose no threat public safety." Notified R3DO (Hanna) and Part 21/50.55 Reactors Group (email). * * * UPDATE ON 10/31/18 AT 1545 EDT FROM SHAWN WINDLEY TO HOWIE CROUCH * * * The following information was excerpted from information received via email: "AAF Flanders had anticipated the qualification process for said filters to have been completed by Sept 15, 2018. AAF requested a second extension by October 31, 2018 to submit a final report to the Commission, however; at this time our qualification is still pending third party approval. AAF Flanders is requesting another extension on the basis of an incomplete qualification of these filters. We anticipate qualification and a completed report on or before 12/15/2018." Notified R3DO (Stoedter) and Part 21/50.55 Reactors Group (email). * * * RETRACTION ON 08/20/19 AT 1140 EDT FROM SHAWN WINDLEY TO JEFFREY WHITED * * * The following information was received via e-mail: "AAF Flanders' evaluation of the condition identified in the interim report has been completed. The condition reported has been determined to be not reportable in accordance with 10 CFR 21. "The subject filters (model number 0-007-C-42-03-NU-11-13-GG FU5) have passed qualification testing in accordance with the American Society of Mechanical Engineers (ASME) AG-1, Section FC with the new urethane and are fully qualified and listed on the Qualified Products List. "The subject filters (model number 0-007-C-42-03-NU-11-13-GG FU5) supplied to Prairie Island Nuclear Generating Plant (PINGP)/Xcel Energy prior to this qualification test had not been installed and were subsequently returned to AAF Flanders. PINGP/Xcel Energy has been notified of the qualification status of the filter model." Notified R3DO (Riemer) and Part 21/50.55 Reactors Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2018-06-20
53463 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2018-06-20 11:45 | 2018-06-20 17:51 | 2018-06-20 | HIGH-PRESSURE CORE SPRAY INOPERABLE "On June 20, 2018, at 1145 hours (CDT), during panel walkdown, it was identified that High-Pressure Core Spray (HPCS) injection valve 1E22F004 was in the open position. Valve 1E22F004 is normally closed for containment integrity purposes. Operations personnel verified that the valve was open locally and that the plant computer indicated the valve is in the 'not closed' position. No alarms or status lamps indicated why the valve would be open and there was no valid demand signal. Reactor power, pressure, level, and feedwater parameters remain steady and unchanged, with no indication of HPCS injection having occurred or in progress. "A low-water level signal, or a high drywell pressure signal, or manual operation initiates HPCS. When a high-water level in the reactor vessel is detected, HPCS injection is automatically stopped by a signal to close injection valve 1E22F004. With valve 1E22F004 in the open position without a demand signal, closure on a high reactor water level condition was not assured. Therefore, HPCS was declared inoperable. The following Technical Specifications were entered: 3.5.1, Emergency Core Cooling Systems (ECCS) - Operating and 3.6.1.3, Primary Containment Isolation Valves (PCIVs). "Subsequently, HPCS injection valve 1E22F004 was observed to be cycling without operator action. The valve was deactivated in the closed position to assure the containment isolation function. "The cause of valve 1E22F004 cycling without operator action is under investigation. "HPCS is a single train safety system that consists of a single motor-driven pump, a spray sparger in the reactor vessel, and associated piping, valves, controls and instrumentation. HPCS is part of the ECCS network, which also includes Low-Pressure Core Spray, Low-Pressure Coolant Injection, and the Automatic Depressurization system. "This event is being reported as an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(v) as, 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident.'" The licensee notified the NRC Resident Inspector. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-06-20
53462 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-06-20 10:03 | 2018-06-20 11:39 | 2018-06-20 | NOTIFICATION OF UNUSUAL EVENT DECLARED DUE TO TOXIC GAS RELEASE On June 20, 2018 at 1003 CDT, the licensee declared a Notification of Unusual Event based on Emergency Action Level (EAL) 6.5.U, toxic gas release on site. The Notification of Unusual Event was terminated at 1025 CDT. The toxic gas release occurred when site personnel were filling a fire suppression carbon dioxide (CO2) tank outside the diesel generator building. The relief valve in the common diesel generator room for Unit 1 and 2 diesel generators inadvertently lifted causing a toxic gas environment by releasing CO2 into the room. The licensee terminated the tank fill stopping the release of CO2, and with the door to the room being opened, the gas cleared in about 20 minutes. The licensee has notified the NRC Resident Inspector. Notified DHS SWO, FEMA Ops, DHS NICC, FEMA NWC (email) and NuclearSSA (email). | 100 | 100 | 94 | 100 | 100 | 94 | -1 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | UNUSUAL EVENT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-06-20
53461 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-06-19 | 2018-06-19 16:00 | 2018-06-19 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION ON PACKAGE The following information was received via E-mail: "North Carolina Radioactive Material Branch (NCRMB) is reporting the following event: "On 6/19/2018, Memorial Mission Hospital, Asheville (NC License, 0091-6) reported receiving two Biodex PET boxes containing F-18 FDG [fludeoxyglucose] from Cardinal Health, Asheville (NC License, 0794-7). Both boxes were delivered to Cardinal Health, Asheville via courier from Cardinal Health, Charlotte (NC License, 0794-1). "Upon receipt of the boxes, Memorial Mission personnel performed surveys and wipes and noted the following contamination for Tc-99m on the boxes with the concentration of contamination being on the side handles of both boxes: Box 1: 88.96 kdpm/300 cm2 Box 2: 46.92 kdpm/300 cm2 "No contamination was found inside either of the boxes containing F-18 patient doses and contamination was only on outside handles of both boxes. Memorial Mission confirmed that no further contaminated packages were received. "Cardinal Health, Charlotte performed wipes and surveys of its work areas, courier vehicle and personnel. No contamination was found at this location with regards to this event. "Cardinal Health, Asheville performed wipes and surveys of its work areas, courier vehicle and personnel. The courier at this location that delivered the two boxes to Memorial Mission Hospital is also a Pharmacy Technician. Removable contamination was found on this person's hands and cleaned. No other contamination was discovered at this location or the courier vehicle. "No other notifications were made to any other agencies in NC. NCRMB was notified same day as the event. There are no other generic implications. "NCRMB has dispatched an inspector to perform an on-site investigation. This report will be updated once more information is discovered, to include corrective actions and any other info needed to close and complete this report. "Reporting Requirement: 10 CFR 20.1906(d)(1): Reports of removable contamination on package > limits in 10 CFR 71.87; removable contamination greater than limits specified in 49 CFR 173.443." NC Tracking Event Number: 180028. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-06-27
53460 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-06-19 07:00 | 2018-06-19 07:58 | 2018-06-19 | SAFEGUARDS REPORT Attempted introduction of contraband into a protected area. The licensee contacted Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2018-06-19
53459 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2018-06-16 11:21 | 2018-06-16 15:56 | 2018-06-16 | MANUAL REACTOR TRIP DURING STARTUP "At 1121 CDT on June 16, 2018, Arkansas Nuclear One, Unit 1 (ANO-1) performed a manual reactor trip due to a Turbine Bypass valve failing open on reactor startup. At the time, ANO-1 was in Mode 2 at approximately 2 percent power. "The failed Turbine Bypass valve resulted in an overcooling event and the Overcooling Emergency Operating Procedure (EOP) was entered. Main Steam Line Isolation (MSLI) automatic actuation occurred on 2 of the 4 channels of Emergency Feedwater Initiation and Control during the overcooling event in the 'B' Steam Generator. The remaining channels of MSLI were manually actuated by the control room staff from the control room. Overcooling was terminated after the closure of the Main Steam Isolation Valve (MSIV) and reactor coolant parameters were stabilized as directed by the Overcooling EOP. Additionally, Gland Sealing Steam was lost to the main turbine due to the closure of the 'B' Steam Generator MSIV and Loss of Condenser Vacuum Abnormal Operating Procedure was entered. "This is a 4-hour non-emergency 10 CFR 50.72 (b)(2)(iv)(B) notification due to a Reactor Protection System actuation (scram) and an 8-hour non-emergency 10 CFR 50.72 (b)(3)(iv)(A) notification for safety system actuation." All control rods fully inserted into the core during the trip. Heat removal is via the Atmospheric Dump Control valves to atmosphere. The NRC Resident Inspector has been notified. The licensee also notified the State of Arkansas. | 0 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-06-16
53458 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2018-06-14 | 2018-06-15 16:55 | 2018-08-17 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received from the State of Utah via email: "The licensee informed the State of Utah they are evaluating a potential medical event. A patient was implanted with 54 Pd-103 seeds in the prostate under ultrasound guidance. Per standard practice, the patient returned for a CT scan to verify the placement of the seeds. The CT scan revealed that 32 of the seeds had been implanted outside of the prostate. In addition, only 51 seeds were located, likely the result of 3 seeds being passed via stool. They believe that several additional seeds are in the rectum and will be passed following an enema." Utah Event Report ID No.: UT180003 * * * UPDATE ON 8/17/2018 AT 1106 EDT FROM TIM BUTLER TO ANDREW WAUGH * * * The following update was received from the State of Utah via email: "The licensee reported a medical event involving a patient treated for prostate cancer. The treatment included implanting 54 Pd-103 brachytherapy [seeds] (Theragenics, Theraseed) containing a total activity of 4 GBq (108.167 mCi), in the patient's prostate for a prescribed therapeutic radiation dose of 12,500 cGy (rad). The prostate gland only received approximately 1,000 cGy (rad). The seeds were implanted on June 14, 2018 under ultrasonic guidance. On June 15, 2018, the patient returned to the facility for a post implant CT scan. The scan showed that the implanted seeds, although in an appropriate pattern, were placed outside the intended target. The Licensee's Radiation Oncology group determined that an additional quality assurance review was warranted. The State performed a reactive inspection during the week of June 15, 2018. The cause was determined to be human error. An unintended dose to the rectum of approximately 18,677 cGy (rad) was received, where no dose was anticipated. Corrective actions included changes to the prostate brachytherapy protocol to incorporate an additional step to ensure the medical physicist and authorized user clearly identifies the prostate gland and the surrounding anatomy. The treatment will be cancelled if the prostate gland and surrounding anatomy cannot be visualized adequately." Notified R4DO (Deese), INES Coordinator (Milligan), and NMSS Event Notifications via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2018-06-25
53457 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-06-13 | 2018-06-13 17:19 | 2018-06-13 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER STUCK The following information was received via E-mail: "We [Oklahoma Department of Environmental Quality] have been informed by Universal Pressure Pumping, Inc. that one of their Berthold LB 8010 fixed gauges has experienced a failure of the shutter mechanism resulting in it being stuck in the open position. The gauge has been removed from the truck and is in storage. The licensee has contacted Berthold and is arranging for one of Berthold's technicians to come to their facility to repair the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-06-21
53456 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2018-06-12 15:00 | 2018-06-12 22:11 | 2018-06-12 | PRESSURE BOUNDARY LEAKAGE IDENTIFIED WHILE SHUTDOWN "On June 12, 2018, at 1500 CDT, a Reactor Coolant System (RCS) Pressure Boundary leak was identified during a Mode 3, hot shutdown walkdown on a High Pressure Injection Line [HPI] to Reactor Coolant Pump (P32C) drain line weld near MU-1066A HPI Line Drain Valve and MU-1066B HPI Line Drain Valve. The 3/4 inch drain line containing drain valves MU-1066A and MU-1066B on the 'C' HPI header (CCA-5 pipe class) has a through-wall defect on the pipe stub or welds between the sockolet and valve MU-1066A. The leak location is in the ASME Class I RCS Pressure Boundary. "The hot shutdown walkdown was being performed as part of a planned outage to investigate excessive Reactor Building Sump inleakage. Total unidentified RCS leakage prior to the investigation was determined to be at 0.165 gpm. After the initial investigation of the leakage, the following Tech Specs [TS] were determined be applicable: TS 3.4.5 - RCS Loops Mode 3, TS 3.4.13 - RCS Leakage, TS 3.5.2 - ECCS. Unit 1 is currently in Mode 3 and in progress of an RCS cooldown to comply with Tech Spec requirements." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(A) |  |  | 0 | 2018-06-12
53455 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-06-12 10:13 | 2018-06-12 12:13 | 2018-06-15 | SAFEGUARDS EVENT Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 6/15/18 AT 1526 EDT FROM RYAN MEYER TO DAVID AIRD * * * This event was initially reported under 10 CFR 73.71. Upon discovery, Grand Gulf Nuclear Station (GGNS) rapidly employed compensatory measures to address this vulnerability. GGNS verified no tampering or sabotage occurred. In addition, GGNS found no evidence that unauthorized access occurred. Therefore, this event is not reportable and this event is being retracted. The licensee has notified the NRC Resident Inspector. Notified R4DO (Taylor) and 73.71 Safeguards Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-06-12
53454 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-06-11 19:55 | 2018-06-11 21:49 | 2018-06-15 | SAFEGUARDS DEGRADATION DUE TO WEATHER CONDITIONS Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The weather warning expired at 2030 CDT. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM DAVE VAN DER KAMP TO OSSY FONT ON 6/15/18 AT 1016 EDT * * * Upon further review, the licensee determined that the event was not reportable under 10CFR73.71, as originally reported, but is reportable under "Other Unspecified Requirements". Notified R4DO (Taylor) and the 73.71 Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 1 | 2018-06-11
53453 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-06-11 | 2018-06-11 14:29 | 2018-06-11 | AGREEMENT STATE REPORT - DAMAGED MOISTURE-DENSITY GAUGE The following was received from the State of Texas via email. "On June 11, 2018, the licensee's radiation safety officer (RSO) reported to the Agency [Texas Department of State Health Services] that one of its Humboldt 5001-EZ moisture/density gauges (serial number 4097) containing a 40 milliCurie americium-241/Beryllium source (NJ04418) and a 8 milliCurie cesium-137 source (7146GQ) had been run over by a dump truck at a temporary job site. The upper casing on the gauge was damaged and the guide bar broke off as the rod was taking a reading. The rod was in the ground when hit by the truck. The technician was taking readings when he noticed a dump truck backing up close to his location. He moved to the side and tried to wave the person driving to stop. The truck didn't stop and hit the gauge. The incident was reported by the RSO and stated the area has been restricted access until the device can be recovered. The RSO traveled to the site and accessed the device. The source was successfully pulled/retrieved into the shielded position, surveyed and being transported to a servicing company for possible repair or disposal. The company will provide full details of the incident within the next few days. Investigation ongoing." Texas Incident #: 9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-06-19
53452 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-06-11 | 2018-06-11 13:27 | 2018-06-11 | AGREEMENT STATE REPORT - STOLEN MOISTURE-DENSITY GAUGE The following was received from the State of Texas via email. "On June 11, 2018, the licensee's radiation safety officer (RSO) notified the Agency [Texas Department of State Health Services] that one of their Troxler 3440 moisture/density gauges (SN: 67091), containing a 40 milliCurie americium 241 source and an 8 milliCurie cesium-137 source, could not be accounted for. The gauge was last used at a temporary job site on May 25, 2018. The technician that used the gauge stated to the RSO that he had returned the gauge to the storage area at their facility in Midland, Texas, that afternoon. He further stated the insertion rod was locked. The gauge, along with another, were to have been picked up by, and transferred to, another licensee (a company associated with the licensee) the week of May 28th. On June 4, 2018, the RSO discovered the gauge had not been picked up/transferred nor was it in the storage area. He began an investigation. The RSO interviewed the technician and facility supervisor and reviewed documentation. The gauge had not been used by the licensee since May 25th. The associated licensee conducted a physical inventory of all of its gauges. The associated licensee's RSO was on vacation and could not be reached until June 11th. After it was confirmed with him that the associated company did not have possession or any further knowledge of the gauge, the RSO made the notification. The RSO is continuing his investigation. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #: 9583 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-06-19
53451 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2018-06-10 10:00 | 2018-06-11 10:21 | 2018-06-11 | AGREEMENT STATE REPORT - STOLEN MOISTURE-DENSITY GAUGE The following was received from the State of Utah via email. "The morning of June 10, 2018, the licensee discovered that a portable nuclear density gauge had been stolen from one of their work trucks. The truck had been parked in the driveway of the AGEC's [Applied Geotechnical Engineering Consultants, Inc.] employee's house. The license claims that the gauge was properly stored in storage container that was bolted to the bed of the truck and the tailgate was locked. The licensee explained that the perpetrator broke through the locked tailgate, cut the barriers around the Troxler box, cut the locks on the Troxler box and removed the portable gauge. The Salt Lake City Police Department was also contacted. The licensee will continue to investigate the incident and will submit a written report to the DWMRC [Division of Waste Management and Radiation Control]." Event Report ID No.: UT180002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2018-06-19
53450 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-05-09 | 2018-06-09 10:48 | 2018-08-14 | AGREEMENT STATE REPORT - INCORRECT DOSE ADMINISTRATION The following report was received from the State of California by email: "[The] National Director Medical Physics, of McKesson Specialty Health, Radiation & Imaging, contacted LA County Radiation Management (LA County) on June 8, 2018 to report a potential Medical Event that occurred at Western Tumor Medical Group on May 9, 2018. The National Director Medical Physics has been remotely reviewing available data at their location in Decatur, Georgia, and while they are not able to definitively conclude the unplanned dose to the patient's small intestine/bowel pending the return of the Western Tumor Medical Group RSO from overseas, it appears that a Medical Event occurred. "The potential Medical Event occurred during an HDR [High Dose Rate] brachytherapy procedure in which the tandem ovoid insert shifted inside of the female patient's pelvis (which has extensive damage from uterine cancer) apparently causing two of the dwells to shift to a position different from that in the treatment plan. As a result, the dose to the non-target small intestine/bowel from the 1st of 3 fractions is believed to have been about 587 cGy (587 rad), instead of the planned approximately 220 cGy (220 rad). The treatment plan was modified for the shifted tandem ovoid position, and the 2nd and 3rd fractions were given resulting in approximately 220 cGy (220 rad) each to the small intestine/bowel. "A site visit will be conducted to meet with the licensee's personnel when the RSO comes back from travel to gain a better understanding of the details of the event, including the delay in the reporting of the event by the RSO, and patient/patient's physician notification." * * * RETRACTION FROM THOMAS GEZA TO VINCE KLCO ON 8/14/18 AT 1425 EDT * * * The following information was received from the State of California via email: "Calculations have been performed by the Licensee's RSO that demonstrated to [the State of California] that [the dosage] fell below the reportability threshold of 10 CFR 35.3045(a)(1) and 35.3045(a)(3) because the dose occurred to the non-target organ, and only in the first of the 3 fractions, causing the numbers to even out, i.e., average down to below reportable numbers (in terms of 50 REM and 50% of planned dose)." California ID # 060818 Notified the R4DO (Deese) and NMSS Events Notifications via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-06-18
53449 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-04-19 | 2018-06-07 16:10 | 2018-06-07 | AGREEMENT STATE REPORT - LEAKING SOURCE The following report was received from the State of Florida: "[The Florida Department of Health / Bureau of Radiation Control] received an email from Florida International University [FIU] reporting a leaking source. On April 19, the RSO [Radiation Safety Officer] opened a cabinet inside CP- 194 and did leak tests on stored sealed sources inside that cabinet. One Ni-63 source (9.4 milliCurie) was contained in a plastic vial with a screw top lid. The RSO removed the plastic vial from the radiation container for one minute to do a swab test, and sent the swab to an approved vendor for analysis. FIU EHS [Environmental Health and Safety] and the RSO were informed that the leak test associated with the Ni-63 source came back with a reading of 0.0119 microCuries (above the max. 0.005 microCurie limit) on May 18th. The RSO removed the radiation container containing the rad source from CP- 194 on May 22nd and moved it to the EHS vault in ACH 4 to await proper disposal. No other contamination was found." Incident Number: FL18-070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-06-15
53448 | 0 | OK DEPT OF ENVIRONMENTAL QUALITY |  |  |  |  | 2018-06-06 | 2018-06-07 16:09 | 2018-06-07 | AGREEMENT STATE REPORT - INCORRECT DOSE ADMINISTRATION The following was received from the State of Oklahoma by email: "We [the Oklahoma Department of Environmental Quality] were just informed of a medical event and abnormal occurrence that happened yesterday at Southwestern Regional Medical Center dba Cancer Treatment Centers of America (OK-27041-01) in Tulsa, OK. The incident involved a patient who was supposed to receive a 110.8 Gy dose of Yt-90 SIR Spheres to the right lobe of the liver. A CT [scan] of the patient after the procedure showed that the microspheres had actually been delivered to the left lobe." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-06-15
53447 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-01-12 | 2018-06-07 12:16 | 2018-06-07 | AGREEMENT STATE REPORT - LEAKING CALIBRATION SOURCE The following information was obtained from the State of Texas via email: "On June 7, 2018, the Agency [Texas Department of State Health Services] received a written report detailing a source had been found leaking in January 2018. The source was a dose calibration reference source. The labeled activity was 198.8 microCuries, Cs137, reference date of 1/1/2012, serial number 1551-38-4, RA number 030880. The leak test was completed twice with results of 9.65 and 12.9 nanoCuries on January 5 and 15, 2018. [Neither] the radiation safety officer nor the medical physicist reported the leak in January. The report was submitted today due to discovery when an inspector found the leak test record during the routine inspection of the facility. The violation was cited in the inspector's report. A second violation was not cited although a record was completed for the leaking source. The source was disposed of at a licensed site on March 20, 2018." Texas Incident #: 9582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-06-15
53446 | 0 | CTI AND ASSOCIATES |  |  |  |  | 2018-06-05 16:00 | 2018-06-06 17:35 | 2018-06-06 | DAMAGED MOISTURE DENSITY GAUGE The licensee's gauge operator was preparing to sample some work being done by a construction company when the company's road grader began backing into his sample area. The operator attempted to wave off the grader but he was in the grader operator's blind spot. The grader struck the gauge side and damaged the housing. The source rod was retracted so the sources were in their shielded position. The RSO [Radiation Safety Officer] was contacted and performed an area survey and a survey on the gauge. There were no abnormal readings. The gauge was swipe tested and the licensee has sent the swipe off for analysis. No overexposures were reported. The gauge was a Troxler model 3440 which contained a 9 mCi Cs-137 source and a 44 mCi Am-241 source. The gauge is currently in secure storage at the licensee's facility. Once the swipe tests are analyzed, the disposition of the gauge will be determined. The site of the incident was Ann Arbor, MI. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-06-14
53445 | -1 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2018-06-05 15:14 | 2018-06-06 15:48 | 2018-07-11 | UNANALYZED CONDITION RESULTING FROM INCORRECT IMPLEMENTATION OF ITEMS RELIED ON FOR SAFETY (IROFS) "Appendix A to 10 CFR 70 (b)(1) "An incorrect implementation of IROFS36c (Limit Cylinder Mover to Electric or Diesel with less than 280L [74 gallons] Fuel Load) has been identified as having occurred for feed deliveries into the Cylinder Receipt and Dispatch Building (CRDB). IROFS36c requires that UF6 transporters/movers inside CRDB truck bays utilize a tractor which has a limited fuel capacity of less than 74 gallons. This requires the Over the Road (OTR) tractor truck to disconnect the trailer in a designated staging area and a local tractor with a fuel tank capacity less than 74 gallons be utilized with the OTR trailers. Methods were used allowing an OTR truck trailer to access the CRDB with the OTR tractor and fuel tanks of the vehicle remaining outside. Activities involving OTR tractor trailers entering the CRDB truck bay in this manner have not been evaluated in the ISA. "10 CFR 70.50 (c)(iii) "(A) There was not a material release, no radiological or chemical hazards were present. "(B) No exposure occurred "(C) A condition exists which resulted in the facility being in a state that was different from that analyzed in the Integrated Safety Analysis. The method for cylinder transport into the CRDB truck bay by an OTR tractor, in proximity to cylinders inside the CRDB, has not been specifically evaluated as the evaluated condition prohibited the use of vehicles with fuel capacities in excess of 74 gallons within the CRDB truck bay. The only piece of equipment which entered the CRDB was the OTR trailer; the tractor remained connected and outside the CRDB. "(D) IROFS36c remains available and reliable to perform its safety function. The identified deficiency only affects OTR tractors that could potentially expose UF6 cylinders in the CRDB to fuel sources greater than 74 gallons. UUSA [Urenco USA] has issued a stop work to prevent the introduction of excessive fuel capable of causing a release of UF6 inventory in the area of concern should a fire occur. The capabilities of existing IROFS are sufficient to meet the performance requirements of 10 CFR 70.61. "(iv) No external conditions affect this event. "(v) A stop work was issued to prevent the access of OTR tractor trucks to the CRDB where proximity to UF6 cylinders could occur. "(vi) An event did not occur at UUSA. UUSA remains in a safe and stable condition. "(vii) Current and planned site status is normal. No emergencies have been or will be declared. "(viii) No local, state, or federal agencies will be notified. "(ix) No press releases will occur. "Condition has been entered into the UUSA Corrective Action Program. Event Record 125051." The licensee will notify R2 (Lopez). * * * RETRACTION ON 07/11/2018 AT 1534 EST FROM BLAKE BIXENMAN TO STEVEN VITTO * * * "EN53445, made June 5th, 2018, reported a condition in accordance with Appendix A to 10 CFR 70 (b)(1) in which the facility was in a state different from that analyzed in the Integrated Safety Analysis, and which resulted in failure to meet the performance requirements of 10 CFR 70.61. "This report was prompted by an incorrect implementation of IROFS36c (Limit Cylinder Mover to Electric or Diesel with <280L Fuel Load) during feed deliveries into the Cylinder Receipt and Dispatch Building (CRDB). An Over the Road (OTR) tractor containing greater than the maximum allowable fuel load was permitted access the CRDB Truck Bay with the OTR truck trailer. "At the time of the report, this method for cylinder transport into the CRDB Truck Bay by an Over the Road (OTR) tractor in proximity to cylinders inside the CRDB had not been evaluated. URENCO USA conservatively assumed a failure in the performance requirements of 10 CFR 70.61 at the time of the 24 hour report. Since the time of the initial report, URENCO USA has completed an assessment of safety significance for the events reported in EN53445. "With detailed results documented in the UUSA corrective action program, Event Record EV125051, the following conclusion has been made: "The fuel delivery events using the OTR truck into the CRDB can be categorized as events with low safety significance since they would not result in breached/ruptures of UF6 cylinders and no uranic material would be released in the event of a fire involving UF6 cylinders in the CRDB Truck Bay. This correlates with a low consequence event. "Based on calculations shown in the 'Assessment of Safety Significance for Events Documented in EV125051', the conditions reported in EN53445 did not result in failure to meet the performance requirements of 10 CFR 70.61. Therefore, the condition reported in EN53445 did not exceed the criteria which would necessitate an event be reported to the NRC. URENCO USA hereby retracts Event Notification 53445." Notified R2DO(Rose), Fuels Group, and NMSS Events Notification email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2018-06-06
53444 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2018-06-05 | 2018-06-06 13:27 | 2018-06-06 | ARIZONA AGREEMENT STATE REPORT - NUCLETRON HIGH DOSE RATE APPLICATOR MALFUNCTIONED DURING TREATMENT Below is a summary of multiple emails received from the State: At 1530 hrs. MST on 6/5/18, the State was notified that a patient was undergoing high dose rate treatment (HDR) when the Nucletron HDR applicator malfunctioned. The treatment plan was to deliver the intended fraction using thirteen dwell points but the HDR applicator failed at dwell point 9 of 13. The vendor, Elekta, was notified and they repaired the applicator. The written directive was modified and the patient will be able to complete the treatment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2018-06-14
53443 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-06-04 09:20 | 2018-06-04 14:00 | 2018-06-04 | MANUAL REACTOR TRIP ON LOWERING STEAM GENERATOR WATER LEVEL "At 0920 CDT, Braidwood Unit 1 reactor was manually tripped due to lowering steam generator water levels following a trip of the 1C main feedwater pump. The cause of the 1C main feedwater pump trip is unknown at this time and is under investigation. "Both trains of Braidwood Unit 1 auxiliary feedwater started automatically following the reactor trip to maintain steam generator water levels. "All systems responded as expected. Steam generator power operated relief valves lifted momentarily and reseated as designed in response to the secondary transient due to the reactor trip. The main steam dump valves are in service to the main condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. AC power is being provided by offsite power with the diesel generators in standby and all safety systems available. There is no impact to Unit 2. "This report is being made per 10CFR50.72(b)(2)(iv)(B) for a RPS actuation, 4-hr. notification, and per 10CFR50.72(b)(3)(iv)(A) for an automatic actuation of the auxiliary feedwater system, 8-hr. notification." All rods inserted into the core during the trip. Concerning the relief valves momentarily lifting and reseating, there is no known primary-to-secondary leakage. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-06-04
53442 | 0 | FRAMATOME INC. |  |  |  |  | 2018-05-31 | 2018-06-02 14:32 | 2018-06-02 | PART 21 NOTIFICATION - FAILURE OF RELAYS TO CHANGE STATE The following report was received via a fax: "Identification of Basic Activity: Eaton NBF66F Relay "Basic Activity Supplied By: Framatome Inc. "Nature of Defect: While performing analysis on AC Eaton NBF relays, Framatome discovered that, unless a specific application technique is utilized while applying epoxy to the pin within the crossbar, the potential for the epoxy to become foreign material is introduced. This foreign material could migrate to the area between the moving and stationary magnets, preventing the relay from completing its change of state when called upon. This condition does not occur in the de-energized direction. Framatome has not been notified of any occurrence of this condition. A different epoxy application technique was utilized between 2008 and May of 2013 on relays provided to HB Robinson (the only customer requiring the epoxy application by Framatome). Thus, a potential for this defect is limited to those relays provided during that time period. "Defect Determination Date: This issue was determined to be a 10 CFR 21 defect on May 31, 2018. "Number and Location of Basic Components: 307 potentially affected safety related relays with epoxy applied to their relay pins were supplied to the H.B. Robinson nuclear plant. "Corrective Actions to Date: The application process was reevaluated and revised in 2013. "Advice related to the Defect: Framatome is working to provide advice to the customer on the path forward related to this defect." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-06-02
53441 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-05-31 | 2018-06-01 15:50 | 2018-06-01 | AGREEMENT STATE REPORT - EXPOSURE TO MEMBERS OF THE PUBLIC The following information was received via E-mail: "On May 31, 2018, during a turn-around at Calcasieu Refining Co., lockout and tagout procedures were not performed for two fixed gauges. Two non-radiation workers were over-exposed for the limit of 2 mR/hr. External radiation exposures are currently estimated at between 20 to 40 millirem whole body. "The two sources were 50 mCi Cs-137 sources in Ohmart Vega Model SH-F1 gauges with serial numbers 70012 and 69998. "This event was reported by the facility on June 1, 2018." LA Event Report ID No.: LA20180010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-06-11
53440 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-05-31 | 2018-06-01 15:21 | 2018-06-01 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED DENSITY GAUGE The following report was received from the Ohio Bureau of Environmental Health and Radiation Protection via email: "The Licensee had a truck with a CPN Model MC1DR gauge in it, stolen at approximately [1330 EDT] on 5/31/18 from a convenience store in southeast Columbus. The gauge contains 10 mCi of Cs-137 and 50 mCi of Am-241 sealed sources. The truck and gauge were recovered by police several hours later. The Licensee got the truck and gauge back about [2100 EDT] that evening. The gauge case had been opened, but the gauge did not appear to be damaged. The Licensee is taking the gauge to Cline Technical Services (a licensed service provider) to have it checked out as a precautionary measure. An ODH [Ohio Department of Health] inspector [will be visiting the] licensee location on Monday, 6/4/18." Ohio Item Number: OH180004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-06-11
53439 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-05-31 | 2018-06-01 14:45 | 2018-07-11 | AGREEMENT STATE REPORT - FAILURE OF RADIOGRAPHY SOURCE TO RETRACT The following information was received via E-mail: "On June 1, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that a radiography crew was unable to retract a 50 Curie Iridium-192 source into an INC 100 exposure device. The crew was working in a remote area in West Texas when they could not get the source to go past the inlet nipple of the exposure device. After a few attempts, the crew contacted the licensee and an individual authorized to recover sources was sent to the site. "The licensee did not have specific information on how the source was retracted, but stated it took the individual about 45 minutes to recover the source. The source was returned to the fully shielded position. The exposure device and source were returned to the licensee's storage area and will be sent to the manufacturer for inspection. The licensee stated the exposure device was surveyed and radiation levels were normal. "The licensee reported that one individual's 0 - 200 millirem self-reading dosimeter did go off scale. The individual's OSL dosimeter has been sent to the licensee's dosimetry processor for reading. The licensee stated it calculated the individual's dose to be 400 millirem based on an interview with the individual. The licensee stated no individual involved received an exposure that exceeded any limit. No member of the general public received an exposure from this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9578 * * * UPDATE FROM ART TUCKER TO GEROND GEORGE ON 7/11/2018 AT 1125 EDT * * * The following information was received from the State of Texas via email: "On June 1, 2018, the licensee reported one of its crews were unable to retract a 50 curie iridium - 192 source to the fully shielded position. The licensee's written report received June 29, 2018, stated one of the radiographers had disconnected the guide tube from the exposure device and saw the source was not in the shielded position. The licensee stated the radiographer would have been in contact with the guide tube for 3-5 seconds. The individuals badge was sent for processing and had a reading of 312 millirem DDE. The licensee's initial calculation for the exposure to the individuals hands was 450 millirem. The Agency questioned the dose assessment to the hand. On July 11, 2018, the licensee's radiation safety officer stated they have contacted a service company to perform the dose calculations for the individuals hands. Pictures of the individuals hands taken on July 11, 2018, show no adverse effects from the exposure." Notified the R4DO (Pick) and the NMSS Events Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-06-11
53438 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-06-01 | 2018-06-01 14:42 | 2018-06-19 | TORNADO MISSILE VULNERABILITIES "During the period of evaluation of tornado missile vulnerabilities and the potential impacts to technical specification (TS) plant equipment, it was determined that the power cables to a safety related motor control center (MCC) in the service water (SW) intake structure are not adequately protected from tornado generated missiles. During walk downs, it was identified that the installed SW pipe tunnel barrier is not adequate. A tornado could generate missiles capable of striking the power cables and rendering a SW MCC inoperable. "These conditions are reportable per 10 CFR 50.72(b)(3)(ii)(B) and per 10 CFR 50.72(b)(3)(v)(D). "This condition is being addressed in accordance with NRC enforcement guidance provided in Enforcement Guidance Memorandum (EGM) 15-002, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' Revision 1, and DSS-ISG-2016-01, 'Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002, Enforcement Discretion for Tornado- Generated Missile Protection Noncompliance,' Revision 1. Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been notified." The licensee will be notifying the Lower Alloways Creek Township. * * * UPDATE ON 6/18/2018 AT 1604 EDT FROM JUSTIN HARGRAVE TO RICHARD SMITH * * * "During subsequent walk downs, PSEG [Public Service Enterprise Group] identified that both the Unit 1 and Unit 2 turbine driven auxiliary feedwater pumps are also not adequately protected from tornado generated missiles. The steam exhaust pipe could be potentially impacted and cause crimping that could reduce steam exhaust flow and pump capacity. EN 53438 is updated to include both Salem units and these additional components. "This condition is being addressed in accordance with NRC enforcement guidance provided in enforcement Guidance Memorandum (EGM) 15-002, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' Revision 1, and DSS-ISG-2016-01, 'Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' Revision 1. Compensatory measures have been implemented in accordance with these documents." The NRC Resident Inspector has been notified. The licensee will be notifying the Lower Alloways Creek Township. Notified R1DO (Burritt). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-06-01
53437 | 0 | CHRISTIANA CARE HOME SERVICES, INC |  |  |  |  | 2018-05-30 | 2018-06-01 13:05 | 2018-06-01 | LOST IODINE-125 SEEDS On 5/30/2018 a physicist for Christiana Care Home Services discovered that 50 Iodine-125 seeds were missing from the Hot Lab. The licensee began investigating to determine what happened to the seeds. The licensee determined that the seeds had been initially brought into the Hot Lab on 2/6/2018. The licensee believes that on 3/16/2018 an employee from Occupational Safety picked up empty trays from the Hot Lab to recycle them as part of their recycling program and that the Iodine-125 seeds may have been on two of the trays picked up. The trays were taken to a trailer where normal scrap metal is placed and were later picked up by the recycling company. The licensee believes, but could not confirm that the recycling company picked up the trays along with the seeds which were then taken to universal waste disposal. The licensee interviewed the occupational safety individual and the individual could not confirm that he saw any Iodine-125 seeds in the trays he placed into the recycling box. The licensee has also contacted the recycling company to determine if the boxes can be retrieved, however, the recycling company stated that the box of scrap metal could not be retrieved at this point. The licensee contacted the Iodine-125 vendor to confirm that the inventory that they have in their possession was correct. The quantity of seeds missing consisted of 50 Iodine-125 seeds with a total activity of 6 millicuries. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2018-06-11
53436 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-05-30 | 2018-06-01 11:39 | 2018-06-01 | AGREEMENT STATE REPORT - IN-LINE DENSITY GAUGE STUCK SHUTTER The following information was received via E-mail: "On May 31, 2018, the Department [PA DEP Bureau of Radiation Protection] was notified by the licensee that a malfunction of a roll pin on a shutter handle occurred at a temporary jobsite in Eighty Four, Pennsylvania. It is initially reportable per 10 CFR 30.50(b)(2). "A roll pin, which holds the shutter handle to the shutter shaft on a Berthhold Model LB 8010 in-line density gauge containing 20 milliCuries of cesium-137 became sheared off during an attempt to move the shutter to the open position, rendering the gauge unusable. The gauge is currently being stored at their Punxsutawney, PA location. The shutter is in the closed position and the gauge is out of service awaiting repair from the manufacturer. There was no other damage to the gauge. No overexposures have occurred. "Radionuclide: Cs-137 Manufacturer: Berthold Model: LB 8010 Serial Number: 10485 Activity: 20 mCi "The cause of the event has been attributed to normal wear and tear on the gauge. A reactive inspection is planned by the Department." PA Event Report ID No: PA180013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-06-11
53435 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-05-31 14:20 | 2018-05-31 16:20 | 2018-05-31 | REACTOR WATER CLEANUP SYSTEM DECLARED INOPERABLE "On May 31, 2018 at 1420 EDT, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow - High function was declared inoperable as a result of indicating downscale. This condition would have prevented the primary containment isolation valves for the RWCU system from automatically isolating on a high differential flow condition. "At 1519 EDT, RWCU was shutdown and the affected penetration flow paths were isolated in accordance with station procedures per Fermi Technical Specifications. "The cause of the event is under investigation. "There was no radiological release associated with this event. All other RWCU primary containment isolation instrumentation functions remained operable and the associated RWCU system primary containment isolation valves were capable of being remotely closed by the control room operators throughout the event. However, the condition is reportable pursuant to 10 CFR 50.72(b)(3)(v)(C), and 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-05-31
53434 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2018-04-04 | 2018-05-31 13:59 | 2018-06-01 | AGREEMENT STATE REPORT - PATIENT SKIN CONTAMINATED WITH FLOURINE-18 The following summary was received from the North Dakota Department of Health via telephone: On April 4, 2018 the licensee reported that a patient undergoing a PET (Positron Emission Tomography) scan was squirted with 15 millicuries of FDG (Fluorodeoxyglucose) - Flourine-18, by the technologist administering the dose. A peak skin dose of 2 Gray was calculated by the licensee Radiation Safety Officer. The North Dakota Department of Health is awaiting additional information from the licensee regarding the event. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE ON 06/01/2018 AT 09:17 FROM BROOKE OLSON TO THOMAS KENDZIA * * * "On April 4, 2018 a patient was imaged with ~15 millicuries of FDG. At the time of the injection, it is now believed that ~15 millicuries dose was inadvertently delivered on the patient's shirt. Since the first dose wasn't administered as intended, a second ~15 millicuries dose was administered into the patient. Per protocol the patient rested for an hour and was imaged. The patient was released from the scan room and was discharged and went to the cafeteria. The [study] physician reviewed the images and found them non-diagnostic due to external contamination. The [study] physician ordered that the images be repeated. The patient was located in the cafeteria and returned to Nuclear Medicine and his shirt was removed. Patient was reimaged approximately an hour after the start of the first scan (approximately 2 hours after the shirt was contaminated) and the second set of images were deemed to be diagnostic. "On May 15, 2018 the RSO [Radiation Safety Officer] learned of the event and began an investigation. The skin dose is estimated to be approximately 2.8 Gy to 100 cm2 of tissue. This exposed tissue was on the patient's torso. The uncertainty in the skin dose calculation is great. Due to the complexity of the calculation, the skin dose was estimated on May 31, 2018. "The study physician is aware of the incident and will notify the referring physician. The patient is unlikely to have noticeable negative effects from the incident, however if the patient did have a tissue reaction, it would have been mild and transient. The patient has not yet been notified of any of the findings since the RSO was made aware, however the patient was aware that he was spilled on and that his shirt was kept for decay. Notice will be sent to the patient offering the ability to obtain a written description of the event. "Continued investigation is in process and will start with a review of reporting requirements and event management related to radioactive spills." Notified the R4DO (Farnholtz), INES (Milligan), and the NMSS Events Notification email group. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2018-06-08
53433 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2018-05-30 07:10 | 2018-05-31 08:54 | 2018-05-31 | TECHNICAL SPECIFICATION DEVIATION "On May 30, 2018, at 07:10 CST, with the reactor operating at 10 MW in the automatic control mode, MURR [University of Missouri Research Reactor] was shut down due to a failure of the Control Rod Operate Switch 1S4 to move the shim control blades in the inward direction. The Reactor Safety (Scram) and Rod-Run-In Systems were unaffected by this failure and remained operational and would automatically and manually initiate, if required. This email is a required notification per MURR TS [Technical Specification] 6.6.c(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1.b, has occurred. MURR was not in compliance with all of the Limiting Conditions for Operations (LCOs) as established in Section 3.0. Specifically, MURR was not in compliance with TS 3.2.a, which states, All control blades, including the regulating blade, shall be operable during reactor operation. Control Rod Operate Switch 1S4 was replaced and retest was conducted satisfactorily, which included verifying inward and outward movement of all 4 shim control blades. Authorization was received from the Reactor Facility Director, as required by TS 6.6.c(4), to restart the reactor and resume 10 MW operation. A detailed event report will follow within 14 days as required by MURR TS 6.6.c(3)." The failure was identified during scheduled testing and the reactor was shutdown by manual Scram in accordance with procedures. The licensee notified the NRC Research and Test Reactor Project Manager (Wertz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2018-05-31
53432 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-05-29 | 2018-05-30 11:14 | 2018-05-30 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following was received from the state of Texas via email: "On May 30, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that on May 29, 2018, a Troxler model 3440 moisture/density gauge was damaged at a field site. The gauge contains an 8 millicurie cesium-137 source and a 40 millicurie americium-241 source. While the gauge was in taking a measurement and the technician and the job site foreman were talking, a bobcat operator working in the area failed to see the gauge and ran over it. The RSO stated the foreman and technician attempted to stop the operator of the bobcat, but were unable to get his attention. The RSO stated the operating rod for the cesium source was slightly bent, but the technician was able to return the source to the shielded position. The RSO stated the gauge was surveyed and radiation levels were normal. The gauge was returned to the licensee's location in San Antonio, Texas, for storage. The manufacturer has been contacted for guidance on what to do with the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # - 9577 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-06-07
53431 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-05-10 | 2018-05-29 17:42 | 2018-05-29 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following was received from the state of Nebraska via email: "DHHS [Nebraska Department of Health and Human Services] - Office of Radiological Health received written notification on 5/29/18 from GL0604 - Mary Our Queen Kenny Center indicating a lost/not found tritium exit sign during their Annual Renewal. Licensee initially telephoned DHHS on 5/10/18 to indicate they could not locate the device at the listed location and would be checking additional buildings. Licensee checked several additional buildings on their campus and contacted the electrician used during recent (2016) renovation in an effort to locate the device. Licensee believes the device was removed either during a prior renovation or due to regular maintenance and repair but cannot verify due to staffing changes. "Source/radioactive material: Sealed Source Luminous Manufacturer: Safety Light Corp. Model number: 880-12-6-10 Serial number: A21170 Radionuclide: H-3 Activity: 7.5 Ci (277.5 GBq)" Nebraska Item Number: NE180005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-06-06
53430 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-05-25 | 2018-05-29 14:48 | 2018-10-12 | AGREEMENT STATE REPORT - PATIENT SKIN CONTAMINATION The following was received from the Commonwealth of Pennsylvania via email: "On May 29, 2018, the Department's [Bureau of Radiation Protection] staff in Central Office became aware of a medical event (ME) at U PENN hospital in Philadelphia. The ME is reportable as per 10 CFR 35.3045(a)(1)(i) and also meets criteria for an Abnormal Occurrence. "On May 25, 2018, a 17 year old pediatric patient underwent an 834 millicurie metaiodobenzylguanidine (MIBG) lodine-131 (I-131) treatment for brain cancer. The dose was delivered in a 30 ml syringe and infused via an automatic pump. The nuclear medical technician present during the infusion reported seeing a small amount of blood, but other than that, nothing unusual was noted. However, upon completion of the infusion, meter readings noted high activities on the patient's clothing and bed linen. The possible reason given being a faulty connection line on the automatic pump. The contamination is believed to have also been present on the skin all weekend. Due to the large dose of I-131 infused, the licensee's staff were not able to see the contamination on the patient's skin until he developed erythema. The licensee is in the process of doing a dose reconstruction for the skin contamination. Based on the reading from the patient and estimated activity in the various contaminated items, the licensee currently estimates that approximately 50% of the intended dosage was successfully infused. The authorized user has been informed and is currently notifying the patient's parents and the referring physician. "A reactive inspection is planned by the Department. More information will be provided upon receipt." PA Event Report ID No: PA 180012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM JOHN CHIPPO TO DONALD NORWOOD AT 1451 EDT ON 7/12/2018 * * * "The University of Pennsylvania (U Penn) reported that a patient's skin became contaminated during medical treatment on 5/25/2018. The 17-year-old pediatric patient was scheduled to receive 30.86 GBq (834 mCi) of I-131 metaiodobenzylguanidine (MIBG) for treatment of brain cancer. The dosage was delivered in a 30 ml syringe and infused via an automatic pump. The nuclear medicine technician present during the infusion saw a small amount of blood, but nothing unusual other than that was noted. However, upon completion of the infusion, radiation surveys revealed high activities of I-131 on the patient's clothing and bed linen. "U Penn stated that the patient's upper right thigh was cleaned. On 5/27/2018, the patient reported discomfort and reddening (i.e. erythema) on the skin of his upper right thigh, which developed into a lesion and further into desquamation (grade 3) the next day. Radioactive contamination is believed to have been present on the patient's skin for 24 to 48 hours. "Based on U Penn measurements, nuclear medicine imaging, and the patient's clinical symptoms, the dose to the skin was estimated to be between 50,000 and 120,000 cGy (rad) to a 15 cm2 area. Radiation safety staff consulted with U.S. DOE's REAC/TS in Oak Ridge TN, to verify dose calculations. Calculations of the activity in the waste and the exposure rate from the patient in previous treatments estimated the activity delivered at 15.54 GBq (420 mCi). It was calculated that approximately 7.77 GBq (210 mCi) went to the waste. "The cause of the incident is believed to be a faulty connection line on the automatic pump. The patient was also disconnected from the infusion pump at the 'Spiros tube' to use the lavatory part way through the procedure. Due to the large dosage of I-131 infused, U Penn staff were unable to detect the contamination on the patient's skin until he developed erythema. "The authorized user was informed and notified the patient's parents and referring physician. Pennsylvania DEP, Bureau of Radiation Protection, performed a reactive inspection on 6/7 and 6/13/2018. U Penn is conducting a full root cause analysis to develop and implement corrective actions. Procedures that have already been implemented for I-131 MIBG patients included placing absorbent chucks between all parts of the infusion line and the patient's body and requiring an authorized user to be contacted for approval if it is necessary to disconnect a patient during the infusion. "Root Cause(s): possible equipment failure, training, and/or human error in connecting the line to the infusion pump. "Actions: A reactive inspection has been completed by the Department. More information will be provided upon receipt from U Penn." Notified R1DO (Bower), NMSS Events Notification E-mail Group, and INES Coordinator (Milligan). * * * UPDATE FROM JOHN CHIPPO TO HOWIE CROUCH AT 1102 EDT ON 8/7/18 * * * The following update was received from the Commonwealth via fax: "Licensee has provided additional information; Corrective Actions include: "A complete evaluation is being performed of the infusion system used for this treatment to identify any deficiencies, including comparison of CT imaging of the Spiros connection used in this treatment and an unused one. "A multidisciplinary I-131 MIBG team with representatives from Nuclear Medicine, Radiation Safety, Nursing and Oncology has been established. The team will meet regularly to review and update policies and procedures for I-131 MIBG therapies. Some immediate steps have included: (1) use of absorbent material under the administration line over the patient's body, (2) a change to the administration procedure to require that the infusion not be stopped unless medically necessary and determined by the Authorized User, (3) planned implementation of continuous patient observation during administration including evaluation of the use of portable video monitoring, (4) a new procedure has been implemented to address patient fluid management prior to and during infusion, (5) a review of the infusion system has commenced with focus on the Spiros connector, including additional training on their use. "Patient specific decontamination procedures have been developed for each treatment treated since the incident. Since decontamination procedures must take into account the patient's age and medical condition, it has been necessary that the medical staff have major input into the procedures for these patients. The knowledge gained from the patient-specific decontamination procedures will be used to refine the decontamination SOP. "For therapeutic doses in which an activity on the skin that would result in desquamation can be two thousandths of a percent of the dose. It is important to be able to make measurements in these difficult environments. Testing has begun to determine the capabilities of systems that might be used to measure betas in environments in which gammas are several orders of magnitude more abundant than betas. "Radiation Safety incident response procedures have been revised to include a time out and immediate involvement of additional Health Physics staff during incidents, including during possible Medical Events. The procedure is aimed at refocusing the attention of Health Physicists on all aspects of the incident response, and to prevent the Medical Event reporting requirements from distracting attention from other aspects of the response. "CAUSE OF THE EVENT: a) A leak in the system caused by a failure of the Spiros connection in the infusion line. b) Policies and procedures relating to I-131 MIBG dose administration lacked coordination and oversight. SOPs have been managed separately by each Department (Nursing, Nuclear Medicine, Oncology, and EHRS). c) Policies and procedures relating to patient contamination and decontamination during dose administration were incomplete. "ACTIONS: A reactive inspection has been completed by the Department." Notified R1DO (Cahill), NMSS Events Notification (email), and INES Coordinator (Milligan). * * * UPDATE FROM JOHN CHIPPO TO OSSY FONT AT 0833 EDT ON 10/12/2018 * * * The following was received from the Commonwealth of Pennsylvania via email: "UPDATE 3, clarifications: "The written directive prescribed 30.23 GBq (817 mCi) of I-131. The dosage administered measured 30.86 GBq (834 mCi) and was delivered over the course of 90 minutes. "The estimated activity delivered to the correct treatment site was determined to be 22.68 GBq (613 mCi), not 15.54 GBq (420 mCi) as previously reported. "No decontamination of the patient (right upper thigh) was performed at the time the contamination of bed linens and pants was discovered. This wasn't completed until signs of erythema were present." PA Event Report ID No: PA 180012 NRC Item# 180252 Notified R1DO (Dentel), and NMSS Events Notification and INES Coordinator (Milligan) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-06-06
53429 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-05-27 06:30 | 2018-05-27 12:42 | 2018-05-27 | REACTOR WATER CLEANUP SYSTEM DECLARED INOPERABLE "On May 27, 2018 at 0630 EDT, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow - High function was declared inoperable as a result of indicating downscale. This condition would have prevented the primary containment isolation valves for the RWCU system from automatically isolating on a high differential flow instrumentation signal. "At 0753, RWCU was shutdown and the affected penetration flow paths were isolated in accordance with station procedures per Fermi Technical Specifications. "The cause of the event is under investigation. "There was no radiological release associated with this event. All other RWCU primary containment isolation instrumentation functions remained operable and the associated RWCU system primary containment isolation valves were capable of being remotely closed by the control room operators throughout the event. However, the condition is reportable pursuant to 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-05-27
53428 | 0 | MILLSTONE |  | 2 | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2018-05-26 22:01 | 2018-05-27 00:40 | 2018-05-27 | OFFSITE NOTIFICATION DUE TO SPURIOUS SIREN ACTUATION County and state governments were notified due to the spurious actuation of a single emergency notification siren located in New London County in the Town of Lyme. The siren was silenced. If required, alternate notification of the public in the area will be through local Emergency Operations Center route alerting. The NRC Resident Inspector has been notified. | 0 | 100 | 100 |  | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-05-27
53427 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2018-05-23 | 2018-05-25 18:04 | 2018-05-31 | AGREEMENT STATE REPORT - FOUND SOURCE The following information was received via E-mail: "On May 23, 2018, a scrap yard identified a radioactive source in an outgoing load of waste intended for a landfill. The radioactive source is one inch long and approximately one-half inch in diameter. The Wisconsin Department of Health Services responded to the scrap yard on May 25, 2018, and measured a maximum exposure rate of 210 mR/hr on contact with the source. The source was confirmed to not be leaking. There are no markings or numbers on the source, and isotope identification is pending. It is not known how long the scrap yard was in possession of the source. The source is now in secured storage at the scrap yard. Additional updates will be provided as information about the source and possible original device become available." Wisconsin Event Report ID No.: WI180008 * * * UPDATE FROM KRISTA KUHLMAN TO DONALD NORWOOD AT 1524 EDT ON 5/31/2018 * * * The following information was received via E-mail: "On May 31, 2018, the department performed additional characterization of the source at the scrap yard with assistance from the EPA. It has been determined that it is a Ba-133 source, with an activity between 350 - 500 microCuries. The department has not been able to determine the origin of the source. It will continue to work with the scrap yard to determine the proper disposal path." Notified R3DO (Cameron) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2018-06-04
53426 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-05-23 07:30 | 2018-05-23 18:32 | 2018-05-23 | FITNESS FOR DUTY "On May 23, 2018 Callaway determined that a violation of one provision of the site's Fitness for Duty (FFD) policy occurred. FFD pre-access testing confirmed a test failure for alcohol. The violation was committed by a non-licensed supervisory employee. The individual did not hold unescorted access to the plant but did perform behavioral observation program (BOP) duties. The BOP qualification has been removed. "The NRC Resident Inspector has been notified by the licensee." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 26.719 |  |  |  | 0 | 2018-05-23
53425 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2018-05-23 | 2018-05-23 15:10 | 2018-05-23 | AGREEMENT STATE REPORT - SHUTTER FOR FIXED GAUGE WOULD NOT OPEN The following report was received from the State of Virginia via email: "On May 23, 2018, the Radiation Safety Officer of the licensee reported to the Agency [Virginia Office of Radiological Health] that an on-site technician noted that the computer system had issued a 'Wheel Stuck' alarm, and found that the shutter of the fixed gauge could not open when ordered to do so due to a broken part in the shutter positioning mechanism. This was discovered on May 19, 2018. "The gauge is a Valmet Automation Model BWM-T, serial number 18500173, with two 400 milliCurie Krypton-85 sources (IUT Model KR85.1, capsule ID number X9093). The device was repaired by HOOSIER Technical Services, and is currently working correctly. "More information has been requested by the Agency regarding the root cause of the problem. This report will be updated when any additional information is received." Virginia Event Report ID No.: VA-18-002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2018-05-31
53424 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2018-05-23 11:28 | 2018-05-23 17:37 | 2018-05-23 | AUTOMATIC REACTOR TRIP ON LOW DEPARTURE FROM NUCLEATE BOILING RATIO "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On May 23, 2018, at approximately 1128 Mountain Standard Time (MST), the Palo Verde Nuclear Generating Station (PVNGS) Unit 2 control room received reactor protection system alarms for low departure from nucleate boiling ratio and an automatic reactor trip occurred. Prior to the reactor trip, Unit 2 was operating normally at 100 percent power. Plant operators entered the reactor trip procedures and diagnosed an uncomplicated reactor trip. All CEAs [control element assemblies] fully inserted into the core. No emergency classification was required per the PVNGS Emergency Plan. "The Unit 2 safety-related electrical buses remained energized from normal offsite power during the event. There was no impact to the required circuits between the offsite transmission network and the onsite Class 1E Electrical Power Distribution System; the offsite power grid is stable. "No major equipment was inoperable prior to the event that contributed to the event or complicated operator response. Unit 2 is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. The cause of the reactor trip is under investigation. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 2 reactor trip." Decay is being removed via steam dumps to condenser. Units 1 and 3 at Palo Verde were unaffected by the transient and continue to operate at 100 percent power. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-05-23
53423 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-05-23 08:48 | 2018-05-23 16:10 | 2018-05-23 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At time 0848 (CDT), Main Steamline Radiation Monitor 2-RE-2328 (Main Steamline 2-04) lost communications and was declared non-functional. "With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 2-04 could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant [CPNPP] has assurance of steam generator integrity and fuel cladding integrity and there is a negligible safety significance to the current condition from a public health and safety perspective. "Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 radiation monitor serves as a backup with alarm function and Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL 2-04. "Corrective actions are being pursued to restore 2-RE-2328 to a functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-05-23
53422 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2018-05-23 | 2018-05-23 14:19 | 2018-05-23 | PART 21 - WEAR OF THERMAL SLEEVE IN WESTINGHOUSE CONTROL ROD DRIVE MECHANISMS The following notification is an excerpt from the received report: "Westinghouse nuclear steam supply system (NSSS) plants that have thermal sleeves in the control rod drive mechanism (CRDM) penetration tubes, wear of the thermal sleeve flange against the tube could have safety consequences that were not previously considered. Recent operating experience, during startup procedures at an Electricite de France (EdF) plant, has shown the possibility for the flange remnant from a thermal sleeve to interfere with control rod movement." Potential affected plants include, A. W. Vogtle 1 & 2, Braidwood 1 & 2, Byron 1 & 2, Callaway, Catawba 1 & 2, Comanche Peak 1 & 2, Diablo Canyon 1 & 2, McGuire 1 & 2, Millstone 3, Seabrook, Sequoyah 1 & 2, Shearon Harris, South Texas 1 & 2, Watts Bar 1 & 2, Wolf Creek, Beaver Valley 1 & 2, D.C. Cook 1 & 2, Indian Point 2 & 3, North Anna 1 & 2, Point Beach 1 & 2, Prairie Island 1 & 2, R. E. Ginna, Salem 1 & 2, Surry 1 & 2, and Turkey Point 3 & 4. Name and address of the individual or individuals informing the Commission. James A. Gresham Westinghouse Electric Company 1000 Westinghouse Drive, Suite 259 Cranberry Township, Pennsylvania 16066 Direct tel: (412) 374-4643 Direct fax: (724) 940-8560 e-mail: greshaja@westinghouse.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-05-23
53421 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-05-10 | 2018-05-23 11:25 | 2018-05-23 | AGREEMENT STATE REPORT - PATIENT CARE NURSE EXPOSED TO I-131 FOLLOWING PATIENT URINATION The following report was received from the State of Florida via email: "The [Bayfront HMA Medical Center] RN [Registered Nurse] called FDOH/BRC/ERCM [Florida Department of Health, Bureau of Radiation Control, Environmental Radiation Control Materials] (Tallahassee - Licensing & Enforcement), to report that she was exposed to I-131 following patient urination during that patient's care. [The RN] was informed that she received a POSITIVE bioassay subsequent to the exposure event. Her shoes were impounded for decay. Other employee bioassays conducted were NEGATIVE. [The RN] reported that she DID NOT conduct urine clean-up during the patient care. The RSO [Radiation Safety Officer], was called, and a VM [Voice Mail] was left requesting a return call. [A State of Florida Bureau of Radiation Control Inspector] was called and directed to conduct an investigation." FL Incident Number: FL18-065 * * * UPDATE ON 05/23/2018 AT 13:57 EDT FROM PAUL NORMAN TO THOMAS KENDZIA * * * "Incident occurred May 10 following Thyroid Ablation (150mCi I-131); RN bioassay performed following week; results slightly greater than background. Bioassay & dosimetry results to be forwarded." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-05-31
53420 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-05-23 | 2018-05-23 10:52 | 2018-05-23 | AGREEMENT STATE REPORT - THREE FIXED GAUGES WITH STUCK SHUTTERS The following information was received from the State of Louisiana via email: "On Friday May 23, 2018 Georgia-Pacific was notified by a third party inspection company performing fixed gauge inspections that three fixed gauges were found with stuck shutters. "The three gauges were: 1.) Ohmart, Model Number HM-8, S/N: 6563, 100 mCi Cs-137 2.) Ronan, Model Number SA8-C10, S/N: 9775GG, 50 mCi Cs-137 3.) Berthold, Model Number P2608.11, S/N: 773/2-03-11, 1.297 mCi Co-60 "Georgia-Pacific is planning to replace the gauge holders and sources." Louisiana Event Report ID No.: LA-20180009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-05-31
53419 | -1 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2018-05-22 12:56 | 2018-05-22 18:38 | 2018-06-21 | GAS VOIDS DISCOVERED IN BOTH TRAINS OF LOW HEAD SAFETY INJECTION "On 5/22/2018, while operating at approximately 100 percent power, Ultrasonic Testing of the Beaver Valley Power Station (BVPS) Unit 1 Low Head Safety Injection (LHSI) pump suction piping identified gas voids in excess of the acceptable limit for void volume. Both trains of LHSI were declared inoperable. Technical Specification (TS) 3.5.2 for both trains of the LHSI system was entered along with TS 3.0.3 which requires the initiation of a plant shutdown. Time of TS entry was 12:56 (EDT). "Plant shutdown was commenced at 15:56 (EDT) in accordance with plant procedures. "At 15:59 (EDT) Train 'A' LHSI was restored to operable status, TS 3.0.3 Action was exited and the power reduction was stopped at approximately 99 percent. "At 17:43 (EDT) Train 'B' LHSI was restored to operable status, TS 3.5.2 Actions were exited. "This is reportable per 10 CFR 50.72(b)(3)(ii) Unanalyzed Condition, 10 CFR 50.72(b)(3)(v) Event or Condition that Could Have Prevented the Fulfillment of a Safety Function and 10 CFR 50. 72(b )(2)(i) TS Required Shutdown. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 6/21/18 AT 1535 EDT FROM SHAWN KEENER TO RICHARD SMITH * * * "Further engineering evaluation has determined that the gas voids that existed at the time of discovery would not have rendered the LHSI [Low Head Safety Injection] system inoperable if it were required to actuate. The engineering evaluation concluded that filling of the containment sump during a Design Basis Accident would result in a void volume reduction such that the void in the LHSI suction piping would not be large enough to significantly impact the operability of the system. Therefore, the system remained operable but degraded. No TSs [Technical Specifications] were required to be entered and no shutdown was required. As such, all three reporting criteria do not apply and are being retracted. "The NRC Resident Inspector has been notified." Notified R1DO (Burritt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2018-05-22
53418 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2018-05-22 10:28 | 2018-05-22 15:36 | 2018-05-22 | FITNESS FOR DUTY - LICENSED OPERATOR CONFIRMED POSITIVE TEST "A licensed operator had a confirmed positive test during a random fitness-for-duty test. The individual was not performing licensed duties. The individual's qualifications and plant access were removed. A work performance investigation has been completed. Work performed by the individual has been verified to be compliant with all standards. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2018-05-22
53417 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-05-21 | 2018-05-22 16:45 | 2018-05-22 | AGREEMENT STATE REPORT - POTENTIAL INDIVIDUAL OVEREXPOSURE Received the following notification from Florida Bureau of Radiation Control. "Sun Nuclear Corporation's RSO, contacted Florida Bureau of Radiation Control to report a WB (Luxel) badge report received from Landauer [global dosimetry solutions] indicating an exposure to a Sun Nuclear employee of 6.6 REM. The RSO believes Landauer mixed-up the badges and incorrectly reported the exposure on an individual's exposure record. A different employee's badge had been left in the calibration room overnight. That badge exposure reading was recorded at a normal exposure level. The RSO contacted Landauer about the situation: Landauer is conducting an internal review. The RSO is currently conducting an internal review and investigation at Sun Nuclear. Florida Bureau of Radiation Control Environmental Manager, has been notified, and will assign an inspector to investigate." Florida report # FL-18-064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-05-30
53416 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-05-22 09:00 | 2018-05-22 13:36 | 2018-05-22 | UNPLANNED PUBLIC NOTIFICATION DURING A DRILL "On 05/22/2018, Cooper Nuclear Station (CNS) was conducting an Emergency Response Organization (ERO) drill which included state and local involvement. At approximately 09:00 CST Nebraska Emergency Management Agency (NEMA) inadvertently broadcasted CNS' declaration of a Notice of Unusual Event for the drill over the public scanner. This resulted in various members of the public or news media inquiring about the perceived event or posting erroneous information via Twitter, television news outlets, newspapers, and radio stations. These news outlets have been informed that CNS was conducting a drill and do not intend to release any stories regarding this event. There is no evidence of a formal news release at this time. However, due to the uncontrolled source of the information, the determination was made to make this report. "This unplanned media event is a 4 hour report, in accordance with 10CFR50.72(b)(2)(xi). This event is not significant with respect to the health and safety of the public. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-05-22
53415 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-05-21 | 2018-05-21 21:49 | 2018-06-08 | AGREEMENT STATE REPORT - POSSIBLE PLUTONIUM SPHERE FOUND Received the following by email from Florida Bureau of Radiation Control. "[A] resident at Waterford [Senior Living Center], recently passed away. His son contacted a licensed Firearms Dealer and Estate Appraiser, to assess his father's estate value. [The appraiser] discovered a metal canister containing a grayish-silver marble-sized sphere. A certificate in the [deceased's] personal effects states that the sphere is Pu, and is a gift given in appreciation of the [deceased's] contributions to The Manhattan Project. Also included in the [deceased] personal effects is a piece of glass said to be from Atomic Bomb Testing. The Certificate is signed by Robert Oppenheimer. [The Estate Appraiser], contacted the ATF. The ATF Special Agent contacted the Bureau of Radiation Control (BRC) Duty Officer. A preliminary investigation is scheduled for Tuesday, May 22, 2018." Florida report # FL18-062. * * * UPDATE ON 05/22/2018 AT 13:32 EDT FROM PAUL NORMAN TO THOMAS KENDZIA * * * "Phone conversation with appraiser and son revealed the following: "Deceased passed away years ago, and his wife, who has had her spouse's possessions since then, is moving from the Senior Center. Their son was given the name of an Estate Liquidator, to assess their belongings. The appraiser came across a metal shoe shine sized canister containing what he described as marble sized pellets and sandy glass, that had Plutonium marked on it. There also was a framed Reference letter addressed to the deceased from Robert Oppenheimer, thanking him for his contributions to The Manhattan Project. Unbeknownst to the son, the appraiser then contacted the Bureau of Alcohol, Tobacco, Firearms and Explosives (ATF) with his concerns. "The son stated that the material in the canister was fused sand from the Trinity test site, and did not know why the appraiser was concerned about it." Florida report # FL18-062. Notified R1DO (Dimitriadis), IRD MOC (Pham), and NMSS Events Notification (email). * * * UPDATE ON 06/08/2018 AT 09:17 EDT FROM TIM DUNN TO OSSY FONT * * * "[Florida Bureau of Radiation Control] would like to update [NMED] item #180240, regarding the Manhattan Project memorabilia thought to be Plutonium: "Lab Results 34.76 grams (spherical shape) 0.623 inches (15.82 mm) diameter Calculated density 16.75 g per cm3 (Uranium is 19.1), so this is some type of alloy. "Analysis of spectra by DOE indicates natural uranium." Florida report # FL18-062. Notified R1DO (Jackson), IRD MOC (Grant), and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-05-29
53414 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-05-20 | 2018-05-21 15:33 | 2018-05-21 | AGREEMENT STATE REPORT - STOLEN MOISTURE-DENSITY GAUGE The following was received from the State of Ohio via email. "The Ohio Department of Transportation (ODOT) reported a Troxler Model 3440 gauge was stolen from a locked storage trailer near a road construction site in Londonderry, OH. The theft occurred during the weekend and was discovered on Monday, 5/21/2018. ODOT reported the theft to the Ohio State Highway Patrol and local law enforcement. "An Ohio inspector will investigate the site on 5/22/18. "Device Name: PORTABLE GAUGE Manufacturer: TROXLER Model Number: 3440 Serial Number: 23963 "Source Number: 1 Source/Radioactive Material: SEALED SOURCE GAUGE Radionuclide: Cs-137 Activity: 0.009 Ci (9 mCi or 333 MBq) IAEA Category: 5 "Source Number: 2 Source/Radioactive Material: SEALED SOURCE GAUGE Radionuclide: Am-241 Activity: 0.044 Ci (44 mCi or 1.628 GBq) IAEA Category: 4" OHIO Item #: OH180003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-05-29
53413 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-05-21 | 2018-05-21 10:41 | 2018-05-21 | OFFSITE NOTIFICATION REGARDING MALFUNCTION OF EMERGENCY NOTIFICATION SIREN "On May 21, 2018, at approximately 0840 Eastern Daylight Time (EDT), Duke Energy confirmed that one emergency notification siren (i.e., B13) located in Brunswick County was malfunctioning. The siren was making an abnormal sound, alternating between low and high pitch. The siren was deactivated upon confirmation of the siren malfunction. There are a total of 38 sirens located in Brunswick and New Hanover Counties. No other sirens were affected. "Duke Energy notified the State of North Carolina, Brunswick County, New Hanover County and Coast Guard of the issue. "There was no impact on the health and safety of the public or plant personnel. The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-05-21
53412 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-05-18 | 2018-05-18 18:12 | 2018-05-18 | AGREEMENT STATE - UNATTENDED RADIOGRAPHY CAMERA The following was received from the State of California via email: "On 05/18/18, RSO [radiation safety officer] contacted RHB [Radiologic Health Branch] to report an incident where one of their radiographic exposure devices was left unattended at a job site inside a refinery. Licensee reported that due to a miscommunication, around 6:00 am [PDT] on 05/18/18 a camera was left unattended in an uncontrolled unit within the Chevron Refinery, in Richmond, CA, for several hours before it was discovered and placed it under licensee's control. The camera involved is a Model Ir-100, S/N 4850, Source S/N 223D containing 86 Ci of Ir-192. RHB will be following up on this investigation. (Note: Currently, Qualspec, LLC is in the process of merging with another licensee, TEAM Industrial Services)" California ID # 051818 THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-05-28
53411 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-05-18 | 2018-05-18 16:08 | 2018-05-18 | AGREEMENT STATE - POTENTIAL UNPLANNED CONTAMINATION The following was received from the State of Texas via email: "On May 11, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that an event had occurred. The licensee stated that a patient had been treated with I-131 for thyroid cancer on May 4, 2018. The patient was instructed on the procedure, restrictions, and their responsibility after the treatment. The patient signed a document stating they understood the instructions. The patient was scheduled to return on May 11, 2018, for a whole body scan. The patient was discharged after the radionuclide was administered. "On May 11, 2018, the patient failed to show up for his 1000 hours appointment. At 1100 hours, the nurse (nurse one) working the scanner area received a phone call from a floor nurse. The floor nurse asked if they had an appointment for the patient in this event. Nurse one stated they did, but he failed to show up for the appointment. The floor nurse stated that the individual was in their treatment area. Nurse one asked how long he had been there and the floor nurse stated he had been brought to them 4 days prior with an injury from a fall. Nurse one asked why radiology had not been informed and the floor nurse stated they were not aware of his previous procedure. "The licensee surveyed the patient and found they were reading above background. The licensee determined areas of the hospital outside the patient's room the patient would have been in and surveyed them. No contamination was found. The licensee removed all material from the patient's room and moved it to its decay room for storage. Access to the patient's room was restricted until it decays to levels not distinguishable from background. The licensee established controls to prevent any further contamination resulting from the patient. The patient was discharged from the hospital to the rehab facility on May 14, 2018. "The Agency was not aware that access was restricted to the patient's room until the written report was reviewed on May 18, 2018. Additional information will be provided as it is received in accordance SA-300." Texas Incident #: I-9575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-28
53410 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2018-05-18 06:51 | 2018-05-18 13:27 | 2018-05-18 | AUTOMATIC REACTOR SCRAM CAUSED BY MAIN TRANSFORMER TRIP "At 0651 [PDT] on May 18th, 2018, Columbia Generating station experienced a Main Transformer trip, that caused a Reactor Scram. Reactor Power, Pressure and Level were maintained as expected for this condition. MS-RV-1A (Safety Relief Valve) and MS-RV-1B (Safety Relief Valve) opened on reactor high pressure during the initial transient. MS-RV-1B appeared to remain open after pressure lowered below the reset point. The operating crew removed power supply fuses for MS-RV-1B and it currently indicates intermediate position. SRV (Safety Relief Valve) tail pipe temperatures indicate all valves are closed. Suppression pool level and temperature have remained steady within normal operating levels. "All control rods inserted and reactor power is being maintained subcritical. "RPV (Reactor Pressure Vessel) water level is being maintained with condensate and feed system with startup flow control valves in automatic. Reactor Pressure is being maintained with the Turbine Bypass valves controlling in automatic. The main condenser is the heat sink. "No ECCS (Emergency Core Cooling Systems) systems actuated or injected; the EOC-RPT (End of Cycle-Recirculation Pump Trip) and RPS (Reactor Protection System) systems actuated causing a trip of the RRC pumps and a reactor scram. "Core recirculation is being maintained with RRC-P-1A (Reactor Recirculation Pump) running. "No release has occurred. "At this time there will be no notifications to state, local or other public agencies. "The NRC Senior Resident has been notified. "The cause of the event is currently under investigation. Plant conditions are stable." The plant is in its normal electrical alignment and offsite power is available to the site. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-05-18
53409 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2018-05-17 15:03 | 2018-05-17 23:02 | 2018-05-17 | EMERGENCY DIESEL GENERATORS INOPERABLE "On May 17, 2018, with the Unit in Mode 4, Clinton Power Station experienced the concurrent inoperability of two Emergency Diesel Generators (DG). This event is being reported as an 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(v) as, 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "On May 17, 2018, at 15:03 CDT, it was identified that the Division 2 DG air start receiver isolation valves 1DG160 and 1DG161 were shut. With these valves shut, the Division 2 DG is inoperable. At the time, Division 1 DG was also inoperable for a 4160V 1A1 partial bus outage. The Technical Specification (TS) Actions for TS 3.8.2, AC Sources Shutdown, and TS 3.5.2, RPV Water Inventory Control, were entered as a result of the inoperability of the onsite AC power sources to isolation valves being credited to limit RPV DRAIN TIME. "Division 2 DG air receivers were realigned at 15:45 CDT and the Division 2 DG auto start function was restored. Offsite power was available throughout this event and there was no impact to the health and safety of the public or plant personnel. "Investigation is ongoing. It has been determined that the air start receiver isolation valves remained closed following system restoration on May 11, 2018. However, the Division 2 DG was not required to be Operable by TS until 00:45 CDT on May 14, 2018 when the Division 1 DG was made inoperable as a result of scheduled plant maintenance. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-05-17
53408 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-05-17 11:15 | 2018-05-17 17:33 | 2018-05-17 | AUTOMATIC ACTUATION OF EMERGENCY DIESEL GENERATOR "At 1115 (CDT) on May 17, 2018 with Unit 2 in Mode 1 at 100% power, the station experienced an auto-start of Emergency Diesel Generator, D5. Preliminary information indicates that the Bus 25 Potential Transformer (PT) fuse drawer was inadvertently opened, causing Breaker 25-16 to open and de-energize bus 25. Operators were able to manually close the D5 EDG output breaker to re-energize bus 25. 22 Component Cooling (CC) Pump auto-started on the loss of 21 CC Pump due to low pressure in the CC system as designed. All equipment functioned as designed. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the EDG. "There was no impact on the health and safety of the public or plant personnel. "The NRC Senior Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-05-17
53407 | 0 | ENVIRONMENTAL TESTING & CONSULTING |  |  |  |  | 2018-05-02 12:00 | 2018-05-17 15:29 | 2018-05-17 | LOST OR STOLEN LEAD PAINT ANALYZER Environmental Testing and Consulting (ETC) is reporting a lost/stolen lead paint analyzer. The device was last seen approximately two weeks ago by the user in the trunk of his/her car. The lost device was having software issues and a backup device was used in its place. ETC has 14 other similar devices that have all been accounted for. No tampering or evidence of theft was observed by the licensee. ETC notified the Michigan Department of Environmental Quality and the manufacturer (Heuresis) of the device regarding the event. Activity: Co-57 sealed source, 5mCi (185 MBq) Serial Number: 1166 Device: Heuresis Pb200i Lead Paint Analyzer THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-05-25
53406 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-05-17 10:45 | 2018-05-17 14:26 | 2018-05-17 | EMERGENCY NOTIFICATION SIREN MALFUNCTIONING "On May 17, 2018, at approximately 1045 Eastern Daylight Time (EDT), Duke Energy confirmed that one emergency notification siren (i.e., B03) located in Brunswick County was malfunctioning. The siren was making an abnormal sound, alternating between low and high pitch. At approximately 1103 EDT, the siren was deactivated. There are a total of 38 sirens located in Brunswick and New Hanover Counties. No other siren was affected. "Duke Energy notified the State of North Carolina, Brunswick County, and New Hanover County of the issue. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-05-17
53405 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-05-16 22:02 | 2018-05-16 23:29 | 2018-05-17 | OFFSITE NOTIFICATION OF FIRES IN THE OWNER CONTROLLED AREA "On May 16, 2018 at approximately 1425 CDT, two grass fires started in the Owner Controlled Area surrounding South Texas Project (STP) Nuclear Generating Station. The Bay City Volunteer Fire Department was called to the site to fight the fire. Reinforcements from Tres Palacios Oaks, Midfield and Markham Fire Departments were called in to assist with firefighting efforts. The grass fires were extinguished on May 16, 2018 at 2046 CDT. The fires occurred outside the protected area of the plant and presented no danger to the public or the safe operation of the units. "On May 16, 2018 at 2202 CDT, STP Nuclear Generating Station issued a press release to inform area residents." The licensee notified the NRC Resident Inspector. * * * UPDATE ON MAY 17, 2018 AT 13:33 EDT FROM BILLY HERZOG TO THOMAS KENDZIA * * * "On May 17, 2018, at 11:10 CDT STP Nuclear Generating Station notified the Texas Commission on Environmental Quality (TCEQ) of the grass fires, resulting in visible emissions, that occurred in the Owner Controlled Area of the STP Nuclear Generating Station on May 16, 2018, between the times of 14:25 and 20:46 CDT. "No further press releases are planned." The licensee notified the NRC Resident Inspector. Notified R4DO (Gepford). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-05-16
53404 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2018-05-16 17:50 | 2018-05-16 22:19 | 2018-05-16 | AUTOMATIC REACTOR TRIP DUE TO LOSS OF MAIN FEEDWATER PUMP "At 1750 CDT, the Arkansas Nuclear One, Unit 1 (ANO-1) reactor tripped due to the trip of the 'B' Main Feedwater Pump. Unit 1 was at 10 percent power with escalation of power in progress with one Main Feedwater Pump in service. Investigation is in progress as to the cause of the Main Feedwater Pump trip. The Main Feedwater Pump trip resulted in RPS [reactor protection system] actuation on loss of both Main Feedwater Pumps and resulted in Emergency Feedwater (EFW) actuation. All Control Rods inserted into the core properly and the reactor was verified shutdown. "EFW experienced a half-trip on the 'A' train of Emergency Feedwater Initiation and Control (EFIC) at time of system actuation, but was successfully actuated manually immediately upon discovery. Train 'B' EFIC actuated in Automatic as designed. The half-trip of the 'A' train of EFIC is currently believed to be associated with EFIC Channel 'C'; however, investigation is underway to verify this. "Currently, ANO-1 has been stabilized and is being maintained in Mode 3 with Auxiliary Feedwater in service. Heat removal is via Turbine Bypass valves to the Condenser. "No radiological releases have occurred due to this event." There was no effect on Arkansas Nuclear One, Unit 2. The licensee notified the NRC Resident Inspector and the State of Arkansas. | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-05-16
53403 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-05-16 11:33 | 2018-05-16 16:51 | 2018-05-16 | FITNESS-FOR-DUTY TEST POSITIVE FOR NON-LICENSED SUPERVISOR At 1133 EDT on May 16, 2018, Southern Nuclear Operating Company determined a non-licensed contractor supervisor had a confirmed positive for a controlled substance during a random Fitness-for-Duty test. The employee's unescorted access to the plant has been suspended. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-05-16
53402 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-05-15 | 2018-05-15 17:28 | 2018-05-15 | NEBRASKA AGREEMENT STATE REPORT - TWO MISSING TRITIUM EXIT SIGNS The following information was obtained from the State of Nebraska via email: "GL0370 Church of Jesus Christ of Latter Day Saints - Norfolk submitted their Annual Renewal and Inventory on March 9, 2018. On May 15, 2018, GL0370 re-submitted their Inventory, indicating that two tritium exit signs were missing. A follow-up phone call placed to the licensee indicated the licensee did not actually conduct an inventory of the devices prior to the March 9th documentation. They have searched through all back records and can find no indication of when the devices were removed. "Source number 1 information: Device name: Sealed Source Luminous Manufacturer: Isolite Model Number: SLX60 Serial Number: 10-7234 Radionuclide: H-3 Activity: 10 Ci "Source number 2 information: Device name: Sealed Source Luminous Manufacturer: Isolite Model Number: SLX60 Serial Number: 10-17588 Radionuclide: H-3 Activity: 10 Ci" Nebraska Item Number: NE180004 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.p | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-05-23
53401 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2018-05-14 13:05 | 2018-05-14 13:17 | 2018-05-14 | SALTWATER SYSTEM NON-CONFORMING WITH LICENSING BASIS FOR TORNADO GENERATED MISSILES "On May 14, 2018, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of a tornado generated missile, Calvert Cliffs identified a non-conforming condition in the plant design such that specific TS equipment is considered to not be adequately protected from a tornado generated missile. A tornado could generate a missile that could strike the Unit 1 Saltwater system header and associated piping. This could result in damage to the unit 1 Saltwater system header which could affect the ability of the Unit 1 Saltwater subsystems to perform their design function if such a tornado would occur. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with NRC enforcement guidance provided in EGM 15-002 and DSS-ISG-2016-01. Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been informed of this notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-05-14
53400 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-05-12 | 2018-05-14 12:39 | 2018-05-14 | TEXAS AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following information was obtained from the State of Texas via email: "On May 14, 2018, the licensee notified the Agency [Texas Department of State Health Services] that on the morning of May 12, 2018, one of its Troxler model 3430+ moisture/density gauges (SN: 69854), containing a 40 milliCurie americium-241 source (SN: 47-19592) and an 8 milliCurie cesium-137 source (SN: 77-13965), had been stolen from a licensee's vehicle while it was parked at a restaurant in Houston, Texas. The gauge was locked inside its transport case which was secured with chains in the back of the licensee's vehicle. The technician had stopped to eat breakfast between picking up the gauge at the licensed site and reporting to the temporary job site. When he arrived at the job site, he found the chains cut, the gauge and standard plate had been stolen, but the transport case was still there. The technician reported the theft to his supervisors who did not report to the licensee's radiation safety officer until May 14th. The theft has been reported to local law enforcement. An investigation into this event is ongoing." Texas Incident Number: 9571 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-22
53399 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-05-11 23:27 | 2018-05-12 06:58 | 2018-05-12 | INADVERTENT ACTUATION OF THE EMERGENCY DIESEL GENERATOR "On 5/11/2018, at 2327 hours CDT, with the plant in Mode 5, Grand Gulf Nuclear Station was making preparations for surveillance test 06-OP-1P75-R-0003, Standby Diesel Generator 1 Functional Test. The Grand Gulf Nuclear Station experienced an auto-start of the Division 1 [Emergency] Diesel Generator [EDG] when the 15AA Bus Potential Transformer (PT) fuse drawer was racked out instead of the line PT fuse drawer for Bus 15AA feeder breaker 152-1514. This resulted in the 15AA Incoming Feeder Breaker 152-1511 from Engineered Safety Features Transformer 12 opening, de-energizing the 15AA Bus. The Division 1 EDG started and energized Bus 15AA. The Division 1 LSS SYSTEM FAIL annunciator was received and Standby Service Water A failed to start due to the 15AA Bus PT fuse drawer being racked out. Standby Gas Treatment Train B was manually initiated per the Loss Of AC Power Off Normal Emergency Procedure. Station equipment operated as expected based on the PT fuse drawer that was racked out. "The Division 1 EDG was manually tripped from the Control Room because cooling from the Standby Service Water A was not available. "RHR [residual heat removal] B was in Shutdown Cooling [mode] and was verified not affected" The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-05-12
53398 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-05-11 10:11 | 2018-05-11 15:19 | 2018-05-11 | CONTAINMENT SHIELD BUILDING INOPERABLE "At 1011 EDT on May 11, 2018, Containment Shield Building Annulus differential pressure exceeded the required limit. The Shield Building was declared inoperable requiring entry into Technical Specification (TS) 3.6.15 Conditions A and B. The event was initiated by failure of the operating annulus vacuum fan. Main Control Room Operators manually started the stand-by annulus vacuum fan to recover pressure. Shield Building Annulus differential pressure was restored to the required value at 1016 EDT and TS 3.6.15 Condition A and B were exited on May 11, 2018 at 1016 EDT. "The failure mechanism for the annulus vacuum fan is being investigated. "The Containment Shield Building ensures the release of radioactive material from the containment atmosphere is restricted to those leakage paths and associated leakage rates assumed in the accident analysis during a Loss of Coolant Accident (LOCA). The Emergency Gas Treatment System (EGTS) would have automatically started and performed its design function to maintain the Shield Building Annulus differential pressure within required limits. "The event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D). The NRC Resident has been notified." | 0 | 58 | 0 | 0 | 58 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-05-11
53397 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-05-01 | 2018-05-10 17:20 | 2018-05-10 | AGREEMENT STATE REPORT - STUCK PROCESS GAUGE SHUTTER The following is a synopsis of information received via E-mail: On 5/9/2018, the Radiation Safety Officer (RSO) for ExxonMobil Chemical Co. (EMCo) reported a device failure to the Louisiana Department of Environmental Quality. On 5/1/2018 during routine annual maintenance and preventive maintenance checks it was discovered that a level density gauge had a shutter stuck in the open position. The gauge was a Ronan Engineering Co. gauge, Model Number SA1-C5 loaded with 100 mCi Cs-137 (10/95). The device s/n is EE815. The source and source holder usually have one s/n for the whole device. A RONAN engineering sales and service company was contacted to fix the problem by repairing the gauge and the shutter to function properly. The gauge is installed on processes and does not pose a health and safety threat to the general public or the EMCo employees. The gauge will remain on the operational process until the repair is made to the device. A service order number was generated by EMCo for the device repair. The shutter was stuck in the open position due to the buildup of grime and corrosive material from the operational environment. This is considered an equipment failure for reporting requirements. Louisiana Event Report ID No.: LA-180008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-05-18
53396 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2018-05-10 16:17 | 2018-05-10 17:03 | 2018-05-11 | NOTIFICATION OF UNUSUAL EVENT "Unit 3 experienced a loss of AC power while in Mode 6. Power was regained automatically from Keowee via the underground path. "Decay heat removal has been restored. Spent fuel cooling has been restored. "Emergency procedures [are] in progress." The Licensee notified the senior NRC resident inspector, State of South Carolina and local authorities. The total loss of 4160 volt AC power was for approximately 30 seconds. The unit is refueled and reactor reassembly complete up to bolting on the reactor head. There was no effect on Units 1 and 2. Notified DHS SWO, FEMA Ops Center, FEMA NWC, DHS NICC, and NuclearSSA * * * UPDATE FROM SCOTT HAWKESWORTH TO HOWIE CROUCH AT 0554 EDT ON 5/11/18 * * * At 0530 EDT, Oconee terminated the notification of unusual event on Unit 3. The basis for termination was that offsite power was restored and the plant is now in its normal shutdown electrical lineup. The licensee has notified Oconee and Pickens counties and will be notifying the NRC Resident Inspector. Notified R2DO (Ehrhardt), NRR EO (Miller), IRD MOC (Gott), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email) and NuclearSSA (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Refueling; FMode3: Refueling | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-05-10
53395 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2018-05-10 02:48 | 2018-05-10 08:59 | 2018-05-11 | VALID EMERGENCY DIESEL START ON PARTIAL LOSS OF OFFSITE POWER "At 0248 [EDT], with the plant shutdown in Mode 4, Nine Mile Point Unit 2 experienced a partial loss of off-site power during relay testing that resulted in an automatic start of the Division 2 Emergency Diesel Generator. All systems responded as expected for the event. The cause is being investigated. The station responded in accordance with appropriate Special Operating Procedures and restored impacted systems. "This event is being reported in accordance with 10CFR50.72(b)(3)(iv)(A)" At the time of the report, the emergency diesel generators are loaded and supplying plant safety equipment. The licensee has notified the state of New York Emergency Management Agency and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-05-10
53394 | 0 | WEYERHAEUSER CORP. |  |  |  |  | 2018-05-05 09:30 | 2018-05-08 14:33 | 2018-05-08 | STUCK SHUTTERS ON TWO GAUGES During a periodic inventory check at the Columbia Falls, MT location, the Facility Radiation Safety Officer discovered two Ohmart SHF1 source holders with inoperable shutter mechanisms. Both Cs-137 sources (10 milliCuries and 50 milliCuries) are in areas where exposure to the sources is minimized by their inaccessible locations. Weyerhaeuser has been in contact with the manufacturer of the level gauge (Ohmart/Vega) about removing the inoperable source holders and replacing with two (2) new source holders. The licensee contacted NRC Region 4 (Torres). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | WA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-05-16
53393 | -1 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2018-05-08 01:39 | 2018-05-08 10:38 | 2018-06-27 | CONTAINMENT LEAK RATE GREATER THAN TECH SPEC "On May 8, 2018 at 0139 Central Daylight Time, Farley Nuclear Plant Unit 1 declared containment inoperable due to total containment leak rate greater than technical specifications. The 1B containment cooler had seat leakage of approximately 30 gallons per minute from a service water drain valve. "Though the containment cooler service water supply is not tested per the Appendix J program, a loss of the containment barrier is possible under accident conditions. "The service water flow path to the 1B containment cooler has been isolated to exit the condition." The licensee will notify the NRC resident inspector. * * * RETRACTION FROM BLAKE MITCHELL TO ANDREW WAUGH AT 2151 EDT ON 6/27/18 * * * "During the time of the leakage reported in event notification 53393 the system was under administrative control. The containment isolation valves for the 1B containment cooler were closed as restoration of the containment cooler was still in progress following the outage. With the system isolated, operations had identified a 50 drop per minute (dpm) leak downstream of a service water drain valve to the 1B containment cooler. To quantify the leak, operations removed the downstream pipe cap and piping to better measure the leak under system pressure. Upon opening the service water containment isolation valves the leak rate was measured at 30 gpm. Operations re-closed the service water containment isolation valves per the pre-briefed contingency actions. It was determined that the service water drain valve (a ball valve) was not properly seated. This was all performed with operations personnel on station in the containment and in the Main Control Room. At no time were the containment isolation valves degraded. Following closure of the containment isolation valves they were also powered down to prevent inadvertent opening." The licensee notified the NRC Resident Inspector. Notified R2DO (Michel). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-05-08
53392 | -1 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2018-05-07 23:00 | 2018-05-08 01:39 | 2018-06-27 | UNANALYZED CONDITION "On May 7, 2018 at 1041 CDT, Unit 1 performed an RCS (reactor coolant system) leakrate procedure that calculated an unidentified RCS leakrate of 0.202 gpm. The leak source investigation concluded at 2150 that the packing for the charging flow control valve (FCV) was the source of the RCS leakage when it was bypassed, which isolated the leakage. A second RCS leakrate calculation was performed after the charging flow control valve was isolated which calculated an acceptable leakrate of 0.00 gpm. "The packing leakage from the charging flow control valve represented leakage external to containment which would result in a greater that 5 Rem dose projection to control room personnel during accident conditions which does not satisfy the GDC19 criteria described in Technical Specification Bases 3.7.10. Therefore the control room emergency filtration system would not be able to fulfill its design function resulting in an unanalyzed condition. "This condition is being reported pursuant to 10CFR50.72(b)(3)(ii) for a 'condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety'. "The packing leak from the charging flow control valve will remain isolated until repaired under work order SNC944374." The NRC Resident Inspector has been notified. * * * RETRACTION FROM BLAKE MITCHELL TO ANDREW WAUGH AT 2151 EDT ON 6/27/2018 * * * "Retraction - There was sufficient margin in the analysis of record to account for the increased leakage in the charging flow control valve that was not known at the time of reporting. Doses at the site boundary and in the Main Control Room would have remained less than the legal limits had a Loss of Coolant Accident occurred based on plant conditions at the time." The licensee notified the NRC Resident Inspector. Notified the R2DO (Michel). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-05-08
53391 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-05-05 | 2018-05-07 22:11 | 2018-06-20 | AGREEMENT STATE REPORT - SOURCE DISCONNECTED FROM GAUGE'S OPERATING ROD "On May 7, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer [RSO] that on the night of May 5, 2018, they discovered the 100 milliCurie (original activity) source had disconnected from the operating rod of a Berthold model P2608.100 gauge. The RSO stated a set of tongs were used to remove the source from the vessel and place it in a lead pig designed for the source. The RSO stated the manufacturer has been contacted for assistance in repairing the gauge. The individuals who removed the source from the vessel were wearing dosimetry and the RSO stated they were sending the dosimeters in for processing. The RSO stated they had no reason to believe any individual exceeded any limit. Additional information will be provided as it is received in accordance with SA-300." Texas Incident # 9570 * * * UPDATE ON 6/20/2018 AT 1117 EDT FROM ART TUCKER TO DONG PARK * * * The following was received via e-mail: "During the licensee's investigation of this event, the radiation safety officer (RSO) found that the source on a second, almost identical, gauge had also separated from the operating rod. The second gauge, model HPS-1, contains a 500 milliCurie cobalt - 60 source. The failure does not create an exposure risk to any individual. The RSO stated they had received the results for the dosimetry sent for processing from the first reported failure and all readings were 0.0 millirem. The highest lifetime dose for any individual in the report was 105 millirem. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Hay), and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-15
53390 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2018-05-04 | 2018-05-07 18:20 | 2018-05-07 | AGREEMENT STATE REPORT - MISADMINISTRATION OF INCORRECT MEDICATION "A lung scan was incorrectly performed at Wesley Medical Center in Wichita, Kansas last Friday, the 4th of May. It was reported [to the State] at approximately 1500 [CDT] on 5/7/2018. The DTPA [pentetic acid] dose was supposed to go through a nebulizer, and an MMA [methylmalonic acid] dose was supposed to be injected for perfusion, but they accidentally injected the DTPA instead. The patient was able to go through the scan as normal, but the end result is that 40 mCi of DTPA (what should have been the MMA dose, by [the State's] understanding) were injected instead of 4 mCi (what should have been the DTPA dose). The bladder dose was over 5 rads. "A full report has been promised by the licensee tomorrow, which will be forwarded to [the NRC] and entered into NMED [Nuclear Material Events Database]." It is unknown if the patient and the prescribing physician have been notified at the time of this report. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2018-05-15
53389 | 0 | WATERFORD | 3 |  |  | [3] CE | 2018-05-07 10:22 | 2018-05-07 17:40 | 2018-05-07 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL "A non-licensed supervisor had a confirmed positive result for alcohol during a random fitness for duty test. The employee's access to the plant has been terminated. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2018-05-07
53388 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-05-07 13:35 | 2018-05-07 16:31 | 2018-05-07 | DISCOVERY OF A CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "On May 7, 2018, during an engineering review of mission time requirements for Technical Specification related equipment, a deficiency was discovered regarding the Emergency Operating Procedure (EOP) guidance for natural circulation cooldown with a stagnant loop. This condition could be the result of a postulated Main Steam Line Break with a loss of offsite power. "During a natural circulation cooldown with a faulted steam generator, flow in the stagnant reactor coolant system (RCS) loop associated with the isolated faulted steam generator (SG) could stagnate and result in elevated temperatures in that loop. This becomes an issue when RCS depressurization to residual heat removal system (RHR) entry conditions is attempted. The liquid in the stagnant loop will flash to steam and prevent RCS depressurization. In this condition, the time required to complete the cooldown would be sufficiently long that the nitrogen accumulators associated with Callaway's atmospheric steam dumps and turbine driven auxiliary feedwater pump flow control valves would be exhausted. The atmospheric steam dumps and turbine driven auxiliary feedwater pump would not be capable of performing their specified safety functions of cooling the plant to entry conditions for RHR operation. This issue has been analyzed by Westinghouse in WCAP-16632-P. This WCAP determined that to prevent loop stagnation, the RCS cooldown rate in these conditions should be limited to a rate dependent on the temperature differential present in the active loops. "The WCAP analysis was used to support a revision to the generic Emergency Response Guideline (ERG) for ES-0.2 "Natural Circulation Cooldown." Figure 1 in ES-0.2 provides a curve of the maximum allowable cooldown rate as a function of active loop temperature differential which is directly proportional to the level of core decay heat. At the time of discovery of this condition, Callaway's EOP structure did not ensure that the ES-0.2 guidance would be implemented for a natural circulation cooldown with a stagnant loop. "Callaway has issued interim guidance to the on-shift personnel regarding this concern and is in the process of revising the applicable EOPs. "This condition is reportable per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shutdown the reactor and maintain it in a safe shutdown condition, (B) Remove residual heat, or (D) mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector of this condition. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2018-05-07
53387 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-05-07 03:36 | 2018-05-07 06:42 | 2018-05-07 | MANUAL RX TRIP DUE TO HIGH-HIGH LEVEL IN MOISTURE SEPARATOR DRAIN TANK "On May 7, 2018 at 0336 [EDT], DC Cook Unit 2 Reactor was manually tripped due to a high-high level experienced in the East Moisture Separator Drain Tank (MSDT) of the Moisture Separator Reheater (MSR). "This notification is being made in accordance with 10 CFR 50.72(b)(2)(iv)(B), Reactor Protection System (RPS) actuation as a four (4) hour report, and under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. The NRC Resident Inspector has been notified. "Unit 2 is being supplied by offsite power. All control rods fully inserted. All Aux Feedwater Pumps started properly. Decay heat is being removed via the Steam Generator Power Operated Relief Valves following Main Steam Stop Valve closure at 0431 due to a slow RCS [Reactor Coolant System] cooldown. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 2 remains stable in Mode 3 while conducting the Post Trip Review. No radioactive release is in progress as a result of this event." | 0 | 0 | 0 | 0 | 30 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-05-07
53386 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-05-07 03:25 | 2018-05-07 05:23 | 2018-05-07 | MANUAL REACTOR TRIP "This 4 and 8 hour notification is being made to report that Salem Unit 2 initiated a manual reactor trip and subsequent automatic Auxiliary Feedwater system actuation. The trip was initiated due to a 21 Reactor Coolant Pump reaching its procedural limit for motor winding temperature of 302F. "Salem Unit 2 is currently stable in Mode 3. Reactor Coolant system pressure is 2235 PSIG and Reactor Coolant System temperature is 547 F with decay heat removal via the Main Steam Dump and Auxiliary Feedwater Systems. Unit 2 has no active shutdown technical specification action statements in effect. All control rods inserted on the reactor trip. All ECCS [emergency core cooling systems] and ESF [emergency safety function] systems functioned as expected. "No safety related equipment or major secondary equipment was tagged for maintenance prior to this event. No personnel were injured during this event." The NRC Resident Inspector was notified. The Lower Alloways Creek Township will be notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-05-07
53385 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-05-04 14:12 | 2018-05-04 16:20 | 2018-05-04 | OFFSITE NOTIFICATION "At 1412 EDT, a portable chemical toilet was found tipped over. Approximately 1 gallon of contents spilled to gravel only. A notification to the Michigan Department of Environmental Quality and local health department is required, as well as a press release. "This event is being reported pursuant to 10CFR50.72(b)(2)(xi)." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-05-04
53384 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2018-05-04 11:45 | 2018-05-04 15:40 | 2018-05-04 | CONCURRENT REPORT FOR AN OFFSITE NOTIFICATION MADE TO THE STATE OF TENNESSEE "This is a concurrent report of a 24-hour report that was made to the state of Tennessee regarding a break in the main fire water loop due to construction activities. The fire loop is fed by city water. The fire water pipe break was isolated by closing isolation valves upstream of the break. A portion of the water and dirt from the excavation flowed into a nearby storm water drainage system. This drainage system has a storm gate which was closed prior to the event to contain the dirt and water. The dirt is still contained in the storm water system located within the protected area of NFS. The dirt is currently being removed from the storm water system. The storm gate will remain closed until the dirt removal activity has been completed. Potential health and safety consequences to the workers, the public and the environment: "There are no actual safety consequences to workers, the public, or the environment. The potential consequence was a slightly elevated but less than the 10 CFR 20 Table 2 limits of contaminated liquid effluent from a construction accident. "The licensee notified the NRC Resident Inspector." Fire watches have been established for the areas affected by the fire loop break. No criticality controls were affected by this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-05-14
53383 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-05-04 09:27 | 2018-05-04 13:52 | 2018-05-04 | AGREEMENT STATE REPORT - BOMB THREAT The following information was obtained from the state of Texas via email: "On May 4, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that on May 4, 2018, at 0927 hours [CDT], one of their managers had received a phone call from an individual who made a bomb threat against the licensee's offices in Beaumont, Texas. The licensee contacted local law enforcement (LLE) who then contacted the Federal Bureau of Investigation (FBI). LLE responded to the location within 7 minutes of the call to them and the FBI was at the location before the radiation safety officer (RSO) arrived at the office 12 minutes after the call was received. The fire department also responded. The building was evacuated and the FBI, LLE, bomb squad, Fire Marshall, and the RSO inspected the building and the areas around the building. No explosive device was found. The facility was released at 1029 hours [CDT]. Additional information will be provided as it is received in accordance with SA-300." TX Incident #: 9568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-14
53382 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-05-04 11:29 | 2018-05-04 13:50 | 2018-05-04 | UNANALYZED CONDITION ASSOCIATED WITH DAMAGING EFFECTS OF TORNADOS "During performance of an extent of condition evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, River Bend Station identified non-conforming conditions in the plant design such that specific TS equipment is considered to not be adequately protected from tornado missiles. The reportable condition is postulated by tornado missiles entering the Diesel Generator Building through conduit and pipe penetrations. A tornado could generate multiple missiles capable of striking Division 1, Division 2, and Division 3 Diesel Generator support equipment rendering all Safety Related Diesel Generators inoperable. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shut down the reactor and maintain it in a safe shutdown condition, (B) Remove residual heat, or (D) Mitigate the consequences of an accident. "This condition was identified as part of an on-going extent of condition review of potential tornado missile related site impacts. "Enforcement discretion per Enforcement Guidance Memorandum EGM 15-002 has been implemented and required actions taken. Corrective actions will be documented in a follow-on licensee event report. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2018-05-04
53381 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2018-03-08 13:23 | 2018-05-04 12:50 | 2018-05-04 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID EDG START DURING OUTAGE TESTING "On March 8, 2018, an invalid system actuation occurred while preparations were underway to perform Safety Features Actuation System (SFAS) integrated response time surveillance testing during the recent Davis Besse Nuclear Power Station refueling outage. Several minutes after connecting a data recorder to monitor the Emergency Diesel Generator (EDG) 1 start signal, at 1323 hours [EST], the EDG started with no valid actuation signals or test inputs present. The EDG successfully came up to speed and voltage as expected. The associated essential 4160 volt electrical bus remained energized from the normal power supply, therefore, the EDG output breaker did not close to supply power to the bus. Troubleshooting determined the inadvertent actuation was due to a short in the test lead wires at the recorder connection caused by a faulty test lead. The test lead was replaced and the SFAS surveillance testing completed satisfactorily. "This event is being reported as an invalid system actuation per 10 CFR 50.73(a)(2)(iv)(A); this 60-day optional telephone notification is being made per 10 CFR 50.73(a)(i) in lieu of submitting a written Licensee Event Report. "The NRC Resident Inspector was notified of the inadvertent EDG start at the time of the event and has been notified of this invalid specified system actuation notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-05-04
53380 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-05-03 12:20 | 2018-05-03 18:40 | 2018-05-03 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "During planned maintenance on Unit 2 Radiation Monitor 2-RE-4270 (Service Water Train B to Discharge Canal Rad Monitor), at 1220 CDT, several other Unit 2 Radiation Monitors that are used for Emergency Action Level evaluation became nonfunctional for about 1 hour. With these radiation monitors non-functional, all of the Emergency Action Levels associated with these monitors could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). A PC11 computer reboot restored the affected radiation monitors to a functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-05-03
53379 | 0 | YANKEE ROWE |  |  |  |  | 2018-05-02 11:24 | 2018-05-03 16:17 | 2018-05-03 | SAFEGUARDS EVENT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have been employed. The licensee notified Region 1 (Nicholson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 1 | MA | ISF |  | 73.71(b)(1) |  |  |  | 1 | 2018-05-03
53378 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2018-05-03 09:30 | 2018-05-03 10:16 | 2018-05-04 | FITZPATRICK 73.71 REPORT An actual entry of an unauthorized person into a protected area, material access area, controlled access area, vital area, or transport. The NRC Resident Inspector will be notified. * * * UPDATE ON 5/3/18 AT 1729 EDT FROM MARK HAWES TO OSSY FONT * * * The license additionally reported the event under 10 CFR 26.719(b)(4). The NRC Resident Inspector was notified. R1DO (Young) notified. FFD Group and 73.71 Safeguards Group notified via email. * * * RETRACTED AT 1617 EDT ON 5/4/18 FROM MARK HAWES TO DONG PARK * * * "It was determined that this event does not meet the reporting criteria of 10 CFR 73 Appendix G Section I (b)." The NRC Resident Inspector has been notified. R1DO (Young) notified. FFD Group and 73.71 Safeguards Group notified via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.719 |  |  |  | 1 | 2018-05-03
53377 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-01-23 11:30 | 2018-05-02 19:53 | 2018-05-02 | AGREEMENT STATE REPORT - PATIENT RECEIVED DOSE LESS THAN PRESCRIBED DOSE The following information was obtained from the state of Washington via email: "Swedish Medical Center (SMC) reported that a patient prescribed to receive 725 MBq (19.59 mCi) of Y-90 microspheres (Sirtex Medical model SIR-Spheres) to the left lobe of the liver, only received 370 MBq (10 mCi). SMC planned a two-artery feed, using 360 MBq (9.73 mCi) per artery per sub lobe. The written directive called for a total of 725 MBq (19.59 mCi) split into two doses. The certified nuclear medicine technologist who drew the dose did not properly review the written directive's instruction to split the total dose into two doses. Instead, the technologist split 370 MBq (10 mCi) into two doses of 190 and 180 MBq (5.14 and 4.86 mCi), respectively. Prior to patient administration, the radiation oncologist also failed to check the drawn doses prior to injecting them. The incident was identified post-injection when the remaining 360 MBq (9.73 mCi) of the original 725 MBq (19.59 mCi) was discovered. The physicians involved believe that the diminished dose may still provide the treatment sought. They will follow up on the patient in six months and will, if deemed necessary, retreat the liver lesions. The referring physician and patient were informed of the incident. SMC's investigation identified several errors: lack of comprehension regarding the dose draw worksheet, miscommunication and failure to review the written directive prior to correcting a dose, and failure to perform a safety pause and properly review the dose to be administered against the written directive prior to administration. Corrective actions included modifying the dose draw spreadsheet, training the nuclear medicine department with regards to the spreadsheet, and modifying the treatment record sheet to include a formal procedural pause prior to administration. The Washington Department of Health, Office of Radiation Protection, did not anticipate conducting an onsite investigation." NMED Item Number: 180058 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-05-10
53376 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2013-07-02 | 2018-05-02 19:22 | 2018-05-02 | AGREEMENT STATE REPORT - DAMAGED GAUGE The following information was obtained from the state of Washington via email: "Earth Solutions NW (ESNW) reported that a moisture/density gauge (CPN model MC-1-DR, serial #MD60308232) was crushed on 7/2/2013 at temporary jobsite in Mill Creek, Washington. The gauge contained a 1.85 GBq (50 mCi) Am-Be source (model CPN-131, serial #AM8232) and a 0.37 GBq (10 mCi) Cs-137 source (model CPN-131, serial #C8232). The gauge operator had placed the gauge in front of his truck. When asked to move his truck, he forgot about the gauge, moved the truck forward, and crushed the gauge. The source rod was retrieved using a shovel and placed in a bucket of sand. Radiation surveys revealed no radioactive contamination at the jobsite. The source rod and other parts of the gauge were returned to the ESNW facility. On 7/17/2013, Hevly Technical Services (gauge contractor) and Washington Department of Health personnel performed leak tests on the Cs-137 and Am-Be sources. Washington State Public Health Laboratories analyzed the leak test samples and detected no radioactivity. The Cs-137 source rod was reinserted into the gauge body and secured with duct tape. The gauge was then placed into its shipping container. Hevly Technical Services transported the gauge to Qal-Tek Associates (radioactive waste broker) for disposal. To prevent recurrence, ESNW provided additional training to gauge users on proper handling, transporting, storage, and emergency procedures." NMED Item Number: 130311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-05-10
53375 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-04-04 | 2018-05-02 17:05 | 2018-05-02 | AGREEMENT STATE REPORT - SHUTTER TEST FAILED The following information was obtained from the state of Washington via email: "[The licensee] called on 4-4-2018 to tell the state that their GL [General License] device failed the shutter test. He said the device was placed out of use and is being sent back to the manufacturer." Washington State Incident Number WA-18-011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-05-10
53374 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-05-01 15:51 | 2018-05-01 20:42 | 2018-05-01 | PLANT RECEIVED DIVISION ONE REACTOR PRESSURE VESSEL LEVEL 1 SIGNAL "At 1551 hrs [CDT] on 5/1/2018, with the plant in Mode 5, a division one Reactor Pressure Vessel (RPV) Level 1 signal was received; however there was no actual change in RPV level. RPV Level remained at High Water Level supporting refuel operations. This caused an actuation of division one Load Shed and Sequencing system that shed and then re-energized the 15 bus. Division one diesel generator started from standby. Residual Heat Removal pump 'A', which was in shutdown cooling mode, was lost during the bus shed, and was re-sequenced upon re-energization of the 15 bus. Upon restoration of shutdown cooling, the RHR pump discharged into the RPV. RCS temperature increased approximately 5 degrees Fahrenheit as a result of the loss of shutdown cooling. The cause of the actuation signal is under investigation. In accordance with NUREG 1022, Event Reporting Guidelines, this event is conservatively reported under 10 CFR 50.72(b)(2)(iv)(A) as an event that results in emergency core cooling system discharge into the RCS as a result of a valid signal, under 10 CFR 50.72(b)(3)(iv)(B)(8) as an event that results in the actuation of emergency ac electrical power systems, and under 10 CFR 50.72(b)(3)(v)(B) as an event or condition that at the time of discovery could have prevented the fulfillment of a safety function (remove residual heat)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION | POT RHR INOP |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(B) |  | 0 | 2018-05-01
53373 | -1 | FORT CALHOUN | 1 |  |  | (1) CE | 2018-05-01 17:41 | 2018-05-01 19:36 | 2018-05-03 | SAFEGUARDS DEGRADATION DUE TO WEATHER CONDITIONS Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The weather event was secured at 1820 CDT. The licensee will notify Region 4. * * * RETRACTION ON 5/3/18 AT 1339 EDT FROM SHERYL LEMIEUX TO DONG PARK * * * "EN 53373 is being retracted. Based on management review, it has been determined that at no time was there an uncompensated barrier at FCS [Fort Calhoun Station], and the actions taken were in compliance with the FCS Physical Security Plan. As a result, no safeguards event went as defined by 10CFR73 Appendix G, Section 1(3)(c) occurred, and the 1-Hour Event Notification is being retracted in accordance with NUREGú1022 Revision 3." Notified R4DO (Azua) and 73.71 Safeguards Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-05-01
53372 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-04-27 16:30 | 2018-04-30 19:21 | 2018-04-30 | AGREEMENT STATE REPORT - LOST PORTABLE GAUGE The following information was obtained from the state of Washington via email: "Today, April 30, 2018, the Washington State Department of Health Radioactive Materials Section was notified of a lost portable gauge. The gauge owner, Intermountain Materials Testing (WA RadMat licensee I0578), notified the Emergency Response Duty Officer at 10:15 am [PDT] about the lost gauge. The company RSO was notified of the incident by an employee earlier today. The employee determined the gauge (CPN MC3 S/N M300405776) was missing at approximately 2:35 pm [PDT] Friday, April 27, 2018. This gauge has a 10 mCi (370MBq) Cs-137 source and 50 mCi (1.85 GBq) Am-241 source. The employee searched for the gauge until 4:30 pm [PDT] before he notified the local Richland, WA Police Department. The gauge was presumed to be left on the ground at a job site near the intersection of Queensgate Dr. and Gala Way in Richland, WA, because it was determined to not be in its storage location at a different job site. This incident has been given the Incident ID WA-18-015 and is reportable under 10 CFR 20.2201(a)(1)(ii) and is a 30 day reportable event. Follow up will be supplied as needed." Washington State Incident Number WA-18-015 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-05-08
53371 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-04-30 11:24 | 2018-04-30 14:53 | 2018-04-30 | AUTOMATIC REACTOR TRIP FOLLOWING TURBINE TRIP "At 1124 CDT, Braidwood Unit 1 experienced an automatic Reactor Trip. The cause of the Reactor Trip was a Turbine Trip with reactor power greater than P-8. The turbine trip was actuated as a result of a Turbine Motoring Generator Trip. The cause of the generator trip is unknown at this time and is under investigation. "After the Reactor Trip occurred, the 1A Auxiliary Feedwater pump was manually started to provide feedwater flow to all four steam generators. The 1A Auxiliary Feedwater pump was subsequently secured and placed in standby when the Startup Feedwater pump was placed in service. "Train A Main Control Room Ventilation Filtration system shifted to Makeup Mode due to a spurious actuation signal. "No secondary relief valves lifted and no secondary steam was released as a result of the Reactor Trip. The Main Steam dump valves are in service to the Main Condenser to provide heat sink cooling. The plant is being maintained at normal operating pressure and temperature. AC power is being provided by Offsite Power with the Diesel Generators in standby and all safety systems available. There is no impact to Unit 2. "This report is being made per 10 CFR 50.72(b)(2)(iv)(B) for a RPS actuation, 4-hr notification, and per 10 CFR 50.72(b)(3)(iv)(A) for a manual actuation of the Auxiliary Feedwater system, 8-hr notification." The licensee notified the NRC Resident Inspector and Illinois Emergency Management Agency. | 0 | 0 | 0 | 48 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-04-30
53370 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-29 05:30 | 2018-04-30 14:18 | 2018-05-02 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the state of Texas via email: "On April 30, 2018, the licensee reported that sometime during the overnight hours of April 28-29, 2018, a Humboldt model 5001 moisture density gauge had been stolen from the back of a company vehicle. The licensee's technician had taken the vehicle with gauge home [to Arlington, TX], contrary to company policy, and had left the gauge chained with locks in the truck. The source rod handle was locked with a padlock. At 0530 [CDT] on April 29th, he discovered the chains had been cut and the gauge stolen. Local law enforcement was notified and the licensee has checked the surrounding area. The licensee will begin checking local pawn shops. More information will be provided as it is obtained in accordance with SA-300. "Device: Humboldt Model 5001 - SN: 2821 Sources: Americium-241 - 40 milliCuries - SN: 0379CX; Cesium-137 - 10 milliCuries - SN: NJ-04061" TX Incident #: 9566 * * * UPDATE ON 5/2/2018 AT 1452 EDT FROM KAREN BLANCHARD TO DONG PARK * * * The following was received via e-mail: "This gauge was recovered today and is being returned to the licensee." Notified R4DO (Azua), ILTAB, NMSS Events Notification, and Mexico via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-08
53369 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-04-12 | 2018-04-30 12:34 | 2018-04-30 | AGREEMENT STATE REPORT - WRONG RADIOPHARMACEUTICAL USED The following is information received via e-mail: "April 19, 2018, [the licensee] called to inquire if one of his facilities had a 'Recordable Event' or if the facility had a 'Reportable Medical Event.' The report and attachments were left in a voice mail at 8:18 pm [CDT]. The event occurred under the [Slidell Memorial Hospital] SMH Therapeutic and Diagnostic Radioactive Material License, LA-0783-L02. The event involved 5.4 mCi Tc-99m-Myoview administered to a patient who was scheduled for a lung scan utilizing [approximately] 5.4 mCi Tc-99m-MAA. The technologist depended on the unit dose for 'STAT' used to be MAA and did not verify the unit dose label. This medical event occurred on 04/12/2018. "The technologist states that a Myoview cardiac dose was in a pig labelled MAA for a lung scan. The pharmacy pulled the dose records, verified the bar coding and determined the technologist was at error. "[The licensee] provided dose calculations for the heart scan dose utilizing 5.4 mCi Tc-99m-Myoview as 0.224 rad effective dose equivalent and highest organ dose of 0.972 rad to the wall of the gallbladder. "There were corrective actions [to] retrain the technologist in patient dose verification prior to injection and request their pharmacy change their label fonts to magnification and bolding the unit dose labels. The referring physician and the patient were notified of the error. "LDEQ [Louisiana Department of Environmental Quality] considers this incident still open and subject to investigation to determine if this event was caused by the facility personnel or if it is an error caused by the pharmacy personnel." Louisiana Event Report ID No.: LA-180007, T 184299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-05-08
53368 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-28 | 2018-04-28 15:18 | 2018-04-28 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was obtained from the state of Texas via email: "On April 28, 2018, the Agency was notified by the licensee's radiation safety officer (RSO) that a Troxler model 3430 moisture/density gauge had been stolen from a company truck [in Houston, TX]. The gauge contains a 40 milliCurie cesium - 137 source and an 8 milliCurie americium source. The gauge was not in the transport case. The RSO did not know if the source rod was locked in the shielded position. The technician who had checked the gauge out had taken the gauge to his apartment (against company policy) and had placed it in the front seat of the truck to recharge it. When the technician came down the next morning to leave, they found a front window of the truck broken and the gauge gone. Local law enforcement has been notified of the theft. Additional information will be provided as it is received in accordance with SA-300." TX Incident #: 9565 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-07
53367 | 0 | DESERT NDT LLC DBA SHAWCOR |  |  |  |  | 2018-04-26 12:30 | 2018-04-27 12:48 | 2018-04-27 | UNABLE TO RETRACT SOURCE DUE TO GUIDE TUBE DAMAGE The following report was excerpted using information provided via email: "On Thursday, April 26, 2018, a crew was performing radiographic operations. At approximately 12:30 p.m. (CST), the crew experienced an incident wherein a 2-inch diameter, 8-foot long pipe rolled off a 2-1/2-foot tall table, resulting in the guide tube being used by the crew to be smashed [under the] pipe. The dent in the guide tube prevented the source from being returned to the fully shielded position. "Exact Location of Event: Pennsboro, WV "Licensed Material Involved: SPEC-150 Exposure Device (s/n 2056) SPEC G-60 Source (s/n ZA0905) lr-192 45 curies "Corrective Action Taken/Planned: To immediately correct the problem and retrieve the source, allowing it to be returned to the fully shielded position, the black sheathing on the outside of the guide tube was removed in the damaged area. Using a hammer, the damaged area was rounded out enough to allow the source to be returned to the fully shielded position. "The guide tube involved in this incident has been removed from service and will be destroyed as to prevent it from being reused. "Retraining on these types of situations will be provided to all employees, and this incident specifically, will be discussed during this quarter's safety meetings within all company locations. "To prevent a reoccurrence of an incident of this type, we have made plans with the company for whom we were providing radiography for to stage and brace piping moving forward. "Extent of Exposure: The personnel responsible for performing source retrieval recorded a total dose of 60 mR during the retrieval. "As soon as this event occurred, the crew performing radiographic operations immediately reassessed and set up appropriate 2 mR/hr boundaries, notified their Site RSO [Radiation Safety Officer] and Branch Manager, and maintained constant visual surveillance until source retrieval personnel arrived at the jobsite. At no time were any unmonitored employees in any immediate danger of being overexposed, nor were any of our company personnel, all of whom were utilizing proper radiation detection equipment." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-05-07
53366 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2018-04-26 18:00 | 2018-04-26 20:23 | 2018-04-26 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because planned maintenance activities were performed on April 23rd through April 25th on the seismic monitoring system without viable compensatory measures established. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Defueled; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-04-26
53365 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-04-26 15:31 | 2018-04-26 18:50 | 2018-04-26 | INADVERTENT INJECTION OF HIGH PRESSURE CORE SPRAY "River Bend Station experienced an inadvertent initiation and injection of High Pressure Core Spray (HPCS) at 1531 [CDT] on 4/26/2018 while operating at 100 percent power. "During replacement of Level Transmitter B21-LTN081C 'Reactor Vessel Low Water Level 1', Main Control Room received an inadvertent initiation and injection of High Pressure Core Spray. The HPCS injection valve was open for approximately 40 seconds before the operators manually closed the valve. "Feedwater Level Control responded per design and maintained Reactor Water Level nominal values. The Division 3 Diesel Generator (DG) also automatically started in response to the actuation signal. The DG did not automatically connect to the Division 3 switchgear since there was not a low voltage condition on the bus. "The manual closure of the injection isolation valve caused the system to be incapable of responding to an automatic actuation signal. The manual override of the injection isolation valve was reset approximately 16 minutes after the event, restoring the system to its standby condition. This event is being reported in accordance with 10 CFR 50.72(b)(2)(iv)(A) as a condition that caused ECCS [Emergency Core Cooling System] discharge to RCS [Reactor Coolant System] and 10 CFR 50.72(b)(3)(v)(D) as a condition that caused the loss of function of the HPCS System. "The Senior NRC Resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-04-26
53364 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-26 | 2018-04-26 17:36 | 2018-04-26 | AGREEMENT STATE REPORT - STUCK SHUTTER The following was received from the state of Texas via email: "On April 26, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that while performing routine testing of an Ohmart Vega model SH-F1 gauge containing a 5 milliCurie cesium - 137 source, the shutter would not fully close. The RSO stated open is the normal operating condition for the gauge and it does not create an exposure risk to any individual. The gauge is used for level indication. The RSO stated they have contacted a service company and they will be on site on April 27, 2018, to inspect the gauge. Additional information will be provided as it is received in accordance with - SA-300." TX Incident #: 9564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-05-04
53363 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2018-04-24 14:00 | 2018-04-26 10:31 | 2018-07-24 | AGREEMENT STATE REPORT - STUCK SHUTTERS The following was received from the State of Arkansas via email: "At approximately 1400 [CDT] on 4/24/2018 the Arkansas Department of Heath Radioactive Materials Program received a phone call from the licensee stating that during routine shutter tests two fixed gauge shutters were not functioning properly; one had a stuck shutter and the other was stiff and might become stuck. The gauges are Thermo MeasureTech Model 7063S, source serial numbers S97D2112 (stuck shutter) and S97D2109 (stiff shutter), each originally containing 2 Ci of Cs137. "Discussion with the licensee indicates that the gauges are mounted on a reactor, outside of normal employee traffic. It is normally open during operations and is only closed during maintenance of the reactor, which is not planned. Cautionary signage is already present. The licensee representative stated that the staff will be made aware of the situation. Licensee maintenance is assessing the situation and will advise the ADH Radioactive Materials program of the plan for handling this situation. "The State of Arkansas is awaiting a written report from the licensee and final disposition information for the gauge. The State's event number is AR-2018-004." * * * UPDATE FROM DAVID STEPHENS TO VINCE KLCO ON 7/24/2018 AT 1025 EDT * * * The following information was received from the State of Arkansas via email: "Subsequent to the previous communication, the licensee wrote on April 25, 2018, that Thermo-Fisher had been contacted to schedule a field service visit to address the situation. [Surveys taken indicated readings below 2 mR/hr. at 1 foot for the suspect gauges]. It has been decided by the licensee to have the service technician inspect all three gauges on site that are of the same model. "On May 21, 2018, a letter from the licensee indicated that on May 8, a field service engineer with Thermo-Fisher Scientific was able to lubricate and unstick the affected shutters using a graphite lubricant. Leak tests indicated no contamination above the threshold. The field service engineer advised the licensee that a plan should be developed for replacement of these gauges as spare parts are no longer available. The licensee will be attempting to replace the affected gauges within the next year; meanwhile, the shutters of the affected gauges will be lubricated and checked once a month. "In an email on July 20, 2018, the licensee stated that they had been informed by Thermo-Fisher that the 7063S model source holder was notorious for having stiff shutters. The pin/spring assembly apparently has very tight tolerances, and any dust or particulates in the mechanism can stiffen shutter function. The licensee stated that they attributed this event to this mechanism being exposed to the elements for over 20 years. "The state of Arkansas considers this incident closed." Notified the R4DO (Gepford) and the NMSS Events Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2018-05-04
53362 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-04-12 | 2018-04-25 17:26 | 2018-04-25 | WASHINGTON AGREEMENT STATE REPORT - INDIVIDUAL TRIED TO OBTAIN THORIUM OXIDE The following information was obtained from the state of Washington via email: [The Washington State Office of Radiation Protection] was notified by the FBI on 4-12-2018 about an individual residing in the state of Washington who was trying to buy Thorium Oxide (ThO) from a company in Florida called International Bio-analytical (IBI labs). "On 4-13-2018, [the State investigator] talked to [the] head scientist for IBI labs. He said the individual (DELETED) attempted to buy ThO 250g from their company. When [IBI Labs] talked to him, a couple red flags went off and he decided not to sell the item to [the individual]. Mainly, [the individual] wanted the item sent to [his home address] rather than a company. This is when [IBI Labs] alerted the FBI as this is out of the norm for his business. "The licensing applicability for ThO does require a license per WAC 246-232-006. However, the license required in a non-registerable GL license per WAC 246-233-010. Non-registerable GLs don't require you to have a license before you get the product. Had the individual provided a normal company address and proper business location, he would have received the item. "[On 4-11-2018, prior to attempting to order the material], [Deleted] with WA radioactive materials talked to [the individual] and explained that his business would need a license in order to receive the material. The individual mentioned he wanted it to do geological neutrino testing, but wouldn't say anymore. "[The IBI head scientist] called [the State] again on 4-18-2018, and told [them] he is not going to sell to the individual until he gets the okay from the State. "[The State] has not heard from the individual since, and [has] updated the FBI to [their] findings. "As of 4-25-2018, no further action is required and the incident is closed." Washington State Incident Number WA-18-013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 2 | 2018-05-03
53361 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-24 03:57 | 2018-04-24 14:44 | 2018-04-24 | CONTAINMENT RADIATION MONITORS INOPERABLE "At 0357 [PDT], Unit 2 Containment High Range Radiation Monitor RM-31 was declared inoperable due to erratic indication. At this time, Containment High Range Radiation Monitor RM-30 was out of service for routine calibration. "With both containment high range radiation monitors inoperable, this impacted DCPP's [Diablo Canyon Power Plant's] ability to evaluate containment radiation data for an unmonitored release in the event of an emergency. Compensatory measures were promptly put in place with the use of a portable radiation monitor as required by emergency preparedness procedures. "This condition is being reported as a loss of assessment capability in accordance with 10 CFR 50.72(b)(3)(xiii). "Actions are in progress to restore RM-30 and RM-31 to operable status. "The NRC Senior Resident Inspector has been notified." * * * UPDATE ON 4/24/18 AT 1716 EDT FROM ERIC THOMAS TO DONG PARK * * * RM-30 was restored to service. Portable radiation monitoring is not required. The licensee will notify the NRC Resident Inspector. Notified R4DO (Vasquez). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-04-24
53360 | 0 | U.S. ARMY |  |  |  |  | 2018-04-06 21:50 | 2018-04-23 13:38 | 2018-04-23 | LOST SOURCES AT CRASH SITE A helicopter went down carrying two Americium sources totaling 11 microCuries. The crash site was searched but the sources were not located. The sources were declared lost, possibly buried at the crash site. The crash site is located within a firing range and personnel are not expected to be exposed. A written report will be submitted to the NRC. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | KY | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-05-01
53359 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-04-23 | 2018-04-23 10:34 | 2018-04-23 | AGREEMENT STATE REPORT - STOLEN TECHNICIUM-99 The following is a synopsis of information received via E-mail: St. Vincent Medical Center in Fernandina Beach, Florida (License Number: 0014-8) received five (5) doses of Technicium-99 on the morning of April 16, 2018 from Cardinal Health in Jacksonville, Florida. Portions of the dose were used on patients. Later that day, the remainder of the unused doses were placed in a 'lock box' which was located outside the building. The doses were to be picked up and returned to Cardinal Health. This morning, April 23, 2018, the driver from Cardinal Health went to retrieve the doses and found the lock box had been broken into and the Tc-99 doses had been removed. The Fernandina Police were notified (report #2018-00007035). The activity of the Tc-99 is estimated to be 30 to 40 mCi. Florida Incident Number: FL18-053 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-05-01
53358 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-04-22 16:46 | 2018-04-22 22:40 | 2018-04-22 | UNDERVOLTAGE ACTUATION OF THE ENGINEERED SAFETY FEATURE BUS "On Sunday, April 22, 2018 at 1646 CDT, a valid actuation of Engineered Safety Feature (ESF) Bus 141 Undervoltage (UV) Relay occurred. At the time, Braidwood Station Unit 1 was performing a pre-planned 1A Diesel Generator (DG) Emergency Core Cooling System (ECCS) Actuation Surveillance, initiating the 1A DG to emergency start and sequence loads on a safety injection signal. Following the 1A DG solely supplying electrical power to Bus 141, the 1A DG lost voltage, resulting in an unplanned UV actuation of ESF Bus 141. The 1A DG output breaker was manually opened and local emergency stop of the 1A DG was attempted. The 1A DG continued to run at idle. Fuel supply was secured to the 1A DG and the engine stopped. Subsequently, operators restored power to ESF Bus 141 from the Unit 1 Offsite Power Source. Shutdown cooling was maintained throughout the event as the 1B Residual Heat Removal train was unaffected by the actuation. "This event is reportable under 10 CFR 50.72(b)(3)(iv)(A) for 'Any event or condition that results in valid actuation of any of the systems listed...', specifically 10 CFR 50.72(b)(3)(iv)(B)(8) for the 'Emergency ac electrical power systems, including: emergency diesel generators (EDGs)...'. "The licensee notified the NRC resident inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-04-22
53357 | 0 | STERIS ISOMEDIX PUERTO RICO, INC. |  |  |  |  | 2018-04-21 14:37 | 2018-04-22 11:42 | 2018-04-22 | FAILURE OF SOURCE RACK DRIVE MECHANISM The following is a synopsis of information received via E-mail: On 4/21/2018 at 1437 AST, the irradiator faulted with a 'Source Pass Cylinder Fault.' Source rack No. 1 moved to safe position in the pool but rack No. 2 remained in the raised position. The Maintenance Manager was notified of the situation. After evaluating the problem with the rack, he found that the air from the source rack No. 2 hoist cylinder was not being released through SVP36 and SVP36A. The Operators loosened a pipe fitting and let air slowly bleed from the rack hoist cylinder. This brought rack No. 2 into a fully lowered position at 1446 AST. The Maintenance Manager contacted the corporate, Radiation Safety Manager and the plant manager and informed them of the situation. The Maintenance Manager removed SVP36 and SVP36A valves and took them to the maintenance shop. There was no debris or water found in the valves. Both valves were replaced. The Maintenance Manager contacted the Plant Manager and the corporate RSM to inform them that the rack problem was caused by the valves not releasing and that valves had been replaced. The Maintenance Manager restarted the irradiator and after one cycle stopped the irradiator to test the valves. The source racks lowered into the pool as designed. Corrective Actions: 1. The solenoid valve vendor will be contacted Monday morning and backup-replacement valves for SVP35, SVP35A, SVP36 and SVP36A will be ordered. 2. Annual replacement of SVP35, SVP35A, SVP36 and SVP36A will be added as an annual PM task. Further investigation into the source valve failure will continue and conclusions will be included in the written report to Region 1 within 30 days. The irradiator is now operating as designed. No personnel were exposed, nor was there the possibility of exposure, to the source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | FAILED CABLE/DRIVE | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 36.83(a)(4) |  |  |  | 0 | 2018-04-30
53356 | -1 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-22 02:22 | 2018-04-22 04:28 | 2018-05-04 | BOTH TRAINS OF RESIDUAL HEAT REMOVAL INOPERABLE "On April 22, 2018 at 0222 EDT, Watts Bar Nuclear Plant (WBN) Unit 2 entered TS [Technical Specifications] LCO [Limiting Condition for Operation] 3.0.3 due to both trains of the Residual Heat Removal System (RHRS) becoming inoperable. During surveillance testing, the gas void values on Emergency Core Cooling System (ECCS) piping common to both trains did not meet acceptance criteria. This caused both RHRS trains to become inoperable. Operations subsequently vented the RHRS to meet the acceptance criteria and exited TS LCO 3.0.3 at 0227 EDT. More frequent surveillances will be conducted to monitor gas void volumes while additional analysis is being performed to determine corrective actions." The NRC Resident Inspector has been notified. * * * RETRACTION FROM TONY PATE TO HOWIE CROUCH ON 5/4/18 AT 1455 EDT * * * "This event is being retracted. The initial report was based on a conservative acceptance criteria for gas accumulation adopted on April 19, 2018 when it was determined that the previously used acceptance criteria for gas accumulation in the ECCS was non-conservative. Additional analysis has subsequently been performed and determined that a higher gas accumulation acceptance criteria does not challenge operability. With a void of less than the acceptance criteria, in the event of ECCS actuation, the system piping support loads will remain within structural limits and the piping system will remain operable. Therefore, both trains of Unit 2 RHRS were operable and the previously reported 10 CFR 50.72(b)(3)(v)(B) event is being retracted. "The NRC Resident Inspector staff has been informed of this event retraction." Notified R2DO (Desai) of this retraction. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2018-04-22
53355 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-04-21 21:52 | 2018-04-22 02:34 | 2018-05-09 | BOTH TRAINS OF RESIDUAL HEAT REMOVAL INOPERABLE "On April 21, 2018 at 2152 EDT, Watts Bar Nuclear Plant (WBN) Unit 1 entered TS [Technical Specifications] LCO [Limiting Condition for Operation] 3.0.3 due to both trains of the Residual Heat Removal System (RHRS) becoming inoperable. During surveillance testing, the gas void values on Emergency Core Cooling System (ECCS) piping common to both trains did not meet acceptance criteria. This caused both RHRS trains to become inoperable. Operations subsequently vented the RHRS to meet the acceptance criteria and exited TS LCO 3.0.3 at 2222 EDT. More frequent surveillances will be conducted to monitor gas void volumes while additional analysis is being performed to determine corrective actions." The NRC Resident Inspector has been notified. * * * RETRACTION FROM ANTHONY PATE TO DONALD NORWOOD AT 1310 EDT ON 5/9/2018 * * * "This event is being retracted. The initial report was based on a conservative acceptance criteria for gas accumulation adopted on April 19, 2018 when it was determined that the previously used acceptance criteria for gas accumulation in the ECCS was non-conservative. Additional analysis has subsequently been performed and determined that a higher gas accumulation acceptance criteria does not challenge operability. With a void of less than the acceptance criteria, in the event of ECCS actuation, the system piping support loads will remain within structural limits and the piping system will remain operable. Therefore, both trains of Unit 1 RHRS were operable and the previously reported 10 CFR 50.72(b)(3)(v)(B) event is being retracted. "The NRC Resident Inspector has been informed of this event retraction." Notified R2DO (Ehrhardt). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2018-04-22
53354 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-04-20 17:30 | 2018-04-20 22:22 | 2018-04-20 | DEGRADED REACTOR VESSEL HEAD "On Friday, April 20, 2018 at 1730 CDT, during the Braidwood Station Unit 1 refueling outage (A1R20), a scheduled ultrasonic test (UT) was performed on the top head to upper center disc weld of the Unit 1 reactor head. The UT identified 19 indications, 9 of which are not acceptable per ASME Section XI, 2001 Edition, 2003 Addenda, Paragraph IWB-3510. "This event is reportable under 10 CFR 50.72(b)(3)(ii)(A) for 'Any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded'. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-04-20
53353 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-04-20 10:42 | 2018-04-20 17:57 | 2018-04-20 | BOTH DIESEL GENERATORS INOPERABLE On Friday, April 20, 2018 at 1042 CDT, Braidwood Station Unit 1 was at 0 percent power in Mode 6. The 1A Diesel Generator (DG) was inoperable with troubleshooting in progress. The 1B DG was being run for a normal monthly run in accordance with 1 BwOSR 3.8.1.2-2, 'Unit One 1B Diesel Generator Operability Surveillance,' and subsequently tripped. The trip was due to a failure of the overspeed butterfly valve actuator and springs, and not an actual overspeed condition. The unit entered Technical Specification (TS) 3.8.2, 'AC Sources - Shutdown,' Condition B for required DG inoperable. All required TS actions were met at the time of the 1B DG inoperability. The offsite power source remains available. At no time was residual heat removal lost. "This event is reportable under 10 CFR 50.72(b)(3)(v)(B) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2018-04-20
53352 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-04-20 | 2018-04-20 16:05 | 2018-04-20 | FITNESS FOR DUTY POLICY VIOLATION A non-licensed supervisory contract worker was found in violation of the Fitness for Duty Program. The individual's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2018-04-20
53351 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-19 17:00 | 2018-04-20 15:42 | 2018-04-20 | AGREEMENT STATE REPORT - DAMAGED GAUGES The following information was obtained by the State of Texas via email: "On April 20, 2018, a consultant for the company called to inform the Agency [State of Texas] that a fire had damaged part of the refinery. The fire happened yesterday, April 19, 2018 around 1700 CDT. The radiation safety officer has been informed and the two are preparing an assessment of the damage. There are 19 gauges in the location of the fire. The fire was located in the allocation unit where phrase fractions are allocated into different hydrocarbon groups for refinement. All but two gauges have been assessed for damage. The two remaining gauges are 1 milliCurie or less in activity and cannot be checked at this time due to safety issues. Once the area is released for entry the gauges will be checked for damage. An update will be provided with gauge identification and correct activity. Updates will be provided in accordance with SA-300 guidelines." Texas Incident No.: I-9562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-04-30
53350 | 0 | RAPID CITY REGIONAL HOSPITAL |  |  |  |  | 2018-03-08 | 2018-04-20 12:05 | 2018-04-20 | PATIENT RECEIVED DOSE LESS THAN PRESCRIBED DOSE The following was received from the licensee via email: "On March 8, 2018 and March 12, 2018, the patient was treated with the incorrect setup. On March 15, 2018, the patient was treated with the correct setup. Following the third treatment, both physicists were in the HDR [High Dose Rate] vault. The patient's setup was still on the treatment table, the physicist who had delivered the first two treatments noticed the accuform in the setup. At this time the patient had already left the facility. His next treatment was scheduled for March 19, 2018. This was discussed with the physician and the decision was made to perform a CT without the accuform, prior to the next treatment. The plan was recreated, using the same dwell weights and positions as the original plan. At this point we discovered that the patient had been under-dosed by more than 50 percent. Physics notified the NRC and the prescribing physician. "As a result of the misadministration discovered March 19, 2018, a root cause analysis was performed. The direct cause of the incident was the failure to properly recreate the initial patient setup. The exclusion of the accuform caused the patient's head to be in the wrong position, leaving a gap between the treatment device and the patient's skin. "Contributing factors include the lack of a specific policy regarding custom immobilization in HDR procedures, this was only the second brachytherapy patient using custom immobilization, the pictures from the simulation did not completely show the accuform, and it is generally a therapist, not a physicist, who reproduces the daily setup using custom immobilization. "Items identified during root cause analysis: 1. At the time of treatment, there was not a policy specifically written for skin brachytherapy 2. The accuform was not used in the patient setup 3. The pictures from the simulation did not completely show the custom setup. 4. At the time of the incident there was not a verification system in place, to track the items needed for each custom setup. "Corrective actions: 1. A policy was created and provided to [NRC R4 (Simmons)] on April 4, 2018. 2. Our new policy ensures that a therapist will be present at the first treatment, and any time a physicist is treating the patient for the first time. 3. In the CT simulation, any custom immobilization used in brachytherapy will be photographed with and without the patient. This will ensure that each piece of the custom device can be clearly visualized. Our IT department will be installing a computer monitor, keyboard and mouse in the HDR treatment vault. This will allow the verification of the setup notes and photographs in the treatment room. 4. Physics is working with our IT department and Elekta to implement a bar code scanning system to track custom setup devices." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-04-30
53349 | -1 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-19 19:44 | 2018-04-20 00:55 | 2018-06-05 | UNANALYZED CONDITION RELATED TO EMERGENCY CORE COOLING GAS ACCUMULATION ACCEPTANCE CRITERIA "On April 19, 2018 at 1944 EDT, Watts Bar Nuclear Plant (WBN) determined that a preliminary analysis shows current acceptance criteria for gas accumulation in the WBN Unit 1 and Unit 2 Safety Injection System (SIS) and Residual Heat Removal System (RHRS) discharge piping may be non-conservative. The surveillances that check void values and allow venting of the systems are to be performed utilizing conservative criteria at more frequent intervals to ensure gas void volumes remain under acceptable limits. Additional analysis is being performed to determine final actions. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 6/5/18 AT 0801 EDT FROM DEAN BAKER TO ANDREW WAUGH* * * "This event is being retracted. The original report was made as a result of errors found in the gas accumulation analysis performed for WBN, such that the analysis in use might be non-conservative. WBN has performed additional analyses related to gas accumulation and determined that both the Safety Injection and Residual Heat Removal systems remained operable and would have been able to perform their safety functions during the past three years. Therefore, this event was not an unanalyzed condition that significantly degrades plant safety. "The NRC Resident Inspector has been notified." Notified the R2DO (Ernstes). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-04-20
53348 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2018-04-19 21:07 | 2018-04-19 23:41 | 2018-04-19 | MANUAL REACTOR TRIP DUE TO TURBINE ISSUE "While performing a turbine startup, a turbine control anomaly caused a steam generator level transient. The rise in steam generator level above the setpoint caused the turbine to automatically trip. The high steam generator level of 73 percent caused a feedwater isolation signal at 2107 EDT, which also tripped both Main Boiler Feed Pumps. The tripping of the Main Boiler Feed Pumps auto started the motor driven Aux Boiler Feed Pumps 21 and 23. "The reactor was manually tripped at 2108 EDT in accordance with AOP-FW-1 Loss of Main Feedwater. All control rods inserted. Electrical power is being provided from offsite via the Station Aux Transformer. Decay heat removal is being provided via the Atmospheric Dump Valves. An investigation into the cause of the turbine control anomaly is underway. The NRC Resident Inspector has been notified." The event did not have an affect on Unit 3 and there is no primary to secondary leakage. | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-04-19
53347 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-04-19 11:52 | 2018-04-19 20:00 | 2018-04-19 | UNDERVOLTAGE ACTUATION OF THE ENGINEERED SAFETY FEATURE BUS "On Thursday, April 19, 2018 at 1152 CDT, a valid actuation of Engineered Safety Feature (ESF) Bus 141 Undervoltage (UV) Relay occurred. At the time, Braidwood Station Unit 1 was performing a pre-planned Bus 141 Undervoltage Actuation Surveillance, initiating the 1A Emergency Diesel Generator (EDG) to emergency start and sequence loads on the UV signal. Following the 1A EDG solely supplying electrical power to Bus 141, the EDG lost voltage resulting in an unplanned UV actuation of the ESF Bus 141. Subsequently, operators restored power to ESF Bus 141 via crosstie of the Unit 2 offsite power source. Shutdown cooling was maintained throughout the event as the 1B Residual Heat Removal train was unaffected by the actuation. "This event is reportable under 10 CFR 50.72(b)(3)(iv)(A) for 'Any event or condition that results in valid actuation of any of the systems listed...', specifically 10 CFR 50.72(b)(3)(iv)(B)(8) for the 'Emergency ac electrical power systems, including: emergency diesel generators (EDGs)...'. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-04-19
53346 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-04-19 15:52 | 2018-04-19 18:16 | 2018-04-19 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following was received from the State of Colorado via email: "The Department [Colorado Department of Public Health and Environment] was notified via phone on 4/19/18 at approximately 1552 MDT. A G Wassenaar's RSO notified the Department that a portable gauge had been run over by a vehicle and the vehicle did not stop. At the time of the phone call, the gauge was broken into multiple pieces and the RSO was about to go out on-site to assess the damage. "State inspectors are responding immediately as well." Colorado Event Report ID No.: CO180008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-04-27
53345 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-04-19 | 2018-04-19 12:47 | 2018-04-19 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following report was received from the Nebraska Department of Health via email: "Eagle Distributing of Norfolk, LLC sold their building which contained tritium exit signs to Our Savior Lutheran Church on October 17, 2017. Eagle Distributing did not inform Our Savior Lutheran Church of the General License [GL] responsibility until March of 2018 when the Annual Renewal for GL0595 came overdue. After Our Savior Lutheran Church was informed of the exit signs and their GL responsibility, Our Savior Lutheran Church conducted a search to locate the signs within the building resulting in 3 missing signs. They have no information as to what could have happened or specific dates of their removal." NE Item Number: NE180003 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-04-27
53344 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-03-30 | 2018-04-18 13:50 | 2018-04-18 | MISADMINISTRATION OF SIR-SPHERES Y-90 MICROSPHERES RESULTING IN AN UNDERDOSE The following was received from the State of Washington via email: "Patient was under treated with Y-90 SIR-Spheres Microspheres. Prescribed dose was 24.59 mCi. Patient was treated with 8.9 mCi. "Background: SIR-Spheres Microspheres Activity Calculator determined a treatment dose of 0.91 GBq (24.59 mCi). Written Directive was signed for 0.91 GBq. Prescribed dose was entered into the Treatment Worksheet as 0.91 mCi. Dose activity delivered to the interventional radiology procedure room (Dose In-Vial) was recorded as 0.96 mCi. "Analysis: Radioactivity units of measurement varied between Written Directive and Treatment Worksheet. Radioactivity activity readings from the dose calibrator were recorded with a systematic error. Calibrator reading multiplication factor(x10) was not applied. Therefore, the vial pre-dispense Y-90 activity reading of 8.62 mCi should have been recorded as 86.2 mCi. Dose activity delivered to the IR procedure room was in fact 9.60 mCi rather than 0.96 mCi. "Y-90 SIR-Spheres treatment on 3/30/2018 was incomplete because the prescribed 0.91 GBq prescribed dose was not administered. Standard post-procedure verification check identified the under treatment. The patient was informed by the prescribing physician and scheduled for a second treatment on 4/6/2018. The second Y-90 SIR-Spheres treatment was performed on 4/6/2018 and the remaining dose was administered to complete administration of the prescribed 0.91 GBq." Washington State Incident Number: WA-18-010. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-04-26
53343 | 0 | PROVIDENCE HOSPITAL |  |  |  |  | 2018-04-17 | 2018-04-18 13:14 | 2018-04-18 | WRITTEN DIRECTIVE FOR RA-223 ADMINISTRATION INCORRECT A quarterly review conducted on 4/17/18, identified that the written directive for administration of Ra-223 was incorrect. The written directive stated that the Ra-223 should be administered orally, but should have stated that it was to be administered intravenously (IV). The review determined that there was no impact to any patients as a result of the error in the written directive. The review identified one case where the written directive was used. However, the technician administered the Ra-223 to the patient via IV and not orally. The corrective actions taken by the licensee were to correct the written directive, and review the directive with the technician to understand why the technician did not consult with the physician when there was an error in the directive. The licensee notified the NRC R3 Office (Warren). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-04-26
53342 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-18 03:00 | 2018-04-18 09:29 | 2018-04-18 | FITNESS FOR DUTY - DISCOVERY OF PARAPHERNALIA THAT COULD BE USED TO FALSIFY URINE TEST On 4/18/2018, at approximately 0300 EDT, a contract cleaning employee notified her supervisor that she had found an oven mitt and a bottle containing a liquid that was possibly urine. The bottle had a temperature strip and heating element attached to it. These items were found in the trash in a bathroom in the training center located near the bathroom used for Fitness-for-Duty testing. The supervisor notified Security. Security responded and took possession of the objects. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2018-04-18
53341 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2018-04-17 10:30 | 2018-04-17 16:29 | 2018-04-17 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "Unit 1 HPCI [High Pressure Coolant Injection] was declared inoperable due to a Main Pump seal leak that was identified during surveillance testing. Unit 1 HPCI was declared inoperable at 1030 EDT. HPCI was secured and was manually re-aligned to an available status." At the time of this notification, repairs have been completed and the licensee is making preparations to re-perform the surveillance. The licensee has notified the NRC Resident Inspector. | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-04-17
53340 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-04-17 04:16 | 2018-04-17 12:02 | 2018-06-08 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "At 0416 CDT on April 17, 2018, the High Pressure Coolant Injection System (HPCI) was isolated due to a water side leak from the gland seal condenser. Unit 1 HPCI remains inoperable pending repairs to the gland seal condenser. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(V)(D), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' This is also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(V)(D). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified of this event." * * * RETRACTION ON 6/8/18 AT 1500 EDT FROM BILL BALL TO BETHANY CECERE * * * "ENS Event Number 53340, made on 4/17/2018 is being retracted. "NRC notification 53340 was made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were met when a leak was identified on U1 HPCls Gland Seal Condenser. "A Past Operability Evaluation [POE] was performed under CR# 1406178. The evaluation concluded that HPCI was degraded, but met the threshold for TS operability. Specifically the POE states that if the leak was left unaddressed for 8 hours (mission time) with HPCI in operation, the additional volume of water that would accumulate on the HPCI room floor would be approximately 5520 gallons which would be within the capacity of the floor drain pumps and spill over into Torus area to prevent water level from reaching a value which would preclude operation of HPCI critical components. Additionally the leak was upstream of the system flow controller, so the leakage rate of 11.5 gpm would not affect the ability of the HPCI pump to provide rated flow of 5000gpm. "As such, the circumstances discussed in the report did not result in any condition that at the time of discovery could have prevented the fulfillment of the safety function of structures of system that are needed to remove residual heat. Thus, there was no impact on nuclear safety. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B). "TVA's evaluation of this event notification is documented in the corrective action program. "The licensee has notified the NRC Resident lnspector." Notified R2DO (Ernstes). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-04-17
53339 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-04-16 14:15 | 2018-04-16 16:36 | 2018-05-07 | AGREEMENT STATE REPORT - TECHNETIUM-99m GENERATOR LOST IN TRANSIT The following was received from the State of Illinois via E-mail: "The Agency [Illinois Emergency Management Agency] received a call on 4/16/18 from GE Healthcare (IL-01109-01, Arlington Heights) stating that a Mo/Tc generator in transit to their facility was unaccounted for. The generator was one of eight being returned from pharmacies in Michigan and was shipped as a Yellow-II package through [common carrier]. The Mo-99 activity was estimated to be 10.35 GBq on 4/11/18. GE Healthcare stated the empty packaging for the generator was returned in the shipment with the bottom of the box having been re-taped. [The common carrier] is working to search their hubs (Grand Rapids, Chicago Heights, and Wheeling). The shipping pharmacies have been interviewed and provided signed manifests. "Details will be provided as they become available. There is currently no reason to believe a deliberate intent to misplace the device [occurred]." GE Healthcare (Emile Poisson) also notified the NRC Operations Center regarding this event. The package was initially shipped from the Kentwood Michigan GE Healthcare location. The outer package was delivered to the correct location at 1415 CDT. GE Healthcare Michigan Licensee Number: 21-26707-01MD. Illinois Item Number: IL180027. * * * UPDATE FROM EMILE POISSON TO HOWIE CROUCH AT 1752 EDT ON 4/17/18 * * * GE Healthcare notified the NRC Operations Center that the missing generator had been located. When the shipping box broke, the generator fell into a box of office chairs that was shipping to St. Mary's Hospital in South Dakota. Personnel at the hospital recognized the generator as radioactive material and turned it over to the hospital's radiology department. The radiology department notified GE Healthcare. GE Healthcare is making arrangements to have the generator shipped to its Illinois facility. There were no reported overexposures. * * * The following additional information was received from the State of Illinois (Foresee) via email: "On 4/17/18, at approximately 1630 CDT, [GE Healthcare] notified IEMA that the package had been located at St. Mary's Hospital in Pierre, SD. Reportedly, hospital staff opened boxes of steel chairs and the generator had been packaged inside. It is unknown if the chairs/associated packaging has been assessed for removable contamination. GE Healthcare is unsure if the hospital is authorized for possession of the generator. GE Healthcare and IEMA are notifying NRC Region IV staff concurrently. The generator arrived in shrink wrapped boxes, delivered by a secondary carrier. GE Healthcare and [the original common carrier] are retracing the shipment to determine at what point the packages were comingled. Terminals at Kentwood, Ml, Chicago Heights, IL and St. Paul, MN are in question. There is currently no reason to believe a deliberate intent to misplace the device [occurred]. GE Healthcare is working to take possession of the generator at this time. Additional details will be provided as they become available." Notified R3DO (Riemer), R4DO (O'Keefe), ILTAB (E-mail) and NMSS Events Notification (E-mail). * * * UPDATE FROM DAN KANE TO STEVEN VITTO AT 1317 EDT ON 4/18/18 * * * Associates In Medical Physics, LLC notified the NRC on behalf of Avera St. Mary's Hospital, South Dakota, regarding the receipt of the generator. Upon receiving the package the hospital surveyed the device and determined no surface contamination was present. The device was shielded and locked within the hospital's hot lab. Arrangements are being made with GE Healthcare to retrieve the generator. Notified R3DO (Riemer), R4DO (O'Keefe), ILTAB (E-mail) and NMSS Events Notification (E-mail). * * * UPDATE FROM EMILE POISSON TO DONG PARK AT 1344 CDT ON 5/7/18 * * * GE Healthcare has taken possession of the generator. Notified R3DO (Kozak), R4DO (Haire), ILTAB (E-mail) and NMSS Events Notification (E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-04-24
53338 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-04-13 | 2018-04-14 21:39 | 2018-04-14 | FLORIDA AGREEMENT STATE REPORT - PATIENT RECEIVED 65 PERCENT OF PRESCRIBED DOSE TO INTENDED TREATMENT SITE The following information was obtained from the state of Florida via email: "An underdose of Y-90 Theraspheres to the patient's liver was reported to the BRC [Florida Bureau of Radiation Control] on 4/14/2018 at 3:15 p.m. [EDT]. Incident occurred on Friday, 4/13/2018 sometime during the afternoon. 60 mCi of Y-90 Theraspheres prescribed, of which 65% was delivered to patient's liver and 35% went to the waist. The RSO [Radiation Safety Officer] to follow up with documentation and a corrective action plan." Florida Incident No.: FL18-050 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-04-23
53337 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-13 20:55 | 2018-04-14 20:55 | 2018-04-14 | TEXAS AGREEMENT STATE REPORT - RECOVERY BY U.S. CUSTOMS AND BORDER PROTECTION OF A FIXED NUCLEAR GAUGE The following information was obtained by the state of Texas via email: "On April 13, 2018, at approximately 8:55 p.m. [CDT], U.S. Customs and Border Protection (CBP) notified the Agency [Texas Department of State Health Services] that it had discovered and identified a cesium [fixed] gauge - Thermo Fisher Scientific Model 5192, containing 200 milliCuries of cesium-137, SN: B8087 - in the bed of a pickup truck of an individual (road construction worker) who was crossing from Texas into Mexico at the Tornillo-Marcelino Serna port of entry in Tornillo, Texas. The individual told the CBP officer that he had found the gauge on the side of the road near Kermit, Texas, and had picked it up and put it in the back of his truck as he was leaving that area to travel to Mexico ('home'); he collects scrap metal and sells it across the border. CBP took possession of the device and the Agency contacted the owner/licensee. The licensee dispatched an employee who retrieved the device at approximately 6:00 a.m. on April 14, 2018. The licensee reported that the device packaging appeared to be secure and has performed a leak test which was sent to a third party for analysis. While there has been no indication that any individual has been exposed above any regulatory limit, the licensee's and Agency's investigations thus far have not been able to definitively make that determination. Therefore, this report is being submitted. More information will be provided as it is obtained in accordance with SA-300." Texas Incident #I-9561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-04-23
53336 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-04-14 10:40 | 2018-04-14 14:34 | 2018-04-15 | AUTOMATIC REACTOR SCRAM AND EMERGENCY CORE COOLING SYSTEM INJECTION "At 1040 EDT, Fermi 2 automatically scrammed on RPV [Reactor Pressure Vessel] Level 3 following a loss of the Division 1 Station System Transformer (SST) #64. All control rods fully inserted. HPCI [High Pressure Coolant Injection] and RCIC [Reactor Core Isolation Cooling] automatically started as designed on Reactor Water Level (RWL) 2 and restored RWL. The lowest RWL reached was 101.8 inches [above Top of Active Fuel]. HPCI injected for approximately 35 seconds. RWL is currently being maintained in the normal level band with RCIC. No Safety Relief Valves (SRVs) actuated. All isolations and actuations for RWL 3 and 2 occurred as expected. Investigation into loss of SST #64 continues. At the time of the scram, all Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generators (EDGs) were operable, and no safety related equipment was out of service. "This report is being made in accordance with 10CFR50.72(b)(2)(iv)(A), any event that results in ECCS discharge into the reactor coolant system as a result of a valid signal and 10CFR50.72(b)(2)(iv)(B), any event that results in the actuation of the Reactor Protection System (RPS) when the reactor is critical. Following the loss of power and reactor scram, the Division 2 EECW [Emergency Equipment Cooling Water] Temperature Control Valve (TCV) controller was in Emergency Manual and maintaining max cooling. Operators placed the controller in Auto and the TCV is controlling normally. "The NRC Senior Resident has been notified." Decay heat is being removed via Division 2 steam dumps to the condenser. The plant is in a modified shutdown electric lineup with offsite power available and stable. Emergency diesel generators did automatically start and load. * * * UPDATE ON 4/14/2018 AT 1838 EDT FROM JEFF MYERS TO HOWIE CROUCH * * * "This update provides additional clarification of the applicable reporting criteria for this event associated with Primary Containment Isolation Actuations. "All isolations and actuations for RWL (Groups 4, 13, and 15) and RWL 2 (Groups 2, 10, 11, 12, 14, 16, 17, and 18) occurred as expected. "This report is also being made in accordance with 10CFR50.72(b)(3)(iv)(A), any event or condition that results in valid actuation of any systems listed in paragraph (b)(3)(iv)(B): RPS, HPCI, and RCIC. "RPV pressure is being maintained by the bypass valves to the main condenser." All actuations that occurred were fully completed and restored. The licensee notified the NRC Resident Inspector. Notified R3DO (Stone). * * * UPDATE ON 4/15/2018 AT 1950 EDT FROM KELLEY BELENKY TO DAVID AIRD * * * "This update provides additional information regarding the specified system actuations and an additional applicable reporting criteria. "The loss of Division 1 Station System Transformer (SST) #64 at 1040 EDT on 4/14/2018 resulted in the automatic initiation of Emergency Diesel Generators (EDG) 11 and 12. The EDGs started as expected and continue to supply their associated busses. This is reportable pursuant to 10CFR50.72(b)(3)(iv)(A), as an event or condition that resulted in a valid actuation of any system listed in paragraph (b)(3)(iv)(B), including EDGs. "In addition, the loss of the Division 1 SST #64 resulted in the expected transfer from the normal to alternate power source for the Low Pressure Coolant Injection (LPCI) swing bus, rendering LPCI loop select inoperable. The alternate power source continued to energize the LPCI swing bus throughout the event until the system was realigned to the normal power source at 1239 EDT on 4/14/2018. This condition is reportable pursuant to 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified R3DO (Stone). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2018-04-14
53335 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-04-13 12:08 | 2018-04-13 21:04 | 2018-04-15 | TWO CRACKS IDENTIFIED AT THE FEED WATER LINE 'B' CONTAINMENT CONCRETE PENETRATION "At 1208 CDT on April 13, 2018, GGNS [Grand Gulf Nuclear Station] identified cracks in the primary containment concrete penetration [outer wall] around feed water line 'B'. There are no available dimensions for crack width or depth until further inspections are performed. "In accordance with NUREG 1022, Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73, Section 3.2.4, any event or condition that results in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, requires that when a principal safety barrier is declared inoperable the condition must be reported under 10 CFR 50.72 (b)(3)(ii)." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM GERRY ELLIS TO HOWIE CROUCH AT 2012 EDT ON 4/15/18 * * * "Grand Gulf Nuclear Station (GGNS) personnel performed an inspection of the wall around feed water line 'B'. This inspection included the protective coating in the identified area and a partial inspection of the underlying concrete. The inspection of the protective coating found a collection of non-linear anomalies, chipping, and flaking. The inspection found non-significant linear indications in the concrete. "Grand Gulf Nuclear Station determined that the collection of non-significant coating imperfections and non-significant indications in the concrete do not constitute serious degradation of primary containment. The indications do not adversely impact the operability, mission time, or safety-function (as described per Technical Specification 3.6.1.1, Primary Containment) of the containment structure. The as-found conditions have been entered into the GGNS corrective action program for final disposition. "The containment structure is operable, therefore, GGNS is retracting this event notification." The licensee has notified the NRC Resident Inspector. Notified R4DO (Kellar). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-04-13
53334 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-13 15:55 | 2018-04-13 20:01 | 2018-04-13 | VALID EMERGENCY DIESEL GENERATOR START DURING TESTING "At 1555 EDT, the Unit 2 'CD' Emergency Diesel Generator (EDG) automatically started and loaded to 4kV Safeguards bus T21C. Testing was in-progress and the start was unplanned. Unit 2 is currently defueled. Unit 1 remains stable at 100 percent power. "The South Spent Fuel Pit Cooling Train lost power due to a load shed. The South Spent Fuel Pit Cooling Pump was restarted on 2 'CD' EDG at 1614 EDT. The North Spent Fuel Pit Cooling Train remained in-service the entire time. There was no observable change in Spent Fuel Pool temperature. "This event is reportable under 10 CFR 50.72(b)(3)(iv)(A), specified system actuation of an emergency diesel generator, as an eight (8) hour report." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-04-13
53333 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-13 | 2018-04-13 17:18 | 2018-04-13 | TEXAS AGREEMENT STATE REPORT - ATTEMPTED BREAK-IN AT A FACILITY HOUSING RADIOGRAPHY EQUIPMENT The following information was obtained from the state of Texas via email: "On April 13, 2018, the Agency [Texas Department of State Health Services] received notification from a radiation safety officer (RSO) for a radiography company. The RSO stated that they experienced an attempted theft at one of their locations. The workday ended at 6:00 p.m. [CDT] yesterday and began at 6:00 a.m. today. At some point during the night hours, the lock on the complex gate was forced to the point of breakage. The complex is surrounded by a six foot fence and contains radiography vehicles, an office, and a radiography storage vault. The attempt to enter the complex was not successful. The company found the bent/broken lock and noted no items disturbed or stolen. The company informed the local law enforcement servicing the area. The company also increased its video surveillance by adding more cameras and signs communicating the area was under surveillance to deter any future attempts of criminal activity." Texas Incident #9560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-04-23
53332 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-13 | 2018-04-13 16:12 | 2018-04-18 | TEXAS AGREEMENT STATE REPORT - OVEREXPOSURE TO A RADIOGRAPHER The following information was obtained from the State of Texas via email: "On April 13, 2018, the Agency [Texas Department of State Health Services] was notified by the Licensee's Radiation Safety Officer (RSO) that an overexposure occurred after a film badge that was sent off earlier this week for an immediate reading came back with a total whole body dose of 6 Rem. On or about April 9, 2018, a radiographer working at a fabrication shop was using a QSA 880D [camera] containing 70 Curies of Iridium-192. After the camera was used to conduct some shots at one location, the radiographer carried the camera and attached cables to a different location. When he walked by a Radiographer Supervisor, the Supervisor's rate alarm starting alarming. The camera was put down, the cranks operated and the source was then fully locked inside the camera. Details of why the source was not fully inserted in the camera are not known at this time. The RSO is enroute to conduct an investigation and interviews on April 16, 2018. The camera and cranks were tested several times and appear to be working normally. No other personnel appeared to receive any significant dose. Additional information will be supplied as it is received in accordance with SA-300." Texas Incident Number: 9559 * * * UPDATE ON 4/18/18 AT 0940 EDT FROM KAREN BLANCHARD TO BETHANY CECERE * * * The update was obtained from the State of Texas via email: "Per new information received from the licensee, please change the activity of the source from 70 Curies to 102.8 Curies. "Investigation into this event is still ongoing." Notified R4DO (O'Keefe) and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-04-23
53331 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2018-04-12 19:00 | 2018-04-13 15:00 | 2018-04-13 | POTENTIALLY DEGRADED ITEMS RELIED ON FOR SAFETY "GNF-A's [Global Nuclear Fuels - Americas] Fuel Manufacturing Operation maintains a safe geometry Radwaste accumulation tank to receive certain liquid discharges from operations. During the annual shutdown work activities and routine inspections, an accumulation of material was identified in a safe geometry Radwaste accumulation tank. "The accumulation appears to have occurred due to reduced recirculation flow, an engineered feature that mixes the contents of the tank as part of a density control. The accumulation of material is an indication that the tank density control had degraded. "Plant operations attempted to remove and quantify the material per normal requirements. On 4/12/18 at approximately 1900 [EDT], GNF-A determined that the material could not be quantified in a timely manner. "In the absence of quantification, GNF-A has conservatively determined that this condition is a failure to meet performance requirements and is therefore reporting it within 24 hours of discovery pursuant to Part 70 Appendix A (b)(2). "Additional controls on the tank geometry remained intact and at no time was an unsafe condition present. In addition, there are no sources that could result in a rapid addition of uranium to the system. "Additional corrective actions, extent of condition, and extent of cause are being investigated." The licensee will be notifying their NRC Program Manager (Vukovinsky), the Radiation Protection Section at North Carolina Department of Health and Human Services, and Hanover County Emergency Management Agency. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2018-04-23
53330 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-04-12 | 2018-04-13 11:44 | 2018-04-25 | TEXAS AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA PIGTAIL CONNECTOR FAILED The following information was obtained from the state of Texas via email: "On April 13, 2018, the Agency [Texas Department of State Health Services] received notice that a radiography camera had an equipment failure yesterday, April 12, 2018. The radiography crew was on a temporary jobsite and was setting up for a job. When the radiographer tried to connect the guide tube, the pigtail on the cable broke and the camera/cable was unusable. The radiographer contacted his radiation safety officer who informed the crew to bring the camera back to the office. The source did not leave the camera. No exposure to an individual occurred. The camera was a Spec-150, #2489 with an Iridium-192 source, G60 -VC1403 at 80 Curies. The manufacturer will be sent the equipment and a full report will be provided by the radiation safety officer within the next few days. Updates will be provide as received in accordance with SA300." Texas Incident #9558 * * * UPDATE ON 04/25/2018 AT 1103 EST FROM ART TUCKER TO STEVEN VITTO * * * "The Agency contacted the licensee and the licensee stated the connector on the source pig tail had separated from the pig tail. The licensee stated the manufacturer is currently inspecting the equipment. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO(Vasquez) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-04-23
53329 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2018-04-13 02:27 | 2018-04-13 06:07 | 2018-04-13 | MANUAL REACTOR TRIP FOLLOWING MAIN FEEDWATER CONTROL PROBLEM "On 4/13/2018 at 0227 [EDT], the Oconee Unit 1 Reactor was manually tripped from 24 percent power due to the inability to control main feedwater flow through the Main Feedwater Control Valves using the Integrated Control System. Due to the RPS actuation while critical, this event is being reported as a 4-hour Non-Emergency per 10 CFR 50.72(b)(2)(iv)(B). "Following the reactor trip, multiple Main Steam Relief Valves failed to reseat at the expected pressure. Using procedure guidance, Main Steam Pressure was lowered by 115 psig, resulting in the closing of all Main Steam Relief Valves. All other post-trip conditions are normal and all other systems performed as expected. Unit 1 is currently in Mode 3 and stable." Decay heat is being removed by the steam generators discharging steam to the main condenser using the turbine bypass valves. Units 2 and 3 are not affected by the Unit 1 reactor trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 24 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-04-13
53328 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2018-04-12 11:18 | 2018-04-12 17:36 | 2018-04-12 | FITNESS-FOR-DUTY REPORT INVOLVING DISCOVERY OF KOMBUCHA TEA INSIDE THE PROTECTED AREA "At 1148 EDT on April 12, 2018, a 16.2 ounce bottle of Kombucha tea was found in a small refrigerator in the Administration Building inside the Protected Area. The bottle was found to have a small amount missing from the contents. Kombucha tea is a fermented tea containing trace amounts of alcohol, and is legally sold without restrictions. Dominion Energy Nuclear Connecticut had previously notified its workforce that Kombucha tea was prohibited from being consumed or carried onsite. The owner has not yet been determined. This is considered an alcoholic beverage and is being reported pursuant to the requirements of 10 CFR 26.719 as a 24 hour report." The NRC Resident Inspector, the State of Connecticut, and local authorities have been notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.719 |  |  |  | 0 | 2018-04-12
53327 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-12 09:20 | 2018-04-12 12:14 | 2018-04-12 | AUTOMATIC REACTOR TRIP "At 0920 EDT on April 12, 2018, the Watts Bar Unit 2 reactor automatically tripped while operating at 100 percent power. All control and shutdown bank rods inserted properly in response to the automatic reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and Steam Dump Systems. "The cause of the automatic reactor trip is being investigated. "The automatic actuation of the Reactor Protection System (RPS) is being reported as a four-hour report under 10 CFR 50.72 (b)(2)(iv)(B). "The expected actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight-hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." The plant is currently stable at normal operating temperature and pressure. The grid is stable and the plant is in its normal shutdown electrical lineup. Unit 1 was unaffected by the Unit 2 trip. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-04-12
53326 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2018-04-11 14:30 | 2018-04-11 20:56 | 2018-04-11 | DEGRADED CONDITION DUE TO INDICATION DURING ULTRASONIC EXAMINATION OF REACTOR NOZZLE PENETRATION "On April 11, 2018, while the Harris Nuclear Plant was shut down for a scheduled refueling outage, the reactor vessel head penetrations were being examined in accordance with the lnservice Inspection Program. Ultrasonic examinations identified a flaw in the head penetration nozzle number 33. The unit is in a safe and stable condition. The flaw will be repaired prior to startup from the refueling outage. "The flaw and repair have no impact on the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-04-11
53325 | 0 | UNITED STATES NAVY |  |  |  |  | 2018-04-05 14:35 | 2018-04-11 11:38 | 2018-04-18 | LOST RADIOACTIVE MATERIAL "A Marine Corps CH-53 helicopter crashed around 1453 PDT on 5 April 2018 at the outlying landing field of Naval Air Facility El Centro, California. This helicopter carries seven in-blade-inspection-systems (IBIS), one per blade, and each one carries a strontium-90 source with an activity of 0.5 milliCuries. The U.S. Navy was able to retrieve five of the IBIS, but two of them were not located after several surveys of the aircraft and the surrounding area. The U.S. Navy is reporting those two sources as lost for a total 1 milliCurie of strontium-90." The Licensee has notified NRC Region 1 (Seeley) and (Elliott). * * * UPDATE FROM L.L. FRAGOSO (VIA EMAIL) TO HOWIE CROUCH AT 1242 EDT ON 4/12/18 * * * "The sixth strontium-90 source has been found buried under the fuselage wreckage. That leaves only one strontium-90 source missing for a total of 0.5 mCi lost." Notified R1DO (Jackson) and NMSS Events Notification (email). * * * UPDATE FROM L.L. FRAGOSO (VIA EMAIL) TO ANDREW WAUGH AT 0902 EDT ON 4/18/18 * * * "The last report was made in error. Upon evaluation of the sixth IBIS (buried underneath a gear box), they found no source pin, hence we still have two missing IBIS sources. Personnel will be surveying the area in the next couple of days in the hope of finding the two missing sources." Notified R1DO (Lilliendahl) and NMSS Events Notification (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2018-04-19
53324 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-04-11 01:50 | 2018-04-11 10:14 | 2018-04-11 | CONDITION THAT COULD IMPAIR FUNCTION OF CONTROL BUILDING AC SYSTEM "At time 0150 CDT on April 11, 2018, a condition was identified that could impair the ability of the Control Building Air Conditioning System to perform its design function. "Engineering determined that the time delay relays HVKA11-80YB or HVKA11-80YD (Division II chilled water LOW FLOW relays) could fail in a manner that challenges the design safety function of the Control Building Chilled Water System during a Loss of Offsite Power (LOP) Event. A failure of the time delay relay HVKA11-80YB or HVKA11-80YD (Division II chilled water LOW FLOW relays) to provide the time delay function would cause both the Division I and Division II HVK chilled water pumps to start after a LOP, which in turn could hinder the auto start of either Division I or Division II chillers. "Currently the Chilled Water System is otherwise operating as designed. All operator actions are in place to ensure the plant meets all required designed safety system functions. Work is currently underway to correct this design vulnerability. "The NRC Resident Inspector has been notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-04-11
53323 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2018-04-11 05:42 | 2018-04-11 09:09 | 2018-04-11 | OFFSITE NOTIFICATION DUE TO HYDRAZINE SPILL "On April 11, 2018, a hydrazine spill resulted in measurable hydrazine levels released at the station outfall to the Susquehanna River over an approximately 16 minute time period. The hydrazine levels exceeded the station NPDES [National Pollutant Discharge Elimination System] permit effluent limitations. The Industrial Waste Treatment system release to the river was secured and no further hydrazine was released to the river. "The concentrations released did not threaten the downstream users or the environment. Pennsylvania Department of Environmental Protection was notified of the NPDES non-compliance on April 11, 2018 at 0542 EDT. "Pursuant to 10 CFR 50.72(b)(2)(xi), this notification satisfies the requirement to notify the NRC of the occurrence of any event or situation related to the health and safety of the public or onsite personnel, or protection of the environment, for which notification to other government agencies has been made. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-04-11
53322 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-03-28 | 2018-04-10 20:38 | 2018-07-30 | AGREEMENT STATE REPORT - BRACHYTHERAPY SOURCE DID NOT FULLY RETRACT The following was received from the State of California via E-mail. "The Regional RSO, Kaiser Permanente Medical Care Program, contacted LA County Radiation Management (LA County) on April 10, 2018 to report a Medical Event that occurred at the Kaiser Therapy Department on March 28, 2018 located in Los Angeles, CA. The event occurred during a HDR [High-Dose Rate] brachytherapy procedure in which the iridium-192 (Ir-192) source did not fully retract post-treatment and remained in the transfer guide tube about 5 cm from the cylinder-transfer guide tube connector. The source remained in this position between the patient's thighs for approximately 15 minutes resulting in the patient receiving about 300 cGy (300 rad) to the thighs. It was later determined that the source wire was bent near the source which is suspected to be the reason the source did not retract fully. "A site visit will be conducted to meet with the licensee's personnel when the RSO comes back from travel to gain a better understanding of the details of the event, especially concerning the delay in removing the source from the immediate vicinity of the patient, the delay in reporting the event to the RSO, as well as to better understand the reason the source wire did not fully retract. " California 5010 Number: 041018 (5010#) * * * UPDATE ON 7/30/2018 AT 1746 EDT FROM ANA CASAJE TO ANDREW WAUGH * * * The following was excerpted from an E-mail received from the State of California: Kaiser Permanente contacted LA County Radiation Management on April 24, 2018 to update this medical event based on new information submitted by their primary medical physicist and corroborated by other HDR personnel present during the incident. The patient's exposure time has been revised from 15 minutes to 5 minutes, and the calculated unintended dose was revised from 300 cGy to 100 cGy. Notified R4DO (Gaddy) and NMSS (Bollock) and NMSS Events Notification group via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-04-18
53321 | 0 | PURDUE UNIVERSITY |  |  |  | 1 KW LOCKHEED POOL | 2018-03-27 15:00 | 2018-04-09 14:48 | 2018-04-09 | FAILURE TO MEET TECHNICAL SPECIFICATION REQUIREMENT "On April 6, 2018 at approximately 1500 EDT, it was determined there was a potential Reportable Occurrence at the PUR-1 facility. There were no unsafe conditions at any time. The PUR-1 Technical Specification 6.7.b.1.c.vi reads, 'An observed inadequacy in the implementation of administrative or procedural controls such that the inadequacy causes or could have caused the existence or development of an unsafe condition with regard to reactor operations.' A visual inspection of the fuel is required annually with no interval to exceed 15 months. While the reactor has not operated and has remained in shutdown condition since June 5, 2017, this surveillance had not occurred for 20 months as of March, 2018. This surveillance was performed on March 27, 2018 but the administrative control which should have prevented the extended interval was not observed by facility staff. There was no existence of unsafe conditions and no [reactor] operations at any time during the period in question." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | IN | NPR | [5 empty] | 0 | 2018-04-09
53320 | 0 | MCLAREN GREATER LANSING HOSPITAL |  |  |  |  | 2018-04-08 07:00 | 2018-04-08 12:20 | 2018-04-08 | SURFACE CONTAMINATION ON OUTSIDE OF PACKAGE EXCEEDING NRC REPORTING LIMITS McLaren Greater Lansing Hospital is reporting receipt of a package of radioactive material with removable surface contamination on the outside of the package greater than NRC reporting limits. The package was received on 4/8/18 around 0700 EDT. Wipe tests performed on the external surface of the package indicated a removable contamination level of 8,427 dpm/300 cm2. Radiation levels of the package measured 0.02 millirem at the surface. The package contained Technetium-99m and was shipped by Cardinal Radiopharmacy of Jenison, MI. No damage to the package was observed. The hospital employee receiving the package immediately notified the shipper about the contaminated package. Surveys were performed in the package receipt area to ensure that contamination was not spread beyond the area. No additional contamination was found in the package receipt area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2018-04-16
53319 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2018-04-07 08:36 | 2018-04-07 12:10 | 2018-04-07 | AUTOMATIC REACTOR TRIP AND PCIS ACTUATION DURING STATOR COOLING SYSTEM TESTING "On April 7, 2018, at 0836 EDT, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped during testing of the stator cooling system. The trip was uncomplicated with all systems responding normally. No safety-related equipment was inoperable at the time of the event. Due to the Reactor Protection System (RPS) actuation while critical, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "Operations responded using Emergency Operating Procedures and stabilized the plant in Mode 3. Reactor water level being maintained via normal feedwater system. Decay heat is being removed through the bypass valves. "Reactor water level reached low level 1 (LL1) as a result of the reactor trip. The LL1 signal causes a Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL1 isolations occurred as designed; the Group 8 valves were closed at the time of the event. Due to the Primary Containment Isolation System (PCIS) actuation, this event is also being reported as an eight-hour, non-emergency notification in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the PCIS. "Unit 2 was not affected. There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. The automatic reactor trip was not complicated and all safety-related systems operated as designed. "Investigation of the cause of the Reactor Protection System actuation is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-04-07
53318 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2018-04-07 04:51 | 2018-04-07 11:59 | 2018-04-07 | AUTOMATIC ACTUATION OF AUXILIARY FEEDWATER SYSTEM (AFW) "On April 7, 2018 at 0451 EDT, with Unit 1 in Mode 3 at 0 percent power, an auto actuation of 'A' and 'B' Motor Driven Auxiliary Feedwater (MDAFW) pumps occurred during the shutdown of Unit 1 for Harris Nuclear Plant's refueling outage. Plant Operators successfully took control of the AFW flow and noted the 'B' Main Feed pump was still running with proper suction and discharge pressures of 430 lbs. and 1000 lbs. "The 'A' and 'B' Motor Driven Auxiliary Feedwater (MDAFW) pumps automatically started as designed when the 'Loss of Both Main Feedwater Pumps' signal was received. The cause of the actuation is still being evaluated. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the Auxiliary Feedwater system. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-04-07
53317 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-04-05 11:17 | 2018-04-05 18:23 | 2018-04-05 | SECONDARY CONTAINMENT HATCH LEFT OPEN "On Thursday, April 5, 2018, at approximately 1117 hours Central Daylight Time, Entergy contract personnel opened the personnel hatch allowing access to the roof of the Secondary Containment Building for the purposes of performing an inspection of various items located on the roof. "During the time period the individuals were on the roof, the hatch was left open. An individual was adjacent to the door with a radio and had constant communication link with the control room operator. "Pursuant 10 CFR 50.72(b)(3)(v)(C), and 10 CFR 50.72(b)(3)(v)(D) this event is being reported as an event or condition that could have prevented the fulfillment of a safety function. "Because the site had an individual briefed and at the door in constant communications with the control room to close the hatch if condition required such an action, this event is not viewed as an actual loss of safety function." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-04-05
53316 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2018-04-05 | 2018-04-05 17:40 | 2018-04-05 | AGREEMENT STATE REPORT - STUCK SOURCE The following was received from the State of North Dakota via email: "American Crystal Sugar Company experienced a stuck sealed source (Berthold Technologies U.S.A., LLC Model SSC-100, 60 milliCuries [Co-60] at calibration) in a source tube located inside a vessel during a routine shutter check at their Hillsboro, ND location. The sealed source is fixed to a cable which allows the source to be lowered through a source tube which is located inside a vessel. Upon attempting to retract the source into the shielded gauge housing (Berthold Technologies U.S.A., LLC Model LB 8120-01) to perform the shutter check, the source did not budge. The licensee contacted Berthold Technologies U.S.A., LLC (manufacturer) regarding the stuck source. Berthold personnel instructed the licensee to apply a penetrating oil to the source tube in an attempt to break it loose. As of the notification time, the source remained lodged in the source tube in its normal operating position. The five detectors associated with this source continue to read radiation levels as expected. The licensee will continue to apply the penetrating oil and attempt to pull it back into the shielded gauge housing and provide an update in the morning. More information will be provided as received." ND Incident Report # ND180001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  |  |  |  | 0 | 2018-04-13
53315 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-04-05 09:04 | 2018-04-05 15:31 | 2018-04-10 | AGREEMENT STATE REPORT - ABANDONED SOURCE The following was received from the State of Illinois via email: "At approximately 0904 [CDT] on 4/5/18, the Agency [Illinois Emergency Management Agency (IEMA)] received a call reporting a radioactive source abandoned near a dumpster in residential Carpentersville, IL. Carpentersville Fire and Hazmat was managing the scene. A patrol with the Carpentersville police department reported finding the source at approximately 0806 [CDT] this morning and utilized the manufacturer label and emergency contact information on the package to notify Siemens Medical Solutions. Police had secured the scene until the fire department had arrived. Siemens' RSO [Radiation Safety Officer] had arrived on scene by 0930 [CDT] and contacted the IEMA radioactive materials section. The RSO confirmed the source to be an improperly abandoned Ge-68 phantom source (model CS-20-1, S/N 11054). Review of the Siemens license confirmed they were authorized for possession of the material and qualified to perform an assessment/transport. After discussion with Fire/Hazmat and IEMA, the RSO took possession of the phantom and the scene was cleared. At 1026 [CDT], the Agency received confirmation of the source being safely placed in Siemens' licensed storage area. Additional leak tests confirmed no contamination and Siemens is tracking down the owner of the source. Preliminary checks show the source was originally shipped to California. Additional details will be provided as they become available. "The radioactive material recovered was a Ge/Ga-68 epoxy-based reference source utilized in the calibration of PET/CT scanners. The Ge-68 source was contained within its storage packaging and exhibited exposure rates of 0.8 mR/h at one foot and 0.090 mR/h at one meter. Although it originally contained 1.39 mCi of Ge/Ga-68 (assay date of March 31, 2016), the source had decayed to approximately 212 microCuries. However, unshielded contact exposure rate could still be as high as 1100 mR/h on contact. The police officer and fire department personnel established a fifty foot perimeter and never got closer than seven feet to the package. There are no exposure concerns resulting from this incident. The package markings were clearly displayed and no effort was apparent to cover or deface." Illinois Report Number: IL180026 * * * UPDATE ON 04/10/18 AT 1347 EDT FROM GARY FORSEE TO ANDREW WAUGH * * * The following update was received from the State of Illinois via email regarding two additional missing sources: "At approximately 0904 [CDT] on 4/5/18, the Agency received a call reporting a radioactive source abandoned near a dumpster in residential Carpentersville, IL. A patrol with the Carpentersville police department reported finding the source at approximately 0806 [CDT] that morning and utilized the manufacturer label and emergency contact information on the package to notify Siemens Medical Solutions. Police had secured the scene until the fire department had arrived. Siemens' RSO had arrived on scene by 0930 [CDT] and contacted the IEMA radioactive materials section. The RSO confirmed the source to be an improperly abandoned Ge-68 phantom source (model CS-20-1, S/N 11054). Review of the Siemens license confirmed they were authorized for possession of the material and qualified to perform an assessment/transport. After discussion with Fire/Hazmat and IEMA, the RSO took possession of the phantom and the scene was cleared. At 1026 [CDT], the Agency received confirmation of the source being safely placed in Siemens' licensed storage area. Additional leak tests confirmed no contamination and the phantom source is pending proper disposal at the manufacturer's Knoxville, TN location. In coordination with Siemens and State of California officials, it was determined the source was originally supplied to Huntington Memorial Hospital in Pasadena, CA. On the evening of 4/5/18, officials with the State of California confirmed Huntington Memorial Hospital's PET/CT unit was serviced and (3) sources shipped for disposal by Zetta Medical (a non-licensed company based out of Lake Zurich, IL). This 11/27/17 servicing by Zetta Medical resulted in the removal and replacement of the following sources: Ge-68 1.14 mCi rod source (S/N 19626), Ge-68 1.14 mCi rod source (S/N 19625), and a Ge-68 1.39 mCi phantom source (S/N 11054). IEMA staff contacted Eckert and Ziegler and confirmed that neither package was received at their company. At this point, IEMA notified first responders and other state and federal partners of the two additional missing sources. IEMA staff dispatched two responders to conduct gamma scintillator surveys of the area where the phantom was found. Extensive searches of the area on the afternoon of 4/6/18, did not result in locating the two missing Ge-68 rod sources. "IEMA performed an investigation at Zetta Medical on 4/9/18. According to provided FedEx manifests and shipping receipts, Zetta Medical's on site technician, packaged the three sources and transported them to a local FedEx drop off location on 12/7/17. The location of the sources from the time of removal on 11/27/17 until 12/7/17 remains under investigation as well. The shipping manifest was obtained that identifies Zetta Medical as the shipper. The intended recipient was Eckert and Ziegler in California. The shipper/recipient information was inadvertently reversed; resulting in the sources being shipped to Zetta Medical in Lake Zurich. The two packages arrived in Lake Zurich, IL on 12/12/17. On 12/13/17, Zetta Medical attempted to ship the sources back to Eckert and Zeigler in Burbank, CA via Pilot Freight Services. The two packages were consigned as UN2915 for return via air out of O'Hare airport to LAX. The two packages were returned to Zetta Medical on 12/19/17. At this point, the sources were stored in Zetta Medical's warehouse for several months. "The Zetta Medical employee claims to have packaged and shipped the two packages (containing three Ge-68 sources total) back to Eckert and Zeigler via FedEx on or around 3/12/18. Although electronic shipping records are retained for outgoing shipments, Zetta Medical representatives said this shipment did not have an electronic record. Video surveillance is present in the company. However, the equipment was not recording for the time period of concern. After speaking with FedEx's corporate Radiation Safety Officer and their review of dispatch records over the last four months, FedEx has determined they have no records of a hazmat (radioactive) package being picked up from Zetta Medical. Police found the abandoned phantom source at the dumpster adjacent to the home of the Zetta Medical employee who claims to have shipped the packages. "It was identified that Zetta Medical has performed unauthorized work with licensed radioactive material. It was also confirmed that representatives of Zetta Medical took possession of at least three Ge-68 sources before losing control of the same. This investigation remains open pending enforcement proceedings and pending paperwork from those entities involved. "The radioactive material recovered was a Ge/Ga-68 epoxy-based reference source utilized in the calibration of PET/CT scanners. Ge-68 has a 271 day half-life, with gamma exposure from the Ga-68 daughter in equilibrium. The recovered Ge-68 source exhibited exposure rates of 0.8 mR/h at one foot and 0.090 mR/h at one meter. Although it originally contained 1.39 mCi of Ge/Ga-68 (assay date of 3/31/16), the source had decayed to approximately 212 microCi. Leak tests were taken on scene and confirmed to not have removable contamination. The police officer and fire department personnel established a fifty foot perimeter and never got closer than seven feet to the package. There are no exposure concerns resulting from this portion of the incident. The package markings were clearly displayed and no effort was apparent to cover or deface. "The two remaining, missing Ge-68 rod sources were originally assayed with 1.14 mCi of activity each. They now each contain approximately 0.2 mCi of Ge-68 and are sealed in a 0.25" x 11" steel rod. There should be no airborne hazard due to the internal matrix unless immersed in fire. Data made available from the manufacturer states if the sources are removed from their shielding, the exposure rate would be approximately 1 mR/h at one foot and 100 microR/h at one meter. There are no exposure concerns reported from this incident; however, efforts to recover the remaining two sources are still ongoing." Notified R3DO (Stone), ILTAB DO (Ahern), and NMSS Events Notification (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-04-13
53314 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-04-02 16:00 | 2018-04-04 14:20 | 2018-04-04 | AGREEMENT STATE REPORT - RECEIVED DOSE LESS THAN PRESCRIBED DOSE The following was received via email from the state of California: "A medical event per 10 CFR 35.3045 was determined to have occurred on April 2, 2018 during a University of California San Diego (UCSD) Y-90 liver therapy procedure. The total delivered dosage was greater than 20 percent less than the prescribed dosage. "The authorized user prescribed MDS Nordion Theraspheres Y-90 activity of 22.7 mCi to be delivered to the left lobe of the patient's liver. During the medical procedure, blockage occurred in the delivery apparatus, and the authorized user was unable to complete the administration of the Y-90 Therasphere dosage. Post-procedural dosage vial chamber measurements were performed that indicated only 32.5 percent (7.4 mCi) of the prescribed Y-90 dosage was delivered. "An MDS Nordion representative was observing the procedure. "The UCSD campus Radiation Safety office was notified that the administration resulted in a medical event and the California Radiation Health Branch was notified. The patient and their referring physician were notified on April 2, 2018. The patient will be scheduled for another Therasphere administration in the near future to complete the treatment plan." California 5010 Number: 040218 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-04-12
53313 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2018-03-06 | 2018-04-04 10:10 | 2018-04-04 | AGREEMENT STATE REPORT - DOSE DELIVERED TO WRONG TREATMENT SITE A patient was prescribed treatment by High Dose Rate (HDR) brachytherapy to a breast keloid in two fractions on 3/6/18 and 3/7/18 of 600 cGy per fraction. The patient contacted the oncologist when a skin/tissue reaction was discovered on 4/2/18. The reaction was not an anticipated response to the treatment plan. The fractions were likely directed to the wrong treatment site due to an improper length HDR catheter. The patient will be evaluated by the oncologist this week. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2018-04-12
53312 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2018-03-05 | 2018-04-03 18:29 | 2018-04-03 | AGREEMENT STATE REPORT - MISSING GENERALLY LICENSED NI-63 SOURCE The following information was received via E-mail: "The licensee indicated that during a lab remodel, an employee removed a Gas Chromatograph (GC) containing a 13.81 mCi, Ni-63 source, Serial Number M2093, a license distributed under general license. The GC was then sent to surplus. The device was then purchased by an unknown party, on an as yet to be determined date. The radiation safety team last physically inventoried the device on August 2, 2017. The current location of the device is unknown." Utah Event Report ID No.: UT180001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2018-04-11
53311 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-04-02 15:41 | 2018-04-03 11:48 | 2018-04-03 | AGREEMENT STATE REPORT - MISSING GENERALLY LICENSED AM-241 SOURCE The following information was received via E-mail: "On 4/2/18, while conducting an inventory at Aladdin Temp-rite LLC, the licensee discovered that one of their generally licensed devices was missing. The device information includes the following: "Manufacturer: Amersham Model: AMCP6 Model #: 103 Serial #: 11070 Isotope: Am-241 (150 mCi) "A follow-up report will be submitted within 30 days." State Event Report ID No.: TN-18-064 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-04-11
53310 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-04-03 00:19 | 2018-04-03 02:53 | 2018-04-03 | LOSS OF SECONDARY CONTAINMENT FOLLOWING SURVEILLANCE TESTING "On April 3, 2018 at 0019 [EDT], the Susquehanna control room received indication that a loss of Secondary Containment Zone 3 differential pressure had occurred. Control room operators noted the loss following completion of surveillance testing. The cause is under investigation. Zone 3 differential pressure was restored to greater than 0.25 inches WC [water column] at 0145 [EDT]. "Zone 3 differential pressures being less than 0.25 inches WC constitutes a loss of Secondary Containment based on not meeting requirements of SR [Surveillance Requirement] 3.6.4.1.1. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG-1022, Revision 3, Section 3.2.7, as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-04-03
53309 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-04-02 15:15 | 2018-04-02 18:33 | 2018-04-02 | CONTRACTOR SUPERVISOR TESTS POSITIVE DURING FITNESS FOR DUTY TEST A contractor employee supervisor had a confirmed positive for illegal drugs during a fitness for duty test. The employee's access to the site has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Under Construction; IMode2: Under Construction | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-04-02
53308 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-03-09 14:00 | 2018-04-02 14:33 | 2018-04-02 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE GUIDE TUBE CRUSHED The following information was received via E-mail: "On Friday, March 9, 2018, Applied Inspection Systems was performing industrial radiography. At approximately 1315 CDT while performing industrial radiography, a pipe fitting sitting on a 'V' pipe stand fell over and crushed the source guide tube. Source Production & Equipment Company was called in to perform source retrieval. There were no over-exposures or reportable exposures. The retrieval crew received a maximum of 40 mR. The source was retrieved and re-inserted back into the camera with no concerns noted. "The SPEC IR-192 Model G-60 source serial number was YK0701, source strength was 35 Ci, and camera serial number was 1381. The industrial radiography camera was a SPEC-150. "This event is considered closed out." Applied Inspection Systems, Inc. License Number: ARK-0576-03310, Reciprocity: RC-493, AI#: 154688. This Arkansas licensee was working under reciprocity in the State of Louisiana at the Calumet-Cotton Valley Refinery, in Cotton Valley, Louisiana. Louisiana Event Report ID No.: LA20180003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2018-04-10
53307 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-04-02 10:24 | 2018-04-02 11:20 | 2018-04-02 | PLANNED TECHNICAL SUPPORT CENTER (TSC) MODIFICATION "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the work activity affects the functionality of an emergency response facility. "A planned modification to the Technical Support Center (TSC) ventilation system started on April 2, 2018. The work activity includes replacement of the air conditioning system. The work duration is approximately three weeks. "If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Coordinator will relocate the TSC staff to an alternate location in accordance with applicable site procedures. The Emergency Response Organization team has been notified of the TSC modifications and the possible need to relocate during an emergency. "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-04-02
53306 | 0 | THE NACHER CORPORATION |  |  |  |  | 2018-03-31 16:30 | 2018-03-31 20:57 | 2018-03-31 | GUIDE TUBE DISCONNECTED WITH RADIOGRAPHY SOURCE NOT RETRACTED The following is a synopsis of the information received during phone notification: On March 31, 2018 at about 1630 CDT, radiography was being conducted on an offshore platform at the +10 foot level. During an exposure the technician (radiographer) noted that the source did not appear to be retracting. The technician observed that the guide tube had become disconnected. The technician lifted the guide tube to align the source cable and the assistant (radiographer) cranked in the source. The technician estimated he held the guide tube for 2 to 5 seconds for the source to be retrieved. The whole evolution took an estimated 30 to 60 seconds. The technicians then shutdown the operation and called the Radiological Safety Officer (RSO). The technician and assistant's whole body dosimetry was read and the technician received 7 mR, and the assistant no millirem (mR). The device that malfunctioned was a Source Product Equipment Company (SPEC) model 150 with a model G60 source of IR 192 with an activity of 77 curies. The RSO calculated the technician's dose to the hand to be 630 mR. The RSO stated that since this is an offshore operation he was reporting this event to the NRC under a reciprocity agreement. The RSO stated that he would be making a report to the state of Louisiana, and to NRC Region 4 as a courtesy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-04-09
53305 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2018-03-31 | 2018-03-31 19:33 | 2018-03-31 | ONE HEAD PENETRATION NOT ACCEPTABLE DURING PENETRATION EXAMINATIONS "On March 31, 2018, during the Indian Point Unit 2 refueling outage, with the reactor defueled and the head removed and located on the head stand, and all fuel from the reactor vessel removed and located in the spent fuel pool, while performing planned examinations on the 97 reactor vessel head penetrations, it was determined that one penetration could not be dispositioned as acceptable per the requirements of 10CFR50.55a for the reactor coolant system pressure boundary. The examinations are being performed to the meet the requirements of 10CFR50.55a(g)(6)(ii)(D), and ASME Code Case N-729-4, to find potential flaws/indications well before they increase to a degree that could potentially challenge the reactor vessel head pressure boundary. All other reactor vessel head penetrations have had a bare metal visual inspection completed with no other indications identified. The station is currently performing the remaining non-destructive examinations required by Code Case N-729-4. "Repairs are currently being planned, and will be completed prior to entering Mode 5 from the current refueling outage. "This is reportable, pursuant to 10CFR50.72(b)(3)(ii)(A) since the as found indications did not meet the applicable acceptance criteria referenced in ASME Code Case N-729-4 to remain in-service without repair. "The NRC Resident Inspector has been informed. " The licensee has also notified the NY Public Service Commission. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-03-31
53304 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-03-31 02:06 | 2018-03-31 10:00 | 2018-03-31 | SECONDARY CONTAINMENT INOPERABLE DUE TO FAILED SURVEILLANCE TEST "At 0206 [CDT] on March 31, 2018, with the plant in Mode 1 at 100% rated core thermal power, Grand Gulf Nuclear Station experienced a loss of Secondary Containment. During the performance of a Standby Gas Treatment System (SGTS) drawn down test with Auxiliary Building train bay door (1A319A) as the secondary containment boundary, Grand Gulf was unable to maintain secondary containment pressure, as required by SR [surveillance requirement] 3.6.4.1.4, greater than or equal to 0.266 inches of water vacuum for 1 hour. Following initial vacuum draw down, secondary containment pressure degraded to 0.225 inches of water vacuum with operators in the field reporting air leakage from door 1A319A. The test was secured and Secondary Containment was declared inoperable and Technical Specification 3.6.1.4 A.1 was entered. Following completion of the failed surveillance test, Secondary Containment was returned to an operable status at 0315 hours on March 31, 2018, by returning the system to a previously known operable configuration by closing doors 1A310, 1A312 and 1A319. This is being report under 10 CFR 50.72(b)(3)(v)(C)." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-03-31
53303 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2018-03-30 13:05 | 2018-03-30 20:47 | 2018-03-30 | PRIMARY CONTAINMENT DECLARED INOPERABLE DUE TO BOTH AIRLOCK DOORS OPEN SIMULTANEOUSLY "On March 30, 2018 at 1305 CDT, with the reactor at 98 percent core thermal power and steady state conditions, plant personnel identified that both doors of the containment personnel airlock were open simultaneously due to failure of the interlock. Personnel were at both the outside and inside doors. Immediate action was taken to close the inner containment personnel airlock door and it was verified closed. Both doors of the containment personnel airlock were open for less than one minute. There was no radioactive release as a result of the event. The cause of the interlock failure is under investigation. "This condition requires an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(ii)(A), the condition of the nuclear power plant, including its principal safety barriers (primary containment), being seriously degraded. This condition is also reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material." The NRC Resident Inspector was notified. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2018-03-30
53302 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2018-02-01 | 2018-03-30 15:50 | 2018-03-30 | PART 21 - REFURBISHED PRESSURE REGULATOR MAY RESULT IN EMERGENCY DIESEL GENERATOR FAILURE TO START The following report is an excerpt from a fax from Engine Systems, Inc.: "ESI [Engine Systems, Inc.] supplied a refurbished pressure regulator assembly, P/N 1776 506, S/N 20776487, to Brunswick Nuclear Plant in August 2017. ESI later determined that two components of the assembly, an upper and lower diaphragm plate, were omitted during reassembly of the refurbished regulator. Reference item 8 on Figure 1 for location of the diaphragm plates within the pilot valve portion of the regulator assembly. These metal diaphragm plates distribute load and retain the associated rubber diaphragm. Omission of the metal plate may not initially affect operation of the pilot valve and therefore may not be detected during functional testing; however over repeated cycles there is a strong possibility that the rubber diaphragm would tear or rupture without the benefit of load distribution and support provided by the metal diaphragm plate. "The regulator assembly is used in the safety-related air start system of the emergency diesel generators (EDGs) at Brunswick Nuclear Plant. Failure of the regulator to function properly due to the omission of a component within the pilot valve portion of the assembly could adversely affect the starting capability of the EDG. Since the EDG is a safety system used to ensure the safe shutdown of the nuclear reactor, this issue is considered to be a reportable defect as defined by 10CFR21." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-03-30
53301 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2018-03-30 | 2018-03-30 12:18 | 2018-03-30 | AGREEMENT STATE REPORT OF OVEREXPOSURE TO CARDIOLOGIST The following report was received from the Mississippi Division of Radiological Health via email: "It was reported, via phone, that an overexposure was received by a Cardiologist in the Ocean Springs Hospital's Catheterization Laboratory. The Cardiologist has received a dose of 5.1 R. The individual reported to the Division of Radiological Health (DRH) of Mississippi that corrective actions were being taken: an investigation was being implemented, dose report(s) were being gathered, and the Cardiologist was being trained on proper handling of ionizing radiation. "DRH immediately responded by requesting the following information: a report detailing the overexposure, dosimetry reports for the current year, a report on the Radiation Safety Committee's investigation, corrective actions that were taken, and if the overexposure was due to radioactive material or an x-ray device. "Licensee notified to send a written report of the initial findings by April 5, 2018." Event Report ID: MS-180004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2018-04-09
53300 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-03-29 13:44 | 2018-03-29 22:28 | 2018-03-29 | UNANALYZED CONDITION DUE TO INOPERABILITY OF EMERGENCY EQUIPMENT COOLING WATER PUMP "At 1344 on March 29, 2018, it was determined [engineering evaluation] that an unanalyzed condition that significantly degraded plant safety previously existed. During a postulated control room abandonment due to a fire, and concurrent with a Loss of Offsite Power (LOOP), the required number of Emergency Equipment Cooling Water (EECW) pumps would not have been available from 10/28/2015 to 3/10/2018. "On March 8, 2018, during relay functional testing it was discovered that the C3 Emergency Equipment Cooling Water (EECW) pump closing springs did not recharge with the breaker transfer switch in emergency. On August 23, 2012, a wire modification was performed that contained a drawing error resulting in wire placement on the incorrect connection points for the C3 EECW pump. On March 10, 2018, the C3 EECW pump breaker wiring was corrected and subsequent testing was completed satisfactorily. "Prior to 10/28/2015, Brown's Ferry Nuclear Plant (BFN) adhered to Appendix R fire protection requirements which did not credit the C3 EECW pump for fire protection from the backup control location. On 10/28/2015, BFN transitioned to National Fire Protection Association (NFPA) 805 fire protection requirements which takes credit for the C3 EECW pump from the backup control location. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety'. This is also reportable as a 60-day written report in accordance with 10 CFR 50.73(a)(2)(ii)(B). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified of this event." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-03-29
53299 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2018-03-29 15:00 | 2018-03-29 16:42 | 2018-03-29 | UNPERMITTED TRITIUM RELEASE WITHIN THE SITE BOUNDARY "On March 29, 2018, Exelon Generation Company, LLC notified the Illinois Environmental Protection Agency (IEPA) and the Illinois Emergency Management Agency (IEMA) in accordance with state regulations of an unpermitted release of radionuclides at the Quad Cities Nuclear Power Station within the site boundary. There has been no detection of the liquid release beyond the site boundary. No impact to human health or the environment are anticipated. "This notification is being made to satisfy 10CFR50.72(b)(2)(xi), notification of the NRC for any event related to the health and safety of the public for which a notification to other government agencies has been or will be made." The source of the Tritium release was from the Rad waste system. The spill was reported to be within the protected area which is within the site boundary. The quantity of the release is unknown at this point as the investigation and spill cleanup is in progress. The Licensee Notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-03-29
53298 | 0 | GM COMPONENTS HOLDING, LLC |  |  |  |  | 2018-03-28 | 2018-03-29 16:07 | 2018-03-29 | NOTIFICATION OF A LOST TRITIUM EXIT SIGN During an annual audit on 3/28/2018, the licensee determined that a self luminous exit sign was missing. Through interviews the licensee determined that an employee had removed the sign during a safety walkdown, because it did not appear to be working, and likely disposed of in the trash. Through a records review the licensee determined the safety walkdown was most likely on 11/1/2017. The licensee information on the self luminous exit sign is that it was a Isolite model SLX60, serial number Y60813, manufactured in 11/2008 with an activity of 7.4 curies of H(3). The licensee continues to investigate this event and has counseled the employee to follow the procedures for these signs. The licensee is planning to put out a general communication on these signs, and for the eventual removal of all the self luminous exit signs. The licensee is preparing a written report. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-04-06
53297 | 0 | EISENHOWER ARMY MEDICAL CENTER |  |  |  |  | 2018-03-28 15:00 | 2018-03-29 10:31 | 2018-03-29 | MISSING I-125 SEED On 3/27/2018, a patient was implanted with a 83 microCi I-125 seed marker in preparation for a breast tumor surgery. Following the surgery on 3/28/2018, at approximately 1500 EDT, the I-125 seed marker went missing. The operating room was surveyed, and the patient was imaged with no discovery of the I-125 seed marker. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.p | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-04-06
53296 | 0 | AUTOMATED PACKAGING SYSTEMS |  |  |  |  | 2018-03-28 | 2018-03-28 15:38 | 2018-03-28 | NOTIFICATION OF A LOST THICKNESS GAUGE The licensee determined today, 3/28/2018, that they had lost an Am-241 thickness gauge source. A few months ago the Am-241 thickness gauge source had been replaced with a non-radioactive thickness gauge source. The licensee had observed the Am-241 thickness gauge source at the plant after it was removed, but when they tried to locate it last week could not find it. They searched the site, including using a radiation detector to search with, and did not locate the Am-241 thickness gauge source. The gauge is an NDC Technologies, probe Model 103, with an Am-241source. The device S/N is 12131, and the source S/N is 7199 LQ with an Assay date of 10/6/1998. No specific source strength was included in the data the licensee had, but they indicated the source strength was low. NDC Technologies license GL-657303-19 indicates the Am-241 source activity is 150 micro Ci. The licensee stated that they are continuing to search for the Am-241 thickness gauge source, and they are preparing a written report. The licensee stated that they have revised their administrative policy for control of radioactive material and are scheduling retaining for their radiation safety officers. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-04-05
53295 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2018-03-28 13:30 | 2018-03-28 14:07 | 2018-03-28 | CONCURRENT REPORT DUE TO DAMAGED TRITIUM EXIT SIGN "At approximately 1330 EDT, 3/28/2018, a report was sent to the State of North Carolina Department of Radiation Protection. The report is below: "'Pursuant to 10A NCAC 15.0309, Global Nuclear Fuel Americas, LLC (GNF-A) is providing this report for discovery of a damaged self illuminated exit sign in the Fuel Manufacturing Operations (FMO) building. On February 26, 2018, it was discovered that one tube out of the twelve originally installed tubes in a generally licensed exit sign was damaged. The sign was in storage and not being used at the time and there was no significant exposure as a result of the event. The sign is believed to be a model number 101 or 201, originally containing a maximum of 25 Ci of tritium manufactured and distributed by: Evenlite, Inc., 220 VFW Avenue.,Grasonville, MD 21638. Arrangements were made to properly dispose of the sign. It was shipped offsite for recovery or disposal on March 23, 2018 to SRB Technologies (NC Radioactive Material License 034-0534-2).' "This report to NRC is being made in accordance with 10 CFR 70 Appendix A (c) - Concurrent Reports (... notifications to other government agencies has been or will be made, shall be reported to the NRC Operations Center concurrent to the news release or other notification.)" The Licensee has notified NRC Region 2. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-04-05
53294 | -1 | UNIVERSITY OF NOTRE DAME |  |  |  |  | 2018-03-28 02:11 | 2018-03-28 02:58 | 2018-03-29 | SUSPICIOUS ACTIVITY REGARDING SECURITY EQUIPMENT AT UNIVERSITY IRRADIATOR BUILDING At 0211 EDT on 3/28/18, an offsite alarm monitoring company notified the Notre Dame Security Police of security cameras being disabled. The University RSO was notified at 0222 EDT that lines to the security camera have been cut. The Notre Dame Security Police verified that there were no attempted or forced entry to the irradiator building, and the lines may have been cut inadvertently for maintenance work. The building houses 3 irradiators of Co-60 sources. * * * RETRACTION ON 3/29/18 AT 0740 EDT FROM ANDREW WELDING TO ANDREW WAUGH * * * The University of Notre Dame determined that there was no hazard because alternate cameras maintained visual contact of the equipment that housed the CAT 1 sources. Notified R3DO (Pelke), ILTAB DO (Whitney), and NMSS Events Notification (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SUSPICIOUS ACT INVOLV CAT 1/2 RAD MATL | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 37.57(b) |  |  |  | 1 | 2018-04-04
53293 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-09-05 | 2018-03-27 15:59 | 2018-03-27 | AGREEMENT STATE REPORT - DELIVERED DOSAGE DIFFERENT FROM PRESCRIBED The following is an excerpt from a report received from the State of Ohio via email: The criteria for a medical event supported by ODH (Ohio Department of Health) is if the 90% prostate volume receives less than 80% of the prescribed dose or more than 120% of the prescribed dose. Upon generating the post treatment plans for nine patients, the Dosimetry staff discovered that four were below 80%. Summary of Prostate Implant Incidents: Case #. Implant Date, Discovery Date, Prescribed Dose (Gy), Estimated D90 (Gy) 1. 9/05/2017, 3/26/2018, 110 Gy, 58.15 Gy 2. 9/28/2017, 3/26/2018, 145 Gy, 100.19 Gy 3. 2/13/2017, 3/26/2018, 110 Gy, 81.28 Gy 4. 2/19/2017, 3/26/2018, 145 Gy, 103.7 Gy Manufacturer: Theragenics Model Number: AgX100 Radionuclide: I-125 Item Number: OH180002 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2018-04-04
53292 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-03-27 | 2018-03-27 14:33 | 2018-03-27 | AGREEMENT STATE REPORT - MISSING SOURCE The following was received from the State of Illinois via email: "On March 27, 2018, the agency [Illinois Emergency Management Agency] was contacted by the licensee's radiation safety officer to report a missing 10 microCi Am-241 source. The source assay date was not immediately available. Reportedly, forms were distributed to the authorized users who would perform the physical inventory. An investigation is ongoing to determine the last physical inventory and responsible individuals. A full report is pending from the licensee by April 26, 2018. A comprehensive source inventory is to be completed within the week. Additional updates will be provided as they become available." Item Number: IL 180024 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-04-04
53291 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-03-26 18:39 | 2018-03-26 20:07 | 2018-03-26 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 1839 Eastern Daylight Time (EDT) on March 26, 2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. "At 1840 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. "At 1840 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO [Limiting Condition for Operation] 3.7.10, Condition B was exited. "The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of Design Basis Accident (DBA) consequences to CRE occupants. From 1839 EDT to 1840 EDT, WBN [Watts Bar Nuclear] was unable to validate that CREVS could fulfill its required Safety Function. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D)." A watch has been posted at the door to prevent recurrence. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-03-26
53290 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2018-03-26 13:38 | 2018-03-26 18:19 | 2018-05-16 | TECHNICAL SPECIFICATIONS REQUIRED SHUTDOWN DUE TO INOPERABLE MAIN STEAM ISOLATION VALVE "On March 25, 2018 at 1833 CDT, while at 100 percent power, Farley Unit 1 (FNP-1) conservatively declared a single Main Steam Isolation Valve (MSIV) inoperable on the 1C Steam Generator line due to indication of Steam Generator pressure rise with a corresponding reduction in flow of that loop. FNP-1 began a reactor shutdown at 0400 CDT on March 26, 2018 to establish plant conditions to support testing the affected main steam line MSIVs while in the required action time of Technical Specification 3.7.2. At 1338 CDT on March 26, 2018, testing confirmed that the single MSIV was inoperable and that valve disassembly will be required. The duration of the valve repair would exceed the required action time of Technical Specification 3.7.2. This report is being made in accordance with 10 CFR 50.72(b)(2)(i), as a plant shutdown required by technical specifications. "The licensee has notified the NRC Resident Inspector." * * * UPDATE FROM DOUGLAS HOBSON TO KEN MOTT AT 0202 EDT ON 5/16/18 * * * "This EN [event notification] is being updated to clarify the reporting criteria as 'Voluntary'. Farley Technical Specification 3.7.2 allows continuous operation in MODE 2 with an INOPERABLE MSIV as long as the other MSIV in the affected Main Steam Line is closed. The initiation of the shutdown was performed as a prudent action to repair and restore OPERABILITY of the affected MSIV and was not a requirement of the Farley Technical Specifications." The licensee notified the NRC Resident Inspector. The R2DO (Masters) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW | [5 empty] | 0 | 2018-03-26
53289 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2018-03-26 10:00 | 2018-03-26 17:02 | 2018-03-28 | AGREEMENT STATE REPORT - STOLEN MOISTURE-DENSITY GAUGE The following is an excerpt from a report received from the State of Nevada: "At 1000 PDT on March 26, 2018, the State of Nevada Radiation Control Program was informed by Aztech Materials and Testing, LLC, that a Humboldt, Model 5001EZ, Serial Number 3491, containing 10 mCi of cesium-137 and 40 mCi americium-241:beryllium, was stolen from the licensee's vehicle. The gauge was secured with two locks in the back of a pickup truck. The State is following the incident and working with local authorities to develop a press release. Local law enforcement and the FBI have been notified. Follow-up information will be provided to NRC on the recovery of the stolen gauge and entered into NMED (Nuclear Material Events Database)." * * * UPDATE FROM JOHN FOLLETTE TO DONALD NORWOOD AT 1730 EDT ON 3/28/2018 * * * The following information was received via E-mail: "The State of Nevada Radiation Control Program has been informed by the Las Vegas Metropolitan Police Department that the stolen portable nuclear gauge has been recovered. Below is the notification: "'All items were recovered in a stolen vehicle (abandoned, no suspects located). Patrol officers will be releasing the items back to Aztech.' "The NMED report will also be updated." Notified R4DO (Gaddy). Notified via E-mail ILTAB (Whitney) and NMSS Events Notification. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2018-04-03
53288 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-03-26 10:58 | 2018-03-26 11:51 | 2018-03-26 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 1058 Eastern Daylight Time (EDT) on March 26, 2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. "At 1100 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. "At 1100 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO [Limiting Condition for Operation] 3.7.10, Condition B was exited. "The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of Design Basis Accident (DBA) consequences to CRE occupants. From 1058 EDT to 1100 EDT, WBN [Watts Bar Nuclear] was unable to validate that CREVS could fulfill its required Safety Function. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D)." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-03-26
53287 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2018-03-25 16:16 | 2018-03-25 23:43 | 2018-04-13 | CONTROL ROD DRIVE PIPING POTENTIALLY INOPERABLE "On March 25, 2018 at 1616 hours [EDT], with the reactor in cold shutdown condition, two control rod drive piping lines were determined to be potentially inoperable in the event of a design basis earthquake due to support defects. The control rod drive piping forms a portion of the reactor coolant pressure boundary and primary containment boundary. "The supports will be repaired prior to plant startup. "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector has been notified." The licensee will notify the Commonwealth of Massachusetts. * * * RETRACTION FROM JOE FRATTASIO TO HOWIE CROUCH AT 1500 EDT ON 4/13/18 * * * "The purpose of the notification is to retract ENS notification 53287 made on 03/25/18 for Pilgrim Nuclear Power Station. The previous notification reported that control rod drive (CRD) piping could be potentially inoperable in the event of a design basis earthquake, at the time of discovery, due to piping support defects. Subsequent evaluation has demonstrated that the piping was not inoperable. "Specifically, after an engineering evaluation, it has been determined that the CRD Hydraulic System operability was never lost and the system was operable, although non-conforming, based on the support configuration not conforming to the pipe support drawings. The affected pipe supports have been restored or reworked to the proper design condition in accordance with the design drawings. The CRD System has subsequently been restored to a fully operable status." Notified R1DO (Jackson) and IRD MOC (Pham). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | UNANALYZED CONDITION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2018-03-26
53286 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-03-23 16:35 | 2018-03-24 01:09 | 2018-03-24 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "This report is made for a loss of Emergency Assessment Capability associated with Emergency Action Levels for Toxic and Flammable Gas and is reportable under 10 CFR 50.72 (b)(3)(xiii). During an emergency equipment inventory it was identified that methods were not available to detect levels of toxic or flammable gas at the IDLH (Immediately Dangerous to Life and Health) level for a number of substances. The IDLH is used to assess the Alert Emergency Action Level. "The ability of the Control Room Staff to detect and respond to the presence of toxic or flammable gas is unaffected. "Because there have been no chemical spills or releases that would require sampling to be performed, the health and safety of the public was not affected. "The NRC Resident Inspector has been notified." The State of Minnesota will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-03-24
53285 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2018-03-23 12:30 | 2018-03-23 21:07 | 2018-03-23 | LOSS OF EMERGENCY ASSESSEMENT CAPABILITY "This report is made for a loss of Emergency Assessment Capability associated with Emergency Action Levels for Toxic and Flammable Gas and is reportable under 10 CFR 50.72(b)(3)(xiii). During an emergency equipment inventory, it was identified that methods were not available to detect levels of toxic or flammable gas at the IDLH (Immediately Dangerous to Life and Health) level for a number of substances due to the detector having an unsuitable range. The IDLH is used to assess the Emergency Action Level Alert Range. "The ability of the Control Room Staff to detect and respond to the presence of toxic or flammable gas is unaffected. "Because there have been no chemical spills or releases that would require sampling to be performed, the health and safety of the public was not affected. "The resident NRC Inspector has been notified." The licensee will be notifying the state of Minnesota. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-03-23
53284 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-09-01 | 2018-03-23 18:36 | 2018-03-23 | AGREEMENT STATE REPORT - LOST AM-241 SOURCE The following information was received via E-mail: "In a letter dated December 20, 2017, the President of Radiology Support Devices (RSD)/Alderson Phantoms reported to the Sacramento office of California Department of Health Services, Radiological Health Branch that 9 (nine) sealed sources were missing. The source activities varied from very low microCi quantities to less than picoCi quantities. It was not recognized that one source met the criteria for immediate reporting until a routine, scheduled inspection by Los Angeles County Radiation Management was performed of RSD. "It was discovered on March 22, 2018 that eight of the nine sealed sources were below the 10 CFR 20 Table C reporting requirements, but one sealed source, 2.89 microCi of Am-241 (North American Scientific; calibration date January 1995, no serial number available) met the NRC 24 hour reportability threshold of 1.0 microCi. "The licensee suspects the sources may have been taken by a previous employee. However, the previous employee has denied taking the sources." California 5010 Number: 032218 Notified Mexican Government Representatives via E-mail. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-04-02
53283 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-03-22 | 2018-03-23 16:49 | 2018-03-23 | AGREEMENT STATE REPORT - RADIOGRAPHY PERSONNEL OVEREXPOSURE The following information was received via E-mail: "On 03/23/18, the Radiation Safety Officer (RSO) (appointed RSO since the merge with TEAM) contacted RHB (California Department of Public Health, Radiologic Health Branch) to report an occupational overexposure to one of their radiographer trainers. On 03/22/18, the licensee was made aware of an overexposure to a trainer when the trainer's instadose dosimeter was processed. The badge reading indicated a whole body exposure of 5769 mR (licensee processes instadose dosimetry every two weeks for all the users). Further investigation revealed that the radiographer assistant that worked with this trainer also received a whole body exposure of 4583 mR. Preliminary investigation indicates the individuals may have received the recorded exposure during radiographic operations conducted at Chevron Refinery, Richmond, CA, where the source apparently may not have been fully retracted into the shielded position following an exposure. It is believed that a confirmatory survey was not performed following the exposure. "The exposure device involved is an INC-IR100 camera, device S/N 6756, with an activity of 88.9 Ci of Ir-192. "Both individuals have been removed from any radiographic operations. The exposure device was inspected and did not show any signs of defects or damages. The licensee's investigation is ongoing and RHB will be following up on this incident. "Note: RHB is in the process of merging the two licenses, Qualspec, LLC and Team Industrial Services RML # 6720." California 5010 Number: 032318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-04-02
53282 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-03-22 | 2018-03-23 12:42 | 2018-03-23 | AGREEMENT STATE REPORT - MISSING TUBE FROM TRITIUM EXIT SIGN The following information was received via E-mail: "Licensee reports that on 3/22/2018 it was determined that a tube from an Everglo Tritium Exit sign was missing. The other three tubes were in the sign. The discovery was made as the sign was being prepared for shipment to disposal. At this time, there is no suspected excessive exposure to employees or members of the public. "Licensee will follow up with additional information [as required] per 10 CFR 20.2201(b). When this report is received by the NC Radioactive Materials Branch, this event will be updated to complete the record." NC Event Tracking Number: 180013 See EN 53279 for corresponding report from licensee. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-04-02
53281 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-03-22 | 2018-03-22 21:47 | 2018-03-22 | AGREEMENT STATE REPORT - BROKEN TRITIUM EXIT SIGN The following is a synopsis of information received via E-mail from the State of California: On March 22, 2018 the Director of Environmental Affairs at NBC Universal (i.e. Universal Studios) in Universal City, California called Los Angeles County Radiation Management to report the discovery of a broken Tritium exit sign. The Tritium sign was subsequently isolated for secure and safe keeping. A Los Angeles County Radiation Management employee will visit Universal Studios on March 23, 2018 to check for Tritium leakage or contamination. The broken sign is a Forever Lite Inc. Tritium sign, S/N 286342, with an expiration date of March 2027, containing 11.21 Curies. California 5010 Number: 032218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-03-30
53280 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-03-22 06:00 | 2018-03-22 15:12 | 2018-03-29 | AGREEMENT STATE REPORT - DISCONNECTED RADIOGRAPHY SOURCE The following is a synopsis of information received via E-mail: On March 22, 2018, LA-DEQ (Louisiana Department of Environmental Quality) received an on-line notification that CAN USA Inc. had an incident where a radiography source was irretrievable during operations at a temporary jobsite at the Phillips 66-Alliance Refinery in Belle Chase, LA. The crew stated they had made an exposure and were performing their post-job survey when the survey meter indicated the source was not in the shielded position. The radiography crew realized the source could not be retracted back into the shielded position and called the assistant RSO (Radiation Safety Officer) for radiation safety assistance. The assistant RSO arrived at the jobsite at 0615 CDT. The assistant RSO covered the source in the guide tube with lead shot bags to reduce the exposure during the retrieval operation. It was determined that the guide tube had disconnected from the exposure device. The guide tube was reconnected, the source was returned to the shielded position, and an investigation into this incident begun. The assistant RSO completed the retrieval work at approximately 0645 CDT. The assistant RSO's direct read pocket dosimeter had an exposure of approximately 60 mR. The exposure device and associated equipment (crankout control and source guide tube) were taken to the CAN USA facility for further evaluation. The equipment is a QSA Global Model 880 Delta exposure device, S/N D9222, utilizing a 70.7 Ci Ir-192 source, S/N 63452-G. An internal investigation continues into this irretrievable source incident. Louisiana Event Report ID No.: LA-180005 * * * UPDATE AT 1730 EDT ON 3/29/18 FROM JOE NOBLE TO JEFF HERRERA * * * The following update was submitted by the Louisiana Department of Environmental Quality via email: "Updated information: "A source retrieval has developed into a situation involving, licensed activities, equipment QC/QA practices and personnel qualifications. "QSA Global Delta 880, S/N D9222; source [approximately] 70 Ci of Ir-192 s/n 63452-G Associated Equipment: 3rd party, drive cable and source guide tube. (not Amersham/QSA Global manufactured equipment) The connector did not appear to be compatible with the exposure device source assembly in the Delta 880 device. (excessive use) A misconnect/disconnect test was not performed on the source assembly and 3rd party associated equipment (drive cable and guide tube). Assessment and Evaluation: the exposure device and associated equipment were transferred to QSA Global, Baton Rouge, LA then to QSA Global Burlington, MA. "CAN USA Inc. was not licensed to perform source retrievals nor did they contact a 'qualified licensed radiation service' company to perform the source retrieval. The Corporate RSO, [deleted] was available by telephone. There was no site/assistant RSO trained or qualified to perform the source retrieval. "Disconnect happened on a 15 foot elevated catwalk [at] an Aromatics Extractor unit # 1797. The facility, Phillips 66-Alliance, [deleted]. Phillips 66-Alliance Contact: [deleted], EHS Officer "Personnel: CAN USA: Two Radiography Instructors were directly involved in the source retrieval. Two Carded Radiographers were working with the equipment when it disconnected on the first exposure. Provided Pocket Dosimeter readings 'provided' were 8 mR, 30 mR, 40 mR and 70 mR. Landaure whole body badges immediately processes for three individuals, with the Maximum exposure 290 mrem. The acting site RSO, [deleted] whole body badge is 'lost' in the system. The individuals involved in the source retrieval are having cytogenetic/chromosomal blood sample analysis by REACTS Medical Dosimetry Dept./ORISE.ORAU; results pending. "Analytical Stress Employees. Three non-radiation workers were evacuated from the vicinity of the disconnected source and evaluated by blood sample analysis. "SWAT Specialty Welding and Turnaround: One non-radiation worker was evacuated from the vicinity of the disconnected source and evaluated by blood sample analysis. "The Departmental [Louisiana Department of Environmental Quality] investigation is still incomplete depending on assessment, evaluation and analysis results." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-03-30
53279 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2018-03-22 | 2018-03-22 16:58 | 2018-03-22 | CONCURRENT REPORT DUE TO LOST TRITIUM EXIT SIGN TUBE "At approximately 1645 EDT on 3/22/2018, a report was made to the State of North Carolina Department of Radiation Protection. The report is below: "At approximately 1600 EDT on 3/22/2018 it was determined that a tube from an Everglo Tritium Exit sign was missing. The other three tubes were in the sign. The discovery was made as the sign was being prepared for shipment to disposal. This report is being made in accordance with 10A NCAC 15.1645(a). There is no suspected excessive exposure to employees or members of the public. "This report to NRC is being made in accordance with 10 CFR 70 Appendix A(c) - Concurrent Reports, '... notification to other government agencies has been or will be made, shall be reported to the NRC Operations Center concurrent to the news release or other notification.'" See EN 53282 for corresponding report from the State of North Carolina. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2018-03-30
53278 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-03-22 | 2018-03-22 10:48 | 2018-03-22 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER FAILED CLOSED The following information was received via E-mail: The licensee reported on 3/22/2018 that the spring for the shutter cable on a Texas Nuclear Corporation (now TN Technologies) Model 5197 fixed nuclear gauge broke. The shutter is closed and surveys have been taken showing no leakage. The licensee has contacted the manufacturer who will dispatch technicians to repair the device. Oklahoma Department of Environmental Quality will update this report when more information is known. * * * UPDATE FROM JENNIFER MCALLISTER TO DONALD NORWOOD AT 1536 EDT ON 3/22/2018 * * * The following information was received via E-mail: The event occurred on 3/15/2018. The source is a TN Tech. Model 57157C, 100 mCi, Cs-137 source. The Serial Number of the gauge is B919. Notified R4DO (Groom) and NMSS Event Notifications. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-03-30
53277 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-03-21 15:50 | 2018-03-22 09:31 | 2018-03-22 | FITNESS FOR DUTY TEST SUBVERSION A non-licensed contract supervisor attempted to subvert a random Fitness For Duty test using a subversion kit on their person. The employee's access to the plant has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-03-22
53276 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2018-03-22 03:00 | 2018-03-22 07:07 | 2018-03-22 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO PRESSURE BOUNDARY LEAKAGE "This notification is being provided in accordance with 10CFR50.72(b)(2)(i), Plant Shutdown required by Technical Specifications, and 10 CFR 50.72(b)(3)(ii)A, Degraded or Unanalyzed Condition. "At 0300 CDT on 3/22/18, on LaSalle Unit 1, a through-wall (welded joint) leak was identified on a 3/4 inch vent line off of the bonnet of the 1B33-F067B, 1B Reactor Recirculation Pump Discharge Valve. This condition qualifies as pressure boundary leakage, which requires entry into Technical Specification 3.4.5, Reactor Coolant System Operational Leakage, Required Action C, to be in Mode 3, Hot Shutdown, by 1500 on 3/22/18 and Mode 4, Cold Shutdown, by 1500 on 3/23/18. This leakage is significantly less than 10 gallons per minute and therefore, does not meet the threshold for entry into the Emergency Action Plan. At the time of discovery, Unit 1 was in Mode 1 - Run." Shutdown began at 0500 CDT and the estimated completion to cold shutdown is 2000 CDT. All necessary shutdown equipment is available. There is no impact to Unit 2. NRC Resident Inspector was notified. | 19 | 100 | 0 | 24 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2018-03-22
53275 | 0 | 3M CORPORATE |  |  |  |  | 2018-03-21 03:00 | 2018-03-21 17:04 | 2018-03-21 | GAUGE SHUTTER MALFUNCTION "On March 21, 2018, at approximately 0300 CDT the shutter on an industrial beta transmission gauge malfunctioned and did not immediately close when commanded to do so. Facility maintenance personnel were able to get the shutter to fully close. The gauge was taken out of service. At approximately 0800 CDT the facility maintenance technician with the most experience working with radiation gauges inspected the device and found that the shutter opened properly, but would not fully close. The licensed service provider under contract to the facility was contacted and provided advice to the facility technician so that the shutter could be fully closed. The facility Radiation Safety Officer verified that the shutter was fully closed using a portable radiation survey meter. Electrical power to the device was locked out to prevent use. The gauge manufacturer was contacted to provide advice and to provide a replacement shutter assembly to be installed by the licensed service provider that the facility uses for more extensive maintenance on radiation gauges. "Isotope, quantity, chemical and physical form: "Kr-85, 1000 millicuries on January 8, 2007, encapsulated sealed source, serial number 05-709, QSA Global model KAC.D1, in LFE model SULP-77A beta thickness gauge, serial number 9281 "The event resulted in no radiation exposure to any individual." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-03-29
53274 | 0 | GENERAL ELECTRIC OF PLEASANTON |  |  |  | 100 KW NTR (TANK) | 2018-03-19 11:30 | 2018-03-20 09:52 | 2018-03-20 | TEST AND RESEARCH REACTOR - NOTIFICATION OF TECHNICAL SPECIFICATION VIOLATION At 1130 PST on 3/19/18, with the reactor at 100% power (100 kW thermal), GE Hitachi Vallecitos Nuclear Test Reactor violated their Technical Specifications (NDO 32765, section 6.1.3.1) when the licensed reactor operator became sick, called for the backup licensed reactor operator, and left the control room. The backup licensed operator entered the control room less than 30 seconds after the other operator left. There were other trained but unlicensed operators in the control room. The reactor remained at 100% power with no issues. This notification is the 24 hour notification required in accordance with GE Hitachi Vallecitos Nuclear Test Reactor Technical Specifications (NDO 32765, section 6.1.3.1). The Technical Specifications also require a 14 day written report which will be submitted. The facility has initiated a corrective action report (28168). GE Hitachi Vallecitos Nuclear Test Reactor, license R-33, is a 100 kW thermal Light Water Highly Enriched Graphite Moderated Reactor. The licensee notified their NRC Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | CA | NPR | [5 empty] | 0 | 2018-03-20
53273 | 0 | RAPID CITY REGIONAL HOSPITAL |  |  |  |  | 2018-03-08 | 2018-03-19 16:43 | 2018-03-19 | MEDICAL EVENT INVOLVING DELIVERED DOSE 50 PERCENT LESS THAN PRESCRIBED DOSE A patient was prescribed 8 fractions of 500 cGy to the temple area. During the third fraction, the physician noticed the first two fractions were performed incorrectly. The first two fractions were performed with an incorrect setup, and the patient received less than 50 percent of the prescribed dose to the temple. The Radiation Safety Officer will provide a detailed written report after an investigation. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-03-27
53272 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2018-03-19 09:30 | 2018-03-19 13:09 | 2018-03-19 | TECHNICAL SUPPORT CENTER OUT OF SERVICE "Emergency Assessment Capability cannot be performed in the Technical Support Center due to an equipment deficiency in the HVAC system which could impact facility habitability. An Alternate Technical Support Center is in place at the Emergency Offsite Facility. Priority maintenance is in progress to correct the deficiency." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-03-19
53271 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-03-19 03:29 | 2018-03-19 10:49 | 2018-03-19 | UNPLANNED ACTUATION OF AUXILIARY FEEDWATER SYSTEM DURING MAINTENANCE "Automatic actuation of the 2B CA (Auxiliary Feedwater) System. At 0329 [EDT on] 03-19-18, with Unit 2 in Mode 5, an actuation of the 2B CA (Auxiliary Feedwater) system occurred during maintenance associated with the 2B Main Feedwater Pump. "The cause of the CA (Auxiliary Feedwater) system automatic start was an unanticipated reset and subsequent trip signal of the 2B Main Feedwater pump during maintenance activities. The 2B CA Pump/Train automatically started as designed when the 'Loss of Both Main Feedwater Pumps' signal was received. The system operated as required. This event is being reported in accordance with 10CFR 50.72(b)(3)(iv)(A) as an event that results in a valid actuation of the CA System. There was no impact on the health and safety of the public or plant personnel. "The NRC Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-03-19
53270 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-03-19 00:30 | 2018-03-19 02:27 | 2018-03-19 | TWO CONTRACTORS INJURED BY ARC FLASH "On 3/16/2018 at approximately 1630 EST, an industrial safety accident occurred at Sequoyah Nuclear Plant that involved an Arc Flash injury of two contract employees. While performing work near a non safety related 6.9kV electrical bus, an arc occurred injuring the two employees. Both personnel were transported to an offsite medical facility for treatment. Neither were contaminated. "The cause of the arc flash is not understood at this time, an accident investigation has been initiated by TVA. The SQN [Sequoyah Nuclear] NRC Senior Resident Inspector has been notified. No safety related systems required to establish or maintain safe shutdown were affected. Both Unit 1 and 2 remain at 100 [percent] power. "TVA has received and responded to media inquiries concerning this event. As a result, this event is considered reportable under 10CFR50.72(b)(2)(xi)." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-03-19
53269 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-03-18 11:58 | 2018-03-18 16:16 | 2018-03-18 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE CONTROL VALVE CLOSURE "At 1158 CDT on March 18, 2018, the Unit 1 reactor automatically scrammed due to a Reactor Protection System (RPS) signal generated from High Reactor Steam Dome Pressure in response to Turbine Control Valve Closure. The reactor had been operating at 100 percent power. Investigation is in progress. "All control rods fully inserted into the core. Main Steam Isolation Valves remained open with Main Steam Relief Valves (MSRVs) operating on the initial transient as expected. Main Turbine Bypass Valves are currently controlling reactor pressure. Reactor Feedwater pumps remained in service to control reactor water level. "Primary Containment Isolation Signals Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. All safety system operated as expected. At no time was public health and safety at risk. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation' and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A)." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-03-18
53268 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP,[3] M-4-LP | 2018-03-17 20:07 | 2018-03-18 12:34 | 2018-03-18 | FITNESS-FOR-DUTY REPORT INVOLVING DISCOVERY OF KOMBUCHA TEA INSIDE THE PROTECTED AREA "At 2007 [EDT] on 3/17/18, a security Officer reported finding a container of herbal tea (Kombucha) on a platform in the Unit 1 Emergency Switchgear Room, which is located inside the Protected Area. Kombucha tea is a fermented tea containing trace amounts of alcohol, and is legally sold without restrictions. Dominion had previously notified its workforce that Kombucha tea was prohibited from being consumed or carried on-site. This is considered an alcoholic beverage and is being reported under the requirements of 10 CFR 26.719. "The individual who brought the beverage on-site was identified and escorted out of the Protected Area." The NRC Resident Inspector has been notified. The licensee will also be contacting the County Administrator for Louisa County, Virginia. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2018-03-18
53267 | -1 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-03-16 | 2018-03-16 22:04 | 2018-11-29 | UNANALYZED CONDITION AFFECTING RESIDUAL HEAT REMOVAL SYSTEM "At 1604 [CDT] on March 16, 2018, Browns Ferry Nuclear Plant (BFN) Engineering reported an unanalyzed condition affecting the Residual Heat Removal (RHR) heat exchangers in a postulated fire event. It was discovered that the Residual Heat Removal Service Water (RHRSW) heat exchanger piping associated [with] the credited heat exchangers in the NFPA 805 Nuclear Safety Capability Analysis (NSCA) could experience water hammer damage. "Fire damage to the cables for the RHRSW outlet motor operated valves could cause the valves to spuriously open and drain the RHRSW piping. Subsequent starting of the RHRSW pumps on the affected header could cause water hammer loads and damage the piping. "Review of NFPA 805 analyses show the cables associated with this condition are routed in Fire Areas 01-03, 02-03, 02-04, 03-03, 16 and 23. There are 11 cases where the deterministically credited heat exchanger could be affected. "Compensatory fire watch measures have been established. "This event requires an 8 hour report in accordance with 10CFR50.72(b)(3)(ii)(B), 'Any event or condition that results in: (B) The nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "CR 1139620 documents this condition in the Corrective Action Program." The NRC Resident Inspector has been notified. * * * RETRACTION AT 2215 EST ON 11/29/2018 FROM NEEL SHUKLA TO MARK ABRAMOVITZ * * * "NRC notification 53267 was made to ensure that the eight-hour non-emergency reporting requirements of 10 CFR 50.72 were met when the licensee discovered an unanalyzed condition with the potential to significantly degrade plant safety. "On August 22, 2018, an independent analysis was completed which determined that the RHRSW system would remain functional during the postulated scenario. Based on this analysis, a revised functional evaluation was performed by BFN which determined that the condition did not constitute an unanalyzed condition that significantly degraded plant safety. For credited RHR heat exchangers for fire events in Fire Areas 01-03, 02-03, 02-04, 03-03, 16, and 23, the RHRSW piping will remain intact and the valves will operate manually after a water hammer event. This condition did not significantly degrade plant safety and is therefore not reportable under 10 CFR 50.72(a)(2)(ii)(B). "On November 16, 2018, TVA canceled the 60 day report which had been submitted for this condition. "TVA's evaluation of this event notification is documented in the corrective action program. "The licensee has notified the NRC Resident Inspector." Notified the R2DO (Shaeffer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-03-16
53266 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2018-03-15 11:30 | 2018-03-16 11:16 | 2018-03-16 | UNANALYZED SCENARIO ASSOCIATED WITH URANIUM RECOVERY AND RECYCLE SYSTEM "On March 15, 2018 during an NRC inspection of the Solvent Extraction area, an inspector identified a potential credible scenario which is not adequately addressed in the applicable Criticality Safety Evaluation (CSE). Plant Environmental Health and Safety (EH&S) staff reviewed the issue and at 1130 [EDT] determined that, based on the available information, the scenario did not appear to be properly analyzed in the CSE and thus the Integrated Safety Analysis (ISA). The scenario is associated with the Uranium Recovery and Recycle System (URRS) 706 hood operation. The process performed in the 706 hood is the transfer of low concentration residues into a container for disposal at a Low Level Radioactive Waste (LLRW) facility. There was no actual event, and no impact to public health and safety, the workers, or the environment. "The issue revolves around the lack of a specific analysis controlling the handling, transport and replacement of the container, a 55 gallon drum, used in that process. A criticality event for the scenario of an inadvertent container handling upset was identified as incredible in the safety basis documents. However, the accident sequence does not meet the definition of incredible as defined in the license application, and thus appears to be an improperly analyzed scenario. "While not properly documented, unlikely, independent, and concurrent changes in process conditions would have to occur to result in a criticality accident. Procedural controls and process barriers which are in place were not identified as Items Relied On For Safety (IROFS) for this scenario. There are, however, passive and administrative IROFS in place for other chemical, fire and criticality safety accident sequences that can be applied to this scenario. These IROFS include requirements for mechanical integrity and spill protection techniques to preclude significant loss of uranium bearing liquid material that would have to accumulate in an improperly handled container. Examples of existing IROFS that control process leaks include SOLX-903 and WASH-119, degradation resistant design to prevent leakage from tanks/vessels; SOLX-503, structural integrity of piping; ADUHNP-901, flange guards; ADUHFS-507 and SOLX-505, valve alignments to prevent spills; and DPH-104, piping integrity. In addition, there is annual training and testing on the proper handling of non-favorable geometry containers. "The hood and associated container were removed from service while the scenario is being evaluated. Issue Report 2018-7306 was entered into our Corrective Action Program, and an extent of condition was performed." Based on the extent of condition, the cylinder wash area has been identified for additional evaluation. * * * UPDATE ON 3/16/18 AT 1643 EDT FROM NANCY PARR TO DAVID AIRD * * * "Based on evaluation of the extent of condition, a similar scenario was identified with the wet combustible trash system in the Uranium Recovery and Recycle System (URRS) area. This event report is updated to include a 24 Hour Event Notification for the wet combustible trash system based on 10 CFR 70 Appendix A(b)(1) 'Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of 10 CFR 70.61.' "The issue revolves around the lack of a specific analysis controlling the handling and transport of containers, 55 gallon drums, used in the wet combustible trash process. A cylinder wash operation is in the area where the wet combustible trash drums are used. Cylinder wash operations were shutdown to preclude significant loss of uranium bearing liquid material that would have to accumulate in an improperly handled drum. Similar procedural controls, process barriers and IROFS from other accident sequences can be applied to this scenario. Wet combustible trash collection may continue since the potential source of liquid material (cylinder wash) has been shut down." Notified R2DO (Nease) and NMSS (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2018-03-16
53265 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2018-03-15 15:24 | 2018-03-15 22:08 | 2018-03-15 | FAILURE TO MEET APPENDIX R REQUIREMENTS "At 1524 [EDT] on Thursday, March 15, 2018, Operations was notified of a failure to meet Appendix R requirements for Peach Bottom Atomic Power Station (PBAPS) Unit 2 and Unit 3. Valves associated with the feedwater system for both units were not properly considered as Hi-Lo Pressure interface valves as required by the Appendix R program. This results in the susceptibility to a hot short condition that could open valves, diverting flow from the reactor, damage piping and prevent injection. U3 [Unit 3] Fire Safe Shutdown Credited Reactor Core Isolation Cooling (RCIC) System is affected. U2 [Unit 2] is affected by a potential leak path through the Reactor Water Cleanup system. "This event is being reported as an occurrence of an event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety under 10 CFR 50.72(b)(3)(ii). "The Station [PBAPS] is performing hourly fire watches for the impacted areas and is also evaluating this condition for corrective action." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-03-15
53264 | 0 | TUV SUD AMERICA |  |  |  |  | 2018-02-19 | 2018-03-15 15:57 | 2018-03-15 | RADIOGRAPHY SOURCE STUCK IN SOURCE TUBE On 2/19/2018, a crew was performing work at the Phillips 66 Refinery in Billings, Montana. While moving the source into the open position, a loud noise was heard originating from the exposure set up area. The crew immediately attempted to crank the source back into the fully shielded position, but the attempt was unsuccessful. It was determined that the part to be inspected had tipped over and fallen onto the source tube, resulting in a crimp which prevented the source from being retracted into the fully shielded position. The source was shielded with lead plates, the crimp reduced, and the source successfully retracted into the fully shielded position. No members of the general public were exposed to any radiation and no workers received a dose exceeding the limit for personnel working with radiation sources. The source tube involved in this incident has been removed from service and destroyed. The exposure device involved in this incident has been inspected, checked for proper functionality, found to be in working order, and returned to service. The device was a QSA 880D exposure device containing an Iridium-192 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2018-03-23
53263 | 0 | ROSEMOUNT NUCLEAR |  |  |  |  | 2018-03-08 | 2018-03-15 10:54 | 2018-03-15 | PART 21 NOTIFICATION - DEFECT REGARDING CERTAIN PRESSURE TRANSMITTERS AND AMPLIFIER CIRCUIT CARD ASSEMBLIES The following notification is an excerpt from the received report: "Pursuant to 10 CFR Part 21, section 21.21(b), Rosemount Nuclear Instruments, Inc. (RNII) is writing to inform you that a total of eleven (11) Model 1154 and 1154 Series H output range code 4 pressure transmitters whose model code includes special option suffix N0026 or N0087 and five (5) 01154-0153-0002 Amplifier Circuit Card Assemblies may not calibrate at all the published values. "Name and address of the individual providing the information: Mr. Gerard Hanson Vice President & General Manager Rosemount Nuclear Instruments, Inc. 8200 Market Blvd Chanhassen, MN 55317 "Nature of the failure and potential safety hazard: During evaluation of two returned 01154-0153-0002 Amplifier Circuit Card Assemblies (CCAs), it was observed that a single resistor (R316) on each affected Amplifier CCA had an incorrect resistance value. "The N0026 and N0087 special options enable a standard upper range limit (URL) of a transmitter with output range code 4 to be increased from 150 inches water to 210 inches water, in combination with a minimum span of 75 inches water. This R316 resistor allows the transmitter to achieve performance specifications, calibration ranges, and spans as indicated by the special option drawing. "In the sub-assembly process, the R316 resistor on a standard Amplifier CCA is replaced to create a new Amplifier CCA part number (01154-0153-0002). The R316 resistor enables the standard lower range limit (LRL) of a transmitter with output range code 4 to be decreased from -150 inches water to -210 inches water (negative pressure values imply pressure applied to the low-pressure side of the transmitter), in combination with a minimum span of 75 inches water. This R316 resistor allows the transmitter to achieve performance specifications, calibration ranges, and spans as indicated by the special option drawing. "The new resistor's material traceability information is recorded on the traveler. In final assembly, each transmitter with special option suffix N0026 and N0087 is assembled using one of these 01154-0153-0002 Amplifier CCAs. It then receives a factory calibration check at 135 inches water to 210 inches water and customer specified calibrated range, to ensure conformance to the minimum span and maximum URL specifications, as defined by the special option drawing. Appropriate manufacturing paperwork is used to document and record each Amplifier CCA serial number, as well as each final assembly transmitter. "To meet site specific application requirements, transmitters may be field recalibrated to different upper and lower range values and/or spans. Model 1154 and 1154 Series H transmitters with special option suffix N0026 or N0087 and Amplifier CCAs whose R316 resistors were not replaced during the sub-assembly process, will have incorrect resistance values and may not calibrate to all upper and lower range values and/or spans published for the applicable special option. However, if an affected transmitter has been successfully calibrated, having the incorrect resistance value will not adversely affect transmitter performance specifications during normal operation or accident conditions. "The manufacturing records for the two returned Amplifier CCAs, part number 01154-0153-0002, were carefully reviewed. The sub-assembly traveler lacked the required material traceability information, indicating that the R318 resistors were not replaced. RNII reviewed all sub-assembly travelers for part number 01154-0153-0002. The issue has been isolated to one lot which included (16) Amplifier CCAs. "On March 8, 2018, RNII concluded that a substantial safety hazard may exist. "The corrective action which has been taken; the name of the individual or organization responsible for that action; and the length of time taken to complete that action: "(a) RNII previously discontinued manufacturing 01154-0153-0002 Amplifier CCAs, there are no Amplifier CCAs currently in production or finished goods. "(b) RNII examined all manufacturing paperwork for all 01154-0153-0002 Amplifier CCAs, and other than the single lot of (16) Amplifier CCAs described above, no additional discrepancies were found. "Any advice related to the potential failure of the item: The end user is advised to determine the impact of this potential non-conformance on its plant operations and safety and take action as deemed necessary. Affected 01154-0153-0002 Amplifier CCA(s) and transmitter(s) can be returned to RNII for rework. Contact RNII to facilitate the return process. "If there are any questions, or you require additional Information related to this issue, please contact: Mike Dougherty (206) 665-1112, Paul Schmeling (952) 949-5359, or Brian VanderWoude (952) 949-5207. "Shipped as piece parts (P/N 01154-0153-0002) to Arkansas Nuclear One and Waterford. "Shipped as part of transmitter (N0026 and N0087) to Palo Verde, St. Lucie, and Calvert Cliffs." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-03-15
53262 | 0 | NEXTERA ENERGY - INTEGRATED SUPPLY |  |  |  |  | 2018-01-16 | 2018-03-15 09:22 | 2018-03-15 | PART 21 NOTIFICATION - INADEQUATE DEDICATION OF RELAYS "On March 13, NextEra Energy completed its evaluation of a deviation concerning relays dedicated at its Corporate Procurement Engineering & Dedication Facility and concluded that the condition represented a defect under 10 CFR 21. "The defect was discovered on January 16, 2018 during pre-installation bench testing. During that bench test, some of the relays exhibited contact chatter. Upon review of the dedication, it was identified that contact chatter had been noted at reduced voltage, and that the condition was improperly dispositioned as acceptable. That conclusion was incorrect as the relays are DC powered and may be required to operate under reduced voltage conditions. "The affected relays were supplied to the Seabrook Nuclear Power Station. None of those relays were installed and all have been quarantined to prevent installation. "Dedicating Entity: NextEra Energy Integrated Supply Chain - Corporate Procurement Engineering & Dedication Facility, West Palm Beach, FL "Device: GE Relay, base model CR120BD" NextEra expects to complete their evaluation by April 14, 2018. For additional information please contact: Albert Lafleur, (561) 845-3343, al.lafleur@fpl.com | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-03-15
53261 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-03-14 17:11 | 2018-03-15 01:39 | 2018-03-19 | <br><br>EN Revision Imported Date : 03/20/18<br><br>EN Revision Text: LOSS OF EMERGENCY NOTIFICATION TONE ALERT RADIO SYSTEM "At approximately 1711 CDT on 14 MAR 2018, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in event of an emergency condition. This condition is reportable under 10CFR50.72(b)(3)(xiii). A backup notification method is available and will be utilized for notifications if needed. "The local telephone company is providing troubleshooting and repair services. A return to service time for the Shubert tower is not currently available. "The NRC Senior Resident Inspector has been informed." The issue was identified during periodic maintenance. The licensee notified all counties within the 10 mile Emergency Planning Zone. * * * UPDATE ON 3/19/2018 AT 1720 EDT FROM STEVE WHEELER TO DONG PARK * * * "This is a follow up notification to update the status of the Shubert radio transmission tower that was reported to be out of service on March 14th per EN53261. The tower was restored to service and determined to be functional at 0759 [CDT] on March 19th, 2018." The licensee notified the NRC Resident Inspector. Notified R4DO (Groom).<br><br> Original EN Text: LOSS OF EMERGENCY NOTIFICATION TONE ALERT RADIO SYSTEM "At approximately 1711 CDT on 14 MAR 2018, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in event of an emergency condition. This condition is reportable under I0CFR50.72(b)(3)(xiii). A backup notification method is available and will be utilized for notifications if needed. "The local telephone company is providing troubleshooting and repair services. A return to service time for the Shubert tower is not currently available. "The NRC Senior Resident Inspector has been informed." The issue was identified during periodic maintenance. The licensee notified all counties within the 10 mile Emergency Planning Zone. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-03-15
53260 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2018-03-13 | 2018-03-14 09:34 | 2018-03-14 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR TESTED POSITIVE FFD TEST A non-licensed contract supervisor had a confirmed positive for illegal drugs during a pre-access drug test. The individual's access has been denied. The NRC Resident Inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.719 |  |  |  | 0 | 2018-03-14
53259 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2018-03-13 10:00 | 2018-03-13 15:54 | 2018-03-13 | OFF-SITE POWER UNAVAILABLE DUE TO WINTER STORM "On March 13, 2018 at 1000 hours [EDT], with the reactor in Cold Shutdown condition, both 345kV incoming power lines and 23 kV Shutdown Transformer became unavailable during the Northeast winter storm. Per procedures, the emergency on-site emergency power supplies (Emergency Diesel Generators) were running and providing power to essential systems. In addition, the back-up Diesel Air Compressor was in service and one Reactor Protection System bus was on the back-up power supply prior to the loss. "With both 345kV incoming power lines and 23 kV Shutdown Transformer unavailable, Pilgrim Nuclear Power Station procedures direct a report be made to the NRC per the requirements of Title 10 Code of Federal Regulations 50.72(b)(3)(v), any event that could have prevented the fulfillment of the safety function. No actual loss of safety function has occurred since the on-site emergency power supplies are maintaining the reactor in a safe shutdown condition and removing residual heat. "The loss of incoming power is under investigation. "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2018-03-13
53258 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2018-03-13 09:30 | 2018-03-13 12:27 | 2018-03-13 | NORTH CAROLINA AGREEMENT STATE REPORT - PACKAGE EXCEEDED REGULATORY RADIATION LIMITS FOR TRANSPORTATION The following information was received from the state of North Carolina via email: "A North Carolina licensee reported the receipt of a package exceeding the limits as defined in 10 CFR 20.1906(d)(2) and 10 CFR 71.47; direct contact readings of the package greater than 200 mR/hr. Origination of the package was: Laguna Verde Power Station in Mexico and the final carrier: Tristate, has been notified. "Licensee reports that the package exceeding the limits was not designated as Exclusive Use on the bill of lading. At this time, it appears to be a manifest error on the part of Laguna Verde Power Station, Radiation Protection. Licensee followed their internal procedures for the handling of packages designated as Exclusive Use when initial surveys of the received package exceeded the limits in 71.47. Licensee reports that carrier Tristate; handles all shipments to the licensee's location as Exclusive Use. "At this time, no public health and safety issues have been identified. It was determined through initial licensee surveys that the driver for this shipment did not receive a dose exceeding the limits and no other product was being transported or offloaded with this shipment. "NC Radiation Protection Section has initiated an investigation and will be responding on-site. Follow up details will be forwarded to the NRC as appropriate following the outcome of this investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2018-03-21
53257 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2018-03-12 | 2018-03-12 15:10 | 2018-03-12 | FLORIDA AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE TO AN EXTREMITY The following information was received from the state of Florida via email: "TLD work record of employee from interval Feb. 26 - March 4, 2018 was received and examined, indicating an acute dose to right hand of 68.8 R and 2.9 R to left hand. [The licensee RSO] is conducting an investigation to determine authenticity of dose or potential other cause. [The licensee RSO] requests all site visits be coordinated through the corporate office in Tennessee. They will fly a representative to meet with BRC [Florida Bureau of Radiation Control] personnel. Per BRC SOP1, Abnormal Occurrence Criteria, this does NOT constitute a reportable event to NRC as it is less than 250 R to extremity." The event occurred at the licensee's Ft. Lauderdale, FL location. The State only provided the licensee's Tennessee license number. The licensee employee was exposed to Flourine-18. Florida Incident Number: FL18-028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-03-20
53256 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-03-12 06:53 | 2018-03-12 14:34 | 2018-03-12 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR TESTED POSITIVE FOR ALCOHOL A non-licensed supervisor tested positive for alcohol during pre-access screening. The individual's access to the plant was denied. The NRC Resident Inspector has been notified. | 84 | 100 | 0 | 84 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2018-03-12
53255 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-03-10 15:15 | 2018-03-12 13:54 | 2018-03-12 | LOUISIANA AGREEMENT STATE REPORT - LOST IRIDIUM-192 SOURCE The following information was received from the state of Louisiana via email: "On March 10, 2018, at approximately 3:15 pm [CST], [the RSO of Alpha-Omega Services, Inc.] contacted the Department [Louisiana Department of Environmental Quality] to inform us that [the common carrier] had not delivered an HDR Radioactive Sealed Source to Lancaster General Suburban Hospital (LGSH), Lancaster, PA 17604. "The shipping date from Alpha-Omega Services in Vinton, LA. was 02/26/2018. The source has not been delivered to LGSH. On March 10, 2018, [the RSO] for [the common carrier] communicated to [Alpha-Omega's RSO], they could not locate the source in the tracking system or in the Memphis, TN hub. It needed to be reported as lost or missing to the NRC. On 03/12/2018, the source has not been located. "The Ir-192 source is a GammaMed 232, 383 GBq, (10.4 Ci), S/N 24-01-6226-001-020818-12254-81, Transportation Index - 6." Louisiana Event Report ID No.: LA-180004 THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-03-20
53254 | 0 | LACROSSE | 1 |  |  | [1] AC (ALLIS CHAMBERS) | 2018-03-13 | 2018-03-12 11:59 | 2018-03-12 | PRESS RELEASE PLANNED "LacrosseSolutions is preparing to issue a short press release related to the detection of tritium above background levels detected in site groundwater sampling wells. Following is a summary of the release: "The LACBWR [LaCrosse Boiling Water Reactor] site contains a network of industrial groundwater monitoring wells. Analytical results from a routine sampling event on December 28, 2017, indicated above background levels of tritium in the monitoring well closest to the reactor building. All wells sampled in December were resampled on February 14, 2018. From that sampling event, one additional well resulted positive for tritium. "The monitoring well closest to the reactor building has a tritium concentration equivalent to the EPA limit for drinking water. No other radionuclides were found in the groundwater monitoring wells. EnergySolutions is using Haley & Aldrich, a national environmental consulting firm experienced in this area, to assist EnergySolutions in further testing and development of a groundwater monitoring plan to monitor the source of the tritium. "On March 6, 2018, Dairyland Power Cooperative directed their employees working at the coal plant next to LACBWR to switch to bottled drinking water instead of well water until more information is known about the source of tritium. This was a prudent and cautious step to address any concerns employees may have. The drinking water wells draw water from a much deeper depth than the groundwater that is approximately equal to the river height. No radionuclides were detected in the drinking water levels above background. "The State of Wisconsin and the federal Nuclear Regulatory Commission were briefed and are closely following the issue." The licensee has been communicating with NRC R3 (Edwards) and NRC HQ (Vaaler) since the initial sampling event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-03-12
53253 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2018-03-10 07:09 | 2018-03-10 13:54 | 2018-03-10 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "HPCI [High Pressure Coolant Injection] was removed from service (unplanned) on 3/10/2018 at time 0709 [CST] by closing HPCI-MO-15, STEAM SUPPLY INBOARD ISOLATION. The inboard steam supply isolation valve is inside Primary Containment. The steam supply valve was closed in an effort to isolate [unidentified] leakage to Primary Containment from a suspected packing leak from HPCI-MO-15. After closing the HPCI-MO-15, Reactor Coolant System Leakage parameters returned to within Technical Specification [TS] LCO [Limiting Condition of Operations] 3.4.4 limits. "Entered into Technical Specification LCO 3.5.1 Condition C - HPCI System Inoperable. "Required Actions for Condition 'C' are to verify by administrative means RCIC [Reactor Core Isolation Cooling] System is operable within 1 hour and restore HPCI System to operable status within 14 days. RCIC was verified operable by administrative means concurrent with declaration of HPCI inoperable. "Normal plant shutdown activities are being planned [for 03/11/2018 at 1200 CDT] to support entry into Primary Containment to initiate any necessary repairs. "HPCI is a single train safety system. This report is submitted as a condition that at time of discovery could prevent the fulfillment of the safety function of an SSC [System, Structure, or Component] needed to mitigate the consequences of an accident. "This condition has been entered into the CNS [Cooper Nuclear Station] Corrective Action Program. CR-CNS-2018-01346" LCO 3.4.4 was entered during unplanned maintenance of the HPCI system. When the HPCI-MO-15 was cycled from closed to open, unidentified leakage in the containment increased above 2 gallons per minute (gpm) in less than a 24 hour period. Also, total unidentified leakage exceeded 5 gpm. The licensee closed the HPCI-MO-15 valve resulting in a decrease in unidentified leakage below TS shutdown limit. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-03-10
53252 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-02-14 | 2018-03-08 10:57 | 2018-03-20 | AGREEMENT STATE REPORT - LEAKING SOURCE The following was received via email from the state of Washington: "On 2/15/2018, the RSO [Radiation Safety Officer] for WSU [Washington State University] contacted DOH [Washington State Department of Health] to report a leaking Cf-252 source. The source was received from University of Nevada - Reno and leak tested on arrival. The initial leak test found 0.0066 uCi of removable contamination. Because the amount of removable contamination detected was very close to the leak testing limit, WSU was asked to check their leak testing process and perform another test. On 2/27/2018, WSU confirmed that the source is in fact leaking and both tests provided the same result and that they are holding the leaking source for disposal. DOH is still awaiting further information on the source manufacturer and model number. More information will be provided in a follow-up report." * * * UPDATE ON 3/20/18 AT 1336 EDT FROM ANDREW HALLORAN TO DONG PARK * * * "The RSO provided more information on the source, including the nominal source certificate, and it was confirmed that the source is not a sealed source and does not have a Sealed Source and Device Registration. WSU never put the sources into use and is holding them for disposal. This incident is now closed." Notified R4DO (Groom) and NMSS Events Resource via email. WA Incident Number: WA-18-007 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-03-16
53251 | 0 | HADDAM NECK |  |  |  | ISFSI | 2018-03-07 21:25 | 2018-03-07 21:57 | 2018-03-07 | FALLEN TREE RESTRICTS ACCESS TO THE SITE "A tree has been reported to be down across the road on Injun Hollow Rd. restricting access to the site. The tree was reported to be on powerlines." The licensee has contacted Eversource for the tree removal, however, there is no estimate for removal at this time. The down tree is not currently affecting shift turnover. The licensee has not implemented contingency plans at this time. The licensee has notified the NRC Region I office (Nicholson) and the Connecticut Department of Environmental Protection. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE | PRESS RELEASE/OFFSITE NOTIFICATION | [7 empty] | NON EMERGENCY | 1 | CT | ISF |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) | 72.75(b)(2) |  | 0 | 2018-03-07
53250 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-03-02 | 2018-03-07 17:20 | 2018-03-07 | AGREEMENT STATE REPORT - EQUIPMENT MALFUNCTION The following was received from the State of Texas via email: "On March 7, 2018 Agency [Texas Department of State Health Services] received notification that a Novoste device jammed with no exposure consequence to the patient. Licensee stated two attempts to complete the therapy procedure had taken place, there was no dose to the patient that would be classified as a medical event. The initial attempt with a beta-rail catheter was not successfully completed. The source train (16, Sr 90) did not move along the beta-rail catheter as expected, the source train was not retracted back into the device robotically. The source train in the Novoste device failed to go into the expected treatment position and stayed in the robotic interventional cardiology device for about 1.5 minutes during the intravascular brachytherapy procedure. The interventional catheter with the indicator source train was removed by the doctor (which he wasn't supposed to do). When the train could not be robotically remove back into the device through the beta rail catheter, the source removal from the patient had to be done manually. The source train was retrieved in 15 seconds and placed back into the Novoste device. The treatment was stopped. The patient was surveyed to confirm no sources in the patient. It was believed the beta catheter developed a kink and could not retract the sources. The second attempt was with a new beta rail catheter and source reset. The treatment continued without any incidents. The source returned to the device without any problems." Incident # 9552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-03-15
53249 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2018-02-27 | 2018-03-07 17:09 | 2018-03-07 | AGREEMENT STATE REPORT- LOST AND THEN FOUND SHIPMENT The following was received from the State of Washington via email: "A shipment of 55 Cs-131 seeds with a total activity at the time of shipment of 10.7 GBq was lost by [common carrier] during shipment from Richland, WA to New York, NY. [Common carrier] stated to Isoray that the package went missing on 2/27/2018. The package was scanned leaving Spokane, WA but was never scanned in at the hub in Memphis, TN. The package description from the licensee is as follows: Isoray's internal order number is SCP181163. The package was 55 seeds, total apparent activity of 139 mCi, shipped as a Limited Quantity of Radioactive Material/Priority Alert Overnight. The total GBq at time of shipment was 10.7. The seeds were shipped non-sterile per the ordering M.D.'s request, they were contained in six 'Mick' cartridges inside of a stainless steel pig. "Update on 3/7/2018: The package was found by [the common carrier] and has been returned to the Isoray facility unopened. Isoray has stored the seeds for decay." Incident Number: WA-18-006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2018-03-15
53248 | -1 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-03-07 11:05 | 2018-03-07 12:25 | 2018-03-08 | <br><br>EN Revision Imported Date : 03/14/18<br><br>EN Revision Text: SAFEGUARDS REPORT - SUSPICIOUS PACKAGE The licensee declared an Unusual Event based on Emergency Action Level (EAL) 6.7.U and, entry into the site Security Plan. All required actions or compensatory measures have been completed. The Notice of Unusual Event was terminated at 1142 CST. There was no impact to the operation of any of the units at the Browns Ferry site. The licensee has notified the NRC Senior Resident Inspector. See EN #53247. * * * UPDATE AT 1816 EST ON 03/07/2018 FROM DAVID RENN TO JEFF HERRERA * * * The licensee provided additional information regarding the event. Notified the R2DO (Musser), IRD MOC (Gott), NRR EO (Miller). * * * RETRACTION AT 0918 EST ON 03/08/2018 FROM JAMIE PAUL TO ANDREW WAUGH * * * The Licensee determined that this event was not reportable under the 73.71 criteria. Notified the R2DO (Musser), IRD MOC (Gott), NRR EO (Miller), ILTAB DO (English), and 73.71 Safeguards Group (email).<br><br> Original EN Text: SAFEGUARDS REPORT - SUSPICIOUS PACKAGE The licensee declared an Unusual Event based on Emergency Action Level (EAL) 6.7.U and, entry into the site Security Plan. All required actions or compensatory measures have been completed. The Notice of Unusual Event was terminated at 1142 CST. There was no impact to the operation of any of the units at the Browns Ferry site. The licensee has notified the NRC Senior Resident Inspector. See EN #53247. * * * UPDATE AT 1816 EST ON 03/07/2018 FROM DAVID RENN TO JEFF HERRERA * * * The licensee provided additional information regarding the event. Notified the R2DO (Musser), IRD MOC (Gott), NRR EO (Miller). * * * RETRACTION AT 0918 EST ON 03/08/2018 FROM JAMIE PAUL TO ANDREW WAUGH * * * The Licensee determined that this event was not reportable under the 73.71 criteria. Notified the R2DO (Musser), IRD MOC (Gott), NRR EO (Miller), ILTAB DO (English), and 73.71 Safeguards Group (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | AL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-03-07
53247 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-03-07 11:05 | 2018-03-07 12:25 | 2018-03-07 | NOTIFICATION OF UNUSUAL EVENT DECLARED The licensee declared an Unusual Event based on Emergency Action Level (EAL) 6.7.U and entry into the site Security Plan. All required actions or compensatory measures have been completed. The Notice of Unusual Event was terminated at 1142 CST. There was no impact to the operation of any of the units at the Browns Ferry site. The licensee has notified the NRC Senior Resident Inspector. See EN #53248. Notified DHS SWO, FEMA Ops, DHS NICC, FEMA NWC (email) and NuclearSSA (email). * * * UPDATE AT 1816 EST ON 03/07/2018 FROM DAVID RENN TO JEFF HERRERA * * * The licensee provided additional information regarding the event. Notified the R2DO (Musser), IRD MOC (Gott), NRR EO (Miller). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-03-07
53246 | 0 | CRANE NUCLEAR, INC. |  |  |  |  | 2017-12-17 | 2018-03-06 18:33 | 2018-03-22 | PART 21 - UNDERSIZED PACKING GLANDS IN CERTAIN CRANE GATE VALVES On 12/17/17, Brunswick Nuclear Plant experienced a packing gland blowout on an in-service Crane Nuclear, Inc., Figure Number 83 1/2 SPL, 10 inch by 8 inch by 10 inch, Bolted Bonnet Gate Valve. Crane Nuclear determined that component drawings for the 10 inch valve as well as the 6 inch by 4 inch by 6 inch Bolted Bonnet Gate Valve were in error. That error was corrected. Crane Nuclear is recommending that affected licensees replace the packing glands of the affected valves in their possession. The affected licensees are Pilgrim Station, Cooper Nuclear Station, Browns Ferry Nuclear, and Brunswick Nuclear. Should you have any questions regarding this matter, please contact Joyce Hamman, Director, Safety & Quality at (678) 451-2280, Burt Anderson, Site Leader, at (630) 226-4990, or Samson Kay, Engineering Manager at (630) 226-4983. * * * UPDATE AT 1435 EDT ON 03/21/18 FROM SAMSON KAY TO DONG PARK * * * The following information was provided as an update via fax: "[Crane Nuclear, Inc.] Recommends one of the following actions be taken: - The valve gland should be replaced to tighten clearances to meet MSS-SP-120 requirements. - Install a packing washer in the current configuration that complies with MSS-SP-120 clearances. Use of a packing washer will allow for load to be evenly distributed across the packing to prevent extrusion through diametral clearances. Note, that existing drawings and bills of materials should be updated to match this configuration if this option is selected. "Should you have any questions regarding this matter, please contact me, Joyce Hamman, Director, Safety & Quality at (678) 451-2280, Burt Anderson, Site Leader, at (630) 226-4990, or Samson Kay, Engineering Manager at (630) 226-4983." Notified R1DO (McKinley), R2DO (Sandal), R4DO (Groom) and Part 21/50.55 Reactors via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-03-06
53245 | 0 | INTERNATIONAL ISOTOPES INC. |  |  |  |  | 2018-02-26 | 2018-03-05 13:38 | 2018-03-16 | <br><br>EN Revision Imported Date : 03/19/18<br><br>EN Revision Text: IODINE-131 SHIPMENT LOST IN TRANSIT The following information was received via E-mail: "A package was shipped on February 22, 2018 with an estimated delivery date of February 26, 2018. The customer requested a morning delivery and contacted us when the package wasn't delivered. We reached out to [the common carrier] the afternoon of February 26. [The common carrier] began tracing the shipment that afternoon. From what [International Isotopes] understands, there may have been a mix-up with the ULD (unit load device) in Oakland. We have provided [the common carrier] with a description of the Type A package. They are very familiar with this package as we ship several of these I-131 Type A's per day. We are still in contact with [the common carrier] daily on this. There are three traces out and all three have hit a dead end. At this point [International Isotopes] would consider the package lost, which in our experience is unusual for [the common carrier]. We have had delays, but after a trace, have been able to locate the package. "Shipper: International Isotopes Inc. Idaho Falls, ID 83401 NRC License No.: 11-27680-01MD "Consignee: Pharmatron Fresno, CA 93710 California License No.: 7624-10 "The package contained: 1,000 mCi of I-131 solution Concentration of 4450.0 mCi/mL Volume = 0.22 mL Vial was Crimp Top Serum Vials, 2mL." * * * UPDATE ON 3/16/18 AT 1253 EDT FROM JOHN MILLER TO DAVID AIRD * * * The following was received via email: "The lost I-131 shipment had been located at the [common carrier] Memphis HUB and was received at the International Isotopes, Inc. facility today, 03/16/2018." Notified R4DO (Rollins), NMSS, ILTAB, and CNSNS (Mexico) via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf<br><br> Original EN Text: IODINE-131 SHIPMENT LOST IN TRANSIT The following information was received via E-mail: "A package was shipped on February 22, 2018 with an estimated delivery date of February 26, 2018. The customer requested a morning delivery and contacted us when the package wasn't delivered. We reached out to [the common carrier] the afternoon of February 26. [The common carrier] began tracing the shipment that afternoon. From what [International Isotopes] understands, there may have been a mix-up with the ULD (unit load device) in Oakland. We have provided [the common carrier] with a description of the Type A package. They are very familiar with this package as we ship several of these I-131 Type A's per day. We are still in contact with [the common carrier] daily on this. There are three traces out and all three have hit a dead end. At this point [International Isotopes] would consider the package lost, which in our experience is unusual for [the common carrier]. We have had delays, but after a trace, have been able to locate the package. "Shipper: International Isotopes Inc. Idaho Falls, ID 83401 NRC License No.: 11-27680-01MD "Consignee: Pharmatron Fresno, CA 93710 California License No.: 7624-10 "The package contained: 1,000 mCi of I-131 solution Concentration of 4450.0 mCi/mL Volume = 0.22 mL Vial was Crimp Top Serum Vials, 2mL." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-03-13
53244 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2018-03-04 03:08 | 2018-03-05 13:14 | 2018-03-05 | TECHNICAL SPECIFICATION DEVIATION "On 3/4/17 at 0308 CST, the MURR [University of Missouri Research Reactor] emergency power generator was switched out of automatic control for approximately 10 to 15 seconds while the reactor was operating due to human error. With the emergency power generator in manual control, the emergency electrical power system is considered inoperable because the emergency electrical power system would not have supplied power in the event of a loss of normal electrical power. "This email is a required notification per MURR Technical Specification (TS) 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence as defined by MURR TS 1.1 happened. Specifically, MURR was not in compliance with the Limiting Condition for Operation TS 3.6.a which states, 'The reactor shall not be operated unless the emergency electrical power system is operable.' When the emergency power generator was switched out of automatic control, a Control Room alarm notified the Console Operator. Another operator placed the emergency power generator back into automatic mode which was the quickest way to regain compliance with TS 3.6.a. The MURR continued to operate at 10 MW. A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3)." The licensee notified the NRC Research and Test Reactor Project Manager (Wertz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2018-03-05
53243 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-03-02 12:00 | 2018-03-03 18:39 | 2018-03-03 | AGREEMENT STATE REPORT - SOURCE RETRACTION FAILURE The following information was obtained from the State of Texas via email: "On March 3, 2018, the Agency [Texas Department of State and Health Services] received notice that a source retraction failure had occurred on March 2, 2018 around 1200 CST. The camera was a QSA Global 880D with a 61 Curie Iridium-192 source. During source retrieval the crank cables snapped and the source was just outside the camera. The Radiation Safety Officer (RSO) reported to the scene and covered up the source with shielding. The RSO made multiple trips to cover the source with lead and after he completed the operation he noticed his 0-200 mrem pocket dosimeter was off scale. The RSO will send off his film badge for an emergency reading on March 5, 2018. No other personnel received any excessive dose from the event. "Additional information will be supplied as it is received in accordance with SA-300." Texas Incident #: I-9550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-03-12
53242 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2018-03-02 23:15 | 2018-03-03 02:19 | 2018-03-03 | POTENTIAL LOSS OF OFFSITE RESPONSE CAPABILITIES "At 2315 EST on March 2, 2018, Pilgrim Nuclear Power Station (PNPS) determined, based on information received from the Commonwealth of Massachusetts, that there may be a potential loss of offsite response capabilities due to ongoing severe natural hazard conditions (i.e., major winter storm) along the coast of Massachusetts. According to information received by PNPS, towns within the 10 Mile EP Radius could be hampered in implementing some protective actions specified in the emergency plan in the unlikely event an emergency were to occur. There is no condition at the Station that would warrant implementation of any emergency plan at this time. PNPS continues to operate safely and is monitoring the weather conditions closely. The Station maintains emergency assessment, response, and communication capability. "This report is being made conservatively in accordance with 10 CFR 50.72(b)(3)(xiii) which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As stated previously, the Station maintains emergency assessment, response, and communication capability. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-03-03
53241 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-02-22 | 2018-03-02 15:13 | 2018-03-02 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was obtained from the State of Georgia via email: "On February 19, 2018, a patient was being treated with Y-90 SIR-Spheres. The targeted site was the liver. The prescribed dose was 39 mCi. The procedure appeared to go normally. A follow-up was performed on the same day. The physician thought the scan indicated there was no significant loss of material. On February 22, 2018, another intervention radiologist re-read the scan and noted approximately 30% entered the abdominal wall. On February 23, 2018, the patient was seen and complained of pain and reddening of the skin. The patient went through additional test to determine the cause. The RSO was notified on March 1, 2018 of the incident. The patient, physician, and manufacture were notified of the incident. "The licensee will submit a more detailed report to determine the root cause, difference between the prescribed and delivered dose, dose to target organ and non-target organ." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2018-03-12
53240 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-03-01 15:55 | 2018-03-01 20:34 | 2018-03-01 | UNPLANNED LOSS OF TECHNICAL SUPPORT CENTER "This is an eight-hour, non-emergency notification for a loss of emergency assessment capability. This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) because the discovered condition affects the functionality of an emergency response facility. Due to the discovery of a breaker coordination issue during an NRC Inspection, the power supply breakers to the Technical Support Center (TSC), including the ventilation system, has been opened to address the condition. This will make the TSC non-functional. "If an emergency is declared requiring TSC activation during this period, the Alternate TSC will be staffed and activated using existing emergency planning procedures. The Emergency Response Organization team has been notified to respond to the Alternate TSC in the event of an ERO [Emergency Response Organization] activation. "There was no impact on the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-03-01
53239 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-03-01 16:43 | 2018-03-01 20:05 | 2018-03-01 | POTENTIAL TORNADO MISSILE VULNERABILITIES "During review of protection of equipment from damaging effects of tornados, Point Beach Nuclear Plant identified a potential vulnerability for the turbine driven auxiliary feedwater pumps due to steam supply piping that is not routed through a Class 1 structure. Immediate compensatory measures were taken to mitigate the potential consequences of a tornado generated missile impact. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) and per 10 CFR 50.72(b)(3)(v)(A) and (D). The identified vulnerability is being addressed in accordance with EGM 15-002 and DSS-ISG-2016-01, enforcement discretion memorandum and interim guidance document for resolution of noncompliance with tornado-generated missile protection. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2018-03-01
53238 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-02-28 | 2018-03-01 15:34 | 2018-03-01 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED MOISTURE-DENSITY GAUGE The following information was obtained from the State of Texas via email: "On February 28, 2018, the radiation safety officer from ENGEO Incorporated, contacted RHB [California Radiologic Health Branch] to report a stolen moisture-density gauge. This is a Troxler moisture-density gauge, Model 3440, Serial Number 23533 containing 9 mCi of Cs-137 and 44 mCi of Am-241. According to the licensee, the operator left the gauge secured to the open bed truck at a job site, and upon his return noticed the gauge had been stolen. The gauge was stolen without the Type A container. The licensee immediately notified San Ramon Police Department (SRPD) of the incident. "Note: On 03/01/18, at approximately 1100 PST, SRPD notified the licensee that they had recovered the gauge near the job site. The licensee is enroute to recover the gauge from SRPD. RHB will be following up on this incident." California Report No.: 5010-022818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-03-09
53237 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-02-28 16:30 | 2018-03-01 15:51 | 2018-03-01 | AGREEMENT STATE REPORT - DAMAGED MOISTURE-DENSITY GAUGE The following report was received from the Texas Department of State Health Services via email: "On March 1, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee that at approximately 1630 CST on February 28, 2018, one of its technicians was performing a density test at a job site when an equipment operator veered off of his path and over into the path where the technician was testing. The technician was barely able to get out of the way of the heavy equipment, but was unable to move a Troxler Model 3440 Plus gauge and it was run over. "The gauge contains a 40 milliCurie Americium-241 source and an 8 milliCurie Cesium-137 source. The casing on the gauge was damaged and the Cesium source rod was bent. The technician straightened the rod and secured the gauge in its transport case. "The licensee's radiation safety officer (RSO) responded to the site and performed a radiation survey of the ground where no elevated levels were identified. The RSO surveyed the device and radiation levels were between five and eight millirem/hour, which the RSO stated is higher than normal. The RSO has contacted the manufacturer for guidance. The gauge is in storage area at the licensee's facility. The gauge is not an exposure risk to any individual. The Agency will respond to the licensee's location to perform additional surveys. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-03-09
53236 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-03-01 07:51 | 2018-03-01 13:53 | 2018-03-01 | FITNESS FOR DUTY - POSITIVE RESULT FOR ALCOHOL A non-licensed, supervisory employee was determined to be under the influence of alcohol during a random test. The employee's unescorted access was terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2018-03-01
53235 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2018-03-01 12:10 | 2018-03-01 13:43 | 2019-11-07 | UNANALYZED CONDITION FOR TORNADO GENERATED MISSILES "On March 1, 2018, during evaluation of protection for Technical Specifications (TS) equipment from the damaging effects of tornado generated missiles, Quad Cities Station identified a non-conforming condition in the plant design such that specific TS equipment is considered to not be adequately protected from tornado generated missiles. Tornado generated missiles could strike the Unit l, Unit 1/2, and Unit 2 Emergency Diesel Generator intake and exhaust stacks, day tank vents, and main fuel oil tank vents. This could result in crimping of the intake/exhaust stacks and vents, which would affect the ability of the Emergency Diesel Generators to perform their function if a tornado would occur. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with NRC enforcement guidance provided in Enforcement Guidance Memorandum (EGM) 15-002, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' Revision 1, and DSS-ISG-2016-01, 'Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' Revision 1. Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been informed of this notification." * * * RETRACTION FROM NICK JOHNSON TO HOWIE CROUCH AT 1900 EST ON 11/7/19 * * * "The purpose of this notification today (11/07/19) is to retract event notification #53235 made on March 1, 2018, for Quad Cities Station. Additional review determined that the current design of all three Emergency Diesel Generators and associated Day Tanks and Main Fuel Oil Storage Tanks Vents is consistent with the licensing basis for Quad Cities Station. There was no non-conformance of Quad Cities' tornado missile protection design, and the EDGs were operable at the time the event notification was made. "Therefore, this event does not meet the criteria of 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D) and ENS report #53235 is being retracted. "The NRC Resident Inspector has been informed of this notification." Notified R3DO (Peterson). | 100 | 85 | 0 | 100 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-03-01
53234 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2018-02-28 11:27 | 2018-02-28 14:45 | 2018-07-24 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK OPEN The following report was received from the State of Arkansas via e-mail: "At approximately 1127 CST on 2/28/2018, the Arkansas Department of Health [ADH] Radioactive Materials Program received a phone call from the licensee stating that during routine shutter tests the gauge shutter handle fell off and the shutter is stuck open. The gauge is a Vega America Corporation (Ohmart) Model A-2102, serial number 6997, originally containing 1.5 Curies [Cesium-137] on 4/30/1968 (calculated current activity approximately 475 milliCuries). "Discussion with the licensee indicates that the gauge is mounted on a digester, outside of normal employee traffic. It is normally open during operations and is only closed during maintenance of the digester, which is not planned. Cautionary signage is already present. The licensee representative stated that the staff will be made aware of the situation. Licensee maintenance is assessing the situation and will advise the ADH Radioactive Materials program of the plan for handling this situation. "The State of Arkansas is awaiting a written report from the licensee and final disposition information for the gauge. The State's event number is AR-2018-003." * * * UPDATE FROM DAVID STEPHENS TO VINCE KLCO ON 7/24/2018 AT 1043 EDT * * * The following information was received from the State of Arkansas via email: "Communication with the licensee on March 28, 2018 indicated the licensee was working with the manufacturer to effect replacement of the gauge, and on April 26, 2018 the licensee communicated that a replacement quote from the vendor had been obtained and logistics were being arranged. On May 30, 2018, the licensee amended their license to obtain the replacement, and on June 15, 2018, a contractor replaced the gauge, placing the old gauge in storage. On June 19, 2018, possession of the old gauge was assumed by QSA Global. "The licensee attributes the failure of the shutter handle to the age of the gauge and the environmental conditions (heat, humidity) it was exposed to in the paper plant. "The State of Arkansas considers this incident closed." Notified the R4DO (Gepford) and the NMSS Events Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2018-03-08
53233 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2018-02-28 10:30 | 2018-02-28 14:33 | 2018-04-11 | AGREEMENT STATE REPORT - PACKAGE CONTAINING CATEGORY 2 SEALED SOURCES MISSING IN TRANSIT The following information was received via E-mail: "QSA Global reported via telephone on 2/28/2018 that a package shipped via [a common carrier] on 2/19/2018 (shipping documents prepared on 2/16/2018), containing two Model A424-9 Ir-192 industrial radiography sealed sources within a Model 650L source changer, was reported as missing via telephone by [the common carrier] at 1030 EST on 2/28/2018. [The common carrier] trace was already initiated and in progress, and tracking indicates last known package location was [the common carrier] hub in Memphis, TN. This was a RQ UN2916, Yellow-III, Type B package with a Transport Index of 1.9 at time of shipment. Package dimensions were 26x22x34 cm. Source changer SN 263. Sources - SN 63782G (111.6 Ci on 2/14/2018) and 73783G (108.0 Ci on 2/14/2018). "This situation is an immediately reportable event per regulation. "The search for the missing package is ongoing. "Agency [Massachusetts Radiation Control Program] currently considers this docket to still be OPEN." Package Origin: Burlington, MA, USA Intended Destination: Bogota, Columbia Notified External: DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, and EPA EOC. Notified External via E-mail: FDA EOC, NuclearSSA, FEMA NRCC SASC, FEMA National Watch Center, DNDO-JAC. * * * UPDATE FROM ANTHONY CARPENITO (VIA EMAIL) TO HOWIE CROUCH AT 1119 EST ON 3/1/2018 * * * QSA Global reported to the Agency that the package was received at its intended destination on 2/26/2018. Agency considers this event to still be OPEN. Massachusetts Radiation Control Program updated Tennessee Division of Radiological Health. Notified R1DO (Bickett), NMSS EO (Rivera-Capella), ILTAB (English), IRD MOC (Pham), and NMSS Events (email). Notified External: DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, and EPA EOC. Notified External via E-mail: FDA EOC, NuclearSSA, FEMA NRCC SASC, FEMA National Watch Center, DNDO-JAC. * * * UPDATE FROM ANTHONY CARPENITO TO ANDREW WAUGH AT 1406 EDT ON 4/11/2018 * * * The following was received from the Commonwealth of Massachusetts via email: "QSA Global provided a 30-day written report received by the Agency on 3/9/18. Agency telephone discussions with QSA Global and [the common carrier] were held on 3/12/18. The following information is provided in order to report previously unreported details: (1) QSA Global confirmed that the 650-L Source Changer is itself a Type B package and was not shipped in an overpack container and therefore was the shipping container, (2) [the common carrier] indicated, as a corrective action, this situation would be included in the lessons learned portion of annual refresher training presented to [the common carrier] employees. In this case, although QSA Global had contact with the international customer on 2/21/18 and 2/23/18, the customer did not follow-up to inform QSA Global when the item actually arrived on 2/26/18 (two days before it was reported to Agency as missing by QSA Global on 2/28/18). "Agency considers this event to be CLOSED." Massachusetts Radiation Control Program updated Tennessee Division of Radiological Health. NMED number: 180099 Massachusetts Event: 15-3140 Notified R1DO (Jackson), NMSS EO (Rivera-Capella), ILTAB (Ahern), IRD MOC (Pham), and NMSS Events (email). THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2018-03-08
53232 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2018-02-28 09:55 | 2018-02-28 10:50 | 2018-04-09 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified Region 1 (Powell). * * * RETRACTION FROM JAMES PARADIS TO DONALD NORWOOD AT 1425 EDT ON 4/9/18 * * * Upon further investigation, it was determined that the discovered vulnerability did not exist as reported. This event notification is therefore being retracted. Notified R1DO (Jackson) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | VT | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-02-28
53231 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2018-02-27 | 2018-02-28 10:37 | 2018-02-28 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK OPEN "At about 0900 CST, Oklahoma Department of Environmental Quality [OK DEQ] received a report from Martin Marietta Materials Bell-Savoy Plant, located in Kemp, Oklahoma. They reported that a factory technician had discovered on February 27, 2018 that the shutter was stuck open on an Ohmart SH-F1 Gauge, serial number 7117GK. The device reportedly contains a 100 milliCurie (as manufactured, the device is believed to be over ten years old) Cesium source, but no source model number or serial number is known at this time. The company has closed off the area irradiated by the exposed source until the shutter can be repaired. No overexposures to humans are known or suspected. The company recently purchased the plant from another owner, and should have a GLD registration with the state, but does not have one. OK DEQ has not been able to locate a registration for the previous owner. This is a preliminary report based on initial information submitted to us, and will be updated when more information becomes available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2018-03-08
53230 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-02-26 22:47 | 2018-02-27 01:15 | 2018-02-27 | POTENTIALLY CONTAMINATED WORKER TRANSPORTED TO OFFSITE MEDICAL FACILITY "At 2247 Eastern [Standard] Time the Unit 1 Control Room was notified of a personnel injury in the Unit 1 lower containment. Unit 1 is currently in Mode 1 at 100 [percent] [Reactor] Power and the individual was working in lower containment. The individual's injury appears to be Heat Exhaustion. Site emergency medical technicians responded to the scene and the individual was transported to a local medical facility via ambulance. At the time of transport, the individual was considered to be potentially contaminated because complete surveys could not be performed while the individual was immobilized for transfer. The individual and clothing were surveyed at the hospital by a resident Radiation Protection Technician and no contamination was found. "This report is being made pursuant to 10 CFR 50.72(b)(3)(xii), 'Any event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment.' "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2018-02-27
53229 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2018-02-25 03:30 | 2018-02-25 11:24 | 2018-02-25 | VIOLATION OF FITNESS FOR DUTY POLICY A non-licensed employee was found in violation of the sites Fitness for Duty Policy. The employee's access authorization to the plant has been terminated. The NRC Resident Inspector has been notified. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Decommissioned | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.719 |  |  |  | 0 | 2018-02-25
53228 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-02-23 17:50 | 2018-02-23 20:29 | 2018-02-23 | FITNESS FOR DUTY - MISUSE OF A CONTROLLED SUBSTANCE BY SUPERVISORY PERSONNEL "At 1750 [EST] on 2/23/2018 credible information was obtained that a non-licensed supervisory person had intentionally misused a controlled substance. Unescorted access has been withdrawn. Per 10 CFR 26.719(b)(2)(i) this is a 24 hour reportable event. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2018-02-23
53227 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-02-18 00:06 | 2018-02-23 18:04 | 2018-02-23 | EMERGENCY DIESEL GENERATORS INOPERABLE "On February 18, 2018, Grand Gulf Nuclear Station experienced the concurrent inoperability of two Emergency Diesel Generators [DG]. This event is being reported as a late 8-hour non-emergency notification per 10 CFR 50.72(b)(3)(v)(D) as an 'Event or Condition that Could Have Prevented Fulfillment of a Safety Function (Accident Mitigation).' "On February 14, 2018 at 0100 [CST], the Division 2 Diesel Generator was declared inoperable, and subsequently removed from service for maintenance. On February 18, 2018 at 0006 [CST], the Division 3 Diesel Generator Jacket Water temperature exceeded the trip setpoint and Division 3 Diesel Generator was declared inoperable. The Division 2 Diesel Generator was restored and declared operable on February 18, 2018 at 0355 [CST], and the Division 3 Diesel Generator was restored and declared operable on February 18, 2018 at 1240 [CST]. As a result, Technical Specification Condition 3.8.1.E was entered at 0006 [CST] on February 18, 2018 and exited at 0355 [CST] on February 18, 2018. "Technical Specification Bases 3.8.1.E.1 states 'With two DGs inoperable, there is one remaining standby AC source. Thus, with an assumed loss of offsite electrical power, insufficient standby AC sources are available to power the minimum required ESF functions.' "Offsite power was available throughout this event and there was no impact to the health and safety of the public or plant personnel. "The NRC Resident Inspector has been notified." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-02-23
53226 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-02-21 | 2018-02-22 18:51 | 2018-02-22 | AGREEMENT STATE REPORT - MEDICAL EVENT The following was received via email from the State of Texas: "On February 22, 2018, the licensee notified the Agency [Texas Department of State Health Services] that it had made the determination a medical event had occurred. On February 19, 2018, a patient received first fraction of treatment plan delivered by high dose rate afterloader (HDR) utilizing iridium-192. The patient returned on February 21st for the second fraction. The physicist was reviewing the information prior to treatment and found an error had occurred with the first treatment. "The licensee investigated and conducted dose reconstruction. The licensee's investigation revealed that the physicist performing the digitization of the 13 channels on HDR applicator had digitized channel #12 and when he went to channel #13 he failed to 'tell' the machine, which added the 5.5 centimeters that should have been in channel #13 onto channel #12. There was a high dwell time at the end of the extended 5.5 centimeters which resulted in a dose to tissue outside the target volume that exceeds 50 rem and 50% or more of the dose expected. The licensee reported a small amount of tissue received, and should tolerate, the extra dose. The referring physician has been notified. More information will be provided as it is obtained and in accordance with SA-300." Texas Incident #: I -9546 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-03-02
53225 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-02-20 | 2018-02-21 16:20 | 2018-02-21 | AGREEMENT STATE REPORT - GAUGE SHUTTER STUCK The following information was received via E-mail: On February 21, 2018, the licensee notified the Agency that on February 20, 2018, routine inspection and maintenance was being performed on a Berthold model LB 8010 gauge containing a 20 millicurie cesium-137 source that was in storage at its facility. During shutter check, the shutter was stiff during opening and then it would not close. The shutter was stuck in the open position. The licensee reported that the storage area is segregated from work areas and no one has received any exposure as a result of this event. The few employees with access to the area where the gauge is located have been notified of the situation. The manufacturer was contacted and repair scheduled. Information will be provided as it is obtained and in accordance with SA-300. Texas Incident #: I-9544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-03-01
53224 | 0 | SAINT MARY'S HEALTH CARE |  |  |  |  | 2018-02-20 12:00 | 2018-02-21 15:33 | 2018-02-22 | DOSE TO PATIENT LESS THAN THE INTENDED DOSE A patient was administered the radiopharmaceutical Xofigo which contains Radium Dichloride (Ra-223 CL2). The dosage is based on patient weight. The patient was administered 119.1 microCi. The patient was then weighed and found to weigh greater than 25 percent more than the weight used to calculate the dosage. This was the fourth treatment session of six prescribed. The referring physician's intended dose would have been 159 microCi, based on the patient's actual weight. This misadministration is being characterized as a personnel error. The patient and the physician have been notified and treatment will continue. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-03-01
53223 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-02-20 12:25 | 2018-02-20 18:46 | 2018-04-04 | ALL THREE AUXILIARY FEEDWATER PUMPS INOPERABLE DUE TO HELB DOOR BEING OPEN "At 1225 CST, all three Auxiliary Feedwater [AFW] pumps were declared inoperable at the Callaway Plant upon discovery that a door (DSK13311) credited for protection of equipment from the effects of a high-energy line break (HELB) hazard had come partially open due to vibration harmonics from the running turbine-driven Auxiliary Feedwater pump (TDAFP). Immediate investigation identified that play in the mechanism that holds the door closed had rendered it susceptible to movement from the vibration harmonics. "The affected HELB door specifically protects safety-related instruments that provide a swap-over signal upon detection of a low suction pressure condition for the AFW pumps and thereby automatically effect a suction transfer for the AFW pumps from the condensate storage tank (normal/standby source) to the Essential Service Water (ESW) system (credited safety-related source). "All of the AFW pump suction transfer instrument channels were declared inoperable. Per Technical Specifications (TS) 3.3.2, 'Engineered Safety Feature Actuation System (ESFAS) Instrumentation,' the applicable Condition(s) and Required Action(s) for inoperable AFW pump suction transfer instrumentation only addresses a single channel being inoperable. Thus, the condition of having all three instrument channels inoperable required entry into TS Limiting Condition for Operation (LCO) 3.0.3. At the same time, however, with the automatic suction transfer capability rendered inoperable, all three AFW pumps, i.e., the TDAFP and the 'A' and 'B' motor-driven AFW pumps, were declared inoperable. Although LCO 3.0.3 was applicable, entry into the Required Actions of LCO 3.0.3 was suspended per the Note attached to Required Action E.1 of TS 3.7.5, 'Auxiliary Feedwater (AFW) System,' which states, 'LCO 3.0.3 and all other LCO Required Actions requiring MODE changes are suspended until one AFW train is restored to OPERABLE status.' "At 1336 CST, Operations took actions to prevent the TDAFP from running, so the remaining [AFW Pumps] could be returned to Operable status. Operations then declared the affected instrumentation and the 'A' and 'B' motor-driven AFW pumps Operable. This allowed LCO 3.0.3 and Conditions A, B, D, and E under TS 3.7.5 to be exited. With only the TDAFP inoperable, TS 3.7.5 Condition C and its Required Actions remain in effect. "Due to the degraded HELB door rendering all three AFW pumps inoperable, the unidentified condition is being reported as an unanalyzed condition that significantly degraded plant safety [per 10 CFR 50.72(b)(3)(ii)(B)] as well as a condition that could have prevented the fulfillment of the safety functions of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat, and mitigate the consequences of an accident [per 10 CFR 50.72(b)(3)(v)(A), (B), and (D), respectively]. "The NRC Senior Resident Inspector has been notified." * * * RETRACTION ON 4/4/2018 at 1109 EDT FROM JONATHAN LAUF TO DAVID AIRD * * * "Event Notification (EN) # 53223, made on 2/20/2018, is being retracted because new information has been obtained that negates the original basis for reporting the unanalyzed condition. Specifically, an evaluation of the HELB that is postulated to occur in the TDAFP room has determined that without crediting door DSK13311 for protection, the affected safety-related instruments would not be exposed to environmental conditions beyond their analyzed capability. "This resulted in a conclusion that the unanalyzed condition of door DSK13311 being open did not prevent the affected safety-related instruments or their supported AFW pumps from performing their required safety functions to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat, and/or mitigate the consequences of an accident, nor did it significantly degrade plant safety. Consequently, the condition did not meet the criteria for an 8-hour notification per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(A), (B), or (D)." The licensee notified the NRC Resident Inspector. Notified R4DO (Drake). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2018-02-20
53222 | 0 | UNIV OF FLORIDA |  |  |  | 100 KW ARGONAUT | 2018-02-16 08:55 | 2018-02-20 16:45 | 2018-02-21 | TECHNICAL SPECIFICATIONS VIOLATION DUE TO INCORRECTLY CALIBRATED REACTOR TRIP INSTRUMENTATION "On 2/16/18, the calorimetric portion of Surveillance Requirement (SR) 3.2.3.3 for Limiting Condition for Operations (LCO) 3.2.3.1 was performed in accordance with University of Florida Test Reactor (UFTR) procedures. Reactor power was stabilized at an indicated power of approximately 94 percent with actual thermal power (calculated by heat balance) at approximately 98kW (98 percent RTP) [rated thermal power]. Indicated power was then adjusted to approximately 99 percent to ensure adequate margin to the license limit of 100kW thermal steady-state (100 percent RTP). At no time was actual reactor power allowed to exceed the license limit. The reactor was then shutdown and secured to perform post-calorimetric verifications. SR 3.2.2.1 and 3.2.3.1 were performed satisfactorily just prior to operation to verify the High Reactor Power trip function and setpoint. Reactor Power Channel 1 was set to actuate at 110 percent and Reactor Power Channel 2 was set to actuate at 108 percent. "At about 1400 on 2/19/18, during review of surveillance parameters and discussion with the operators, UFTR management determined that Limited Safety System Setting 2.2.1 and LCO 3.2.2.1 had been violated. The Technical Specifications allowable value for the automatic High Reactor Power trip function is less than or equal to 110 percent RTP. There was a period of approximately 5 hours of operation prior to adjustment of the power channels, however, during which actual thermal power was greater than indicated power (but less than 100kW thermal). During this period, if a power excursion had occurred, the High Reactor Power trip would have actuated at approximately 114 percent RTP. This condition is reportable in accordance with Sections 6.7.2.a.3 and 6.7.2.a.4 of the UFTR Technical Specifications. As described above, this condition was corrected by adjusting indicated power on both reactor power channels to greater than actual thermal power. "The NRC Project Manager, assigned inspector, and Non-Power Reactor Licensing Branch Chief (acting) have been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | FL | NPR | [5 empty] | 0 | 2018-02-20
53221 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2018-02-20 09:25 | 2018-02-20 15:36 | 2018-02-20 | FITNESS FOR DUTY - CONTRACT SUPERVISOR SUBVERTS FITNESS FOR DUTY TEST "At 0925 [EST] on February 20, 2018, a non-licensed supervisory contractor subverted a random Fitness for Duty test. The contractor's site access has been terminated. "The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2018-02-20
53220 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2018-02-20 09:56 | 2018-02-20 15:35 | 2018-02-20 | TRANSPORT OF POTENTIALLY CONTAMINATED PERSON TO A MEDICAL FACILITY "At 0956 CST on 2/20/2018, an employee working in a non-contaminated section of the Radiological Control Area was transported offsite for a personal medical issue. The required radiological survey was not completed prior to the employee being transported offsite by ambulance. A radiological protection technician accompanied the employee and completed a survey during the transfer to the hospital, confirming no contamination of the employee. "This event is reportable pursuant to 10 CFR 50.72(b)(3)(xii). "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2018-02-20
53219 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2018-02-17 02:00 | 2018-02-17 10:29 | 2018-02-17 | DAMAGED BUS BAR IDENTIFIED POTENTIALLY AFFECTING HIGH PRESSURE CORE SPRAY "This report is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. While troubleshooting an issue with the Unit 1B Diesel Generator Oil Circulating pump, damage of a bus bar was identified at the breaker that supplies the Unit 1B Diesel Generator Auxiliaries. One of the loads fed from this breaker is the Division 3 DC Battery Charger. It has been determined that the degradation of the bus bar may have prevented the Division 3 DC Battery Charger from performing its function which could have prevented the High Pressure Core Spray System (HPCS) from performing its design safety function. Since HPCS is a single train safety system, it has been determined that this failure could potentially affect the safety function of this system, and is reportable as an 8 hour notification." The NRC Resident Inspector has been notified. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-02-17
53218 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2018-01-28 | 2018-02-16 15:46 | 2018-02-21 | AGREEMENT STATE REPORT - SHUTTER WOULD NOT OPEN The following was received from the State of Wisconsin: "On February 16, 2018 WI DHS [Wisconsin Department of Health Services] was notified that at the licensee's Stevens Point facility a scanning gauge had a malfunction with the automatic control mechanism and the shutter would not open. The issue was originally identified by the licensee's on-site [personnel] on January 28, 2018 and a service provider was able to fix the issue on January 31, 2018. The corporate RSO [Radiation Safety Officer] became aware of the issue after an on-site visit on February 15, 2018 and reported it to WI DHS the next day. The department will follow-up with the licensee to determine the cause of the shutter control mechanism failure and delay in reporting issues to the corporate RSO." Wisconsin Event: WI 180006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2018-02-26
53217 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-02-16 10:14 | 2018-02-16 13:58 | 2018-02-16 | AUTOMATIC REACTOR TRIP DURING SOLID STATE PROTECTION SYSTEM TESTING "At 1014 [EST] hours on 2/16/18, with Unit 1 in Mode 1 at approximately 100 percent power, the reactor automatically tripped when the Reactor Trip Breakers opened during Train B Solid State Protection System (SSPS) testing. The trip was uncomplicated with all systems responding normally post-trip. Operations manually started the motor driven auxiliary feedwater pumps. The turbine driven auxiliary feedwater pump (TDCAP) auto-started on low steam generator level. A Feedwater Isolation occurred as designed due to the Reactor Trip and Lo Tave condition. Operations stabilized the plant. Decay heat is being removed by the condenser. Unit 2 is not affected. "Due to the Reactor Protection System actuation while critical, actuation of the TDCAP and motor driven auxiliary feedwater pumps along with the Feedwater Isolation, this event is being reported as a four-hour, non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B) and an 8 hour non-emergency notification per 10 CFR 50.72(b)(3)(iv)(A). "There was no impact on the health and safety of the public or plant personnel. The NRC Resident Inspector has been notified. " | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-02-16
53216 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2018-02-16 02:01 | 2018-02-16 04:43 | 2018-02-16 | AUTOMATIC TRIP DUE TO LOSS OF EXCITATION ON MAIN GENERATOR "On February 16, 2018 at 02:01 EST Indian Point Unit 3 automatically tripped on a turbine trip due to a loss of main generator excitation. All control rods fully inserted and all plant equipment responded normally to the unit trip. This is reportable under 10 CFR 50.72(b)(2)(iv)(B). "The auxiliary feedwater system actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). During the event offsite power remained available and stable. No primary or secondary reliefs lifted. The plant is stable, in Mode 3, at no load operating temperature and pressure. Decay heat removal is via the steam generators to the main condenser via the condenser steam dumps. No radiation was released. "Indian Point Unit 2 was unaffected by this event and remains at 100 percent power. "A post trip investigation is in progress. "The licensee has notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-02-16
53215 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2018-02-15 21:53 | 2018-02-16 02:50 | 2018-03-30 | AUTOMATIC REACTOR TRIP DUE TO LOW DEPARTURE FROM NUCLEATE BOILING SIGNAL "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 15, 2018, at approximately 2153 Mountain Standard Time (MST), the Palo Verde Nuclear Generating Station (PVNGS) Unit 1 Control Room received Reactor Protection System alarms for Low Departure from Nucleate Boiling Ratio and an automatic reactor trip occurred. Prior to the reactor trip, Unit 1 was operating normally at 100 percent power. Plant operators entered the emergency operations procedures and diagnosed an uncomplicated reactor trip but noted that Reactor Coolant Pumps 1B and 2B were not running due to a loss of power. All CEAs [Control Element Assemblies] fully inserted into the core. Following the reactor trip, all nuclear instruments responded normally. No emergency classification was required per the PVGS Emergency Plan. "The PVGS Unit 1 safety related electrical busses remained energized from normal offsite power during the event. The Unit 1 'B' Diesel Generator is currently removed from service for maintenance. Due to ongoing planned maintenance on NAN-X02, Startup Transformer 2, fast bus transfer for NAN-S02 (from NAN-S04) was blocked. This resulted in a loss of offsite power to NAN-S02 and NBN-S02. The offsite power grid is stable. Unit 1 is currently stable in Mode 3 with the reactor coolant system at normal operating temperature and pressure. "The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been informed of the Unit 1 reactor trip." * * * UPDATE ON 2/16/18 AT 1640 EST FROM DAVID HECKMAN TO DONG PARK * * * "Unit 1 is stable in Mode 3 following an uncomplicated trip. Offsite power has been restored to non-safety related electrical busses. Troubleshooting continues to determine the cause of the event. "During performance of the alarm response procedure, it was identified that the seismic monitoring (SM) system had been in alarm since the reactor trip and was incapable of performing its emergency plan function. Pursuant to 10 CFR 50.72(b)(3)(xiii), this condition constitutes a major loss of emergency assessment capability. Compensatory measures have been implemented in accordance with PVNGS procedures to provide alternative methods for HU2.1 event classification with the SM system out of service. Maintenance is currently in progress to restore SM system functionality." The licensee notified the NRC Resident Inspector. Notified R4DO (Werner). * * * UPDATE AT 1537 EDT ON 03/30/18 FROM LORRAINE WEAVER TO JEFF HERRERA * * * "Station staff completed an evaluation of event EN #53215 reported on February 15, 2018, and determined that the seismic monitoring system remained capable of assessing a seismic event following the reactor trip. Therefore, a major loss of emergency assessment capability pursuant to 10 CFR 50.72(b)(3)(xiii) did not occur as reported in the update on February 16, 2018. "The NRC Resident Inspectors have been notified." Notified the R4DO (Gaddy). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(xiii) |  |  | 0 | 2018-02-16
53214 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-02-15 14:00 | 2018-02-15 17:36 | 2018-02-15 | FITNESS FOR DUTY - CONTRABAND DISCOVERED IN THE PROTECTED AREA A can of alcohol (8.4 ounces) was discovered unopened in a refrigerator inside the protected area. Site security took possession of the can of alcohol. The owner of the can of alcohol is unknown. This report is being made under 10 CFR 26.719(b)(1) as a 24 hour telephone notification. The can had an expiration date of April 2017. The licensee notified the NRC Resident Inspector and the Regional Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.719 |  |  |  | 0 | 2018-02-15
53213 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2018-02-15 11:00 | 2018-02-15 13:39 | 2018-02-15 | NOTIFICATION OF UNANALYZED CONDITION AFFECTING ACCIDENT MITIGATION FOR TORNADO GENERATED MISSILES "On February 15, 2018, during evaluation of protection for Technical Specifications (TS) equipment from the damaging effects of tornado generated missiles, LaSalle Station identified a non-conforming condition in the plant design such that specific TS equipment is considered to not be adequately protected from tornado generated missiles. Tornado generated missiles could strike the components supporting the operation of Control Room (VC) and Auxiliary Electric Room (VE) ventilation. This could result in inoperable VC/VE systems, which provide a protected environment for occupants to control the unit following an uncontrolled release of radioactivity, hazardous chemicals, or smoke if a tornado were to occur. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with NRC enforcement guidance provided in Enforcement Guidance Memorandum (EGM) 15-002, Revision 1, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' and DSS-ISG-2016-01, Revision 1, 'Clarification of Licensee Actions in Receipt of Enforcement Discretion' per Enforcement Guidance Memorandum EGM 15-002, 'Enforcement Discretion for Tornado Generated Missile Protection Noncompliance.' Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been informed of this notification." | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-02-15
53212 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-02-15 03:06 | 2018-02-15 05:04 | 2018-02-15 | MAIN STEAM LINE RADIATION MONITOR DETERMINED TO BE NON FUNCTIONAL "At time 0306 [CST], Main Steamline Radiation Monitor 2-RE-2326 (Main Steamline 2-02) reading spiked and declared non-functional. "With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 2-02 could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10CFR50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant [CPNPP] has assurance of steam generator integrity and fuel cladding integrity and there is a negligible safety significance to the current condition from a public health and safety perspective. "Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 radiation monitor serves as a backup with alarm function and Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL 2-02. "Corrective actions are being pursued to restore 2-RE-2326 to functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-02-15
53211 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2015-01-01 | 2018-02-14 17:52 | 2018-02-14 | AGREEMENT STATE REPORT - LOST PO-210 SOURCE The following report was received via e-mail: "The general licensee's president said he lost the static eliminator sometime in 2015. The general licensee's president said he used the device once and it did not work well. The general licensee also said the static eliminator must be lost and is probably in the dump somewhere." Make/Model: NRD / P-2021 Serial: A2KD940 Source: Po-210, 10 mCi in April 1995 Mississippi Report: MS-180002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2018-02-22
53210 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-02-14 09:41 | 2018-02-14 18:04 | 2018-02-14 | FITNESS FOR DUTY A non-licensed contract supervisor had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.719 |  |  |  | 0 | 2018-02-14
53209 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-01-09 | 2018-02-14 14:56 | 2018-02-14 | AGREEMENT STATE REPORT - IODINE-131 SPILL The following report was received via fax: "On February 13, 2018, during a routine inspection, the licensee informed the Department [Pennsylvania Department of Environmental Protection] of a contamination event that occurred on January 9, 2017 (over a year earlier). The event is reportable under 10 CFR 30.50 (b)(1)(i). "On January 9, 2017, during a routine injection of 5 milliCuries of iodine-I31 (l-131) into a feline, the needle was removed before the injection was complete, resulting in a spill of I-131 onto the fur of the animal. The spill was not noticed until the animal was being relocated from the injection table to the isolation cage. This resulted in contamination of the technician's skin, clothing, and shoes, and the floor of the injection room. The technician immediately decontaminated her skin, and placed the contaminated clothing into a plastic bag for decay. It was estimated by the licensee she received a skin dose of 1 millirem. The floor of the room was decontaminated and access to the room was restricted over the period of a week until decontamination was complete. All surrounding areas and personnel were monitored and no other contamination was discovered. "The Department [Pennsylvania Department of Environmental Protection] plans to have a 'call for conference' with the licensee and issue violations regarding this event. More information will be provided as received." Pennsylvania report: PA180004 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-02-22
53208 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2018-02-08 | 2018-02-13 16:00 | 2018-02-13 | AGREEMENT STATE REPORT - PERSONNEL OVEREXPOSURE The following report was received from the Maryland Department of the Environment Radiological Health Program via email: "On February 8, 2018, the Maryland Department of the Environment - Radiological Health Program was contacted by Johns Hopkins Medical Institution (MD-07-005-03) of an incident in which one researcher had received a total effective dose equivalent exceeding 5 Rem and likely an extremity dose exceeding 50 Rem. The licensee received results of a researcher's 4th quarter 2017 radiation badge readings. The researcher was conducting tracer studies using PET isotopes C-11 and F-18 in animals. The researcher has been monitored since February 2012 and has frequently used F-18 in similar studies with no problems. Use of PET isotopes in the lab has been halted pending an investigation by the licensee. The Maryland Radiological Health Program will schedule a reactive investigation. "The result of the whole-body radiation badge readings (monitoring period Oct 1 - Dec 31, 2017) was: Deep Dose: 12,818 milliRem Lens of the Eye: 28,280 milliRem Shallow Dose: 46,206 milliRem Beta Dose: 33,388 milliRem "The researcher's assigned extremity ring badge was not worn during the 4th quarter of 2017. "The licensee will submit a written report as required within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2018-02-21
53207 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2018-02-12 13:00 | 2018-02-13 13:28 | 2018-02-13 | AGREEMENT STATE REPORT - FIXED GAUGE BROKEN SHUTTER The following report was received via e-mail: "The licensee notified the Department [South Carolina Department of Health and Environmental Control] at 1115 [EST] on February 13, 2018, that it had discovered a broken shutter on one of its gauges during the six-month shutter checks on February 12th. The gauge is a Berthold Model LB7440D containing 100 mCi of Cs-137. Source serial number is N-A04538DZ242A and source holder serial number is 2179. The gauge is still in service and a radiation reading of 2 mR/hr was observed on the surface of the gauge. There is no radiation exposure risk to personnel." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2018-02-21
53206 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-02-09 | 2018-02-13 12:57 | 2018-03-20 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE STUCK SHUTTER The following report was received via e-mail: "On February 12, 2018, the licensee notified the Agency [Texas Department of State Health Services] that one of its fixed nuclear gauges had a shutter stuck in the closed position. The gauge is an Ohmart-Vega model SH-F1B containing 40 milliCuries of cesium-137. Arrangements have been made with a service company to make repairs. There is no risk of exposure to employees or members of the public. More information will be provided as it is obtained in accordance with SA-300." Texas Event: I-9540 * * * UPDATE ON 3/13/2018 AT 1120 EDT FROM ART TUCKER TO DAVID AIRD * * * The following was received via e-mail: "The license number provided earlier was incorrect. The license number is L00005. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Rollins) and NMSS Events Notification (via email). * * * UPDATE ON 3/20/2018 AT 1446 EDT FROM KAREN BLANCHARD TO DONG PARK * * * The following was received via e-mail: "The license number initially provided was correct. The device in this event is listed on the licensee's General License Acknowledgment (G01819) and not on the Radioactive Materials License (L00005). Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Groom) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-02-21
53205 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2018-02-12 16:09 | 2018-02-12 17:00 | 2018-02-12 | UNAUTHORIZED INDIVIDUAL IN THE PROTECTED AREA Actual intrusion of an unauthorized person into the protected area. The licensee notified the NRC Resident Inspector | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2018-02-12
53204 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2018-02-12 12:00 | 2018-02-12 13:47 | 2019-10-11 | UNANALYZED CONDITION FOR TORNADO GENERATED MISSILES "On February 12, 2018, during evaluation of protection for Technical Specifications (TS) equipment from the damaging effects of tornado generated missiles, Dresden Station identified a non-conforming condition in the plant design such that specific TS equipment is considered to not be adequately protected from tornado generated missiles. Tornado generated missiles could strike the Unit 2, Unit 2/3, and Unit 3 Emergency Diesel Generator main fuel oil tank vents. This could result in crimping of the vents, which would affect the ability of the main fuel oil tanks to perform their function if a tornado would occur. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with NRC enforcement guidance provided in Enforcement Guidance Memorandum (EGM) 15-002, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' and DSS-ISG-2016-01, 'Clarification of Licensee Actions in Receipt of Enforcement Discretion' per Enforcement Guidance Memorandum EGM 15-002, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance,' Revision 1. Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been informed of this notification." * * * RETRACTION ON 10/11/19 AT 1031 EDT FROM SAMANTHA COSENZA TO BETHANY CECERE * * * "The purpose of this notification is to retract event notification 53204 made on February 12, 2018, for Dresden Station. Additional review determined that the current design of all three Emergency Diesel Generators and associated Main Fuel Oil Storage Tanks Vents is consistent with the licensing basis for Dresden Station. There was no non-conformance of Dresden's tornado missile protection design, and the EDGs were operable at the time the event notification was made. "Therefore, this event does not meet the criteria of 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(D). The ENS 53204 report is being retracted. "The NRC Resident Inspector has been informed of this notification." Notified R3DO (Hills). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2018-02-12
53203 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2018-02-12 04:12 | 2018-02-12 11:21 | 2018-02-12 | LOSS OF VENTILATION IDENTIFIED DURING TECHNICAL SUPPORT CENTER TEST "On February 12, 2018, during performance of a TSC Diesel Generator Functional Test, the TSC Ventilation could not be placed in Filter Mode. Filter Mode operation is credited in the TSC habitability analysis of record. The TSC was declared non-functional due to the unavailability of the filtration system. "The Emergency Operations Facility (EOF) is available for use as a backup TSC. Additionally, the TSC would be available for emergency response purposes for events that do not involve a release in progress. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1605 EST ON 2/12/2018 FROM JEREMY MORTON TO MARK ABRAMOVITZ * * * At 1258 CST, TSC ventilation was declared operable. A start permissive lever was adjusted to remedy interference. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-02-12
53202 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2018-02-11 22:03 | 2018-02-11 23:36 | 2018-02-11 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE OUT OF SPECIFICATION "On February 11, 2018 at 2203 [EST], the Susquehanna Control Room received indication that a loss of Secondary Containment Zone 2 differential pressure [DP] had occurred. Control Room operators noted a differential pressure of <.25" WC [inches Water Column] for several seconds. System DP was restored to normal in 1 minute. The cause of the pressure swings is under investigation. "Zone 2 differential pressures being less than 0.25" WC constitutes a loss of Secondary Containment based on not meeting requirements of SR 3.6.4.1.1. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-02-11
53201 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-02-10 18:35 | 2018-02-10 22:37 | 2018-02-10 | BOTH INNER AND OUTER CONTAINMENT AIRLOCK DOORS INOPERABLE AT THE SAME TIME "On 2/10/18 at 1835 CST at Grand Gulf Nuclear Station, while the 208 ft. Containment Airlock Outer Door was tagged-out for planned maintenance, the 208 ft. Containment Inner Door was determined to be inoperable. Grand Gulf had performed 06-ME-1M23-R-0001, Personnel Airlock Door Seal Air System Leak Test, on the 208 ft. Containment Airlock Inner Door which had been deemed satisfactory. While performing planned maintenance on the outer door an additional review of the paperwork determined that the test was actually unsatisfactory on the inner door. TS 3.6.1.2 Condition C was entered at 1835 CST on 2/10/18 for both 208 ft. Containment Airlock Doors being inoperable. Maintenance of the Outer Door is expected to be completed, and the airlock returned to operable status, prior to TS required action completion time." The licensee notified the NRC Resident Inspector. | 70 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-02-10
53200 | 0 | CENTRO DE RADIOTERAPIA |  |  |  |  | 2018-02-06 | 2018-02-08 14:47 | 2018-02-23 | SKIN REACTION RESULTING FROM RADIATION THERAPY The following event was received from Auxilio Mutuo Radiation Therapy Center via phone: A patient who had undergone three gynecological intracavitary brachytherapy procedures was noticed to have a skin reaction. The skin reaction was noticed on the third of the three treatments occurring on 1/24/2018. At this point, it was unclear if the skin reaction was related to the treatments. On 2/6/2018, the attending physician saw the patient and declared that the skin reaction was caused by the radiation treatments, because it had progressed to moist desquamation. The prescribed dose was 400 cGy per fraction for 3 fractions for a total of 1,200 cGy to a depth of 5 cm. This event is under further investigation. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | PATIENT INTERVENTION DAMAGE | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 35.3045(b) |  |  |  | 0 | 2018-02-16
53199 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2018-02-07 14:24 | 2018-02-07 17:02 | 2018-02-07 | AGREEMENT STATE REPORT - PACKAGE ARRIVED WITH SURFACE CONTAMINATION The following was received from the State of Colorado via email: "Red Rocks Radiation Oncology received a package of Ra-223 Xofigo that had removable contamination levels of approximately 23,000 cpm on the outside of the package. The Ra-223 package was delivered by a Cardinal courier from the Cardinal Health facility in Denver, CO which distributes all radiopharmaceuticals (license CO 392-03 is the Cardinal Health license for general radiopharmaceuticals, they share the same building as CO 1219-01). The inner packaging of the Ra-223 shipment did not evidence removable contamination, nor did the car used to transport the Ra-223 package. Cardinal Health has received the wipes and decontamination waste from Red Rocks Radiation Oncology to attempt to determine the isotope causing the removable contamination. The investigation is currently ongoing." Event Report ID No.: CO180003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2018-02-15
53198 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2018-02-07 10:40 | 2018-02-07 15:04 | 2018-02-07 | EMERGENCY NOTIFICATION SIRENS INADVERTENTLY ACTUATED "At approximately 1040 CST, seven (7) Dresden Nuclear Power Station Offsite Emergency Notification sirens (i.e., Siren Nos. DR1, DR4, DR5, DR6, DR9, DR10, and DR11) were inadvertently activated. The Kendall County, IL Emergency Management Agency notified the Exelon Generation Company, LLC. Emergency Response Organization that at 1040 CST, a contract individual inadvertently cut a wire that resulted in the actuation of these seven sirens for three minutes. The contract organization personnel are addressing the issue with the sirens. "The Kendall and Will County Emergency Management Agency contacted Exelon Generation Company regarding this event. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) as an event where other government agencies were notified. "The NRC Resident Inspector has been informed of this notification." The sirens are operable. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-02-07
53197 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-02-06 08:00 | 2018-02-06 16:10 | 2018-02-06 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of California via email: "On February 6, 2018, at approximately 0845 [PST] [the RSO] of Southwest Calibration & Training, Radioactive Materials License #7567-36, contacted RHB [CA Radiologic Health Branch] Brea concerning the moisture/density gauge, CPN, MC1-DRP, serial #MD40507411 (Cs-137 0.375 GBq, Am-241 1.8 GBq) that had been stolen from a transport vehicle [in] Indio, CA at approximately 0800 [PST]. At 0930 [PST], the RSO of Premier Testing & Inspection, Inc., telephoned RHB Brea to inform that the Authorized User had contacted local law enforcement in Indio, [CA] and was filling out a police report with them. A copy of the theft report will be forwarded to the RHB Brea office to be included as part of this report. [The RSO for Premier Testing & Inspection, Inc.] will contact local newspapers to attempt to retrieve the stolen radioactive gauge as well as notifying local servicing vendors of radioactive gauges to be alert for the serial number of the stolen gauge in case it turns up for service. The investigation will continue to determine if the radioactive gauge can be recovered in a reasonable time frame. This is being reported to the NRC Operations Center as a 24-hour report under 10CFR30.50(b)(2) since the radioactive gauge has been stolen and it cannot be determined what condition the sources are currently in." 5010 NUMBER: 020618 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-02-14
53196 | -1 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-02-04 04:45 | 2018-02-04 12:00 | 2018-03-29 | FAILURE OF CONTAINMENT PENETRATION THERMAL RELIEF CHECK VALVES TO MEET SURVEILLANCE ACCEPTANCE CRITERIA "At 0445 [EST] on February 4, 2018, Watts Bar Unit 1 entered Technical Specification 3.6.1 condition A and 3.6.3 condition A.1 and A.2 due to inoperable containment penetration thermal relief check valves 1-CKV-31-3407 and 1-CKV-31-3421 associated with one train of the Containment Incore Instrument Room Chiller system. During surveillance testing, the thermal relief check valves failed to open and pass flow as required by acceptance criteria. The two penetrations were subsequently drained and isolated in accordance with the surveillance procedure to remove any thermal expansion concerns. Technical Specification 3.6.1 was exited February 4, 2018 at 0512 once the two penetrations were drained and isolated. "The purpose of the thermal relief check valves is to allow flow from an isolated penetration back into the upstream containment piping to prevent over-pressurization due to thermal expansion. Over-pressurization of an isolated containment penetration could potentially cause the penetration or both of the isolation valves to fail and provide a direct flow path to the environment from the potentially contaminated containment atmosphere under certain Design Basis Accidents. Therefore, failure of the thermal relief check valves to open could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(C). "NRC Resident Inspector has been notified." * * * RETRACTION AT 1336 EST ON 03/29/2018 FROM TONY PATE TO TOM KENDZIA * * * "The purpose of this notification is to retract ENS notification 53196 made on 2/4/2018 for Watts Bar Nuclear Plant. The previous notification reported a surveillance failure of two containment penetration thermal relief check valves that, at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. "After Engineering evaluation, it has been determined there is reasonable assurance the two thermal relief check valves (1-CKV-31-3407 and 1-CKV-31-3421) were capable of performing their specified safety function to isolate containment and act as a thermal relief device during a design basis accident. The basis of the evaluation included: 1. No maintenance activities or interactions with the check valves had occurred since last tested. 2. All surveillance testing for the valves was within required frequency. 3. The opening force for a new check valve of the same size and similar to 1-CKV-31-3407 and 1-CKV-31-3421 is 0.38 pounds. Engineering analysis has determined the minimum failure pressure of the piping systems associated with the containment penetration in question is 450 psig. If it is assumed the force applied on the check valve seat reaches 450 psig, the force applied on the seat would reach 111 pounds or 300 times the force required to open a new, clean check valve. Based on engineering judgement of previous operating experience where the pressure required to open the same stuck check valve was within a safety factor of 6 to potential equipment damage, the thermal relief check valves would have opened prior to equipment damage and thus the identified condition would not have resulted in adversely affecting the containment isolation boundary. "Entry into Technical Specification (TS) 3.6.1 condition A on 2/4/2018 at 0445 has been retracted. Although not a loss of safety function, the containment penetrations associated with 1-CKV-31-3407 and 1-CKV-31-3421 remain inoperable and are being tracked by TS 3.6.3 condition A.1 and A.2." The NRC Resident Inspector has been notified. Notified the R2DO (Rose). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-02-04
53195 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-02-02 | 2018-02-02 17:07 | 2018-02-05 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER STUCK OPEN The following report was received from the State of Texas via e-mail: "On February 2, 2018, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that a nuclear gauge shutter had failed to operate. The gauge is a Vega SHLG-2 gauge containing a 4,000 milliCurie Cesium-137 source. The source is a plunger type source and it is in the exposed position. The licensee stated the unit the gauge is installed on will be shutdown in the near future and the gauge will be repaired at that time. The licensee has contracted a service provider for the repairs. The Agency [Texas Department of State Health Services] has requested additional information. Additional information will be provided as it is received." Texas Incident #: I-9537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-02-12
53194 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2018-02-01 12:16 | 2018-02-02 13:50 | 2018-03-02 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPH CAMERA The following report was received via email: "The radiographers placed the camera on a pipe, several feet from the ground, to take a shot. They did not secure the camera to the pipe. During the crank out process the camera fell off the pipe, face first, crimping the guide tube and causing the source to become stuck. The company called their radiographer crew located in Jacksonville, FL, to assist them in the retrieval of the source. The RSO and the helper from that office are trained in source retrieval. In the meantime, the area was cordoned off and secured until assistance could arrive. The incident occurred at approximately 1216 EST and completed the source retrieval at approximately 1900 EST. The source was not damaged. The exposure device and drive cable were put out of service and sent to the manufacturer for inspection/repair. The guide tube was damaged due to the fall and was disposed. "The licensee will be submitting a report within a few days with detailed information. The licensee will be in the State for the remainder of the month providing us an opportunity to do an on-site inspection." Camera: QSA Model 880 Delta Source: Ir-192, 91 Ci RSO dose: 310 mrem, Helper dose: 118 mrem | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2018-02-12
53193 | 0 | XCEL ENERGY |  |  |  |  | 2018-01-26 | 2018-02-01 16:23 | 2018-02-01 | PART-21 NOTIFICATION - IMPROPER LUGS IN A BREAKER CUBICLE The following notification is an excerpt from the received report: "On November 30, 2017, an internal wire in a 480VAC cubicle, breaker B3424, was discovered to be terminated using incorrect size wire lugs. This deviation was identified by Monticello Nuclear Generating Plant (MNGP) electrical maintenance staff during bench testing of the cubicles in preparation for implementation of a modification. "The cubicles were received by MNGP in September, 2017 from Westinghouse Electric Co. "On January 26, 2017, MNGP completed an evaluation of this deviation and concluded this condition represents a significant safety hazard. As a result, this condition is a defect and is reportable pursuant to 10 CFR 21.21 (d)(4). "Basic Component: Westinghouse: Eaton Breaker Cubicle Part No. 10149D92G05 "On November 30, 2017, an internal wire in a 480VAC cubicle, breaker 83424, was discovered to be terminated using incorrect size wire lugs. This condition was discovered during bench testing in preparation for implementing a modification to the Control Room Ventilation (CRV) system. The wire connection was found loose and was able to be lifted off of the terminal without removing the screw. Upon further examination, the internal diameter of ring termination lugs was found to be too large, providing only a partial surface area for screw head contact. "The affected lugs were on contactor coil resistor terminations internal to the cubicle. Without sufficient contact area or connection to the wiring on the resistor, control power could be lost to the contactor coil resulting in the fan V-EF-40A not starting, which would prevent proper ventilation to the room housing safety related batteries required to be operable during an accident scenario. Therefore, MNGP determined that a substantial safety hazard could have been created had the breaker cubicle been installed with the defect uncorrected. "This defect was evaluated according to the station's Part 21 reporting process. The evaluation was completed on January 26, 2018 and the reporting officer was informed on January 30, 2018. "Westinghouse was notified of this condition and the condition was incorporated into their corrective action program, number 100506324. The Westinghouse contact person is Adam Tokar, 724-722-6042. No further information on the vendor's corrective actions is known. "MNGP entered the condition into the MNGP Corrective Action Program under 501000005918. Monticello has corrected the lugs on the installed breaker, B4423. The remaining uninstalled cubicles purchased by Monticello are being corrected in accordance with MNGP procedure MWl-8-M-4.06, Conductor Termination, prior in installation in the plant." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-02-01
53192 | -1 | RIVER BEND | 1 |  |  | [1] GE-6 | 2018-02-01 10:57 | 2018-02-01 14:23 | 2018-03-23 | MANUAL REACTOR SCRAM "At 1057 CST on February 1, 2018 with the unit in Mode 1 at approximately 27% power, a manual actuation of the Reactor Protection System (RPS) was initiated due to an unexpected trip of the B Recirc Pump with A Recirc Pump in fast speed. B Recirc Pump tripped during transfer from slow to fast speed resulting in single loop operation. Operators were unable to reconcile differing indications of core flow. This resulted in a conservative decision to initiate a manual scram. The cause of the B Recirc Pump trip and the apparent issues with core flow indication are under investigation. The plant is currently stable in Mode 3. "The plant response to the scram was as expected. All control rods [fully] inserted as expected; the feedwater system is maintaining reactor vessel water level in the normal control band and reactor pressure is being maintained with steam line drains and main turbine bypass valves. "The NRC Senior Resident [Inspector] has been notified." * * * RETRACTION AT 1015 EDT ON 03/22/2018 FROM DAVID DABADIE TO OSSY FONT * * * "This event was initially reported under 10 CFR 72(b)(2)(iv)(B) as a manual actuation of the RPS due to an unexpected trip of the B Reactor Recirculation Pump with the A Reactor Recirculation Pump running in fast speed (Single Loop Operations). Operations was unable to reconcile differing indications of core flow and made the conservative decision to perform a planned shutdown in accordance with normal operating procedures. Therefore, this event 'resulted from and was part of a pre-planned sequence during testing or reactor operation' as specified in 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50.73(a)(2)(iv)(A) and NUREG-1022 Section 3.2.6. Consequently, this event is not reportable as an actuation of RPS. "The NRC Resident Inspector has been notified." R4DO (Groom) has been notified. | 0 | 0 | 0 | 27 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2018-02-01
53191 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2018-02-01 07:49 | 2018-02-01 13:50 | 2018-02-01 | FITNESS FOR DUTY - CONFIRMED POSITIVE TEST "A non-licensed [employee] supervisor had a confirmed positive test for alcohol during a random fitness-for-duty [FFD] test. The individual's unescorted access to the plant has been [terminated]. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 26.719 |  |  |  | 0 | 2018-02-01
53190 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2018-02-01 11:08 | 2018-02-01 11:59 | 2018-02-01 | UNUSUAL EVENT - FIRE IN THE TURBINE BUILDING LASTING GREATER THAN 15 MINUTES "Nine Mile Point unit 2 experienced an unusual event due to a small fire in the turbine building that was immediately extinguished and then reflashed. The fire was declared out at 1119 [EST], 2/1/18. The fire was caused when steam leak repair injection equipment failed and leaked onto hot piping. There was no equipment damage or impact to plant operation. The fire was extinguished by the fire brigade. Offsite assistance was not required." The fire resulted from Furmanite repair of a Moisture Separator Reheater inlet flow control valve. The unusual event will be terminated when sufficient lagging is removed to verify the extent of leaked fluid. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA, DHS NICC, and NNSA (via e-mail). * * * UPDATE AT 1240 EST ON 2/1/2018 FROM ANTHONY PETRELLI TO MARK ABRAMOVITZ * * * The unusual event was terminated at 1211 EST. The licensee notified the NRC Resident Inspector. Notified the R1DO (Janda), NRR EO (Miller), IRD MOC (Grant), DHS SWO, FEMA, DHS NICC, and NNSA (via e-mail). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-02-01
53189 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2018-01-31 13:10 | 2018-01-31 18:19 | 2018-01-31 | MOMENTARY LOSS OF SECONDARY CONTAINMENT "At 1310 hours [CST] on January 31, 2018, the Unit 2B fuel pool radiation monitor spiked high due to an invalid actuation which caused the U1 and U2 reactor building ventilation system to isolate, B train standby gas treatment system (SBGTS) started, and the control room ventilation system also isolated as designed. Secondary containment vacuum was lost for approximately one minute, and then subsequently returned to an acceptable level in accordance with Technical Specification 3.6.4.1, 'Secondary Containment.' As a result of this transient, secondary containment was inoperable for approximately one minute. No emergency conditions were determined to exist. Troubleshooting of the radiation monitor spike is underway. "Given the temporary loss of secondary containment vacuum, this event is reportable under 10CFR50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-01-31
53188 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2018-01-30 18:22 | 2018-01-30 21:56 | 2018-01-30 | MANUAL REACTOR SCRAM DUE TO MAIN TURBINE LOAD OSCILLATIONS "On 1/30/2018 at 1750 [CST], the Reactor Pressure Control Malfunctions ONEP [Off Normal Event Procedure] was entered due to main turbine load oscillations of approximately 30 MWe peak to peak. At 1822 [CST], a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown due to continued main turbine load oscillations. "Reactor SCRAM ONEP, Turbine Trip ONEP, and EP-2 were entered. Reactor water level was stabilized at 36 inches narrow range on startup level and reactor pressure stabilized at 933 psig using main turbine bypass valves. "Reactor Water Level 3 (11.4 inches) was reached which is the setpoint for Group 2 (RHR to Radwaste Isolation) and Group 3 (Shutdown Cooling Isolation). No valve isolated in these systems due to all isolation valves in these groups being in their normally closed position. The lowest Reactor Water level reached was -36 inches wide range. "No other safety system actuations occurred and all systems performed as designed. "That event is being reported under 10CFR 50.72(b)(2)(iv)(B) as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical and also reported under 10CFR 50.72(b)(3)(iv)(A), as any event or condition that results in actuation of RPS." The MSIVs are open with decay heat being removed via steam to the main condenser using the bypass valves. Off site power is stable, and the plant is in a normal shutdown electrical lineup. RCIC (Reactor Core Isolation Cooling) was out of service for maintenance, and the reactor water level did not reach the system activation level. The cause of the main turbine load oscillations being investigated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-01-30
53187 | 0 | MISSOURI BAPTIST MEDICAL CENTER |  |  |  |  | 2018-01-29 09:30 | 2018-01-29 17:20 | 2018-01-29 | RECEIVED DOSE GREATER THAN PRESCRIBED DOSE A patient received SAVI (Strut-Adjusted Volume Implant) High Dose Rate Treatments on January 26, 2018 and January 29, 2018. After the treatment, it was noted that the dwell time on one catheter appeared unusual. The treatment from January 26 was then reviewed and it was discovered that the catheters were labeled incorrectly during the initial treatment planning process. The physician was notified to review the delivered dose. Another physicist was contacted and remotely viewed the delivered treatment of the January 29 treatment as well as the treatment plan from January 26. This physicist came to the same conclusion that the catheters had been mislabeled on the January 26 CT scan. The skin received a greater dose than intended for one delivered fraction. 1cc received 848cGy, intended 256cGy and 0.1cc received 1500cGy, intended 282cGy. A decision was made by the physician to cancel all further radiation treatments using the SAVI device and the catheter was removed. The patient was notified of the event, as well as the referring physicians. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2018-02-06
53186 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-01-10 | 2018-01-26 15:11 | 2018-01-26 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN The following information was received via email: "On January 12, 2018, GL0704 Pacific Aurora, LLC (formerly Aurora Coop West) contacted [the Nebraska Department of Health and Human Services (NEDHHS)] regarding their overdue Annual Invoice and Current Inventory. The Environmental Manager [EM] noted that Aurora Coop West was bought by Pacific Ethanol on December 16, 2017 and has combined into one entity: Pacific Aurora, LLC. The EM indicated he was unable to locate several of the tritium exit signs on the inventory but would attempt location for one additional week. NEDHHS Office of Radiological Health received written notification on January 25, 2018 of one lost/missing tritium exit sign. The EM assumes the sign may have been moved during a renovation. Should the sign be located, the EM has indicated they will contact [NEDHHS]. "Device Name: Radioluminescent Sign Manufacturer: Safety Light Corp. Model Number: SLX60 Serial Number: 418040 Radionuclide: H-3 Activity: 11.5 Ci." NEDHHS Item Number: NE180002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-02-05
53185 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2018-01-26 08:53 | 2018-01-26 13:06 | 2018-01-26 | REACTOR COOLANT SYSTEM OPERATIONAL LEAKAGE "On January 26, 2018, a containment entry was made to identify the source of elevated Unidentified Reactor Coolant System (RCS) operational leakage. A through-wall leak was identified on a Class 1 piping weld on the letdown line at 0853 EST. It was determined that the leak was RCS pressure boundary leakage. Ginna entered Technical Specification (TS) LCO [Limiting Condition for Operation] 3.4.13, RCS Operational Leakage, Condition B. for the existence of pressure boundary leakage. This condition requires the plant to be in MODE 3 within 6 hours and MODE 5 within 36 hours. The leak was isolated and TS LCO 3.4.13 exited at 1015 EST. "This event is reportable within 8 hours in accordance with 10CFR50.72(b)(3)(ii)(A) for 'Any event or condition that results in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded'. "The Station [Ginna] is developing an evaluation and a repair plan at this time. "This condition has no impact on public health and safety. "The licensee has informed the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2018-01-26
53184 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-01-25 19:01 | 2018-01-26 01:37 | 2018-01-26 | OFFSITE NOTIFICATION DUE TO SCREEN WASH PUMP MOTOR FIRE "At 1901 PST on January 25, 2018, the Control Room received a fire alarm, followed by screen wash and 480v load center alarms a few minutes later. The intake operator and on-site fire department personnel were promptly dispatched to the scene and confirmed within 15 minutes there was no active fire. As a conservative measure, off-site fire assistance was initially requested, however [this request] was canceled a short time later. While on-site fire personnel were locally assessing the damage to screen wash pump 1-2, a brief flare-up occurred at the pump motor which was immediately extinguished. Units 1 and 2 remained stable and two screen wash pumps remain available. There is no risk to plant safety or personnel and both units continue to operate at power. Current efforts are focused on determining the cause of the situation." The licensee notified the NRC Resident Inspector and CAL FIRE. The licensee issued a media/press release. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-01-26
53183 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2018-01-25 12:00 | 2018-01-25 18:20 | 2018-02-15 | POTENTIAL DEFICIENCY ASSOCIATED WITH AN ITEM RELIED UPON FOR SAFETY "During a self initiated review, ISA [Integrated Safety Analysis] Staff performed a preliminary review of the ISA to determine whether or not there was a chemical safety issue concerning the proximity of combustible fuel to the yard tractors/shuttle lifts that UUSA's [Urenco USA] Logistics organization uses to move UF6 [Uranium Hexa Fluoride] cylinders around outside on site. "ISA staff determined that the ISA lacked sufficient information regarding the proximity of combustible fuel to the IROFS36c [Item Relied Upon for Safety] controlled yard tractors/shuttle lifts. ISA determined that revisions to one, or more, of the applicable IROFS Boundary Definition Documents was necessary to establish operator actions to ensure that the volumetric fuel limit is not compromised due to the proximity of other fuel sources, therefore UUSA is conservatively making this report. "UUSA remains in a safe and stable condition. UUSA Logistics has issued a stop work that prohibits applicable cylinders from traveling where proximity to combustible fuel could occur. "10 CFR 70.50(c)(iii) (A) There was not a material release, no radiological or chemical hazards were present. (B) No exposure occurred (C) A deficiency exists in the ISA in which the limiting of external fuel sources near IROFS36c controlled yard tractors/shuttle lifts was not discussed (D) IROFS36c remains operable and available to perform its safety function. The identified deficiency only affects applicable UF6 cylinders that could be moved in proximity to other fuel sources. UUSA has issued a stop work to adequately address the deficiency. (iv) No external conditions affect this event (v) A stop work was issued to prevent the movement of applicable UF6 cylinders where proximity to other fuel sources could occur (vi) An event did not occur at UUSA. UUSA remains in a safe and stable condition (vii) No emergencies have been, nor will any be declared (viii) No state or other federal agencies will be notified (ix) No press releases are planned." The licensee will be contacting the NRC Region 2 office (Ortiz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2018-01-25
53182 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-01-25 | 2018-01-25 17:16 | 2018-01-25 | AGREEMENT STATE REPORT - TWO NUCLEAR GAUGES FOUND WITH SHUTTERS STUCK OPEN The following report was received from the Texas Department of State Health Services via email: "On January 25, 2018, the Agency [Texas Department of State Health Services] was notified that two of the licensee's Ohmart-Vega Model SHLG fixed nuclear gauges were found to have shutters stuck in the open position during preventative maintenance. These gauges normally operate with the shutter in the open position. There is no increased risk of exposure to any member of the public or licensee employees. Coordination is underway between the licensee, the service company, and the manufacturer for the gauges to be removed and returned to the manufacturer for repair or disposal. "Source Information: SN: 3253CM 2,000 milliCuries cesium-137 SN: 4021CM 2,000 milliCuries cesium-137" Texas Incident #: I-9533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-02-02
53181 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2018-01-19 | 2018-01-23 16:03 | 2018-01-23 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following was received from the state of Nebraska via email: "On 1/19/18, GL0635 [General License] Crete Cold Storage called NEDHHS [Nebraska Department of Health and Human Services], Office of Radiological Health to inquire about reporting requirements if they could not locate GL [generally licensed] devices. Licensee assumed devices were lost during a renovation. Licensee was given reporting instructions via e-mail. On 1/23/18, NEDHHS Office of Radiological Health was notified via letter by GL0635 that four (4) tritium exit signs were reported lost." All four signs were manufactured by Safety Light Corporation, Model 2040, Serial numbers 252778, 252779, 252781 and 252774. Nominal material content is 11.5 Ci of tritium per sign. Nebraska NMED Report No.: NE180001 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2018-01-31
53180 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-01-23 04:00 | 2018-01-23 05:02 | 2018-01-26 | LOSS OF ASSESSMENT CAPABILITY DUE TO TECHNICAL SUPPORT CENTER PLANNED MAINTENANCE "At 0400 [CST] on 1/23/2018 the Braidwood Technical Support Center (TSC) HVAC [Heating, Ventilation and Air Conditioning] Emergency Makeup Air Filter train was taken out of service to perform a planned Makeup Air Filter charcoal replacement. The TSC HVAC Makeup Air Filter train will be rendered nonfunctional during the charcoal replacement. Subsequent charcoal and HEPA filter testing will restore functionality of the TSC HVAC Makeup Air Filter train. The expected duration of the charcoal replacement and subsequent testing is 30 hours. "If an emergency is declared requiring TSC activation during the time TSC HVAC is non-functional, the TSC will be staffed and activated using existing emergency planning procedure unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to a major loss of emergency preparedness capability. An update will be provided once the TSC HVAC Emergency Makeup Air Filter train functionality has been restored. "The licensee has notified the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-01-23
53179 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2014-02-19 | 2018-01-22 15:16 | 2018-01-22 | AGREEMENT STATE REPORT - FACILITY FAILED TO REPORT SUSPECTED OVEREXPOSURE The following was received via email: "On 1/19/18, while conducting an inspection at [Roane Medical Center] RMC of a standard diagnostic nuclear medicine program with no written directive, an inspector identified, in review of facility dose records, evidence of an overexposure to a nuclear medicine technician of a dose of 118.425 Rem for period of January 20, 2014 to February 19, 2014. Investigation by the facility subsequently determined that the exposure was not likely a real exposure to the individual. However, facility failed to report the suspected overexposure. Dose was subsequently removed from the individual's dose history based on their investigation." State Event Report ID NO.: TN-18-012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-01-30
53178 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-01-22 11:15 | 2018-01-22 15:09 | 2018-01-22 | OFFSITE NOTIFICATION DUE TO OIL SPILL "At 1115 EST, on 1/22/18, Fermi 2 determined that the site was in violation of its National Pollutant Discharge Elimination System (NPDES) permit due to an oil sheen being observed in a overflow canal that had breached the installed oil booms and entered navigable waterways. "Approximately 5-10 gallons of oil has reached navigable water, which resulted in exceeding State limits. The oil is currently contained with no additional leakage to navigable waters and cleanup is in progress. The cause of the oil entering the overflow canal is under investigation. "Reports will be made to the Michigan Department of Environmental Quality (MDEQ) and other local agencies. Since these reports are in the process of being made, this is considered a News Release or Notification to Other Government Agencies, therefore this event is reportable under 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." The Licensee has notified the National Response Center. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-01-22
53177 | 0 | VELAN INC. |  |  |  |  | 2017-11-01 | 2018-01-18 16:06 | 2018-01-24 | PART 21 NOTIFICATION - CHECK VALVE DISC THICKNESS COULD CAUSE VALVE TO STICK OPEN The following is a summary of the information received from Velan Inc. via facsimile: Affected item: Velan Inc. Disc (part number 8205-012) in 4NPS Class 150 through 900 Swing Check Valve Callaway Nuclear Plant discovered that a Velan check valve installed in 1999 was stuck open. Velan investigated and determined that in 1979, a design change increased the thickness of the disc to allow the check valve to be used in higher pressure applications than the original design. In 1985, the valve body cavity was enlarged which would preclude the disc from sticking. Therefore, the only affected valves are the valves manufactured between 1979 and 1985. Velan's records only go back to 1982 for purchase orders of this valve. Their records indicate 157 discs of this part number were shipped to U.S. utilities. The following actions are being taken with respect to the disc: - Cancel disc part number 8502-012 - Create a new disc part number to fit the body geometry of 1985 and before -Create another disc part number to fit the current body geometry. All affected utilities will be notified within a week, for information and to determine a course of action. As a minimum, Velan will recall all discs of the aforementioned part number in inventory at these utilities. For any additional information on this matter please contact Victor Apostolescu at 514-748-7748 x 2134 or at victor.apostolescu@velan.com. This disc has been purchased by nuclear plants in all four USNRC regions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-01-18
53176 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2018-01-18 12:02 | 2018-01-18 17:03 | 2018-01-18 | EMERGENCY DIESEL GENERATOR ACTUATION DUE TO LOSS OF ONE OF TWO OFFSITE POWER SUPPLIES "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in a valid actuation of the Emergency Diesel Generator. "On January 18, 2018 at 1202 EST, V.C. Summer Nuclear Station (VCSNS) lost one of its two redundant offsite power supplies. The loss of the 115kV power supply created an undervoltage condition on the normal incoming Engineered Safety Features power supply to safety related bus 1DA. The 'A' Emergency Diesel Generator started and loads sequenced as designed. The 'A' Residual Heat Removal pump started but did not inject any water into the Reactor Coolant System. The 'A' Emergency Feedwater Pump started and ran for approximately 2 minutes. Other plant equipment and systems also responded as expected. "The loss of the 115kV power supply occurred due to an issue with a component in a switchyard, external to VCSNS. The cause of the event is still under investigation. "All loads have been transferred back to the offsite 115kV power supply at 1318 EST. The diesel generator was secured at 1321 EST, reset and is ready to auto-start. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-01-18
53175 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2018-01-09 | 2018-01-18 12:39 | 2018-01-18 | ILLINOIS AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received from the State of Illinois via email: "The agency [Illinois Emergency Management Agency, Bureau of Radiation Safety] was notified on 1/16/18 of a medical event that occurred on 1/9/18. Agency personnel were able to contact the licensee and obtain details on 1/17/18. The licensee's RSO advised that he was out of state for a training class and was not informed by his staff until he returned. "Licensee administered Y-90 Theraspheres to a patient in 2 doses, each treating a separate lobe of the liver. The physician wrote two prescriptions, one for each lobe. One lobe required 10 mCi, in which the entire 10 mCi dose was delivered. The second prescribed dose was for 7 mCi. Upon performing residual measurements, it was discovered that the delivered dose was 28 percent less than the 7mCi specified in the written directive. There were no equipment malfunctions reported, nor were there any medical reasons for the underdose (stasis was not reached). The AU [Authorized User] was notified, as was the referring physician. "When considering the organ as a whole, three separate fractions were prescribed, under three separate written directives (34 mCi + 10 mCi +7 mCi), yielding a total dose of 94.44 Gy. The administered dose was 93.94 Gy. The resultant composite differential is 50 rem, with 99.5% of the desired dose administered to the organ. A written report is pending from the licensee." Illinois Item No.: IL180012 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-01-26
53174 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2018-01-17 12:28 | 2018-01-18 10:03 | 2018-01-18 | NON-POWER REACTOR MANUALLY SCRAMMED "Technical Specification 3.2.3 item 1 requires that a minimum of two level channels be operable and set to scram the reactor at less than 7.4MW. A reactor startup was in progress to 1MW for training with one of three level channels out-of-commission. The reactor reached 1MW at 1219 EST on 1/17/18. The shift supervisor was completing the checklist that requires observing level channels to verify they are responding. The shift supervisor noticed that only one channel was responding and scrammed the reactor at 1228 EST. Preliminary investigation found a faulty connection point at the detector signal cable. Corrective actions and retesting is ongoing." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MA | NPR | [5 empty] | 0 | 2018-01-18
53173 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2018-01-17 20:02 | 2018-01-17 22:41 | 2018-01-17 | SHIELD BUILDING INOPERABLE "At 2002 EST on January 17, 2018, annulus differential pressure exceeded its pressure limit. At that time, the Shield Building was declared inoperable requiring entry into Technical Specification 3.6.15, Conditions A and B. Action was taken by field operators to swap annulus vacuum control dampers to restore annulus differential pressure. At 2024 EST, annulus differential pressure was restored to required limits, the Shield Building was declared operable, and LCO 3.6.15, Conditions A and B were exited. "The temporary loss of the Shield Building resulted from a failure of the annulus vacuum control system to maintain the required differential pressure. Manual swap-over of pressure control to the backup damper restored differential pressure to required limits allowing exit from TS LCO 3.6.15 and restoration of the Shield Building safety function. "The Shield Building ensures that the release of radioactive material from the containment atmosphere is restricted to those leakage paths and associated leakage rates assumed in the accident analysis during a Loss of Coolant Accident (LOCA). The Emergency Gas Treatment System (EGTS) would have automatically started and performed its design function to maintain annulus vacuum within required limits. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-01-17
53172 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2018-01-12 | 2018-01-17 19:42 | 2018-01-17 | AGREEMENT STATE REPORT - GAUGE WITH RADIOACTIVE SOURCE DISPOSED OF IN LOAD OF SCRAP METAL - RECOVERED The following information was received from the State of California via E-mail: "The California Radiation Control Program (CDPH-RHB) was notified by US CBP [Customs and Border Patrol] on 1/12/18 that a shipping container that had arrived at the Oakland port triggered a radiation detector upon attempting to depart the port. The shipping container contained scrap metal that was later determined to have been rejected at a South Korea port due to radiation detected upon receipt there. "The Oakland port CBP personnel detected Cs-137, with a maximum dose rate on the outside of the shipping container of 86 microR/hr (gross). The radiation apparently had not been detected when the container was shipped out of the Oakland port to South Korea. "The shipping container was held at the Oakland port by CBP until Tuesday 1/16/18, when it was released to AS Metals with the provision that CDPH-RHB would be present when the container was opened to determine the source of the radiation and subsequent disposition. CDPH-RHB went to a scrap yard site on 1/16/18 and found the source of the radiation was a gauge that was labeled (in handwriting as the original gauge label was missing) as containing 100 mCi of Cs-137. The gauge shutter was locked in the closed position. Dose rates were measured as approximately 40 mR/hr contact and 3 mR/hr at one foot distance, and the radioactive material was confirmed to be Cs-137. "The apparent generally licensed gauge, which appeared very old, is being held in secure storage by AS Metals pending an attempt by CDPH-RHB to identify the general licensee who lost control of the gauge. This may be difficult due to the missing original label on the gauge, and because AS Metals has not been able to determine how or where they came into possession of the gauge." California 5010 Number: 011618 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-01-25
53171 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2018-01-15 | 2018-01-17 16:45 | 2018-01-19 | AGREEMENT STATE REPORT - DELIVERED DOSAGE DIFFERENT FROM PRESCRIBED On January 15, 2018 a medical event occurred at the licensed facility in which a patient received a prescribed dose less than 80 percent of the target dose to the liver. The dose was delivered via Y-90 microspheres. The State will investigate this medical event. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2018-01-25
53170 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2018-01-17 09:52 | 2018-01-17 15:08 | 2018-01-17 | AUTO-START OF EMERGENCY DIESEL GENERATOR DUE TO TRANSFORMER FUSES BEING DISCONNECTED "At 0952 EST on 01/17/2018 with Unit 1 and Unit 2 operating at 100 percent, the normal supply breaker to the Unit 1J Emergency Bus tripped open due to an under-voltage condition when the potential transformer fuses were inadvertently disconnected. This resulted in a loss of power to the Unit 1J Emergency Bus from its normal off-site power supply. Number 3 Emergency Diesel Generator automatically started on an under-voltage signal and loaded onto the Unit 1J Emergency Bus, as designed. "All equipment performed as expected during the event and there were no unexplained occurrences. Maintenance has verified the fuses have been reconnected and at 1221 EST, off-site power was restored to Unit 1J Emergency Bus. At 1254 EST Number 3 Emergency Diesel Generator was secured in accordance with Station Operating procedures. "All Electrical distribution systems have been restored to a normal alignment. "There were no radiation releases due to this event, nor were there any personnel injuries or contamination events. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to the auto start of Number 3 Emergency Diesel Generator." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2018-01-17
53169 | 0 | RADIATION SAFETY ASSOCIATES, INC |  |  |  |  | 2018-01-16 14:00 | 2018-01-17 11:13 | 2018-01-17 | NUCLEAR INSTRUMENT WITH RADIOACTIVE SOURCE DISPOSED OF IN LOAD OF SCRAP METAL - RECOVERED A load of scrap metal was returned by the recycler to the originator (Ulbrich Stainless Steels and Special Metals, Inc.) after their radiation detector alarmed on the load of metal. After arriving back at Ulbrich, the load was checked and a Dickey-John Dewpointer instrument containing a 7 microCurie Radium-226 source was found. The Dewpointer instrument is believed to have been purchased by Ulbrich more than 20 years ago. The Dewpointer instrument had no stickers or warning labels indicating that it contained a radioactive source. The Dewpointer instrument had been surplused and tossed in the trash. The Dewpointer instrument is currently in the possession of Radiation Safety Associates, Inc. (license number: 06-30007-01). Ulbrich has taken responsibility for assuring proper disposal of the instrument. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2018-01-25
53168 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2018-01-05 | 2018-01-16 21:14 | 2018-01-18 | AGREEMENT STATE REPORT - DELIVERED DOSAGE DIFFERENT FROM PRESCRIBED The following was received from the State of Wisconsin via email: "An email the Department [Wisconsin Department of Health Services] received on January 5, 2018 was believed to be an update to the previous notification. Upon further review by the Department, it was discovered that the email pertained to a second medical event identified by the licensee on January 5, 2018. This was a medical event as described in DHS 157.72(1)(a)1.a. The prescribed dose was 145 Gy; the dose delivered was 105 Gy. The licensee uses D90 (dose delivered to 90 percent of the clinical target volume) less than 80 percent for determining medical events. Using the licensee's dose based criteria; the dose received by the prostate was 62% of the intended dose. "DHS inspectors will investigate this medical event." Wisconsin Event: WI180001 The previous notification stated above, which occurred on January 4, 2018, is documented in EN# 53148. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2018-01-24
53167 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2017-11-30 22:30 | 2018-01-16 10:06 | 2018-01-16 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 2230 CST on November 30, 2017, with the Duane Arnold Energy Center (DAEC) operating at 100 percent power, an invalid Group 3 isolation on the 'B' side of the Primary Containment Isolation System [PCIS] occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation and Purge, Containment Nitrogen Compressor Suction and Discharge, Recirculation Pump Seals, and Post Accident Sample System. "This event was caused by a fault on the 1D25 Instrument AC Inverter. The fault was caused by an insufficient design clearance to ground and was corrected by increasing the clearance. "All equipment responded in accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2018-01-16
53166 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-01-09 16:05 | 2018-01-12 14:28 | 2018-01-12 | AGREEMENT STATE REPORT - LOST SOURCE/UNRECOVERABLE The following was received via email: "The RSO [Radiation Safety Officer] called in a preliminary notification at 4:05 PM [CST] on 01/09/2018. The notification was, Citgo Petroleum Corp (CPC) had lost a XRF unit overboard while working in the Calcasieu River (CR) in Lake Charles, LA. [The RSO] stated the Citgo had a Dive team working in the CR to recover the XRF unit. On 01/10/2018 recovery efforts continued. On 01/11/2018 the update indicated the Dive Team effort was unsuccessful and the individuals from CPC would continue the recovery effort. The NRC notification of the 'LOST SOURCE/ UNRECOVERABLE' is being made by LDEQ with this report. "The XRF device, a Niton, Model XLP-703A, loaded with a Cd-109 source with the decayed activity of 12.34 mCi. The Cd-109 source S/N is 10722 and was last leak tested on 10/27/2017. The unit was being used for analysis when it slipped from the operator's control into the CR. A Dive Team Contractor was contacted and an effort made efforts to recover the device on 01/10/18 and 01/11/2018. The sonar and diving search effort was unsuccessful. The source was not recovered, the Dive Team abandoned the effort, and CPC will continue attempts to recover the device. "On 01/11/2018 CPC notified they had lost a XRF Device, Niton Model XLP-703A in the CR that has not been recovered. The battery pack remained with the operator and the shielded device with the Cd-109 source sank into the CR. Scaled back recovery efforts for the device will continue. It is unlikely that the XRF device will be recovered. "This lost Cd-109 source is in a shielded device with river water shielding. This lost source does not pose a health and safety threat to the General Public or the Employees of CPC. "LA Event number: LA-180002" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-01-22
53165 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2018-01-11 10:41 | 2018-01-11 16:06 | 2018-01-11 | SECONDARY CONTAINMENT MOMENTARY LOW PRESSURE "On January 11, 2018, at 1041 EST, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system resulted in the Technical Specification (TS) for secondary containment pressure boundary not being met for less than one minute. The maximum secondary containment pressure observed during that time was approximately 0.117 inches of vacuum water gauge. "Secondary containment pressure was returned to within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS Surveillance Requirement (SR) 3.6.4.1.1 by starting Division 1 of the Standby Gas Treatment System (SGTS) in addition to the RBHVAC system already in operation. Secondary containment pressure is currently stable. Secondary containment was declared Operable at 1045 EST. There were no radiological releases associated with this event. "Declaring secondary containment inoperable as a result of not meeting TS SR 3.6.4.1.1 is reportable under 10CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2018-01-11
53164 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2018-01-10 11:15 | 2018-01-11 12:05 | 2018-01-11 | AGREEMENT STATE REPORT - FILTER REPLACEMENT The following was provided from the State of Tennessee (TN) via email: "The event occurred in the licensee's Metal Melt Facility (MMF). [The Radiation Safety Officer] RSO noted that a 4 inch by 4 inch section of a HEPA filter from the HEPA filter bank was missing. According to RSO, filter bank was pulling from area that has not been active since February 2017. Air effluent stack sampling and real time monitoring system did not indicate elevated radiation levels. The damaged filter was replaced. Licensee will forward investigation report to the TN Division of Radiological Health upon completion." Tennessee Event Report Number: TN-18-007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2018-01-19
53163 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2018-01-09 | 2018-01-10 15:19 | 2018-01-10 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER FAILED TO CLOSE The following information was received via E-mail: "The licensee reported that a shutter on a fixed gauge (Isotope Measuring Systems, Inc. model 5221-02) containing five (5) five curies of Americium-241 sealed sources had one of the five shutters on the device fail to close during device calibration on January 9, 2018. This failure was reported to the Iowa Department of Public Health (IDPH) on January 10, 2018. The licensee has contacted the manufacturer and a service representative will arrive on site Thursday, January 11, 2018 to assess the cause of the shutter failure. IDPH will provide additional information to the NRC after receiving the manufacturer service representatives field report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2018-01-18
53162 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2018-01-10 09:28 | 2018-01-10 13:53 | 2018-01-10 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE CONTROL VALVE FAST CLOSURE SCRAM SIGNAL "At 0928 CST on January 10, 2018, the Unit 3 reactor automatically scrammed due to a Reactor Protection System (RPS) signal generated from Turbine Control Valve Emergency Trip System pressure low. The reactor had been operating near 73 percent power for an emergent issue for Turbine Control Valve (TCV) No. 3. With TCV No. 3 out of service and closed, the unit was operating with RPS in a half scram condition. A subsequent failure of the TCV No. 2 sensing line resulted in RPS coincidence logic being met for TCV fast closure SCRAM. The investigation of the TCV No. 2 sensing line failure continues. "All control rods fully inserted into the core. Main Steam Isolation Valves remained open with Main Turbine Bypass Valves controlling reactor pressure. Reactor Feedwater pumps remained in service to control reactor water level. "Primary Containment Isolation Signals Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. Neither High Pressure Coolant Injection nor Reactor Core Isolation Cooling initiation signals were received. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a preplanned sequence during testing or reactor operation.' It is also reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) and requires an LER within 60 days per 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-01-10
53161 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2018-01-09 | 2018-01-10 11:55 | 2018-01-10 | AGREEMENT STATE REPORT - SOURCE CABLE DAMAGED IN HIGH DOSE RATE AFTERLOADER UNIT The following information was received via E-mail: "On January 9, 2018, the licensee informed the Department [Pennsylvania Department of Environmental Protection] of a problem with their Flexitron HDR [high dose rate] unit. It is reportable per 10 CFR 30.50(b )(2). "After a service provider completed a source exchange on an Elekta Flexitron Model 136149A02 HDR remote afterloader unit containing 9.6 curies of iridium-192 on Friday morning, January 5, 2018, the unit was tested for operation three times and worked properly. At approximately 1400 EST on the January 5, 2018, a hospital physicist was starting his QA procedures on the unit. At that point, the source would not come out of the safe position and he received an error code. The physicist then contacted the service provider and he returned to the site. The service provider tried multiple tasks to get the source to engage, all were unsuccessful. He felt there was some form of obstruction or possibly a drive issue. He then scheduled to be onsite January 9, 2018 with a fellow engineer to further investigate the issue. They discovered the source cable was badly frayed and could not be safely removed and placed into the existing transport containers. Currently, the source and cable have been taped in place so they will not move and the device has been locked in its storage closet at the facility. The Department is in contact with the hospital Radiation Safety Officer and further information is not available at this time. "The Department will perform a reactive inspection. More information will be provided as received." PA Event Report ID No: PA180001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2018-01-18
53160 | -1 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-01-09 19:28 | 2018-01-10 02:13 | 2018-03-08 | <br><br>EN Revision Imported Date : 03/09/18<br><br>EN Revision Text: BOTH TRAINS OF CONTAINMENT AIR RETURN FANS INOPERABLE "During normal power operations at 100 percent power on Unit 2, both trains of Containment Air Return Fans (CARF) were declared inoperable at 19:28 [EST] on January 9, 2018 due to a common issue with control power fuses. The fuses potentially could not handle the in-rush current upon re-energizing the circuits. This condition resulted in a loss of a reasonable expectation that the Unit 2 Containment Air Return Fans would meet their design safety function and mitigate an accident. This loss of safety function is reportable under 10CFR50.72(b)(3)(v)(D), 8 hour report. The site entered T.S. 3.0.3 at 19:28 and exited at 20:54 when repairs to 2B CARF were completed. 2A CARF repairs are complete. There was no impact on the health and safety of the public or plant personnel. The senior NRC Resident Inspector has been notified." The licensee verified this problem does not affect unit-1. * * * RETRACTION AT 0939 EST ON 03/08/2018 FROM JUSTIN BLACK TO TOM KENDZIA * * * "A subsequent evaluation determined that the fuses for the Containment Air Return Fans (CARFs) would be able to perform their safety function and were operable at the time of discovery. The limiting safety condition for the fuses is the return to power following a Loss of Offsite Power (LOOP). The evaluation determined that the fuses would satisfy their safety function upon re-energizing the circuits if a LOOP occurred and would not impact the ability of the CARFs to perform their safety function. The subject fuses were replaced on January 9, 2018." The Licensee notified the NRC Senior Resident Inspector. Notified the R2DO (Musser).<br><br> Original EN Text: BOTH TRAINS OF CONTAINMENT AIR RETURN FANS INOPERABLE "During normal power operations at 100 percent power on Unit 2, both trains of Containment Air Return Fans (CARF) were declared inoperable at 19:28 [EST] on January 9, 2018 due to a common issue with control power fuses. The fuses potentially could not handle the in-rush current upon re-energizing the circuits. This condition resulted in a loss of a reasonable expectation that the Unit 2 Containment Air Return Fans would meet their design safety function and mitigate an accident. This loss of safety function is reportable under 10CFR50.72(b)(3)(v)(D), 8 hour report. The site entered T.S. 3.0.3 at 19:28 and exited at 20:54 when repairs to 2B CARF were completed. 2A CARF repairs are complete. There was no impact on the health and safety of the public or plant personnel. The senior NRC Resident Inspector has been notified." The licensee verified this problem does not affect unit-1. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2018-01-10
53159 | -1 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2018-01-09 17:59 | 2018-01-09 23:38 | 2018-02-28 | <br><br>EN Revision Imported Date : 03/01/18<br><br>EN Revision Text: UNANALYZED CONDITION IDENTIFIED DURING NATIONAL FIRE PROTECTION ASSOCIATION 805 IMPLEMENTATION "On January 9, 2018, at 1759 CST, during review of NFPA 805 requirements and circuit analysis, it was determined that the NFPA 805 analysis and Fire Safe Shutdown Modeling did not consider all fire-induced failures. As such, a condition could possibly exist during a postulated fire where both safety related electrical trains could be impacted. "This notification is to report a condition involving the fire safe shutdown analysis. The condition could result in an adverse impact on the ability of operators to respond to a postulated fire in these areas. Therefore, this notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "Compensatory fire watches have been established in the affected areas." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM ANTONIO BENFORD TO HOWIE CROUCH AT 1752 EST ON 2/28/18 * * * "Following additional refinements to the NFPA 805 Fire PRA Model, the circuits which initiated the initial report of an unanalyzed condition have now been evaluated and have proven that no significant degradation to plant safety existed. Therefore, EN 53159 is being retracted. "The NRC Resident Inspector has been notified." Notified R2DO (Michel).<br><br> Original EN Text: UNANALYZED CONDITION IDENTIFIED DURING NATIONAL FIRE PROTECTION ASSOCIATION 805 IMPLEMENTATION "On January 9, 2018, at 1759 CST, during review of NFPA 805 requirements and circuit analysis, it was determined that the NFPA 805 analysis and Fire Safe Shutdown Modeling did not consider all fire-induced failures. As such, a condition could possibly exist during a postulated fire where both safety related electrical trains could be impacted. "This notification is to report a condition involving the fire safe shutdown analysis. The condition could result in an adverse impact on the ability of operators to respond to a postulated fire in these areas. Therefore, this notification is being made pursuant to 10 CFR 50.72(b)(3)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. "Compensatory fire watches have been established in the affected areas." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2018-01-09
53158 | 0 | CURTISS WRIGHT NUCLEAR DIVISION |  |  |  |  | 2017-10-17 | 2018-01-09 15:28 | 2018-01-09 | PART 21 - FAILURE OF UNDER-VOLTAGE RELEASE MECHANISM The following is a synopsis of information received via E-mail: On October 17, 2017, Palisades alerted Curtiss-Wright of the failure of the under-voltage dropout mechanism in a molded case circuit breaker to trip the breaker in an under-voltage condition. The specific component was a Westinghouse / Eaton Cutler Hammer P/N KD2200U18, containing CAT# UVH3LB08, Style 1492D79G24 under-voltage release mechanism (manufactured prior to 1999). Six of these components were supplied to Palisades in 1992. Findings indicated that the under-voltage release mechanism's failure was a result of a misalignment of the solenoid due to excessive play in the design/manufacturing process which allowed the plunger to miss the target that would cause the breaker to trip in an under-voltage condition. Palisades identified this failure and mentioned two previous failures, one in 1996, and one in 2009. The under-voltage trip mechanism was redesigned in the 1997-1998 time frame. The new design has not exhibited any reported failures. The observed failure on a 1992 breaker having failed in the installed condition took 50 trials to repeat the failure. Given that the excessive play could be a result of combined tolerances, worn tooling, as well as the design itself, and since the OEM has redesigned this mechanism almost 20 years ago, Curtiss-Wright would recommend end users to conduct their own evaluation to determine if a defect, which could create a substantial safety hazard, exists. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2018-01-09
53157 | 0 | MASSACHUSETTS INSTITUTE OF TECH |  |  |  | 6000 KW TANK RESEARCH HW | 2018-01-08 16:00 | 2018-01-09 11:01 | 2018-01-09 | TECHNICAL SPECIFICATION VIOLATION "On January 8, 2018, two in-core experiments were removed from their in-core positions at a time when one of the two minimum required Neutron Flux Level instruments was inoperable. "This is in violation of Technical Specification No. 3.2.3, Specification No. 2." The reactor was shutdown for maintenance at the time of the event. The licensee notified their NRR Project Manager (Boyle). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MA | NPR | [5 empty] | 0 | 2018-01-09
53156 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2018-01-03 | 2018-01-08 17:36 | 2018-01-08 | AGREEMENT STATE REPORT - NUCLEAR GAUGE INVOLVED IN A FIRE The following information was received via E-mail: "The Radiation Safety Officer (RSO), reported Friday, 1/5/2018 that a fire occurred on 1/3/2018 at the refinery in the Coker Unit Drum D. The RSO made the Department [Louisiana Department of Environmental Quality (LDEQ)] notification when the area cooled and he could assess the situation. "The Louisiana State Police were notified on 1/3/2018 at approximately 1530 CST. The Department was notified at approximately 1330 CST on 1/5/2018 when the situation had been assessed after the unit cooled enough for entry. "A level/density gauge on Coker Process Drum D was involved in a unit fire. The level/density gauge was an Ohmart-Vega device/source holder, model SHG1-45, S/N 3813CP housing 500 mCi of Cs-137 S/N 26165309. "On 1/3/2018, ExxonMobil Refining & Supply had a fire on the Coker unit in Drum D. In the assessment process of the radiation sources from becoming a radiation exposure hazard, it was discovered that the gauge/device shielding was compromised through a melted opening in the lead shielding. "ExxonMobil called a service contractor, BBP Sales, to evaluate the situation and determine the best course of action to correct the problem. The service contractor was unable to repair the device/source holder and determined the source holder would have to be replaced. This is not a radiation exposure hazard and does not pose a health and safety situation for the ExxonMobil employees or the general public. "The source holder was intact for the most part with the exception of a degraded/melted spot on the shielding. The radiation exposure level from the opening was 30 mR/hr at 1 ft. BBP Sales was notified and called in to make an assessment and recommendation for corrective action of this situation. BBP Sales locked the shutter, secured the device, placed it in a storage container and isolated the storage container. Some additional lead was placed over the opening and the exposure reading was reduced to approximately 4 mR/hr. The storage container was placed behind a radiation labeled barricade. It is considered in storage until it is replaced and the damaged level gauge is shipped for disposal. The 500 mCi Cs-137 source did not appear damaged or compromised. The RSO performed wipes on the device and the wipes were sent to Suntrac Services for analysis. "This event is considered closed for reporting requirements by LDEQ. This is not equipment failure. This event is a level/density gauge damaged in a refinery fire. This event is being reported to the NRC as required by Regulatory Requirement 10 CFR 30.50(b)(4) and LAC 33:XV.341.B.4" Louisiana Event Report ID No.: LA-180001; SPOC T182036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2018-01-16
53155 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2018-01-07 | 2018-01-08 16:40 | 2018-01-08 | AGREEMENT STATE REPORT - NUCLEAR GAUGE SHUTTER FAILED TO SHUT The following information was received via E-mail: "On January 8, 2018, the Agency [Texas Department of State Health Services] received a report from the licensee's radiation safety officer (RSO) stating the shutter on an Ohmart Vega model SH-F1 gauge, containing a 60 milliCurie cesium-137 source, failed to shut during an operational check. Open is the normal operation position of the gauge shutter. No licensee employee received any exposure as a result of this event. The gauge was repaired the following morning. An investigation into this event is ongoing. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-01-16
53154 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-01-06 11:26 | 2018-01-06 18:14 | 2018-01-06 | MAIN STEAM LINE RADIATION MONITOR DETERMINED TO BE NON-FUNCTIONAL "At 1126 [CST], main steamline radiation monitor 2-RE-2326 (Main Steamline 2-02) reading was determined to be erratic and was declared non-functional. "With this radiation monitor non-functional, all of the emergency action levels for a steam generator tube rupture in steam generator 2-02 could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant [CPNPP] has assurance of steam generator integrity and fuel cladding integrity and there is a negligible safety significance to the current condition from a public health and safety perspective. "Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator or fuel cladding. The N16 [Nitrogen-16] radiation monitor serves as a backup with alarm function and Radiation Protection technicians have been briefed on taking local readings with a Geiger-Mueller tube on MSL [Main Steam Line] 2-02. "Corrective actions are being pursued to restore 2-RE-2326 to functional status. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-01-06
53153 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2018-01-06 05:24 | 2018-01-06 06:05 | 2018-01-06 | DECLARATION OF UNUSUAL EVENT DUE TO ABNORMAL INTAKE STRUCTURE LEVEL "Oyster Creek Declared an Unusual Event HU 6 Hazardous Event for an Abnormal Intake Structure Level Less than or equal to -3.0 feet MSL [Mean Sea Level] on points 23 and 24 in the Main Control Room at time 0524 [EST]." The licensee notified the NRC Resident Inspector, State, and local authorities. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 1/6/18 AT 2325 EST FROM JAMES RITCHIE TO BETHANY CECERE * * * "Oyster Creek Terminated Unusual Event HU 6 Hazardous Event for an Abnormal Intake Structure Level at time 2308 [EST]." The licensee notified the NRC Resident Inspector, State, and local authorities. Notified R1DO (Werkheiser), NRR EO (King), IRD MOC (Gott), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2018-01-06
53152 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-11-01 | 2018-01-05 16:48 | 2018-01-05 | AGREEMENT STATE REPORT - POSSIBLE OVEREXPOSURE The following was excerpted from an email received from the State of Florida: "Received a notification letter from a licensee [NDE, Inc.] reporting a possible overexposure. According to the [Radiation Safety Officer] RSO for NDE, an employee had the leather pouch that his badge and his pocket dosimeter were in cut open resulting in his badge falling out near where radiography was taking place. The missing badge was discovered during a routine check of his pocket dosimeter which read 2 mRem for the shift. The badge was sent to Landauer for analysis and the recorded dose for the time period of Oct. 10 - Nov. 9, 2017 was 23.420 Rem. After conducting interviews, the RSO concluded that the overexposure was due to the badge being so close to the source, and the employee did not receive the recorded dose. After compiling the daily pocket dosimeter readings, the estimated dose to the employee would have been 57 mRem for that time period." Incident Number: FL 18-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2018-01-15
53151 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2017-11-22 | 2018-01-05 17:16 | 2018-01-05 | PART 21 - DEFECT IN THERMOSTATIC VALVE ASSEMBLIES The following information was excerpted from a facsimile received from Engine Systems, Inc.: "Two thermostatic valve assemblies were supplied by [Engine Systems, Inc.] ESI that were found to have retaining straps, subcomponents of the internal thermostatic element, detached from the correct position. For each valve assembly, one of the thermostatic elements (the centrally located element) contained this defect. The straps are used in conjunction with a spring to retain the element in a closed position. As the temperature of the sensed fluid increases, a temperature sensitive wax expands to open the element while acting against the spring. As the temperature of the fluid decreases, the wax contracts and the spring returns the element to its closed position. Absence or failure of the straps would prevent proper operation of the element. "The thermostatic valve assembly is used on an emergency diesel generator [EDG] set to regulate the temperature of lubricating oil (other EDGs use this same type of valve for jacket water temperature regulation). If one of the elements within the assembly were to fail, as is the case with a missing strap, regulating capacity of the thermostatic valve could be affected. However, the failure mode in the case of missing straps is in the open position (element does not return closed) and the remaining eight elements would compensate by closing to regulate the fluid temperature. More importantly, detached retaining straps could migrate to other components in the lube oil system. Acting as foreign material, the straps could adversely affect the ability of these critical components to perform their safety-related function within the emergency diesel generator's lube oil piping. The foreign material aspect of this defect makes it a reportable issue. "Information of such defect or failure to comply was obtained on November 22, 2017. "This issue is an isolated incident affecting two thermostatic valves supplied to one nuclear plant [DC Cook]. The nuclear plant detected the issue during inspection and returned the assemblies to ESI. No further action is required on the part of DC Cook. "ESI's investigation revealed that this issue was induced by a test technician who, in an effort to minimize the amount of test fluid remaining in the assembly after pressure testing, manually actuated the center thermostatic element (there are 9 total elements) to drain a small pocket of residual fluid. This effort to prevent the formation of oxidation had an unintended consequence and resulted in a more serious issue. Though this is an isolated incident as it pertains to items supplied from ESI, this same model thermostatic valve assembly is used extensively on EDGs in the nuclear industry. Those customers that perform valve maintenance, including thermostatic element replacement, should be aware of the possibility of the straps becoming detached if care is not taken." If you have any questions, you may call: Tom Horner Quality Assurance Manager Tel: (252) 977-2720 ESI Report ID: 10CFR21-0120, Rev. 0, dated 01/05/18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2018-01-05
53150 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-11-06 | 2018-01-05 16:12 | 2018-01-05 | AGREEMENT STATE REPORT - STUCK SHUTTERS ON FIXED NUCLEAR GAUGES The following was excerpted from an email received from the state of South Carolina: "On January 5, 2018, the licensee called [South Carolina Department of Health and Environmental Control] to provide notification of stuck shutters on 2 sets of three-rod Berthold Model LB300L fixed gauging devices. The shutters were stuck in the open position. The gauging devices contain Co-60 in amounts of 0.11, 0.41, and 1.81 milliCuries in one and 0.189, 0.5, and 1.50 milliCuries in the other. The [licensee's] Radiation Safety Officer found the shutter stuck in the open position on November 6, 2017 and the licensee notified the State on January 5, 2018. The licensee called Berthold to come out to evaluate corrective measures on the shutter mechanisms. Berthold technicians came to the plant on December 19, 2017. After being informed of proper procedures on reporting requirements, the licensee stated that a written report will be sent within 30 days of the event. "Updates to this event will be made through the NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2018-01-15
53149 | 0 | VIRGINIA OFFICE OF RAD HEALTH |  |  |  |  | 2018-01-04 | 2018-01-05 12:16 | 2018-01-05 | AGREEMENT STATE REPORT - STUCK SOURCE IN DENSITY GAUGE The following report was received via email from the Virginia Office of Radiological Health: "On January 4, 2018, the Radiation Safety Officer of the licensee reported that the metal (insertion) rod that enables the source holder to move to its 'ON' position (moves the source in and out of the vessel) broke during routine periodic maintenance. The gauge is a Texas Nuclear Model 50315, serial number B0047, with a 100 milliCurie Cesium-137 source (effective 1993). The gauge is used to measure the density of material inside a process vessel. The gauge is currently in its normal operative state, which is to send a signal to the detector to control density in the vessel. The source was pushed back into the vessel to allow for normal operation after the rod broke, but it is not able to be removed. The licensee has contacted ThermoFisher Scientific for further actions." Virginia Event Report ID No.: VA-18-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2018-01-15
53148 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2018-01-04 | 2018-01-05 08:30 | 2018-01-05 | AGREEMENT STATE REPORT - DELIVERED DOSAGE DIFFERENT FROM PRESCRIBED The following was received from the State of Wisconsin: "On January 4, 2018, the Department [Wisconsin Radiation Protection Section] received a telephone call and email from the licensee's medical physicist that a medical event of a prostate brachytherapy procedure was identified on January 4, 2018. The total dose delivered differs from the prescribed dose by 20% or more. This is a medical event as described in DHS [Department of Health Services] 157.72(1)(a)1.a. The prescribed dose was 145 Gy; the dose delivered was 105 Gy. The licensee uses D90 (dose delivered to 90% of the clinical target volume) < 80% for determining medical events. Using the licensee's dose based criteria; the dose received by the prostate was 75% of the intended dose. The post-implant computed tomography scan occurred on December 6, 2017. The subsequent dosimetric analysis was on January 3, 2018. The department will perform a site investigation to determine the root cause of this medical event. "DHS inspectors will investigate this medical event." Wisconsin Event: WI180001 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2018-01-15
53147 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2018-01-04 14:10 | 2018-01-04 17:57 | 2018-01-04 | MANUAL REACTOR SCRAM DUE TO PARTIAL LOSS OF OFFSITE POWER DURING WINTER STORM "On January 4, 2018, at 1410 hours EST, with the reactor at approximately 100 percent power and steady state conditions, the winter storm across the Northeast caused the loss of offsite 345 kV Line 342. Reactor power was reduced to approximately 81 percent and a procedurally required manual reactor scram was initiated. All control rods fully inserted. "As a result of the reactor scram, indicated reactor water level decreased, as expected, to less than +12 inches resulting in automatic actuation of the Primary Containment Isolation Systems for Group II - Primary Containment Isolation and Reactor Building Isolation System, and Group VI - Reactor Water Cleanup System. "Reactor Water Level was restored to the normal operating band. The Primary Containment Isolation Systems have been reset. The Reactor Protection System signal has been reset. "Following the reactor scram, the non-safety related Control Rod Drive Pump "B" tripped on low suction pressure. Control Rod Drive Pump "A" was placed in service. All other systems operated as expected, in accordance with design. "This event is reportable per the requirements of Title 10, Code of Federal Regulations (CFR) 50.72 (b)(2)(iv)(B) - "RPS Actuation" and 10 CFR 50.72 (b)(3)(iv)(A) - "Specified System Actuation." "This event had no impact on the health and/or safety of the public. "The NRC Resident Inspector has been notified." The main steam isolation valves are open with decay heat being removed via steam to the main condenser. Offsite power is still available from 345kV line 355. As a contingency, emergency diesel generators are running and powering safety busses per licensee procedure. The licensee notified the Commonwealth of Massachusetts. The licensee will be notifying the town of Plymouth as part of their local notifications. The licensee will be issuing a press release. | 0 | 0 | 0 | 81 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2018-01-04
53146 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2018-01-02 | 2018-01-03 15:29 | 2018-01-03 | AGREEMENT STATE REPORT - PACKAGE DAMAGED IN TRANSIT The following information was received via E-mail: "This First Notice constitutes early notice of events of possible safety or public interest significance. The information is as initially received without verification or evaluation, and is basically all that is known by the Department [Arizona Department of Health Services] staff at this time. "On January 2, 2018 at approximately 1745 MST, the Department received notification from the licensee of a damaged package containing ten densometers, with each densometer having an activity of 10 milliCuries of Americium-241. The licensee performed a survey of the package and obtained a reading of 25 mrem/hr on contact at the bottom of the package. The Agency continues to investigate the event." Arizona First Notice: 18-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2018-01-11
53145 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2018-01-02 22:00 | 2018-01-03 11:03 | 2018-01-03 | AGREEMENT STATE REPORT - TWO PORTABLE NUCLEAR GAUGES STOLEN The following was excerpted from an email received from the State of New Jersey: "RSO [Radiation Safety Officer] reported that 2 portable nuclear gauges were stolen from the lab. A police report has been filed with the Woodbridge, NJ police department." "The gauges each contain: Cs-137 (10 mCi or under each) and Am/Be-241 (44 mCi or under each)." * * * UPDATE FROM JACK TWAY TO DONALD NORWOOD AT 1527 EDT ON 1/3/2018 * * * The following was excerpted from an email received from the State of New Jersey and provides specific information about the gauges that were stolen: 1. Troxler Model 3411B, s/n 16739 containing Cs-137, not to exceed 9 mCi, AEA Technology/QSA, Inc. Model No. CDCW556 or IPL Model No. HEG-137, and Am-241/Be, not to exceed 44 mCi, AEA Technology/QSA, Inc. Model No. AMNV.997 or IPL Model No. AM1.NO2, 3021 or 3027. 2. Troxler Model 3411B, s/n 18556 containing Cs-137, not to exceed 9 mCi, AEA Technology/QSA, Inc. Model No. CDCW556 or IPL Model No. HEG-137, and Am-241/Be, not to exceed 44 mCi, AEA Technology/QSA, Inc. Model No. AMNV.997 or IPL Model No. AM1.NO2, 3021 or 3027. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2018-01-11
53144 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-12-01 | 2018-01-03 09:49 | 2018-01-03 | AGREEMENT STATE REPORT - OVEREXPOSURE EVENT The following was excerpted from an email received from the state of Georgia: "On Tuesday, January 2, 2018 it was reported to the Department [Georgia Radioactive Materials Program] by Theragenics Corporation in Buford, GA that an employee's dosimetry report indicated that he had exceeded the annual shallow dose limit of 50 rem. An investigation has been conducted by the employer and it was determined that two abnormal occurrences happened during this wear period: "1. For approximately 2 hours the technician worked a non-routine job to clean and rebuild the central region of a cyclotron in order to return the cyclotron to operation. This was designated as a high radiation area and exposures of others that worked the same job had high exposures also but no one else exceeded the annual limits. "2. On November 13, 2017 the cyclotron technician was having difficulty operating the manipulator arms and pneumatic screwdriver within a hot cell so without contacting HP [health physics] or cyclotron management he decided to remove 10 screws in the target rail of the hot cell by hand. He held target rails with his left hand and removed the screws with a screwdriver with his right hand. The projected activity on that day was 62.61 Ci and the job took 1 to 5 minutes. "Theragenics was notified of the event on December 1, 2017. The report was sent to the department [Georgia Radioactive Materials Program] on December 28, 2017 and was received on January 2, 2018 "The skin exposure to the left extremity was reported as 71.865 rem for the biweekly monitoring period of November 6, 2017 to November 19, 2017." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2018-01-11
53143 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-01-02 11:37 | 2018-01-02 17:17 | 2018-01-02 | UNPLANNED LOSS OF EMERGENCY RESPONSE EQUIPMENT DUE TO LOSS OF PLANT COMPUTER "At 1137 CST on January 2, 2018, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 experienced an unplanned loss of the Plant Computer System (PCS). The loss of the Unit 2 PCS resulted in a loss of emergency assessment capability to the CPNPP Technical Support Center (TSC) and Emergency Operations Facility (EOF) for greater than 60 minutes. "This report is being made pursuant to 10 CFR 50.72(b)(3)(xiii), any event that results in a loss of emergency assessment capability, off-site response capability, or off-site communications ability. "The NRC Resident Inspector has been informed." Repairs are on-going. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2018-01-02
53142 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2017-12-30 07:17 | 2018-01-02 13:16 | 2018-01-02 | TECHNICAL SPECIFICATION REQUIRED REPORT FOR AN ABNORMAL OCCURRENCE "On 12/30/17 at 0717 CST, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to the loss of negative pressure in the reactor containment building. Prior to the shutdown, the reactor was operating for a period of time during the loss of negative pressure which is a deviation from MURR Technical Specifications (TS). This email is a required notification per TS 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1, had occurred. Specifically, MURR was not in compliance with all TS Limiting Conditions for Operations (LCOs). MURR was not in compliance with TS's 3.4.b and 3.4.a.(6). "TS 3.4.b. states, 'Reactor containment integrity shall be maintained at all times except when: (1) The reactor is secured...' TS. 3.4.a.(6) states, 'For reactor containment integrity to exist, the following conditions shall be satisfied:...(6) The reactor containment building is at a negative pressure of at least 0.25 inches of water with respect to the surrounding areas: and...' "While on Routine Patrol on the morning of 12/30/17, an operator noted that the differential pressure gauge between the reactor containment building and the MURR laboratory building was reading zero (0.0) inches of water vacuum. The operator on Routine Patrol radioed the Lead Senior Reactor Operator in the Control Room, and the reactor was shut down. The cause of the loss of negative pressure was the closing of a backup ventilation exhaust door from the reactor containment building. With the backup ventilation exhaust door closed, the ventilation system was only supplying air to the reactor containment building, not allowing a balanced air recirculation to maintain a negative pressure. "The backup ventilation exhaust door actuator was found to be inoperable. The backup ventilation exhaust door operation was repaired by melting ice that had formed in the air supply lines to the door's operating air cylinder. Condensation that had formed in the air lines was removed, and heat trace and insulation were installed around all the backup door air supply lines. The compliance procedure for verifying backup ventilation doors' operability was conducted satisfactorily as post-maintenance testing. Permission from the Interim Facility Director was obtained prior to the reactor returning to operation later on 12/30/17. A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2018-01-02
53141 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2018-01-01 10:15 | 2018-01-01 12:45 | 2018-01-01 | OFFSITE NOTIFICATION - EMERGENCY NOTIFICATION SIREN INADVERTENT ACTUATION "A South Texas Project Offsite Emergency Notification siren (#7) was inadvertently going off. The Matagorda County Sheriff's office notified the Emergency Response Organization at the station of the siren actuation. Station personnel are addressing the issue with the siren. "The Matagorda County Sheriff's office was the only offsite agency that was contacted during this event. "This notification is being made under 10CFR50.72(b)(2)(xi) as an event where other government agencies were notified." The licensee has personnel at the siren which is no longer alarming (1.5 hours after alarm notification). The licensee notified the NRC Resident Inspector | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2018-01-01
53140 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2016-09-29 11:00 | 2017-12-29 13:00 | 2017-12-29 | PACKAGE RECEIVED WITH REMOVABLE SURFACE CONTAMINATION EXCEEDING APPLICABLE LIMITS "Consistent with paragraphs 111.1 and V.1 of the NRC Confirmatory Order of December 14, 2017 in EA-17-090, GNF-A makes the following report. "GNF-A [Global Nuclear Fuels - Americas] is making this report to the NRC Operations Center, pursuant to 10 CFR 20.1906(d)(1) to state that the NRC has concluded GNF-A received a package on September 29, 2016, which had removable radioactive surface contamination on its external surfaces that exceeded the applicable limits set forth in 10 CFR 71.87(i). "This report is solely for the purposes of reaching resolution from an October 25, 2017 alternative dispute resolution because GNF-A maintains that the removable radioactive surface contamination on the external surfaces of the package (an open metal dumpster) and the removable surface contamination on scrap pipes contained in the dumpster did not exceed the applicable limits set forth in 10 CFR 71.87(i). "Safety Significance of Event: At no time was an unsafe condition. "Status of Corrective Action: Issue resolved during Alternative Dispute Resolution." The licensee will inform the NRC Region II Project Manager, State of North Carolina and New Hanover County Emergency Management. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 20.1906(d)(1) |  |  |  | 0 | 2017-12-29
53139 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-12-29 | 2017-12-29 12:13 | 2017-12-29 | AGREEMENT STATE REPORT - LOST CATEGORY 2 RADIOGRAPHY EXPOSURE DEVICE The following information was received via E-mail: "On December 29, 2017, the Agency [Texas Department of State Health Services] received a call from the licensee's corporate radiation safety officer (CRSO) reporting a lost exposure device. The CRSO stated one of the licensee's radiographers at one of their licensed storage locations had placed a QA model D880 exposure device (serial # D15021) containing a 40.9 curie iridium-192 source on the tailgate of the truck at the licensee's Beaumont location. The radiographer left the licensee's location and headed to their work location. When the radiographer reached Groves, Texas, they realized they had not secured the device and pulled over. The device was not on the tailgate. The radiographer contacted the radiation safety officer and a search was begun. The CRSO stated at least two teams are searching the route looking for the device. The distance to be searched is about 20 miles based on the current information. The CRSO stated the device did have both storage caps on the device. The CRSO stated the dose rate on the device was 17 millirem on contact with a TI [Transportation Index] of 0.4. The CRSO stated they have contacted local law enforcement who are responding to the licensee's location. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9528 Notified External: DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, and EPA EOC. Notified External via E-mail: Mexico, FDA EOC, NuclearSSA, FEMA National Watch Center, DNDO-JAC. * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 1638 EST ON 12/29/2017 * * * The following information was received via E-mail: "The missing device has been found. Additional information will be provided in accordance with SA-300." * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 1700 EST ON 12/29/2017 * * * The following information was received via E-mail: "The Agency received the following information on the event. The radiographers did not go to Grove Texas, but only made it to Nederland, Texas making the search area between 8 and 10 miles. At the time the device was recovered approximately 40 people were searching for it on foot. The searchers included firefighters, emergency response personnel, and licensee personnel. Pictures of the device show the outer coating was scratched, but the device itself did not appear damaged. Additional information will be provided as it is received in accordance wit SA-300." Notified Internal NRC: R4DO (Haire), NMSS Regional/INES Coordinator (Rivera-Capella), IRD MOC (Grant), ILTAB (Davis), and NMSS Events Notification. Notified External: DHS SWO, FEMA Ops Center, USDA Ops Center, HHS Ops Center, DOE Ops Center, DHS NICC Watch Officer, and EPA EOC. Notified External via E-mail: Mexico, FDA EOC, NuclearSSA, FEMA National Watch Center, DNDO-JAC. THIS MATERIAL EVENT CONTAINS A "CATEGORY 2" LEVEL OF RADIOACTIVE MATERIAL Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2018-01-08
53138 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-11-01 | 2017-12-28 12:50 | 2017-12-28 | AGREEMENT STATE REPORT - TOTAL DOSE DELIVERED DIFFERED FROM PRESCRIBED DOSE BY GREATER THAN 20% The following information was received from the State of Wisconsin via email: "On December 28, 2017, the Wisconsin Department of Health Services (DHS) received notice that the licensee identified a prostate manual brachytherapy procedure where the total dose delivered differed from the prescribed dose by 20% or more. The implant occurred in November 2017 and post-implant dosimetric analysis was performed on December 27, 2017. The prescribed dose was 110 Gy; the dose delivered to the treatment site (D90) was 56.5% of the intended dose. "DHS inspectors will investigate this medical event. "Event Report ID No.: WI170023" The licensee will compensate for the underdose with subsequent scheduled beam therapy. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2018-01-05
53137 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2017-12-22 23:48 | 2017-12-23 05:00 | 2017-12-23 | HIGH PRESSURE CORE SPRAY SYSTEM DECLARED INOPERABLE "High Pressure Core Spray System was declared inoperable due to the discovery of a through-wall leak on the Minimum Flow line. Leak rate is 60 drops per minute from ASME Class 2 Piping. The leak has been isolated and the High Pressure [Core Spray] System has been placed in Secured Status. "High Pressure Core Spray is considered a single train safety system. Inoperability of [the] High Pressure Core Spray System is considered an event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D). "The NRC Senior Resident Inspector was notified." Technical Specifications Limiting Condition for Operation 3.5.1 Condition B was entered, requiring restoration of the High Pressure Core Spray System in 14 days. The licensee plans to notify State and Local Governments (Lake, Geauga, and Ashtabula Counties). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-12-23
53136 | -1 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-12-06 16:48 | 2017-12-22 16:40 | 2020-01-30 | AGREEMENT STATE REPORT - NUCLEAR MEDICINE EMPLOYEE OVER EXPOSURE The following report was received via e-mail: "On December 6, 2017, the Radiation Safety Officer at Glendale Adventist Medical Center notified the Principal Radiation Protection Specialist at Los Angeles County Radiation Management that at Glendale Adventist Medical Center, a nuclear medicine employee had unusually high readings on his Landauer dosimeters over the last several months: 490 mrem DDE [deep dose equivalent](July 2017), 490 mrem DDE (August 2017), 892 mrem DDE (September 2017), 12,870 mrem DDE (October 2017), and 166 mrem DDE (November 2017)." California Report: 120617 * * * RETRACTION ON 1/30/2020 AT 1232 EST FROM THOMAS MIKO TO ANDREW WAUGH * * * The following information was received from the state of California via email: "The Radiation Safety Officer at Glendale Adventist Medical Center in Glendale, California performed an in-house investigation, and has stated in his report to Los Angeles County that he does not believe that the employee actually received the exposures recorded on his dosimeters. Policy and procedure changes were implemented to avoid having employee dosimeters artificially exposed to x-ray equipment (while not being worn by the employee), which they believe to be the cause of the elevated exposure reports. Los Angeles County did not rescind this report until now, because they waited to perform reviews of the same employee's dosimetry records for the length of 2018 and 2019. No new incidents have occurred. Please rescind the attached report that was submitted in December of 2017." Notified R4DO (Dixon) and NMSS Events (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2018-01-01
53135 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-10-25 20:50 | 2017-12-22 11:09 | 2017-12-22 | INVALID ACTUATION OF COOLING WATER SYSTEM "At 2050 [CDT] on October 25, 2017, during the Unit 2 refueling outage, with no fuel in the Reactor Vessel, control room operators found that Unit 1 Train B Containment Fan Coil Units (FCUs) had swapped from chilled water to cooling water (CL). Construction Electricians were installing a new relay 2Sl-22X when the plunger on adjacent relay 2Sl-23X was bumped, which caused the swap of the Unit 1 Containment Fan Coil Units (CFCUs) from chilled water to cooling water. Relay 2SI-23X is a slave relay that starts 22 Turbine Driven Auxiliary Feed Water Pump, illuminates blue lights on various control switches, closes MV-32159 Loop A/B CLG WTR HDR XOVR MV B, closes chilled water Isolation Valves to Unit 1 Train B, and closes chilled water Isolation Valves to Unit 2 Train B. "This actuation was as expected. CL is a shared system and, upon a Safety Injection (SI) signal on either unit, the CL header splits into two trains and, as a result, the CL supply is isolated to the chillers that supply chilled water to both units' CFCUs. By design, CL is the safety related source of cooling to the CFCUs. "22 Turbine Driven Auxiliary Feed Water Pump did not start as the unit was in 'No Mode' with the control switch for the pump in manual. MV-32159 did automatically close per design. Unit 2 Chilled Water was already isolated due to work in progress with the unit in 'No Mode.' "There was no impact on public health and safety. "This event is being reported as a 60-day telephone notification in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an invalid actuation of a containment heat removal system (the FCUs were running, but were swapped to their safeguards source due to an invalid actuation of a relay)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Defueled |  | Power Operation | Defueled |  | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-12-22
53134 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-10-23 08:56 | 2017-12-22 11:09 | 2017-12-22 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATOR "At 0856 [CDT] on October 23, 2017, during the Unit 2 refueling outage, with no fuel in the Reactor Vessel, an unexpected auto start of the Unit 2 Train B Emergency Diesel Generator (D6) occurred when construction electricians inadvertently bumped the plunger for relay 2Sl-20X while working in the relay rack. Relay 2Sl-20X is a slave relay that actuates a light on the control board, starts D6, and starts 22 Residual Heat Removal (RHR) pump on a Safety Injection signal. In this instance, the RHR pump did not start as its control switch was in pull-out. It is expected that the control board light lit for the brief time the relay plunger was depressed, but this could not be confirmed. The D6 actuation resulted in an unexpected annunciator for D6 EMERGENCY GENERATOR SI SIGNAL EMERGENCY START. Operators responded per the alarm response procedure, performed a walk down of running D6 and then performed a shutdown of D6. D6 started and functioned as expected. "There was no impact on public health and safety. "This event is being reported as a 60-day telephone notification in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an invalid actuation of an emergency diesel generator." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Defueled; FMode2: Defueled | NON EMERGENCY | 3 | MN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-12-22
53133 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-12-20 15:59 | 2017-12-20 21:22 | 2017-12-20 | EMERGENCY ALERT SYSTEM OUT OF SERVICE "During review of the documentation for the 11/16/17 outage of the NOAA/NWS [National Oceanographic and Atmospheric Administration/National Weather Service] tower, it was identified that there was also record of a trouble ticket being issued on 11/19/17 for the NOAA/NWS tower. Further discussions with the National Weather Service determined that the tower did experience an outage on 11/19/17 which affected the ability to activate EAS [Emergency Alert System]/Tone Alert Radios. Final determination that the EAS/Tone Alert Radios were affected during this outage was made at 1559 [CST], which was the time that the National Weather Service sent the e-mail to the EP [Emergency Planning] Manager and EP Offsite Coordinator with notification that activation of the EAS/Tone Alert Radios was affected during the outage. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10CFR 50.72(b)(3)(xiii). "The transmission outage was on 11/19/2017 0853 until 1100 but CNS [Cooper Nuclear Station] was not notified until 1559 on 12/20/2017. "The NRC Senior Resident has been informed" | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-12-20
53132 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-12-20 10:40 | 2017-12-20 18:18 | 2017-12-20 | SYSTEM ACTUATIONS DUE TO OPENING OF FEEDER BREAKER TO SHUTDOWN BOARD "On December 20, 2017, at 1040 Eastern Standard Time (EST), the Watts Bar Nuclear Plant (WBN) 1B-B 6.9kV Shutdown Board (SDBD) normal feeder breaker opened. The loss of voltage to the 1B-B SDBD resulted in the start of the 1B-B Motor Driven Auxiliary Feedwater (MDAFW) pump, the Unit 1 Turbine Driven Auxiliary Feedwater (TDAFW) pump, and the start of all four Emergency Diesel Generators (EDGs). Power was restored to the 1B-B 6.9 kV SDBD when it loaded on to its associated EDG. "Following initial investigation, the 1B-B 6.9 kV SDBD was transferred to its alternate offsite power source, Common Station Service Transformer (CSST) C at 1217 EST. At 1230 EST, the 1B-B 6.9 kV SDBD alternate feeder breaker opened. The loss of voltage to the 1B-B SDBD did not result in the restart of the 1B MDAFW pump, the Unit 1 TDAFW pump, or EDGs; this equipment remained running from the earlier event. Power was restored to the 1B-B 6.9 kV SDBD when it loaded on to its associated EDG. "Restoration of normal offsite power to the 1B-B SDBD was completed at 1654. "Other than several common Unit Technical Specifications having not been met, Unit 2 was not operationally impacted by the transfer of the 1B-B Shutdown Board to onsite power and remains in Mode 1 at 100% power. "This report is made per 10 CFR 50.72(b)(3)(iv)(A). "NRC Resident Inspector has been notified." The licensee investigation continues for the cause of the event. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-12-20
53131 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-12-20 | 2017-12-20 09:29 | 2017-12-20 | AGREEMENT STATE REPORT - VEHICLE ACCIDENT INVOLVING A TROXLER GAUGE The following was received via email from the State of Florida: "Vehicle accident involving a transported Troxler gauge. Driver rear ended the vehicle in front and was transported to hospital. Troxler case was in back of pick up truck and apparently suffered a broken clasp but gauge still intact. [Florida State Inspector] is responding to investigate and take possession of the gauge until the RSO arrives on scene." Incident Number: FL17-300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-12-28
53130 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-11-09 | 2017-12-19 17:40 | 2017-12-19 | AGREEMENT STATE REPORT - POTENTIAL OVER-EXPOSURE The following was excerpted from an email received from the State of Florida: The State of Florida received a notice of an over-exposure from the licensee. An employee received a whole body dose of 5019 mR read on her dosimeter on 10/10/2017. The investigation determined that the most likely cause of the over-exposure was due to an unusual number of equipment failures with the synthesis units requiring employee intervention to correct the issues. Dose rates and doses to the employee were not being monitored real time. The employee has been retrained on the standard operating procedures. Alarming personal electronic dosimeters have been purchased and are in use to alert personnel of the radiation fields. Florida Incident Number: FL17-299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-12-27
53129 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-11-14 | 2017-12-19 18:28 | 2017-12-19 | AGREEMENT STATE REPORT - STOLEN AND RETRIEVED TROXLER GAUGE The following information was excerpted from an email received from the State of Florida: The State of Florida received a notice on 11/15/17 that a Troxler Gauge and a company vehicle was stolen from the licensee by an employee. A City of Orlando Police report was issued (2017-442672). On 12/7/2017, a notice was received from the licensee to inform State of Florida Bureau of Radiation Control that the gauge was found intact and undamaged. The Troxler moisture density gauge is a model number 3440; serial number 27931; Cs-137/AmBe; 8mCi/40mCi. Florida Incident Number: FL17-298. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-12-27
53128 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2017-12-19 13:40 | 2017-12-19 17:17 | 2018-02-14 | <br><br>EN Revision Imported Date : 02/15/18<br><br>EN Revision Text: DIESEL GENERATORS (DGs) DECLARED INOPERABLE DUE TO A COMMON ISSUE "During regular power operations at 100% power, DG#1 and DG#2 were declared inoperable due to a common issue associated with indicating lights and the associated sockets installed in various control and auxiliary circuits for both DG's. "The indicating lights in question are incandescent 120V AC style 120MB bulbs in a socket with a 550 ohm resistor. Style 120MB light bulbs have a failure mechanism where the bulb can cause a short circuit rather than the more common open circuit that is expected when an incandescent bulb filament fails. Cooper originally believed that the socket's integral resistor was sufficient to protect the circuit. In testing performed by an outside laboratory and confirmed on-site using warehouse stock, it was determined that the integral resistor may not have the power dissipation capability to protect the circuit ln which the light and socket are installed if a bulb fails in short circuit. "This condition resulted in both DG's being declared inoperable at 1340 [CST] due to a loss of reasonable expectation that they would meet their safety function required action to start, load and run to support loads required to mitigate the consequences of an accident. This is a loss of safety function under 10CFR 50.72(b)(3)(v)(D) subject to an 8 hour report. "As a result of both DG's being inoperable, the Control Room Emergency Filtration System is also inoperable. This is also a loss of safety function subject to an 8 hour report for the same criterion. "The Senior Resident has been notified." * * * RETRACTION AT 0942 EST ON 02/14/2018 FROM DAVID VAN DERKAMP TO JEFF HERRERA * * * "CNS is retracting the 8-hour non-emergency notification made on December 19, 2017 at 1340 CST (EN# 53128). Subsequent evaluation concluded a postulated lamp short circuit failure in any of the affected circuits would not impact the ability of the Diesel Generators to perform their safety function and therefore, were operable. With DG operability not affected, the Control Room Emergency Filtration System also remained operable. "The NRC Resident Inspector has been notified." Notified the R4DO (Werner).<br><br> Original EN Text: DIESEL GENERATORS (DGs) DECLARED INOPERABLE DUE TO A COMMON ISSUE "During regular power operations at 100% power, DG#1 and DG#2 were declared inoperable due to a common issue associated with indicating lights and the associated sockets installed in various control and auxiliary circuits for both DG's. "The indicating lights in question are incandescent 120V AC style 120MB bulbs in a socket with a 550 ohm resistor. Style 120MB light bulbs have a failure mechanism where the bulb can cause a short circuit rather than the more common open circuit that is expected when an incandescent bulb filament fails. Cooper originally believed that the socket's integral resistor was sufficient to protect the circuit. In testing performed by an outside laboratory and confirmed on-site using warehouse stock, it was determined that the integral resistor may not have the power dissipation capability to protect the circuit ln which the light and socket are installed if a bulb fails in short circuit. "This condition resulted in both DG's being declared inoperable at 1340 [CST] due to a loss of reasonable expectation that they would meet their safety function required action to start, load and run to support loads required to mitigate the consequences of an accident. This is a loss of safety function under 10CFR 50.72(b)(3)(v)(D) subject to an 8 hour report. "As a result of both DG's being inoperable, the Control Room Emergency Filtration System is also inoperable. This is also a loss of safety function subject to an 8 hour report for the same criterion. "The Senior Resident has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-12-19
53127 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-12-15 | 2017-12-19 17:05 | 2017-12-19 | AGREEMENT STATE REPORT - UNDERDOSE The following information was received from the State of Illinois: "The University of Chicago Medical Center reported an underdose of Y90 Theraspheres today [12/19/17] to a patient. 53.4 % of dose was delivered with 46.6% stuck in catheter. 21 mCi was ordered and 11.21 was delivered. CT scan verified dose administered in correct location. On 12/18/17, it was still undetermined why remaining dose hung up in catheter. Additional dose [is] being ordered to complete the therapy as a fractionated dose. The licensee is investigating why the catheter became blocked. A 15 day written report will follow." Illinois Incident: IL177059 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-12-27
53126 | 0 | CRANE NUCLEAR INC. |  |  |  |  | 2017-11-17 20:17 | 2017-12-19 12:46 | 2017-12-19 | PART 21 - CHAPMAN GATE VALVE WEAK LINK ANALYSIS DEFECT The following information was excerpted from a facsimile received from Crane Nuclear: "This letter provides notification of a defect in a Weak Link Analysis provided to the Tennessee Valley Authority (TVA) by Crane-Aloyco, Inc. (CAI), a Crane Nuclear, Inc. (CNI) predecessor business unit, for a Chapman Gate Valve, Figure L900, Item # 18, Drawing CC05307, Revision B for the Browns Ferry Nuclear (BFN) plant. "The subject valve was originally procured from Crane Chapman in 1968. In 1988, TVA requested Crane to supply a Weak Leak Analysis for the original valve. A Weak Link Analysis (OTC-258 Rev.0) was developed by CAI, which identified a maximum thrust capacity of approximately 112,000 lbf. "In November 2017, Crane Nuclear, Inc. developed a new Weak Link Analysis for the valve. Crane Nuclear, Inc. provided the new Weak Link Analysis (WL-103 Rev. 0) to TVA on November 17th, 2017. Crane Nuclear. Inc. identified in the new Weak Link Analysis a maximum thrust capacity of approximately 96,000 lbf. "CNI is reviewing our records to determine if the maximum thrust rating in any other Weak Link Analyses provided by CNI for gate valve designs with an SMB-4T or SMB-5T actuator exceeds the rating for the thrust bearings. "Should you have any questions regarding this matter, please contact me, Joyce Hamman, Director, Safety & Quality at (678) 451-2280, Burt Anderson, Site Leader, at (630) 226-4990, or Samson Kay, Engineering Manager at (630) 226-4983." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-12-19
53125 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2017-12-18 07:10 | 2017-12-18 10:44 | 2017-12-18 | INADVERTENT EMERGENCY SIREN ACTIVATION DURING TESTING On December 18, 2017 at 0710 CST, five (5) sirens in the Ft. Calhoun Station Emergency Planning Zone for Pottawattamie County, Iowa, were inadvertently activated for less than one (1) minute. There was no emergency. The plant is permanently offline and undergoing decommissioning. This siren actuation was a result of a Pottawattamie County testing error and was cancelled. The licensee notified the State of Iowa, Pottawattamie County, the National Weather Service, local radio station and informed NRC Region 4 (Browder). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-12-18
53124 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2017-12-17 07:55 | 2017-12-17 11:56 | 2017-12-17 | OFFSITE NOTIFICATION FOLLOWING SULFRIC ACID SPILL "Ginna notified New York State Department of Environmental Conservation of a sulfuric acid spill of approximately 270 gallons in the AVT, All Volatile Treatment, building. Ginna is currently contacting offsite support for hazardous chemical cleanup. The spilled sulfuric acid is currently contained within the secondary containment structure associated with the sulfuric acid tank. There is no release to the environment. There is no impact to habitability in the AVT building at this time." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-12-17
53123 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-12-17 03:16 | 2017-12-17 05:48 | 2018-01-29 |  | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-12-17
53122 | 0 | EXELON NUCLEAR CORPORATE |  |  |  |  | 2017-12-15 14:30 | 2017-12-16 08:10 | 2018-04-10 | CORPORATE INDIVIDUALS REMOVED FROM THE FITNESS FOR DUTY RANDOM POOL "On 12/15/17 at 1430 [CST], it was discovered by corporate Fitness for Duty (FFD) personnel that two individuals in the Corporate Emergency Response Organization (ERO) and one Corporate FFD Authorization (FFDA) individual were removed from the random FFD testing pool by the security database, Illuminate. It was identified that a database coding error removed the FFD random pool flag when an additional clearance was requested for these individuals. The individuals involved did not have Unescorted Access (UA) or Unescorted Access Authorized (UAA). "Review by corporate FFD personnel and the security database vendor (Endevor) found this coding error affected only those individuals not holding UA/UAA but who require additional clearances which require being in the FFD random pool (e.g., ERO, FFDA). Corporate security personnel found no other individuals to be affected by this issue. No individuals with UA/UAA are affected by this issue. "Affected individuals have been added to the FFD random pool and pre-access testing will be performed for the three identified individuals prior to resuming duties requiring inclusion in the FFD random pool. A code modification for the security database has been created to prevent error recurrence, testing has begun with implementation targeted for Monday 12/18/17. Quarterly reviews will continue to take place for verification purposes. "The issue does not affect any Exelon Sites or the process for granting UA/UAA. "No other utilities are known to use the Illuminate security database." * * * UPDATE ON 04/10/18 AT 1919 EDT FROM MARK HAWES TO ANDREW WAUGH * * * "On 7/25/17, it was determined that on 4/1/17, when James A. FitzPatrick Nuclear Power Plant (JAF) changed ownership and transferred individuals into the Exelon Fitness for Duty (FFD) security program Illuminate, one individual was inadvertently excluded from the Follow-up portion of the program. This individual's record in the industry Personnel Access Data System (PADS) remained accurate and Illuminate was updated on 7/12/17; however, this individual did not receive four months of Follow-up FFD testing as required by 10 CFR 26.69(b)(4)(iii). No additional FFD program violations occurred by this individual and no other individuals involved in the transfer were affected by this error. A computer code modification by the Illuminate database vendor (Endevor) was created to prevent error recurrence. "The failure to transfer an individual into the FFD Follow-up Program on 4/1/17, is a significant FFD programmatic failure which is reportable per 10 CFR 26.719(b)(4)." The individual was a non-licensed JAF employee who had Unescorted Access. The licensee notified the NRC Resident Inspector. Notified R1DO (Jackson), R3DO (Stone), and FFD Group (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 3 | IL | OTH | GEN | 26.719 |  |  |  | 0 | 2017-12-16
53121 | 0 | SOR MEASUREMENT AND CONTROL |  |  |  |  | 2017-10-18 | 2017-12-15 18:02 | 2018-02-05 | <br><br>EN Revision Imported Date : 02/06/18<br><br>EN Revision Text: PART 21 - DEVIATION IN ORIGINAL QUALIFICATION TESTING OF SOR SAFETY RELATED SWITCHES The following is a excerpt from a report received via email: "On October 18, 2017 a deviation in the original qualification testing of SOR safety-related switches was discovered by a NRC vendor inspection conducted from October 16-20, 2017. SOR continues to evaluate those items cited by NON 99900824/2017-201-01 Items 1 through 3 and other effects on safety related components identified by SOR. "The qualification test report was written in 1992. Due to the age of the report, SOR continues to retrieve records and consult contracted sources. The evaluation is expected to be completed as soon as possible or by February 27, 2018. "If you have any questions regarding this matter, please contact: Mike Bequette, Vice President of Engineering Email: mbequette@sorinc.com Tel 913-956-3040" * * * UPDATE ON 2/5/2018 AT 1719 EST FROM MELANIE DIRKS TO DAVID AIRD * * * The following is an excerpt from a report received via email: "SOR has identified the following reportable deviations: "The Test Report did not account for all [Measuring and Test Equipment] uncertainties. The following are affected: -Qualified Life -LOCA [Loss of Coolant Accident] profile -HELB1 [High Energy Line Break] profile -HELB2 profile "During qualification testing, observed repeatability in excess of 1 percent of span was not adequately addressed for some models. The following will be affected: -Vacuum switches (post LOCA only) -Temperature switches "The Test Report presents data that is intended to provide a means to calculate reductions in qualified life depending on the conditions of the end use. However, there is a risk that this information could be overlooked by the end user. Following are the potential contributing factors to qualified life: -Temperature rise due to electrical load on switch element -Temperature rise on direct mount temperature switches due to elevated process temperature "SOR has conducted or is conducting the following corrective actions: -Provided details in this report regarding the NQ models strings and non-standard models potentially affected -Identified the contact list of customers potentially affected by this deviation within this notification -Notifying the utilities as indicated with a copy of this notification attached targeting completion by February 8, 2018 -Revise and update test report 9058-102 to revision 3 targeting completion and availability by February 28, 2018" Notified R1DO (Powell), R2DO (Heisserer), R3DO (Duncan), R4DO (Deese), and Part 21 Group (via email).<br><br> Original EN Text: PART 21 - DEVIATION IN ORIGINAL QUALIFICATION TESTING OF SOR SAFETY RELATED SWITCHES The following is a excerpt from a report received via email: "On October 18, 2017 a deviation in the original qualification testing of SOR safety-related switches was discovered by a NRC vendor inspection conducted from October 16-20, 2017. SOR continues to evaluate those items cited by NON 99900824/2017-201-01 Items 1 through 3 and other effects on safety related components identified by SOR. "The qualification test report was written in 1992. Due to the age of the report, SOR continues to retrieve records and consult contracted sources. The evaluation is expected to be completed as soon as possible or by February 27, 2018. "If you have any questions regarding this matter, please contact: Mike Bequette, Vice President of Engineering Email: mbequette@sorinc.com Tel 913-956-3040" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 4 | KS | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2017-12-15
53120 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2017-12-14 14:00 | 2017-12-15 15:40 | 2017-12-15 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following report was received from the Arizona Radiation Regulatory Agency via email: "On December 13, 2017, at approximately [1345 CST], the Agency [Arizona Radiation Regulatory Agency] received notification from the licensee of a possible medical event involving Yttrium-90. The patient received approximately 60 percent of the prescribed dose. The Agency has requested additional information and continues to investigate the event." Arizona First Notice: 17-017 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2017-12-25
53119 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2017-12-13 13:28 | 2017-12-14 11:29 | 2017-12-14 | FITNESS FOR DUTY REPORT "On December 13, 2017, Callaway determined that a violation of one provision of the site's Fitness For Duty (FFD) policy had occurred. FFD testing confirmed the use of a controlled substance. The violation was committed by a non-licensed, supervisory employee. The individual's unescorted access to the plant has been removed. "The NRC Resident Inspector has been notified by the licensee. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MO | POW |  | 26.719 |  |  |  | 0 | 2017-12-14
53118 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-12-12 17:57 | 2017-12-12 23:04 | 2017-12-12 | UNPLANNED LOSS OF EMERGENCY RESPONSE EQUIPMENT "At 1757 CST on December 12, 2017, South Texas Project Electric Generating Station (STPEGS) Unit 1 and Unit 2 experienced an unplanned partial loss of the Integrated Computer System (ICS). The partial loss of Unit 1 and Unit 2 ICS resulted in a major loss of emergency assessment capability to STPEGS Unit 1 and Unit 2 Technical Support Center (TSC) for greater than 75 minutes. Assessment capability has been verified to be available in the Emergency Operations Facility (EOF). "This report is being made pursuant to 10 CFR 50.72(b)(3)(xiii), any event that results in a major loss of emergency assessment capability, off site response capability, or off site communications ability. "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-12-12
53117 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-12-12 | 2017-12-12 | 2017-12-27 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "At approximately 1330 CST on Tuesday, December 12, 2017, Grand Gulf Nuclear Station declared Division 3 'C' Battery inoperable due to questions concerning battery terminal connection continuity. Technical Specification 3.8.4, DC Sources - Operating, Condition E, Required Action E.1, requires the station to declare the High Pressure Core Spray System inoperable immediately. The Division 3 'C' Battery and High Pressure Core Spray System was declared operable and the LCOs [Limiting condition of operation] were declared met at 1731CST on Tuesday, December 12, 2017. Based on field measurements of terminal torque and resistance, the as-found and as-left terminal resistance micro-ohm readings indicated satisfactorily all times. Formal evaluation of the as-found condition of the battery is in progress. "This report is to notify the NRC of a loss of safety function on the High Pressure Core Spray System." The NRC Resident Inspector was notified. * * * UPDATE AT 1612 EST ON 12/27/17 FROM GERRY ELLIS TO S. SANDIN * * * The report is retracted based on the following: "This was initially reported under 50.72(b)(3)(v)(D). However, after subsequent investigation of the identified condition, a degraded condition was confirmed to not exist. The 1C3 battery bank connections were torque checked, inspected, and resistance values were checked. All torque, resistance values and seismic condition were confirmed to be satisfactory. The operability evaluation confirmed that the battery was and remained operable, and therefore the initial determination of operability and reportability was incorrect. "Division 3 Battery 1C3 was at the time of discovery OPERABLE and therefore this is not a reportable condition." The licensee informed the NRC Resident Inspector. Notified the R4DO (Haire). | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-12-12
53116 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-12-12 15:19 | 2017-12-12 17:52 | 2017-12-12 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTUATION OF EMERGENCY NOTIFICATION SIREN "A South Texas Project [STP] Offsite Emergency Notification Siren (#7) was inadvertently going off. A resident who lived near the siren notified the Matagorda County Sheriff's Office at 0905 CST of the event and subsequently left a message with the STP Emergency Response staff. The Emergency Response staff dispatched maintenance to repair the siren and then later notified the Control Room at 1519 CST that the Sheriff's department was notified. The siren was inspected and reset. No issues were found with the siren. "The Matagorda County Sheriff's Office was the only offsite agency that has been notified. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-12-12
53115 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-12-12 09:18 | 2017-12-12 17:40 | 2017-12-12 | AUTOMATIC START OF EDG DUE TO LOSS OF ESF TRANSFORMER "At approximately 0918 CST on Tuesday, December 12, 2017, the Grand Gulf Nuclear Station experienced a loss of the Engineered Safety Features (ESF) Transformer 11 which was powering the Division 1 ESF bus. Subsequently, the station experienced an automatic start of the Division 1 Emergency Diesel Generator [EDG], partial isolation of the primary and secondary containment buildings and the isolation of the Reactor Core Isolation Cooling System [RCIC]. "It is not currently understood why the RCIC system isolated during this event. A team is investigating this issue separately from the loss of the ESF 11 transformer. "The cause of the event is under investigation at this time. "No other issues or unexpected events occurred. "The NRC Resident Inspector has been notified of the event." | 16 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-12-12
53114 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-12-09 03:28 | 2017-12-11 16:29 | 2017-12-11 | AGREEMENT STATE REPORT - IRRADIATOR DISABLED SOURCE RACK The following information was received from the State of South Carolina by email: "On Monday, December 11, 2017 at [1100 CST], the Department [South Carolina Department of Health and Environmental Control] was notified by [the] Corporate RSO [Radiation Safety Officer] of STERIS Isomedix Services that one of the source racks had been stuck in the 'up' position. The incident happened at [0328 CST] on Saturday, December 8, 2017. The worker saw that there was an unload fault on the system indicating that the rack was stuck so he called maintenance to try to correct the problem. At [0340 CST] the Radiation Safety Officer [and then the corporate RSO were notified] about the event. [The RSO] called and left a message on an employee voicemail rather than calling the 24 hour emergency phone number. "The workers were able to go into the penthouse to correct the problem and lower the source rack back into the pool. The workers found that a carrier had a cracked hinge. They checked all of their other carriers and replaced a total of two carrier doors. The RSO informed the CRSO [Corporate Radiation Safety Officer] that the situation was resolved at [0724 CST]. The licensee stated that a written report will be sent within 30 days of the event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-12-19
53113 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-12-06 | 2017-12-11 14:43 | 2017-12-11 | AGREEMENT STATE REPORT - EQUIPMENT MALFUNCTION - STUCK SHUTTER The following was received via fax: "On Wednesday, December 6, 2017, a contract technician from BBP Sales conducted Georgia-Pacific semiannual shutter checks. It was found that a handle would not turn to close a shutter for a level gauge. The gauge was a Ronan holder model SAI-F37 manufactured in 1987. The sealed source serial number is MI104. This is a 150 mCi Cesium-137 source. "Louisiana Department of Environmental Quality (LDEQ) was notified on December 11, 2017. "The source holder will have to be replaced as there is no way to remove the shutter for repair." LA Report ID: LA20170018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-12-19
53112 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-12-11 08:57 | 2017-12-11 11:06 | 2017-12-11 | MANUAL REACTOR TRIP IN RESPONSE TO INDICATION OF MULTIPLE DROPPED CONTROL RODS "While operating at 97% power, the Watts Bar Unit 2 reactor was manually tripped at 0857 EST on December 11, 2017 due to multiple dropped control rods. All control and shutdown bank rods inserted properly in response to the manual reactor trip. All safety systems including Auxiliary Feedwater actuated as designed. The plant is stable with decay heat removal through Auxiliary Feedwater and the Steam Dump System. "The cause of the dropped rods is being investigated. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv)(B). The actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv)(A). "The NRC Senior Resident Inspector has been notified for this event." No safety or relief valves lifted during this event. | 0 | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-12-11
53111 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2017-12-10 23:50 | 2017-12-11 00:35 | 2017-12-11 | UNUSUAL EVENT DUE TO A SMOKE DETECTOR ALARM RECEIVED INSIDE CONTAINMENT "St. Lucie Unit 1 declared an Unusual Event due to a smoke detector alarm received in the Unit 1 Containment Building that was unable to be confirmed within 15 minutes. A Containment entry was completed and no evidence of fire was found. The Unusual Event was terminated at 00:26 on 12/11/17. "State and local officials have been notified by the licensee. "The NRC Resident Inspector has been notified of this by licensee." Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), and DHS Nuclear SSA (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-12-11
53110 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-12-09 13:48 | 2017-12-09 18:42 | 2017-12-11 | MANUAL REACTOR SCRAM DUE TO LOSS OF DIVISION 1 AC POWER TO NUMEROUS COMPONENTS "At approximately 1347 [CST] on 12/09/17, the Main Control Room received annunciators that indicated a trip of the 4160 V 1A1 breaker 1AP07EJ, 480V XFMR 1A and A1 breaker. Numerous Division 1 components lost power (powered from unit subs 1A and A1). The Division 1 containment Instrument Air isolation valves had failed closed by design due to the loss of power. Due to the loss of containment instrument air, several control rods began to drift into the core as expected and, by procedure, the reactor mode switch was placed in the shutdown position at 1353 [CST]. All control rods fully inserted. "Also due to the loss of power, the Fuel Building ventilation dampers failed closed by design. With the normal ventilation system secured, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge at 1348 [CST]. The Control Room entered EOP-8, Secondary Containment Control. Secondary Containment differential pressure was restored within Technical Specification requirements at 1351 [CST] by starting the Division 2 Standby Gas Treatment system. "This event is being reported as a manual actuation of the Reactor Protection System (RPS) and as a Condition that Could Have Prevented Fulfillment of a Safety Function. "The cause is currently under investigation. The NRC Resident has been notified." The licensee informed the NRC Resident Inspector. * * * UPDATE FROM DALE SHELTON TO VINCE KLCO AT 1658 EST ON 12/10/2017 * * * "During a review of plant logs it was identified that the primary to secondary containment differential pressure was identified to be outside of Technical Specification 3.6.1.4 limits of 0 plus or minus 0.25 psid at 2009 on 12/9/17 due to the primary containment ventilation system dampers closing as a result of the loss of power. This parameter is an initial safety analysis assumption to ensure that primary containment pressures remain within the design values during a Loss of Coolant Accident (LOCA). As a result, this condition is reportable as an unanalyzed condition that significantly degrades plant safety. "The NRC Senior Resident Inspector has been notified." Notified the R3DO (Stone). * * * UPDATE FROM MICHAEL ANTONELLI TO VINCE KLCO ON 12/11/17 AT 1805 EST * * * "During the post transient review of the trip of the 4160 V 1A1 breaker 1AP07EJ, 480V XFMR 1A and A1, it was identified that the unplanned INOPERABILITY of the Low Pressure Core Spray (LPCS) system due to the loss of power to the injection valve constitutes an event or condition that could have prevented fulfillment of a safety function and is reportable under 10CFR50.72(b)(3)(v)(D) for Accident Mitigation. The High Pressure Core Spray (HPCS) remained available to perform the core spray function, if necessary, during a design basis Loss of Coolant Accident (LOCA), however HPCS and LPCS are each considered single train safety systems. "The NRC Senior Resident Inspector has been notified." Notified the R3DO (Stone). | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | POT UNCNTRL RAD REL | UNANALYZED CONDITION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) | 0 | 2017-12-09
53109 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2017-12-08 15:20 | 2017-12-08 17:26 | 2017-12-08 | AGREEMENT STATE REPORT - LOST POLONIUM SOURCE The following information was excerpted from an email received from the State of Kansas: The licensee is reporting that an ionizer containing a radioactive source (Model Number P-2063-1000) was lost. The licensee currently has 3 other ionizers of the same model. The device radioactive source was Polonium-210 (SN: A2KT674) with an activity of 31.5 mCi and was last leak tested on 9/20/2016. The device was checked out by the licensee and placed within the secure test floor while testing electrical devices at the Integra Technologies facility. The missing device use was last logged on 8/25/2017. The licensee believes that their maintenance department mistakenly threw the device away. Upon discovering that the device was missing, the licensee searched their facility several times over without finding the device. The prevention for further loss is that the remaining 3 units will be mounted in permanent locations using security screws so they cannot be removed by unauthorized personnel. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2017-12-18
53108 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-12-08 13:10 | 2017-12-08 17:25 | 2017-12-08 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO A LEAKING CHECK VALVE "U/2 HPCI [Unit 2/High Pressure Coolant Injection] was declared inoperable due to leak by of the pump discharge check valve after pump shutdown from flow testing. This resulted in cycling of the minimum flow valve. The discharge valve was closed to prevent the continued cycling of the minimum flow valve. This condition was identified during normal surveillance testing." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-12-08
53107 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2017-12-07 13:01 | 2017-12-07 15:03 | 2017-12-07 | OFFSITE NOTIFICATION OF GROUNDWATER RESULTS TO STATE AND LOCAL AGENCIES "This non-emergency notification is being made in accordance with 10 CFR 50.72(b)(2)(xi), any event or situation related to the protection of the environment for which notification to other government agencies has been made. Dominion Energy is in the process of informing the Virginia Department of Health, Department of Environmental Quality, Department of Emergency Management, and the Surry County Administrator of recent groundwater monitoring results at Surry Power Station in accordance with NEI 07-07, Industry Groundwater Protection Initiative (GPI). "On December 6, 2017 at 1138 EST, Surry Power Station received analysis results of recent samples from the on-site groundwater monitoring program. As part of the program, 10 new groundwater monitoring wells were recently placed in service within the Protected Area to provide early detection, to better define the site's hydrology, and if necessary, to mitigate any potential leaks. The analysis results from one of the new wells indicated tritium activity level above the GPI communication threshold. Samples were re-analyzed, resulting in different values, with the highest result of 59,300 picoCuries per liter. Since each result was above the voluntary reporting threshold, Surry stakeholder communication was implemented in accordance with the NEI GPI Voluntary Communication Protocol, Criterion 2.2. "There are no known active leaks at this location; however, Dominion Energy is continuing to investigate the source of the tritium and the reason for the variability in the sample results. "Tritium was not detected in the on-site monitoring locations outside of the Protected Area. No tritium has been detected in the on-site and off-site drinking water wells. Since the activity is contained within the site restricted area, the health and safety of on-site personnel and members of the public are not affected. "A 30-day report will be submitted to the NRC in accordance with NEI 07-07. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-12-07
53106 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2017-12-06 09:58 | 2017-12-06 12:42 | 2017-12-06 | DIESEL FUEL OIL TANK SUPPLY NON-CONFORMING WITH LICENSING BASIS FOR TORNADO GENERATED MISSILES "On December 6, 2017, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornado generated missiles, Three Mile Island Nuclear Station identified a non-conforming condition in the plant design such that specific TS equipment is considered to not be adequately protected from tornado generated missiles. A tornado could generate a missile that could strike the emergency diesel generator (EDG) fuel oil supply tank (DFT) vent stack. This could result in crimping of the stack, which could affect the ability of the DFT to perform its design function if such a tornado would occur. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v)(D) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "This condition is being addressed in accordance with NRC enforcement guidance provided in EGM 15-002 and DSS-ISG-2016-01. Compensatory measures have been implemented in accordance with these documents. "The NRC Resident Inspector has been informed of this notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-12-06
53105 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-12-05 20:00 | 2017-12-06 01:55 | 2017-12-06 | UNPLANNED LOSS OF MULTIPLE RADIATION MONITORS DURING MAINTENANCE "At 2000 (CST), Comanche Peak experienced a failure of SCADA B of the PC11 Radiation Monitor System. This failure caused a loss of Unit 1 Main Steam Line 1-01 and 1-03 Radiation Monitors (1-RE-2325 and 1-RE-2327) and Train A and Train B Station Service Water Radiation Monitors (1-RE-4269 and 1-RE-4270). With the Main Steam Line Radiation Monitors nonfunctional, all of the emergency action levels for a steam generator tube rupture in steam generators 1-01 and 1-03 could neither be evaluated nor monitored. With the Station Service Water Radiation Monitors non-functional, all of the emergency action levels for a radioactive release through station service water could neither be evaluated nor monitored. This unplanned condition is reportable as a loss of assessment capability per 10 CFR 50.72(b)(3)(xiii). "Comanche Peak Nuclear Power Plant (CPNPP) has assurance of steam generator integrity, reactor coolant system integrity, and fuel cladding integrity and there is a negligible safety significance to condition from a public health and safety perspective. Additionally, compensatory measures are in place to assure adequate monitoring capability is available to implement the CPNPP emergency plan in the unlikely event of challenges to the steam generator, reactor coolant system, or the fuel cladding. Until these radiation monitors were restored, Operations implemented compensatory measures to monitor the Condenser Off Gas Radiation Monitor for early signs of a steam generator tube leak/rupture and Radiation Technicians were briefed on taking local readings with a Geiger-Mueller tube on the Main Steam Lines. Chemistry Technicians were performing hourly samples of Station Service Water and reporting results to the Control Room. "Corrective actions were pursued to restore the non-functional radiation monitors back to service. Those actions are complete and all radiation monitors have been restored to service. "The NRC Resident Inspector has been notified." PC11 is a computer common to both Units. The failure happened during radiation monitor maintenance to a single monitor, which unexpectedly affected multiple monitors. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-12-06
53104 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2017-12-04 | 2017-12-05 17:22 | 2017-12-06 | MATERIAL CONTROL AND ACCOUNTING PROCESS MONITORING ALARM RESOLUTION In accordance with 10 CFR 74.57(f)(2), a report to NRC is required for the following event. On December 4, 2017, the alarm threshold limit was exceeded for the abrupt loss exceeding five formula kilograms of SSNM (strategic special nuclear material). The potential alarm situation was initially reported to Measurement Control personnel and all processing was secured. Per E41-116 and the Fundamental Nuclear Material Control Plan (FNMCP), an Alarm Investigation Team was established since a process monitoring test exceeded its alarm threshold limit. The licensee secured the input process and continued the output process while investigating the alarm condition. The licensee is expected to conclude processing the output later in the evening and will have final calculations in the morning. The licensee will notify the NRC Resident Inspector and the NRC Project Manager. * * * UPDATE FROM CHRIS TERRY TO DONALD NORWOOD AT 0826 EST ON 12/6/2017 * * * "In accordance with 10 CFR 74.57(f)(2), a report to NRC is required for the following event. On December 4, 2017, the Alarm Threshold Limit was exceeded for PU-3 Main Extraction (Column Based) system. NMC Measurement Control received the PU-3 Process Monitoring Test for December 5, 2017 at approximately 1000 EST, at which time it was discovered by the NMC Process Monitoring Lead that the alarm threshold limit was exceeded. This was reported to the Measurement Control Unit Manager on December 5, 2017 at approximately 1150 EST. The re-analysis that was done cleared the alarm at approximately 1930 EST on December 5, 2017. The initial test difference exceeded the Alarm Threshold Limit. The final difference after re-analysis was below the Alarm Threshold Limit. "Per E41-116 and the FNMCP, an Alarm Investigation Team was established since a process monitoring test exceeded its alarm threshold limit. NRC Ops was contacted at 1722 EST on December 5, 2017." Notified R2DO (Walker), NMSS (Erlanger), IRD (Pham), ILTAB (YIP), NMSS Events Notifications, and Fuels Group (OUO). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALARM RESOLUTION | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 74.57 |  |  |  | 1 | 2017-12-13
53103 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-12-04 | 2017-12-04 | 2017-12-19 | AGREEMENT STATE REPORT - PATIENT RECEIVED LESS THAN PRESCRIBED Y-90 DOSE The following was received from the State of Wisconsin via email: "On December 4, 2017, the department [State of Wisconsin Department of Health Services] received a telephone call and email from the licensee's lead nuclear medicine technologist about a Y-90 TheraSphere dose that was not delivered as prescribed to the patient. The procedure occurred at 11:00 AM on December 4, 2017. The written directive stated that the dose delivered should be 120 Gy. The estimated dose delivered to the liver was 17.7 Gy. The nuclear medicine technologist discovered contamination in the operating room where the procedure took place, which implied that some of the dose did not get into the patient during the treatment. The licensee is suspecting that there was an issue with the administration kit. The licensee has contacted the manufacturer and the manufacturer is planning a site visit. The licensee has removed the contaminated administration kit and placed it in a waste bag for decay in storage. The room where the administration occurred has also been cleaned. The department [State of Wisconsin Department of Health Services] will follow up with a site visit to investigate the incident. "Event Report ID No.: WI170019" A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM DAVID REINDL TO VINCE KLCO ON 12/19/17 AT 1217 EST * * * The following information was excerpted from an email received from the State of Wisconsin: ". . . After performing a site visit on December 14, 2017 it was determined that there was actually no contamination resulting from this event. The licensee requested that we amend the notice to reflect this change . . . . In the publicly available text there are two statements that should be changed. The text 'The nuclear medicine technologist discovered contamination in the operating room where the procedure took place, which implied that some of the dose did not get into the patient during the treatment' should be changed to 'The nuclear medicine technologist discovered no contamination in the operating room where the procedure took place'. Additionally the following text should be deleted, 'The room where the administration occurred has also been cleaned'." Notified the R3DO (Dickson) and NMSS Events Notification Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-12-12
53102 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2016-12-01 | 2017-12-04 16:07 | 2017-12-04 | AGREEMENT STATE REPORT - FAILURE OF SOURCE CONNECTION The following report was received from the Illinois Emergency Management Agency via email: "Illinois Emergency Management Agency discovered a radiography incident involving McNDT Leasing, which had not been properly reported. The incident involved an exposure device (QSA Global model 880 Delta, serial #D13616) and a 3.7 TBq (100 Ci) Ir-192 source. A radiography team arrived at a job site on 12/1/2016 and, during equipment set up, noticed the drive cable connector was bent. Upon obtaining a new crank assembly, the team could not successfully crank out the source. The reel of the crank assembly did not move. After another failed attempt, they detached the crank assembly from the exposure device and noticed that place where the connector attaches to the source pigtail was worn and bent. The team returned to their facility and exchanged exposure devices. Preliminary investigation indicated that either the exposure device was damaged in previous work and had not been reported, or daily inspection and maintenance checks were inadequate or not performed prior to 10/11/2017. Corrective actions included obtaining new equipment. "No exposures occurred since the source was not able to be cranked out of the device." "Device/Equipment: Camera/ Radiography Manufacture: QSA Global, Inc. Model Number: 880 Delta Equipment Serial Number: D13616 "Radionuclide: Ir-192 Activity: 100 Ci" Illinois Item Number: 170517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-12-12
53101 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2017-11-30 16:57 | 2017-11-30 17:17 | 2017-12-01 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE An Unusual Event was declared at 1657 EST due to an earthquake detected onsite. The Unusual Event was declared under EAL HU1.1. There is no release in progress due to this event. There are no protective actions recommended at this time. The Licensee will notify the NRC Resident Inspector. Note: See also EN #53099 for Salem Unusual Event. * * * UPDATE FROM JOSHUA MYERS TO DONALD NORWOOD AT 1742 EST ON 11/30/2017 * * * "An earthquake was felt onsite at time 1645 EST. Multiple phone calls were made to the Control Room confirming the earthquake. It was verified there was an earthquake felt in Delaware with a magnitude of 4.4. Neither seismic monitor at Salem Unit 1, Salem Unit 2, and Hope Creek actuated. There is no indication of any damage to any systems or plant structures. Plant walk-downs have been initiated in accordance with plant operating procedures for a seismic event. No injuries have been reported to the Control Room." The licensee will notify the NRC Resident Inspector and State and local government agencies. Notified R1DO (Gray), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), and DHS Nuclear SSA (email). * * * UPDATE FROM THOMAS CLARK TO DAVID AIRD AT 2137 EST ON 11/30/2017 * * * The licensee terminated the Unusual Event at 2125 EST on 11/30/2017 following plant walkdowns that revealed no damage to plant structures, systems, or components. The NRC Resident Inspector has been notified. Notified R1DO (Gray), IRD (Grant), and NRR EO (Miller), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), and DHS Nuclear SSA (email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-12-01
53100 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-11-28 | 2017-11-30 | 2017-12-01 | AGREEMENT STATE REPORT - TWO NUCLEAR GAUGES INVOLVED IN FIRE The following report was received via E-mail: "On November 30, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's consultant that two nuclear gauges were involved in a fire on November 28, 2017. The consultant stated they could not gain access to the gauges until this date. The gauges are Thermo Fisher model 5203 gauges containing a two (2) curie (original activity) cesium-137 source. The consultant stated the dose rate on one of the gauges was reading 180 millirem an hour on a preliminary radiation survey. This dose rate appears to be higher than normal. A contamination survey was performed in the area of the gauges, but the results were not available at the time of the report. The gauges are located 20 - 30 feet above the ground and do not create an exposure risk to any individuals. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9524 * * * UPDATE AT 0740 EST ON 12/1/2017 FROM ART TUCKER TO MARK ABRAMOVITZ * * * The following information was received via E-mail: "The licensee has provided the following additional information: "The source holders are visibly intact, however they are black with soot. Both of the gauges were surveyed. For B-1228 the readings are normal but B-1227 has a localized spot on the lower left-hand location of the shield where the readings are 180 mR/hr at contact and 14 mR/hr at 1 ft. Additional shielding has been attached to the lower left hand location of the shield to reduce the dose rate to 3 mR/hr at 1 ft. Sealed Source leak tests have been performed and the results will be communicated as soon as they are assayed. No personnel (member of the general public or radiation workers) have been within 5 feet of either source due to the unsafe structural conditions due to the fire. Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (O'Keefe) and NMSS Events Notification (via e-mail). * * * UPDATE FROM ART TUCKER TO DONALD NORWOOD AT 1511 EST ON 12/1/2017 * * * The following information was received via E-mail: "The licensee reported that the results of the leak test performed on the two gauges indicated the sources were not leaking (less than 0.0001 microCi). Additional information will be provided as it is received in accordance with SA-300." Notified the R4DO (O'Keefe) and NMSS Events Notification (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-12-08
53099 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-11-30 16:57 | 2017-11-30 17:17 | 2017-11-30 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE An Unusual Event was declared at 1657 EST due to an earthquake detected onsite. The Unusual Event was declared under EAL HU1.1. There is no release in progress due to this event. There are no protective actions recommended at this time. The Licensee will notify the NRC Resident Inspector. Note: See also EN #53101 for Hope Creek Unusual Event. * * * UPDATE FROM JOSHUA MYERS TO DONALD NORWOOD AT 1742 EST ON 11/30/2017 * * * "An earthquake was felt onsite at time 1645 EST. Multiple phone calls were made to the Control Room confirming the earthquake. It was verified there was an earthquake felt in Delaware with a magnitude of 4.4. Neither seismic monitor at Salem Unit 1, Salem Unit 2, and Hope Creek actuated. There is no indication of any damage to any systems or plant structures. Plant walk-downs have been initiated in accordance with plant operating procedures for a seismic event. No injuries have been reported to the Control Room." The licensee will notify the NRC Resident Inspector and State and local government agencies. Notified R1DO (Gray), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), and DHS Nuclear SSA (email). * * * UPDATE FROM THOMAS CLARK TO DAVID AIRD AT 2137 EST ON 11/30/2017 * * * The licensee terminated the Unusual Event at 2125 EST on 11/30/2017 following plant walkdowns that revealed no damage to plant structures, systems, or components. The NRC Resident Inspector has been notified. Notified R1DO (Gray), IRD (Grant), and NRR EO (Miller), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), and DHS Nuclear SSA (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-11-30
53098 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-11-30 10:26 | 2017-11-30 16:02 | 2017-11-30 | SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE BRIEFLY INDICATED OUTSIDE OF TECH SPEC LIMIT "On November 30, 2017 at 1026 EST, the Susquehanna Control Room received indication that a loss of Secondary Containment Zone 2 differential pressure had occurred. Control Room operators noted a differential pressure of 0.0 inch WC [water column] for several seconds, followed by a high DP of 0.5 inch WC. System DP was restored to normal in 3 minutes. The cause of the pressure swings is under investigation. "Zone 2 differential pressures being less than 0.25 inch WC constitutes a loss of Secondary Containment based on not meeting requirements of SR 3.6.4.1.1. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev. 3, Section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-11-30
53097 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-11-28 | 2017-11-30 | 2017-12-19 | AGREEMENT STATE REPORT - RADIOGRAPHY TRAINEE OVEREXPOSURE The following report was received via e-mail: "On November 28, 2017, the Agency [Texas Department of State Health Services] was contacted by the licensee's Radiation Safety Officer (RSO) who reported that on November 28, 2017, they were notified by their dosimetry processor that one of their radiographer trainee's exposure badges was reported to read 62 Rem. The RSO stated the trainee was returning to the Longview office from West Texas to be interviewed. The badge reading was for the month of October 2017. The RSO stated the trainee had operated the radiography camera crank out device, but had not changed out any film. It is believed the dose is to the badge only. The RSO stated they had not observed any adverse health effects in the trainee. On November 29, 2017, the Agency contacted the RSO and requested additional information. The RSO stated the trainee stated that they had not dropped their dosimeter and accidently exposed it. The trainee had stated that they had been wearing an alarming rate meter and it had never alarmed. The trainee's daily exposure record did not indicate any abnormal exposures. The radiographer supervising the trainee did not recall any abnormal operations while supervising the trainee. The RSO stated the trainee had not received any type of medical treatments during the exposure period. The RSO stated they were considering sending blood samples to REAC/TS for analysis. The RSO stated the dosimetry processor reported the exposure to the badge was angular. The RSO stated the trainee has been assigned duties that would not give them any additional exposure. "The licensee will provide the Agency [Texas Department of State Health Services] any information gathered in the interview with the trainee. The RSO cannot state with certainty that the exposure is not real, therefore the Agency is providing this report to the Nuclear Regulatory Commission. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9523 * * * UPDATE ON 12/12/2017 AT 0955 EST FROM ART TUCKER TO STEVEN VITTO * * * The following report was received via e-mail: "On November 28, 2017, the Agency was contacted by the licensee's RSO who reported that the OSL [Optically stimulated luminescence] badge reading for one of their radiographer trainees was reported to read 62 rem. On December 8, 2017, the Agency interviewed the individual with the high badge reading and the licensee's radiation safety officer (RSO). The interviews did not provide any additional information that would explain the high badge reading. The RSO stated a blood sample from the individual was submitted to Radiation Emergency Assistance Center/Training Site (REAC/TS) on December 5, 2017. Additional information will be provided as it is received in accordance with SA-300." R4DO (Deese), INES Officer (Milligan), and NMSS Events Group have been notified. * * * UPDATE ON 12/19/2017 AT 0828 EST FROM ART TUCKER TO ANDREW WAUGH * * * The following report was received via e-mail: "On December 18, 2017, the licensee [Interteck Asset Integrity Management Inc.] reported 'I have received the test report and the result is negative. No dicentric chromosome was observed in a total of 500 metaphase cells analyzed.' indicating the exposure was to the badge only. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Pick), INES Officer (Milligan), and NMSS Events Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-12-08
53096 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-11-29 11:25 | 2017-11-29 18:09 | 2017-11-29 | FITNESS-FOR-DUTY REPORT INVOLVING DISCOVERY OF KOMBUCHA TEA INSIDE THE PROTECTED AREA "On 11/29/2017, at approximately 1125 (Pacific Time), an employee reported finding a container of herbal tea (Kombucha) in a refrigerator in a warehouse building break room, which is located inside the Protected Area. Kombucha tea is a fermented tea containing trace amounts of alcohol. Based on the product labeling, which indicates the beverage may contain more than 0.5 percent alcohol by volume, and which also includes a government alcoholic beverage health warning label, this is being considered an alcoholic beverage, and is being reported under the requirements of 10 CFR Part 26.719. "An investigation is under way to identify who may have brought the kombucha tea on-site. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 26.719 |  |  |  | 0 | 2017-11-29
53095 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2017-11-27 | 2017-11-28 | 2017-12-06 | FITNESS FOR DUTY REPORT - FALSE POSITIVE ON BLIND SAMPLES "[On] Monday, 11/20/17, [the licensee] received a call from the MRO [Medical Review Officer] staff that the Opiate blind submitted on 11/14/17 did not test as expected. The confirmatory test was positive for codeine and morphine but negative for 6-acetylmorphine. [The licensee] requested a retest by the MRO to the laboratory. The MRO staff contacted the provider of the blind specimens for documentation of the blind analysis. The lab was requested on 11/21/17 to perform the retest by the MRO. [On] 11/27/17, the results from the lab on the retest were virtually the same as the original test result. The lab's Certifying Scientist provided a letter documenting their findings. The MRO staff informed us [Wolf Creek] and we requested copies of all documentation from the provider of the blinds, the lab and any notes from the MRO staff. Informed Superintendent Access Screening of the test results. [The licensee] contacted two plants to verify reportability under 10 CFR 26.719. [The licensee] initiated CR 00117707 to document the occurrence. Superintendent contacted licensing and management." The licensee will inform the NRC Resident Inspector and R4 NRC Security Inspector. * * * RETRACTION ON 12/6/17 AT 1559 EST FROM LARRY HAUTH TO DONG PARK * * * "This event was reported under 10 CFR 26.719(c)(3). Further review shows that this event should have been reported under 10 CFR 26.719(c)(1), which only required a Licensee Event Report, not an Event Notification. This notification is retracted." The licensee will notify the NRC Resident Inspector. Notified R4DO (Hipschman) and FFD Group via email. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 26.719 |  |  |  | 0 | 2017-11-28
53094 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-11-24 | 2017-11-27 15:26 | 2017-11-29 | AGREEMENT STATE EVENT REPORT - STOLEN PORTABLE GAUGE The following was received from the State of Ohio via email: "The licensee's technician performed work using the gauge at a job site in Blue Ash, Ohio on 11/24/17. After leaving the job site, the technician stopped at several locations [before] arriving home. The gauge was discovered missing on 11/27/17 when the technician arrived at the licensee's facility. The storage container for the gauge was not broken into indicating that it had not been locked. A report was filed with the Cincinnati Police Department. "Device Name: PORTABLE GAUGE Manufacturer: CAMPBELL PACIFIC NUC Model Number: MC-1 Serial Number: 70603768 Activity: Cs-137:10mCi and Am-Be: 50mCi" Ohio Reference Number: OH 2017-070 * * * UPDATE AT 0919 EST ON 11/29/2017 FROM STEPHEN JAMES TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "On 11/28/17 ODH [Ohio Department of Health] inspectors visited each of the locations the technician visited after leaving the job site on 11/24/17. The inspectors searched in dumpsters, other containers, and around the buildings to try to locate the device. They also took radiation surveys in each of the areas. The surveys indicated no increased radiation levels and the gauge was not found by the ODH inspectors. This incident remains open." Ohio Report: OH170010 Notified the R3DO (Duncan) and NMSS Events Resource (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-12-05
53093 | 0 | GEORGE WASHINGTON UNIVERSITY |  |  |  |  | 2017-11-07 | 2017-11-27 12:06 | 2017-11-27 | LOST IODINE-125 IMPLANT SEED The following is an excerpt from the 30 day report submitted from George Washington University Hospital: "On Tuesday, 11/7/2017, one of the pathologists' assistants completed the first seed case of the new week. After placing the seed in the vial which included the prior week's seeds, she counted only 10 seeds. However, there should have been 11; e.g. 10 from the previous week plus the new one from the current week. "Radiation safety confirmed that there were 10 seeds in the vial. Since only 10 lot numbers were written on the vial, this suggests that only 10 seeds were ever placed in the vial (as opposed to 11 being put in the vial, and one of them falling out at some point.) "Radiation safety confirmed that there were 11 flow sheets. Each flow sheet was initialized by a pathologists' assistant that the seed had been recovered and stored in the cabinet. This suggests that one of the pathologists' assistants was distracted and signed the sheet without placing the seed in the vial as per procedure. "The pathology laboratory was surveyed by two individuals from the Radiation Safety Office. The surveys covered all areas of the lab including the work stations, sinks, floors, waste specimens, desks, and storage cabinets. The seed was not located. "The licensed material that has been lost is a single I-125 seed, made by IsoAid for the localization of nonpalpable breast lesions. The seed is a sealed source approximately 5 mm in length. It had a nominal activity of 200 microCi on October 24, 2017." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2017-12-05
53092 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-11-26 12:25 | 2017-11-26 16:16 | 2017-11-26 | UNPLANNED EMERGENCY CORE COOLING SYSTEM (ECCS) INJECTION DURING A PLANNED SAFETY INJECTION TEST "On November 26, 2017, at 1225 Eastern Standard Time (EST), the Watts Bar Nuclear Plant (WBN) Unit 2 experienced an unplanned ECCS discharge to the Unit 2 Reactor Coolant System (RCS) while de-pressurized, in Mode 5, with the Pressurizer vented to the Pressurizer Relief Tank. ECCS injection via the Boron Injection flow path occurred during planned Safety Injection system Engineered Safety Features Actuation System (ESFAS) testing. The Boron Injection flow path should have been isolated and should not have resulted in any injection flow to the Unit 2 RCS. Since the injection was not a part of the pre-planned test this is reportable under 10 CFR 50.72(b)(2)(iv), System Actuation. "All other systems responded as expected in accordance with the ESFAS testing procedure. The unintended ECCS injection flow was isolated and flow through the Boron Injection path was verified to be stopped at 1232 EST. The Unit 2 Pressurizer level and pressure remained below any limits and no safety limits were challenged. "NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(A) |  |  |  | 0 | 2017-11-26
53091 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-11-25 20:25 | 2017-11-26 00:36 | 2017-11-26 | MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEED WATER "At time 2025 [CST] on 11/25/17, Unit 2 reactor was manually tripped due to a loss of all Main Feedwater. Operators observed both Main Feed Pumps tripped and SG [Steam Generator] levels decreasing, resulting in the direction for a manual reactor trip. The reactor trip actuated a turbine trip, both Motor Driven Auxiliary Feedwater Pumps started on the loss of both Main Feed Pumps, and Steam Generator Lo Lo levels started the Turbine Driven Auxiliary Feedwater Pump. All systems responded as expected. There was no work in progress at the time of the incident. "Currently Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IP0-0078 and the Emergency Response Guideline Procedure Network has been exited. Decay Heat is being rejected to the Main Condenser via Steam Dump Valves." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-11-26
53090 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-11-25 02:38 | 2017-11-25 06:02 | 2018-01-16 | <br><br>EN Revision Imported Date : 01/17/18<br><br>EN Revision Text: MANUAL REACTOR SCRAM DURING STARTUP "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, IRM [Intermediate Range Monitor] channels A, C, and D received a spurious upscale trip signal which immediately cleared. Upon investigation, operability of RPS [Reactor Protection System] scram function for Intermediate Range Detectors was placed in question. This event is being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical." The licensee notified the NRC Resident Inspector. * * * UPDATE ON NOVEMBER 26, 2017, AT 1850 FROM GRAND GULF TO MICHAEL BLOODGOOD * * * "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, Intermediate Range Monitor neutron flux detector (IRM) channels A, C, and D received a spurious Upscale Trip signal which immediately cleared. Upon investigation, IRM channels A, C, and D were declared Inoperable. IRM G was already Inoperable for another reason. RPS scram function from IRM channels B, E, F, and H was always Operable and available. That event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "This Revised Statement to Event Notification # 53090 is being made to make it clear that only four IRM channels (A, C, D, G) were Inoperable and that the IRM RPS SCRAM function was still available from the four remaining Operable IRM channels (B, E, F, and H)." The licensee notified the NRC Resident Inspector. Notified R4DO (O'Keefe) * * * RETRACTION ON 01/16/2018 AT 1629 EST FROM JASON COMFORT TO DAVID AIRD * * * "On 11/25/17, at 0149 [CST], with reactor power just above the point of adding heat, Intermediate Range Monitor neutron flux detector (IRM) channels A, C, and D received a spurious Upscale Trip signal which immediately cleared. Upon investigation, IRM channels A, C, and D were declared Inoperable. IRM G was already Inoperable for another reason. At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. RPS scram function from IRM channels B, E, F, and H was always Operable and available. That event was initially being reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "After the trip alarms were received, the Operators spent approximately twenty minutes investigating possible causes and implications, and consulted with Reactor Engineering and the Shift Technical Advisor. The investigation showed that the plant was stable and the upscale IRM alarms were spurious. A review of plant technical specifications by the operators determined that a plant shutdown was not required. After further discussions, Operations concluded that a shutdown to allow further investigation of the issue was the prudent course of action. Prior to shutting down, Operations spent approximately twenty minutes reviewing procedures, notifying personnel to exit containment, and conducting a brief. The shutdown was then conducted by inserting a manual reactor scram by placing the reactor mode switch in SHUTDOWN. "This was initially reported under 10 CFR 50.72(b)(2)(iv)(B) as an actuation of the RPS. Based on the sequence of events, and Operator actions in conducting the shutdown, the event is considered 'part of a pre-planned sequence during testing or reactor operation' as specified in 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A). In accordance with NUREG-1022, Section 3.2.6, the event is not reportable as an actuation of RPS." The licensee notified the NRC Resident Inspector. Notified R4DO (Taylor).<br><br> Original EN Text: MANUAL REACTOR SCRAM DURING STARTUP "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, IRM [Intermediate Range Monitor] channels A, C, and D received a spurious upscale trip signal which immediately cleared. Upon investigation, operability of RPS [Reactor Protection System] scram function for Intermediate Range Detectors was placed in question. This event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical." The licensee notified the NRC Resident Inspector. * * * UPDATE ON NOVEMBER 26, 2017, AT 1850 FROM GRAND GULF TO MICHAEL BLOODGOOD * * * "At 0238 [CST] a manual reactor scram was inserted by placing the Reactor Mode Switch in Shutdown. At 0149 [CST], with reactor power just above the point of adding heat, Intermediate Range Monitor neutron flux detector (IRM) channels A, C, and D received a spurious Upscale Trip signal which immediately cleared. Upon investigation, IRM channels A, C, and D were declared Inoperable. IRM G was already Inoperable for another reason. RPS scram function from IRM channels B, E, F, and H was always Operable and available. That event is being reported under 10CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS), when the reactor is critical. "This Revised Statement to Event Notification # 53090 is being made to make it clear that only four IRM channels (A, C, D, G) were Inoperable and that the IRM RPS SCRAM function was still available from the four remaining Operable IRM channels (B, E, F, and H)." The licensee notified the NRC Resident Inspector. Notified R4DO (O'Keefe) | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-11-25
53089 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2017-11-22 20:43 | 2017-11-23 02:54 | 2018-01-11 | <br><br>LPCI INOPERABILITY DUE TO OVERVOLTAGE RELAY ACTUATION "On November 22, 2017, at 2043 [CST], Unit I MCC [Motor Control Center] 18/19-5 overvoltage relay target was found actuated and would not reset. MCC 18/19-5 was powered from the normal feed, Bus 19. Bus 19 voltages were verified to be normal. The overvoltage relay actuation would result in MCC 18/19-5 being de-energized in the event of a DBA LOCA [Design Basis Accident Loss of Coolant Accident] in which the 1/2 Emergency Diesel Generator fails to energize Bus 18, therefore rendering both divisions of the Low Pressure Cooling Injection (LPCI) mode of Residual Heat Removal (RHR) system inoperable. Technical Specification 3.5.1 Condition E was entered, requiring restoration of LPCI in 72 hours. "The overvoltage target was subsequently able to be reset at 2114 [CST], restoring the LPCI function of RHR. Technical Specification 3.5.1 Condition E was exited at that time. "This event is reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function." The licensee notified the NRC Resident Inspector.<br><br>EN Revision Imported Date : 01/16/18<br><br>EN Revision Text: LPCI INOPERABILITY DUE TO OVERVOLTAGE RELAY ACTUATION "On November 22, 2017, at 2043 [CST], Unit I MCC [Motor Control Center] 18/19-5 overvoltage relay target was found actuated and would not reset. MCC 18/19-5 was powered from the normal feed, Bus 19. Bus 19 voltages were verified to be normal. The overvoltage relay actuation would result in MCC 18/19-5 being de-energized in the event of a DBA LOCA [Design Basis Accident Loss of Coolant Accident] in which the 1/2 Emergency Diesel Generator fails to energize Bus 18, therefore rendering both divisions of the Low Pressure Cooling Injection (LPCI) mode of Residual Heat Removal (RHR) system inoperable. Technical Specification 3.5.1 Condition E was entered, requiring restoration of LPCI in 72 hours. "The overvoltage target was subsequently able to be reset at 2114 [CST], restoring the LPCI function of RHR. Technical Specification 3.5.1 Condition E was exited at that time. "This event is reportable under 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM RONALD SNOOK TO STEVEN VITTO ON 01/11/18 AT 1913 EST * * * "The purpose of this notification today (01/11/18) is to retract the ENS Report made on November 23, 2017 at 0248 hours EST (ENS Report #53089). "Upon further review, it was determined that the Unit 1 MCC 18/19-5 overvoltage relay target that was found actuated and would initially not reset was caused only by intermittent degraded DC control power. During this event, MCC 18/19-5 remained powered from the normal feed Bus 19, and Bus 19 voltages were verified to be normal. "It was further determined from plant drawings that under this condition the degraded DC control power to the Unit 1 MCC 18/19-5 overvoltage relay has no impact to the Technical Specification 3.5.1 required capability to auto transfer power from the normal Bus 19 to the alternate Bus 18 should Bus 19 lose power such as during a DBA LOCA. This overvoltage relay was installed in the early 1990's only to support enhanced reliability of the power supply to the LPCI injection valves, and its actuation due to degraded DC control power would not impact the ability to auto transfer to alternate Bus 18. Therefore, both divisions of the Low Pressure Cooling Injection (LPCI) mode of Residual Heat Removal (RHR) system would have remained fully operable under the as-found relay condition, and Technical Specification 3.5.1 Condition E was not required to be entered. "On December 6, 2017, it was determined that a loose fuse clip terminal had caused the DC control power to the overvoltage relay to become degraded which in turn caused the relay target and its reset to become erratic. This fuse clip terminal was repaired on December 6, 2017. Based on the subsequent reviews of this event, the LPCI system was not required to be declared inoperable in accordance with Technical Specifications 3.5.1 during the period of the MCC 18/19-5 overvoltage relay actuation (i.e., 31 minutes on 11/22/17), and hence was not required to be reported under 10CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. "Therefore, based on this information, ENS Report #53089 is being retracted. "The NRC Resident Inspector has been notified." R3DO(Jeffers) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-11-23
53088 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2017-11-17 | 2017-11-22 15:22 | 2017-11-22 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE Eye plaque brachytherapy was being performed using I-125 seeds with a prescribed dose of 85 Gray. After the dose, the Iso-dose curve was noted to be different from the brachytherapy plan i.e. the dose was deeper than expected. Investigation revealed that a new model plaque was used which differed from the previous model. This resulted in an underdose with 65 Gray actually administered. Oregon Report: 17-0073 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2017-11-30
53087 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-11-22 | 2017-11-22 14:37 | 2017-11-22 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA MALFUNCTION The following report was received via e-mail: "A crew with [Shawcor] experienced a malfunction on the evening of November 21, 2017, with the INC IR-100 exposure device they were using when performing radiographic operations at Ward Petroleum (10404 E. 146th, Thornton, CO). "Exposure Device: INC IR-100 (s/n 6839) "Source: INC (s/n T0799) 65 curies "After completing a radiographic exposure, the crew attempted to crank the source back into the exposure device; however, they were still able to crank the source out even after the button on the exposure device popped up to indicate the source was fully retracted and locked in place. After an attempt to crank the source out and back into the exposure device, the button was still popping up prematurely. Realizing there was a problem with the locking mechanism, the crew ensured their 2 mR/hr boundary was properly established and immediately contacted the Site RSO/Branch Manager. The crew maintained visual surveillance of the area until [the RSO], along with [the Assistant Site RSO], arrived at the jobsite. "When [the RSO and Assistant Site RSO] arrived at the jobsite, they also ensured the 2 mR/hr boundary was properly established and began to assess the situation. There was no visible damage to any associated equipment (guide tube, crank assembly, etc.). They attempted several times to crank the source out and back into the fully shielded position; each time the button popped up prematurely even though the source was not locked into the exposure device. While holding down the button on the exposure device, [the RSO] was able to crank the source back in and upon releasing the button, the source locked in place. Surveys were completed to ensure the source was fully shielded. "At no time during the incident did any crew member's dosimeter go off-scale and there was no threat of overexposure at any time to our company's employees, nor un-monitored workers. All personnel involved were wearing and utilizing proper radiation detection equipment, including OSL [Optically Stimulated Luminescent] badges, pocket dosimeters, alarming rate meters, and they were properly utilizing survey meters. "The INC exposure device will be sent back to the manufacturer for maintenance and repair, if necessary." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-11-30
53086 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-11-20 | 2017-11-22 13:40 | 2017-11-22 | AGREEMENT STATE REPORT - POTENTIAL MEDICAL UNDERDOSE The following information was received via e-mail: "ODH [Ohio Department of Health] was notified of a potential medical event by Fairview Hospital. The licensee performed a permanent prostate seed implant using I-125 according to the treatment plan. When the post implant dosimetry was performed, the D90 coverage was calculated to be 73% of the prescribed dose. After an initial investigation by the licensee, it was determined the under dose was caused by an 18% increase in prostate size compared to the pre-plan, which was prescribed 6 weeks prior to treatment. "At the time of reporting, the licensee had informed the referring physician but they did not inform the patient. The licensee believes that once the inflammation subsides the D90 coverage will be within the prescribe treatment plan. "NMED will be updated once ODH receives additional information from the licensee and conducts an investigation of the event." Ohio Event: OH170009 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-11-30
53085 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2017-11-22 09:37 | 2017-11-22 10:28 | 2017-11-22 | ST. LUCIE UNIT 2 UNUSUAL EVENT DUE TO A SMOKE DETECTOR ALARM RECEIVED INSIDE CONTAINMENT "St. Lucie Unit 2 declared an Unusual Event due to a smoke detector alarm received in the Unit 2 Containment Building that was unable to be confirmed within 15 minutes. A Containment entry is currently being planned to determine the validity of the alarm. "State and local officials have been notified by the licensee." The NRC Resident Inspector has been notified. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 11/22/17 AT 1143 EST FROM JULIUS FLETCHER TO JEFF HERRERA * * * "Personnel entered Containment to determine conditions and found no evidence of smoke, fire or damage to equipment. Event terminated at 1127 EST 11/22/17." The NRC Resident Inspector has been notified. Notified R2DO (Suggs), R2 DRA (Dudes), NRR (Brock), IRD (Gott), and NRR EO (Miller), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-11-22
53084 | 0 | ENGINE SYSTEMS, INC. |  |  |  |  | 2017-11-20 | 2017-11-21 17:07 | 2017-11-21 | PART-21 - AUXILIARY FEEDWATER PUMP POWER SUPPLY FAILURE The following report is an excerpt from a fax from Engine Systems, Inc.: "Engine Systems Inc. (ESI) began a 10CFR21 evaluation on October 17, 2017 upon notification of a potential issue with power supply P/N 2938604 supplied to Vogtle Nuclear Plant. The power supply is installed in a safety-related control panel for the Terry Turbine driven auxiliary feedwater pump. Analysis determined the power supply failure was due to an internal rectifier diode failure which resulted in a short circuit on the power supply output. "The evaluation was concluded on November 20, 2017 and it was determined that this issue is a reportable defect as defined by 10CFR Part 21. The power supply failure will adversely affect speed control of the turbine driven auxiliary feedwater pump and therefore may prevent safe shutdown of the nuclear reactor. "This issue applies to all customers that have power supply P/N 2938604 within the date code range 0648 through 0723. ESI has supplied power supplies within the suspect date code range to [Vogtle and Farley]." Point of Contact: Tom Horner, Quality Manager, 252-977-2720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-11-21
53083 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2017-10-06 09:10 | 2017-11-21 14:22 | 2017-11-21 | INVALID SPECIFIED SYSTEM ACTUATION "On October 6, 2017 at 0910 CDT hours, with Unit 1 in Mode 1 (Power Operation), the 1A Diesel Generator Cooling Water Pump (DGCWP) automatically started. The cause was the misoperation of the 1B/C RHR [Residual Heat Removal] Room Cooler Fan (1VY03C) control switch, which was placed in the start position instead of the intended pull-to-lock position. The start of the 1VY03C fan resulted in the automatic actuation of the 1A DGCWP. This system actuation is reportable in accordance with 10CFR50.73(a)(2)(iv)(A). The invalid actuation was not part of a pre-planned sequence during testing or reactor operation. "The 1A DGCWP, an emergency service water system that does not normally run and that serves as an ultimate heat sink, responded satisfactorily. "This call is being made in accordance with 10CFR50.73(a)(1), which states that in the case of an invalid actuation reported under 10CFR50.73(a)(2)(iv), other than an actuation of the reactor protection system when the reactor is critical, the licensee may provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written Licensee Event Report." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-11-21
53082 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2017-11-20 | 2017-11-21 11:57 | 2017-11-27 | AGREEMENT STATE REPORT - FIXED GAUGE DAMAGED HOUSING The following information was received via e-mail: "The RSO [Radiation Safety Officer] for Goodyear contacted us [Oklahoma Department of Environmental Quality] yesterday afternoon. [The RSO] stated that a roller had broken loose from their line, and it damaged the housing for a registered generally licensed device (fixed gauge) they have on the property. The gauge is a Honeywell Measurex. 50 mCi Sr-90. "There was no loss of control, but there was damage. They [Goodyear] took immediate action. The source is secure and shielded at this time." * * * UPDATE AT 1049 EST ON 11/27/17 FROM JENNIFER McALLISTER TO S. SANDIN VIA EMAIL * * * "Generally Licensed Device Site Registration Number: GLD0013 "Source Serial No.: 0953BG" Notified R4DO (O'Keefe) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2017-11-29
53081 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2017-11-20 15:48 | 2017-11-21 11:26 | 2017-11-21 | FITNESS-FOR-DUTY REPORT A non-licensed contract employee had a confirmed positive for illegal drugs during a random fitness-for-duty test. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.719 |  |  |  | 0 | 2017-11-21
53080 | 0 | WALSH & KELLY, INC. |  |  |  |  | 2017-11-20 | 2017-11-20 11:35 | 2017-11-20 | GENERAL LICENSE TRITIUM EXIT SIGNS MISSING On 9/28/17, a contractor hired by Walsh & Kelly, Inc. contacted the NRC RIII Office to request instructions for disposal of four (4) Tritium Exit signs which he had removed. He was instructed to return the signs to Walsh & Kelly, Inc. The signs were returned which Walsh & Kelly acknowledged. An onsite inspection by RIII staff on 11/20/17, was unable to locate or determine the disposition of the four (4) Tritium Exit signs; Manufacturer: Isolite Activity: 10 Ci/each Quantity: 4 Model: SLX-60 S/Ns: 11-36128, 11-36129, 11-36130 and 11-36131 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-11-28
53079 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-11-19 | 2017-11-20 10:31 | 2017-11-20 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of Illinois via email: "The Agency [Illinois Emergency Management Agency] was notified on 11/19/17 by the licensee's RSO [Radiation Safety Officer] that a grey Dodge Caravan containing a Troxler Model 3430 gauge [serial number 33605] containing 9 mCi Cs-137 and 44 mCi Am241/Be had been stolen from a technician's residence sometime during the night/early morning. The licensee believes it is a random theft of the vehicle and the equipment inside. A police report has been filed and the investigation is ongoing. "Item Number: IL170001" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-11-28
53078 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-11-17 | 2017-11-18 01:06 | 2017-11-18 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from the State of California via email: "On 11/17/17, the RSO [Radiation Safety Officer] contacted RHB [CA Radiologic Health Branch] to report a stolen moisture density gauge. The stolen gauge is a CPN Model MC-1DR, S/N MD90209216, containing 10 mCi of Cs-137 and 50 mCi of Am-241. The user had taken the gauge home and left it secured in the back of his truck. The truck was parked at his residence . . .. According to the user, most likely between midnight and 5 AM of 11/17/17, the chain locking the gauge to the truck bed was removed and the case was dragged behind a building where the locks on the box were broken and the gauge was removed. The box was recovered without the gauge. [The] RSO had notified San Jose Police Department of this incident (Event # P173210429). RHB will be following up on this investigation. "5010 NUMBER (Date Notified): 111717" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-12-11
53077 | 0 | FISHER CONTROLS INTERNATIONAL |  |  |  |  | 2017-09-28 | 2017-11-17 15:17 | 2017-11-17 | PART 21 REPORT - CORRECTIVE ACTION FOR FISHER INFORMATION NOTICE 2015-01 INSUFFICIENT The following is a synopsis of information received via E-mail: Fisher Information Notice (FIN) 2015-01 was published 3/18/2015 regarding Fisher Type 461 valve plug machining. FIN 2015-01 details an issue in which a valve plug was returned to Fisher after the customer discovered a machining error was present in the plug. This Type 461 valve plug is intended to have a groove machined across the seating surface to provide a controlled leak rate through the valve when the plug is on the seat. It has been determined that the corrective action implemented in association with FIN 2015-01 was insufficient to ensure accurate machining and to prevent reoccurrence of this issue. This Part 21 Notification (issued as FIN 2017-05) applies to Type 461 Plugs sold or reworked since the publication date of FIN 2015-01. Specifically this notification applies to assembly item number 25A0413X162 that Fisher Controls International LLC (Fisher) supplied to Florida Power and Light (FPL) St. Lucie per FPL Order 2363439 (Fisher Order Number 025-X204270) and to item number 29A7841X052 that Fisher supplied to Entergy Waterford 3 per Entergy Order 10297987 (Fisher Order Number 026N-187174). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-11-17
53076 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2017-05-01 | 2017-11-16 15:42 | 2017-11-16 | AGREEMENT STATE REPORT - MISSING POLONIUM-210 SEALED SOURCE The following information was received via E-mail: "On November 16, 2017, the Massachusetts Radiation Control Program determined that one NRD, LLC, Model P-2021-8201, S/N A2KQ898, static control device, containing a 10 milliCurie, polonium-210 sealed source, could not be located by the licensee (Current decayed activity is approximately 600 microCurie with an original assay date of 5/5/2016). "When questioned by the Program, the licensee stated that it noticed that the device has been missing since sometime in May of 2017. The licensee believes that they transferred the device from their Lenox, MA facility to their Pittsfield, MA facility and it is somewhere within their Pittsfield facility. However, the licensee stated that it's very unlikely they will find the device due to the facility size and complexity. "The Program notified the licensee of its responsibility for providing a written report within 30 days of their telephone report in accordance with the requirements of 105 CMR 120.281(B). "Root cause and corrective action are not known at this time and the Program intends to perform a special inspection. "This event remains open." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2017-11-24
53075 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2017-11-15 | 2017-11-16 15:43 | 2017-11-16 | AGREEMENT STATE REPORT - RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT The following information was received via E-mail: "Desert NDT, LLC dba Shawcor (Shawcor) reported that a 3.15 TBq (85 Ci) Ir-192 sealed source (SPEC model G-60, serial #YJ2608) had disconnected from a drive cable connected to a SPEC model SPEC-150 radiography exposure device (serial #786) at a temporary job site in Watford City, ND on 11/15/2017. "Upon completion of an exposure, the radiography crew performed a radiation survey while approaching the exposure device. At approximately 35 feet from the device, they noticed an elevated reading of approximately 20 mR/hr. At this point, the crew determined the source had not retracted into the safe, shielded position. The crew moved away from the device, secured the area, maintained a 2 mR/hr barrier and contacted the Branch Manager. The Branch Manager, who is trained in source retrieval, responded to the site. He successfully recovered the source following Shawcor established procedures. The Branch Manager inspected the exposure device and associated equipment. He determined no damage had occurred to the exposure device, guide tube, and/or crank assembly, rather the drive cable was not properly connected to the source pigtail. "At no time during the event did the radiography crew member's pocket dosimeters go off-scale. In response to the initial notification, the North Dakota Department of Health requested the licensee send the exposure device and associated equipment involved in the event to the manufacturer for further evaluation." North Dakota Item Number: ND170001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-11-24
53074 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-11-15 20:07 | 2017-11-16 08:17 | 2017-11-16 | LOSS OF PUBLIC PROMPT NOTIFICATION SYSTEM CAPABILITY "At 0008 CST on 11/16/2017, Cooper Nuclear Station [CNS] was notified by Omaha Weather that the NOAA broadcast and the Shubert radio tower for this area is off. This affects the tone alert radios used to notify the public in event of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10CFR50.72(b)(3)(xiii). "The transmission outage actually began at 2007 [CST], 11/15/2017, but CNS was not notified until 0008 [CST], 11/16/2017. Backup notification methods remained available throughout the period. "At time 0447 CST on 11/16/2017, Cooper Nuclear Station was notified that the NOAA broadcast and Shubert radio transmission tower was returned to service. "Nemaha County, NE, Richardson County, NE, and Atchison County, MO authorities within the 10 mile EPZ were notified by Cooper Nuclear Station of the condition and the effect on the tone alert radios at 0642 [CST], 11/16/2017. This is reportable under 10CFR50.72(b)(2)(xi) as a 4 hour report. "The NRC Senior Resident has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2017-11-16
53073 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-11-15 | 2017-11-15 13:25 | 2017-11-15 | AGREEMENT STATE REPORT - INCORRECT WRITTEN DIRECTIVE FOR LIVER PATIENT The following report was received from the Pennsylvania Bureau of Radiation Protection via facsimile: "The event involved a patient who was scheduled to be treated with 16 mCi of Y-90 SirSpheres to the left lobe of the liver. The written directive (WD), however, was incorrectly written for the right lobe of the liver. The authorized user (AU) did in fact deliver the correct dose to the correct lobe and the discrepancy was only noticed after the procedure was complete. No harm is expected as the patient received the intended dose to the correct location. The cause of the event was noted as human error resulting from: (1) Failure of the AU to indicate the correct treatment site on the WD. (2) Failure of the AU to forward documentation of the pre-therapy information to the RSO (or designee) prior to the therapy. (3) Failure of clinical staff to identify the discrepancy on the WD during the patient time out just before implantation of the microspheres. "Corrective actions include: Before drawing up the dose/activity in Nuclear Medicine (and preferably before the dose/activity is ordered from the manufacturer), the AU must forward pre-therapy documentation (WD, pre-post therapy worksheet, etc.) to the RSO (or designee) to ensure documentation is correct/appropriate. "The Department [Pennsylvania Bureau of Radiation Protection] will perform a reactive inspection. The licensee will update their procedure to include additional checks for the written directive." Event Report ID No: PA 170016 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-11-23
53072 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2017-11-14 11:30 | 2017-11-14 17:35 | 2018-01-30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2017-11-22
53071 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-11-06 | 2017-11-14 16:17 | 2017-11-14 | AGREEMENT STATE REPORT - DOSE GREATER THAN 50 REM DELIVERED AT A SITE NOT INTENDED FOR TREATMENT The following report was received from the Ohio Department of Health via email: "On Friday, November 10, 2017, ODH [Ohio Department of Health] received notification that a cancer patient may have received a dose greater than 50 rem at a site not intended for treatment. A follow-up call was made on Monday November 13, 2017. The licensee stated they believe the Elekta Flexitron (model 136149A02) remote afterloader software package used an incorrect catheter model during the first treatment fraction. The error was discovered while preparing the second fraction. "ODH will be sending an inspector to investigate the event this week. "See licensee initial description below: "A patient was planned to be treated with HDR [High Dose Rate] brachytherapy for GYN [Gynocology] cancer with three fractions. The HDR treatment was planned with a single curved catheters through a Tandem and Cylinder. A dosimetrist preformed a CT based treatment plan for the first fraction. During planning, the dosimetrist did not digitize the catheter correctly. A physicist checked the HDR plan in a hurry and failed to detect the incorrect reconstructed catheter shape in the planning software. During the treatment delivery, the delivery system translated the incorrectly reconstructed catheter as a linear catheter, resulting in the treatment length from the intended 9.0 cm to 15.7 cm. On the second fraction, a new plan was created based on the CT of the day. The dosimetrist did the digitization correctly this time. During the planning check (a routine process), the physicist noticed the differences between the two plans and discovered the error on the first fraction treatment." Remote afterloader HDR Device: ELEKTA Model Number: 136149A02 Sealed Source Brachytherapy Source: IR-192 Model Number: 136147 Ohio Event Number: OH170008 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-11-22
53070 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-01-10 03:00 | 2017-11-14 15:13 | 2017-11-14 | INVALID ACTUATION OF A GENERAL CONTAINMENT ISOLATION SIGNAL AFFECTING MORE THAN ONE SYSTEM "This 60-day telephone notification is being made per the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting more than one system. "On September 15, 2017, during a TVA [Tennessee Valley Authority] review of Operations logs, it was determined that a reportable condition occurred in January 2017 but no NRC report had been made. On January 10, 2017, at 0300 Central Standard Time (CST), Browns Ferry Nuclear Plant, Unit 3, received Primary Containment Isolation System (PCIS) Groups 2, 3, 6, and 8 isolation signals. The Group 2, 3, 6, and 8 isolations caused the initiation of all three trains of the Standby Gas Treatment (SBGT) system and Control Room Emergency Ventilation (CREV) subsystem 'A.' At 0311 CST, Operations personnel discovered that the 3A1 RPS circuit protector had tripped on undervoltage. "Plant conditions which initiate PCIS Group 2 actuations are Reactor Vessel Low Water Level (Level 3) or High Drywell Pressure. The PCIS Group 3 actuations are initiated by Reactor Vessel Low Water Level (Level 3) or Reactor Water Cleanup Area High Temperature. The PCIS Group 6 actuations are initiated by Reactor Vessel Low Water Level (Level 3), High Drywall Pressure, or Reactor Building Ventilation Exhaust High Radiation (Reactor Zone or Refuel Zone). The PCIS Group 8 actuations are initiated by Low Reactor Vessel Water Level (Level 3) or High Drywall Pressure. At the time of the event, these conditions did not exist; therefore the actuation of the PCIS was invalid. "All affected equipment responded as designed. This condition was the result of an undervoltage condition on the 3A1 circuit protector. During trouble shooting, the undervoltage setpoints were found to be 116 VAC and 115 VAC, when the normal as left acceptance band is 109.7 VAC to 111.3 VAC. The 3A RPS protective relays had been previously replaced in September 2016. The most likely cause of the undervoltage condition in these relays is infant mortality. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-11-14
53069 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-11-14 11:18 | 2017-11-14 12:42 | 2017-11-14 | UNUSUAL EVENT DECLARED DUE TO HYDROGEN LINE LEAK At 1118 CST on 11/14/17, Cooper Nuclear Generating Station declared an Unusual Event due to a hydrogen leak on a main generator purge line. The leak was reported to be caused by Maintenance cutting into a one inch line. The total size of the leak is unknown, however, it is estimated to be depressurizing in the main generator at approximately 1lb per hour. The current pressure is 52 to 53 lbs. pressure and is stable. The operations staff have entered their abnormal procedure and are taking actions to isolate the leak. Operators have isolated the source of hydrogen and have opened the exterior roll up doors to increase the airflow and minimize the concentration of hydrogen in the area. The area has been evacuated and hot work has been stopped. The NRC Resident Inspector has been notified. Notified DHS, FEMA, NICC and NNSA (via email). * * * UPDATE AT 1433 EST ON 11/14/2017 FROM ROY GILES TO MARK ABRAMOVITZ * * * "On 11/14/2017, Nebraska Public Power District will issue a press release concerning the declaration of a Notification of Unusual Event (EN#53069) declared today at 1118 [CST] for a small hydrogen leak in the turbine building. "This is a four hour report per 10CFR50.72(b)(2)(xi) for any event or situation for which a news release is planned or notification to other government agencies has been or will be made which is related to heightened public or government concern." Notified the R4DO (Kozal). * * * UPDATE AT 1904 EST ON 11/14/17 FROM TRENT SYDOW TO JEFF HERRERA * * * At 1744 CST the licensee exited from the Unusual Event. The leak was patched under a temporary repair. The patch was tested to verify the leak has stopped. The NRC Resident Inspector was notified. Notified the R4DO (Kozal), IRDMOC (Gott), NRR EO (Miller), DHS, FEMA, NICC and NNSA (via email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2017-11-14
53068 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-11-13 08:02 | 2017-11-13 17:26 | 2017-11-13 | FITNESS FOR DUTY - POSITIVE RESULT FOR ALCOHOL "A licensed supervisor had a confirmed positive test for alcohol. The employee was escorted offsite and their plant access has been terminated and a five year denial placed in Personnel Access Data System (PADS). "This is being reported per 10 CFR 26.719(b)(2)(ii). "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 26.719 |  |  |  | 0 | 2017-11-13
53067 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-11-12 03:03 | 2017-11-13 03:57 | 2017-11-13 | CONTAINMENT SPRAY PUMP CONTROL SWITCHES OUT OF SERVICE "At 2119 [CST] on 11/12/2017 a Control Room board walk down discovered that both of the Unit 2 Containment Spray Pump control switches were in pull-out. With the control switches in pull-out, the pumps would not automatically start as required. Unplanned TS [Technical Specifications] 3.0.3 was entered at 2119 as a result of not complying with TS 3.6.5, Containment Spray and Cooling Systems, which requires both trains of Containment Spray to be Operable while in Mode 4. Unit 2 had entered Mode 4 at 0303 on 11/12/2017. TS 3.0.3 was exited at 2127 on 11/12/2017 when both Containment Spray Pump control switches were placed in Automatic restoring Operability. Preliminary investigation determined that while Unit 2 was in Mode 5, Surveillance SP 2099, Main Steam Isolation Valve Logic Test, had taken the Containment Spray Pump control switches to pull-out but did not re-align the control switches to automatic after the test was complete. This 8-hour Non-Emergency report is being made per 10 CFR 50.72(b)(3)(v)(D), Accident Mitigation. The NRC Senior Resident Inspector has been informed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-11-13
53066 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-11-10 | 2017-11-10 20:06 | 2017-11-10 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following report was received via e-mail: "On 11/10/19, California Office of Emergency Services (OES) contacted RHB [Radiologic Health Branch] to report a stolen moisture density gauge. This gauge is a CPN Model MC-3, S/N M311000525 containing 10 mCi of Cs-137 and 50 mCi of Am-241. The gauge was stolen while momentarily unattended in the licensee's facility parking lot. The lot has video surveillance and the footage is being reviewed by the RSO for information. Immediately after the incident, a report was filed with the Concord Police Department. RHB will be following up on this investigation." California report: 111017 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-11-20
53065 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-11-10 | 2017-11-10 16:24 | 2017-11-10 | AGREEMENT STATE REPORT - PROCESS GAUGE STUCK SHUTTER The following report was received via e-mail: "On November 10, 2017, the Agency was notified by the licensee's service provider that during routine test of an Ohmart Vega model SHD-45 nuclear gauge, the shutter failed to close. Open is the normal operation position. The gauge contains a 250 millicurie (original activity) cesium-137 source. The service provider stated the gauge is not an exposure risk to any individual. The service provider stated no corrective action has been determined." Texas Incident: I-9520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-11-20
53064 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-11-09 | 2017-11-09 17:52 | 2017-11-09 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following report was received via e-mail: "The Corporate Radiation Safety Officer [RSO] notified LDEQ [Louisiana Department of Environmental Quality] that a Troxler Moisture/Density gauge (TMDG) Model # 3411B was run over by a compactor/heavy equipment at one of their temporary job sites. The gauge was left unattended by the operator of the gauge on the construction site while discussing materials results with the jobsite foremen. FCI's [Fugro Consultants Inc.] investigation determined that the cause of the incident was human error and that TMDG sources were not damaged or leaking. The outer housing on the device was damaged. The TMDG was not in use at the time of the incident, the push rod was not extended, and the sources were in the shielded position. The incident happened November 8, 2017, at approximately 8:30 AM. The incident was reported to LDEQ at approximately 3:00 PM. "The TMDG Model # 3411B, S/N 14273 was loaded with a Cs-137 9 mCi source model # TA-102112, and an Am-241(AmBe) 40 mCi source model # TA-102451. "The incident happened at a temporary jobsite in West Baton Rouge Parish. The facility: Shintech Ethane Cracker Plant, 26270 Highway 405, Addis, LA. A site RSO is in charge of the investigation, radiation issues, and recommendations for corrective actions. Results are reported to and under the direction of the RSO. "The damaged gauge was a Troxler, Model 3411B, S/N 14273, loaded with 9 mCi of Cs-137 and 40 mCi of Am/Be. The gauge housing was damaged, but there was no indication the radioactive sources were compromised or leaking. The survey readings were minimal at the surface of the gauge and background in the area of use. The TMDG was loaded into the storage/shipping container and transported to Troxler Electronics Lab., Greenwell Springs Road, Baton Rouge, LA, where the gauge integrity is being evaluated and the sources leak tested. If there is a change in the testing results, the information will be updated. "LDEQ Radiation Staff Personnel visited the Troxler Electronics Lab facility on Greenwell Spring Road to assess the TMDG situation. The LDEQ Staff found the radiation survey reading were in the normal range for a gauge with the sources in the shielded position. "This event is being reported under 10 CFR 30.50(b)(2) and LAC 33:XV.341.B.2. "All equipment involved in this incident were isolated and were not a threat to the general public. There was no threat to FCI of Shintech personnel and it appears to be safe." LA Event Number: LA 170017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-11-17
53063 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2017-11-07 | 2017-11-08 19:10 | 2017-11-08 | AGREEMENT STATE REPORT - LOST URANIUM SOURCE "The RSO [Radiation Safety Officer] from the University of Nevada, Las Vegas, phoned to report a missing/lost source of 3 microcuries of U-235, 90% enriched, 1.4 grams, form metallic (non-dispersible). The source package was received and surveyed on 10/30/2017, surface 90microrad/hr and 11microrad/hr at 1 meter. The source was then delivered to the Office of the Professor who ordered the source where it sat to be taken to a research area. The package was placed under a desk next to a trash can and a recycle can in the Professor's office. The Professor forgot about the package and never delivered it to the research area, but saw the source on November 3rd under the desk, then failed to deliver the source once again and the source was left over the weekend. On Monday, November 6th, when the Professor remembered the source, the source was gone. On November 7th the Professor reported the lost/missing source to the RSO. The RSO immediately started an investigation. The garbage in the Professor's office was collected on Monday evening, November 6th. The dumpster the trash went to was emptied Tuesday morning, November 7th, into the normal waste stream. The RSO looked through all the dumpsters and was unable to find the package. Because of the low activity of the source it would probably not be detected at the landfill. The RSO is emailing a preliminary report, ASAP. This is an ongoing investigation." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2017-11-16
53062 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-09-02 | 2017-11-08 15:06 | 2017-11-29 | AGREEMENT STATE REPORT - MATERIAL STOLEN AND NOT RECOVERED The following information was received from the State of Ohio via email: "A local Health District employee had a Niton Xlp 300 XRF with a 50 mCi Cadmium-109 source stolen overnight on Saturday, September 2, 2017. It was in the car in their garage and someone came in and took it. The employee had worked late at a job site that day and brought the gauge home instead of returning to the office. Employee's garage door did not close for some reason that night and they were unaware that it was open when they went to bed. There were several other cars broken into that night in employee's neighborhood. A report was filed with local police department. Device has not yet been recovered." Source/Radioactive Material: Sealed Source; Radionuclide: Cd-109; Activity: 50mCi; Device Name: X-RAY Fluorescence (XRF); Model Number: Niton XLp 300; Manufacturer: Thermo Scientific Analytical; Serial Number: 98149. Ohio Item Number: OH170007 * * * UPDATE AT 0919 ON 11/29/17 FROM STEPHEN JAMES TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "Note: According to device owner, the manufacturer told them that this incident was NOT reportable to their regulatory agency. The owner reported the event on 11/6/17 as a result of more research on their part. "UPDATE: The gauge was found by a member of the public in their yard, where it had apparently been abandoned. The local health district was notified based on contact information on case. The case was still locked when found. The device is now back in the possession of the local health district as of 11/27/17." Notified the R3DO (Duncan), NMSS Events Resources and CNSC (via e-mail) . THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-11-16
53061 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-11-08 08:24 | 2017-11-08 11:52 | 2017-11-08 | SWITCHYARD AUTOTRANSFORMER FIRE DUE TO EQUIPMENT FAILURE "At 0824 EST on 11/8/17, a Switchyard Autotransformer began to burn due to an equipment failure. The autotransformer supports interconnectivity between each side of the switchyard and is not required for switchyard operation. There was no work in progress on the associated autotransformer at the time of the event. The autotransformer and the switchyard are outside the protected area approximately one mile away. The fire was contained to the autotransformer only. The fault has been electrically isolated and there was no effect on either MNS [McGuire Nuclear Site] Unit 1 or Unit 2 operations. No personnel were injured as a result of the fire. Local Fire Department responded and has contained the fire. MNS fire brigade leader along with switchyard maintenance have confirmed no effects to the MNS bus lines, power availability, or the ability for the site to generate power. "Environmental personnel have made a notification to the National Response Center due to the oil and foam mixture occurring as a result of the fire response. McGuire hazmat personnel are currently working to contain this oil and foam mixture. Environmental personnel are also submitting a report to the NC [North Carolina] Department of Environmental Water Quality within 24 hours. There is no impact to the public. "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-11-08
53060 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-11-07 19:57 | 2017-11-07 22:32 | 2017-11-08 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP "On 11/7/2017 at 1957 [EST], VC Summer Nuclear Station automatically tripped due to a turbine trip. The cause of the turbine trip is under investigation at this time. "All systems responded as expected. All Control Rods fully inserted and all Emergency Feedwater pumps started as required. The plant is stable in Mode 3. "This event is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The unit is currently stable in Mode 3 with decay heat removal via the Main Steam to the Main Condenser. "The NRC Resident Inspector has been notified." The licensee will notify the South Carolina State Emergency Management Division, the Fairfield, Richland, Lexington and Newberry Counties. * * * UPDATE FROM BETH DALICK TO VINCE KLCO ON 11/8/17 AT 1409 EST * * * "All systems responded as expected, with the exception of 'B' Steam Generator Feedwater Isolation Valve XVG1611 B-FW. This valve did not appear to automatically close and was slow to indicate closed from the Main Control Board. All Control Rods fully inserted and all Emergency Feedwater pumps started as required. The plant is stable in Mode 3." Notified the R2DO (Musser). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-11-07
53059 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2017-11-07 18:10 | 2017-11-07 22:09 | 2017-11-07 | UNIT 1 HIGH PRESSURE COOLANT INJECTION INOPERABLE "On November 7, 2017 at 1810 [CST], Unit 1 High Pressure Coolant Injection (HPCI), was manually isolated following failure of the remote turbine trip pushbutton to function. Unit 1 HPCI Operability Testing was in progress to the point of securing the HPCI turbine with the remote manual pushbutton. The pushbutton failed to trip the turbine resulting in operator action to lower the flow controller setpoint and isolating the HPCI steam line. HPCI remains isolated and is Inoperable pending resolution of the Turbine Trip circuitry. "This event is being reported as a condition that could have prevented fulfillment of a safety function in accordance with 10CFR50.72(b)(3)(v)(D). The HPCI system is a single train system and the loss of HPCI could impact the plant ability to mitigate the consequences of an accident. The Reactor Core Isolation Cooling (RCIC) system was confirmed operable. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-11-07
53058 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2017-11-06 14:45 | 2017-11-07 14:19 | 2017-11-07 | FITNESS FOR DUTY PROGRAM VULNERABILITY "It was determined that a licensed employee was not placed in an additional Fitness-For-Duty (FFD) testing program as directed by the MRO (Medical Review Officer). Upon discovery, the individual was subsequently tested . . . and determined Fit-For-Duty per 10 CFR 26 requirements. "This event is being reported pursuant to 10 CFR 26.719(b)(4). "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2017-11-07
53057 | 0 | WATERFORD | 3 |  |  | [3] CE | 2017-11-07 03:37 | 2017-11-07 10:49 | 2017-11-07 | LOSS OF INBOUND COMMERCIAL LINES AND FTS LINES TO FACILITY "On November 7, 2017, at approximately 0337 (CST) hours, Waterford 3 [WF3] Control Room received a phone call from Entergy's Load Dispatcher to inform us that the NRC was unable to call Waterford 3 by ENS [emergency notification system] phone or by PABX [private automatic branch exchange] phone. The NRC was called by the Waterford 3 Control Room using the PABX at 0339 (CST) hours. However, the ENS phone could not call the NRC. Also, outside lines were not able to call in to Waterford 3. "Offsite prompt Public Warning Sirens were available at all times. State and Local notification capability was available via PABX. WF3 Emergency Response Organization notification capability was available at all times. WF3 site Emergency Response Facility intercommunications were available at all times. "This event is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) due to a loss of offsite communications capability. "ENS communication and full PABX functionality was reestablished at 0452 (CST) on November 7, 2017. "The licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-11-07
53056 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2017-11-07 05:04 | 2017-11-07 08:29 | 2017-11-07 | UNIT 1 AUTOMATIC REACTOR TRIP DUE TO MAIN UNIT GENERATOR OVER CURRENT "On November 7, at 0504 [EST], BVPS [Beaver Valley Power Station] Unit 1 experienced an automatic reactor trip due to Main Unit Generator over current. The Auxiliary Feedwater system activated and remains in service. Offsite power supply is available. Normal and Emergency busses are being supplied by Offsite power. One Source Range channel failed to energize due to its corresponding Intermediate Range instrument being under compensated. It was manually energized and is not indicating as expected. The second Source Range instrument energized but is reading erratically. Both Source Range instruments have been declared inoperable and the appropriate Technical Specification has been complied with by making the Control Rods not capable of withdrawal and isolating all dilution flow paths. Plant trip response was as expected without complications, and all control rods fully inserted in the core. The plant is currently stable in Mode 3. "This event is being reported as an actuation of the Reactor Protection system 10 CFR 50.72(b)(2)(iv)(B) and a Specified System Actuation (Auxiliary Feedwater System) 10 CFR 50.72(b)(3)(iv)(A). "BVPS Unit 2 is unaffected by this event and remains at 100% power in Mode 1. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-11-07
53055 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-11-06 | 2017-11-06 13:21 | 2017-11-06 | AGREEMENT STATE REPORT - STUCK SHUTTER The following information was received from the State of Texas by email: "On November 6, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that a shutter was stuck in the closed position. The Ronan SA1 shutter was closed for maintenance on a hopper and failed to reopen. The gauge contains a 50 millicurie Cesium-137 source. The Licensee stated a service company has been contacted to repair the gauges in the next few days. No individual received significant exposure to radiation due to this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident Number: I-9519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-11-14
53054 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-11-05 12:40 | 2017-11-05 17:11 | 2017-11-05 | LOSS OF SECONDARY CONTAINMENT PRESSURE DUE TO VOLTAGE TRANSIENT "At approximately 1240 CST on 11/05/17, the Main Control Room received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR [volt-ampere reactive] Compensator (SVC) caused by a voltage transient on the 138 kV feed due to thunderstorms in the area. As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no running VF fans, secondary containment differential pressure rose to slightly greater than 0 inches water gauge which exceeded the Technical Specification requirement of greater than 0.25 inches vacuum water gauge at 1241. The Control Room entered EOP-8, Secondary Containment Control. This event is being reported as a Condition that Could Have Prevented Fulfillment of a Safety Function under 10CFR50.72(b)(3)(v)(C). Secondary Containment differential pressure was restored within Technical Specification requirements at 1242 by starting the Standby Gas Treatment HVAC (VG) system. "The NRC Resident Inspector has been notified." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-11-05
53053 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2017-11-03 16:49 | 2017-11-04 14:00 | 2017-11-04 | FITNESS FOR DUTY - LICENSED EMPLOYEE CONFIRMED POSITIVE FOR FITNESS FOR DUTY A licensed employee had a confirmed positive test for a controlled substance during a random fitness-for-duty test. The employees plant access has been placed on administrative hold. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 26.719 |  |  |  | 0 | 2017-11-04
53052 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2017-11-03 20:22 | 2017-11-03 21:08 | 2017-11-06 | INDIAN POINT UNIT 3 REACTOR TRIP ON LOW STEAM GENERATOR LEVEL "On November 3rd, 2017 at 2022 EDT, the Indian Point Unit 3 Reactor Protection system automatically actuated at 100 percent power. Annunciator first out indication was from 33 SG [Steam Generator] Low Level. This automatic reactor trip is reportable to the NRC under 10 CFR 50.72(b)(2)(iv)(B). All control rods fully inserted on the reactor trip. All safety systems responded as expected. The Auxiliary Feedwater System actuated as expected. Offsite power and plant electrical lineups are normal. All plant equipment responded normally to the unit trip. No primary or secondary code safeties lifted during the trip. "The Auxiliary Feedwater System actuated following the automatic trip as expected. This is reportable under 10 CFR 50.72(b)(3)(iv)(A). The Emergency Diesel Generators did not start as offsite power remained available and stable. The Unit remains on offsite power and all electrical loads are stable. Unit 3 is in Hot Standby at normal operating temperature and pressure with decay heat removal using auxiliary feedwater to the steam generators and normal heat removal through the condenser via the high pressure steam dumps. Unit 2 was unaffected and remains at 100 percent power. "A post trip investigation is in progress." The licensee indicated that Radiation Monitor number 14 spiked twice during the transient, however, is currently not indicating any signs of radiation. The licensee will notify the NRC Resident Inspector and the NY Public Service Commission. * * * UPDATE AT 1523 EST ON 11/06/17 FROM RAMIREZ OVIDIO TO JEFF HERRERA * * * "The initial notification stated that Indian Point Unit 3 Reactor Tripped on 33 SG [Steam Generator] Low Level, this is incorrect. Indian Point Unit 3 Reactor Tripped on a Turbine Trip. The Turbine Trip was caused by a Generator Back-up Lockout Relay. The Turbine Trip was the 'first' annunciator first-out but was acknowledged instead of silenced during initial operator actions. The Turbine Trip first-out being acknowledged allowed a Low Steam Generator first-out to later annunciate. A Low Steam Generator Level is an expected condition post trip. "This update does not change any actions taken by the operating team or required notifications under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "A post trip investigation remains in progress. "The licensee will notify the NRC Resident Inspector and the NY Public Commission." Notified the R1DO(Cook) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-11-03
53051 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2017-11-03 | 2017-11-03 | 2017-12-14 | STATION VENT RADIATION MONITOR EFFICIENCY FACTOR NON-CONSERVATIVE "On 11/3/17, with the unit operating in Mode 1 at approximately 100 percent power, an issue was identified with the Station Vent Radiation Monitors. The noble gas channels utilize an efficiency factor for isotope Kr-85 instead of the required Xe-133. For the normal range radiation monitors, the efficiency factor is non-conservative, resulting in both monitors being declared inoperable at 1045 hours EDT. As a result, the Normal Control Room Ventilation System was shut down and isolated, and the Control Room Emergency Ventilation System started in accordance with Technical Specification Required Actions at 1122 hours. "The inoperability of both Station Vent Normal Range Radiation Monitors represents a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. The Station Vent Accident Range Monitors also utilize an efficiency factor for Kr-85 instead of Xe-133, but for the Accident Range Monitors the efficiency factor is conservative. Because alternate means exist to determine release rate, which include use of grab samples and field surveys, this degraded capability does not represent a major loss of emergency assessment capability. "The NRC Resident Inspector has been notified." * * * RETRACTION FROM NICK DOWNING TO DONALD NORWOOD AT 0927 EST ON 12/14/2017 * * * "On 11/3/2017, the efficiency factors for the Station Vent Normal and Accident Range Radiation Monitors were revised to the proper setting for the required isotope, the normal range monitors were declared Operable, and the Control Room Normal Ventilation System was returned to service. "An evaluation of the issue with the Station Vent Normal Range Radiation Monitors was performed, which determined the Control Room Ventilation isolation setpoint is well below the point at which the dose to the Control Room Operators would exceed General Design Criteria (GDC) limits following a Design Bases Accident. The error introduced from using an incorrect efficiency value did not challenge the margin to the GDC limits; therefore, the Station Vent Normal Range Monitors remained operable, and this issue did not prevent the monitors from fulfilling their safety function to mitigate the consequences of an accident. "The NRC Resident Inspector has been notified." Notified R3DO (Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-11-03
53050 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2017-10-03 | 2017-11-03 09:34 | 2017-11-03 | LOSS NI-63 GAS CHROMATOGRAPH SOURCE On October 3, 2017, Agilent Technologies was notified of a potential loss of an electron capture detector (ECD) that is a component of a gas chromatograph. The ECD contains an embedded sealed source (Ni-63; 15 milliCuries). The device was being shipped from Syngenta Crop Protection LLC., Greensboro, NC, to CSC, LLC. field repair center in Winchester, Tennessee. The gas chromatograph was packaged on June 28, 2017 with an estimated shipment date during the week July 3, 2017. The carrier is not known at this time. The device has not been located at the repair site. An investigation is being performed by the licensee to locate the device. The ECD source serial number YA779, Model 1533, SSD: NR-0348-D-111-B. Agilent Technologies holds an NRC license (07-28762-01) and is located at 2850 Centerville Road, Wilmington, DE 19808. * * * UPDATE AT 1430 EDT ON 11/3/17 FROM DAVID BENNETT TO JEFF HERRERA * * * The device was located at the repair center by repair center personnel. The device will to be returned to the licensee. Notified the R1DO (McKinley), ILTAB (via email), NMSS (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2017-11-13
53049 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-11-01 14:25 | 2017-11-01 22:26 | 2017-11-01 | DESIGN DEFICIENCIES IDENTIFIED DURING ENGINEERING REVIEW "At 1425 [CDT] on November 1, 2017, Operations was notified of a condition affecting Unit 3 4kV Shutdown Boards 3EA, 3EB, 3EC, and 3ED. It was discovered that multiple potential transformer (PT) primary fuses are GE type EJ1 size 0.5 AMP which does not coordinate with the PT's secondary fuses. "A fault on the associated cable could clear the primary PT primary fuses for the 4kV Shutdown Board. This would result in the board tripping 4kV motor loads, disconnecting from Off-site power and connecting to the Emergency Diesel Generator. However, since the PT fuse is cleared, the under-voltage trips on the 4kV motors would remain in if there is no Common Accident Signal (CAS) present. The 4kV motor loads include Residual Heat Removal (RHR) Pumps, Core Spray (CS) Pumps, Residual Heat Removal Service Water (RHRSW) Pumps, and Emergency Equipment Cooling Water (EECW) pumps. "Review of NFPA 805 analyses show the cables for all four U3 4kV Shutdown Boards are routed in Fire Area 03-03 and Fire Area 16. Therefore a fire in either area could result in a loss of all four U3 4kV Shutdown Boards motor loads. Cables for 4kV Shutdown Board 3EA and 3EB are both routed in Fire Area 21 which could result in a loss of both Division I Shutdown Board motor loads. "Compensatory fire watch measures have been established. "This event requires an 8 hour report in accordance with 50.72(b)(3)(ii)(B), 'Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety.' "The NRC Resident Inspector has been notified. "CR 1354129 was initiated in the Corrective Action Program." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-11-01
53048 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2017-11-01 12:25 | 2017-11-01 16:33 | 2017-11-01 | UNIT 2 FAILED LLRT SURVEILLANCE TEST DUE TO EXCESSIVE LEAKAGE "On November 1, 2017 at 1225 CDT, both the 2-220-58A Feed Water Inboard Check Valve and the 2-220-62A Feed Water Outboard Check Valve failed Local Leak Rate Testing (LLRT) acceptance criteria due to excessive leakage. These valves are considered primary containment isolation valves, and as such, are required to ensure that an adequate primary containment boundary is maintained. "Technical Specification (TS) 5.5.12, 'Primary Containment Leakage Rate Testing Program,' establishes limits for Primary Containment leakage. Based upon the results of the LLRT, Dresden, Unit 2, may not have met the limits for primary containment leakage during the last operating cycle as specified in TS 5.5.12.C. "Dresden Unit 2 is currently in Mode 5 for a refueling outage and per Dresden TS 3.6.1.1, 'Primary Containment,' Primary Containment is not required in the current mode of operation (i.e., Mode 5). However, in accordance with 10 CFR 50.72(b)(3)(ii)(A), this event is reportable as a condition that resulted in a principal safety barrier being seriously degraded. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-11-01
53047 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-09-22 | 2017-10-31 15:36 | 2017-10-31 | AGREEMENT STATE REPORT - FAILED SEALED SOURCE LEAK TEST The following information was received from the State of New York via fax: "On October 10, 2017 Eastman Kodak Company reported that the results of a leak test showed 0.006 micro curies of removable contamination. The source that was surveyed is an NRD Model A2003, s/n 2977, static elimination device that contains 18.25 mCi of Am-241. The leak test was collected on September 22 and sent to an outside lab for analysis on September 25. The results of the survey were reported on October 9. "Eastman Kodak will suspend the use of the source until the results of a retest are available. Surfaces adjacent to the device will be surveyed to determine if contamination spread. "Event Report ID No.: NYDOH-17-10" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-11-08
53046 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2017-09-07 | 2017-10-31 12:02 | 2017-11-02 | WRONG IROFS PROCEDURE FOLLOWED PRIOR TO FILLING CYLINDER The following event occurred on 9/7/17 but was not discovered until 1511 MDT on 10/30/17. "Appendix A to 10 CFR 70(b)(2). "While performing an extent of condition on a previous condition report in the UUSA [URENCO USA] corrective action program, UUSA discovered a product cylinder that had been introduced to the process inadvertently as a new or washed cylinder when it in fact was a heeled cylinder. The discrepancy caused the incorrect IROFS [Items Relied On For Safety] to be applied when connecting the cylinder to the process; IROFS16a for new/washed cylinders and IROFS16e/f for heeled cylinders. "The IROFS applicable (16e/f), administratively limits moderator (hydrogenous) mass in heeled cylinders containing enriched uranic material to ensure sub-criticality by limiting cylinder vapor pressure and heeled 30B cylinder weight. IROFS16e was completed SAT using the IROFS16a surveillance and the Product connect procedure. IROFS16f, an independent weight check and vapor pressure check, was not completed during the cylinder connect. "The IROFS performed (16a), administratively limits moderator mass (hydrocarbon oil and water) in new and cleaned 30B cylinders containing enriched uranic material to ensure sub-criticality by allowing no visible oil and by limiting cylinder vapor pressure. "Both of the aforementioned IROFS prevent criticality by limiting moderator mass, however the performance is different in heeled cylinders. IROFS16e/f are implemented by independently limiting cylinder vapor pressure and weight prior to introducing product into the cylinder. "Cylinder UREU103960 was connected to the process on September 7, 2017, filled with product material, heated, and liquid sampled. A criticality DID NOT occur. Existing sample results show normal for contaminants boron, technetium, and silica. Sample testing for purity showed UF6 at a temperature 24C acceptable per ASTM C996 standards of [greater than] 99.5 [percent]. "10 CFR 70.50(c)(1)(iii): "(A) The IROFS not performed prevent criticality. No criticality occurred, no radiological hazard, nor chemical hazards were present. "(B) No exposure occurred. "(C) UUSA Shift Operations inadvertently treated the cylinder with the wrong classification. The pedigree of the cylinder was misinterpreted and the IROFS16a surveillance was performed instead of the correct IROFSI6e/f surveillance. "(D) IROFS remain available and reliable to perform their function. IROFS16 series are applicable during cylinder connects and are established by the performer of the cylinder connect evolution. The IROFS are not affected for future cylinder evolutions. "(iv) The cylinder is currently inside the Cylinder Receipt and Dispatch Building. No external conditions affect this event. "(v) UUSA immediately treated the cylinder as an anomalous condition in accordance with internal procedures and Operations Reporting Manual. The cylinder had been through the sampling process and the results are being reviewed by UUSA NCS/ISA Engineering staff. "(vi) No criticality event occurred. The cylinder is in a criticality safety anomalous condition. There are currently no other cylinders immediately adjacent and the area has been roped off. "(vii) No emergencies have been, nor will any be declared. "(viii) No state or other federal agencies will be notified. "(ix) No press releases are planned. "SAFETY SIGNIFICANCE OF EVENTS: No Event Occurred "SAFETY EQUIPMENT STATUS: The cylinder is in a criticality safety anomalous condition. Existing sample results from cylinder contents are being reviewed. "STATUS OF CORRECTIVE ACTIONS: Condition has been entered into facility's Corrective Action Program" The licensee will inform NRC Region 2 (Sykes). * * * UPDATE AT 1629 EDT ON 11/02/2017 FROM RICARDO MEDINA TO JEFF HERRERA * * * "11/2/2017 1429 MST Update: Based on existing liquid sample results, conservatively assuming a moderator concentration of 0.5 percent, the filled cylinder's heel meets the acceptance criteria. This demonstrates a criticality event to be highly unlikely and therefore, the anomalous condition was exited at 1242 MST." Notified the R2DO (Ehrhardt), NMSS (via email) and Fuels Group (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2017-10-31
53045 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-10-30 | 2017-10-30 19:25 | 2017-10-30 | AGREEMENT STATE REPORT - LOST TROXLER MOISTURE DENSITY GAUGE The following information was received from the State of California via email: "On 10/30/17, California Office of Emergency Services contacted RHB [Radiologic Health Branch] to report a lost moisture density gauge. The lost gauge is a Troxler Model 3440, S/N 23171, containing 9 mCi of Cs-137 and 44 mCi of Am241/Be. According to the RSO [Radiation Safety Officer], the gauge user left the gauge on the tailgate of his truck without properly securing it, and drove off to the next job site. A passing driver alerted the gauge user of a falling object from his truck at the intersection of Floyd Street and Oakdale Street in Modesto, CA. The user immediately went back to the intersection, but was unable to locate the gauge. The RSO has notified the Modesto Police Department of this incident. He will be posting a reward for the safe return of the gauge on Craigslist. The RHB will be following up on this investigation. "5010 Number: 103017" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-11-07
53044 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-10-30 09:42 | 2017-10-30 15:50 | 2017-10-30 | TEMPORARY LOSS OF CONTROL ROOM ENVELOPE BOUNDARY "At 0942 Eastern Daylight Time (EDT) on October 30, 2017, a Main Control Room (MCR) alarm was received for low control room positive pressure. "At 0943 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10 Control Room Emergency Ventilation System (CREVS) was declared not met for both trains and Condition B entered. "At 0945 EDT the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. "The safety function of the CRE boundary is to ensure the in-leakage of unfiltered air into the CRE will not exceed the in-leakage assumed in the licensing basis analysis of Design Basis Accident (DBA) consequences to CRE occupants. From 0942 EDT to 0943 EDT WBN [Watts Bar Nuclear] was unable to validate that CREVS could fulfill its required Safety Function. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D). "NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-10-30
53043 | 0 | AMETEK SOLID STATE CONTROLS |  |  |  |  | 2017-10-30 | 2017-10-30 12:36 | 2017-10-30 | PART 21 - EATON AUXILIARY SWITCH INSTALLED EG FRAME MOLDED CASE CIRCUIT BREAKER POTENTIALLY DEFECTIVE The following is excerpted from an email received from Ametek: "COMPONENT DESCRIPTION: "Eaton auxiliary switches, catalog number AUX2A2BPK installed in EG Frame Molded Case Circuit Breakers (30A - 125A). "PROBLEM YOU COULD SEE: "Eaton auxiliary switches manufactured after May 2015 and installed in EG Frame Breakers (30A - 125A) could experience intermittent operation of the auxiliary switch due to a design defect of the auxiliary switch. The design defect of the auxiliary switch can result in the auxiliary switch to fail to change state during breaker operation. "CAUSE: "Ametek Solidstate Controls identified intermittent auxiliary switch operation during testing. Eaton confirmed a problem with the auxiliary switches used in EG Frame Breakers manufactured since May of 2015. The auxiliary switch in the EG frame breakers may not operate reliably, resulting in the auxiliary switch returning to, or staying in, its shelf state. The auxiliary switch is being redesigned to improve the mechanical interface reliability between the breaker mechanism and the auxiliary switch. "EFFECT ON SYSTEM PERFORMANCE: "The breaker overcurrent protection and shunt trip function are not affected by this defect. If the auxiliary switch defect occurs in the DC Input breaker (B1) while the system is operating, the static switch will transfer the load to Bypass (alternate Source) and the Inverter will shut down. If the defect occurs during startup, the Inverter will not start. If the auxiliary switch defect is present in any other breaker, it will result in a failure to annunciate a breaker closed indicator. A list of affected equipment with the breaker locations is provided below. "ACTION REQUIRED: "Replacement auxiliary switches from Eaton are expected to be available sometime in the second quarter of 2018. An immediate solution is not available. For circuit breakers in the B1 position, Ametek Solidstate Controls recommends replacing the auxiliary switch as soon as a redesigned auxiliary switch is available. "For all other breakers, the state of the breaker should be verified prior to performing any maintenance until the auxiliary switch can be replaced. In this situation, the auxiliary switch should be replaced at the earliest convenience. "AMETEK SOLIDSTATE CONTROLS CORRECTIVE ACTION: "If you wish to replace the auxiliary switches, Ametek Solidstate Controls will work with you to arrange replacements. Please contact Mr. Mark Shreve of our Client Services group at 1-800- 222-9079 or 1-614-846-7500 ext. 6332. mark.shreve@ametek.com "A copy [including Eaton EG Frame Part Number, Ametek Part Number, Serial Number, Equipment Part No., Customer, Breaker Location and Total] will also be provided to the affected licensees - Ameren, TVA, Southern Nuclear, Duke, and Krsko." Curtiss Wright also received eight (8) of the suspect breakers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-10-30
53042 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2017-10-30 04:04 | 2017-10-30 12:48 | 2017-10-30 | DEFECTIVE WELD IDENTIFIED ON REACTOR COOLANT PUMP SEAL UPPER ROOT "During a scheduled refueling outage, an inspection of components inside containment revealed a suspected weld defect on 1CV-309B, 1P-1B RCP Labyrinth Seal 1PT-124 Upper Root. "10 CFR 50.2 (2)(i) defines the reactor coolant pressure boundary as being connected to the reactor coolant system, up to and including the outermost containment isolation valve in system piping which penetrates primary reactor containment. The weld defect is located on the transmitter side of 1CV-309B. This can be isolated from the RCS by shutting 1CV-309B and 1CV-308B, 1P-1B RCP Labyrinth Seal 1PT-124 Lower Root. "Based on the definition provided in 10 CFR 50.2, the condition is considered reportable under 50.72(b)(3)(ii). "Unit 1 is currently in mode 3. Repairs for the condition are being determined. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-10-30
53041 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2017-10-30 02:47 | 2017-10-30 10:38 | 2017-10-30 | SEVERE WEATHER CAUSES LOSS OF POWER TO SUPPORT BUILDINGS There was a loss of power from the local grid which did not affect the power block. The support buildings lost power and a UPS failed which affects computers, switching, and telephones. This includes a loss of the Emergency Response Data System (ERDS). The Joint Information Center and Emergency Operations Facility were not affected. Though this is a major loss of communications ability, alternate communications methods are available. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-10-30
53040 | 0 | SAINT VINCENT HOSPITAL |  |  |  |  | 2017-10-27 15:28 | 2017-10-28 13:29 | 2017-10-28 | MEDICAL EVENT - DOSE MISADMINISTRATION A patient receiving treatment for a liver disease was prescribed 60 milliCuries of Y-90 SIR-Spheres. The delivered dose was calculated to be 11 milliCuries and stasis was not achieved. The patient was notified of the misadministration and is scheduled to receive the fully prescribed dose. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2017-11-06
53039 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2017-10-27 10:20 | 2017-10-27 12:11 | 2017-10-27 | NEBRASKA AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was obtained from the state of Nebraska via email: "Nebraska Department of Health and Human Services, Office of Radiological Health was notified on October 27, 2017, by the Radiation Safety Officer (RSO) from Panhandle Geotechnical and Environmental, of a loss of control and damage to a portable gauge (licensed material) on Friday, October 27, 2017 outside of a temporary jobsite located near Kimball, Nebraska. The licensed material is a Troxler 3400 series moisture density gauge, serial number 30894, containing 9 mCi of Cs-137 and 44 mCi of Am-241:Be. The licensee reported to the State that an employee placed the license material on the standardization block performing the normal gauge standardization behind the pickup truck. The source rod was not extended during this time. When the employee was told to move the vehicle in order to move a shipping container to the job site, the employee placed the vehicle in reverse and backed into the gauge. The employee pulled forward after hearing the damage to the gauge and placed the pickup in park. The employee got out of the vehicle and assessed the situation. After noticing the damage to the gauge, the employee called the RSO and alerted nearby personnel to stay away from the area. No personnel were injured and the nearest person was at least 50 feet away. The employee moved the pickup further away (~20 feet from the gauge) and caution taped the area, prohibiting access. The RSO arrived at 1240 hrs. (Central Daylight Time) and performed a radiation survey and a wipe test. The RSO did not find any elevated readings and the sources were not leaking. The RSO and employee placed the gauge back in the shipping container and will deliver the gauge to licensed facility for repairs. A 30 day written report is to follow." State Event Report ID No.: NE-17-0006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2017-11-06
53038 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-10-26 | 2017-10-26 | 2017-12-15 | BOTH DIVISIONS OF DRYWELL VACUUM RELIEF DECLARED INOPERABLE "At 1055 [CDT], drywell purge supply/initial vacuum relief 1E61F003B was declared INOPERABLE for Drywell Vacuum Relief System while performing a monthly surveillance. 1E61F003B is a Division II powered valve. Division 1 Emergency Diesel Generator is INOPERABLE due to a tagout. At 1455, under LCO 3.8.1.B.2 the station declared both divisions of Drywell Vacuum Relief INOPERABLE. GGNS [Grand Gulf Nuclear Station] identified that a loss of Safety Function occurred due to a loss of two 10-inch vacuum relief lines from the Drywell required by Technical Specification 3.6.5.6 and therefore could have prevented fulfillment of its safety function. That event is being reported under 10CFR50.72(b)(3)(v)(D), as any event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. " Both divisions inoperable has placed the plant in a 72-hr. LCO shutdown action statement. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM RALPH FLICKINGER TO HOWIE CROUCH AT 1643 EST ON 12/15/17 * * * "At 1055 [CDT on 10/26/17], Drywell purge supply/initial vacuum relief 1E61F003B was declared INOPERABLE for Drywell Vacuum Relief System while performing a monthly surveillance. 1E61F003B is a Division II powered valve. Division 1 Emergency Diesel Generator was INOPERABLE due to a tagout. At 1455 [CDT on 12/26/17], under LCO 3.8.1.B.2, the station declared both divisions of Drywell Vacuum Relief INOPERABLE. GGNS identified that a loss of Safety Function occurred due to a loss of two 10-inch vacuum relief lines from the Drywell required by Technical Specification 3.6.5.6 and therefore could have prevented fulfillment of its safety function. "This was initially reported under 10 CFR 50.72(b)(2)(v)(D). Div. 1 EDG was initially taken out of service at 1455 on 10/26 for preplanned maintenance (OP-EVAL). It was subsequently declared INOPERABLE-INOP due to a visible flaw indication in the exhaust manifold (1117 on 10/27). A subsequent Maintenance Functional Failure Evaluation and Past Operability Determination concluded the diesel was capable of performing its intended function for the required mission time, and therefore met the definition of OPERABLE. "NUREG-1022 provides clarification for 10 CFR 50.72(b)(2)(v). NUREG Section 3.2.7, paragraph 4, states '...unless a condition is discovered that would have resulted in the system [otherwise] being declared inoperable, reports are not required when systems are declared inoperable solely as a result of Required Actions for which the bases is the assumption of an additional random single failure (i.e., . ..LCO 3.8.1, 'AC Sources Operating,' Required Actions .., B.2, or C.1). Per ACTION 3.8.1 .B.2, both trains of Drywell vacuum and Drywell Purge were inoperable for the purposes of Tech Specs. However, the normal power supply was available to Division 1 and there were no conditions which would have rendered the Division 1 diesel inoperable. Therefore, per Section 3.2.7 of NUREG-1022, this was not a Loss of Safety Function and was not reportable under 50.72(b)(2)(v)(D)." The licensee has notified the NRC Resident Inspector. Notified R4DO (Deese). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-10-26
53037 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2017-10-25 | 2017-10-26 17:00 | 2017-10-26 | PART 21 - SPEED SWITCH ISSUE RESULTS IN EMERGENCY DIESEL GENERATOR FAILURE TO START The following information was received by facsimile from the vendor: "Component: Speed switch P/Ns ESl50267C, ESl50267E, ESl50267H, and ESl50267K. "Summary: Engine Systems Inc. (ESI) began a 10CFR21 evaluation on September 12, 2017 upon notification of a potential issue with speed switch P/N ESl50267K supplied to Hope Creek Nuclear Generating Station. The speed switch had reportedly failed in service which resulted in a failure to start of the emergency diesel generator (EDG). An analysis performed by Exelon Powerlabs determined the failure was due to a shorted capacitor that is installed on the speed switch's relay output contacts to ground. The evaluation was concluded on October 25, 2017 and it was determined that this issue is a reportable defect as defined by 10CFR Part 21. The speed switch output contacts are utilized in the engine's start circuitry and failure to function properly could adversely affect the safety-related operation of the emergency diesel generator set. "Impact on Operability: If the resistance path to ground were sufficiently low, the ability of the relay output contacts to pick-up and/or drop-out associated components would be compromised. The speed switch relays are used in safety-related EDG start circuitry to control various electrical relays. Failure to properly control any of these components could adversely affect the safety-related operation of the emergency diesel generator. "Root cause evaluation: The root cause of the failure is a deficiency in the design and selection of the EMC (Electromagnetic compatibility) mitigating components. Consideration was not given for the impact of voltage transients imparted on the capacitors during coil de-energization. For customers without suppression from the inductive kick, the magnitude of voltage transients may be sufficient to damage and ultimately degrade the capacitors to the point of failure." Affected nuclear plants include Nine Mile Point, Quad Cities, Dresden, Davis Besse and Hope Creek. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-10-26
53036 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2017-10-26 02:12 | 2017-10-26 05:54 | 2017-10-26 | AUTOMATIC REACTOR TRIP FOLLOWING A LOSS OF LOAD "On October 26, 2017 at 0212 EDT St. Lucie Unit 2 experienced a reactor trip due to a loss of load event resulting in an RPS [Reactor Protection System] actuation. The cause of the loss of load is currently under investigation. Following the reactor trip, an Auxiliary Feedwater Actuation Signal occurred due to low level in the 2A Steam Generator. One of the two Main Feed Isolation Valves to the 2A Steam Generator did not close on the Auxiliary Feedwater Actuation Signal. 2A Steam Generator level was restored by Auxiliary Feedwater. The 2B Steam Generator level is being maintained by Main Feedwater. All CEAs [Control Element Assemblies] fully inserted into the core. Decay heat removal is being accomplished through forced circulation with stable conditions from Auxiliary Feedwater/Main Feedwater and Steam Bypass Control System. Currently maintaining pressurizer pressure at 2250 psia and Reactor Coolant System temperature at 532 degrees F. "St. Lucie Unit 1 was unaffected and remains in Mode 1 at 100 percent power. "This report is submitted in accordance with 10 CFR 50.72(b)(2)(iv)(B) for the reactor trip and 10 CFR 50.72(b)(3)(iv)(A) for the Specified System Actuation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-10-26
53035 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2017-10-24 10:30 | 2017-10-25 09:55 | 2017-10-25 | FITNESS FOR DUTY REPORT "GE Hitachi Security became aware of Potentially Disqualifying Information regarding a contract worker who was approved for access to two plant sites by the GEH Access Authorization Unit (AAU). As part of the initial review of this information, it was further discovered that the requisite employment verification performed by the AAU failed to properly verify employment for at least one year of the required scope. "Affected plant sites have been notified and the individual's access terminated pending further investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FITNESS FOR DUTY | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 26.719 |  |  |  | 0 | 2017-10-25
53034 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2017-10-24 13:50 | 2017-10-24 14:49 | 2017-10-24 | SAFEGUARDS REPORT - DISCOVERED A VULNERABILITY IN A VITAL AREA BARRIER "At approximately 1350 hours EDT on 10/24/2017, Robinson Nuclear Plant discovered a vulnerability in a Vital Area (VA) barrier that could have allowed unauthorized or undetected access to a vital area. Compensatory measures were immediately established. "The vulnerability was the result of authorized work. A plate was immediately installed to cover the opening prior to personnel leaving the work area. The initial investigation did not reveal any evidence of unauthorized entry or tampering. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-10-24
53033 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-10-19 11:05 | 2017-10-23 17:30 | 2017-10-23 | AGREEMENT STATE REPORT - WHOLE BODY MONITOR EXCEEDED THE ANNUAL OCCUPATIONAL EXPOSURE LIMIT The following was received via email from the State Of Louisiana: "The RSO [Radiation Safety Officer] was notified by Landauer that an individual's August 1-31, 2017, personal whole body monitor exceeded the annual occupational exposure limit. MG [Mistras Group, Inc.] contacted the Radiography Instructor (RI) and conducted an internal investigation with the radiation safety personnel and the RI that concluded September 20, 2017. It concluded with the exposures were incremental over the annual monitoring period and there was no evidence the whole-body badge had received the exposures and the RI had not received the exposures to his monitor. At this time MG is not pursuing this issue further to reduce the exposure to the whole-body monitor. The RI was issued safety equipment that was not under the RI's constant control or observation at all times. "The RI notified the Department, LDEQ [Louisiana Department of Environmental Quality], on October, 19, 2017, [at approximately] 1105 [CDT]. LDEQ was notified due to the fact the RI was not employable to perform radiography work in his field due to the radiation exposure levels. "This was a complaint from a Radiography Instructor (RI) whose personal whole-body badge exposure reading levels exceeded the 5,000 mRem/5 Rem occupational annual limit. The RI called in a complaint because he was no-longer employed by MG and with the excessive exposure he was not employable to work in a radiation restricted area. "A LDEQ investigator took the call from the RI. The excessive exposure reported by Landauer to MG for the August 2017 monitoring period was 5,440 mRem Dose Equivalent. MG reported the excessive exposure during a phone call during the LDEQ preliminary investigation. The MG went on to explain that the RI was still in possession of his September 2017 personal whole body monitor." Event Report ID: LA-170016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-10-31
53032 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2017-10-20 10:00 | 2017-10-23 12:34 | 2017-10-23 | AGREEMENT STATE REPORT - GAMMA KNIFE MALFUNCTION On 10/20/17, at 1000 PDT, a Gamma knife treatment was in process when the machine malfunctioned and recorded an error. The backup battery on the UPS (Uninterruptible Power Source) was low and resulted in the machine pausing and returning the source to the shielded position. The patient received approximately one third of the prescribed dose. The service provider was contacted and is scheduled to report to the hospital today (10/23/2017) to replace the backup battery. Elekta Leksell Gamma Knife Model Perfexion Serial number NM-001-NM201 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2017-10-31
53031 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2017-10-23 04:00 | 2017-10-23 09:35 | 2017-10-23 | LEAKAGE IDENTIFIED ON ONE INCH LINE SOCKET WELD FOR THE B RECIRCULATION PUMP "On Monday, October 23, 2017, with PBAPS [Peach Bottom Atomic Power Station] Unit 3 in Mode 3 at the beginning of a refueling outage, personnel entered the drywell to perform an inspection. At approximately 0400 [EDT], leakage was identified on a one-inch diameter instrument line socket weld for the 'B' recirculation pump. Because the leak was misting, the leakage rate could not be quantified. However, Unit 3 reactor coolant unidentified leakage prior to plant shutdown was 0.18 gpm. This line is considered part of the primary coolant pressure boundary. "This event is being reported as an occurrence of an event or condition that results in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded under 10 CFR 50.72(b)(3)(ii). "The Station is preparing an evaluation and repair plan at this time. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-10-23
53030 | 0 | WEST BRANCH REGIONAL MEDICAL CENTER |  |  |  |  | 2017-10-23 07:40 | 2017-10-23 09:11 | 2017-10-23 | DELIVERY OF TC-99 SHOWED INCREASED RADIATION LEVEL ON CONTACT WITH PACKAGE At 0740 EDT on 10/23/2017, while performing equipment quality control, the nuclear medical technician identified that the incoming case containing less than 100 milliCuries of Tc-99 measured from 190-220 mR/hr on contact. The technician performed a surface wipe to identify contamination and determined that there was no leakage or spill of contamination. At 0850 the radiation safety officer was notified of the event. The case was then placed into a waste decay storage area away from other personnel. The company that shipped the package was also contacted regarding the situation. The type of isotopes provided were provided based on the ordered quantity, however, the technician reported that there might be other isotopes in the container, however could not verify without opening the container to look inside. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2017-10-23
53029 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-09-21 22:30 | 2017-10-20 16:52 | 2017-10-20 | AGREEMENT STATE REPORT - LOST Cs-137 VIAL STANDARD The following information was received from the state of New York via fax: "On 10/5/17 the Department [New York State Department of Health] was notified of a lost Cs-137 vial standard (Solid Sealed Source, Eckert and Ziegler, S/N: 1258-41-15, Activity 194.4 microCi on 12/01/2007) from the hot lab of a mobile PET imaging service provider coach. "A report from the licensee [Alliance HealthCare Services, Inc.] gave the following timeline. On 9/21/17 the driver of the mobile imaging coach slammed on the brakes going over the GW [George Washington] bridge to avoid an accident on the way to Bronx-Lebanon Hospital. Upon arrival, the driver went to assess damage in the hot lab and notified an Alliance manager of the incident. The cabinet that held up the L block had fallen away from the wall and broke a portable sink. Some other items had been dislodged. He and another driver put the cabinet back into place and put items back in their respective places. They discarded pieces of the broken sink in a trash can on the side of the parking lot of the client facility. The next morning an Alliance Tech did a visual inventory and confirmed that all sources were present. "On 10/3/17 another Alliance Tech went into the hot lab on the coach and discovered that the lead pig for the Cs-137 vial standard was empty. The Alliance staff searched for the vial but could not locate it on the coach. It was reported to the RSO [Radiation Safety Officer] on 10/5/17. "On 10/06/17 a physicist did a survey to determine whether the vial was on the coach and had rolled under a piece of equipment. They determined that the vial was not on the coach and did not find any contamination. "Alliance believes that the source was thrown out in the general waste stream outside Bronx-Lebanon Hospital, along with pieces of the broken sink from the hot lab. The NYSDOH notified both the NYS Dept. of Environmental Conservation and the New Jersey Dept. of Environmental Protection of possible waste alarm trips. "Event Report ID No. NYDOH-17-09" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-10-30
53028 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2017-10-20 | 2017-10-20 15:59 | 2017-10-20 | AGREEMENT STATE REPORT - MISSING XRF DEVICE RETURNED TO MANUFACTURER FOR REPAIRS The following information was received from the State of New Jersey via email: "The licensee [Lew Corporation] called [the NJ Department of Environmental Protection's Bureau of Environmental Radiation] to report that one of their XRF devices is apparently lost. The device is a Protec LPA-1, serial number 2106, containing a Co-57 source with an activity of 7.2 mCi as of January 2017. The unit was shipped to the manufacturer, Protec, back in July for repairs. The licensee has proof from the delivery service that the device was signed for at Protec's office in Massachusetts back in July. Protec has now informed the licensee that they don't know the location of the device and are considering it lost. A written report from the licensee will be supplied within 30 days. The Massachusetts radiation control office has been informed." The LPA-1 is a handheld Lead Paint Analyzer using X-Ray Florescence (XRF) and K-Shell technologies to non-destructively detect the presence of lead on a painted surface. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2017-10-30
53027 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-10-20 13:37 | 2017-10-20 14:42 | 2017-10-23 | AGREEMENT STATE REPORT - STOLEN GAUGE The licensee notified the South Carolina Department of Health and Environmental Control that an Instrotek Model 3500 moisture density gauge serial number 3055 was stolen from the licensee's truck during a lunch break. The gauge contained 11 mCi of Cs-137 and 44 mCi of Am-241:Be. LLEA was notified of the incident. * * * UPDATE AT 0948 EDT ON 10/23/2017 FROM ANDREW M. ROXBURGH TO JEFF HERRERA * * * The following update was received from the South Carolina Department of Health and Environmental Control via email: "The licensee notified the Department [South Carolina Department of Health and Environmental Control] at approximately 1330 [EDT] on October 20, 2017 that one of its gauges had been stolen from the back of one of its trucks while on a lunch in Myrtle Beach, SC. The gauge is an Instrotek Model 3500 moisture density gauge serial number 3055. The gauge contained 11 mCi of Cs-137 and 44 Ci of Am-241:Be. The licensee is in the process of getting a copy of the police report to submit to the Department." Notified the R1DO (Bickett), ILTAB and NMSS_Events (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-10-30
53026 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2017-10-18 10:05 | 2017-10-19 10:03 | 2017-10-19 | INDIVIDUAL CONTAMINATED WHILE OFFLOADING URANYL NITRATE "24 Hour Event Notification based on 10 CFR 70.50(b)(1) for an unplanned contamination event that requires access to the contaminated area to be restricted for more than 24 hours, by imposing additional radiological controls or by prohibiting entry into the area. "On October 18, 2017 at approximately 1005 EDT, while operators were unloading a LR-230 container of liquid uranyl nitrate, the liquid offload hose became disconnected from the container fitting. The event resulted in a uranyl nitrate exposure to one operator and a release in the offloading area. The estimated quantity of spilled solution was 6-8 gallons. "The operator used the emergency shower and was cleared by Health Physics and Medical personnel. Operations and Health Physics personnel cleaned up the spill of low-enriched uranyl nitrate. While decontamination efforts are essentially complete, efforts continue to assure there is no smearable contamination. "This event has been entered into the facility Corrective Action Prevention And Learning system (CAPAL)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2017-10-19
53025 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-09-21 | 2017-10-18 14:41 | 2017-10-18 | AGREEMENT STATE REPORT - FAILED FIXED NUCLEAR DENSITY GAUGE SHUTTER The following information was received via e-mail. "The licensee discovered that the shutter to a fixed nuclear density gauge was missing on 9/21/17 during routine leak tests. Prominent barriers were immediately put in place around the fenced area containing the gauge to further cordon off the area to prevent any access to the area. Three days prior to discovery, the licensee performed routine cleaning in which the shutter was observed in place at that time. The gauge is located on top of winding equipment 6.5 feet high, located inside of a fenced area. The fenced area provides an additional 4 feet from the gauge separating areas where personnel may traffic on the ground. The radiation beam for the gauge is pointing down from its location and travels about 6 inches to the target plate. By facility design, placement of the gauge includes additional barriers and fencing, access to the gauge by any person is restrictive and following interviews with the licensee, no exposures are suspected to have occurred due to the faulty shutter. "The manufacturer completed repairs to the fixed gauge on 10/6/17. "Gauge Information: NDC Amersham Model # 103, Serial # 11302. "Source Information: Am-241, 150 mCi, QSA Global, Inc. Model # AMC.P6, Serial # 5244AR." NC Tracking Number: 170042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-10-26
53024 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2017-10-18 | 2017-10-18 14:16 | 2017-10-18 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was received via e-mail: "L3 Technologies reported a leaking foil sealed source to the Agency (Massachusetts Radiation Control Program). A wipe of the source was taken on Monday, 10/16/17 and results were received on Wednesday, 10/18/17. The leak test was measured at 0.0089 microCuries. "Source Information: Ni-63, 15 mCi, Model # 19233, Serial # L7947. "Device Information: Hewlett Packard Model # 5890, Serial # C-128/83. "The foil source is housed in a gas chromatograph unit that has not been used in many years. The unit is covered and locked away in a storage room. Personnel do not routinely access the unit. Leak tests have been performed every 6 months. There is no immediate risk of contamination at the facility. "The licensee expressed that they will appropriately dispose of the source and unit. "The licensee is required to submit a written report to the Agency [Massachusetts Radiation Control Program] within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2017-10-26
53023 | 0 | PALO VERDE NUCLEAR GENERATIING |  |  |  |  | 2017-10-11 | 2017-10-18 11:55 | 2017-10-18 | PART 21 NOTIFICATION - HPSI MOTOR LEAD INSULATION GOUGED "On October 11, 2017, Arizona Public Service Company (APS) completed an evaluation of a deviation and concluded the condition represented a defect under 10 CFR 21. "On August 25, 2017, a 1000 horsepower, High Pressure Safety Injection critical spare pump motor was discovered to have a gouge in the insulation in one of the three primary leads providing three-phase power to the motor. This deviation was identified by Palo Verde Electrical Maintenance staff during a pre-storage inspection. The gouge was inside the main terminal box, close to the (T2) terminal landing and was deep enough to expose the internal conductive wire. This motor was received on April 5, 2017, following refurbishment at the Westinghouse, Waltz Mill, Pennsylvania, facility. "APS concluded this condition could result in the motor failing to perform its safety function and thus could create a substantial safety hazard. The motor was shipped back to the Westinghouse, Waltz Mill facility on October 6, 2017 for repair. "The NRC resident inspector has been informed. "Vendor: WESTINGHOUSE INTERSTATE 70 MADISON EXIT 54, MADISON, PA 15663 "Device: WESTINGHOUSE MOTOR, 1000 HP; 3557 RPM FULL LOAD 3600 SYNC., 4000 VAC, 3 PHASE, 60 HZ - S/N 76F60563 (No model number)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-10-18
53022 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2017-10-18 02:09 | 2017-10-18 05:27 | 2017-11-14 | HPCI DECLARED INOPERABLE "Eight hour report due to HPCl [High Pressure Coolant Injection] inoperability. "HPCl valve operability testing was performed on October 18, 2017. Following satisfactory completion of opening stroke timing, the control switch for HPCI-MOV-MO19, HPCI Injection Valve, was taken to close. The valve indicates that it moved to an intermediate position, but it has not indicated that it has fully closed. This resulted in the valve being declared inoperable. This valve is normally closed and automatically opens on a HPCI initiation signal. "HPCl was previously declared inoperable at time 0136 [CDT] on October 18 for surveillance testing. Entry was made into Tech Spec LCO 3.5.1 Condition C - HPCI System Inoperable at that time. Required Actions for Condition C are to verify by administrative means RCIC System is operable within 1 hour and restore HPCI System to operable status within 14 days. RClC was verified operable by administrative means concurrent with declaration of HPCI inoperable. "Troubleshooting activities for HPCI are being planned. "HPCI is a single train safety system. This report is submitted as a condition that at time of discovery could prevent the fulfillment of the safety function of an SSC [structures, systems, and components] needed to mitigate the consequences of an accident. "This condition has been entered into the CNS Corrective Action Program." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 11/14/17 AT 0849 EST FROM DAVID VAN DER KAMP TO BETHANY CECERE * * * "CNS is retracting the 8-hour non-emergency notification made on October 18, 2017 at 0209 CDT (EN# 53022). Subsequent evaluation concluded HPCI-MOV-MO19 was still capable of performing its safety function with the failed torque switch identified during troubleshooting and would have supported the operability of the HPCI system. HPCI-MOV-MO19 only has a safety function to open to support HPCI safety function. The failed torque switch only affects the close function of the valve; therefore the HPCI system remained fully capable of performing its required safety function and was operable with the identified condition. "The NRC Resident Inspector has been notified." Notified R4DO (Haire). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-10-18
53021 | 0 | DEPARTMENT OF THE ARMY |  |  |  |  | 2017-10-17 | 2017-10-17 16:43 | 2017-10-17 | FOUR LOST TRITIUM EXIT SIGNS "During a periodic safety inspection of an installation facility, the Safety Manager noted that up to four tritium exit signs were missing from mounting locations above partition wall doorways. Photoluminescent equivalents had been installed in their place. The exit signs were manufactured by Safety Light Corporation with an effective life cycle of ten years set to expire on November 2017. Model numbers and activity levels of the missing signs are unknown. A local search for items returned negative results and the exit signs were determined lost on 16 October 2017. Interviews conducted with base operations personnel and contract employees indicate tritium exit signs were removed on or around 16 August 2017 and replaced with a non-radioactive equivalent. It is believed that the exit signs were disposed of in a municipal waste dumpster on the installation. An internal investigation is underway to gather additional information and determine root cause. "The U.S. Army Garrison - Carlisle Barracks reported the lost exits signs as a general license holder pursuant to 10 CFR 31.5. Telephonic reporting requirement in 10 CFR 20.2201(a)(1)(ii) applies. A formal written report will be submitted within 30 days after making the telephone report with the NRC that 10 CFR 20.2201(b) requires." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2017-10-25
53020 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-10-17 11:34 | 2017-10-17 13:22 | 2017-10-17 | OFFSITE NOTIFICATION DUE TO SANITARY LIFT STATION OVERFLOW "At approximately 0319 EDT on 10/14/17, site personnel discovered a sanitary lift station overflowing in the protected area. The overflow entered a nearby storm drain that discharges into Outfall 12. The estimated release volume was approximately 50 gallons. At 1134 EDT on 10/17/17 an initial notification was made to South Carolina Department of Health and Environmental Control. The cause of the overflow is still under investigation. Functionality of the lift pump has been restored and cleanup is complete. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-10-17
53019 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-10-16 14:25 | 2017-10-16 22:09 | 2017-10-16 | REACTOR COOLANT SYSTEM SHUTDOWN COMMUNICATION LINE VENT THROUGH WALL DEFECT "At 1425 CDT on 10/16/17, investigation into a boric acid indication was determined to be a through wall leak at the socket weld that joins the 3/4 inch line 2RC-92 to valve 2RC-8-37. Unit 2 is currently in Mode 5 with Reactor Coolant system (RCS) Operational Leakage limits not applicable. The leak is downstream of two first off RCS isolation valves that are normally closed. The leak is not quantifiable as it only consists of a small amount of dry boric acid at the location. This failure constitutes welding or material defects in the primary coolant system that cannot be found acceptable under ASME Section Xl. "Therefore, this is a degraded condition reportable under 10 CFR 50.72(b)(3)(ii)(A). "At the time of this notification, the Prairie Island Nuclear Generating Plant Unit 2 is in Mode 5 for a planned refueling outage. The identified defect will be repaired prior to entering Mode 4. "This condition does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-10-16
53018 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2017-10-16 08:51 | 2017-10-16 17:59 | 2017-10-16 | FITNESS FOR DUTY - NON LICENSED SUPERVISOR SUBVERTED TEST "A non-licensed supervisory contractor subverted a random Fitness for Duty (FFD) test. At 0851 [EDT] on October 16, 2017, a contractor supervisor was notified to report for a random FFD test and [the individual] did not report to the testing facility and left the premises. The contractor's site access has been terminated. The NRC Resident Inspector was notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2017-10-16
53017 | 0 | NEW YORK STATE DEPT. OF HEALTH |  |  |  |  | 2017-09-21 | 2017-10-16 11:08 | 2017-10-16 | AGREEMENT STATE REPORT - POST IMPLANT LOSS OF IODINE-125 SEED The following information was received from the State of New York via facsimile: "On September 21, 2017 the Department [New York State Department of Health] was notified that a Best Medical International, Inc., Model #2301 lodine-125 seed used for localization of non-palpable lesions and lymph nodes was lost. On September 18, a patient was implanted with a 125.2 microCurie lodine-125 seed. The seed was verified to be implanted by use of a survey meter. When the patient returned for explant three days later, the iodine-125 seed could not be detected. The licensee surveyed the patient's vehicle, house, laundry, and trash and no radioactivity was detected. The licensee reported placing the seed 'superficially' within the patient and the licensee speculates that the seed may have become dislodged from the patient at some point between the implant and explant." New York Report ID No.: NYDOH-NY-17-08 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2017-10-24
53016 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-10-15 17:00 | 2017-10-16 08:36 | 2017-10-16 | AGREEMENT STATE REPORT - STOLEN WELL LOGGING SOURCES The following information was received from the State of California: "The Licensee discovered at approximately [1700 PDT] on 10/15/17 that two 3 Ci Am-241Be well logging sources had been stolen from their storage area at Weller Ranch in Kern County. Locks had been cut and the sources were removed from the approximate 12-foot storage pipe. Additionally, an approximate 2500 [pound] calibration water tank was also missing. "The FBI was notified by CA Radiologic Health Branch [RHB] at approximately [2030 PDT] on 10/15/17. "RHB will be onsite 10/16/17." California 5010 Number: 101517 * * * UPDATE FROM ROBERT GREGER TO DONALD NORWOOD AT 1511 EDT ON 10/16/2017 * * * "The two well logging sources have been accounted for. An unauthorized individual had accessed the sources, removing them from their storage location on his father's ranch land and discarding them a short distance away without any knowledge of what they were. The unauthorized individual also took the water calibration tank for his personal use. "The well logging sources are back in the possession of the licensee." Notified R4DO (Vasquez) , NMSS Events Notification, CNSNS (MEXICO) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-10-24
53015 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2017-10-13 19:48 | 2017-10-14 16:37 | 2017-10-14 | FITNESS FOR DUTY - NON LICENSED SUPERVISOR FAILED RANDOM DRUG TEST "At approximately 19:48 Mountain Standard Time on October 13, 2017, Palo Verde Nuclear Generating Station (PVNGS) staff confirmed a non-licensed supervisor tested positive for drugs during a random 'Fitness for Duty' test. The person's access authorization was terminated in accordance with station procedures." The NRC resident inspector has been notified by the licensee. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2017-10-14
53014 | -1 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-10-13 17:00 | 2017-10-13 22:46 | 2018-06-08 | ACCIDENT MITIGATION - HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE "On October 13, 2017 at 1700 CDT, Unit 1 High Pressure Coolant Injection (HPCI) was declared Inoperable due to discovery of a leak on a sensing line to 1-PCV-073-0043, Lube Oil Cooler & Gland Seal Condenser Pressure Control Valve. The leak is a steady stream located where the sense line connects to the valve. "This constitutes an unplanned HPCI System inoperability and requires an 8 hour ENS notification in accordance with 10 CFR 50.72(b)(3)(v)(D), due to the failure of a single train system affecting accident mitigation and a 60 day written report in accordance with 10 CFR 50.73(a)(2)(v)(D)." The NRC Resident Inspector has been notified by the Licensee. * * * RETRACTION ON 6/8/18 AT 1500 EDT FROM BILL BALL TO BETHANY CECERE * * * "ENS Event Number 53014, made on 10/13/2017 is being retracted. "NRC notification 53014 was made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10 CFR 50.72 were met when a leak on a threaded union, along with piping vibration, was identified on U1 HPCls Lube Oil Cooler & Gland Seal Condenser Pressure Control Valve sensing line (1-PCV-073-0043). "A Past Operability Evaluation [POE] was performed under CR# 1347736. The evaluation concluded that HPCI was degraded, but met the threshold for TS operability. Specifically the vibrations shown were evaluated and deemed to not impact pipe integrity. These vibrations were also evaluated for seismic events. Based on this the POE concluded that HPCI was capable of performing its intended safety function for its designed mission time. "As such, the circumstances discussed in the report did not result in any condition that at the time of discovery could have prevented the fulfillment of the safety function of structures of system that are needed to remove residual heat. Thus, there was no impact on nuclear safety. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B). "TVA's evaluation of this event notification is documented in the corrective action program. "The licensee has notified the NRC Resident lnspector." Notified R2DO (Ernstes). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-10-13
53013 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2017-09-08 | 2017-10-13 | 2017-12-19 | AGREEMENT STATE REPORT - LOSS OR THEFT OF LICENSED NUCLEAR MATERIAL The following was reported from the State of Mississippi: Description of Incident: Licensee reported that their Niton gun was discovered to be misplaced or stolen on September 8, 2017. A letter was received by Mississippi State Department of Health: Division of Radiological Health (DRH) from the licensee on October 13, 2017 briefly detailing that their equipment had been lost or stolen. DRH intends to issue a violation letter to Southern Recycling due to the late notification. Also, due to lacking information, DRH cannot confirm if the device reported to have been stolen/lost contains radioactive material. DRH has attempted to contact the Licensee a number of times to acquire more information; however, there has been no response. DRH will continue contacting the licensee for more information and will update this report once complete. Isotope(s): Cd-109 (potentially lost source not confirmed), with an activity of 10 mCi. The DRH Health Physicist stated that this would give a reading of approximately 20 mRem at one foot if unshielded. Mississippi has assigned an incident number of MS17006. * * * UPDATE AT 1055 EDT ON 10/31/17 FROM H. BENJAMIN CULPEPPER TO S. SANDIN VIA EMAIL * * * "DRH was able to contact Licensee regarding the lost source. Licensee originally bought the device in 2007 to use at their facility. After a period of time, the device was more ineffective than effective, causing the Licensee to send the Niton gun for repairs. Licensee was informed that the source would have to be changed in order to alleviate the issue, but Licensee did not seek that avenue due to high costs. Even with the Niton gun being ineffective, Licensee maintained possession of the device until losing it three (3) years ago. "The Licensee's coworker recently reminded them that DRH should be informed about the missing source. "After contacting DRH about the missing source, DRH contacted a representative from Thermo Scientific to discuss the lifetime of the source. It was discovered that the source's assay date is 2/1/2006 and was shipped to the first owner on 12/6/2006. No other radioactive material was shipped to the Licensee in question from Thermo Scientific. "Knowing that the lost source is Cd-109, which has a half-life = 462.6 days, it was discovered that the 10 mCi source will have decayed (as of today) to an activity level of 0.01618 mCi. Also, if the source was one (1) foot away from the target, the target would receive a dose-rate = 33.86 microR/hr." DRH closed this case on 10/30/2017. Notified R4DO (Werner) and NMSS Events Notification via email. * * * UPDATE ON 12/19/2017 AT 0945 EST FROM H. BENJAMIN CULPEPPER TO ANDREW WAUGH * * * The following report was received via email: "The Source Serial Number for the Cd-109 source is U3134." Notified R4DO (Pick) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2017-10-23
53012 | 0 | IDAHO STATE UNIVERSITY |  |  |  |  | 2017-10-13 | 2017-10-13 15:46 | 2017-10-13 | LOST OR MISSING MATERIAL A series 50 nuclear accident dosimeter S/N AP237 with a 1 gram 62 mCi Pu-239 source was determined missing on 10/13/17. The dosimeter was one of 14 received by Idaho State University from the Department of Energy (DOE) in 1991. In 2003, this particular dosimeter was found to have detectable surface contamination and determined to have a compromised source. The device was removed from local inventory in 2003 pending transfer. Attempts were made to transfer the device to Idaho National Lab (INEL), but were declined. The device is believed to have been placed in the Idaho State University nuclear waste stream, and may have been transferred in 2006 or 2011 with other waste via Thomas Gray to US Ecology, but there are no supporting records. Investigation is ongoing. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-10-23
53011 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-10-12 11:05 | 2017-10-13 13:45 | 2017-10-13 | AGREEMENT STATE REPORT - DOSE DELIVERED LESS THAN PRESCRIBED The following information was received from the State of Ohio via email: "On 10/12/17 during an infusion of Y-90 SIRSpheres that began at 11:05 a.m. [EDT], the treatment device malfunctioned and ceased delivery of the radioisotope, resulting in an under-dosing of the patient's liver. No contamination of the facilities or personnel was detected. All activity that was not delivered into the patient was placed back into the acrylic box and secured in the nuclear medicine hot lab for decay. A SIRSpheres representative was present during the treatment, but the cause of the malfunction is not known at this time. Once sufficient decay of the radioisotope has occurred, the delivery device will be shipped to SIRSpheres for technical analysis and root cause determination." The patient was informed on the day of the event. Ohio Item Number: OH170006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-10-23
53010 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2017-10-12 09:30 | 2017-10-12 20:26 | 2017-10-12 | FITNESS FOR DUTY - POSITIVE FOR ILLEGAL DRUGS DURING INITIAL SCREENING A contract employee supervisor had a confirmed positive for illegal drugs during an initial screening test. The individual's access to the plant has been terminated. The NRC Resident Inspector has been notified by the Licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 26.719 |  |  |  | 0 | 2017-10-12
53009 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-08-11 | 2017-10-11 13:58 | 2018-04-26 | AGREEMENT STATE REPORT - MEDICAL UNDERDOSE The following report was received via e-mail: "On October 10, 2017, the Department [Wisconsin Department of Health Services] received a telephone call and email from the licensee's medical physicist that a medical event occurred on August 11, 2017, involving a permanent implant of I-125 seeds for a prostate manual brachytherapy procedure where the total dose delivered differs from the prescribed dose by 20 percent or more. This is a medical event as described in DHS 157.72(1)(a)1.a. The prescribed dose was 145 Gy; the dose delivered was 90 Gy. The licensee uses D90 (dose delivered to 90 percent of the clinical target volume) < 80 percent of prescribed, for determining medical events. Using the licensee's dose based criteria; the dose received by the prostate was 62 percent of the intended dose. The underdose was identified during the post-implant computerized tomography scan on September 11, 2017 and subsequent dosimetric analysis on October 10, 2017. "DHS [Wisconsin Department of Health Services] inspectors will investigate this medical event." Wisconsin Event Report: WI170016 * * * UPDATE ON 4/26/18 AT 1238 EDT FROM JOSEPH ROSS TO BETHANY CECERE * * * The following update was received from the Wisconsin Department of Health Services (DHS) by email: "During the ongoing investigations of other medical events reported to the Wisconsin Department of Health Services in 2017, licensee reviewed historic permanent implants of I-125 seeds for prostate manual brachytherapy. The licensee recently identified two additional implants that resulted in a D90 dose to the prostate that was greater than 130 percent of the prescribed dose. The licensee noted that there were no adverse outcomes to the patients. "The first implant occurred on August 28, 2015. The prescribed dose to 90 percent of the prostate (D90) was 145 Gy and the D90 delivered was 192 Gy. "The second implant occurred on June 17, 2016. The prescribed dose to 90 percent of the prostate (D90) was 145 Gy and the D90 delivered was 189 Gy. "DHS is reviewing the circumstances surrounding these two implants as part of the investigation into the previously reported medical events." Notified R3DO (Stone) and NMSS Events. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-10-19
53008 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-10-10 11:35 | 2017-10-11 11:16 | 2017-10-11 | ALARM SYSTEM BREACH The following report was received from the Texas Department of State Health Service via email: "On October 10, 2017, the Agency had an alarm system breach at 1135 CDT. Security called our program stating the alarm to the source room was alarming. I went down to the room to check it out. I checked the door and it was locked, turned off the alarm system by entering the code, and called the security company and provided information to stop law enforcement from responding to the location. The postal service technician was next door and I asked her who opened the door, she said the contractors asked her to open the door and she stated she went to building operations office and got the key and opened the door for the contractors. And she said when the alarm went off, the door was closed and security guard was informed. That is when our program received the call to go down there. An investigator from our program stayed with the contractors and set the alarm when they were finished. A complete investigation will be completed. Investigation ongoing. Update will be provided in accordance with SA300." Texas Incident#: I-9516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-10-19
53007 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-10-06 | 2017-10-10 10:35 | 2017-10-10 | AGREEMENT STATE REPORT - STUCK/BROKEN SHUTTERS ON TWO FIXED NUCLEAR GAUGES The following information was received from the Commonwealth of Pennsylvania via email/fax: "Event Description: The licensee reported that on October 6, 2017, while performing a lockout procedure for a major outage, the workers noted that two shutters were stuck in the open position. The shutters were both on Berthold Model LB7410 gauges and contained 300 milliCuries of americium-241 each. Both gauges are located in a pit area within major piping lines and a locked gate. This is an inaccessible area, thus no overexposures have occurred. Both units have been taken out of service and a service provider was contacted and has developed a plan to repair or replace the units if necessary. "Cause of the Event: Equipment failure. "ACTIONS: The Department [PA Bureau of Radiation Protection] will perform a reactive inspection. More information will be provided upon receipt. "Event Report ID No: PA170015" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-10-18
53006 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-10-08 14:17 | 2017-10-09 19:48 | 2017-10-09 | AGREEMENT STATE REPORT - STOLEN Cd-109 SOURCE The following report was received via e-mail: "California OES [Office of Emergency Services] notified RHB [Radiation Health Branch] Sacramento of the following hazardous material spill report on October 8, 2017: "On October 8, 2017, at 1417 [PDT], XRF equipment user, from Millennium Consulting Associates, notified Cal OES that the Niton XRF equipment, Model XLp303, S/N 21870, he uses was stolen from his vehicle that was parked in front of his residence in Alameda. CA. The theft was noticed by the licensee on Sunday October 08, 2017 about 1145. "The Niton XLp300 contains a licensed material Cd-109, 40 mCi as of 08/28/16. [The licensee] reported this incident to the Alameda Police on October 8, 2017at 14:45, the Case # is 17-5776." California Report Number: 5010-100817 A Niton XLp300 is used to analyze lead content. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-10-17
53005 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2017-10-09 14:05 | 2017-10-09 14:23 | 2017-10-09 | NOTIFICATION OF UNUSUAL EVENT - FLAMMABLE GAS IN THE TURBINE BUILDING While troubleshooting a hydrogen differential pressure gauge, operators found a hydrogen concentration greater than the lower explosive limit (4% hydrogen concentration). The licensee evacuated the turbine building. The licensee is ventilating the area to allow personnel access to isolate and repair the leak. The plant Fire Brigade is on standby. This event was declared for GU-2: release of toxic or flammable gas. The main generator pressure and hydrogen concentration are stable. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE AT 1630 EDT ON 10/9/2017 FROM NORMAN KUZEL TO MARK ABRAMOVITZ * * * The unusual event was terminated at 1617 EDT because the leak was isolated and the hydrogen concentration in the Hydrogen Control Cabinet was zero percent. The licensee notified the NRC Resident Inspector. Notified the R1DO (Jackson), IRD MOC (Stapleton), NRR (King), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Power Operation | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-10-09
53004 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-10-09 07:37 | 2017-10-09 09:15 | 2017-10-09 | UNUSUAL EVENT DECLARATION FOR TOXIC GAS SPILL At 0737 CDT on 10/9/17, Point Beach declared an Unusual Event with Emergency Action Level HU 3.1 due to report of toxic gas from a spill in a service building within the protected area. The spill is contained and cleanup operations are in progress. The spill was not in a contaminated area or vital area. The janitorial worker injured while mixing cleaning chemicals in a closet was taken to the hospital. The licensee notified the NRC Resident Inspector. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 10/9/17 AT 1111 EDT FROM DENNY SMITH TO BETHANY CECERE * * * "Point Beach has terminated the Unusual Event at 0944 [CDT] on 10/9/2017. The Unusual Event condition is no longer warranted. "The NRC Resident Inspector has been notified." Notified R3DO (Hills), NRR EO (King), IRD (Stapleton), DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-10-09
53003 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-10-06 19:45 | 2017-10-06 21:46 | 2017-10-06 | LOSS OF CONTROL ROOM HABITABILITY ENVELOPE "On October 6, 2017 at 1945 EDT, a loss of Control Room Habitability Envelope (CRE) was declared due to failing to meet the requirements of SR 3.7.3.4 during 72 month surveillance testing. Measured in-leakage exceeded the SR acceptance value. "The CRE is required to be maintained such that occupants can control the reactor safely under normal conditions and maintain it in a safe condition following a radiological event, hazardous chemical release, or a smoke challenge. The station remains in compliance with Technical Specification required action statements. "This event is being reported under 10 CFR 50.72(b)(3)(v)(D) and per the guidance of NUREG 1022, Rev. 3, Section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Control Room Habitability Envelope." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-10-06
53002 | 0 | PARAGON ENERGY SOLUTIONS |  |  |  |  | 2017-10-06 | 2017-10-06 15:29 | 2017-11-29 | PART 21 INTERIM REPORT - SWITCH WITH UNACCEPTABLE CHATTER The following information is excerpted from a report received via email: "Seismic qualification testing revealed contact block (CB) chatter greater than 2 milliseconds (msec) contrary to the acceptance requirements of the seismic test procedure developed for the activity. This switch has not been provided to the customer, however, a second suspect switch with a similar configuration and parts is installed in the customer's facility. "The condition is isolated to when OT2A CBs are configured in an alternating Normally Open (NO) / Normally Closed or Normally Closed (NC) / Normally Open (NO) arrangement. The CBs do not exhibit chatter when 3 or less CBs are configured this way. The chatter is not exhibited when configured in a NO/NC, NO/NC, configuration. When the fourth CB is added to the switch assembly in an alternating configuration is when the contact chatter exceeds greater than 2 msec. "Paragon Engineering has requested TVA Engineering to provide a reduced spectra specific to the installed location for further evaluation. Paragon Engineering has not been able to complete this activity within the 60-day period allowed under 10 CFR 21. "One suspect switch has been provided to and installed at the customer's facility. The customer's facility is TVA - Watts Bar Unit 2." * * * UPDATE ON 11/29/17 AT 1648 EST FROM RAY CHALIFOUX TO DAVID AIRD * * * The following is an excerpt from the final Part 21 report received via email: "Paragon ES [Energy Solutions] successfully completed qualification of a seismic specimen to the originally provided spectra using older vintage contact blocks. A reduced response spectra was requested from the licensee to verify that this condition did not present a substantial safety hazard for the existing installed switch. "The licensee alternatively completed an evaluation of the condition and determined a substantial safety hazard did not exist." Notified R2DO (Blamey) and Part 21 Reactors Group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-10-06
53001 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2017-10-05 | 2017-10-06 13:11 | 2017-10-06 | AGREEMENT STATE REPORT - LOST BRACHYTHERAPY SEED "On October 5, 2017, Johns Hopkins Outpatient Center, notified the Maryland Radiological Health Program (RHP) that on October 5, 2017, following a prostate seed implant procedure, the licensee discovered that one (1) seed was unaccounted for. The Pd-103 seed has an activity of approximately 1.5 milliCuries. The number of seeds implanted into the patient was 42 out of 47 seeds ordered. Four (4) seeds remained in the applicator. This left one (1) seed unaccounted for. Two physicists counted 42 seeds implanted, verified on two separate C-arm images. All personnel were scanned with a sodium iodide survey meter as they exited the room. All equipment, tables, waste bags, surgical covers, linens, etc. were scanned multiple times. The floor was systematically and methodically scanned, including the patient's Foley bag, with negative results. "The patient will return tomorrow [October 6, 2017] for a follow-up CT and chest x-ray. Radiation Oncology will re-count the seeds. Theragenics Corporation will also be contacted to determine if only 46 seeds were shipped. These seeds are received precalibrated and presterilized. "A reactive inspection will be conducted to investigate this event." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2017-10-16
53000 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2017-10-04 02:50 | 2017-10-04 05:53 | 2017-10-04 | PERRY COMMENCED TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On October 4, 2017, at 0250 hours [EDT], the Perry Nuclear Power Plant commenced a Technical Specification (TS) shutdown by lowering reactor power from 100 percent rated thermal power to 98 percent to comply with TS LCO 3.0.3. Reactor power was further reduced to 82 percent rated thermal power at 0430 hours [EDT]. "The plant had entered TS 3.0.3 at 0155 hours [EDT] upon loss of MCC [Motor Control Center], Switchgear, and Miscellaneous Electrical Equipment Areas HVAC System train A while train B was removed from service for maintenance. MCC switchgear ventilation train A was declared inoperable based on excessive belt noise and a dropped belt on MCC switchgear supply fan A. This also constitutes a loss of safety function. "This event is being reported in accordance with 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector was notified." * * * UPDATE ON 10/04/17 AT 0926 EDT FROM DAN HARTIGAN TO STEVEN VITTO * * * "Due to the loss of both trains of MCC, Switchgear, and Miscellaneous Electrical Equipment Areas HVAC, actions were taken in LCO 3.8.7 for AC and DC Distribution Systems, LCO 3.8.4 for DC Sources, LCO 3.8.1 for AC Sources, and the associated support systems, the High Pressure Core Spray system was also declared inoperable, which is a single train safety system and therefore, an additional loss of safety function. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(B), 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72 (b)(3)(v)(D). "At 0620 hours [EDT] the A train of MCC, Switchgear, and Miscellaneous Electrical Equipment Areas HVAC and High Pressure Core Spray was declared operable and LCO 3.0.3 was exited. The plant was restored to 100% [percent] power at 0804 [EDT]. "The NRC Resident Inspector was notified." Notified R3DO(Hills). | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION | POT RHR INOP | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2017-10-04
52999 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-10-03 08:00 | 2017-10-03 16:58 | 2017-10-03 | SECONDARY CONTAINMENT INOPERABLE DUE TO UNEXPECTED ISOLATION OF EXHAUST VALVE "On October 3, 2017, at 0800 PDT, Reactor Building (Secondary Containment) pressure momentarily rose above the Technical Specification (TS) limit. Secondary Containment was declared inoperable and TS Action Statement 3.6.4.1.A was entered. The pressure rise was due to unexpected isolation of an exhaust valve in the Reactor Building ventilation system during electrical switchgear inspections. The cause of the closure is still under investigation. "The Control Room operators reopened the Reactor Building exhaust valve and pressure returned to within limits automatically. Secondary Containment was declared operable at 0802 PDT and TS Action Statement 3.6.4.1.A was exited. "This condition is being reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and accident mitigation." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-10-03
52998 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2017-10-02 11:15 | 2017-10-03 15:52 | 2017-10-03 | INITIAL PART 21 NOTIFICATION - CAMERON MODEL 752B DIFFERENTIAL PRESSURE TRANSMITTERS "This report is made per 10 CFR Part 21.21(d)(3)(i) on the identification of a defect or a failure to comply. "By the letter dated August 31, 2017, Westinghouse notified Callaway Plant that they were unable to complete a 10 CFR 21.21(a) evaluation for a product advisory which was issued by Cameron Measurement Systems for a concern with the Model 752B transmitter product line. The product advisory identified the potential for instability in the transmitter output signal under certain grounding conditions. Callaway was supplied transmitters that could be affected under Westinghouse part numbers 8765D64G03, 8765D64G04, and 8765D64G05. The Westinghouse notification letter served as the transfer of reporting responsibilities for this concern from Westinghouse to Callaway in accordance with 10 CFR 21.21(b). "The 10 CFR Part 21 evaluation is based on the technical information provided by Westinghouse. The notification letter describes that shifts up to 10-20 percent of instrument scale (1.6-3.2mA) can be observed within the transmitter output under the grounding conditions such as those introduced by the original equipment manufacturer during testing. Westinghouse evaluations concluded that such instabilities would be self-revealing within plant applications for which the transmitter output signal was supplied to a Westinghouse 7300 system, assuming the transmitter stanchion was grounded. Not all transmitters within this product line were subject to this concern. "On 10/02/2017 Callaway personnel completed the 10 CFR Part 21 evaluation. Of the transmitters identified above, only one is currently installed at Callaway in location BNLT0930, Refueling Water Storage Tank Protection A Level Transmitter. No instabilities (oscillations) have been observed in this transmitter but plans are being made to replace the transmitter. "If one of the susceptible transmitters were installed for RCS flow application (low flow reactor trip function), the allowed sensor drift to accommodate changes in transmitter performance would be required to be limited to 1percent of instrument span per an 18-month operating period. Current margin available within the set point uncertainty analysis for this Reactor Trip function is 0.62 percent of instrument span. The observed shift in output of 10-20 percent of instrument span would thus exceed the available margin for this protective function. Therefore, the safety function for this device could not be assured for all transmitter configurations. This condition could create a substantial safety hazard due to the loss of safety function of a basic component which meets the criteria of major degradation of essential safety-related equipment. "For the situation at Callaway, no other reporting criteria apply since there is no evidence that the installed transmitter BNLT0930 is susceptible to the concerns noted in the product advisory. "The NRC Resident Inspector has been notified of this issue." | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2017-10-03
52997 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-10-02 | 2017-10-03 12:15 | 2017-10-03 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECTED WHILE WORKING IN THE FIELD The following report was received from the Texas Department of State Health Service via email: "On October 2, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that one of its radiography crews had experienced a source disconnect while working at a field site. The radiography crew was using a QSA 880D exposure device containing a 75 curie iridium-192 source. The radiographers had completed a shot and as they approached the exposure device their alarming rate meters alarmed. The radiographers retreated to the end of the crank out device and attempted to retract the source. The source could not be retracted. The radiographers contacted their radiation safety officer (RSO) who responded to the scene. The RSO was able to drive the source into the collimator and place shielding over the source. The RSO inspected the drive cable and found that the drive cable had pulled out of the drive cable connector to the source pigtail. The RSO connected a new crank out device to the source and was able to retract the source into the fully shielded position in the camera. The RSO stated he inspected the drive cable at the connection and it appeared the cable had been stretched. The RSO stated the connector had obvious crimp marks on it. The RSO stated the equipment would be returned to the manufacturer for inspection. No individual received an overexposure due to this event. No member of the general public received any exposure from this event. The Agency has requested additional information from the licensee. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #:I 9515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-10-11
52996 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2017-09-30 01:34 | 2017-09-30 09:06 | 2017-09-30 | SECONDARY CONTAINMENT DECLARED INOPERABLE "At 0134 [EDT] on September 30, 2017, Nine Mile Point Unit 2 entered Tech Spec 3.6.4.1 when secondary containment was declared inoperable due to secondary containment differential pressure being above the Tech Spec Surveillance Requirement of -0.25 inches vacuum water gauge. The Division II Standby Gas Treatment System was started to restore differential pressure at 0135 [EDT] on September 30, 2017 the differential pressure was restored, the secondary containment was declared operable and the Tech Spec3.6.4.1 exited. "Secondary containment being inoperable is a 8-hour report for 10 CFR 50.72(b)(3)(v)(C), Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. "The cause of this condition is being investigated. "The NRC Resident Inspector has been notified." The licensee will also inform the State of New York. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-09-30
52995 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-09-27 10:00 | 2017-09-27 14:26 | 2017-09-27 | ACCIDENT MITIGATION - LOSS OF SECONDARY CONTAINMENT "Security personnel reported to the Main Control Room that at time 1000 CDT [on 9/27/2017], an alarm indicated that a secondary containment door was open beyond the normal delay time allowed for entry and exit. Security personnel responded and found the door open and unattended with the dogs extended meaning that the door was unable to be closed. Security personnel secured the door at time 1004 CDT. No deficiencies were found with the door. The fact the door was open and unattended beyond the time allowed for normal entry and exit results in Technical Specification 3.6.4.1 'Secondary Containment-Operating,' not being met because surveillance requirement SR 3.6.4.1.3 is not met. This surveillance requires that doors be closed except during normal entry and exit. By definition in NUREG-1022, when Secondary Containment is inoperable, it is not capable of performing its specified safety function which in turn makes this condition reportable in accordance with 10 CFR 50.72(b)(3)(v)(D)." The NRC Resident Inspector has been notified. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-09-27
52994 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2017-09-27 09:07 | 2017-09-27 12:38 | 2017-09-27 | AGREEMENT STATE REPORT - STUCK WELL LOGGING TOOL The following information was received from the State of Oklahoma via email and a follow-up phone call: Oklahoma Department of Environmental Quality notified us that they were notified on September 27, 2017, at 0907 CDT, by Century Geophysical Corp. (OK-04017-05) that a well logging tool was stuck at approximately 14 feet in a cased borehole. The tool contains a 1 Ci Am/Be source. They will provide more details on the source as soon as they are available. The initial plan is to dig the tool out. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2017-10-05
52993 | 0 | KALISPELL REGIONAL MEDICAL CENTER |  |  |  |  | 2017-05-01 | 2017-09-26 15:39 | 2017-09-27 | MEDICAL EVENT WRITTEN DOSE DIRECTIVE IS DIFFERENT THAN PRESCRIBED DOSE An endocrinologist specified a therapy dose of 20 milliCuries of I-131. An authorized dose directive was incorrectly written for 30 milliCuries of I-131. The patient was administered the initially determined dose of 20 milliCuries of I-131. Medical personnel determined that there was no impact on the patient. Hospital supervision notified the on-site Authorized User, the Radiation Safety Officer and the Medical Physicist. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE AT 1345 EDT ON 9/27/17 FROM ANDRE VANTERPOOL TO RICHARD L. SMITH * * * The actual event date was May 1, 2017, and the discovery date was September 25, 2017, at approximately 1500 MDT. Notified R4DO (Proulx) and NMSS Events Notification (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | MT | OTH | AGR | 35.3045(a)(1) |  |  |  | 0 | 2017-10-04
52992 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-09-26 05:43 | 2017-09-26 11:03 | 2017-09-26 | AUTOMATIC START OF THE 2B EMERGENCY DIESEL DUE TO A VALID UNDERVOLTAGE SIGNAL "At approximately 0543 [EDT], while [recovering from the performance of] 2B Emergency Diesel Generator and ESFAS testing, a [subsequent] valid undervoltage actuation signal was sent to the 2B Emergency Diesel Generator (EDG). The 2B AC emergency bus (2BA03) was load shed, the 2B EDG automatically started, and tied to 2BA03. The 2BA03 bus was loaded by the automatic load sequencer. The actuation was identified by the Control Room operators and the 2B EDG was locally monitored while in service. "This actuation is reportable due to the automatic actuation of a system listed in 10 CFR 50.72(b)(3)(iv)(B). "The reactor was not critical at the time of the event and not challenged throughout the event. "Decay heat removal and spent fuel pool cooling were not challenged throughout the event. "The NRC Resident Inspector has been notified." The cause of the undervoltage condition is under investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-09-26
52991 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-09-24 | 2017-09-25 14:04 | 2017-09-25 | AGREEMENT STATE REPORT - STUCK / BROKEN SHUTTER The following information was received from the Commonwealth of Pennsylvania via email: "Notifications: On September 25, 2017, the licensee informed the Department [PA DEP Bureau of Radiation Protection] of a failure of an electronic component of a fixed gauge. It is reportable per 10 CFR 30.50(b)(2)(i). "Event Description: The electronic component of the automatic shutter on an IMS Model 5301-01 gauge containing approximately 20 curies of Cesium-137 failed to close on its own. The licensee immediately notified the RSO, as per their emergency procedure, who was able to remotely log in to the computer software system and bypass the automatic mode to close the shutter. The gauge is housed in a secure and entry restricted enclosure and instructions have been given to all operators to ensure that the shutter is closed while not in use. The manufacturer, IMS, was notified and is scheduled to make repairs on September 26, 2017. All regulatory precautions were taken and no overexposures have occurred. "Cause of the Event: Equipment failure. "ACTIONS: The Department will perform a reactive inspection. The manufacturer has already been scheduled to correct the problem. More information will be provided upon receipt." PA Event Report ID No.: PA170014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-10-03
52990 | 0 | PA BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-08-25 | 2017-09-25 08:23 | 2017-09-25 | AGREEMENT STATE REPORT - STUCK / BROKEN SHUTTER The following information was received via email: "On September 22, 2017, the licensee informed the Department [PA DEP Bureau of Radiation Protection] of a failure of a collimator block. This event is reportable per 10 CFR 30.50(b)(2). "On August 25, 2017, the licensee identified a failure of the collimator block attached to the shutter assembly on one of its Thermo Measure Tech Model 5204 gauges containing 4 curies of Cesium-137. The gauge was immediately removed from service. A licensed service provider was contacted and the broken shutter mechanism was removed and replaced with a spare. The shutter mechanism was then tested and confirmed as operating properly. Survey results indicated no abnormal amounts of radiation in the area before or after the repair work. All regulatory precautions were taken and no overexposures occurred. "The cause of the event was equipment failure. The Department will perform a reactive inspection. A service provider has already corrected the problem. More information will be provided upon receipt." PA Event Report ID No.: PA170013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | AGR |  |  |  |  | 0 | 2017-10-03
52989 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2017-09-22 15:00 | 2017-09-22 20:08 | 2017-09-22 | SEISMIC MONITORING COMPUTER OUT-OF-SERVICE "The following event description is based on information currently available. If through subsequent reviews of this event additional information is identified that is pertinent to this event or alters the information being provided at this time a follow-up notification will be made via the ENS or under the reporting requirements of 10 CFR 50.73. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(xiii) for a major loss of emergency assessment capability at the Palo Verde Nuclear Generating Station (PVNGS). On September 21, 2017 at 0915 MST, the seismic monitoring (SM) computer was declared non-functional for the performance of a planned surveillance test. On September 21, 2017 at 1201 MST, the SM system computer became non-responsive during the performance of the test. Control room staff attempted to reboot the computer and were unsuccessful. Maintenance and troubleshooting efforts began thereafter to initiate repairs. As a compensatory measure, PVNGS procedures for seismic event evaluation provide alternative methods for event classification of a seismic event with the SM system out of service. "The SM system functions to provide indication that the Operational Basis Earthquake (OBE) threshold has been exceeded following a seismic event and is used in the PVNGS Emergency Plan to perform classification of Initiating Condition 'Seismic event greater than OBE levels' and Emergency Action Level HU2.1. "On September 22, 2017 at 1500 MST, maintenance personnel performing software repair efforts determined hardware replacement is required. The required component will not be available before 72 hours from the start of the event. Because the SM system is not expected to be restored within 72 hours, this condition is being reported as a planned event constituting a major loss of emergency assessment capability with viable compensatory measures in place. "The NRC Resident Inspector has been informed of this condition." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-09-22
52988 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-09-22 | 2017-09-22 18:18 | 2017-10-10 | AGREEMENT STATE REPORT - SECURITY CAMERAS HACKED AT RADIOGRAPHY LICENSEE The following report was received from the Texas Department of State Health Services via email: "On September 22, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that an unusual event had occurred at their facility. The RSO stated that while he was working on his computer, he noted that the display for 16 security cameras went blank. He stated that the cameras were offline for 50 minutes. The RSO stated they contacted their information technology (IT) company providing their computer system services and that service investigated the problem. The RSO stated as soon as the problem occurred they 'locked down' the system. He did not provide any information on what 'locked down' meant. The RSO stated he was told by the IT service that their computer system had been hacked from the outside. The RSO stated the IT company stated the breach was restricted to the server controlling the cameras. Any of the licensee's security related or sensitive information was stored on a separate server and it was not accessed during the breach. The RSO stated that the security system for the radioactive material was not affected. The RSO stated he would provide copies of all reports from the IT service company related to this event. The Federal Bureau of Investigation will be notified of this event. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9512 * * * UPDATE AT 1002 EDT ON 10/10/17 from IRENE CASARES TO S. SANDIN VIA EMAIL * * * "On September 22, 2017, we received notification that a video system had been hacked at the facility. The person reporting the information was [the CEO/RSO] and he stated he had called his computer technician at his contracted company to check into the matter. He provided information from the technician stating that the surveillance system was hacked at the main contractor's company and the video at the radiography company was effected through an open port or plug into the video stream communication line. The video surveillance system monitoring screen(s) went black but displayed the words 'HACKED.' The technician stated that the video system was the only unit effected. He also stated that more than one of his clients had the same thing happen at other facilities he services. The breach did not come through the main computer server nor did it effect any of the vault system communication lines at the radiography company. "[The Texas Department of State Health Services] went to the facility on October 4, 2017 to view the system set up and ask questions about the connections to the video and computer systems. The security system inspection was started by meeting with the Operations Manager and CEO / Radiation Safety Officer in the front office. The situation was discussed and explained in detail. Afterwards [the Texas Department of State Health Services] went to the vault area and viewed the system along with the video surveillance cameras around the building. [The Texas Department of State Health Services] spoke with the computer technician over the phone asking various questions regarding the systems setup and communication lines. [The Texas Department of State Health Services] ended the tour in the computer and communications room while speaking with the Operations Manager and CEO/RSO. "There are small backup batteries and a main generator to supply power to the building, communication lines, and video surveillance system when a disruption in electric service occurs. The system for the vault has its own communication line separate from the video surveillance lines in the building. The security plan for the facility was established by a consultant who supplied the document to the RSO through hand delivery of the document. The security plan is not on any computer system at the facility. It is locked in a secure cabinet and only one person knows its location and has the key to the cabinet on his person at all times. "The system was reviewed and appears to not be the point of interest for the hack. The breach was to the main video surveillance company and not directly the target for the radiography sources. The company supplying the video surveillance has made corrections to the system and passwords were changed. In addition, more security such as upgraded firewalls and a message alerting system was added to the facility management's mobile phones. This should delay and or eliminate future breach of the video and security system and provide immediate alerts to the company for all the system components. No pictures or drawings were made during this inspection to ensure the system remains secure and not available through open records from our Agency." Notified the R4DO (Hipschman), HQCAT (e-mail), R4CAT (e-mail), and NMSS Resources (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 1 | 2017-10-02
52987 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2017-09-22 | 2017-09-22 14:05 | 2017-09-22 | AGREEMENT STATE REPORT - IRRADIATOR ACCESS CONTROLS INOPERABLE The following information was received via email: "An irradiator operator was leaving the panoramic irradiator vault and was following procedures to close the vault door. Audio and Visual alarms functioned properly and the vault door was sliding shut when the door stopped. The operator took immediate actions and was able to close and lock the door. All security systems were checked, found to be working and engaged. He tagged the Irradiator 'out-of-service' until an investigation can be conducted and corrective actions are implemented. "The source rack remained in the shielded position during this event. There was no threat to public health, safety or homeland security. UMCP [University of Maryland College Park] will provide RHP [Radiation Health Program] with a written report. A RHP Inspector will conduct an investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2017-10-02
52986 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-09-14 | 2017-09-22 11:36 | 2017-09-22 | AGREEMENT STATE REPORT - STUCK CLOSED SHUTTER The following information was received via E-mail: "On September 18, 2017, the Agency [Texas Department of State Health Services] received a reciprocity request from a nuclear gauge manufacturer to perform repairs on a Ronan Engineering model SA1-F37 gauge at the licensee's facility. The gauge contains a 500 millicurie (original activity) source. On September 22, 2017, the Agency contacted the licensee and asked if the gauge shutter was functioning properly. The individual stated the shutter on the gauge would not fully close. The individual was instructed to contact the licensee's radiation safety officer (RSO) and instruct the RSO to contact this Agency. The RSO contacted the Agency and stated the problem was discovered when testing the gauge on September 14, 2017. The RSO stated the gauge shutter was not open, but stuck in the closed position. The RSO stated it appears the pin that connects the shutter operating arm to the operating rod is no longer in place and the shutter cannot be moved. The RSO stated the gauge is located in an area where the access is controlled and does not pose an exposure risk to their workers or members of the general public. The manufacturer is scheduled to be on the site September 26, 2017, to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-10-02
52985 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2017-09-21 16:04 | 2017-09-22 11:00 | 2017-09-22 | AGREEMENT STATE REPORT - INADVERTENT DISPOSAL OF AN ELECTRON CAPTURE DETECTOR GAS CHROMATOGRAPH The State of Kansas was notified that an Electron Capture Detector Gas Chromatograph (ECD-GC) owned by Occidental Chemical Corporation (OxyChem) was inadvertently disposed of as electronic waste. The contracted waste company, Clean Harbors Wichita, ships waste to the recycler, ERI, in Fresno, CA. OxyChem provided ERI pictures of the missing Varian ECD GC to aid in identification. The missing ECD-GC is a model 3400 (Serial Number A-8080), containing 8 mCi Ni-63 as of 1990. The current activity is calculated as 6.58 mCi. The State of Kansas is providing a courtesy notification to the State of California Radiation Program Office. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2017-10-02
52984 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2017-09-21 17:30 | 2017-09-21 21:07 | 2017-09-21 | CONTROL ROOM EMERGENCY VENTILATION AC SYSTEM INOPERABLE "On September 21, 2017 at 1730 [CDT] the Control Room Emergency Ventilation Air Condition (CREV AC) system was declared inoperable due a refrigerant leak from the air conditioning compressor. As a result, Technical Specification 3.7.5 Condition A was entered for Units One and Two. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10CFR50.72(b)(3)(v)(D) because the CREV system is a single train system. The loss of CREV AC could impact the plant's ability to mitigate the consequences of an accident." The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-09-21
52983 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-09-21 08:59 | 2017-09-21 12:13 | 2017-09-21 | AGREEMENT STATE REPORT - DAMAGED GAUGE AT CONSTRUCTION SITE The following report was received from the South Carolina Department of Health and Environmental Control via email: "The licensee notified the Department [South Carolina Department of Health and Environmental Control] that a piece of heavy equipment backed over a Instrotek Model 3500 moisture density gauge serial number 2323. The gauge contained 10 mCi of Cs-137 and 40 Ci of Am-241:Be. The gauge operator had contacted his RSO [Radiation Safety Officer] at the time of the incident. The BRH [Bureau of Radiation Health] inspector arrived on scene. The gauge was surveyed and tested for removable contamination. The highest reading found was on the bottom of the gauge at the shutter. The shutter was in the closed position. The reading was 15 mR/hr which is consistent with the radiation profile identified in SSD NC-1241-D-101-S. There was no removable contamination found." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-09-29
52982 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2017-09-15 | 2017-09-20 16:03 | 2017-09-20 | AGREEMENT STATE REPORT - DAMAGED PORTABLE GAUGE The following information was received via e-mail from the state of Ohio: "On 9/15/17 at approximately 11:15 AM, the Ohio Department of Health (ODH) was notified by GPD Geotechnical Service, LLC. that a portable gauging device (CPN Model MC-1-DRP which contained a 10 mCi Cesium-137 source and 50 mCi Americium-241:Be source) had been run over and that the device had sustained heavy damage to the casing and the source handle was broken off. The gauging device was run over by a piece of construction equipment at their jobsite located at 225 Elyria Street, Lodi, OH 44254. "An ODH inspector, responded to the location of the incident and was met by the licensee's RSO. The inspector was lead to the gauging device which had been surveyed and had been determined to have no abnormal radiation readings and that both radioactive sources were intact and properly secured with in the device. The device was secured in its transportation case and placed in the field technician's vehicle. The inspector also conducted a wipe test with no abnormal readings observed. "In an interview with the field technician the inspector determined that the technician was approximately 10 to 15 feet away from the device but did not have direct line of site to the device as it was partially obstructed due to the construction equipment. It was also observed by the inspector that the equipment operator's view of the gauging device was obstructed due to the configuration of the equipment and the proximity in which the device was placed on the ground in front of the equipment. "Licensee's leak test showed no removable contamination and the device has been sent to a service provider for repair." Item Number: OH170005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2017-09-28
52981 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-09-20 | 2017-09-20 16:39 | 2017-09-20 | AGREEMENT STATE REPORT - POTENTIAL TEDE EXPOSURE IN EXCESS OF 25 REM Louisiana Department of Environmental Quality called to report a potential overexposure. Welding Testing X-Ray, Inc., contacted Louisiana Department of Environmental Quality to report an irregular excessive whole body badge exposure for a radiographer. The badge was for August 2017 reporting period of August 1 through 31, 2017. The whole body badge exposure reflected 754 rem. This individual worked as part of a two man crew at various jobsites. All of the other crew members readings were within the expected range for typical trained radiographers. The individual was advised to contact REAC/TS [Radiological Emergency Assistance Center / Training Site] in Oak Ridge, TN for blood testing and cytogenetic testing. The individual did not exhibit any skin irritations or other signs of radiation sickness. The licensee is investigating the exposure. Louisiana State advised the licensee to remove the individual from radiation work until the issue is resolved. Event Report ID No.: LA-2017-0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-09-28
52980 | 0 | KANSAS STATE UNIVERSITY |  |  |  | 250 KW TRIGA MARK II | 2017-09-19 14:49 | 2017-09-20 13:13 | 2017-09-20 | REACTOR BAY VENTILATION INOPERABLE The following was received via email: "The exhaust plenum monitor (EPM) was sent out for calibration a couple of weeks ago. It was received back on September 17, 2017, and returned to service. [On 9/20/17,] one of the senior reactor operators noticed that the noble gas detector was not responding properly. It was turned off. A relay on the EPM controls reactor bay ventilation, which is required to be operable per Technical Specifications. If the EPM alarms, ventilation is turned off. This relay was rewired to use only the two operating EPM detectors. Despite this, the reactor bay ventilation was observed to not operate as expected. The problem was traced back to a separate faulty relay, which was subsequently bypassed. The senior reactor operator had access to a control room breaker, and planned to manually cut power to the ventilation system if the EPM or continuous air monitor alarmed. An experiment was installed that has the potential to release radioactive gases; the reactor was started up at 1449 CDT and shut down at 1743 CDT. No increases in radiation levels were observed during or after operations. The ventilation system was operating during reactor operations. "As previously mentioned, reactor bay ventilation is required to be operable per Technical Specifications. Operable is defined as being capable of performing it's intended function in a normal manner. Manually cutting power to the ventilation system via control room breaker is not considered normal operation for the ventilation system. According to Technical Specifications, the reactor may be operated with the ventilation system inoperable, but reactor experiment operations with the potential to release radioactive gases or aerosols must be secured. While the apparatus was secured according to the definition in Section 1 of the Technical Specifications, the experiment was still performed, and so experiment operations were not secured in accordance with the Limiting Condition of Operation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | KS | NPR | [5 empty] | 0 | 2017-09-20
52979 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-08-24 | 2017-09-19 10:38 | 2017-09-20 | AGREEMENT STATE REPORT - DOSE DELIVERED 20% GREATER THAN PRESCRIBED AND GREATER THAN 50 REM TO THE TARGETED AREA The following information was received from the State of Georgia via email: "Emory University had new software installed for their HDR on 2/2/2016. During the time span of 3/2016 through 6/2017 [five] 5 patients received doses that were greater than 20% [percent] and greater than 50 rem to the targeted area. The misadministration was due to a software defect with Elekta's Oncentra Brachy Software version 4.5.2. using the ring applicator. The licensee was only aware of the defect on Aug 22, 2017 when Elekta notified all of their customers of the defect. Emory unofficially notified the State of Georgia on Aug 24, 2017 of a possibility that several of their patients may have been involved in a medical event. The medical event was confirmed on Sept 19, 2017 that [five] 5 patients were involved in a medical event. "Cause and Corrective Actions: The events were due to a software issue utilizing the Oncentra Brachy Software version 4.5.2. A misadministration occurred due to an inconsistent step size when treating the ring source path. A source step size of 2.5 mm was planned. What was reported in the case explorer was a 5 mm step size. "Device/Associated Equipment: Oncentra Brachy Software version 4.5.2. in a Elekta Nucleotron MicroSelection v3 HDR using a ring applicator." The targeted area that received the greater than 50 rem was the tissue of the upper vaginal wall. The defect in the equipment is identified and described in EN #52922. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2017-09-28
52978 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-09-19 | 2017-09-19 16:54 | 2017-09-20 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The following information was received from the State of Florida via email: "[The State of Florida Bureau of Radiation Control] received a call from [the licensee] RSO to report a stolen Troxler gauge. An employee from GFA International had the gauge stolen from the back of his truck while at a convenience store. Awaiting the police report for more information." The stolen gauge is a Troxler Moisture Density Model 3430, S/N 29415, containing two sources; 8 mCi Cs-137 and 40 mCi Am241/Be. * * * UPDATE ON 9/20/17 AT 1215 EDT FROM TIM DUNN TO DONG PARK * * * The following information was received from the State of Florida via email: "[The State of Florida Bureau of Radiation Control] received a call from [the licensee RSO] to report that the gauge has been found. A contractor onsite found the gauge on 9/19 and secured it until [the licensee RSO] could be located and took possession of the gauge on 9/20. The case has a small crack, but all radiation readings are normal." Incident Number: FL17-256 Notified R1DO (Kennedy) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-09-20
52977 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2017-09-19 | 2017-09-19 13:16 | 2017-09-26 | AGREEMENT STATE REPORT - WELL LOGGING SOURCES STUCK DOWN HOLE The following information was received via fax: "On September 19, 2017, the [Alabama Department of Public Health] received a phone call from Schlumberger, stating that they had failed to notify the Agency [Alabama Department of Public Health] upon entering the State, to perform a job on September 13, 2017, and that two sources (Cf-252 - 18.3 mCi and Cs-137 - 1.78 Ci) are stuck down hole. "Schlumberger stated that the first fishing attempt had failed to recover the sources, and the second attempt is now underway. Gathering information is continuing." Alabama Incident: #17-26 * * * UPDATE FROM MYRON RILEY TO VINCE KLCO AT 1148 EDT ON 9/26/2017 Via Fax * * * "On September 24, 2017, after several days of fishing for the logging tools, all recovery attempts had been unsuccessful and the sources were cemented in place down hole. "The licensee will follow up with a written report and a picture of the plaque to be placed on the well head." Notified R1DO (Bower) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 0 |  | OTH | AGR |  |  |  |  | 0 | 2017-09-27
52976 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2017-09-18 17:24 | 2017-09-19 00:01 | 2017-09-19 | CONTROL ROOM ENVELOPE NOT MAINTAINED "At 1724 [CDT] on 9/18/17 during Control Room Ventilation testing Door-61, South Control Room Door, became wedged against its door stop and stuck open. Door-61 is a credited High Energy Line Break (HELB) / Fire / Flood Barrier in addition to its function to maintain the Control Room envelope. The door stop was subsequently unbolted from the floor and the door was free to close. Door-61, South Control Room Door, has since been inspected, and at 1750 [CDT], was declared functional as a HELB / Fire / Flood Barrier and Operational for purposes of maintaining the Control Room Envelope. During the 26 minutes the door was stuck open, the Control Room was in an unanalyzed condition with regards to protection from a High Energy Line Break." The licensee notified the NRC Resident Inspector. | 98 | 100 | 0 | 98 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  | 0 | 2017-09-19
52975 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-09-17 | 2017-09-18 20:08 | 2017-09-18 | AGREEMENT STATE REPORT - FOUND TROXLER GAUGE The following is a report emailed from the California Department of Public Health, Radiologic Health Branch (RHB): "On 09/18/17, RHB received a call from an employee at an unlicensed facility (Clorox Company) in Fairfield, CA, regarding recovery of a lost/stolen moisture density gauge. The gauge is a Troxler Model 3450, S/N 1083 gauge containing approximately 9 mCi of Cs-137 and 44 mCi of Am-241. On Sunday afternoon (09/17/17) one of the Clorox employees noticed a locked container left on the side of the street in front of their facility. On Monday (9/18/17) morning, the locked container was noticed to have been moved farther from the road and closer to their facility. Clorox called Troxler and Fairfield Police, but neither could pick up the container. The Clorox employee then contacted RHB, and received instruction on how to safely store the container until RHB arrives at the facility. RHB picked up the gauge the same day and brought it back to the storage facility at the Richmond Regional office. A survey performed by RHB at the Clorox facility using a Thermo Scientific Rad Eye B20, S/N 30744, calibrated 03/09/17, indicated 0.4 mR/hr at one meter, which is a typical reading for a moisture density gauge in its transportation container. The type A transportation container appeared to be in good condition and was locked with two padlocks. RHB had the padlocks cut, and located a copy of a license indicating the gauge belongs to RMA Group in Rancho Cordova, CA (License # 7565-34). RHB has not received any notification from the licensee regarding a lost or stolen gauge. RHB will be contacting the licensee to follow up on this incident." California 5010 Number: 091817 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-09-26
52974 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-09-17 09:38 | 2017-09-17 16:49 | 2017-09-17 | EMERGENCY DIESEL GENERATOR AND PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATIONS "On September 17, 2017, during planned surveillance activities involving Emergency Diesel Generator (EDG) 4, unexpected voltage and frequency indications were noted when EDG 4 was synchronized to Emergency Bus E4. With EDG 4 in manual mode, the Operator responded by lowering load to reopen the EDG 4 output breaker. Opening of the EDG 4 output breaker with the breakers from Balance of Plant (BOP) Bus 2C, which normally feeds the Emergency Bus E4, opened; resulted in de-energizing Emergency Bus E4. The EDG 4 voltage regulator and governor automatically reverted to auto control, and EDG 4 reconnected to Emergency Bus E4. Normal frequency and voltage were restored with EDG 4 in auto control. "The momentary power interruption to Emergency Bus E4 resulted in Unit 2 Primary Containment Isolation System (PCIS) Group 2 (i.e., Drywell Equipment and Floor Drain, Residual Heat Removal (RHR) Discharge to Radwaste, and RHR Process Sample), Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems), and Group 10 (i.e., air isolation to the drywell) isolations. The actuations of Primary Containment Isolation Valves (PCIVS) were completed and the affected equipment responded as designed. Per design, no Unit 1 safety system group isolations or actuations occurred. "These actuations are being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). "Additional Unit 2 actuations included PCIS Group 3 (i.e., Reactor Water Cleanup), Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation), and the automatic start of Standby Gas Treatment (SGT) System subsystems A and B. These systems functioned as designed. "This event did not impact public health and safety. The NRC Resident Inspector has been notified. "The safety significance of this event is minimal. Safety systems functioned as designed following the power perturbation on E4. Plant systems responded as designed. The cause of the event is under investigation." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-09-17
52973 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-09-16 13:30 | 2017-09-16 15:53 | 2017-09-16 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "On September 16th, 2017 at 1330 hrs. [EDT], a loss of secondary containment differential pressure (D/P) occurred due to an equipment failure. This caused a reduction in Reactor Building Zone 2 (Unit 2) D/P to less than the required 0.25 inches WC per SR [Surveillance Requirement] 3.6.4.1.1. "2V206B, Reactor Building Zone 2 Equipment Compartment Exhaust Fan, was manually started and Reactor Building Zone 2 D/P was restored to greater than 0.25 inches WC by 1333 hrs. "Reactor Building Zone 1 (Unit 1) and Zone 3 (Units 1&2) ventilation remained in service and stable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev. 3, section 3.2.7, as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-09-16
52972 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-09-15 | 2017-09-15 18:02 | 2017-09-15 | TEXAS AGREEMENT STATE REPORT - LOSS OF CONTROL OF RADIOACTIVE MATERIAL The following information was obtained from the state of Texas via email: "On September 15, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that an event involving two radiography crews had occurred. The RSO stated two crews had completed work at field sites near Midland, Texas, and contacted the licensee and stated they were terminating their employment with the licensee and going to work for a new company. The radiographers were instructed to take the trucks and sources to the licensee's location in Midland, Texas, and turn in their equipment. "When the radiographers failed to show up at the Midland office in what the RSO thought was a reasonable period of time, he contacted local law enforcement and reported the trucks and cameras as missing. Law enforcement pulled both trucks over about an hour out of Midland, Texas, and placed the radiographers in custody. The RSO stated law enforcement stayed with the trucks and exposure devices until members of the licensee's workforce could get to the location. The trucks and sources were returned to the Midland office. The RSO did not know the activities of the sources, but stated they were quantities of concern. The RSO stated he did not think the radiographers intended to steal the sources, but were going to return to Houston, Texas, using the licensee's vehicles. "The RSO agreed to provide additional information on September 16, 2017." Texas Incident # I-9510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-09-25
52971 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-09-08 13:53 | 2017-09-15 15:17 | 2017-09-15 | AGREEMENT STATE REPORT - ORPHAN SOURCE DISCOVERY The following information was received by the State of Illinois by email: "IEMA [Illinois Emergency Management Agency] was notified at [1353 CDT] on 9/8/17 that a load of ferrous metal was being rejected from a scrap metal recycling facility (Omnisource in Indiana) back to Gaby Iron in Chicago Heights. The max exposure rate was reported at 20 microR/hour (4 microR/hour background). The load is being returned under DOT SP IN-IL-17-010. "The suspect load was inspected Monday, September 11th. An Alnor dew pointer device with an intact 7 microCurie Ra-226 source was recovered. No removable contamination was identified. The device was impounded by IEMA and is pending return to an appropriate entity. No additional radiation sources were discovered and the remainder of the load was released without further restriction. Pending appropriate disposal or return to the manufacturer, this matter is being considered closed." The device was an Alnor Instrument portable gauge; Model 7350; Serial Number 230667. The Amersham sealed source was a model RAM.X452; Ra-226; 7 microCurie activity. NMED Report: IL177030 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-09-25
52970 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2017-09-14 16:00 | 2017-09-15 08:15 | 2017-09-15 | AGREEMENT STATE REPORT - TWO LOST TRITIUM EXIT SIGNS The following report was received by email: "On September 14, 2017, the licensee discovered that two exit signs containing H-3 were missing. The licensee searched their facility and asked individuals about the location of the exit signs, but were unsuccessful in finding them. The licensee then notified the DWMRC [Department of Waste Management and Radiation Control] of the missing signs. The licensee will continue to investigate the incident and will submit a written report to the DWMRC. "Manufacturer: Forever Light Model: unknown Serial #: 281280 and 281278 Acquired by the licensee in 2005 (activity 11.21 Ci) "Utah Event Report ID No: UT170006" THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2017-09-25
52969 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-09-13 14:00 | 2017-09-14 16:38 | 2017-09-14 | AGREEMENT STATE REPORT - DAMAGED TROXLER GAUGE The following information was received from the State of California via email: "On September 14, 2017, [The RSO] of Southwest Calibration & Training notified the RHB Brea office that United Inspection & Testing, Inc., RML # 4788-33, had a Troxler, 3411B, serial #6644 radioactive gauge run over and damaged. On September 14, 2017, RHB Brea contacted [The RSO] of United Inspection & Testing, Inc. [The RSO of United Inspection & Testing, Inc.] informed our office that the radioactive gauge had been run over by a backhoe on the afternoon of September 13, 2017 at approximately 1400 [PDT], at the intersection of Banana Street and Daurin Street at a construction site in Fontana, CA. As a result of the accident the radioactive gauge had the handle broken off. The RSO was able to return the Cs-137 source to its shielded position, but it could not be locked in the shielded position due to the damage to the gauge. The authorized user of the gauge was also struck by the backhoe and died of his injuries. [The RSO of the United Inspection & Testing, Inc.] retrieved the gauge from the accident site and transported it to Southwest Calibration & Training to be inspected. [The RSO] of Southwest Calibration & Training reported that the Troxler radioactive gauge read 0.9 mR/hr at 1 foot. The gauge was extensively damaged and may not be repairable." California 5010 Number: 091417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-09-22
52968 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2017-09-13 15:30 | 2017-09-14 09:10 | 2017-09-14 | CONTRACTOR MANAGER CONFIRMED POSITIVE FOR ALCOHOL On September 13, 2017, Southern Nuclear Operating Company (SNC) determined a Contractor Manager confirmed positive for alcohol during a for cause fitness-for-duty test. The employee's unescorted access to the plant has been terminated. The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2017-09-14
52967 | -1 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-09-13 00:47 | 2017-09-13 01:08 | 2017-09-15 | UNUSUAL EVENT DUE TO LETDOWN RELIEF VALVE DISCHARGE TO THE PRESSURIZER RELIEF TANK At 0047 EDT, the licensee declared a notification of unusual event under emergency action level (EAL) S8 due to actuation of the letdown relief valve which resulted in reactor coolant system leakage to the pressurizer relief tank exceeding 10 gpm. The plant was in mode 3 at the time making preparations to proceed to cold shutdown to support their refueling outage. Operators were in the process of reducing reactor coolant system letdown from 120 gpm to 45 gpm when the letdown system relief valve lifted. The relief discharged to the pressurizer relief tank at approximately 12 gpm. Operators isolated the letdown line which reduced the leakage to approximately 1 gpm. Plant staff is in the process of determining where the 1 gpm leakage is from and evaluating the basis for terminating the unusual event. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). * * * UPDATE FROM BUD HINCKLEY TO HOWIE CROUCH AT 0807 EDT ON 9/13/17 * * * At 0800 EDT, the licensee terminated the notification of unusual event. The basis for termination was that the letdown line was isolated which reduced leakage to less than the EAL threshold of 10 gpm. The cause of the letdown relief lifting is still under investigation. The licensee has notified the NRC Resident Inspector and will be notifying the state of Michigan and Berrien County. The licensee has issued a press release to the media concerning this event. Notified R3DO (Riemer), IRD MOC (Stapleton), NRR (Miller), DHS SWO, DHS NICC, FEMA Ops Center, FEMA National Watch Center (email) and Nuclear SSA (email). * * * RETRACTION FROM BUD HINCKLEY TO HOWIE CROUCH AT 1617 EDT ON 9/15/17 * * * "The condition reported in Event Notification #52967 pursuant to 10 CFR 50.72(a)(1)(i) has been evaluated, and determined not to have met the threshold for classification as an Unusual Event under Emergency Action Level (EAL) S-8 and is being retracted. "During the events of 9/13/17, Control Room staff calculated Reactor Coolant System (RCS) leakage to the Pressurizer Relief Tank (PRT) through the Letdown Relief Valve to be greater than the EAL S-8 threshold of 10 gallons per minute. Subsequent review of trends associated with PRT level increase during the event determined that the RCS leakage to the PRT was less than 10 gallons per minute and therefore did not represent an Unusual Event under EAL S-8. "The NRC Resident Inspector was notified of this retraction." Notified R3DO (Riemer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2017-09-13
52966 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-09-12 12:28 | 2017-09-12 19:11 | 2017-09-12 | SECONDARY CONTAINMENT PRESSURE MOMENTARILY ABOVE TECHNICAL SPECIFICATION LIMIT "On September 12, 2017, at 1228 PDT, Reactor Building (Secondary Containment) pressure momentarily rose above the Technical Specification (TS) limit. Secondary Containment was declared inoperable and TS Action Statement 3.6.4.1.A was entered. The pressure rise was due to unexpected isolation of the supply and exhaust valves in the Reactor Building ventilation system due to an electrical transient on the power panel feeding the valve operators' solenoid pilot valves during maintenance. The cause of the electrical transient is under investigation. "The Reactor Building differential pressure controller restored the building pressure to within limits. The Control Room operators reopened the Reactor Building ventilation supply and exhaust valves. Secondary Containment was declared operable at 1228 PDT and TS Action Statement 3.6.4.1.A was exited. "This condition is being reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and accident mitigation." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-09-12
52965 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-09-11 | 2017-09-12 16:14 | 2017-09-12 | AGREEMENT STATE REPORT - THREE GAUGES WITH STUCK SHUTTERS The following information was received from the State of Texas via email: "On September 12, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that during routine inspections, three Berthold nuclear gauges were found with shutters stuck in the open position. Two of the gauges were model LB7442D each containing a 30 millicurie (original activity) cesium-137 source and one was a model LB300L containing a 44.7 millicurie (original activity) cobalt-60 source. "The shutter on the model LB300L gauge was stuck in the open position. The lock on the shutter on one of the model LB7442D gauge could not be removed. The locking latch on the other model LB7442D gauge would not operate. The RSO stated a service company has been contacted to repair the gauges and is expected to be on site by September 15, 2017. No individual will receive significant exposure to radiation due to this event." Texas Report: I-9509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-09-20
52964 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2017-09-12 11:31 | 2017-09-12 14:20 | 2017-09-12 | STANDBY LIQUID CONTROL SYSTEM PIPING FAILURE "On September 12, 2017 at 1131 CDT, both Unit 3 Standby Liquid Control system (SLC) subsystems were declared inoperable for a through wall leak on the common discharge piping. With both subsystems inoperable, the SLC system was unable to fulfill its safety function. "This event is reportable under 10 CFR 50.72(b)(3)(v)(A) for an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to shut down the reactor and maintain it in a safe shutdown condition and under 10 CFR 50.72(b)(3)(v)(D) for a system that was unavailable for accident mitigation. "The NRC Resident Inspector has been notified." With both trains of SLC inoperable, the licensee entered an 8-hr. action statement to restore at least one train to operability. If unable to do so, then the plant will enter a 12-hr. shutdown action statement. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-09-12
52963 | 0 | HEMLOCK SEMICONDUCTOR OPERATIONS |  |  |  |  | 2017-09-11 14:30 | 2017-09-12 09:46 | 2017-10-17 | SHUTTER STUCK IN THE OPEN POSITION "License No 21-32682-01 "Fixed Gauge Stuck Shutter-Stuck in the open/normal operating position No exposures Vega America Source Holder Model SHLG-2-45 Radionuclide: Cesium-137 5000mCi Source serial number 1485CO Source holder serial number 19509171 "At approximately 1430 hrs (EDT) on 9/11/2017 the site RSO attempted to operate the shutter on source holder 10071949 (Hemlock identifier). The shutter operation failed; the shutter is stuck in the open position. There were no exposures as a result of the failed shutter operation. Operating the shutter was part of a field training program for area operations personnel. The source holder is located on site on the HP DPR Tank. "[The RSO is] in contact with Vega Americas, the manufacturer, to determine a resolution plan. [The RSO] will follow up with a detailed report within 7 days and a complete investigation/resolution report once the gauge manufacturer has performed repairs on the gauge." * * * UPDATE FROM KELLY DEERING AT 1111 EDT ON 9/13/17. INCORPORATED 10/17/17 * * * "Reference: Fixed Gauge Stuck Shutter (written report) License No. 21-32682-01 Event No. 52963 Radionuclide: Cesium-137 5000 mCi Manufacturer: VEGA Americas (Cincinnati, Ohio 45209) Model Source Holder: SHLG-2-45 VEGA Americas Source Serial Number: 1485CO VEGA Americas Source Holder Serial Number: 19509171 Hemlock Semiconductor SAP Equipment Number: 10071949 "On Tuesday, September 11, 2017 at approximately 1430 EDT, the RSO was conducting radiation training for operations personnel in the area. While attempting to operate the shutter on the source holder located on S-557 HP DPR tank, the shutter mechanism would not close. The shutter is stuck fully open, in the normal operating position. [The RSO] contacted the manufacture, Vega Americas, and they suggested applying lubricant to the shutter mechanism to attempt to operate the shutter mechanism. The shutter mechanism was lubricated multiple times throughout the day. The following morning the shutter would still not operate. The NRC was contacted to report the incident at that time. The NRC was contacted via phone and the incident was reported on September 12 at 0930 EDT. There were no radiological exposures as a result of the shutter malfunction. "As part of a preventative maintenance plan the source shutters are lubricated and operated every 6 months. April 2017 was the last time scheduled routine maintenance was performed. This specific source was operated approximately 30 days with no issues being noted. Because this source is located at the top of a tower, a cover was previously built to help protect the source holder from the weather. There has been no loss of production as a result of the shutter malfunction. "Hemlock Semiconductor Operations is in contact with Vega Americas, the manufacturer who is licensed with the NRC to repair the source holders. Vega's technician is scheduled to be on site September 18th, 2017 to perform repairs on the stuck shutter; we will not attempt to operate the shutter until repairs have occurred. The state of the stuck shutter has been thoroughly communicated to all personnel that are assigned to the general area. All operators assigned to the specific tower where the gauge is located, are Authorized Gauge Users. Area leaders, emergency response department and plant management have also been communicated to in reference to the stuck shutter. Any individual not assigned to the tower must badge into the area and contact an authorized gauge user to gain access to the tower where the gauge is located. The authorized gauge user will then contact the RSO or assistant RSO for approval for tower access. The gauge is located and operating in a manner consistent with our normal operating status. The normal signs and barriers are in place. "This incident, any findings by Vega and any subsequence action items will be documented in our GIMS database (incident reporting and action item tracking tool), and a follow up email will be sent to the NRC." * * * UPDATE FROM KELLY DEERING TO DONALD NORWOOD AT 1125 EDT ON 10/17/2017 * * * "Vega Americas field technician arrived at Hemlock Semiconductor on 9/18/2017. The following is directly from his field report: "'9/18/2017: [The Repair Technician] arrived on site and met with [RSO]. The customer has a stuck shutter on a SHLG-2-45 with a 5000mCi Cs-137 source, S/N 1485CO, CO# 6121698, TAG# LX-577007-A, dated 1/11 and with source holder S/N 19509171. [The Repair Technician] freed the shutter mechanism. Some water was released from the shaft well when the shutter was freed. Water intrusion appears to be the cause of the stuck mechanism. There was some buildup of either corrosion products or other material accumulated on the shaft of the operating mechanism. [The Repair Technician] cleaned the shaft using a scrub pad. [The Repair Technician] reattached the rubber top seal using spray adhesive. [The Repair Technician] operated the shutter multiple times without further issue. [The Repair Technician] performed a leak test and a survey at the customer's request. [The Repair Technician] recommended operating the shutter mechanism once a week for the next 2 months. If there are no further issues, then [the Repair Technician] recommended no further action. Shutter checks can be returned to a normal 6 month schedule. If the shutter becomes stuck again then [the Repair Technician] recommended the source holder be removed from service and repaired.' "Per the recommendation we have been operating the shutter mechanism weekly. There have been no issues and the shutter is operating freely. Leak test and survey checks showed no issues with the source holder. This incident has been documented internally and will continue to be monitored. If the shutter continues to operate freely, Hemlock Semiconductor will consider this incident closed." Notified R3DO Daley and NMSS Events Notifications | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-09-12
52962 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-09-11 16:48 | 2017-09-11 21:48 | 2017-09-11 | EMERGENCY DIESEL GENERATOR ACTUATION ON LOW VOLTAGE "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) as an event that resulted in a valid actuation of the Emergency Diesel Generator. "On September 11, 2017 at 1648 [EDT] the 'A' Emergency Diesel Generator (EDG) started on the low voltage signal from Bus 1DA as a result of a 115KV grid perturbation. All emergency buses remained energized from offsite power. The EDG did not tie to the 1DA bus because the offsite power voltage recovered within the designed recovery time limit. The diesel generator has been secured, reset and is ready to auto start. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-09-11
52961 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2017-07-14 14:53 | 2017-09-11 15:00 | 2017-09-11 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "This report is being made as required by 10 CFR 50.73(a)(2)(iv)(A) to describe an automatic actuation of containment isolation valves in more than one system. Because the actuation was invalid, this 60-day telephone notification is being made instead of a written LER [Licensee Event Report], in accordance with 10 CFR 50.73(a)(1). "On 07/14/17, at approximately 1453 hours [EDT], an electrical transient occurred due to an off-site lightning strike that de-energized one of the station's two qualified off-site power sources. This resulted in an automatic fast transfer of four 4 kV electrical buses to the alternate off-site source. The fast transfer occurred as designed without complications. The loss of power had numerous impacts on plant equipment that occurred in accordance with plant design, including a Group 2 primary containment isolation on both units. The Group 2 isolation affected multiple systems, including Reactor Water Cleanup, Instrument Nitrogen, and the Drywell Floor Drain. "The fault on the off-site transmission line immediately cleared after the lightning strike and at 1457 hours [EDT] the transmission system operator gave the station permission to reclose the breaker to the off-site source. Following system restorations and equipment walkdowns, plant operators re-established normal connections to the off-site source on 7/14/17 at 2322 hours [EDT] in accordance with station procedures. "The containment isolation occurred as a result of the loss of an off-site power source and was not due to actual plant conditions or parameters meeting design criteria for containment isolation. Therefore, this is considered to be an invalid actuation. "The NRC Resident Inspector has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-09-11
52960 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2017-09-10 18:55 | 2017-09-10 22:20 | 2017-09-10 | MANUAL REACTOR TRIP ON LOWERING STEAM GENERATOR WATER LEVEL "On 09/10/17 at 1855 [EDT], [Turkey Point] Unit 4 reactor was manually tripped from 88% RTP [Rated Thermal Power] due to a failure of 4C Steam Generator main feed regulating valve causing lowering S/G [Steam Generator] level. All other systems operated normally. Auxiliary Feed Water initiated as designed to provide S/G water level control. EOP's [Emergency Operating Procedures] have been exited and General Operating procedures (GOP'S) were entered. Unit 4 is stable in Mode 3 at NOT/NOP [Normal Operating Temperature/Normal Operating Pressure]." The licensee is investigating the failure of the feed regulating valve. Offsite power is available. Decay heat is being removed via main feedwater with steam discharged to atmosphere using the ADVs [Atmospheric Dump Valves]. There is no known primary-secondary steam generator tube leakage. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-09-10
52959 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2017-09-10 11:51 | 2017-09-10 20:45 | 2017-09-10 | TWO CONTROL BAY CHILLERS DECLARED INOPERABLE "At 1151 [CDT] on September 10, 2017 Browns Ferry Units 1 and 2 declared 'B' Control Bay chiller inoperable. 'A' Control Bay chiller was previously declared inoperable. This resulted in inoperability of the equipment in the U1 and U2 4kV Shutdown Board Rooms. The declarations of the equipment in the Shutdown Board Rooms is a loss of safely function for electrical components (4kv Shutdown Boards and 480V Shutdown Boards) required for shut down of the U1 and U2 reactors and maintaining them in a safe shutdown condition, as well as RHR capability and Accident Mitigation. "lnoperability of these boards also requires declaring two trains of Standby Gas Treatment inoperable resulting in a loss of safety function for Units 1, 2 and 3 for systems needed to control the release of radioactive material. This event requires an 8 hour report IAW 50.72(b)(3)(v), 'Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident." The NRC Resident Inspector has been notified. CR 1336821 was initiated in the Browns Ferry Corrective Action Program. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2017-09-10
52958 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2017-09-09 10:00 | 2017-09-09 15:04 | 2017-09-09 | MECHANICAL DRAFT COOLING TOWER FANS DECLARED INOPERABLE "At 1000 EDT on September 9, 2017, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to failure of the over speed fan brake inverter. The brakes prevent fan over speed from a design basis tornado. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. Investigation into why the Division 2 MDCT fan over speed brake inverter failed is in progress. This report is being made pursuant to 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident based on a loss of a single train safety system." The licensee entered two (2) LCO Action Statements (AS); 14-day LCO AS 3.5.1 for ECCS (HPCI Inoperable) and 72-hour AS 3.7.2 for UHS. The licensee has two spare inverters on-site. After replacement and successful post-maintenance testing the licensee expects to exit both AS before 72-hours. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-09-09
52957 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2017-09-09 11:09 | 2017-09-09 11:50 | 2017-09-09 | HURRICANE WARNING ISSUED AFFECTING SITE WITHIN 36 HOURS Crystal River Unit 3 is currently undergoing decommissioning and is permanently shut down. The licensee entered their adverse weather procedure EM-220D based on a Hurricane Warning affecting the site within 36 hours. All applicable sections of EM-220D are complete or in progress. No fuel movement activities are in progress. All equipment including Emergency Diesel Generators (EDGS) is available to perform required spent fuel cooling. The licensee will inform the NRC Region I Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | FL | POW | [5 empty] | 0 | 2017-09-09
52956 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2017-09-08 17:14 | 2017-09-08 17:51 | 2017-09-11 | NOTIFICATION OF UNUSUAL EVENT - HURRICANE WARNING "At time 1700 [EDT] today, the National Weather Service issued a Hurricane Warning for the area including the St. Lucie Nuclear Power Plant. On that basis, a Notice of Unusual Event was declared at time 1714 [EDT]. In anticipation of severe weather, the site has completed proceduralized high wind preparations. "Both units are currently stable at 100% power." The licensee notified both State and local agencies and has informed the NRC Resident Inspector. No safety-related systems are out of service. The electrical grid is stable. Notified DHS SWO, FEMA Operations Center, DHS NICC, FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 9/9/17 AT 1743 EDT FROM DALE THOMAS TO S. SANDIN * * * "At 1701 [EDT] today (09/09/17), a 24-hour update was made to state and local governments following the National Weather Service issuing yesterday's hurricane warning for the area including St. Lucie Plant. On that basis, a Notice of Unusual Event was declared yesterday (09/08/17) at 1714 [EDT]. There are no changes in plant status for either Unit. "In anticipation of severe weather, the site previously completed high wind preparations. Our plants have been specifically built to withstand natural disasters such as hurricanes, tornadoes, earthquakes, flooding and tidal surges. This approach will ensure the safety of operations and our employees and the communities surrounding our plants. "Both units are currently stable at 100% power level and will remain at that power since hurricane force winds are not currently projected to reach St. Lucie Plant. "The NRC Resident Inspector has been informed." Notified R2DO (Michel). * * * UPDATE ON 9/10/17 AT 1730 EDT FROM DALE THOMAS TO DONG PARK * * * "At 1648 [EDT] today (09/10/17), a 24-hour update was made to state and local governments following the National Weather Service issuing Friday's hurricane warning for the area including St. Lucie Plant. On that basis, a Notice of Unusual Event was declared yesterday (09/08/17) at 1714 [EDT]. There are no changes in plant status for either Unit. "In anticipation of severe weather, the site previously completed high wind preparations. Our plants have been specifically built to withstand natural disasters such as hurricanes, tornadoes, earthquakes, flooding and tidal surges. This approach will ensure the safety of operations and our employees and the communities surrounding our plants. "Both units are currently stable at 100% power level and will remain at that power since hurricane force winds are not currently projected to reach St. Lucie Plant. "The NRC Resident Inspector has been informed." Notified R2IRC (Franke). * * * UPDATE ON 9/11/17 AT 1405 EDT FROM BRIAN KELLY TO BETHANY CECERE * * * "The Hurricane Warning has been terminated by the National Weather Service for St. Lucie County including the Plant Site. At time 1313 [EDT] on 9/11/17, St. Lucie Nuclear Power Plant has terminated from the Unusual Event Classification." Unit 1 is currently shutdown in Mode 3, Hot Standby. Unit 2 continues to operate in Mode 1, 100 percent power. The licensee notified State and Local Government Agencies, and the NRC Resident Inspector. Notified R2IRC (Munday), R2DO (Michel), NRR EO (King), IRD MOC (Gott), DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2017-09-08
52955 | -1 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2017-09-08 11:30 | 2017-09-08 16:45 | 2017-10-19 | HPCI SYSTEM INOPERABLE "On September 8, 2017 at 1130 hours CDT, Unit Two High Pressure Coolant Injection (HPCI) Minimum Flow Valve MO 2-2301-14 flow indicating switch (FIS 2-2354) failed to meet the Technical Specification Allowable Value during calibration testing. Technical Specification Table 3.3.5.1-1 Allowable Value (3.f) requires greater than or equal to 634 gpm (3.14 inches water column as required by procedure). HPCI was subsequently declared inoperable. "This event is being reported as a condition that could have prevented fulfillment of a safety function in accordance with 10CFR50.72(b)(3)(v)(D). The HPCI system is a single train system and the loss of HPCI could impact the plant's ability to mitigate the consequences of an accident. The Reactor Core Isolation Cooling (RCIC) system was confirmed operable. "Note: On September 8, 2017 at 1140 hours CDT, the HPCI Minimum Flow Valve MO 2-2301-14 flow indicating switch (FIS 2- 2354) was successfully recalibrated and HPCI was returned to Operable status. "The NRC Senior Resident Inspector has been notified." * * * RETRACTION AT 1216 EDT ON 10/19/17 FROM RYAN DECKER TO DONG PARK * * * "The purpose of this notification today (10/19/17) is to retract the ENS Report made on September 8, 2017 at 1545 hours CDT (ENS Report #52955). "Upon further investigation, it was determined that a surveillance procedure contained an overly restrictive statement that directed operators to immediately declare the High Pressure Coolant Injection (HPCI) system inoperable when the HPCI Minimum Flow Valve MO 2-2301-14 flow indicating switch (FIS 2-2354) fails. This statement was in conflict with existing Technical Specification (TS) 3.3.5.1, Condition E, that allows seven days to restore the HPCI FIS (instrument channel only) to an operable status prior to entry into TS 3.3.5.1, Condition H, which requires declaring HPCI inoperable immediately. Hence, during the period of FIS inoperability (i.e., 10 minutes), the HPCI system was not required to be declared inoperable in accordance with Technical Specifications. Therefore, based on this information, ENS Report # 52955 is being retracted. "Note: On September 8, 2017 at 1140 hours CDT, the HPCI Minimum Flow Valve MO 2-2301-14 flow indicating switch (FIS 2-2354) was successfully recalibrated and HPCI was returned to Operable status. "The NRC Resident Inspector has been notified." Notified R3DO (Daley). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-09-08
52954 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2017-09-07 15:07 | 2017-09-08 12:49 | 2017-09-08 | FITNESS FOR DUTY - CONFIRMED POSITIVE FFD TEST "A non-licensed employee supervisor had a confirmed positive for a prohibited substance during a random fitness-for-duty [FFD] test. The individual's unescorted access to the plant has been removed. The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.719 |  |  |  | 0 | 2017-09-08
52953 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-09-07 | 2017-09-08 12:34 | 2017-09-08 | AGREEMENT STATE REPORT - DISCONNECTED SOURCE ON SPEC 150 EXPOSURE DEVICE The following information was received from the State of Texas via email: "On September 8, 2017, the Agency [Texas Department of State Health Services - Radiation Branch] was notified by the licensee's radiation safety officer (RSO) that one of their crews had experienced a source disconnect on September 7, 2017 at a field site. The crew was using a SPEC 150 exposure device containing a 92 curie iridium - 192 source. The crew was working inside a shooting bay at a customer's location when the event occurred. The radiographers had completed an exposure and attempted to retract the source. The RSO stated the radiographers could not get the lock on the camera to trip. As they approached the camera they noted the dose rate reading on their dose rate meter was pegged so they retreated to the area where they operated the crank out device and called the RSO. The RSO, who is authorized by their license to recover sources, drove to the location and performed the source recovery. The RSO placed shielding over the source which was located in the collimator and removed the guide tube from the camera. The RSO found the drive cable sticking through the front of the camera. He disconnected the crank out device from the rear of the camera and found the drive cable had gone completely through the camera. The RSO found that the drive cable had broken inside the drive cable protective housing about 18 feet from the source. The RSO manually retracted the source into the camera by pulling on the drive cable. The source was returned to its fully shielded position. The licensee will send drive cable assembly to the manufacturer for inspection. No over exposure or exposure to a member of the general public occurred as a result of this event. Additional information on this event will be provided in accordance with SA-300." Texas Incident #: I-9508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-09-18
52952 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2017-09-07 23:14 | 2017-09-08 00:06 | 2017-09-11 | NOTIFICATION OF UNUSUAL EVENT - HURRICANE WARNING "At 2300 today, the National Weather Service issued a hurricane warning for the area including Turkey Point Nuclear Units 3 & 4. On that basis, a Notice of Unusual Event was declared at 2314 [EDT]. In anticipation of severe weather, the site has completed proceduralized high wind preparations. Our plants have been specifically built to withstand natural disasters such as hurricanes, tornadoes, earthquakes, flooding and tidal surges. This approach will ensure the safety of operations and our employees and the communities surrounding our plants. "Both units are currently stable at 100% power level. "The NRC Resident Inspector has been informed." No safety systems are out of service. The electrical grid is stable but grid risk is high. Notified DHS, FEMA, NICC, and NSSA (e-mail). * * * UPDATE AT 0458 EDT ON 09/11/17 FROM TIM JONES TO JEFF HERRERA * * * "At 0400 [EDT] on 09/11/17, conditions at Turkey Point Nuclear have met established exit criteria to downgrade the Notice Of Unusual Event (NOUE). The previously reported EAL [Emergency Action Level] has been exited." "The NRC Resident Inspector has been informed." Notified the R2DO (Michel) and R2OC (Miller), IRDMOC (Gott), NRREO (Miller), DHS, DOE, FEMA, HHS, USDA, EPA, FDA, DHS NICC, and NSSA (e-mail). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2017-09-08
52951 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-09-06 | 2017-09-07 13:32 | 2017-09-07 | AGREEMENT STATE REPORT - LEVEL GAUGE STUCK SHUTTER The following was received from the State of Illinois via email: "At approximately 1052 [CDT] on 9/7/17, the RSO for lngredion (IL-01065-02) reported a shutter stuck in the 'on' position for a level gauge at their licensed facility in Bedford Park. The inoperable condition of the shutter and the resulting removal of the gauge from service occurred on 9/6/17. Reportedly, due to the mounting location of the device, no potential for exposure to personnel existed. The gauge has been removed and locked out by SAHCI [Stan A Huber Consultants, Inc.]. No surfaces of the gauge exceed 2 mR/hour and appropriate action for disposal is pending. "The licensee reports an electronic switching device operates the shutter. This automatic device was bent and deformed as part of the operating process and the rod portion of the shutter was cracked most of the way through. As part of the remediation process, the shutter push rod broke off completely. Several unsuccessful attempts were made using WD40 and a pin to close the shutter. The gauge was removed from operation by SAHCI, keeping the primary beam away from all personnel. A 2x4x4 inch lead brick was secured to the face of the gauge. The exposure rate at the face of the gauge was less than 2mR/hr at all accessible surfaces. The gauge was secured in the locked radioactive material storage cabinet. The storage cabinet has five nuclear gauges stored within. The outside of the storage cabinet is less than 2mR/hr at the surface. "The current plan is to properly dispose of the stuck shutter gauge. [SAHCI] request a disposal quote. "The SSDR indicates maximum exposure rates for this device (max 500 mCi Cs-137) when the shutter is in the 'ON' position are less than 50 mR/hr at 5 cm and less than 5 mR/hr at 30 cm." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-09-15
52950 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2017-09-06 11:57 | 2017-09-06 15:41 | 2017-09-06 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL "On September 6, 2017 at 1157 [EDT], Nine Mile Point Unit 1 experienced an automatic reactor scram with a Main Steam Isolation Valve (MSIV) and Containment isolation. The scram was due to reactor vessel low water level. The cause of the reactor vessel low water level is under investigation. All control rods fully inserted. Following the scram, pressure was momentarily controlled through the use of the Emergency Condenser (EC) system. At 1205, pressure control was established through the main steam lines to the condenser through the turbine bypass valves. All plant systems responded per design following the scram. The reactor scram is a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B). "The following systems automatically actuated after the scram as expected. These system actuations are an 8-hour report per 10 CFR 50.72(b)(3)(iv)(A): 1. The High Pressure Coolant Injection (HPCI) system. HPCI initiated at 1157 and was reset at 1158 when RPV level was restored above the HPCI system low level actuation set point. HPCI is a flow control mode of the normal feedwater systems, and is not an Emergency Core Cooling System. 2. The Core Spray system actuated, but did not discharge to the Reactor Coolant system. The Core Spray system was secured at 1216. 3. Containment and MSIV isolation on reactor vessel low-low water level signal. "Nine Mile Point Unit 1 is currently in Hot Shutdown, with reactor vessel water level and pressure maintained within normal bands. Decay heat is being removed via steam to the main condenser using the turbine bypass valves. The offsite grid is stable with no grid restrictions or warnings in effect. "The licensee has notified the NRC Resident Inspector." No safety relief valves lifted during the transient. The main steam isolation valves were opened after the isolation signal cleared to facilitate decay heat removal. Offsite power is supplying all plant loads. There was no effect on Unit 2. The licensee notified New York State Department of Environmental Protection and will be issuing a press release. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-09-06
52949 | 0 | WEST VIRGINIA UNIVERSITY HOSPITAL |  |  |  |  | 2017-09-05 16:30 | 2017-09-06 15:25 | 2017-09-06 | BRACHYTHERAPY TREATMENT DELIVERED DOSE LESS THAN PRESCRIBED DOSE "In compliance with 10CFR35.3045(c), WVU [West Virginia University] Hospitals License # 47-23066-02, Docket # 03020233 is making telephone notification declaring a medical event. "On September 5, 2017 a patient was being administered the first fraction of a planned five fraction HDR interstitial brachytherapy treatment, treating the cervix. The written directive prescribed 5, 5Gy fractions for a total dose of 25Gy. During the first fraction, 5 separate interlocks were tripped at which time the manufacturer was contacted [at] 1535 [EDT]. Based on discussions between the medical physics team and the manufacturer, the manufacturer determined the error was caused by fluid in the catheter which may have contaminated the source and the afterloader unit. The manufacturer advised to suspend treatment, and stop all use of the afterloader until it could be decontaminated and the source could be exchanged. (Scheduled for September 7, 2017). "At the time the treatment was stopped, the patient received 0.32Gy of the planned 5Gy fraction, based on a 12.1 seconds treated of a planned 576.8 second treatment fraction. "Based on 10CFR35.3045(a)(1), the fraction of the dose differed by more than 50 rem to organ or tissue, and 10CFR35.3045(a)(1)(iii) the fractionated dose delivered differs from the prescribed dose for a single fraction, by 50 percent or more. "In compliance with 10CFR35.3045(e), the patient and referring physician have been notified. "Upon decontamination and source exchange the patient is scheduled to complete the treatment per the written directive (September 7-9, 2017). "In compliance with 10CFR35.3045(d), a written report will be submitted to the Region One Office within 15 days." The Licensee has notified R1(Gallaghar). A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2017-09-14
52948 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2017-09-06 11:15 | 2017-09-06 14:11 | 2017-09-06 | OFFSITE NOTIFICATION DUE TO POTENTIAL RELEASE OF TRITIUM BEARING WATER AND SECONDARY CHEMICALS INTO THE PROTECTED AREA "Inspection of an underground pipe used to discharge the contents of the Unit 3 Condensate Polishing Facility in accordance with the National Pollutant Discharge Elimination System (NPDES) Discharge Permit identified the potential for small amounts of water containing tritium and Secondary chemicals to be released to the ground within the plant Protected Area. The water met all permit limits for discharge to the normal discharge point. Groundwater tritium levels were well below reportable limits. The line has been removed from service. The Connecticut Department of Energy and Environmental Protection was notified at 1115 [EDT] on September 6, 2017. "This event is being reported in accordance with 10CFR50.72(b)(2)(xi) for 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-09-06
52947 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2017-09-05 11:11 | 2017-09-05 17:16 | 2017-09-05 | PRIMARY CONTAINMENT DECLARED INOPERABLE DUE TO BOTH AIRLOCK DOORS OPEN SIMULTANEOUSLY "On September 5, 2017 at 1111 EDT, with the reactor at 100 percent core thermal power and steady state conditions, plant personnel identified that both doors of the emergency personnel airlock of the equipment hatch were open simultaneously due to failure of the interlock. Personnel were at both the outside and inside doors, personnel heard air movement through the air lock. Immediate action was taken to close the inner containment personnel airlock door and it was verified closed. Both doors of the emergency personnel airlock of the equipment hatch were open for less than one minute. There was no radioactive release as a result of the event. The cause of the interlock failure is under investigation. "This condition requires an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(ii)(A), the condition of the nuclear power plant, including its principal safety barriers (primary containment), being seriously degraded. This condition is also reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT UNCNTRL RAD REL |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(C) |  |  | 0 | 2017-09-05
52946 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2017-09-02 11:48 | 2017-09-02 19:36 | 2017-09-02 | AREA RADIATION MONITOR FAILURE "MCR (Main Control Room) area radiation monitor R-1 failed at 1148 [EDT on] 9/2/2017. This caused a loss of capability to classify EAL [Emergency Action Level] RA3.1, Dose Rates greater than 15 mrem/hr in either of the following areas requiring continuous occupancy to maintain plant safety functions: Control Room (R-1) or CAS [Central Alarm Station]. Compensatory measures are currently in place with a portable radiation monitor in the MCR with alarm setpoints consistent with R-1. Priority maintenance is being planned to restore R-1 to service." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-09-02
52945 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-09-01 21:40 | 2017-09-02 01:36 | 2017-09-02 | MANUAL REACTOR TRIP DUE TO TWO DROPPED RODS "At time 2140 [CDT] on September 1, 2017, CPNPP [Comanche Peak Nuclear Power Plant] Unit 2 experienced two (2) dropped rods, one control, one shutdown. The reactor was then manually tripped. "This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(B) for reactor trip and 10CFR 50.72(b)(3)(iv)(A) for an actuation of auxiliary feedwater. "Currently Unit 2 is being maintained in Hot Standby (Mode 3) in accordance with Integrated Plant Operating Procedure IP0-007B, Emergency Response Guideline Procedure Network has been exited. Decay Heat is being rejected to the Main Condenser via Steam Dump Valves (Turbine Bypass Valves). "The NRC Resident Inspector has been notified." All rods inserted into the core during the trip. No relief or safety valves actuated during the plant transient. The electrical grid is stable and supplying plant loads. Unit 1 was not affected by the transient. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-09-02
52944 | 0 | VARIAN MEDICAL SYSTEMS |  |  |  |  | 2017-08-30 | 2017-09-01 13:30 | 2017-09-08 | IRIDIUM-192 SOURCE LOST DURING SHIPMENT A 3.792 Curie Ir-192 source was removed from a Varian High Dose Rate afterloader and prepared for shipment by common carrier. The packaged source was picked up from Glens Falls Hospital in Glens Falls, New York by a representative of the common carrier on August 21, 2017. The destination of the source was to Alpha-Omega Services in Vinton, Louisiana for disposal. The source arrived at the common carrier's local station in Manands, New York on August 22, 2017. When the licensee checked package tracking information on August 30, 2016, the licensee noted that the package indicated that it was still at the common carrier's local station. The licensee attempted to contact the common carrier on August 30, 2017 without success. The licensee successfully contacted the common carrier on August 31, 2017 and the common carrier initiated a 'station trace' at that time. At the present time the source has not been located. The common carrier is still searching. * * * UPDATE ON 9/8/17 AT 1531 EDT FROM KATHARINE ARZATE TO DONG PARK * * * The Ir-192 source was located by the common carrier at 1837 PDT on 9/1/17. The package was delivered to the recipient on 8/29/17. Notified R1DO (Dentel), NMSS Events Notification, and Canada. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf Note: This device is assigned an IAEA Category 3 value based on the actual radioactivity of the source, not on the device type. (Reference IAEA RG-G-1.9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NY | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-09-11
52943 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2017-09-01 10:15 | 2017-09-01 12:59 | 2017-09-01 | PRESUMED LOSS OF SPECIAL NUCLEAR MATERIAL - UNAUTHORIZED, UNINTENDED REMOVAL "[This event was made by the] Nuclear Material Safeguards Coordinator, Westinghouse Columbia Fuel Fabrication Facility (CFFF). The facility manufactures nuclear fuel enriched to no greater than 5 weight percent U235 for use in commercial light water reactors. "Report is being made under 10 CFR 74.11, 'Reports of loss or theft or attempted theft or unauthorized production of nuclear material.' This event is a presumed loss (unauthorized unintentional removal) of nuclear material. "Fuel rods WD1SKLB4, WD2DSMAW, and WD2ZRZF7 could not be located on site and are presumed to have been physically loaded into a fuel assembly and shipped to a customer on 7/31/2017. Based on a preliminary investigation evidence suggests these rods were physically loaded into a fuel assembly without scanning the rods and performing the transaction to document they were loaded into the assembly. The fuel rods contained a total of 5,575 grams Uranium and 258 grams U-235. The assembly in question is currently at a customer site." Westinghouse has made notifications to Region 2, and is in the process of notifying the customer. They plan to send inspectors to the customer to verify the fuel rods, or have that assembly returned to their facility for inspection. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | 74.11(a) |  |  |  | 1 | 2017-09-11
52942 | 0 | CA DEPT OF PUBLIC HEALTH |  |  |  |  | 2017-08-30 | 2017-08-31 13:32 | 2017-08-31 | AGREEMENT STATE REPORT - DAMAGED MOISTURE/DENSITY GAUGE The following report was received from the California Department of Public Health, Radiologic Health Branch (CA RHB) by email: "On August 30, 2017, the President and ARSO of Earth-Strata, Inc., contacted the CA RHB Brea office [at 1415 PDT] to report a moisture/density gauge had been run over by a bulldozer at a construction site in Santa Clarita, CA. The gauge is a CPN MC-3, S/N M36087027 (10 mCi Cs-137, 50 mCi Am:Be-241). [The licensee] stated that the gauge was on the ground with the Cs-137 source in the shielded position when it was struck by the bulldozer. The area around the gauge was isolated until the gauge operator was instructed by [the ARSO] to place the gauge in the transport case for transport to Maurer Technical Services to be inspected and to perform an emergency leak test. [The licensee] stated that the plastic cover of the gauge had been broken and the guide tube and source rod had broken off of the top of the source shield. [The licensee] stated that after the gauge was inspected by Maurer personnel, it was determined that the Cs-137 source remained in the shielded position and the Am:Be-241 source remained intact and was still attached to gauge. Maurer Technical Services will assist in the disposal of the gauge. The investigation will remain open and any citations will be deferred until the licensee provides the 30-day report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR | 30.50(b)(2) |  |  |  | 0 | 2017-09-08
52941 | 0 | MICHIGAN DEPARTMENT OF CORRECTIONS |  |  |  |  | 2017-08-18 14:00 | 2017-08-31 12:40 | 2017-08-31 | STOLEN THEN IMPROPERLY DISPOSED OF TRITIUM EXIT SIGNS A trustee prisoner was found to have removed 10 tritium 'bulbs' from 10 tritium exit signs at Marquette Branch Prison. The trustee prisoner was using the tritium bulbs as night lights. Eight of the 10 tritium bulbs were recovered. The trustee prisoner admitted to having broken two of the tritium bulbs and then flushed them down a toilet. The activity level of the tritium bulbs is unknown at this time. The recovered eight tritium bulbs are currently in secure storage. These tritium bulbs will be disposed of by an approved/licensed contractor. The trustee prisoner has been removed from trustee status. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-09-08
52940 | 0 | ZION |  |  |  | ISFSI | 2017-08-30 18:24 | 2017-08-30 22:37 | 2017-08-30 | INDEPENDENT SPENT FUEL STORAGE INSTALLATION FUEL OIL SPILL "At approximately 1824 [CDT], the ISFSI was notified of a diesel spill of approximately 70 gallons onto gravel and concrete. The spill originated as a 500 gallon tank was being transported and fell from the forks. The pump on top of the tank was damaged causing the leak. No personnel were injured and there was no pathway to a waterway. Notification was made at 2045 to IEMA [Illinois Emergency Management Agency]. The reason for notification is due to 10CFR50.72(b)(xi), notification to off-site government agency. The spill was cleaned up by site personnel and supervised by the Environmental Manager." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Independent Spent Fuel Storage Installation | OFFSITE NOTIFICATION | [9 empty] | NON EMERGENCY | 3 | IL | ISF |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-08-30
52939 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-08-30 | 2017-08-30 16:18 | 2017-08-30 | AGREEMENT STATE REPORT - SHUTTER FAILED OPEN The following report was received via e-mail: "On August 30, 2017, the licensee noticed that a shutter indicator light on a Pm-147 Honeywell-Measurex fixed gauge device, on a paper mill line, was not functioning correctly. The light was on and indicating that the shutter was closed, when the shutter was actually in the open position. However, the device shutter is still working and communicating as usual. The licensee utilized a survey meter to determine that even though the light was on, the shutter was open. The licensee roped off the area, instructed all operators to the status of the shutter, and re-instructed to always use a survey meter if they needed to approach the device and to assume the shutter is open. The licensee is continuing operations, but controlling access to the area while a fix is arranged. The licensee is in contact with the manufacturer to determine the next steps. The state is in contact with the licensee and will be continuing to follow the situation." Wisconsin Event: WI 170013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-09-07
52938 | 0 | NUTHERM INTERNATIONAL, INC |  |  |  |  | 2017-08-29 | 2017-08-30 11:33 | 2017-08-30 | PART 21 REPORT - RELAY FAILURE NUTHERM MODEL 700DC The following excerpted report was received via fax: "On the basis of our evaluation, it is determined that Nutherm lnternational, Inc. does not have sufficient information to determine if the subject condition would, or has, created a Substantial Safety Hazard or would have created a Technical Specification Safety Limit violation as it relates to the subject plant applications. "On 8/28/2017 Cooper notified the NRC of a reportable condition under 10CFR Part 21. An Allen Bradley relay base model 700DC exhibited early failure after 133 hours of service. This relay, model 700DC, has been dedicated/qualified for multiple applications for various plants. "The Allen Bradley 700DC series relay coil failed after 133 hours of service. This failure was determined by Cooper Nuclear Station to have been a component infant mortality likely caused by a manufacturing flaw that likely occurred due to a tensioning issue at the start of the coil wire winding process. Failure of the coil will result in failure of the relay, which could result in a safety hazard. "Nutherm International, Inc. has concluded its review of all procurements of the 700DC series relays that use the coil in question and have found forty-nine (49) units shipped to customers which could potentially have this defect: Nebraska Public Power Cooper Nuclear Station and Indiana Michigan Power Company Donald C. Cook Nuclear Plant. "Initial actions of determining the units affected were completed 8/30/2017. The impacted customers were notified of this condition 8/30/2017. Nutherm International, Inc. does not have sufficient information to determine this condition would, or has, created a Substantial Safety Hazard or would have created a Technical Specification Safety Limit violation as it relates to the subject plant applications. Nutherm has no current orders for these units and has no units in stock. No further actions will be taken at this time. "This issue has been identified as a 'component infant mortality' failure caused by a manufacturing flaw. The manufacturing flaw appears to be a random failure and was identified by Cooper Nuclear Station as likely to have occurred due to a tensioning issue at the start of the coil wire winding process. Failure of the coil would be expected to occur within a few days of operation. The units that have been installed and in operation for more than two months could be considered to not contain this random manufacturing flaw." Point of Contact: Thomas Sterbis - 618-244-6000 See also NRC event: 52934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-08-30
52937 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-08-30 02:10 | 2017-08-30 10:35 | 2017-08-30 | UNPLANNED LOSS OF EMERGENCY RESPONSE EQUIPMENT "At 0210 CDT on August 30, 2017, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 experienced an unplanned loss of the Plant Computer System (PCS). The loss of the Unit 2 PCS resulted in a loss of emergency assessment capability to the CPNPP Technical Support Center (TSC) and Emergency Operations Facility (EOF) for greater than 60 minutes. As of 0530 CDT the Unit 2 PCS has been restored. Assessment capability has been verified to be available in the TSC and EOF. "This report is being made pursuant to 10CFR50.72(b)(3)(xiii), any event that results in a loss of emergency assessment capability, off site response capability, or off site communications ability. "The NRC Resident Inspector has been informed." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-08-30
52936 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-08-29 12:00 | 2017-08-29 14:42 | 2017-08-29 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN "On August 22, 2017 at 2321 hours, Grand Gulf Nuclear Station entered Technical Specification conditions for three Limiting Condition for Operations (LCOs) not met due to Residual Heat Removal 'A' (RHR 'A') being declared inoperable. "LCOs not met: 1) 3.5.1 for one low pressure ECCS [Emergency Core Cooling System] injection/spray subsystem. 2) 3.6.1.7 for one RHR containment spray subsystem, and 3) 3.6.2.3 for one RHR suppression pool cooling subsystem. "The station has made the decision to shutdown the plant based on the results of troubleshooting performed on the RHR 'A' pump. The restoration of RHR 'A' pump will not be completed prior to the end of the 7 day LCO completion time. "Grand Gulf Nuclear Station initiated plant shutdown required by Technical Specifications 3.5.1, 3.6.1.7, and 3.6.2.3 at 1200 hours CDT on 08/29/2017 due to expected restoration of RHR 'A' exceeding the completion time of 7 days prior to restoring operability." The licensee notified the NRC Resident Inspector. | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2017-08-29
52935 | 0 | FISHER CONTROLS INTERNATIONAL, LLC |  |  |  |  | 2017-08-28 | 2017-08-28 17:45 | 2017-08-28 | PART 21 REPORT - FLOW SCANNER 6.6 CODE ERROR The following information was received via e-mail: "Fisher Information Notice: FIN 2017-04: Erroneous Rotary Seating Torque Calculation in FlowScanner Software "This Fisher Information Notice (FIN) applies only to the equipment identified in Appendix A, which lists serial numbers and order numbers that were delivered to customers. Specifically, it applies to FlowScanner 6.6 (build 6.6.000.29) and 6.6 SP1 (build 6.6.000.67). Appendix B of this document includes a decision tree to help customers further determine if this FIN applies to any work performed. "The purpose of this FIN is to alert affected customers that, as of 29 June 2017, Fisher Controls International LLC (Fisher) became aware of a situation which may affect the performance of the aforementioned equipment. Fisher is informing affected customers of this circumstance in accordance with Section 21.21 (b) of 10 CFR 21. "In the process of updating a customer's older FlowScanner software version to 6.6.000.67 (SP1), the customer performed additional software acceptance validation and discovered a discrepancy between the two software versions when calculating Seating Torque values for Rotary Valve assemblies with Lever Arm linkage type. An equation in 6.6.000.67 is the cause for the discrepancy. This equation was incorrectly written in code with a lack of an additional set of parentheses to order the execution of mathematical functions correctly. In code writing, this is considered a typographical error. "When FlowScanner 6.6 was in development, there was a need to incorporate a new actuator design into the FlowScanner torque calculations. Because of the design of this actuator, the torque equations and configuration database in FlowScanner required modification. This code was modified on 7 November 2012. FlowScanner 6.6 (build 6.6.000.29) and 6.6 SP1 (build 6.6.000.67) were released subsequent this date and contained the erroneous calculation. Shipments of software were stopped on 30 July 2017 and no shipments took place between 29 June 2017 and 30 July 2017. This code was not transferred to the QUIKLOOK FS software utilized on the QUIKLOOK 3-FS diagnostic system. Thus, this error does not extend into QUIKLOOK FS software. "The equation has been corrected and full-installation CDs will be ready for distribution to affected customers by 1 December 2017. In addition, a Corrective Action Request (CAR 2017-009) has been initiated by Fisher to prevent reoccurrence of this issue. Additionally, Software Error Notice SEN17-01 was created and released to affected customers on 2 August 2017. "Fisher requests that the recipient of this FlN review it and take appropriate action in accordance with 10 CFR 21. If there are any technical questions or concerns, please contact: Guy Scaggs Quality Manager Emerson Automation Solutions Fisher Lifecycle Services 757 Old Clemson Rd Columbia, SC 29229 Phone: (803) 462-6203 Guy.Scaggs@Emerson.com "Appendix A - List of Affected Equipment Table 1: FlowScanner 6000 Safety Related Orders with V6.6 Supplied FISHER CONTROLS INTERNATIONAL - Marshalltown EXELON POWERLABS LLC - COATESVILLE FLORIDA POWER AND LIGHT CO - SEABROOK STATION NEXTERA ENERGY - DUANE ARNOLD Table 2: Stand Alone Software Orders- Safety Related V6.6 DOMINION NUCLEAR CONNECTICUT INC. - Millstone Power Station OMAHA PUBLIC POWER DISTRICT - Fort Calhoun Nuclear Station FISHER CONTROLS INTERNATIONAL LLC - Fisher Controls International LLC SOUTHERN CO - Southern Company NEXTERA ENERGY POINT BEACH LLC - Point Beach Nuclear Plant "Appendix B - Decision Tree for Applicability How to determine if this FIN applies to you: Are you using FlowScanner 6.6 or 6.6 SP1? If 'YES', do you use FlowScanner 6.6 or 6.6 SP1 to complete a 'Dynamic Scan' test on rotary valves with lever arm linkages? Such as any TAG configured with 'LEVER ARM' in the 'Linkage Type' field for example Fisher Types 1052, 2052, and 1061 If 'YES', do you manually select the significant points for Seating Torque and Break Out Torque from the 'Dynamic Scan' test? If 'YES', do you use the Seating Torque result value provided by FlowScanner for any qualification, validation, or acceptance activities? If you answered 'NO' to ALL of these questions, this software error does not affect your usage of the FlowScanner 6.6 or 6.6 SP1 software. If you answered 'YES' to ANY of the questions, further evaluation of the affected Seating Torque test results may be necessary. A workaround has been issued to affected customers." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-08-28
52934 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2016-04-25 21:17 | 2017-08-28 14:47 | 2017-08-28 | PART 21 REPORT - RELAY FAILURE DUE TO OPEN COIL "Pursuant to 10 CFR 21, this is a non-emergency notification by Nebraska Public Power District (NPPD) concerning a defect in an Allen-Bradley 700DC-P220Z2 relay received at Cooper Nuclear Station. "On August 28, 2017, NPPD completed a 10 CFR 21 evaluation of a condition that was identified on April 25, 2016, associated with an Allen-Bradley 700DC-P220Z2 relay delivered by NuTherm. The evaluation was performed to determine the applications where the relays were approved for installation, where they were installed in the plant, and determine if the failure of the relays could result in a Substantial Safety Hazard as defined in 10 CFR 21. "A model 700DC-P220Z2 relay failed after 133 hours of service. An independent laboratory determined the relay contained a wound wire fault at the beginning of the spool near the spool edge. The wire that faulted was connected to the right coil terminal. The fault was at a stress point where the wire came out of the insulating material channel and started onto the spool. Continuity testing indicated that the wire was open between the fault area and the terminal, within the potting material. The relay failure was a case of component infant mortality. It appeared the fault was caused by a manufacturing flaw that likely occurred due to a tensioning issue at the start of the coil wire winding process. "This deviation presents a Substantial Safety Hazard as defined in 10 CFR 21, as this relay model was approved for use in safety related applications. The relay that failed was installed in the starter for the HPCI auxiliary lube oil pump and caused the HPCI system to be inoperable. This was reported to the NRC in ENS Notification 51882 at 0154 EDT on April 26, 2016 as a loss of safety function, but was not characterized as a 10 CFR Part 21 issue at that time. The relay model was approved for use in numerous HPCI starters and the Recirculation Pump discharge valves." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2017-08-28
52933 | 0 | HENRY FORD HOSPITAL |  |  |  |  | 2017-08-28 07:00 | 2017-08-28 12:39 | 2017-08-28 | RECEIPT OF A CONTAMINATED PACKAGE This incident is being reported under 10CFR20.1906(d) and 10CFR71.87(i). A contaminated package was received from Cardinal Health at approximately 0700 EDT on 8/28/17. The package contained 49.41 mCi of I-131 and had removable surface contamination. The first wipe test exhibited 0.4 microCi/300 sq. cm Tc-99m and the second wipe was 0.25 microCi Tc-99m/300 sq. cm. The interior of the package was not contaminated. The package was isolated pending disposition. Cardinal Health was contacted. Their delivery van and driver were surveyed and exhibited no contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2017-09-05
52932 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-08-28 08:37 | 2017-08-28 10:55 | 2017-08-28 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP "On 8/28/2017 at 0837 [EDT], VC Summer Nuclear Station automatically tripped due to a turbine trip. The turbine trip was caused by the Main Generator Differential Lockout due to a fault on the center phase lightning arrester on the Main Transformer (XTF-001). "There were no complications with the trip. All control rods fully inserted. Balance of Plant (BOP) buses automatically transferred to their alternate power source XTF 31/32. All Emergency Feedwater pumps started as required. All systems responded as required. The plant is stable in Mode 3. Station personnel are investigating the cause of the fault on the main transformer lightning arrester. "This event is reportable per 10 CFR 50. 72(b)(2)(iv)(B) and 10 CFR 50. 72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." The unit is currently stable in Mode 3 with decay heat removal via the Main Steam to the Main Condenser. The licensee will inform both State and local authorities. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-08-28
52931 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-08-15 22:15 | 2017-08-25 15:32 | 2017-08-25 | AGREEMENT STATE REPORT - STUCK SOURCE The following was received from the State of Louisiana via email: "[On] 08/16/2017, [at] 1315 [CDT], [the RSO for Turner Specialty Services] called the Radiation Section of LDEQ [Louisiana Department of Environmental Quality] to report a source retrieval that occurred on 08/15/2017 [at] 2215 [CDT] at SALSOL CHEMICALS. The report was forwarded to the inspection staff on 08/17/2017. "The camera was being setup initially to be used on this temporary jobsite at the Chemical Plant. The equipment evaluation and jobsite was being prepared for the radiographic exposures. The exposure device mis-connect/disconnect incident happened on the initial exposure crankout. The source remained in the collimator until the source could be manually returned to the shielded position. The equipment is a QSA Global Exposure device, Model 880 Delta, S/N D6149 loaded with 61.2 Ci Ir-192 source. The source is an AEA Technology Model A-424-9. "This licensee is approved for source retrievals under their O&E Safety Procedures. The RSO and associates were able to return the source to the shielded position with minimal personnel exposures. A retrieval crew was assembled and they were able to retrieve the source and return it to the shielded position. After the source was in the shielded position, a Go/NoGo test and a misconnect test were performed on the controls and exposure device. Two radiographers and a site RSO conducted the retrieval activities. The retrieval process was safely completed later on the night of 08/15/2017. The individuals involved in the retrieval were wearing Instadose Personnel monitors that recorded exposures of [approximately] 250 mRem. The source assembly was sent to QSA Global, Inc. for further evaluation. Any adverse results of the evaluation will be forwarded as additional information. "There was no threat of radiation exposures to the SALSOL CHEMICALS employees or any adverse threat to the Health and Safety to the general public." Event Report ID No.: LA170013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-09-04
52930 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-08-25 15:27 | 2017-08-25 16:44 | 2017-08-31 | SAFEGUARDS REPORT Due to inclement weather, a vulnerability existed which could have allowed access to a protected area for which compensatory measures had not been employed. The licensee will notify the NRC Resident Inspector and the Matagorda County Sheriff's Department. * * * UPDATE ON 08/31/17 AT 2050 EDT FROM BILLY HERZOG TO BETHANY CECERE * * * At 1938 CDT on 8/31/17, security measures were re-established. The licensee has contacted the Matagorda County Sheriff's Department. The licensee will notify the NRC Resident Inspector. Notified the R4DO (Gaddy) and 73.71 Safeguards Group (by email). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-08-25
52929 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-08-24 | 2017-08-25 16:02 | 2017-09-05 | AGREEMENT STATE REPORT - DAMAGED PACKAGING - SOURCE INTACT The following was received from the State of Illinois via email: "The corporate RSO [Radiation Safety Officer] for [common carrier] contacted the agency [Illinois Emergency Management Agency] at approximately 1300 [CDT] on August 25, 2017 to notify that last night (August 24, 2017) a Type A package containing 140 GBq of high dose rate brachytherapy lr-192 seeds had suffered physical damage at a [common carrier] facility in South Holland, IL. The package was en route from Community Hospital in Munster, IN to an out of state site for Alpha Omega and shifted during transit. The impact resulted in a cracked rim of the Type A package; however, there was no loss of contents, contamination, or exposure to personnel. Exposure rate surveys verified package contents but no contamination surveys were completed. The incident is being reported to the National Response Center concurrently." Item number: IL177027 National Response Center Incident Report # 1188386 * * * UPDATE ON 9/5/17 AT 1142 EDT FROM ROY PARKER TO BETHANY CECERE * * * This update is to correct the title of the original event report from "Damaged Source" to "Damaged Packaging - Source Intact" to better reflect the source integrity status. Notified R1DO (Dentel), R3DO (Stone), and NMSS Event Notification (by email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2017-09-04
52928 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2017-08-24 15:15 | 2017-08-25 15:20 | 2017-08-25 | AGREEMENT STATE REPORT - CONTAMINATION RESULTING FROM Y-90 SETUP The following was received from the State of Kansas via email: "During Therasphere setup, a technician forgot to prime the syringe and inserted it into the vial of Y-90. She realized the syringe was not primed, but because the syringe cannot be removed, her attempt at priming it opened the vial inadvertently. It got tracked all over the room and to some extent all around the Interventional Radiology (IR) department. IR is now completely closed. She was put in a bunny suit immediately and sent to emergency to get deconned at the shower. There was no risk of internal contamination due to the rapidity of the decon after the incident. Highest contamination is at 90k on her scrubs. Most of the contamination was on her lead apron. The clothes are currently sequestered and lacking skin contamination, she was sent home. They are currently in the process of cleaning up and recovering to get IR back in business. "An investigator will be sent on Monday to gain first-hand knowledge of the incident. The RSO and ARSO were at a conference, arriving home last night, and were not present during the incident. "Reporting under 10 CFR 30.50(b) (corresponding to K.A.R. 28-35-184b in Kansas Annotated Regulations), area closed to workers and public for more than 24 hours due to an unplanned contamination." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2017-09-04
52927 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2017-08-25 11:15 | 2017-08-25 14:42 | 2017-08-25 | OFFSITE NOTIFICATION DUE TO EXCEEDING CHLORINE EFFLUENT LIMIT "On August 24, 2017 a malfunction internal to the River Water Chemistry Control System resulted in measurable free available chlorine levels over a one-hour period at the station outfall to the Susquehanna River. The chlorine levels exceeded the station NPDES [National Pollutant Discharge Elimination System] permit effluent limitations. The River Water Chemistry Control System was shutdown until the condition is corrected. "The concentrations released did not threaten the downstream users or the environment. Pennsylvania Department of Environmental Protection was notified of the NPDES non-compliance on August 25, 2017 at 1115 [EDT]. "Pursuant to 10 CFR 50.72(b)(2)(xi), this notification satisfies the requirement to notify the NRC of the occurrence of any event or situation related to the health and safety of the public or onsite personnel, or protection of the environment, for which notification to the other government agencies has been made. "The NRC Resident Inspector has been notified." Notified DOE, EPA, USDA, HHS, and FEMA. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-08-25
52926 | 0 | ELEKTA |  |  |  |  | 2017-07-13 | 2017-08-25 11:47 | 2017-08-25 | PART 21 NOTIFICATION - ONCENTRA SOFTWARE PROBLEM MAY CAUSE UNINTENDED STEP SIZE DURING BRACHYTHERAPY TREATMENT On July 13, 2017, a user in France notified Elekta that they discovered a software issue during their Quality Assurance audit of Elekta's Oncentra Brachy software. Elekta investigated and determined a software issue exists in Oncentra software versions 4.5, 4.5.1, and 4.5.2. On August 11, 2017, Elekta issued an important field safety notice (IFSN) worldwide. The software issue will be resolved in the next issued version of the Oncentra software. See related NRC event numbers 52922 and 52914. Elekta point of contact: Debra Bensen, RSO, debbie.bensen@elekta.com or (770) 670-2518. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-08-25
52925 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-08-24 18:00 | 2017-08-24 22:09 | 2017-08-25 | NORTH CAROLINA AGREEMENT STATE REPORT - MISSING PORTABLE NUCLEAR GAUGE The following information was obtained from the state of North Carolina via email: "North Carolina Radioactive Materials Branch (RMB) was notified on 8/24/17 at 7:58 PM [EDT] that a portable nuclear gauge went missing at around 6:00 PM at a job site at Ten-Ten Road in Garner, NC 27603. "Licensee: ECS Southeast, LLP License Number: 092-0253-1 Gauge Manufacturer: Instrotek Xplorer Model #: 3500 Serial #: 3194 "The gauge contains 11 milliCuries of cesium-137 and 44 milliCuries of americium-241: beryllium. The gauge was not trigger locked and not locked in its original carrying case at the time it went missing. RMB is investigating the incident and working with local authorities to develop a press release. Local law enforcement and the FBI have been notified. Follow-up information will be provided to the NRC as this investigation is ongoing." * * * UPDATE AT 1058EDT ON 08/25/17 FROM TRAVIS CARTOSKI TO S. SANDIN VIA EMAIL * * * "NC Radioactive Materials Branch (RMB) would like to report that the missing gauge has been found this morning 8/25. Three members of the RMB were dispatched last night to initiate an investigation and reconvened this morning to continue. The gauge appeared to have no damage and is being returned to the manufacturer for verification. Surveys were taken on and around the gauge once it was found and all surveys appeared normal indicating the sources were still intact within the gauge. "Through interviews of personnel on-site, it was determined that source rod was never extended from when the gauge went missing to when it was found. An on-site construction worker found the gauge unattended yesterday afternoon and secured it until this morning. "RMB is continuing its investigation from a compliance stand point. Further details will be provided to satisfy the details of this incident following conclusion of this investigation." Notified R1DO (Kennedy) and NMSS Events Notification and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-09-01
52924 | 0 | FORT CALHOUN | 1 |  |  | (1) CE | 2017-08-24 15:40 | 2017-08-24 17:36 | 2017-08-24 | SAFEGUARDS REPORT - DISCOVERY OF A POTENTIAL VULNERABILITY THAT WOULD RESULT IN UNMONITORED PROTECTED AREA ACCESS The licensee discovered a potential vulnerability that, given the right environmental conditions, would result in unmonitored access to the Protected Area. No current vulnerability exists due to current environmental conditions. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-08-24
52923 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-08-23 16:00 | 2017-08-24 12:19 | 2017-08-24 | AGREEMENT STATE REPORT - LOST SOURCE FROM A DENSITY GAUGE The following information was received via E-mail: "Eagle US 2 LLC in Lake Charles (formerly Westlake Chemicals) called to say they lost a Cs-137 source from a density gauge at 1600 [CDT] Wednesday, August 23, 2017. At purchase, the source was 200 mCi. The source is no longer in the device holder/housing. They surveyed for it and have not located it yet. They are continuing to search for it. Source housing is Ronan Model # SAIC10 and Source Serial Number is Ronan # 9527GG." Louisiana Event Report ID No.: LA20170014 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-09-01
52922 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-08-08 | 2017-08-24 06:53 | 2017-08-24 | PART 21 REPORT - ONCENTRA BRACHY SOFTWARE ERROR The following is excerpted from a report received from the Georgia Department of Natural Resources: On August 8th, a patient was undergoing a gynecological treatment using a ring applicator with the microSelectron HDR utilizing Oncentra Brachy Software version 4.5.2. On the 2nd of a 4 fraction treatment of ring and tandem, a mistreatment occurred due to inconsistent step size when treating the ring source path. A source step size of 2.5 mm was planned. What was reported in the case explorer was a 5 mm step size. This plan was sent to the TCS [Treatment Control System] and delivered at a 5 mm steps size. It was intended to treat specific areas, but the delivered areas were 2.5 mm - 60 mm different than intended. This was confirmed using gafchromic film on a QA plan after treatment was completed. This event was reported by the State of Mississippi - see related EN 52914. Elekta identified that this issue occurs when using Applicator Models with a measured source path in combination with a specific afterloader configuration, as follows: Oncentra Brachy - Version 4.5, 4.5.1, 4.5.2, Applicator Modeling with a measured source path, RDStore default step size 5.0 mm, 10.0 mm Afterloader - microSelectron HDR/PDR V2, V3/Digital Applicators - Ring Applicator Sets, Ring CT/MR Applicator sets, Interstitial CT/MR Rings, Vienna CT/MR Rings, Advanced Gynecological Applicator - Venezia with Lunar-shaped ovoids In Elekta bulletin [IFSN 806-01-BTP-001] the Ring applicator will be used to represent all applicable applicators. Where ring is mentioned also lunar-shaped ovoids apply (Advanced Gynecological Applicator). Where 5.0 mm is used as a default step size this could also be 10.0 mm. Oncentra Brachy incorrectly handles the placement of the ring applicator models with the measured source path in combination with the microSelectron treatment unit, for which the default step size differs from 2.5 mm. Three other facilities previously reported this issue and the manufacturer had started working on a bug fix and field notification. All other cases found the issue during QA, so no patients were involved. Veenendaal has put a stop to the delivery of the Applicator Modeling until the Oncentra Brachy v 4.5.3 is released. An Important Field Safety Notification was sent to all customers concerning the use of ring source paths with applicator modeling on 8/11/17 (IFSN 806-01-BTP-001 attached). An Oncentra Brachy patch is in process to fix this safety issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-08-28
52921 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-08-23 03:40 | 2017-08-23 10:51 | 2017-08-23 | LOSS OF OFFSITE TELEPHONE LINES "At approximately 0340 CDT on Wednesday, August 23, 2017, Grand Gulf Nuclear Station was notified by the Entergy System Dispatcher that the NRC had called them and told them that the NRC could not contact Grand Gulf on the Emergency Notification System (ENS) line nor commercial telephone. Control Room personnel immediately tested several offsite lines including the NRC ENS line and found the lines were non-functional. "Offsite prompt Public Warning Sirens were available at all times. State and Local notification capability was available via UHF radio communication. GGN Emergency Response Organization notification capability was available at all times via satellite phone activation of group paging. GGN site Emergency Response Facility intercommunications were available at all times via site internal telephones. In-plant and offsite team communications were available at all times via UHF radio. "This event is being reported (8-hour notification) as an event or condition that adversely impacted offsite communications in accordance with 10 CFR 50.72(b)(3)(xiii), specifically the loss of the NRC Emergency Notification System (ENS). "The phone company has been contacted and actions are being taken to restore normal communications capability at this time. "The NRC Resident Inspector has been notified." * * * UPDATE AT 1701 EDT ON 08/23/17 FROM LEROY PURDY TO JEFF HERRERA * * * At 1701 EDT on 8/23/17 the phone systems at Grand Gulf have been restored. The licensee will be notifying the NRC Resident Inspector. Notified the R4DO (Farnholtz) | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-08-24
52920 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2017-08-22 09:30 | 2017-08-23 10:45 | 2017-08-23 | AGREEMENT STATE REPORT- MEDICAL EVENT MISADMINISTRATION This following report was phoned in, followed by an email: "On August 22, 2017, Chesapeake Urology, notified the Maryland Radiological Health Program (RHP) that a male patient was injected with 176.1 microCuries of Ra-223 (Xofigo) instead of 108.4 microCuries of Ra-223 (Xofigo); 62.5 percent greater than the prescribed dose. The wrong unit dose was handed to the authorized user for patient administration. The event occurred at approximately 0930 [EDT] hours on 08/22/2017 at the licensee's address of 21 Crossroads Drive, Suite 200, Owings Mills, MD 21117. Maryland RHP was notified by telephone at 1505 hours. Two patients were scheduled for treatment on August 22, 2017. Both doses were assayed in the morning. Each dose had the proper patient name on the lead pig and on each respective syringe. The incorrect dose was selected and injected without cross referencing the identity of the patient. The event was discovered at approximately 1130 hours when the second Xofigo dose was to be administered. The patient and the referring physician have been informed of the misadministration. A written notification from the licensee is expected in about a week. This is a preliminary notification." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2017-08-31
52919 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-08-20 21:08 | 2017-08-21 05:30 | 2017-08-23 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO NON-FUNCTIONAL TSC VENTILATION "On August 20, 2017 at 2108 hours CDT, Byron Station Technical Support Center (TSC) ventilation system supply fan (0VV23C) was identified as non-functional. This failure affects the ability of the TSC ventilation system to maintain adequate radiological habitability in the event of an emergency with an airborne radiological release. All other capabilities of the TSC are unaffected by this emergent condition. Currently troubleshooting/investigation is being performed. This condition is considered a major loss of emergency assessment capability and is reportable under 10CFR50.72(b)(3)(xiii). If an emergency is declared requiring TSC activation during this period, the TSC will be staffed and activated using existing emergency planning procedures. If the TSC becomes uninhabitable, the Station Emergency Director will relocate the TSC staff to an alternate TSC location in accordance with applicable procedures. "This notification is being made in accordance with 10CFR50.72(b)(3)(xiii) due to the potential loss of an emergency response facility because of the unavailability of the ventilation system. An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATE FROM JOHN CONROY TO HOWIE CROUCH AT 1504 EDT ON 8/23/17 * * * TSC ventilation was returned to service at 1150 CDT on 8/23/17. The licensee has notified the NRC Resident Inspector. Notified R3DO (Dickson). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-08-21
52918 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-08-20 16:05 | 2017-08-20 22:46 | 2017-08-24 | MANUAL REACTOR SCRAM DUE TO A RISE IN MAIN CONDENSER BACK PRESSURE "On August 20, 2017 at 1605 PDT, Columbia Generating Station was manually scrammed from 100 percent power due to a rise of Main Condenser back pressure. Manual scram of the unit is procedurally required upon a loss of Main Condenser back pressure. Preliminary investigations indicate that the Main Condenser air removal suction valve (AR-V-1) closed, resulting in the Condenser back pressure rising to within 1.0 inch Hg of the setpoint with reactor power greater than 25 percent. Further investigations continue. All control rods fully inserted. "In addition to the closure of the air removal suction valve, one of two Reactor Feedwater startup flow control valves did not adequately operate to control Reactor vessel level and resulted in a high-level (Level-8) actuation tripping the Reactor Feedwater System. All other systems operated as expected. Reactor water level is currently being controlled manually with the start-up level control isolation valve. AR-V-1 has been manually opened with a jumper and temporary air supply. Reactor decay heat is being removed via bypass valves to the Main Condenser. "This event is being reported under the following: 10 CFR 50.72(b)(2)(iv)(B), which requires a four-hour notification for any event or condition that results in actuation of the Reactor Protection System when the reactor is critical." The licensee notified the NRC Resident Inspector. The licensee plans to issue a press release. * * * UPDATE ON 8/24/17 AT 1937 EDT FROM MATT HUMMER TO DONG PARK * * * "The licensee is updating the notification to include an 8 hour notification under 10 CFR 50.72(b)(3)(iv)(A) for a specified system actuation due to a Level 3 isolation signal which occurred approximately 20 minutes after the scram. The licensee is currently in cold shutdown to repair the Reactor Feedwater startup flow control valve. "The licensee has notified the NRC Resident Inspector." Notified R4DO (Farnholtz). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-08-20
52917 | 0 | WASHINGTON UNIVERSITY |  |  |  |  | 2017-08-18 14:00 | 2017-08-19 16:14 | 2017-08-19 | MEDICAL EVENT - Y-90 THERASPHERES ADMINISTERED TO THE WRONG LIVER LOBE "A medical event occurred on 8/18/2017 when Y-90 TheraSpheres meant for treatment of the patient's left liver lobe were administered to the patient's right liver lobe. The patient treatment plan was for radioembolization of the left lobe of the liver on 8/18/17 and radioembolization of the right liver lobe approximately one month later. The interventional radiologist (IR) and radiation oncologist authorized user (AU) signed off on planning activity for the left lobe via the left hepatic artery on 8/2/17 and 8/3/17, respectively. The AU completed the 8/18/17 written directive to deliver 124 Gy to the left lobe via the left hepatic artery (LHA). The IR placed the catheter for treatment in the right hepatic artery which supplies the right liver lobe. The AU, medical physicist and radiation technologist came to the procedure room. A time out procedure was done asking all parties to confirm 124 Gy to the left lobe via the LHA. The IR gave a verbal affirmation of this plan. The IR discovered the error when reviewing patient notes following the procedure. He immediately notified the AU who then notified the Radiation Safety Officer (RSO). The AU estimated dose to the right lobe to be 63 Gy. The RSO continues investigating the event. The patient and the referring physician were notified of the medical event." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 35.3045(a)(3) |  |  |  | 0 | 2017-08-28
52916 | 0 | NIST |  |  |  |  | 2017-08-18 14:00 | 2017-08-19 12:07 | 2017-09-08 | UNPLANNED CONTAMINATION EVENT - BROKEN FLAME-SEALED GLASS AMPOULE "The purpose of this communication is to provide additional details surrounding the circumstances that led to the identification of unplanned contamination in one of the laboratories designated as a restricted area under the US NRC license SNM-362. As indicated verbally during the initial report at 1207 EDT, and required by 10 CFR 30.50(b)(1), this event is described as having a broken flame-sealed glass ampoule that resulted in contamination of the lead-shielding storage area on top of the countertop and other surfaces within room C11 in building 245 of the NIST Gaithersburg, MD campus. This was discovered at approximately 1400 EDT on 8/18/2017. "The ampoule contained a well-characterized solution of Am-241 with an activity of approximately 47 MBq (most restrictive ALI [Annual Limit on Intake] is 0.006 uCi) and is registered in our database as being in a solution of nitric acid. "The initial report requirements of 10 CFR 30.50(b)(1)(i) through (iii) are satisfied by the phone notification and supplemented by this communication and attachments. Additional information regarding corrective actions taken and planned, as well as evaluations and/or assessments, will be provided to our Project Manager and Region I in the near future and the required written report will be provided within the required 30 days. "After reporting event #52916, at the direction of the Radiation Safety Officer and with the support of the NIST Senior Management, multiple efforts will continue to evaluate the extent of the condition and a Stop Work Order will be issued effective today for all other laboratories at NIST Gaithersburg that store similar ampoules until the extent of condition is evaluated and/or mitigated. "Extensive surveys of the area and air monitoring have confirmed that the contamination is isolated to portions of room C11." Access has been restricted to room C11. The licensee notified NRC R1 (Ullrich) and NRC HQ PM (Naquin) regarding this event. * * * UPDATE FROM MANUEL MEJIAS TO HOWIE CROUCH AT 1209 EDT ON 9/6/17 * * * The licensee received three bioassay results from personnel exposure to the contaminant. Two of the bioassays were negative. The third bioassay indicated the exposed individual received 9.1 REM whole body with 87 REM to the bone surface of the target organ. Additional bioassays are being performed. The licensee notified R1 (Ullrich and Jackson) and HQ (Naquin). Notified R1DO (Dentel), NMSS (Rivera-Capella), and NMSS Events Notification (email). * * * UPDATE AT 1838 EDT ON 09/08/17 FROM MANUEL MEJIAS TO S. SANDIN * * * "The purpose of this communication is to provide additional details regarding Event # 52916 as results of radiological surveys, interviews, and bioassays are obtained. As indicated verbally during the NRC Ops Center phone update today at 18:38 EDT, new survey and interviews information have led us to believe that ingestion was a possible pathway for the individual that had a positive bioassay. Given the difference in the intake retention fraction (IRF) for ingestion versus inhalation pathway, we have performed additional calculations of the previous bioassay results. These calculations have identified the potential for a total effective dose equivalent of 25 rem or more. "Given the potential for dose of 25 rem or more, consultation was done with the REAC/TS team. Additional bioassays and medical evaluation will be performed. "A courtesy notification was provided earlier today to R1 (Ullrich) and HQ (Naquin)." Notified R1DO (Dentel), NMSS (Collins) and INES Coordinator (Rivera-Capella), INES National Officer (Milligan) via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR | 30.50(b)(1) |  |  |  | 0 | 2017-08-28
52915 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-08-18 20:55 | 2017-08-18 23:41 | 2017-08-18 | AUTOMATIC SCRAM WHILE AT 100 PERCENT POWER "At 2055 CDT on August 18, 2017, an automatic actuation of the reactor protection system occurred while the plant was operating at 100 percent power. No plant parameters requiring the actuation of the emergency diesel generators or the emergency core cooling system were exceeded. The main feedwater system remained in service following the scram to maintain reactor water level, and the main condenser remained available as the normal heat sink. "The scram occurred after a planned swap of the main feedwater master controller channels in preparation for scheduled surveillance testing. When the channel swap was actuated, the feedwater regulating valves moved to the fully open position. The scram signal originated in the high-flux detection function of the average power range monitors, apparently from the rapid increase in feedwater flow. "The cause of the apparent feedwater controller malfunction is under investigation. The NRC Resident Inspector has been notified." No safety relief valves opened. Decay heat is being removed via steam to the main condenser using the bypass valves and steam drains. The licensee intends to go to Cold Shutdown to investigate the malfunction. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-08-18
52914 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2017-08-18 | 2017-08-18 17:43 | 2017-10-19 | AGREEMENT STATE REPORT - PATIENT UNDERDOSE The following report was received via e-mail: "The licensee's RSO reported a possible medical event for four separate patients, involving a Nucletron Model microSelectron-HDR 106.990 remote afterloading brachytherapy unit. This was noticed during review by the medical physicist. The licensee notified Elekta for confirmation of the software error. The RSO confirmed on 8/18/2017, that two (2) patients were under dosed by more than 20% and the other two (2) patients were being reviewed by the medical physicist. "An Elekta Notification was sent out to all MS Radioactive Licensees on 8/17/2017, that possess a Nucletron Model microSelectron-HDR." Source: 12 Ci, Ir-192, Elekta Model 105.002 Mississippi Report: MS-170002 * * * UPDATE AT 1649 EDT ON 10/19/17 FROM JASON MOAK TO S. SANDIN VIA EMAIL * * * "Update: 10/18/2017 "Licensee reported four (4) medical events utilizing the tandem and ring applicator model within Elekta's Oncentra Brachy Software version 4.5.2. Licensee written report received, 8/23/2017, for the period between 11/8/2016 and 8/15/2017, stated two of the four patients treated using Nucletron Model microSelectron-HDR 106.990 remote afterloading brachytherapy unit and utilizing the tandem and ring applicator model within Oncentra's Treatment Planning software received a dose less than 20% of the prescribed dose to the treatment site (base of the uterus). All of the treated patients received greater than 50 Rem and 50 percent or more of the dose expected from the administration to unintended tissue (vaginal canal). The written directives called for a prescribed dose of 28 Gy for three patients and 27 Gy for one patient, to be delivered in four (4) separate fractions to the base of the uterus. All four (4) fractions were affected for one patient, three (3) fractions for two patients, and only one (1) fraction for one patient, which received 50 percent or more of the dose expected from the administration. "Patient / Estimated Dose Delivered to Treatment Site / Percent of Intended Dose from Written Directive / Affected Number of Fractions / Expected Range of Doses to Unintended tissue / Estimated Dose to Unintended Tissue "Patient A / 18.44 Gy / 65.84 % / 4 / 126 cGy and 175 cGy per treatment fraction / > 28 Gy "Patient B / 21.78 Gy / 77.7 % / 3 / 126 cGy and 175 cGy per treatment fraction / > 7 Gy per fraction (total > 21 Gy) "Patient C / 23.39 Gy / 83.55 % / 3 / 126 cGy and 175 cGy per treatment fraction / > 7 Gy per fraction (total > 21 Gy) "Patient D / 26.84 Gy / 99.41 % / 1 / 126 cGy and 175 cGy per treatment fraction / > 14 Gy for one fraction "A software error occurs in the Oncentra Treatment Planning Software version 4.5.2, whenever the built-in tandem and ring applicator model is used. The microSelection afterloader step size of a measured source path is 2.5 mm. An override to the default step size of 5 mm (RDStore), from the step size of the measured source path in the planning software occurred. A change in the source position step size, from 2.5 mm to 5 mm was not realized by the licensee for the ring catheter but was implemented for the delivery plan. The dose distribution, prescription point values, and dose volume histogram readouts were all based on a 5 mm spaced tandem and a 2.5 mm spaced ring. When the plans were exported to the treatment unit and delivered, the afterloading brachytherapy unit utilized a source step size of 5 mm for both the tandem and ring applicators, thus a discrepancy between the planned and delivered dose distributions occurred. "The licensee has suspended use of the tandem and ring applicator model within the software and will define all catheters for the tandem and ring applicator manually until further notice of Elekta's software correction. "The referring physician and patients have been notified. No adverse health effects were noted for the patients due to the medical events. "Activity: 12 Ci Licensee Authorization "Update: (8.85 Ci - 5.195 Ci) "Date of Incident: 11/8/2016 through 8/15/2017 "List any other actions required of DRH [Mississippi Division of Rad Health]: Licensee notified to send 15-day written report. Elekta Notification, FCA-NU-0004, FCO Reference No. 806-01-BTP-001, was sent out to all MS Radioactive Licensees on 8/17/2017, that possess a Nucletron Model microSelectron-HDR. Licensee's written report received August 23, 2017. "DRH conducted a reactive inspection of the licensee on September 1, 2017, to determine the cause and further clarify the medical events. The medical events were discussed with the licensee's RSO's, medical physicist(s), and the chair of Radiation Oncology on September 1, 2017, and again on October 17, 2017 and October 18, 2017, with the licensee's medical physicist. "Case Closed: Yes "Date Closed: 10/19/2017" Notified R4DO (Vasquez) and NMSS Events Notification via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2017-08-28
52913 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-08-12 | 2017-08-17 17:55 | 2017-08-17 | PART 21 REPORT - RELAY MOUNTING PLATE MOUNTED UPSIDE DOWN "Pursuant to 10 CFR 21, this is a non-emergency notification by Energy Northwest concerning a defect in General Electric (GE) Nuclear HMA124A2 relays received at Columbia Generation Station. "On August 12, 2017, Energy Northwest completed a 10 CFR 21 evaluation of a condition associated with GE Nuclear HMA124A2 relays supplied by GE Hitachi Nuclear Energy Americas, LLC, and intended for use at Columbia Generating Station. The evaluation was performed to determine the applications where the relays were approved for installation, and where they were installed in the plant, and to determine if the failure of the relays could result in a Substantial Safety Hazard as defined In 10 CFR 21.3. "Two of the HMA124A2 relays received had back plates that were mounted upside down, causing the terminals to not match the standard configuration. Although the internal wiring to the physical stud locations was correct, the numbering scheme embossed on the back plate did not match the correct configuration. With the incorrectly mounted back plate, the internal coil of the energizing circuit could be wired to the incorrect portion of the control circuitry, which would not energize when required and could result in the failure of a safety function. This deviation presents a Substantial Safety Hazard as defined In 10 CFR 21.3, as these relays were approved for use in safety related applications; however, there was no actual risk to plant safety since this deviation was recognized and resolved by station craft prior to installation of the relays. This condition is reportable under 10 CFR 21.21(d)(1) as a defect as defined in 10 CFR 21.3. "The defective HMA124A2 relays were installed in the plant in the correct configuration with post-maintenance testing performed to ensure operability of the relays. The remaining HMA124A2 relays were examined and no additional defects were identified. GE Hitachi has been notified of the condition." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEFECTS AND NONCOMPLIANCE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 21.21(d)(3)(i) |  |  |  | 0 | 2017-08-17
52912 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-08-17 12:05 | 2017-08-17 17:24 | 2017-08-17 | ACTUATION OF TURBINE DRIVEN AUXILIARY FEEDWATER PUMP DUE TO LOSS OF 6.9KV SHUTDOWN BOARD "On August 17, 2017, at 1205 Eastern Daylight Time (EDT), the Watts Bar Nuclear Plant (WBN) lost power to the 1B-B 6.9kV Shutdown Board. The loss of power to this safety related bus resulted in an automatic start of the Unit 1 Turbine Driven Auxiliary Feedwater Pump (TDAFWP). The motor driven AFW pumps did not start and were not expected to start for this event. No other system actuations occurred as a result of loss of power to the 1B-B 6.9kV Shutdown Board. Power to the 1B-B Shutdown Board was restored at 1505 EDT on August 17, 2017. "During the loss of power to the 1B-B Shutdown Board, a reduction in containment and control rod drive mechanism cooling occurred. At 1233 EDT, lower containment average temperature exceeded the procedural limitations specified, and Technical Specification 3.6.5 Condition A was entered for containment average air temperature not within limits. Lower containment average temperature was restored to within limits at 1525 EDT on August 17, 2017. This is reportable as a potential loss of safety function. "Other than several common Unit Technical Specifications having not been met, Unit 2 was not operationally impacted by the loss of power to the 1B-B Shutdown Board and remains in Mode 1 at 100% power. "The NRC Resident Inspector has been notified." The loss of power occurred during restoration from Emergency Diesel Generator maintenance. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2017-08-17
52911 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-08-17 14:42 | 2017-08-17 16:48 | 2017-08-17 | NON WORK RELATED ONSITE FATALITY "At 1315 Central Daylight Time (CDT) on 8/17/2017, the South Texas Project Unit 1 Control Room was notified that a contract employee had experienced a non-work-related medical emergency within the Protected Area. The individual was transported to Matagorda Regional Medical Center in Bay City, TX. At 1442 CDT, the Unit 1 Control Room was notified that the patient was declared deceased. "The Occupational Safety and Health Administration (OSHA) will be notified. This notification is being made under 10CFR50.72(b)(2)(xi) as an event for which another government agency is being notified. The deceased individual was not radioactively contaminated. "The NRC Senior Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-08-17
52910 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-08-16 11:30 | 2017-08-17 12:12 | 2017-08-17 | AGREEMENT STATE REPORT - FIXED GAUGE LOST SHUTTER The following report was received via e-mail: "The licensee called to notify the state that during their annual inventory review, they found that one of their Thermo Measure Tech 5192 fixed gauges had lost its shutter. Upon searching, the shutter was later found on the floor. The call to the state was made on August 17, 2017 at 1010 [EDT]. The Radiation Safety Officer stated that surveys were done and that the highest reading around the gauge was less than 0.5 mR/hr. He also stated that a consultant has been called to replace the shutter and to evaluate the damaged gauge and several other gauges throughout the plant. The licensee stated that a written report will be sent within 30 days of the event. Updates to this event will be made through the NMED system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-08-25
52909 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2017-08-16 10:39 | 2017-08-16 15:41 | 2017-08-16 | LOSS OF POWER TO TECHNICAL SUPPORT CENTER "On 8/16/2017, at 1039 [EDT], an un-planned trip of the Peach Bottom Station Blackout Transformer 34.5 kV feeder breaker 1005 and a loss of the 191-00 line occurred causing a loss of power to Unit 1 and the TSC. Power was not restored to the TSC or the ventilation system within 1 hour. Power was subsequently restored to the TSC at 1207 hours [EDT] and the ventilation system was restored to available. "This report is being submitted pursuant to 10CFR50.72(b)(3)(xiii) as a Major Loss of Emergency Preparedness Capabilities due to a reduction in the effectiveness of the Onsite Technical Support Center (TSC). "The NRC Resident Inspector has been informed of this notification." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-08-16
52908 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-08-15 15:13 | 2017-08-15 20:21 | 2017-08-15 | FITNESS FOR DUTY - BLIND SAMPLE RETURNED WITH INACCURATE RESULTS "A blind sample provided from an independent laboratory to fleet testing facility was returned with inaccurate results. This is in violation of 10 CFR 26.719(c)(3) and requires a 24-hour report." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2017-08-15
52907 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-08-14 | 2017-08-15 16:52 | 2017-08-15 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was provided by the State of California via email: "On 08/14/17, RHB [California Radiation Health Branch] received an incident report from Office of Emergency Services regarding a damaged moisture density gauge. A CPN gauge, Model MC-3, S/N M380108935, containing 10 mCi of Cs-137 and 50 mCi of Am-241 was run over by a heavy construction equipment at a job site in the city of Santa Clara, CA. The top of the gauge housing was damaged with a broken rod, however, the user managed to retrieve the source back into shielded position. The damaged gauge was placed in the transport case and taken to the licensee's facility for disposal. Fire department was at the incident site, performed surveys using a survey meter (no survey meter information available) and the readings did not indicate any contamination. According to the gauge user, Fire Department readings indicated 500 uR/hr at the damaged gauge and 6 uR/hr at 15 feet from the gauge. The gauge will be transported to CPN for leak testing and disposal on 08/15/17. RHB will be following up on this incident." California 5010 Number: 081417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-08-23
52906 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-08-14 | 2017-08-15 14:24 | 2017-08-15 | AGREEMENT STATE REPORT - IRRADIATOR SOURCE RACKS INOPERABLE Following a panoramic irradiator two day shutdown, a restart with three source racks commenced. Air pressure was applied to raise the source racks. During the restart, two source racks (racks 1 and 3) did not descend into the irradiator pool as designed. During an investigation, two release valves associated with the two source racks did not operate properly. Operators manually released air pressure and all source racks descended into the irradiator pool. The deficient release valves were replaced and the source racks were satisfactorily retested. The source racks all properly descended into the pool. The time the source racks were inoperable for approximately 1.5 hours. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-08-23
52905 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2017-08-15 11:46 | 2017-08-15 14:07 | 2017-08-15 | DISCOVERY OF NON-CONFORMING CONDITIONS DURING TORNADO HAZARDS ANALYSIS "On August 15, 2017, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornados, Callaway Plant identified a non-conforming condition in the plant design such that specific Technical Specification equipment is considered not to be adequately protected from tornado missiles. "The recirculation lines for all three independent trains of Auxiliary Feedwater (AFW) connect to the Condensate Storage Tank (CST) inside the CST Valve House, which is not a tornado missile-resistant structure. The direct impact by a design basis missile could result in crimping of the recirculation lines, thereby creating the potential to cause damage to the Train A and B Motor-Driven Auxiliary Feedwater Pumps (MDAFPs) and the Turbine-Driven Auxiliary Feedwater Pump (TDAFP) by restricting recirculation flow to less than the design requirements. "This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) for any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, and per 10 CFR 50.72(b)(3)(v) for any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) shut down the reactor and maintain it in a safe shutdown condition, (B) remove residual heat, or (D) mitigate the consequences of an accident. "These conditions are being addressed in accordance with NRC's Enforcement Guidance Memorandum EGM 15-002 and Interim Staff Guidance DSS-ISG-2016-01 [enforcement discretion and interim guidance documents]. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-08-15
52904 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2017-08-15 07:48 | 2017-08-15 08:07 | 2017-08-15 | UNUSUAL EVENT DUE TO FIRE ALARM IN CONTAINMENT On August 15, 2017 at 0748 EDT, an Unusual Event was declared at Millstone Unit 2 due to a fire alarm indication in containment that was unable to be verified extinguished within 15 minutes. Current containment parameters do not indicate an actual fire. A containment entry is planned to verify that there is no fire. Unit 2 continues at 100% power. Unit 3 was unaffected. The NRC remains in Normal mode. The licensee notified the NRC Resident Inspector and State and local government agencies. Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. * * * UPDATE FROM TODD STRINGFELLOW TO DONALD NORWOOD AT 0953 EDT ON 8/15/2017 * * * At 0951 EDT, the Unusual Event was terminated. No signs of an actual fire were present upon containment entry. All alarms are cleared and they are investigating the cause of the alarm. The licensee notified the NRC Resident Inspector and State and local government agencies. Notified R1DO (Gray), NRR EO (Miller), and IRD (Gott). Notified DHS SWO, FEMA Ops Center, DHS NICC. Notified FEMA National Watch and Nuclear SSA via E-mail. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-08-15
52903 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2017-08-14 22:57 | 2017-08-15 04:58 | 2017-08-15 | SECONDARY CONTAINMENT MOMENTARY LOW VACUUM "On August 14th, 2017 at 2257 [EDT], while shutting down the Annulus Exhaust Gas Treatment System (AEGTS) Train B, secondary containment pressure momentarily lowered. This resulted in the Technical Specification (TS) for Secondary Containment to not be met for 15 seconds. The minimum Secondary Containment vacuum observed during that time was 0.52 inch of vacuum water gauge. "Secondary Containment pressure was returned to within the TS operability limit of 0.66 inch of vacuum water gauge (TS SR 3.6.4.1.1) by the AEGTS Train A that remained in operation. There were no radiological releases associated with this event. "Declaring Secondary Containment inoperable is reportable under [10 CFR] 50.72(b)(3)(v)(C) & (D) for an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to:(C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-08-15
52902 | -1 | MICRON TECHNOLOGY, INC. |  |  |  |  | 2017-08-14 | 2017-08-14 15:30 | 2017-08-15 | TWO NUCLEOSTAT IONIZER BARS IDENTIFIED MISSING Two NRD Nucleostat Ionizer Bars were determined to be missing after a search of metal recycling, potential other locations, and an inventory. The two NRD Nucleostat Ionizer Bars were identified to be missing from a shipment that was received on July 31, 2017. This shipment contained one of the three expected NRD Nucleostat Ionizer Bars. The licensee stated that the area where the cardboard boxes are broken down and stored still remains to be searched. The licensee stated that the local metal waste disposal facility was contacted regarding the event and will be contacting the local landfill regarding the issue. Device Information: NRG Nucleostat Ionizer Bars Part Number: P-2001-006 Serial Numbers: A2LA345 and A2LA347 Activity: 14.06 milliCuries of Po-210 * * * RETRACTION AT 1247 EDT ON 08/15/17 FROM ASHLEY KUNZ TO JEFF HERRERA * * * At 0900 MST on 8/15/2017 the two devices were found intact. A team of Emergency response technicians and site services janitorial members searched the remaining area containing broken down cardboard boxes. The two devices were placed into a locked area pending review by the manufacturer prior to being placed into use. Because the devices were found intact, this event is being retracted. Notified the R4DO(Farnholtz), NMSS Events, ILTAB and CNSC (via email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-08-22
52901 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2017-08-14 14:28 | 2017-08-14 15:23 | 2017-08-14 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures had not been employed. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2017-08-14
52900 | -1 | NIST |  |  |  |  | 2017-08-14 14:54 | 2017-08-14 14:54 | 2017-08-16 | MATERIAL IDENTIFIED LOST AFTER INVENTORY The NIST (National Institute of Standards and Technology) determined that 24.9 microCuries of Cf-252 is being considered lost after performing an examination of inventory records. The missing material was identified during a leak test conducted on Wednesday August, 9, 2017. After identification of the missing material, NIST performed a physical inspection of all laboratories and examined physical inventory records. NIST has identified that there is a potential for this material to have been shipped to the Department of Energy and is still awaiting a response to verify that information. NIST has performed a courtesy notification to the NRC R1 (Ullrich) and PM (Naquin) regarding this incident. * * * RETRACTION AT 1631 EDT ON 8/16/2017 FROM MANUEL MEJIAS TO MARK ABRAMOVITZ * * * "The purpose of this communication is to provide additional details surrounding the circumstances that have led to location of the Cf-252 source reported as missing under 10CFR20.2201(a)(i) at 14:54EDT on 8/14/2017. A call to the Ops Center was made today at 16:31EDT. The purpose of the call was to retract Event #52900 after successfully locating the source with NIST unique identifier number RS75-0086 (known by the Department of Energy as NS-86). The source was located inside a restricted area, the same room where the empty storage container was located. "After reporting event #52900, at my direction as Radiation Safety Officer and with the support of NIST Senior Management, multiple efforts were started to investigate the probable disposition of the source (also as directed by 10CFR20.2201(b)(iii)). During those efforts, all records for shipments of Cf-252 were reviewed and colleagues at the DOE were contacted to exhaust the possibility that the material had been transferred out of NIST. Having no record of the source departing the facility, a new round of radiological surveys was started of the restricted facilities where the source had been previously authorized. After removal of all other neutron-emitting shielding containers from the immediate area, a residual field of neutron radiation was detected. This seemed indicative of the presence of a source. At this time it was observed that a radioactive source was outside of the storage containers. This source is/was of very small dimensions [approximately one inch in diameter]. The source matched the description and nearby was found the hazards information tag that corresponded to RS#75-0086. "Given that the source was always in a restricted area with low-occupancy, we have determined that no hazards to individuals have resulted from this source misplacement." Notified ILTAB (Ahern), R1DO (Gray), and NMSS Events Resource (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2017-08-22
52899 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2017-08-11 20:35 | 2017-08-11 22:35 | 2017-08-11 | INTRODUCTION OF CONTRABAND INTO PROTECTED AREA "The actual introduction of contraband into a protected area." The licensee did not change security posture as a result of this situation. The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-08-11
52898 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-08-11 11:24 | 2017-08-11 16:12 | 2017-08-11 | COMANCHE PEAK AUTOMATIC TURBINE TRIP FROM 10 PERCENT POWER "At 1124 CDT on 11 August 2017, CPNPP [Comanche Peak Nuclear Power Plant] Unit 2 experienced an automatic turbine trip and trip of both main feedwater pumps on high steam generator water level (P-14, 81.5 percent level) in steam generator 2-02. Following the turbine trip, the auxiliary feedwater system actuated as required. The plant was stabilized at 2-3 percent reactor power with auxiliary feedwater feeding all steam generators with all levels within their normal bands. "The cause of the high steam generator level appears to be a mechanical malfunction of steam generator 2-02 flow control valve bypass valve 2-LV-2163 (SG 2-02 FW BYP CTRL VLV) to close when demanded. Troubleshooting and repair of 2-LV-2163 is in progress. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) for an actuation of auxiliary feedwater. "The NRC Resident Inspector has been notified." | 0 | 3 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Startup | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-08-11
52897 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-08-10 10:34 | 2017-08-10 17:14 | 2017-08-10 | NON LICENSED SUPERVISOR CONFIRMED POSITIVE FOR ALCOHOL A non licensed supervisor confirmed positive for alcohol during a fitness for duty test. The employee's access has been terminated. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.719 |  |  |  | 0 | 2017-08-10
52896 | 0 | REED COLLEGE |  |  |  | 250 KW TRIGA MARK I | 2017-08-09 10:30 | 2017-08-10 16:40 | 2017-08-10 | POTENTIAL TECHNICAL SPECIFICATION VIOLATION "I'm calling under Technical Specification 6.7.2.4 to report a potential Technical Specification violation. The relevant Technical Specifications are 3.2.2 and 3.2.3, specifically related to a non-operational power monitoring channel. Because this channel was inoperable at low powers, the source interlock was not capable of performing its intended function. Potential violations occurred an August 1st, 3rd, and 4th. The condition was identified on August 9th." The licensee notified the NRC Project Manager (Wertz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | OR | NPR | [5 empty] | 0 | 2017-08-10
52895 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-08-09 | 2017-08-10 14:48 | 2017-08-10 | AGREEMENT STATE REPORT - SHUTTER FAILURE DUE TO WATER INTRUSION The following report was received from the Texas Department of State Health Services via email: "On August 10, 2017, the licensee's radiation safety officer notified the Agency [Texas Department of State Health Services] that a fixed gauge (Ohmart Vega, SHLG-2, SN 8551CM, 3000 milliCuries, Cs-137) had a stuck shutter. A repair company was called and the technician completed repairs on the gauge within one day. Shutter failure was from water intrusion in the slide channel causing the shutter to rust and reduce movement. The gauge was cleaned and lubricated. A monthly maintenance procedure will be placed in effect to reduce or eliminate this issue." Texas Incident: I-9503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-08-18
52894 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2017-08-09 16:06 | 2017-08-09 17:35 | 2017-08-09 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN FOR REACTOR COOLANT SYSTEM LEAKAGE "On 8/9/17, a Unit 1 containment entry was made in order to investigate increased Reactor Coolant System (RCS) unidentified leakage. The team noted a through-wall leak from the tubing/socket weld area of 'C' Hot Leg Sample Valve. The sample valve and RCS pressure boundary were declared inoperable, and a 6-hour action statement to place Unit 1 in Hot Shutdown was entered at 1338 [EDT] hours as required by Technical Specification 3.1.C.3. "At 1606 [EDT] hours on 8/9/17, Unit 1 shutdown was commenced, and at 1637 [EDT], Unit 1 was at Hot Shutdown. This report is being submitted pursuant to 10CFR50.72(b)(2)(i) as a result of power reduction required by Technical Specifications. Further, this report is being submitted pursuant to 10CFR50.72(b)(3)(ii)(A) for any event or condition that results in the condition of the nuclear power plant, including its principle safety barriers, being seriously degraded. "The NRC Resident [Inspector] has been notified of this event and is on site. "There was no radiation release associated with this event, nor were there any personnel injuries or contamination events." | 0 | 0 | 0 | 32 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2017-08-09
52893 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2017-08-08 | 2017-08-09 15:27 | 2017-08-09 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED MOISTURE DENSITY GAUGE The following was received from the Maryland Department of the Environment via email: "On August 8, 2017, Hillis-Carnes, Maryland Licensee MD-03-054-01, notified the Maryland Radiological Health Program (RHP) that a field technician had his van carjacked at the Key's Point temporary job site. His Troxler moisture density gauge model 3430 (serial number 31733) was still in the van and locked. The licensee notified Baltimore police. "On August 9, 2017, the Maryland Department of the Environment Emergency Response Division was notified by the Baltimore police that the van and the Troxler gauge were recovered at O'Donnell Heights the evening of August 8. An RHP inspector went to the site and took possession of the gauge and is notifying the licensee so they can retrieve it. "Troxler 3430 has a Cesium 137 sealed source less that 9 milliCuries and a 44 milliCurie AmBe source. No indication of any damage." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2017-08-17
52892 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-08-08 20:44 | 2017-08-08 22:33 | 2017-08-08 | LOSS OF SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "On August 8th, 2017 at 2044 hrs. [EDT] a loss of secondary containment differential pressure (D/P) occurred due to an apparent equipment failure. This caused a reduction in Reactor Building Zone II (Unit 2) D/P to less than the required 0.25 inch WC [water column] per SR [Surveillance Requirement] 3.6.4.1.1. "Reactor Building Zone II Exhaust Fans were manually swapped and Reactor Building Zone II D/P was restored to greater than 0.25 inch WC by 2112 hrs. "Reactor Building Zone 1 (Unit 1) and Zone 3 (Units 1&2) ventilation remained in service and stable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-08-08
52891 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2017-08-08 15:54 | 2017-08-08 20:22 | 2017-08-08 | HIGH PRESSURE CORE SPRAY SYSTEM SUPPRESSION POOL LEVEL INSTRUMENTATION INOPERABLE "On August 8, 2017, at 1554 hours [EDT], during restoration from testing of the High Pressure Core Spray (HPCS) Suppression Pool Level High Instrumentation, unexpected as-left indications were found that impacted both of the required channels of instrumentation. Subsequent venting of the instrumentation lines was completed and both channels of instrumentation are reading consistent with previously taken as-found data. The instrumentation was declared OPERABLE at 1635. The initial cause of the unexpected as-left indications appears to be the introduction of air into the instrumentation lines during the calibration activities. "This is considered a loss of safety function based on both of the HPCS Suppression Pool Level High Instrumentation channels being declared INOPERABLE and the loss of the automatic HPCS suction swap to the Suppression Pool on a high level. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D). The [NRC Resident Inspector] has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-08-08
52890 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2017-08-04 | 2017-08-08 17:12 | 2017-08-08 | AGREEMENT STATE REPORT - Y-90 TREATMENT UNDERDOSE The following information was provided by the State of California via email: "The RSO [Radiation Safety Officer] of Loma Linda Medical Center notified the RHB [Radiologic Health Branch] Brea ICE [Inspection, Compliance and Enforcement] office on August 7, 2017, that a medical event occurred on Friday, August 4, 2017. A patient was admitted to the hospital for treatment of liver carcinoma. The treatment plan involved use of Nordion model TheraSpheres (Y-90 glass microspheres manual brachytherapy) for radio-embolism to the right lobe of the liver. The patient's written directive called for aggregate treatment of 121Gy (5.241 GBq) of Y-90 to the right lobe target area, but only 9.7 Gy (0.420 GBq) was delivered. The overall percent delivery to target tissue was 8.1%. "The patient's lung dose from shunting was 1.01 Gy at 4.8% lung shunting factor. The patient and referring physician were informed of the event on 8/4/2017. The medical event is still being investigated, but is thought that a slow injection flowrate may have caused sedimentation of the microspheres in the delivery system. After a few days for decay, a more intensive review of the delivery system will be conducted." CA 5010 Number: 080417 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2017-08-16
52889 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2017-08-05 22:35 | 2017-08-06 00:26 | 2017-08-06 | AUTOMATIC REACTOR SCRAM DURING TESTING "At 2235 [EDT] Nine Mile Point Unit 2 experienced an automatic scram on high reactor pressure. Turbine stop valve testing was in progress at the time of the scram. All control rods inserted. Pressure control is via the turbine bypass valves. The cause of the scram is being investigated. "This is a 4-Hour report for 10CFR50.72(b)(2)(iv)(B) RPS [Reactor Protection System] Actuation. "The NRC Resident Inspector has been notified." Reactor water level is being maintained with normal feedwater flow. No safety or relief valves lifted. The plant is in its normal shutdown electrical lineup. | 0 | 0 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-08-06
52888 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2017-08-04 15:11 | 2017-08-04 17:25 | 2017-09-27 | SECONDARY CONTAINMENT INOPERABLE DUE TO OPENING IN SERVICE WATER PIPING "On August 4, 2017, at 1511 EDT, Unit 1 Secondary Containment was declared inoperable due to a small (i.e., approximately 0.75 inch diameter) hole in Service Water system piping which was found during ultrasonic testing activities. The affected portion of piping penetrates Secondary Containment and flow in the piping creates a vacuum condition; thus bypassing Secondary Containment. The identified hole is being evaluated with respect to its impact on operability of the Service Water system. "This condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(C), as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "This event did not result in any adverse impact to the health and safety of the public. "Initial Safety Significance Evaluation: The initial safety significance of this event is minimal. At the time of discovery, Unit 1 was at 100% steady state conditions. Reactor Building Ventilation was in service in a normal alignment. No abnormal radioactivity conditions existed within Secondary Containment. "Corrective Actions: Temporary repair of the affected Unit 1 Service Water piping has been completed. This repair was evaluated by Engineering and it has been determined that the repair meets the requirements to maintain Secondary Containment operable. Unit 1 Secondary Containment operability was restored at 1704 EDT on August 4, 2017." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM MIKE BRADEN TO RICHARD SMITH AT 1447 EDT ON 9/27/17 * * * "Based upon further evaluation, Duke Energy is retracting Event Notification 52888. The safety objective of Secondary Containment is to limit the release of radioactivity to the environment after an accident so that the resulting exposures are kept to a practical minimum and are within regulatory limits. A bounding engineering evaluation was performed which demonstrates that potential releases from Secondary Containment could not have resulted in offsite or control room doses exceeding regulatory limits. Furthermore, the condition did not impact Technical Specification operability of Secondary Containment in that the ability of Secondary Containment to maintain the required vacuum was not impacted. Therefore, this condition does not represent an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and is not reportable in accordance with 10 CFR 50.72(b)(3)(v)(C), and the event notification is being retracted." The NRC Senior Resident was notified of this retraction. Notified R2DO (A. Masters). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-08-04
52887 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-08-04 | 2017-08-04 17:24 | 2017-08-04 | AGREEMENT STATE REPORT - UNDERDOSE TO PATIENT The following information was received via E-mail: "The licensee's RSO reported an event that resulted in an underdose to the patient. At 1215 CDT on August 4, 2017, licensee staff were administering a 40.4 mCi dose of Y-90 microspheres to the patient. The preliminary finding is that the patient took a deep inspiration which moved the base catheter and possibly changed its position or created a kink in the catheter. The first 3-4 aliquots were delivered before the plunger met resistance and the procedure aborted. The licensee estimates that 21.5 mCi was delivered (underdose 46.9%). They estimate that the patient received 50+ Gy to the intended area and there were no microspheres to an unintended target. Written report forthcoming." Illinois Item Number: IL177016 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-08-14
52886 | 0 | LOUISIANA ENERGY SERVICES |  |  |  |  | 2017-08-03 15:00 | 2017-08-04 10:56 | 2017-08-04 | ADMINISTRATIVE CRITICALITY CONTROLS NOT USED The following was received from the licensee via email: "(1) Radiological or chemical hazards involved, including isotopes, quantities, and chemical and physical form of any material released. "There was no material released. "(2) Actual or potential health and safety consequences to the workers, the public, and the environment, including relevant chemical and radiation data for actual personnel exposures to radiation or radioactive materials or hazardous chemicals produced from licensed materials (e.g., level of radiation exposure, concentration of chemicals, and duration of exposure); "No personnel were exposed to radiation, radioactive materials or hazardous chemicals. IROFS54a [Items Relied On For Safety] and IROFS54b are administrative criticality controls for the SCDT [Small Component Decontamination Train] and limit the amount of U-235 to less than 730g. The material was put into the SCDT without using bookkeeping procedures which could have potentially led to a criticality in the SCDT. "(3) The sequence of occurrences leading to the event, including degradation or failure of structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences; and "Last week material from the pH adjustment tanks on the LECTS [Liquid Effluent Collection and Transfer System] slab tanks was moved into the SCDT without the use of administrative criticality control IROFS54a and 54b. During a work package review yesterday (8/3/2017) the transfer into the SCDT was questioned by the lSA engineering group. Material was approximately 250ml of waste water and 12L of NaOH solution in a 5 gallon bottle. Conservative estimate of the total amount of U-235 in the Slab Tanks at the time the 250ml of waste water was removed was less than 600 g U-235. "(4) Whether the remaining structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences are available and reliable to perform their function; "The amount of material transferred into the SCDT was below subcritical mass limits therefore UUSA [URENCO USA] could not enter into a condition in which 10 CFR 70.61 performance requirements would not have been met "(5) External conditions affecting the event; "None. "(6) Additional actions taken by the licensee in response to the event; "When the event was discovered an anomalous condition was declared and Recycling and Engineering made a conservative estimate of how much material could potentially be in the SCDT. It was determined that if they had transferred all of the waste water from the slab tank into the SCDT it would still have been below the acceptance criteria for IROFS54a and IROFS54b. Furthermore the 250mL of waste water and the 12L of NaOH solution were transferred in a 5 gallon container which is a single parameter safe value for 6 w/o% enrichment. Based on this discovery at no time would the SCDT have exceeded 10 CFR 70.61 performance requirements. "(7) Status of the event (e.g., whether the event is on-going or was terminated); "No event took place, the material transferred to the SCDT never exceeded subcritical mass limits. "(8) Current and planned site status, including any declared emergency class; "No emergency class declared. Stop work issued for the LECTS and Decontamination room recycling activities. Anomalous condition is in the process of being lifted "(9) Notifications, related to the event, that were made or are planned to any local, State, or other Federal agencies; "One hour (late) report to the NRC; this is a conservative response based on a prior NOV. No other notifications were made. "(10) Status of any press releases, related to the event that were made or are planned. "None." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ALL SAFETY ITEMS UNAVAILABLE | [9 empty] | NON EMERGENCY | 2 | NM | FUE |  | PART 70 APP A (a)(4) |  |  |  | 0 | 2017-08-08
52885 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-08-02 14:00 | 2017-08-03 14:47 | 2017-08-03 | AGREEMENT STATE REPORT - FIXED GAUGE SOURCE STUCK IN DIP TUBE The following information was received via E-mail: "On August 2, 2017, at approximately 1400 CDT, [the] Radiation Safety Officer of ExxonMobil notified the Louisiana Department of Environmental Quality (LDEQ) of an equipment malfunction. A Model LB300 IS Berthold level/density gauge installed on G-Line High Pressure Separator Vessel, V5300 and possessing seven nominally 50 mCi Co-60 sealed sources, was undergoing a routine annual shutter test in which the sealed sources were being pulled upwards in their dip tubes via connecting cables to the top of the source holder. The source in dip tube No.1 became stuck in its dip tube and could not be pulled upward further. The source in dip tube No.1 could not be successfully returned to its normal operating position. The sources in dip tubes Nos. 3, 4, and 5 were successfully pulled up to the top of the source holder. According to [the RSO], the sources in dip tubes Nos. 2 and 6 had already become stuck in their dip tubes and not returned to the source holder during the previous shutter test conducted during June 2016, and that now there are three sources, source serial numbers, 1369-08-02, 1370-08-02 and 1374-08-02, respectively stuck within their dip tubes Nos. 1, 2, and 6. The licensee placed a service call to [a] Berthold contract service engineer on August 2, 2017, but was unable to contact him and left a voicemail message. [The Berthold contract service engineer] will conduct a maintenance inspection of the gauge as soon as possible. The above sources have gone through approximately 3.2 half-lives since installation and so the true activity of the above Co-60 sources is approximately 5.4 mCi. This is not an emergency situation. ExxonMobil Radiation Safety Office staff is monitoring the vessel condition and have the situation under control. There is not a potential for off-site exposure." Louisiana Event Report ID No.: LA170011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-08-11
52884 | 0 | DEFENSE THREAT REDUCTION AGENCY |  |  |  |  | 2017-08-02 18:00 | 2017-08-02 20:04 | 2017-08-03 | LOST SOURCE Following a training exercise, the training individual, placed the training source on a vehicle roof and shortly determined the source was missing. The source is a Category 3 source consisting of a small quantity of NRC licensed special nuclear material. The source has not been found. The DTRA investigation continues. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). * * * UPDATE ON 8/3/17 AT 0733 EDT FROM GERALD GOODFELLOW TO DONG PARK * * * The special nuclear material was found at 0729 EDT. Notified R1DO (Lilliendahl), NMSS (Smith), ILTAB (Davis), and NMSS Events Notification via email. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA Emergency Ops Center, FDA Emergency Ops Center (email), FEMA NWC (email), DHS Nuclear SSA (email), and FEMA NRCC SASC (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdfNM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN SNM | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 74.11(a) |  |  |  | 1 | 2017-08-10
52883 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2017-08-02 15:00 | 2017-08-02 18:53 | 2017-08-02 | AGREEMENT STATE REPORT - FAILED NUCLEAR MOISTURE/DENSITY GAUGE HANDLE LOCKING MECHANISM The following information was received from the State of Arizona via email: "During a routine inspection, the Arizona Radiation Regulatory Agency discovered that the handle locking mechanism of a CPN MC-3 Portaprobe (Serial # M39068944) containing 370MBq (10mCi) of Cesium-137 and 1.85 GBq (50mCi) of Americium-241/Beryllium, failed to function as intended. While testing the locking mechanism, the inspector was able to lower the Cs-137 source out of its housing, exposing the source, while the handle and trigger were in the locked position. The licensee was notified and the gauge was immediately placed out of service. The utilization log for the gauge was checked and it was determined that the gauge had not been in use for the previous 6 months. None of the users had reported issues with the gauge prior to that time. The licensee committed to having the gauge serviced as soon as possible. "The Agency [Arizona Radiation Regulatory Agency] is continuing to investigate the event. "The [Arizona] Governor's office and U.S. NRC are being notified of this event. "[Arizona] First Notice: 17-011" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2017-08-10
52882 | -1 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-07-26 | 2017-08-02 14:51 | 2017-08-10 | LOST IRIDIUM SOURCES IN TRANSIT The following is excerpted from a report emailed from the Georgia Radioactive Materials Program: On 7/26/17, two Ir-192 Elekta sources (each approximately 11.2 Ci) were shipped from Alpha-Omega Services in Vinton, LA, via a common carrier with two different destination points. They made it to the common carrier's warehouse in Memphis, TN, but then were "lost." An investigation for both cases has been opened with the common carrier and the common carrier point of contact has been notified via email. The packages were expected on 7/28/17 at their respective destinations. Serial number 31016 to UPMC Altoona in Altoona, PA and serial number 10729 to Arrowhead Radiation & Oncology Imaging Center in Glendale, AZ. * * * RETRACTION ON 8/10/17 AT 1114 EDT FROM GREG REESE TO BETHANY CECERE * * * The following is excerpted from an email from the Georgia Radioactive Materials Program: Georgia is requesting retraction of the Georgia NMED Report of 8/2/17. The two sources referenced therein were never lost. Notified R1DO (Bickett), R4DO (Gepford), NMSS Events Notification and CNSNS (Mexico) by email. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example: level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2017-08-10
52881 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2017-08-01 09:34 | 2017-08-01 17:00 | 2017-09-11 | HIGH PRESSURE COOLANT INJECTION STEAM SUPPLY VALVE FAILED TO REPOSITION "At 0934 CDT, while appropriately removed from service for pre-planned testing, the High Pressure Coolant Injection (HPCI) inboard steam isolation valve, MO-2238, valve position indication was found to be inadequate. As a result, MO-2238 was declared inoperable in accordance with Technical Specification (TS) 3.6.1.3. This resulted in a condition that caused the HPCI system to be inoperable. "The cause of the inadequate valve position indication is currently being investigated. This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D). "The NRC Resident Inspector has been informed." * * * RETRACTION ON 09/11/17 AT 1144 EDT FROM BOB MURRELL TO BETHANY CECERE * * * "The purpose of this notification is to retract a previous report made on 8/1/17 at 1700 (EDT) (EN 52881). NRC notification was initially made as a result of the High Pressure Coolant Injection (HPCI) inboard steam isolation valve, MO-2238, valve position found to be inadequate. "Subsequent to the initial report, NextEra Energy Duane Arnold (NextEra) has determined that the condition observed on 8/1/17 for MO-2238 did not exist prior to removing the system from service for pre-planned testing, but was observed during post maintenance testing. Consequently, the failure does not meet the reporting requirements of 10 CFR 50.72 or 10 CFR 50.73. "The NRC Resident Inspector has been notified." Notified the R3DO (Riemer). | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-08-01
52880 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2017-07-25 | 2017-08-01 10:28 | 2017-08-01 | AGREEMENT STATE REPORT - MISADMINISTRATION DUE TO PROBLEM WITH A DELIVERY CATHETER The following report was received from the Tennessee Department of Environmental Conservation Division of Radiological Health via email: "[A] Yttrium-90 TheraSpheres patient procedure misadministration [occurred] due to [a] 'kinked' delivery catheter. [Approximately] 60 Gray [was] administered of [the] prescribed 120 Gray. [Two] manufacturer representatives were in attendance throughout procedure, 'proctoring' the physician. According to both proctors, the case was performed per manufacturer instructions, but unfortunately, the kinked catheter prohibited the complete dose from being administered." Tennessee Radiological Event No. TN-17-147 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2017-08-09
52879 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2017-07-31 14:00 | 2017-07-31 18:32 | 2017-07-31 | UNANALYZED CONDITION FOR HOT LEG INJECTION SCENARIOS "At 1400 [EDT], St. Lucie completed a review of Unit 1 Hot Leg Injection scenarios. St. Lucie Unit 1 was licensed with a Hot Leg Injection capability that relies upon manual actions to accomplish the function. This review concluded that some postulated single electrical train failure scenarios were not fully addressed in plant procedures. Because of the potential to extend Hot Leg Injection initiation beyond the analysis start time, St. Lucie is reporting this condition under 10 CFR 50.72(b)(3)(ii)(B). "The affected off-normal procedures were immediately revised to include necessary instructions to restore power to selected valves during a postulated loss of electrical power to restore the Hot Leg Injection strategy. Unit 1 remained at 100% power. "The NRC Resident Inspector has been notified." A review found this condition was not applicable for Unit 2. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-07-31
52878 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-07-28 | 2017-07-28 16:00 | 2017-07-28 | AGREEMENT STATE REPORT - DOSE RECEIVED EXCEEDED PRESCRIBED DOSE The following information was received from the State of Florida via email: "[The State of Florida] received a call from the [Mayo Clinic] RSO [Radiation Safety Officer] to report a medical event that occurred at Mayo clinic. While performing a 90cc volume liver ablation, a female patient was to receive a 340 Gy dose, but it was later discovered that the dose delivered was 800 Gy. The physician has been notified, and is contacting the patient to inform her of the overdose and verify that there are no unusual side effects. A written report from the RSO will be sent to this office before Aug. 11th detailing the cause of the incident and corrective actions to be taken. "Incident Number: FL17-230" The isotope involved is Y-90 [Yttrium-90] Spheres. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-08-07
52877 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2017-07-28 15:43 | 2017-07-28 16:40 | 2017-07-28 | NOTIFICATION TO OFFSITE AGENCY OF NON-ROUTINE FLOW OF FIRE PROTECTION WATER TO THE OHIO RIVER "On July 20, 2017, a fire protection supply line at BVPS [Beaver Valley Power Station] Unit 1 experienced a mechanical joint separation. When the mechanical joint separated there was an unplanned flow of water from the fire protection line to the ground, which eventually re-entered the Ohio River via storm drains. The source of the water to the BVPS Unit 1 Fire Protection System is the Ohio River. The fire protection water was not treated with chemical additives. The water flow from this fire protection line was terminated on the same day. "Due to the situation described above, FENOC [FirstEnergy Nuclear Operating Company] provided written documentation describing this occurrence to the Pennsylvania Department of Environmental Protection, (PADEP) on July 28, 2017. "This offsite notification to PADEP requires a 4-hour report per 10 CFR 50.72 (b)(2)(xi). "No press release is planned. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-07-28
52876 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-07-28 12:06 | 2017-07-28 15:22 | 2017-07-28 | ALERT DECLARED DUE TO LOW OXYGEN LEVELS INSIDE CONTAINMENT "Containment atmosphere oxygen level was measured at 18.4 percent. This is below normal habitability level. The cause of the low oxygen level is a nitrogen leak inside containment Nitrogen has been isolated from containment and operators are preparing to purge containment." The licensee notified the State of California, local authorities and the NRC Resident Inspector. Notified the DHS SWO, FEMA OPS, USDA OPS, HHS OPS, DOE OPS, DHS NICC, EPA EOC. Notified FDA EOC, NuclearSSA, FEMA NWC and FEMA NRCC SASC via email. * * * UPDATE FROM ALLEN DURACHER TO VINCE KLCO ON 7/28/17 AT 2142 EDT * * * The ALERT was terminated on 7/28/17 at 1819 PDT. The containment atmosphere was restored to normal conditions. The nitrogen source was isolated. The cause of the nitrogen leak into containment is under investigation. The licensee will notify the NRC Resident Inspector. The licensee has notified the State of California and the local authorities. The licensee plans to issue a press release. Notified the R4DO (Hay), NRR EO (Miller), IRD MOC (Grant). Notified the DHS SWO, FEMA OPS, USDA OPS, HHS OPS, DOE OPS, DHS NICC, EPA EOC. Notified FDA EOC, NuclearSSA, FEMA NWC and FEMA NRCC SASC via email. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | ALERT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2017-07-28
52875 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-07-27 | 2017-07-28 09:51 | 2017-07-28 | AGREEMENT STATE REPORT - FIXED NUCLEAR GAUGE SHUTTER STUCK IN CLOSED POSITION The licensee, International Paper, provided notification to the South Carolina Department of Health and Environmental Control of a stuck shutter on a Berthold Model LB7440 fixed gauging device. The shutter is stuck in the closed position. Corrosion was found on the shutter roll pin causing the shutter mechanism to fail. The gauging device contains 10 mCi of Cs-137. A measurement of 20 mR/hr was detected in front of the gauge. The licensee has removed the gauge from service and is awaiting a shipping container to return the gauge to the manufacturer. SC license # 060. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-08-07
52874 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-07-27 13:15 | 2017-07-27 18:54 | 2017-07-27 | HIGH PRESSURE CORE INJECTION SYSTEM DECLARED INOPERABLE "[Unit 2] HPCI was declared inoperable due to improper valve alignment stemming from an incorrect sequence directed from a work order. [Unit 2] HPCI was inoperable for 20 minutes and was manually re-aligned to an operable status." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-07-27
52873 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-07-27 03:00 | 2017-07-27 04:51 | 2017-08-21 | SAFEGUARDS REPORT - PHYSICAL SECURITY Discovered vulnerability in a safeguards system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DANNY BRADFORD TO DONALD NORWOOD AT 1853 EDT ON 8/21/2017 * * * This event was determined to be loggable under 10 CFR 73, Appendix G, II, in accordance with the guidance in NRC Generic Letter 91-03. The licensee notified the NRC Resident Inspector. Notified the 73.71 Safeguards Group (via E-mail) and the R4DO (Vasquez). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | TX | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-07-27
52872 | 0 | WATTS BAR |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-07-25 04:28 | 2017-07-25 11:07 | 2017-07-25 | MANUAL REACTOR TRIP DUE TO ROD POSITION INDICATION SYSTEM BEING INOPERABLE "On July 25, 2017, at 0428 Eastern Daylight Time (EDT) Watts Bar Nuclear Plant (WBN) Unit 2 was in Mode 3, beginning a Reactor Startup. While in the initial phase of withdrawing the first of four Control Rod banks, the two associated group demand position indicators deviated greater than 2 steps from each other. In accordance with Technical Requirement 3.1.7, Position Indication System, Shutdown, with one or more group demand position indicators inoperable, the reactor trip breakers are to be opened immediately. Operations personnel opened the reactor trip breakers immediately by initiating a manual trip of the Reactor Protection System (RPS). The Auxiliary Feedwater system was in service and controlling Steam Generator water levels at the time of the event and did not receive any valid actuation signals. No other system actuations occurred as a result of this reactor trip and all systems operated as designed. "The cause of the position indication system inoperability is currently under investigation. "NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-07-25
52871 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-07-24 20:44 | 2017-07-24 23:50 | 2017-07-25 | OFFSITE NOTIFICATION TO THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION "At time [2044 EDT], Limerick Generating Station notified the Pennsylvania DEP [Department of Environmental Protection] that there was an imminent overflow of our plant waste water pond (holding pond) due to heavy rainfall in the area. Level in the plant waste water pond was approximately «" from the overflow. Prior to overflowing, plant alignment changes enabled us to lower level in the hold pond to prevent the overflow. PADEP was subsequently notified that an actual overflow condition did not occur." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-07-25
52870 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2017-07-24 16:38 | 2017-07-24 19:25 | 2017-07-24 | AUTOMATIC REACTOR TRIP DUE TO LOAD REJECTION "At 1638 [EDT] on 7/24/2017, Oconee Unit 3 experienced an automatic reactor trip due to a load rejection when the generator output breakers both tripped open unexpectedly while 525kV switchyard maintenance was being performed. The trip was uncomplicated with all systems responding normally post-trip. Due to the RPS [Reactor Protection System] actuation while critical, this event is being reported as a 4-hour non-emergency notification per 10 CFR 50.72(b)(2)(iv)(B). "The plant responded normally to the reactor trip, and there was no impact on the health and safety of the public or plant personnel. "Operations responded using the Emergency Operating Procedure and stabilized Unit 3 in MODE 3. "The NRC Senior Resident Inspector has been notified." Decay heat is removed by discharging steam to the main condenser using the turbine bypass valves. Unit 1 and 2 are not affected. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-07-24
52869 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-05-25 16:47 | 2017-07-24 13:36 | 2017-07-24 | INVALID HIGH PRESSURE CORE SPRAY (HPCS) SYSTEM ACTUATION IN MODE 5 "At 1647 [PDT] on May 25, 2017, during the performance of a post-maintenance test for replacement of a Reactor Pressure Vessel (RPV) low water level 3 indicator switch (MS-LIS-24A), a pressure perturbation in the common pressure reference line resulted in tripping of the RPV Level 2 instruments and an unplanned start of High Pressure Core Spray (HPCS) pump (HPCS-P-1) and its supporting emergency diesel (DG3). The Reactor Pressure Vessel was flooded up during the refueling outage, thus, the actuations of the HPCS pump and its supporting emergency diesel (DG3) were unplanned and invalid. The HPCS pump did not inject into the RPV due to the RPV level being above Level 8 which is an interlock to close the HPCS RPV injection valve (HPCS-V-4). "During the event, the single train HPCS system initiated normally but did not inject into the reactor pressure vessel as expected due to flooded-up conditions of the reactor pressure vessel for refueling outage activities. The emergency diesel generator started normally in response to the initiation signal of HPCS. Both HPCS and the emergency diesel generator functioned successfully. All systems responded in conformance with their design and there was no safety significance associated with this event. "At the time of the event, the licensee notified the NRC Resident [Inspector]." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | WA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-07-24
52868 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2017-07-21 | 2017-07-21 10:05 | 2017-07-21 | AGREEMENT STATE REPORT - INDIVIDUAL OVEREXPOSURE OF PHARMACY TECHNICIAN The following report was received from the Florida Department of Health Bureau of Radiation Control via email: "[The Florida Department of Health Bureau of Radiation Control] received an email reporting an overexposure at Triad Isotopes Inc. On Jun 5, 2017, Triad's Corporate Safety Officer received exposure notifications (both whole body and ring dosimeters) from Landauer involving the same individual." The first notification was for the period 4/1/2017 - 4/30/2017; doses were: whole body Deep Dose Equivalent (DDE) =2545 mrem, Lens Dose Equivalent (LDE) =2545 mrem, Shallow Dose Equivalent (SDE) =2452 mrem. The second notification was for the period 5/15 - 5/21; doses were: left ring dosimeter 11000 mrem, right ring dosimeter 4670 mrem. "On Jun. 5, 2017 Triad overnighted the whole body badge for the period of 5/1/2017 5/31/2017 to be read . Landauer notified Triad of the exposure notification on Jun. 9, 2017, whole body doses were: DDE=10953, LDE=14971 mrem, SDE=17913 mrem. Probable causes and corrective actions are outlined in the report from Triad. ERCM [Environmental Radiation Control Materials] will conduct the follow-up." Technician A was immediately prohibited from entering the restricted area or handling radioactive materials. The isotopes involved are believed to be Mo-99/Tc-99m, Tc-99m, and Ga-68. An investigation was performed and identified the root causes as multiple procedural adherence issues, a human behavior error, and possible exposure to badges while not being worn. Retraining of all employees has been conducted and other steps are on-going. Florida Incident Number: FL17-225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2017-07-31
52867 | 0 | SUSQUEHANNA NUCLEAR LLC |  |  |  |  | 2017-07-14 16:46 | 2017-07-21 10:40 | 2017-07-21 | PART 21 NOTIFICATION - EATON/CUTLER HAMMER A200 SERIES STARTER The following information was received by the licensee via email: "Pursuant to 10 CFR 21, this is a non-emergency notification by Susquehanna Nuclear, LLC concerning a defect in an Eaton/Cutler Hammer A200 series starter that failed while in service at Susquehanna Steam Electric Station. The failed starter was manufactured by Eaton Corporation in 2014 and purchased by Susquehanna from AZZ/NLI as part of an MCC bucket assembly. The starter failed with its contacts stuck in the energized state when it was de-energized. A failure analysis identified the contactor sticking to be due to the pole faces of the coil laminations and those of the armature laminations adhering to one another at normal operating temperatures. There was residue/material on the pole faces which closely matched Polydimethylsiloxane (PDMS) and silicone grease. One of the characteristics of PDMS is that at cooler temperatures it is more of a solid consistency, and at higher temperatures it becomes more viscous and tacky. "A previous Part 21 report submitted by Curtiss-Wright QualTech NP (Event Notification Number 51611) in December 2015 provided notification of Eaton/Cutler Hammer A200 series starters failures due to silicon based mold release that remained on the molded parts and would come between the moving (magnet) and fixed armatures. The Part 21 stated that when heated for extended period of time, the material would become sticky causing anywhere from a minor delay in opening to a frozen closed condition. Eaton/Cutler Hammer determined that the silicone mold release was first introduced into the manufacturing facility in May 2008 and used periodically until October 2012. According to Eaton/Cutler Hammer, any starters manufactured after January 1, 2013 should be silicon mold release free. "Following the failure of the 2014 starter at Susquehanna, Eaton Corporation performed an investigation and reconfirmed that silicon mold release was banned from molding production in October 2012 and has not been used since that time. Eaton concluded that the contamination does not appear to be systemic, but rather random and intermittent and that the contamination was most likely introduced either by operators and assemblers on the manufacturing lines, or by others who disassemble and inspect the product after shipment from their plant. Susquehanna does not take the components apart during receipt for testing or visual inspection. Eaton concluded that there is no evidence that the issue is systemic and considers it a random event. Susquehanna has evaluated the condition and has concluded that the condition could create a substantial safety hazard." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-07-21
52866 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2017-07-19 17:30 | 2017-07-20 15:40 | 2017-07-20 | LOSS OF HELICOPTER INTEGRATED BLADE INSPECTION SYSTEM WITH 500 MICROCURIE STRONTIUM 90 SOURCE "At 1730 on 19 July 2017, HM-15 aircraft 13 had the Main Rotor Fairing, commonly referred to as the 'beanie', depart in flight. The 'beanie' cover is constructed of fiberglass, is circular in shape and 5 feet in diameter, weighing approximately 20 pounds. In addition to the beanie, we discovered that one of the In-flight Blade Inspection System (IBIS) Indicators also departed the aircraft. Loss of this IBIS Indicator is of concern because it contains strontium-90 which is radioactive material. Loss of this IBIS Indicator was not discovered until the aircraft shutdown on its line at Naval Station Norfolk. "Location lost: Approximately 100 miles west of Norfolk, VA over the Roanoke River near Lake Gaston. The location is just north of the Virginia / North Carolina border over the Roanoke River approximately 3 miles east of the Kerr Lake Power Plant." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2017-07-28
52865 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2017-07-20 12:30 | 2017-07-20 13:30 | 2017-07-20 | POTENTIAL TORNADO MISSILE VULNERABILITIES "In order to address the concerns outlined in RIS 2015-06 'TORNADO MISSILE PROTECTION,' an evaluation of tornado missile vulnerabilities and their potential impact on Technical Specification (TS) plant equipment was conducted. This evaluation concluded that the following Structures, Systems, and Components (SSCs) are potentially vulnerable to tornado generated missiles: "The Davis-Besse Nuclear Power Station (DBNPS) Unit 1 Emergency Diesel Generator (EDG) Fuel Oil Storage Tanks (FOST) (DB-Tl53-l, DB-T-153-2) support the EDG operation for 7 days. The vents on the FOST are necessary to support the transfer of fuel from the FOST to the EDG day tank. These vents are not protected and are vulnerable to a potential tornado-generated missile impact. This postulated strike could impact fuel transfer to the EDG day tank and, therefore does not support operability of both EDGs for Technical Specification 3.8.1. "Tornado generated missiles striking the FOST vent piping could potentially affect pump performance and challenge the structural integrity of the tank. This would render both the FOST and corresponding EDG inoperable. This condition is reportable per 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(A). "The potential vulnerabilities for the FOST vents (as discussed above) are being addressed in accordance with NRC EGM-15-002 Revision 1 and DSS-ISG-2016-01 NRC enforcement discretion and interim guidance documents. Immediate compensatory measures were taken to mitigate the potential consequences of an onsite tornado generated missile impact on the FOST vents." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2017-07-20
52864 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2017-07-18 | 2017-07-19 17:11 | 2017-07-19 | KANSAS AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received from the state of Kansas via email: "A medical event occurred during a Yttrium-90 TheraSphere treatment of a patient's liver cancer. The patient received approximately 24 percent of the dose prescribed in the written directive. There was no harm to the patient other than the inconvenience of rescheduling the treatment to receive the remainder of the dose. "[The licensee is] investigating the event and will submit a report within the required 15 days. With this procedure the vial containing the TheraSpheres cannot be viewed due to being inside a lead pig. Therefore, a digital radiation dosimeter is placed near the delivery device. As the dose is delivered to the patient, the readings drop to or near zero. In this case, the technologists and the physician stated the dosimeter was reading 0.0 at the end of the procedure. "[The licensee's] immediate corrective action will be for radiation safety staff to verify the instrument readings when the physician feels the entire dose has been delivered." The prescribed dose or quantity was not provided by the State. Kansas NMED Item Number KS170006 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2017-07-27
52863 | 0 | WATERFORD | 3 |  |  | [3] CE | 2017-07-17 16:17 | 2017-07-17 17:37 | 2017-09-14 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER During a rain and lightning storm, plant operators observed arcing from the main transformer bus duct and notified the control room. The decision was made to trip the main generator which resulted in an automatic reactor trip. The plant entered EAL SU.1 as a result of the loss of offsite power for greater than fifteen minutes. Plant safety busses are being supplied by both emergency diesel generators while the licensee inspects the electrical system to determine any damage prior to bringing offsite power back into the facility. Offsite power is available to the facility. No offsite assistance was requested by the licensee. During the trip, all rods inserted into the core. Decay heat is being removed via the atmospheric dump valves with emergency feedwater supplying the steam generators. The main steam isolation valves were manually closed to protect the main condenser. There were no safeties or relief valves that actuated during the plant transient. There is no known primary-to-secondary leakage. Reactor cooling is via natural circulation. All safety equipment is available for the safe shutdown of the plant. The licensee has notified the NRC Resident Inspector, Louisiana Department of Environmental Quality and the local Parish emergency management agencies. Notified DHS SWO, FEMA, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). * * * UPDATE ON 7/17/17 AT 2007 EDT FROM MARIA ZAMBER TO DONG PARK * * * This notification is also made under 10 CFR 50.72(b)(3)(v)(D). "This is a non-emergency notification from Waterford 3. "On July 17, 2017 at 1606 CDT, the reactor automatically tripped due to a loss of Forced Circulation, which was the result of Loss of Offsite Power (LOOP) to the electrical (safety and non-safety) buses. Both 'A' and 'B' trains of Emergency Diesel Generators (EDGs) started as designed to reenergize the 'A' and 'B' safety buses. The LOOP caused a loss of feedwater pumps, resulting in an automatic actuation of the Emergency Feedwater (EFW) system. "Prior to the reactor trip, at 1600 CDT, personnel noticed the isophase bus duct to main transformer 'B' glowing orange due to an unknown reason. Due to this, the main turbine was manually tripped at 1606 CDT. Following the turbine trip, the electrical (safety and non-safety) buses did not transfer to the startup transformers as expected due to an unknown reason. "The plant entered the Emergency Operating Procedure for LOOP/Loss of Forced Circulation Recovery. "At 1617 CDT, an Unusual Event was declared due to Initiating Condition (IC) SU1 - Loss of all offsite AC power to safety buses [greater than] 15 minutes. "All safety systems responded as expected. "The plant is currently in mode 3 and stable with the EDGs supplying both safety buses and with EFW feeding and maintaining both steam generators. Offsite power is in the process of being restored." The licensee has notified the NRC Resident Inspector, Louisiana Department of Environmental Quality and the local Parish emergency management agencies. * * * UPDATE FROM ADAM TAMPLAIN TO HOWIE CROUCH AT 2203 EDT ON 7/17/17 * * * The licensee terminated the Notification of Unusual Event at 2056 CDT. The basis for terminating was that offsite power was restored to the safety busses. The licensee has notified Louisiana Department of Environmental Quality, St. John and St. Charles Parishes, Louisiana Homeland Security Emergency Preparedness, and will be notifying the NRC Resident Inspector. Notified IRD (Stapleton), NRR (King), R4DO (Hipschman), DHS SWO, FEMA, DHS NICC, FEMA National Watch Center (email) and Nuclear SSA (email). * * * UPDATE FROM SCOTT MEIKLEJOHN TO HOWIE CROUCH AT 1724 EDT ON 7/19/17 * * * This update is being reported under 10 CFR 50.72(b)(3)(v)(B). "During the event discussed in EN# 52863, at 1642 CDT [on July 17, 2017], Condensate Storage Pool (CSP) level lowered to less than 92% resulting in entry to Technical Specification (TS) 3.7.1.3. Level in the CSP was lowered due to feeding from both Steam Generators with EFW. Normal makeup to the CSP was temporarily unavailable due to the LOOP. Filling the CSP commenced at 1815 CDT [on July 17, 2017], and TS 3.7.1.3 was exited on July 18, 2017 at 0039 CDT." The licensee notified the NRC Resident Inspector. Notified R4DO (Hipschman). * * * UPDATE FROM SCOTT MEIKLEJOHN TO HOWIE CROUCH AT 1233 EDT ON 9/14/17 * * * "Waterford 3 is retracting a follow up notification made on July 19, 2017 for EN# 52863, concerning the loss of safety function associated with the Condensate Storage Pool (CSP) per 10 CFR 50.72(b)(3)(v)(B). The Condensate Storage Pool was performing its required safety function by providing inventory to the Emergency Feed Water pumps when the required Tech Spec level (T.S. 3.7.1.3) dropped below 92%. The Technical Specification was entered at 1624 [CDT] on July 17, 2017 and exited after filling at 0039 on July 18, 2017. The total allowed outage time allowed by Tech Spec 3.7.1.3 is 10 hours to be in Hot Shutdown if not restored. The Condensate Storage Pool level was restored to greater than 92% prior to exceeding the allowed outage time. Based on level being restored and the Condensate Storage Pool performing its required safety function, 10 CFR 50.72(b)(3)(v)(B) does not apply. Prior to the automatic reactor trip, Condensate Storage Pool level was greater than 92%. "The NRC Resident Inspector has been notified of the retraction." Notified R4DO (Groom). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | POT UNABLE TO SAFE SD | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 4 | LA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(A) | 0 | 2017-07-17
52862 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-05-18 11:15 | 2017-07-17 10:55 | 2017-07-17 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATOR "The following information is provided as a 60-day telephone notification to the NRC in accordance with 10 CFR 50.73(a)(1) reported under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of the Division 3 emergency diesel generator (DG). The event occurred on May 18, 2017, at 1115 CDT. As allowed by 10 CFR 50.73(a)(1), the notification is being made via telephone. "(a) The specific train(s) and system(s) that actuated were: During troubleshooting of blown fuses for the Reserve Auxiliary Transformer (RAT) main feed metering and relaying circuit, the Division 3 DG automatically started as a result of a loss of power signal, the RAT feed breaker for the offsite power source opened after a 15 second time delay as a result of a degraded voltage signal, and the DG output breaker subsequently closed. The loss of voltage and degraded voltage signals were generated when maintenance technicians opened the wrong test switch in the Division 3 4160-Volt Switchgear 1E22S004. "(b) Whether each train actuation was complete or partial: Upon receiving the simulated loss of voltage and degraded voltage signals, the Division 3 DG started and the DG breaker closed as expected. No additional actuations occurred. "(c) Whether or not the system started and functioned successfully: Upon receiving the simulated loss of voltage and degraded voltage signals, the Division 3 DG and the DG breaker were verified to have properly functioned in response to the invalid signals. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-07-17
52861 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2017-07-14 17:24 | 2017-07-14 21:44 | 2017-07-15 | LOSS OF THE TECHNICAL SUPPORT CENTER VENTILATION SYSTEM "Oyster Creek Generating Station has experienced a loss of the Technical Support Center (TSC) ventilation system due to an electrical perturbation. "If an emergency is declared requiring TSC activation during the time TSC ventilation is non-functional, the TSC will be staffed and activated using existing emergency planning procedures unless the TSC becomes uninhabitable due to ambient temperature, radiological, or other conditions. If relocation of the TSC becomes necessary, the Emergency Director will relocate the TSC staff to an alternate location in accordance with applicable site procedures. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii) due to a loss of the TSC. An update will be provided once the TSC ventilation has been restored to normal operation. "The NRC Resident Inspector has been notified." * * * UPDATE AT 0537 EDT ON 07/15/17 FROM JIM RITCHIE TO S. SANDIN * * * TSC ventilation was restored at 0128 EDT on 07/15/17. The licensee will inform the NRC Resident Inspector. Notified R1DO (Dimitriadis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-07-14
52860 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2017-07-14 | 2017-07-14 16:36 | 2017-07-14 | AGREEMENT STATE REPORT - LOST AND RECOVERED PORTABLE GAUGE The following was received from the State of Nevada via email: "It was reported to the Nevada Radiation Control Program duty officer that a portable gauge had been recovered at a temporary job site in Las Vegas, Nevada. The individual who reported the event is a Nevada radioactive material licensee and said on 7/14/2017, at approximately 0735 [PDT], 'a nuclear density gauge was found in North Las Vegas at Cheyenne Ave and Berg St on the road. The gauge was recovered by an employee and quickly brought it to a secure storage location. The gauge was found in good condition and not damaged or source exposed.' At 0930 [PDT] on 7/14/2017, it was reported to the Nevada Radiation Control Program, by the ARSO from the company who lost the gauge, the gauge fell off the tailgate of a transport vehicle at a temporary jobsite, and the operator realized the loss and returned to the site within 5 minutes, but the gauge had already been recovered by [the reporting licensee]. The operator from [the licensee who lost the gauge] was informed that the gauge was recovered by [the reporting licensee] and relayed that information to the ARSO at [the licensee who lost the gauge]. The gauge was intact, no damage, transported back to the owner's storage location, and taken out of service. An investigation of the event will commence [on] 07/17/2017." Item Number: NV170006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2017-07-24
52859 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2017-03-24 15:48 | 2017-07-14 15:45 | 2017-07-14 | INVALID SPECIFIED SYSTEM ACTUATION DURING TESTING "This telephone notification, as allowed by 10 CFR 50.73(a)(1), is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of containment isolation valves in more than one system which occurred during the most recent refueling outage at Fermi 2. On 3/24/2017, at approximately 1548 EDT, when synchronizing an emergency diesel generator (EDG) to the grid during testing, an electrical perturbation occurred. Further investigation found that the EDG was slightly out of phase when it was attempted to be synchronized to the grid. The electrical perturbation resulted in an unexpected half-scram of Reactor Protection System (RPS) A and actuation (closure) of some containment isolation valves. The actuations were invalid as they were not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation. Fermi 2 was shut down for a refueling outage at the time, and therefore, the half-scram of RPS A occurred after the safety function had already been completed. Containment isolation valves actuated (closed) in Division 1 of the Torus Water Management, Drywell Pneumatics, and Drywell Floor and Equipment Drain Sumps systems. All valves operated as expected. Since containment isolation valves in more than one system were actuated by this perturbation, this event constitutes an event or condition that resulted in manual or automatic actuation of the system listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B)(2) and is reportable under 10 CFR 50.73(a)(2)(iv)(A). "The NRC Resident Inspector has been informed of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-07-14
52858 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2017-07-13 | 2017-07-14 11:13 | 2017-07-14 | AGREEMENT STATE REPORT - DAMAGED SHUTTER The following information was received from the State of Arizona via email: "This First Notice constitutes EARLY notice of events of POSSIBLE safety or public interest significance. The information is as initially received WITHOUT verification or evaluation, and is basically all that is known by the Agency [Arizona Radiation Regulatory Agency] Staff at this time. "During an inspection of the licensee on July 13, 2017, an inspector found one portable gauge where the radiation source exposure shutter would not close when moved to the closed position. The inspector's dose measurement at contact with the device was approximately 100 mR/hr. The gauge is a Troxler model 3430, Serial Number 30302, containing 8 milliCuries of Cesium-137 and 40 milliCuries of Americium-241. The licensee has contacted a repair company to fix the gauge as soon as possible. "The Agency is investigating the event. "The Governor's office and U.S. NRC are being notified of this event. " Arizona First Notice: 17-009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2017-07-24
52857 | -1 | CRANE NUCLEAR, INC. |  |  |  |  | 2017-06-05 | 2017-07-13 17:59 | 2018-03-21 | PART 21 - DEFECTIVE SAFETY RELATED VALVES The following was excerpted from a letter by Crane Nuclear, Inc.: "The plug valve designs provided for XOMOX model figure numbers 037AX, 067EG, and 037. These valves have been identified as used in nuclear and/or safety related applications. "The stem for the Subject valve models was identified as being undersized based on allowable yield stress analysis of the stem while in torsion. The high stress condition was due to the high torque required to seat/unseat the plug when installed with a Ultra High Molecular Weight Polyethylene (UHMWPE) sleeve material. High friction factor inherent with this material causes torsional stress to exceed the upper limit of yield strength of the valve which could result in fatigue/yielding of the stem, thus preventing the valve from opening and closing while in service. Historical research performed thus far has not identified any notifications from the customer(s) regarding stem failure of the subject valves, indicating that the valves may still be in operation with no performance related or operating issues. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for the action; and the length of time that has been or will be token to complete the action. "Notifications letters have been sent to the affected plants advising them of the condition, and recommending that the sleeve material be replaced with a lower friction Polytetrafluorethylene (PTFE) material that would significantly reduce the required input operating torque, thereby reducing the risk of failure of the stem material. "XOMOX has been advised to modify design calculations to provide a larger margin for allowable yield strength of the stem material to ensure the stem is properly sized when Ultra High Molecular Weight Polyethylene (UHMWPE) sleeve material is used. "Crane will continue to review XOMOX records to determine if any other sites are impacted, which we expect to complete by August 31, 2017. "Should you have any questions regarding this matter, please contact Samson Kay, Manager of Engineering at (630) 226-4983 or Jennifer Bregovy, Manager of Quality and Safety at (630) 226-4949." The following facilities received these safety related orders: TVA Sequoyah, Pennsylvania Power & Light Susquehanna. * * * UPDATE AT 1205 EDT ON 8/29/17 FROM SAMSON KAY TO MARK ABRAMOVITZ * * * The following information was received via fax: "Crane Nuclear (CNI) has initiate the final phase of the Part 21 research and is currently reviewing over 15,000 documents from the original XOMOX Canada historical archive to determine if any other nuclear sites were impacted by the subject Part 21. The investigation encompasses sales orders spanning from 1968 to 1992. CNI expects to complete the review by 10/30/2017." Point of Contact: Samson Kay (630-226-4983) or Jennifer Bregovy (630-226-4949) Notified the R1DO (Cook), R2DO (Lopez), and Part 21 Resources (via e-mail). * * * UPDATE AT 1627 EDT ON 11/01/17 FROM SAMSON KAY TO S. SANDIN VIA FAX * * * The following information was provided as an update: "Crane Nuclear (CNI) has completed approximately 40% of the review of the historical archive and will not be able to complete the review by the previously requested 10/30/2017 deadline. "The historical review covers the following scope: -XOMOX UK DEVON, ENGLAND - Safety-Related and N-Stamped Valves/Parts issued between 1987 - 1993 -XOMOX Canada & XOMOX A&M - Safety-Related Parts from 1979 - 1993 -XOMOX Cincinnati TUFFLINE - Safety-Related and N-Stamped Valves and Parts issued between 1970 -1993 -XOMOX Crane Nuclear - Safety-Related and N-Stamped Valves and Parts issued from 2001 until present. "Note: Parts and valves were no longer supplied by XOMOX as safety-related or nuclear after 1993 until Crane Nuclear acquired XOMOX in June 29, 2001. "The following sites . . . were identified as a safety-related valves effected by this letter. All sites were supplied to customer 'Delaval' which no longer exists. At the current pace of review, CNI expects to complete the review of the historical archive by 1/30/2018." Delaval supplied valves to these Original Plant Name(s); TVA (doesn't show which plant), Comanche Peak Units 1&2, Columbia, Cleveland Electric, Midland Nuclear Power Plant Units 1&2 and TVA, - Hartsville and Phipps Bend Nuclear Plants both of which were cancelled before completion. Notified R1DO (McKinley), R2DO (Ehrhardt), R3DO (Duncan), R4DO (Werner) and Part 21/50.55 Reactors via email. * * * UPDATE AT 1553 EDT ON 01/31/18 FROM JOYCE HAMMAN TO DONG PARK * * * The following information was provided as an update via fax: "The historical research is complete. Our review of the records from 1973 through 2001 identified 25 valves that were supplied with a stem-sleeve material combination that could exceed the upper limit of yield strength of the valve, which could result in fatigue/yielding of the stem, thus preventing the valve from opening and closing while in service. Those valves were supplied to: "Northeast Utilities, Millstone; Houston Lighting & Power, South Texas Project; Niagara Mohawk, Nine Mile Point; Transamerican Delavel, Oakland; Power Systems, Rocky Mount; Bechtel Energy Corp., 5 Miles West Wadsworth; Pennsylvania Power & Light, Susquehanna; NY Power Authority, Fitzpatrick; TVA, Sequoyah; Omaha Public Power, Ft. Calhoun. "Notification letters have been sent to some of the affected plants advising them of the condition, and recommending that the sleeve material be replaced with a lower friction Polytetrafluoroethylene (PTFE) material that would significantly reduce the required input operating torque, thereby reducing the risk of failure of the stem material. Crane will complete the notifications to the other sites no later than 2/9/18. "Should you have any questions regarding this matter, please contact me, Joyce Hamman, Director, Safety & Quality at (678) 451-2280, Burt Anderson, Site Leader, at (630) 226-4990, or Samson Kay, Engineering Manager at (630) 226-4983." Notified R1DO (Janda), R2DO (Heisserer), R3DO (Dickson), R4DO (Deese) and Part 21/50.55 Reactors via email. * * * RETRACTION AT 1308 EDT ON 03/21/18 FROM SAMSON KAY TO DONG PARK * * * The following information was provided as an update via fax: "Crane reviewed diagnostic testing of 106 XOMOX plug valves for the purpose of validating the assumed torque values specified by XOMOX guidance. From the review of the diagnostic testing, we determined that on average, the actual torque required to stroke the valve (also referred to as the 'break torque') was approximately 56%-67% lower than the calculated value based on the UHMWPE sleeve material for valves with a 150 lbs. pressure class. Statistical analysis confirmed that the test results were within a 95% confidence interval. Consequently, a conservative factor of at least 56% can be applied to the published XOMOX torque value when evaluating stem stress. Applying this factor to the valves previously identified under this Part 21 confirmed that stress limits are below the material allowable for yield strength. This conclusion is supported by operating history (e.g., no reported stem failures) in the field. "Based on these findings, Crane Nuclear, confirms that a condition adverse to quality and safety does not exist and that a Part 21 no longer applies. CNI, requests this Part 21 to be retracted. "Should you have any questions regarding this matter, please contact me, Joyce Hamman, Director, Safety & Quality at (678) 451-2280, Burt Anderson, Site Leader, at (630) 226-4990, or Samson Kay, Engineering Manager at (630) 226-4983." Notified R1DO (McKinley), R2DO (Sandal), R3DO (Duncan), R4DO (Groom) and Part 21/50.55 Reactors via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-07-13
52856 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2015-11-02 | 2017-07-13 16:05 | 2017-07-13 | AGREEMENT STATE REPORT - FIXED GAUGE SHUTTER MALFUNCTION The following was received from the State of Nevada via email: "Report of an equipment failure incident to the State of Nevada Radiation Control Program, fixed gauge malfunctioning shutter, Ohmart model SR-A, S/N: 1015GK at the Robinson Mine, Ruth, Nevada phoned in on 01/26/2016 at 1400 [PST]. "The RSO of Robinson Mine reported the shutter malfunction. He called the vendor to come on site and force the shutter closed. They were successful. The gauge was locked out/tagged out, but not removed from the service area in the mill central processing plant. The vendor stated the shutter malfunctioned because the shielding shifted due to process vibrations. The RSO has been instructed to submit a plan for the gauge." Gauge contained 1.85 MBq of Cs-137. Item Number: NV160003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2017-07-21
52855 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2016-06-27 18:45 | 2017-07-13 16:05 | 2017-07-13 | AGREEMENT STATE REPORT - MISSING AND RECOVERED TROXLER GAUGE The following was received from the State of Nevada via email: "On 06/27/2016 at 1845 [PDT], it was reported to the State of Nevada, Radiation Control Program that a moisture/density gauge, Troxler model 3440, containing 40mCi of Am-241/Be and 8mCi of Cs-137 was missing/lost. The gauge fell out of the back of a transport vehicle and was lost in Reno, Nevada. The gauge user set the gauge on the tailgate of his truck and took a phone call. He was distracted by the phone call and did not place the gauge in it's transport case or secure the gauge and drove back to the office where he realized the gauge had fallen out of the transport vehicle. The gauge user immediately called the RSO and retraced his route to find the gauge. The gauge was not found and it was reported to the Nevada Highway patrol, Washoe County Sheriff and Reno Police Department. The State is following the incident and working with local authorities to develop a press release. Follow-up information will be provided to NRC on the recovery of the lost gauge and entered into NMED. "Update 6/29/2016: 2 hours following the press release, the gauge was recovered and returned to the owner." Item Number: NV160010 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2017-07-21
52854 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2016-01-27 16:35 | 2017-07-13 16:05 | 2017-07-13 | AGREEMENT STATE REPORT - MISSING AND RECOVERED TROXLER GAUGE The following was received from the State of Nevada via email: "Incident involving a lost Troxler Portable gauge, Model 3430, S/N 23626 was reported to the State of Nevada Radiation Control Program on 01/27/2016 at 1635 [PST]. "The RSO of Las Vegas Valley Water District reported the gauge missing. An operator was distracted before the transportation of the gauge and failed to block and brace the gauge or close the tailgate of the transport vehicle. The operator had forgotten the pound plate on-site and walked to where he left it, retrieved the plate but then was distracted and did not secure the gauge. He then started back to the office but realized part way back he had lost the gauge from the back of his vehicle. He retraced his steps, called the RSO and asked another operator to help find the gauge. The gauge was not found at that time. The RSO call the Las Vegas Metropolitan Police [LVMPD]. The Duty Officer for the State of NV, RCP [Radiation Control Program] was notified. "Update 01/28/2016: The RCP Duty Officer received a call from LVMPD ARMOR that the General Contractor on site found the gauge on 01/27/2016 and took it his storage and secured it over night. "Update 01/29/16: The person who found it was non English speaking and locked it up at his work. He brought it back in the morning to the general contractor who called Armor the next morning. John and I gave 3 violations for security, blocking & bracing and type A container breach (pop rivets with their license information). "We [Radiation Control Program] leak tested the gauge and it was negative, and they are having either Troxler or the local InstroTek repair it next week. It is tagged out of service right now. "Update 05/10/2016: The LVWD has retrained all staff on properly securing device prior to driving vehicles. Investigation is considered closed." The Troxler Model 3430 usually contains 8mCi of Cs-137 and 40 mCi of Am241/Be. Item Number: NV160002 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2017-07-21
52853 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2013-08-07 | 2017-07-13 16:05 | 2017-07-13 | AGREEMENT STATE REPORT - DAMAGED RADIOGRAPHY DEVICE The following was received from the State of Nevada via email: "A radiography device was involved in a structural collapse at Barrick Goldstrike Mines, north of Carlin. A wind gust collapsed a steel tank and the scaffolding around it where a radiographer (met chem reciprocity) was working. The device fell approx. 60 ft., damaging the shutter end. The radiographer was not seriously injured and determined that the radiation source was secure and there was no leakage. He packaged the camera and returned to Utah." Item Number: NV130013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2017-07-21
52852 | 0 | CURTISS WRIGHT |  |  |  |  | 2017-07-13 | 2017-07-13 15:39 | 2017-07-13 | PART 21- HEX CAP SCREWS PRODUCED WITH PRE-EXISTING CRACKS The following was submitted by the licensee via facsimile: "This Part 21 initial notification is being submitted pursuant to the requirements of 10CFR21.21(d)(3)(i). "Initial Notification for Hex Cap Screws produced from one heat of material - Nova Machine Products Fastener Part Numbers BPRT.008227.30, BPRT.008468.30, and BPRT.008342.30. "This Part 21 initial notification addresses Nova Machine Products hex cap screws which contain pre-existing cracks as a result of a manufacturing process error (Forged blanks were rapidly cooled after forging instead of air cooled). "The fasteners in question were all produced from one heat of material, which was used to produce one blank size, which was then used to produce the three hex cap screw part numbers stated above. "Fasteners were only supplied to Exelon TMI and Exelon Peach Bottom and are isolated to one heat of material and one manufacturing run. Containment actions are already underway with Exelon and Nova Machine. "Nova Machine and Exelon have been and continue to be in communication on this matter. This appears to be an isolated instance. "If there are any questions pertaining to this communication, please contact Frank Furfari, Sr. Quality Assurance Manager at 216-898-8394." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-07-13
52851 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2017-07-12 11:00 | 2017-07-13 10:33 | 2017-07-13 | AGREEMENT STATE REPORT - MISADMINISTRATION OF TREATMENT The following information was received from the State of Colorado via email: "This is an initial report regarding a misadministration event in Colorado. "University of Colorado Hospital (License Number: CO 828-01) had a misadministration of Y-90 microspheres (SIRTex SIRSpheres) on Wednesday, July 12, 2017. At approximately 11 [MDT], the post administration measurements of the waste from the SIRSpheres Administration indicated that the activity administered to segment 2/3 of the patient's liver was only 68.7 percent of the prescribed activity. The written directive called for an activity of 0.24 GBq and residual waste activity measurements indicated that 0.165 GBq was delivered. The physician indicated that stasis was not reached during the administration to this segment. There was a separate administration to segment [four] of the liver in which stasis was reached. "Follow-up information will be provided after they are available." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2017-07-21
52850 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-07-12 12:38 | 2017-07-12 16:05 | 2017-07-12 | UNANALYZED CONDITION RELATED TO GDC-5 [GENERAL DESIGN CRITERION-5] FOR DUAL UNIT OPERATION "On July 12, 2017, at 1238 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) determined that a preliminary analysis shows adequate Essential Raw Cooling Water (ERCW) flow may not be in place during dual unit limiting design basis conditions of one unit in Hot Shutdown on Residual Heat Removal (RHR) cooling when the other unit experiences a Loss of Coolant Accident (LOCA). Based on preliminary analysis, during a Unit 1 LOCA, Unit 1 receives adequate flow when following existing procedural guidance; however, Unit 2 may not receive adequate flow to meet cool-down requirements with design basis maximum temperatures. During a Unit 2 LOCA, however, current procedural guidance is not adequate to ensure the proper system alignment to establish correct ERCW Component Cooling Water (CCS) Heat Exchanger A and B flow rates for either unit's cool down requirements. "Unit 2 has been shutdown for an extended period of time such that the flow delivered by ERCW is adequate to serve both Unit 1 in a LOCA and Unit 2 in less than Mode 3. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-07-12
52849 | 0 | ACUREN INSPECTION |  |  |  |  | 2017-06-28 17:30 | 2017-07-12 12:08 | 2017-07-12 | STUCK RADIOGRAPHY CAMERA SOURCE "On June 28, 2017, at approximately 1725 EDT, a RT [Radiographic Testing] crew was performing radiography in Morgantown, WV. After completing a weld, they proceeded to move the exposure device to the next location. Due to the terrain and trench conditions, the crew was utilizing a 7 foot guide tube with a 7 foot extension tube with the exposure device on the top side of the trench. "While exposing the source, the trench below the exposure device shifted causing the exposure device to barrel roll into the trench. The radiographer attempted to retract the source, but was unsuccessful. He then adjusted his boundaries and notified the RSO [Radiation Safety Officer] and Operations Manager [OM] of the situation. "The RSO proceeded to the Akron, OH lab to gather the retrieval equipment while the OM discussed the situation with the technician over the phone. Multiple photos of the scene were sent to the OM, at which time, it was determined that the guide tube had most likely been damaged during the fall. Within 15 minutes of the initial notification, both the RSO and OM were on their way. "Once in route to the job site, the OM notified the Assistant Director of Radiation Safety of the situation. He then contacted another RSO to assist in the retrieval. "At approximately 2130 EDT, the retrieval team arrived on site and continued to assess the situation. The exposure device was at the bottom of a trench, on its side. The source was in an unshielded position. The team believed that the source was just outside of the exposure device due to readings that were taken with the Teletector. "With multiple attempts of pulling the cranks, the team was eventually able to position the source into the 4 HVL [Half-Value Layer] collimator that was still strapped to the pipe. At this point, the team was able to get a better view of the front of the camera and confirmed that the extension tube had been crimped right at the connection to the bayonet. The exposure device was then pulled backwards by the cranks in an attempt to straighten the tubes. When challenging the cranks, the team confirmed that the source would not be able to be retracted by normal means. "The team then planned to move the exposure device back to an area of the trench that gave them better access to the damaged tube. They noted that the bungie cord holding the collimator to the pipe was behind the set screw that holds it to the guide tube stop. Knowing that they did not want to lose the 4 HVL of shielding provided by the collimator, they decided that the bungie would need to be removed first. "With the use of remote tongs and an extendable hook, the collimator was freed from the bungie. At this time, the team proceeded to pull the exposure device back approximately 10 feet to an area with adequate lighting and room to continue with the retrieval process. As the device was being pulled backwards, the guide tube remained over the pipe. The extendable hook was then used to move the remainder of the guide tube and collimator to the camera side of the pipe with the collimator pointing down into the ground. "With the dose rates at ALARA, the team proceeded with lead shot bags. At first, the bags were walked by rope with one person on either side of the trench. Once the dose rates were lowered even further, the team applied several more until the dose rate at the front of the exposure device was less than 5 mR/hr. The team then approached the exposure device with tools in hand. The tube was unable to be uncrimped completely with the protective coating on the tube. The damaged area was then stripped and uncrimped to the best of the team's ability. Once complete, the area was cleared and the source was retracted back into its shielded position inside of the exposure device. Once the confirmatory surveys were made, [Assistant Director of Radiation Safety] was notified of the successful retrieval." The three individuals involved in the source retrieval received 13, 5 and 4 mRem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2017-07-20
52848 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-07-11 07:50 | 2017-07-11 17:45 | 2017-09-20 | FLOW INDICATING SWITCH FOR HIGH PRESSURE CORE SPRAY UNRELIABLE INDICATION "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. On July 11th, 2017, it was discovered that the flow indicating switch for the high pressure core spray (HPCS) minimum flow valve was providing unreliable indication. There was no flow through the line at the time the condition was discovered. This switch provides the flow signal to the HPCS minimum flow valve logic. "The switch was declared inoperable and the required actions of Technical Specification 3.3.5.1 were entered. This condition could have prevented the HPCS system, a single train safety system, from performing its specified safety function. Troubleshooting is underway to determine the cause of and correct the condition." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DAN SHARPE TO KARL DIEDERICH AT 1710 EDT ON 9/20/17 * * * "The condition reported in Event notification #52848 pursuant to 10 CFR 50.72(b)(3)(v)(D) has been evaluated, and determined not to have met the threshold for classification as an Event or Condition the Could Have Prevented Fulfillment of a Safety Function. "Engineering analysis has concluded that the affected switch was capable of performing its required support function to provide the flow signal to the HPCS minimum flow valve logic. Thus, the HPCS system remained capable of performing its specific function for the identified condition." The NRC Resident Inspector has been notified. Notified R4DO (G. Miller). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-07-11
52847 | 0 | DEPARTMENT OF THE NAVY |  |  |  |  | 2017-07-05 | 2017-07-11 12:53 | 2017-07-11 | LOST CHEMICAL AGENT DETECTOR The following report was received via email: "During routine maintenance and inventory of the equipment one of the devices could not be accounted for during the evolution. An extensive internal investigation was conducted by the local command and thorough search for the missing device was conducted and ultimately concluded the device was not located and determined lost. The device was declared lost 5 July 2017. "Naval Surface Warfare Center Crane reported the lost chemical agent detector containing a 10 millicurie Nickel-63 (Ni-63) source. As the quantity exceeds 10 times the quantity listed in 10 CFR 20 Appendix C, a telephone notification is required to the NRC within 30 days per 10CFR20.2201. A follow up written report will be submitted within 30 days after this initial notification. "The device, Serial Number 09-4326, contains one foil-sealed source of Ni-63 and does not to exceed 10 milliCuries. The source is Eckert and Ziegler Isotope Products Laboratories Model NER-004. The Ni-63 source is encapsulated in a 304 steel cup with 1 millimeter wall thickness. The source cup is fitted into a ceramic enclosure of 10 millimeter wall thickness. The Ni-63 source is sealed in a detection chamber located inside the housing of the detector. The device has two radioactive material labels to warn personnel of the radioactive source inside the device. One label is on the outside of the device and the other is on the detector housing on the inside of the instrument. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2017-07-19
52846 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-07-10 | 2017-07-11 12:08 | 2017-07-11 | AGREEMENT STATE REPORT - TROXLER GAUGE DAMAGED AT CONSTRUCTION SITE The following report was received from the North Carolina Department of Health and Human Services via email: "North Carolina Licensee ECS Carolinas, LLP, License Number 092-0253-1 reported that a Troxler Model 3440, S/N 24665 Moisture Density Gauge had been damaged on July 10, 2017 at a construction site in Chapel Hill, NC. The gauge contained 8 mCi of Cesium-137 and 40 mCi of Americium-241. An approved technician backed up a company vehicle over the gauge. North Carolina Radiation Protection immediately dispatched an inspector on site to perform a reactive inspection same day. Event Date and Notification Date: July 10, 2017. Licensee had cordoned off a 15+ foot barrier around the vehicle and the gauge. Surveys taken at various distances from the gauge and on contact confirmed that the sources were intact and shielded in the gauge. The gauge sustained minimal damage to the guide rod and the source rod was not extended at the time of the incident. No other local or federal authorities were contacted for this event. The gauge was returned to the manufacturer for repair or disposal. A 30-Day Report is pending from the licensee and follow-up information will be provided. NC Event Report Tracking Number: 170026. Event reportable due to: 10 CFR 30.50(b)(2)(ii)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-07-19
52845 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-07-10 16:02 | 2017-07-10 19:26 | 2017-07-10 | OFFSITE NOTIFICATION DUE TO CONTRACT EMPLOYEE FATALITY "At approximately 14:10 Eastern Daylight Time (EDT), the Control Room was notified of a contract employee experiencing a non-work related medical emergency within the protected area in the service building. First responders were immediately dispatched. Off-site assistance was requested. The individual was transported to the New Hanover Regional Medical Center. No radioactive material or contamination was involved. At 16:02 EDT, hospital officials notified plant personnel that the patient was declared deceased. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) for a situation related to the health of on-site personnel for which a notification to other government agencies is planned. The Occupational Safety and Health Administration (OSHA) will be notified. "The NRC Resident Inspector has been notified." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-07-10
52844 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-07-10 02:50 | 2017-07-10 07:35 | 2017-07-10 | LOSS OF SECONDARY CONTAINMENT DUE TO FAILURE OF NON-SAFETY RELATED DISCHARGE DAMPER "On July 10th, 2017 at 0250 hrs. [EDT] a loss of secondary containment differential pressure (D/P) occurred due to failure of a non-safety related discharge damper associated with 2V205B Reactor Building Zone II Exhaust Fan. This caused a reduction in Reactor Building Zone II (Unit 2) D/P to less than the required 0.25 inches WC [Water Column]. "2V205A Reactor Building Zone II Exhaust Fan was manually started and Reactor Building Zone II D/P was restored to greater than 0.25 inches WC by 0301 hrs. "Reactor Building Zone 1 (Unit 1) and Zone 3 (Units 1&2) ventilation remained in service and stable. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev. 3, section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment system." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-07-10
52843 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2017-07-09 21:58 | 2017-07-10 05:42 | 2017-07-10 | LOSS OF SAFETY FUNCTION - CONTROL ROOM ENVELOPE INOPERABLE "At 2158 [CDT] a door to the Control Room Envelope was left unsecure. GGNS [Grand Gulf Nuclear Station] identified that a loss of Safety Function occurred due to a breach in the Control Room Envelope resulting in inoperability of both divisions of Standby Fresh Air and therefore could have prevented fulfillment of its safety function. The Control Room Envelope was inoperable for one minute. This event is being reported under 10CFR 50.72(b)(3)(v)(D), as any event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-07-10
52842 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2017-06-19 | 2017-07-06 10:32 | 2017-07-06 | AGREEMENT STATE REPORT - LOSS OF Ni-63 GAS CHROMATOGRAPH SOURCE The following information was received from the Commonwealth of Kentucky via email: "On July 5, 2017, Murray State University [General License 401-111-20] reported the loss of an electron capture detector (ECD) contained in a Hewlett-Packard gas chromatograph model 6890. The ECD contained 15 mCi of Ni-63, S/N US00000603. The licensee stated they shipped the ECD on 1/14/16 by [common carrier] to Agilent Technologies, Inc. On 6/19/17 Agilent Technology verified with the licensee they had not received the device. The licensee believes the package containing the ECD was picked up with other items shipped that day by mistake." Kentucky Event Report ID No.: KY170006 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-07-14
52841 | 0 | UNIV OF MISSOURI-COLUMBIA |  |  |  | 10000 KW TANK | 2017-07-05 | 2017-07-05 16:19 | 2017-07-05 | ABNORMAL OCCURRENCE DUE TO SOURCE RANGE INOPERABILITY DURING REACTOR START-UP "On 7/4/17 at 0232 CDT, the University of Missouri-Columbia Research Reactor (MURR) was shut down due to the suspected inoperability of the Source Range Nuclear Instrument Channel during reactor startup. This is a required notification per MURR Technical Specification (TS) 6.6.c.(1) to report to the NRC Operations Center that an Abnormal Occurrence, as defined by MURR TS 1.1, had occurred. Specifically, MURR was not in compliance with all Limiting Conditions for Operations (LCOs). MURR was not in compliance with TS 3.5.a.3. and its associated note (1). TS 3.5.a.3 states, 'The reactor shall not be operated unless the following instrument channels are operable: ...3. Source Range Nuclear Instrument Channel...'. Note (1) clarifies that the Source Range Nuclear Instrument Channel is 'required for reactor startup only.' During the first rod withdrawal of the reactor startup, the Source Range Nuclear Instrument Channel indication was erratic. Therefore, it was decided to shut down the reactor. "The Source Range Nuclear Instrument Channel was repaired by replacing two power supplies in its instrument drawer, the required compliance procedures were conducted on the nuclear instrument, and permission from the Facility Director was obtained prior to the reactor returning to operation later on 7/4/17. Currently, MURR is at 10 MW. A detailed event report will follow within 14 days as required by MURR TS 6.6.c.(3)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | MO | NPR | [5 empty] | 0 | 2017-07-05
52840 | 0 | BWX TECHNOLOGIES, INC. |  |  |  | URANIUM FUEL FABRICATION | 2017-07-04 15:33 | 2017-07-04 16:30 | 2017-07-05 | NO ITEMS RELIED ON FOR SAFETY AVAILABLE / ALERT DECLARED DUE TO LOSS OF PARAMETER CONTROL TO PREVENT CRITICALITY IN THE RESEARCH TEST REACTOR AREA "On July 4, 2017 at 1533 [EDT] it was identified that two desiccant filters serving a dry train ventilation system on a uranium processing glovebox line contained a uranium compound. The two containers were located within close proximity to one another, but were separated during maintenance activities associated with the equipment prior to knowledge of the uranium mass presence. This was assumed to be a non-uranium-bearing system and there were no documented controls in the Integrated Safety Analysis to prevent accumulations. The system was not included in typical duct surveys to identify such accumulations. Uranium processing operations were shut down and the plant is in the summer shutdown outage. There was no immediate risk of criticality or threat to the safety of workers or the public as a result of this event. Security is controlling access to the area and the area will remain shutdown." The initial 10 CFR 70 Appendix A(a)(4) 1 hour report notification was made at 1630 EDT. While making that telephone notification, at approximately 1646 EDT, the licensee communicator notified the Headquarters Operations Officer that the licensee had declared an Alert at 1556 EDT. The Alert declaration was based on a loss of control of all parameters preventing criticality for which control cannot be immediately re-established per the site's Emergency Plan. There is no release and a release is not projected. The licensee's Emergency Operations Center has been activated. The licensee will notify the NRC Resident Inspector. The licensee notified the Commonwealth of VA and local agencies. Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA EOC via conference call. Notified FDA EOC, FEMA NWC, Nuclear SSA and FEMA NRCC SASC via email. * * * UPDATE AT 0231 EDT ON 07/05/17 FROM CHRIS TERRY TO S. SANDIN * * * The licensee has completed preliminary NCS [Nuclear Criticality Safety] calculations based on conservative theoretical analysis and concluded that vessel no. 1, which has the higher loading of material, could achieve a k-effective >1 if conditions were changed, Vessel no. 2 would remain sub-critical under all conditions. The licensee will reconvene their technical staff in the morning to determine what controls could be applied to the higher loaded vessel to evaluate two possible options; the first option is to characterize the material in the sub-critical vessel no. 2 for a better informed NCS analysis of the higher loaded vessel no.1 and the second option is to poison the higher loaded vessel no. 1. The situation remains stable and the licensee continues to restrict access to the RTR Processing Area. Notified R2DO (Heisserer), NMSS (Moore), IRD (Stapleton) and NMSS Events Notification and Fuels Group via email. * * * UPDATE AT 0938 EDT ON 07/05/17 FROM ROBERT JOHNSON TO S. SANDIN * * * The licensee is still reviewing the NCS calculations to identify the appropriate course of action and will reconvene the technical staff at 1300 EDT. Following this meeting, additional surveys of the area will be performed. Notified R2DO (Heisserer), NMSS (Moore), IRD (Stapleton) and NMSS Events Notification and Fuels Group via email. * * * UPDATE AT 1437 EDT ON 7/5/17 FROM ROBERT JOHNSON TO JEFF HERRERA * * * The Licensee is reporting no change in status they are still in an Alert condition. The licensee reported that the density of the desiccant is being re-evaluated. It is expected that actual density is less than initial assumed density which is favorable. The net effect should be to reduce the estimated grams inside the unit. Reduced estimated grams will improve the safety margin and assist the recovery process. Additional calculations and modeling is being conducted and more information is expected at a licensee discussion meeting at 1600 EDT. The Emergency Operations Center remains staffed at this time. The NRC Resident Inspector has been notified. Notified R2DO (Heisserer), NMSS (Moore), IRD (Grant) and NMSS Events Notification and Fuels Group via email. * * * UPDATE AT 1954 EDT ON 7/5/2017 FROM ROBERT JOHNSON TO MARK ABRAMOVITZ * * * "On July 5, 2017 at 1857 (EDT) BWXT LOG-Lynchburg downgraded form an Alert status. Based on a conservative estimate of U-235 mass and an accurate characterization of the desiccant material involved, Nuclear Criticality Safety (NCS) has determined that a criticality is highly unlikely. Updated evaluations based on as-found conditions and technical information provided by the system manufacturer demonstrated the maximum amount of U-235 in system #1 and system #2. Current NCS controlled parameters in place are mass, moderation, spacing, and container geometry. NCS has determined that the worst case K-adjusted is below the normal license limit. Based on this information, there was no immediate risk of criticality or threat to the safety of workers or the public as a result of the event. Access to the area remains restricted under the control of Security and the Emergency Operations Center." The licensee will notify the NRC Resident Inspector. Notified R2DO (Heisserer), NMSS (Moore), IRD (Grant) and NMSS Events Notification, Fuels Group (via email). Notified DHS SWO, DOE Ops Center, FEMA Ops Center, HHS Ops Center, DHS NICC, USDA Ops Center, EPA EOC via conference call. Notified FDA EOC, FEMA NWC, Nuclear SSA and FEMA NRCC SASC via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | ALL SAFETY ITEMS UNAVAILABLE | [8 empty] | ALERT | 2 | VA | FUE |  | 70.32(i) | PART 70 APP A (a)(4) |  |  | 0 | 2017-07-17
52839 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2017-07-03 10:15 | 2017-07-03 12:32 | 2017-07-03 | MANUAL REACTOR SCRAM ON LOW CONDENSER VACUUM "At 1015 [EDT] a manual reactor scram was inserted due to degrading main condenser vacuum. All rods inserted into the core as expected and all systems functioned as expected during the scram. "This event is reportable within 4 hours per 10 CFR 50.72(b)(2)(iv)(B) 'any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' "At 1033 [EDT] an automatic reactor scram occurred on low reactor water level. Due to the previous manual reactor scram, all rods were [already] inserted. "This event is reportable within 8 hours per 10 CFR 50.72(b)(3)(iv)(A) 'any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a preplanned sequence during testing or reactor operation. (1) Reactor protection system (RPS) including : Reactor scram and reactor trip.'" Decay heat is being removed using main feedwater and the turbine bypass valves. The licensee notified the NRC Resident Inspector. This event was characterized as a "configuration control event" where a valve misposition allowed the offgas line to flood. | 0 | 0 | 0 | 42 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-07-03
52838 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2013-12-12 | 2017-07-03 11:22 | 2017-07-03 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION The following report was received from the South Carolina Department of Health and Environmental Control via e-mail: "This event was first reported to the State as an allegation but is now being reported as an incident because of our recent IMPEP [Integrated Materials Performance Evaluation Program] review. "The unplanned contamination was because of the dissolution of a Po-210 Static Eliminator containing 125 microcuries. The contamination was discovered when a Graduate Research Assistance was surveying himself upon exiting the lab. The RSO was notified and the lab was thoroughly decontaminated. The laboratory was posted and access was restricted. The licensee was required to report this incident within 24 hours of discovery because the unplanned contamination caused a restricted area to be closed for more than 24 hours." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-07-11
52837 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2017-07-01 14:20 | 2017-07-01 17:35 | 2017-07-01 | SODIUM HYPOCHLORITE IN EXCESS OF STATE PERMIT LIMITS "At 1420 EDT on 7/1/17, Fermi 2 determined that the site was in violation of its National Pollutant Discharge Elimination System (NPDES) permit due to chemical addition pumps (for the cooling tower reservoir) being out of service for approximately seventeen hours. This resulted in sodium hypochlorite concentrations exceeding state limits. As of 0855 EDT [on] 7/1/17, the levels of sodium hypochlorite were restored to less than measureable values. "Reports will be made to the Michigan Department of Environmental Quality (MDEQ) and other local agencies. Since these reports are in the process of being made, this is considered a news release or notification to other government agencies, therefore this event is reportable under 10 CFR 50.72(b)(2)(xi). "The NRC Resident Inspector has been notified." The licensee also notified Monroe County. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-07-01
52836 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2017-06-30 01:30 | 2017-06-30 09:04 | 2017-06-30 | CONDENSATE STORAGE TANK DECLARED INOPERABLE "On June 30, 2017 at time 0130 [EDT], the Condensate Storage Tank (CST) was declared inoperable per Technical Specification 3.7.6. A pin hole sized through wall leak was discovered on the downstream side of CD-123, 32 Auxiliary Boiler Feed Pump Bearing Cooling Relief Valve, which is unisolable to the CST. No type of Non-Destructive Examination (NDE) can be used to effectively characterize the defect. Based on the inability to characterize the defect and the fact that the degradation mechanism is not readily apparent, the valve is considered inoperable because the valve has lost its ability to maintain a pressure boundary. As a result, the CST is inoperable. Currently, the CST has 580,000 gallons of water contained in the tank, which is well above the minimum required amount of 360,000 gallons. City water is the backup means to supply water to the Auxiliary Feedwater System, and this has been verified to be operable in accordance with the Actions of the Technical Specification. The CST must be restored to operable status within 7 days. "The CST provides cooling water to remove decay heat and the minimum amount of water in the Condensate Storage Tank is the amount needed to maintain the plant for 24 hours at hot shutdown following a trip from full power. The CST satisfies Criteria 2 and 3 of 10 CFR 50.36. "This event was determined to be reportable as a Loss of Safety Function pursuant to 10 CFR 50.72(b)(3)(v)(B)." The licensee will notify the NRC Resident Inspector and the State of New York. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2017-06-30
52835 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-06-28 | 2017-06-29 15:58 | 2017-06-29 | AGREEMENT STATE REPORT - UNABLE TO RETRACT SOURCE DUE TO CRIMPED GUIDE TUBE The following report was received from the Texas Department of State Health Services via email: "On June 29, 2017, the Agency [Texas Department of State Health Services] was notified by a licensee's radiation safety officer (RSO) that one of his radiography crews experienced an event. The radiographers were testing a 24 inch pipe and the shoots required the use of an extension on the guide tube and the use of a stand. While retracting the 56 curie iridium-192 source back to the QSA 880D camera, the stand fell on the guide tube extension crimping it far enough that the source could not be retracted beyond the crimp. The radiographers set up new boundaries and contacted the RSO. The RSO stated the source was driven to the end of the guide tube and shielding was placed over the source. The guide tube extension was removed from the camera and disconnected from the guide tube. The crank out assembly was dismantled and the drive cable was pulled through the camera and guide tube extension. The cable was inserted through the camera and the source retracted into the exposure device. The individual who recovered the source received 287 millirem (as indicated on their self-reading dosimeter.) The equipment was delivered to the manufacturer for inspection and repair or disposal. Additional information will be provided as it is received in accordance with SA-300. "Texas Incident Number: I9499" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-07-07
52834 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2015-01-12 | 2017-06-29 14:42 | 2017-06-29 | AGREEMENT STATE REPORT - MALFUNCTION OF LOCKING MECHANISM ON RADIOGRAPHY EXPOSURE DEVICE The following was reported by the New Mexico Radiological Health Division via email: "Desert NDT (dba Midwest Inspection Services) reported a malfunction with the locking mechanism on a radiography exposure device (INC model IR-100, serial #4644). The incident involved an Ir-192 source (INC model 32, serial #X717) with an activity of 3,589 GBq (97 Ci). After completing an exposure on 1/12/2015 [at a temporary job site near Malaga, NM], the radiographer performed radiation surveys on the radiography device and noted that readings were high. The radiographer attempted to crank the source into the fully shielded position, but was unsuccessful. The 2 mR/hour boundary was verified and the RSO was contacted. The RSO responded to the site and had to drill a hole in the retaining ring on the locking mechanism. By pulling the retaining ring back, he was able to turn the key, push the button, and retract the source. The exposure device locking mechanism was replaced. "New Mexico ID Number: NM150001 and NMED ID Number: 150291" This is a late report entry identified by an audit. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2017-07-07
52833 | 0 | SUMMER | 1 |  |  | [1] W-3-LP,[2] W-AP1000,[3] W-AP1000 | 2017-06-29 08:57 | 2017-06-29 12:43 | 2017-06-29 | AUTOMATIC TRIP DUE TO A LOSS OF NORMAL FEEDWATER FLOW TO B STEAM GENERATOR "On 6/29/2017 at 0857 [EDT], VC Summer Nuclear Station automatically tripped due to a loss of normal feed water flow to the B Steam Generator. "There were no complications with the trip. All control rods fully inserted. All emergency feedwater pumps automatically started and recovered steam generator levels. "The plant is stable in Mode 3. Station personnel are investigating the cause of the loss of normal feedwater to the B Steam Generator. This is reportable per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). "The NRC Resident Inspector has been notified." The licensee notified the State of South Carolina as well as Fairfield, Lexington, Richland and Newberry Counties regarding the event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2017-06-29
52832 | 0 | NJ RAD PROT AND REL PREVENTION PGM |  |  |  |  | 2017-06-28 | 2017-06-28 17:03 | 2017-06-28 | AGREEMENT STATE REPORT - ORPHANED Cs-137 SOURCE RECOVERED The following information was received from the State of New Jersey via email: "Received a preliminary report today that a metal recycling center (Sims Metal Management) has isolated a Cs-137 source estimated to be about 30 mCi. Exposure readings on contact are 5 R/hr. Source is isolated and secure. The owner of Sims Metal Management contacted Ecology Services who arrived today, identified the nuclide, took the contact readings, conducted wipe tests and will package it and properly and dispose of it in the near future. Ecology Services received reciprocity from NJ for this work. There are no reported markings on the source. DEP [NJ Department of Environmental Protection] personnel will investigate further. More to follow." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | AGR |  |  |  |  | 0 | 2017-07-06
52831 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2017-06-28 07:15 | 2017-06-28 09:49 | 2017-07-05 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following is excerpted from an email from the Maryland Department of the Environment: On 06/28/2017 at 7:15 EDT, the State project engineer (PE) reported that his project trailer had been broken into and a portable nuclear gauge (serial number 062051) was stolen. The equipment was kept stored, with a lock on the outside of the trailer and then locked inside the trailer. The gauge was stored locked in its carrying case. The gauge model number is Troxler 3440. The gauge contains an 8 mCi Cs-137 source and 40 mCi Am-241/Be source. Prince George's County Police Department was notified. * * * UPDATE AT 1507 EDT ON 7/5/17 FROM ALAN JACOBSON TO MARK ABRAMOVITZ * * * The following report was received via e-mail: "The Maryland Department of the Environment (MDE) has reported that the portable nuclear gauge stolen on June 28, 2017 from a Maryland Department of Transportation, State Highway Administration (SHA) Project has been recovered. The gauge was apparently found abandoned on a residential property in District Heights, Maryland and recovered by Prince Georges County Police on July 4, 2017 with assistance from the Prince Georges County Fire/EMS Department's HAZMAT Division. The gauge was not damaged. Inspectors from the MDE's Air and Radiation Administration inspected the gauge, confirmed the device was not damaged and it was returned to the SHA Radiation Safety Officer on July 5, 2017." Notified the R1DO (Ferdas), ILTAB (Tucker), IRD (Grant), and NMSS Resources (via e-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2017-07-06
52830 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2017-06-26 17:56 | 2017-06-27 01:05 | 2017-06-27 | SECONDARY CONTAINMENT DECLARED INOPERABLE "On June 26, 2017 at 1756 PDT, Reactor Building (Secondary Containment) pressure rose above the Technical Specification (TS) requirement multiple times from 1756 to 1800. "Secondary Containment was declared inoperable and entry into Technical Specification Action Statement 3.6.4.1.A was made. There was a significant change in average wind speed and barometric pressure occurring at that time. "At 1800 PDT, Secondary Containment pressure was restored to within limits and TS 3.6.4.1.A was exited. Environmental conditions have stabilized. The Reactor Building Differential Pressure controllers are working as designed. "This condition is being reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and accident mitigation. "The licensee has notified the NRC Resident Inspector." | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2017-06-27
52829 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2017-06-26 | 2017-06-26 18:39 | 2017-06-26 | MANUAL REACTOR TRIP DUE TO LOSS OF MAIN FEEDPUMP "On June 26, 2017, at 1531 [EDT], Indian Point Unit 2 inserted a manual reactor trip prior to Steam Generator levels reaching the automatic reactor trip setpoint. Steam Generator water level perturbation resulted from a loss of 22 Main Boiler Feed Pump. All Control Rods verified inserted. The Auxiliary Feedwater System started as designed and supplied feedwater to the Steam Generators. Heat removal is via the Main Condenser through the High Pressure Steam Dumps. Offsite power is being supplied through the normal 138kV feeder 95332. The cause of the 22 Main Boiler Feed Pump loss is currently under investigation. Entergy is issuing a press release/news release on this issue." Unit 2 is stable and in Mode 3. There was no impact on Unit 3. The licensee notified the State of New York and the NRC Resident Inspector. | 0 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2017-06-26
52828 | 0 | ITT ENIDINE INC. |  |  |  |  | 2017-06-26 | 2017-06-26 14:42 | 2017-06-26 | PART 21 - POTENTIAL TRANSDUCER COMPONENT DEFECT The following information was received via fax: "This letter is a Part 21 notification to the US Nuclear Regulatory Commission of a potential component defect. "The ITT Conoflow models GT25CA1826 and GT25CD1826 current to pressure (l/P) transducers produce a calibrated 3.0 to 15.0 psi output pressure from a 4.0 to 20.0 mA DC (input) signal. "On May 5, 2017 a non-safety related GT25CA1826 was received for evaluation. This transducer would not respond to the 4 to 20 mA operating signal. The failure was caused by a defective solder joint at a coil lead terminal on the printed circuit board. The circuit board was replaced and the unit worked correctly. "An immediate inspection of all stock revealed additional parts with defective solder joints. Based on our [Enidine] investigation, circuit boards with defective solder joints are limited to two lots, received on April 29, 2016 and May 27, 2016. Preventive measures have been implemented to prevent recurrence. "We [Enidine] have produced and shipped the following safety related products that have used parts from these two lots of circuit boards: Enertech Purchase Order No.: 638764 Utility/Station P.O. No.: 15018770 Qty: 2 Part Number: GT25CD1826 Serial Numbers: 628974 and 628975 Customer/Station: Enertech\Gefran [Benelux NV] Enertech Purchase Order No.: 638942-1 Utility/Station P.O. No. 500603219 Qty: 1 Part Number: GT25CA1826 Serial Numbers: 629276 Customer/Station: Enertech\Arizona Power [Palo Verde] Enertech Purchase Order No.: 639238 Utility/Station P.O. No.: 343472 Qty: 2 Part Number: GT25CD1826 Serial Numbers: 629454 and 629455 Customer/Station: Enertech\CCI [Control Components Inc.] "Facilities which have procured suspect product will be notified and advised how to examine their stock for the potential defect. ITT will provide verified replacements for any defective or suspect circuit boards." Enidine 105 Commerce Way Westminster, SC 29691 Phone: (864)-647-9521 Fax: (864}-647-9574 Jeff Gotthelf Engineering Manager | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-06-26
52827 | -1 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2017-06-25 11:00 | 2017-06-25 14:57 | 2017-07-26 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which procedural compensatory measures were not employed within time limits. Region IV (Ray Kellar) will be contacted regarding this one hour report as San Onofre does not have an NRC Resident Inspector. * * * UPDATE FROM TIM CUSICK TO VINCE KLCO ON 6/25/17 AT 2020 EDT * * * All compensatory measures are in place. The licensee will notify Region IV. Notified the R4DO (Gaddy). * * * RETRACTION ON 7/26/17 AT 1700 EDT FROM PHYLLIS DOMINGUEZ TO DONG PARK * * * The purpose of this notification is to retract a previous report made on 6/25/2017 (EN 52827) made under 10CFR73.71. Subsequent to the initial notification, a follow up engineering evaluation determined that the compensatory measure was not required. Region 4 will be notified as SONGS does not have a Resident Inspector Notified R4DO (Hay) and 73.71 Safeguards group via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  |  | Defueled | Defueled |  | Defueled | Defueled | NON EMERGENCY | 4 | CA | POW |  | 73.71(b)(1) |  |  |  | 1 | 2017-06-25
52826 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-06-24 10:28 | 2017-06-24 15:42 | 2017-06-24 | LOSS OF SECONDARY CONTAINMENT "On June 24, 2017 at 1028 [EDT], a loss of secondary containment occurred due to trip of 2V217A Zone III Filtered Exhaust Fan causing a reduction in D/P [differential pressure] to less than the required 0.25 WC [water column]. "2V217B Zone III Filtered Exhaust Fan started on low flow in AUTO as designed and secondary containment D/P was restored to greater than 0.25 WC by 1029 hours. "This event is being reported under 10 CFR 50.72(b)(3)(v)(c) and per the guidance of NUREG 1022, Rev. 3, section 3.2.7 as a loss of a safety function. There is no redundant Susquehanna secondary containment system." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-06-24
52825 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2017-06-23 20:18 | 2017-06-23 23:58 | 2017-06-24 | AUTOMATIC REACTOR SCRAM ON MAIN GENERATOR TRIP "While performing a scheduled generator voltage regulator test, River Bend Station experienced an automatic scram when the main generator tripped. It is unknown at this time why the main generator tripped. "There were no equipment issues that materially impacted post scram operator response. "The intention at this time is to go to cold shutdown while the cause of the trip is investigated." All rods inserted during the scram. Reactor water level is being maintained via normal feedwater with decay heat being removed via turbine bypass valves to the main condenser. The electrical grid is stable and supplying plant loads via the normal shutdown electrical lineup. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-06-24
52824 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-06-23 | 2017-06-23 16:47 | 2017-06-27 | AGREEMENT STATE REPORT - POSSIBLE DOSE EXCEEDING LIMITS RECEIVED The following information was received via E-mail: This event occurred at a field site in or near Orla, Texas. "On June 23, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee's radiation safety officer (RSO) that an event had occurred involving one of their radiography crews. The RSO stated while performing radiography operations at a field site, a radiographer had approached a SPEC 150 exposure device (camera) containing an 81 Curie iridium-192 source to disconnect the guide tube. After reaching down to disconnect the guide tube, the radiographer noticed the guide tube was not completely attached to the camera and their exposure device (ND 2000 dose rate meter) was pegged high on the times ten scale. The source was then fully retracted to the fully shielded position. The radiographer stated his hand was in close proximity to the guide for about 10 seconds. The radiographer stated his self-reading dosimeter was reading 52 millirem after the event. The RSO stated the radiographers were on their way back to their office. The RSO stated the TLD badges for radiographers would be sent in for reading by their dosimetry processor. The RSO stated the radiographers would be interviewed and the licensee would inform the Agency on Monday, June 26, 2017, what their investigation revealed. The RSO did not have any additional information. Additional information will be provided as it is received in accordance with SA-300. Texas Incident #: I-9496 * * * UPDATE FROM ART TUCKER (VIA EMAIL) TO HOWIE CROUCH AT 1027 EDT ON 6/27/17 * * * The following information was received via E-mail: "On June 27, 2017, the Agency contacted the licensee and inquired on the status of the radiographer exposed during this event. The licensee's radiation safety officer (RSO) stated they have not seen any changes in the appearance of the radiographer's hands. The RSO stated the radiographer has not felt any discomfort in his hands. The RSO stated a blood sample will be sent to Radiation Emergency Assistance Center/Training Site (REAC/TS) in Oak Ridge, Tennessee, for analysis. Additional information will be provided as it is received in accordance with SA-300." Notified R4DO (Vasquez), NMSS Events Notification and NSIR (Milligan) by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-07-03
52823 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2017-06-21 | 2017-06-23 16:13 | 2017-06-23 | AGREEMENT STATE REPORT - LEAKING SEALED SOURCE The following information was received from the Commonwealth of Massachusetts via email: "The licensee reported on June 23, 2017 that licensee learned from its licensed leak test service provider on June 21, 2017 that one 6 millicurie, cobalt-57 sealed source out of 25 sources received in a package on June 16, 2017 from the source manufacturer, Eckert & Ziegler Isotope Products, tested positive for leakage. The leakage was reported as being 4.2 times the limit of 0.005 microCuries (0.021 microCuries). The other 24 sources showed no contamination. "The leaking sealed source is an Eckert & Ziegler Isotope Products Model 3901-2 source, serial number P6-883. "The licensee reported that the leaking source was contained and secured in an individual zip lock type plastic bag; that there is no facility contamination based on area surveys performed; that the external surfaces of the package received, that had contained all of the 25 source, had been wipe tested and that the package was not contaminated; and that the sources were not used pending leak test results. "The licensee reported that it notified the source manufacturer on June 21, 2017, received a return authorization number from the manufacturer, and shipped the source back to the manufacturer on June 22, 2017. "The Agency [Massachusetts Radiation Control Program] considers this event to be open." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2017-07-03
52822 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2017-06-22 11:30 | 2017-06-23 11:37 | 2017-08-02 | AGREEMENT STATE REPORT - IRRADIATOR EQUIPMENT MALFUNCTION The following information was received from the State of North Carolina via email: "On June 22, 2017 at [1130 EDT], North Carolina Radiation Protection Section (RPS) was informed by the Radiation Safety Officer for Hospira, Inc. (Pfizer), Rocky Mount, NC (License 064-0969-1) that they were experiencing an issue involving their Wet Shielded Irradiator (Nordion Model JS-8900, Serial Number IR-183, approved for 4,800,000.00 Ci of Co-60). RSO stated that during routine maintenance checks the Source 1 Rack of the irradiator would not trip the down switch to confirm the source rack was in the down position on the control panel and that they were following emergency procedures. Nordion was then contacted by the licensee to obtain assistance. RPS inspectors were immediately dispatched to the licensee's site. "Once on site, RSO informed RPS that visual confirmation was made of source position via hydraulic cylinders that were fully extended, comparison of cable tightness on roof was observed, and that no indication of radiation in the vault was detected; all leading to the unconfirmed indication that the source rack had moved to the down position. With the assistance from Nordion, Hospira staff were able to initiate bypass procedures and gain access to the vault where confirmation was made that the source racks were in the down position. "Nordion advised that a faulty down position switch was the cause for the failure. Switch was repaired on site by Hospira engineers, same day. Following repair, Hospira personnel cycled the sources which were brought up into position for one sterilization cycle and then the sources were brought down to test the position sensor. The test was successful, as indicated by the down position indicator lamps and screen on the operator's panel. Nordion staff was informed of the successful test and Hospira staff continued procedural tests to confirm full functionality. After confirming cycling up and down of the source racks, Hospira personnel performed full monthly QA check before resuming operations. 30-Day report is pending to RPS." * * * UPDATE ON 8/2/2017 AT 1042 EDT FROM TRAVIS CARTOSKI TO DONG PARK * * * The following information was received from the State of North Carolina via email: "We have completed our investigation and have no further information to provide in this event report. We would like to request [NMED] Event 170315 be Closed & Complete." Notified R1DO (Lilliendahl) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-07-03
52821 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2017-06-22 20:43 | 2017-06-23 01:00 | 2017-06-23 | LOW PRESSURE CORE SPRAY DECLARED INOPERABLE DUE TO LOSS OF COOLING "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. The Unit 1 Low Pressure Core Spray (LPCS) Pump Injection System was declared inoperable at 2043 [CDT] due to a loss of corner room area cooling and loss of motor cooling. The common diesel generator cooling water pump received an auto trip signal while being secured. The LPCS pump remained in standby during the event. This condition prevents LPCS, a single train safety system, from performing its design function. This is a reportable condition as an 8 hour ENS notification. "The required action of Technical Specifications (TS) 3.5.1, 'ECCS - Operating,' was entered on June 22, 2017 at 2043 CDT when the condition was identified and the LPCS system was determined to be inoperable. Investigation into the cause of the condition is in progress." The Low Pressure Core Spray (LPCS) Pump Injection System was declared operable, and the TS LCO was exited at 2112 CDT. * * * UPDATE FROM RICHARD IMMKE TO DONALD NORWOOD AT 1518 EDT ON 6/23/2017 * * * "Update to previous ENS notification at 0100 EDT on 6/23/17. The last statement was revised to say the Low Pressure Core Spray System remains Inoperable." "The Low Pressure Core Spray (LPCS) Injection System remains inoperable." The licensee notified the NRC Resident Inspector. Notified R3DO (Pelke). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-06-23
52820 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2017-06-20 14:44 | 2017-06-22 20:33 | 2017-06-22 | SECONDARY CONTAINMENT DECLARED INOPERABLE DUE TO BOTH AIRLOCK DOORS OPEN SIMULTANEOUSLY "On June 20, 2017, at 1444 hours [EDT], with the reactor at 100% core thermal power and steady state conditions, plant personnel identified that both doors in one of the secondary containment airlocks (Door #58 and Door #85) were open briefly as part of normal passage of personnel. "The Technical Specification definition of SECONDARY CONTAINMENT INTEGRITY states 'At least one door in each access opening is closed.' Actions were taken to immediately close both doors and restore operability of secondary containment. PNPS [Pilgrim Nuclear Power Station] is providing an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(v)(C), an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The NRC Resident Inspector has been notified." The licensee notified the Commonwealth of Massachusetts. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-06-22
52819 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-05-03 | 2017-06-22 10:15 | 2017-06-22 | AGREEMENT STATE REPORT - THEFT OF INTELLECTUAL PROPERTY The following information was received via facsimile: "On June 22, 2017, the Agency [Texas Department of State Health Services] determined, based on a review of documentation related to a security incident at a licensee which was received on June 15, 2017 and an onsite meeting at the licensee on June 16, 2017, that this event was reportable to the Agency. Specifically, on May 3, 2017, the licensee determined that the Radioactive Sealed Source Manager, an employee in the Trustworthy and Reliability Program, had downloaded a large amount of confidential information including inventory of radioactive material. "The IT contractor for the licensee reported that the Radioactive Sealed Source Manager downloaded the data from the licensee server on April 25, 2017. The employee was terminated on May 3, 2017. On May 3, 2017, the Houston Police Department and the Federal Bureau of Investigation were notified of the incident. During an exit interview on May 4, 2017, the employee admitted to downloading procedures, security information, and inventories because he wanted to start his own company to compete against the licensee. No theft occurred of radioactive material. "On May 5, 2017, the portable hard drive was returned to the licensee. A lawsuit was filed against the individual on May 22, 2017 and a temporary restraining order was filed on May 24, 2017. The licensee hired an onsite armed security guard during normal working hours for 30 days. The investigation by LLE, the FBI, and the Agency is ongoing. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 1 | 2017-06-25
52818 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-27 00:29 | 2017-06-22 09:32 | 2017-06-22 | INVALID SPECIFIED SYSTEM ACTUATION DUE TO FAILED RELAY "On April 27, 2017 at 0029 EDT, Unit 2 received an invalid partial Group 2 isolation due to a failed relay (2D11-K80) on the auxiliary trip unit. Both of the U1 and U2 Standby Gas Treatment (SGT) trains started and the U2 Group II primary containment and all secondary containment inboard isolation valves closed. Also, the refuel floor isolation dampers closed, the reactor building supply and exhaust fans tripped, and the refueling floor supply and exhaust fans tripped. "This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) since the containment isolation and auto-start of SGT on both units was not part of a pre-planned sequence and the event resulted in the invalid actuation of general containment isolation valves in more than one system. "All primary and secondary containment inboard isolation valves and SGT systems functioned successfully. The failed relay was replaced and the systems were restored to normal alignment. "The licensee will notify the NRC Resident Inspector." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-06-22
52817 | -1 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-06-21 10:00 | 2017-06-21 16:25 | 2017-08-02 | POSTULATED FIRE EVENT COULD ADVERSELY IMPACT SAFE SHUTDOWN EQUIPMENT "During the review of an electrical circuit coordination calculation to support an ongoing revision of the Fire Safe Shutdown Analysis (FSSA), a lack of appropriate circuit protection coordination was identified in the coordination of electrical protective devices on 118 VAC electrical panels operating in bypass mode of operation. "One or more of these electrical panels could be lost for various 10 CFR Appendix R III.G.2 fires outside the Control Room at CPNPP [Comanche Peak Nuclear Power Plant] due to circuit coordination issues. This could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "Immediate compensatory actions are being taken to establish (or confirm already existing) fire watches in the Fire Areas containing the associate circuits which can potentially jeopardize the FSSA. "This condition is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition. "The NRC Resident Inspector has been notified." * * * RETRACTION ON 8/2/17 AT 1638 EDT FROM BRIAN MITCHELL TO BETHANY CECERE * * * "On 06/21/2017 Comanche Peak reported an ENS Report (no. 52817) related to the potential loss of 118 VAC electrical panels operating in bypass mode of operation for various 10 CFR [50] Appendix R III.G.2 fires outside the Control Room due to circuit coordination issues. This could adversely affect safe shutdown equipment and potentially cause the loss of the ability to conduct a safe shutdown as required by 10 CFR 50 Appendix R. "Subsequent analysis by Engineering has determined that the affected panels remain coordinated for fire generated faults and can be credited as available by the Fire Safe Shutdown Analysis for a fire outside of the Control Room. "Based on the above, the condition described in the ENS report no. 52817 is not considered to be an unanalyzed condition as described in 10 CFR 50.72(b)(3)(ii)(B)." The licensee notified the NRC Resident Inspector. Notified R4DO (Azua). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2017-06-21
52816 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2017-06-19 | 2017-06-21 13:51 | 2017-08-28 | AGREEMENT STATE REPORT - DOSE DELIVERED TO SITE ADJACENT TO INTENDED TARGET The following State of Utah report was received by email: "The licensee delivered a 500 cGy fraction of HDR [High Dose Rate] brachytherapy to a site adjacent to the intended target. This treatment was a supplemental boost to external beam radiotherapy, and the mistreated volume was included in the target volume of the external beam plan." The State of Utah was notified of the event on June 21, 2017 by electronic mail opened at 1125 MDT. Utah Event Report ID No: will be provided in follow up report. * * * UPDATE at 1212 EDT ON 8/28/17 FROM SPENCER WICKHAM TO MARK ABRAMOVITZ * * * The following information was received via e-mail: "The licensee name needs to be changed from 'University of Utah, Radiological Health Department' to 'Jordan Valley Medical Center, LP'." Notified the R4DO (Gaddy) and NMSS Events Notification via e-mail. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2017-06-29
52815 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-06-19 | 2017-06-20 11:51 | 2017-06-20 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON GAUGE The following report was received by the State of Texas via email: "On June 20, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that the shutter on a Thermo Fisher model SUP-1C gauge containing a 100 milliCurie source would not close. The gauge is located in a remote location at the facility and does not create an exposure risk to any individual. The manufacturer has been contacted and will be on site today, June 20, 2017, to repair the gauge. Additional information will be provided as it is received in accordance with SA-300." The source is Cs-137. The gauge serial number is TG-564. Texas Incident #: I 9495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-06-28
52814 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2017-06-19 23:53 | 2017-06-20 08:18 | 2017-06-20 | HIGH PRESSURE COOLANT INJECTION INOPERABLE "At 2353 CDT on 6/19/2017, while performing the High Pressure Coolant Injection (HPCI) quarterly surveillance following planned maintenance, the HPCI turbine did not start as expected due to the HPCI turbine stop valve failing to open. This issue is being reported under 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function at the time of discovery. Investigation into the failure of the HPCI system to start is in progress. The unit remains at 100% power. The health and safety of the public was not affected. "The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-06-20
52813 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-06-19 21:15 | 2017-06-20 03:31 | 2017-06-20 | PRIMARY CONTAINMENT DECLARED INOPERABLE DUE TO FAILURE OF DRYWELL TO SUPPRESSION CHAMBER VACUUM BREAKER TO FULLY CLOSE "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D), 'any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.' "At time 2115 CDT on June 19, 2017, one torus to drywell vacuum breaker failed to indicate that it was closed after being cycled for surveillance testing. The vacuum breaker had been cycled open and then closed to satisfy SR 3.6.1.8.2 - Perform a functional test of each required vacuum breaker. Failure of the vacuum breaker to indicate closed after the control switch was taken to the closed position represents a failure to satisfy SR 3.6.1.8.2 and SR 3.6.1.8.1 - Verify each vacuum breaker is closed. Primary containment is allowed to have a bypass area between the drywell and suppression chamber less than or equivalent to a one inch diameter hole. The are of bypass was indeterminate while the vacuum breaker did not indicate fully closed. Primary containment was declared inoperable during the time the vacuum breaker did not indicate fully closed. "The vacuum breaker control switch was subsequently cycled open and closed one additional time. At time 2311 CDT, the vacuum breaker indicated fully closed. At that time, primary containment was declared operable. "Currently, all twelve Drywell to Suppression Chamber vacuum relief valves are closed and in the normal line-up. "The NRC Senior Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-06-20
52812 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2017-06-16 16:35 | 2017-06-17 00:32 | 2017-06-17 | LOSS OF SAFETY FUNCTION DUE TO KEOWEE DAM UNITS BEING DECLARED INOPERABLE "Keowee Hydro Units [KHU] 1 and 2 were both declared inoperable at 1635 [EDT] on 6-16-17 due to discovery of breaker 1GSC-1 (KHU-1) in the intermediate position, and breaker 2GSC-1 (KHU-2) in the open position. Keowee Hydro Units are required to be operable per TS [Technical Specification] 3.8.1 (AC Sources - Operating), TS 3.8.2 (AC Sources - Shutdown), and TS 3.7.10 (Protected Service Water, applies only to KHU aligned to the Overhead Power Path). All Tech Spec required conditions were entered, and all required actions completed. Both Standby Buses were energized from a Lee Combustion Turbine via an isolated power path at 1715 [EDT] on 6-16-17 in accordance with TS 3.8.1 Condition (I), Required Action (I.1). "It has been determined by station personnel that a loss of safety function did occur between 1635 [EDT] (when the Keowee Hydro Units were declared inoperable) and 1715 [EDT] (when the Standby Buses were energized from a Lee Combustion Turbine via an isolated power path). "Investigation has determined the cause of breakers 1GSC-1 and 2GSC-1 being out of their required closed position to be inadvertent bumping while performing station work activities. Breakers 1GSC-1 and 2GSC-1 have been reclosed, and both Keowee Hydro Units have been declared operable as of 2351 [EDT] on 6-16-17." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2017-06-17
52811 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2017-06-16 17:00 | 2017-06-16 18:20 | 2017-06-16 | UNANALYZED CONDITION IDENTIFIED "At 1700 EDT on June 16, 2017 it was determined that an unanalyzed condition was identified that failed to meet performance criteria. This report is conservatively being made in accordance with 10CFR70 Appendix A (b)(1). "In the powder process, a non-radioactive additive is added to a can of uranium in a hood. A previous process hazard analysis (PHA) determined that a criticality in the associated HEPA filters was not credible during this step. A recent update to a criticality analysis identified a potential condition where small amounts of uranium could build up in the HEPA filter over decades. The ISA [Integrated Safety Analysis] team met and decided that current safety controls will need to be implemented as IROFS [items relied on for safety] to assure that performance criteria are met. The operation is currently shut down and no unsafe condition existed. "Safety Significance of Events: At no time was an unsafe condition present. "Safety Equipment Status: The operation was shutdown. "Status of Corrective Actions: Additional corrective actions, extent of condition, and extent of cause are being investigated." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2017-06-26
52810 | 0 | TE CONNECTIVITY |  |  |  |  | 2017-06-02 | 2017-06-16 12:04 | 2017-06-16 | PART 21 NOTIFICATION - POTENTIAL DEFECT IN ETR14 CLASS TE CONNECTIVITY RELAYS TE Connectivity reported that one of their relays, TE Part Number 7-1423177-5, ETR141B3BNC2023004, failed at TVA Labs during normal continuously energized operation. An investigation conducted with TVA Labs identified that a mis-oriented capacitor may have caused the failure. Although the failure occurred with only one part number, all relays in the ETR14 family with date codes from 1604 to 1650 contain the suspect capacitor. A root cause analysis is underway by the vendor. If you have any questions or require any additional information, please contact me by email or telephone: Terry Ducker Quality Manager TE Connectivity Aerospace, Defense and Marine Division 1396 Charlotte Highway Fairview, NC 28730 E-mail: duckert@te.com Telephone: 828-338-1063 Fax: 828-338-1101 Quantity Supplied - Customer: 41 - Alabama Power 5 - ATC Nuclear 3 - Curtiss-Wright Nuclear 10 - Curtiss-Wright/QualTech NP 2 - Duke Energy Progress/Harris 16 - Energy Northwest/Columbia 4 - Engine Systems Inc 2 - Entergy/Pilgrim 39 - Entergy/River Bend 25 - Exelon/Limerick 2 - Exelon/Oyster Creek 12 - Exelon/Peach Bottom 2 - GE Hitachi Nuclear Energy 2 - Georgia Power/Hatch 2 - Nextera Energy Point Beach 5 - Talen Energy/Susquehanna 2 - TE/Germany 4 - TE/UK 6 - TVA/Browns Ferry 4 - TVA/Sequoyah 2 - TVA/Watts Bar Unit 1 9 - Xcel Energy/Monticello | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-06-16
52809 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2017-06-14 | 2017-06-16 09:01 | 2017-06-16 | AGREEMENT STATE REPORT - LOSS OF CONTROL OF LICENSED MATERIAL The following was received from the Commonwealth of Kentucky: "Sometime in February 2009 during the decommissioning of the licensee's laboratory, the electron capture detector (ECD) contained in a Varian model 3700 gas chromatograph went missing. The ECD was an Amersham model NBC containing 8 mCi of Ni-63, S/N A404, assay date 2/14/1992. The licensee discovered the device was missing during a routine inspection by the KY Radiation Health Branch. This event is actively being investigated by the licensee." KY Event Report ID No: KY170005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2017-06-26
52808 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-06-15 12:19 | 2017-06-15 18:23 | 2017-06-15 | TEMPORARY LOSS OF SHIELD BUILDING "At 1219 [EDT] on June 15, 2017, annulus vacuum exceeded its pressure limit. At that time, the Shield Building was declared inoperable in accordance with Technical Specification 3.6.15 Condition A and B, due to the inoperability of the Shield Building (CRE). At 1222 [EDT], annulus pressure returned to normal, Shield Building was declared operable and LCO 3.6.15, Condition A and B were exited. "The temporary loss of the Shield Building resulted from a loss of pressure control in the Auxiliary Building caused by a loss of Auxiliary Building General Ventilation. The Auxiliary Building Gas Treatment System was started to maintain Auxiliary Building pressure within limits and the non-safety related Annulus Vacuum system automatically restored annulus pressure. "The Shield Building ensures that the release of radioactive material from the containment atmosphere is restricted to those leakage paths and associated leakage rates assumed in the accident analysis during a LOCA. The EGTS system [Emergency Gas Treatment System] would have automatically started and performed it's design function to maintain Annulus Vacuum within required values. "This event is being reported pursuant to 10 CFR 50.72(b)(3)(v)(D). "NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-06-15
52807 | 0 | PROVIDENCE ALASKA MEDICAL CENTER |  |  |  |  | 2017-06-14 | 2017-06-15 15:26 | 2017-06-28 | PATIENT RECEIVED A HIGHER DOSE THAN PRESCRIBED On 6/14/17 a patient undergoing treatment using Sir-Spheres (Y-90) received a dose of 540 Gray instead of the 110 Gray prescribed. This occurred due to a calibration error. The prescribing physician discussed the error with the patient who was released and returned home. The Radiation Safety Officer (RSO) is investigating the incident. No adverse effect to the patient has been observed to date. * * * UPDATE PROVIDED BY YONGLI NING TO JEFF ROTTON AT 1816 EDT ON 06/28/2017 * * * The original report is being updated to reflect that the dose information provided initially was for the liver (prescribed organ). Thera-Spheres were used in the procedure versus the Sir-Spheres as stated in the original report. The licensee also provided received dose information for the lung of 25.76 Gray from the event described above. Notified the R4DO (Kellar) and NMSS Events Notification group via email. A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2017-06-23
52806 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-06-15 09:58 | 2017-06-15 13:14 | 2017-06-15 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "At 0958 hours (CDT), during planned surveillance testing of the Division 3 Shutdown Service Water (SX) subsystem, the Division 3 SX pump tripped for unknown reasons. The Division 3 SX subsystem was declared inoperable and in accordance with Technical Specification 3.7.2, Action A.1, the High Pressure Core Spray (HPCS) system was declared inoperable. Since the HPCS system is a single train safety system, this event is reportable under 10CFR50.72(b)(3)(v)(D). An investigation is underway to determine the cause of the SX pump trip. "The NRC Resident has been notified." | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-06-15
52805 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-04-16 10:53 | 2017-06-15 11:32 | 2017-06-15 | INVALID EDG ACTUATION DURING SURVEILLANCE TESTING "This is to report the Salem Unit 2, 2C Emergency Diesel Generator (EDG) actuation due to an invalid signal. "This report is being made per paragraphs 10CFR50.73(a)(1) and 10CFR50.73(a)(2)(iv)(A) to address the invalid actuation of the 2C EDG on April 16, 2017, while performing the 2C Safeguards Equipment Controller (SEC) Mode OPS Surveillance test. "Plant conditions: Salem Unit 2 was in mode 5 at the time of the invalid actuation. "On April 16, 2017, at approximately 1053 [EDT] while performing Solid State Protection System (SSPS) testing of the 2C SEC, the 2C Emergency Diesel Generator (EDG) output breaker was manually opened per the associated procedure step. The EDG output breaker unexpectedly reclosed and the 2C 4kV vital bus loaded onto the EDG in SEC Mode 2. "The cause of the 2C EDG output breaker reclosure and 2C 4kV Vital bus loading during testing was determined to be two faulty input block switches in the 2C SEC. When Step 5.2.27 of the test procedure was performed, the 2C SEC 'input block' switches failed to block a 'blackout' actuation signal. This resulted in the breaker reclosure and loading of the 2C Vital Bus onto the EDG. Trouble shooting identified that the two failed switches exhibited high resistance across the switch contacts which is indicative of being in a 'fail to block' (the input signal) condition. "The licensee has notified the NRC Resident Inspector." The licensee will also notify the States of New Jersey and Delaware. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-06-15
52804 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-06-13 07:30 | 2017-06-14 16:29 | 2017-06-14 | AGREEMENT STATE REPORT - INCORRECT SOURCE SHIPMENT The following report was received from the Louisiana Department of Environmental Quality [LDEQ] via email: "Event Date and Time: On June 13, 2017, 0730 [CDT] the e-mail was received by LDEQ. The report was for two Elekta Clients under timely renewals who both received Ir-192 sources for HDR [High Dose Rate] units. Neither set of documentation matched the sources it was accompanying. Both sources were manufactured, calibrated and shipped from the A&O [Alpha-Omega Services, Inc.], LA facility on April, 27, 2017. "Facility #1: A report of an HDR source being shipped to Texas Oncology PA where the source activity was less than the activity ordered and documented from the source received. The source received was actually 8.98 Ci Ir-192, but the shipping documents and source information listed the source as 11.28 Ci Ir-192. The mis-documented source was returned and a new source with the correct activity and documentation was requested. The source was an exchange source as a replacement source for the Texas Oncology PA, dba Texas Cancer Center Sherman [TCCS], Sherman, TX 75090. TX License # L05019, Amendment #23, Expiration date: January 31, 2016. The licensee is under a timely renewal and on Amendment #31. The Source S/N D36G1424. "Facility #2: The report of an HDR source being shipped to New York Oncology Hematology PC (NYOH), Albany, New York, 12206. NYSDH Radioactive Material License No. 5284, Amendment #6, DH Number 09-1113. The HDR source received was 13.88 Ci of Ir-192 on May 10, 2017. The documentation for the source received was 11.01 Ci of Ir-192. This source is being held for decay and will be put into service June 13, 2017. A&O sent a source with incorrect documentation that is in violation NYOH license for activity received and activity installed in the HDR unit. The Source S/N D36G1425. "A&O is a source supplier for Elekta HDR units. Elekta's ordering process notifies A&O when sources should be shipped/supplied their licensees. "Event Location: The shipments originated from Alpha and Omega Services, Vinton, LA 70668 and were delivered to TCCS, Sherman, TX 75090 and NYOH, Albany, New York 12206. Neither facility received the quantity of radioactive material they ordered and were licensed to receive nor was the documentation for the radioactive material correct. The facilities were licensed each to receive an Ir-192 HDR source. "Event type: Calibrating, shipping and delivery of radioactive material in quantities greater than the licensed activities and under documented quantities. The licenses were correct, but the sources shipped were greater than the facility was licensed to receive and/or the documentation accompanying the RAM Ir-192 sources for each HDR units was incorrect. A&O explained that their reference numbers were mixed up during the manufacturing process. "The A&O errors were detected by TCCS and NYOH licensees when they were performing their QC/QA on the active sources prior to patient treatment. "The shipments were intact and not damaged. The sources were secure and in the hands of trained radiation safety personnel. Health and safety to the radiation workers and general public was not the issue. The issue was the reference numbers did not match the calibration activities of each source and wrong activities were shipped. "Notification: On June 8, 2017, the error, quantities of RAM greater than licensed activity was discovered and reported to A&O. On June 8, 2017, the replacement source was shipped to TCCS. The incident preliminary notification was reported to the LDEQ, Assessment Radiation Section by e-mail on June 13, 2017. Reported to the NRC as LAC 33:XV.340.C. For not reviewing a radioactive material license before transferring radioactive material and LAC 33:XV.328.L.1.C. A permanent label was not affixed to the source or device containing the information on the radionuclide." LA Event Report ID No.: LA-170009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-06-22
52803 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-17 11:20 | 2017-06-14 08:42 | 2017-06-14 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "On April 17, 2017 at 1120 EDT, following scheduled maintenance, the Reactor Protection System (RPS) 'A' bus was returned to its normal supply, the RPS 'A' motor generator (MG) set. The RPS MG set had been running loaded for 1 hour when the RPS 'A' bus tripped. Maintenance personnel had connected probes of a grounded oscilloscope to check for proper operation of the MG set, resulting in the RPS 'A' bus trip. The controlling procedure did not contain a caution about using only an ungrounded oscilloscope. The trip of the RPS 'A' MG set resulted in a half scram and an invalid isolation signal causing primary containment isolation valves in multiple systems to isolate. "This event is reportable per 10 CFR 50.73 (a)(2)(iv)(A) since the containment isolation was not part of a pre-planned sequence and the event resulted in the invalid actuation of general containment isolation valves in more than one system. "Corrective actions include revising the governing procedure with the proper precaution and limitation to require the use of an ungrounded oscilloscope. A training needs analysis will also be performed to cover the lessons learned from this event. "The licensee notified the NRC Resident Inspector." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-06-14
52802 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-06-12 09:14 | 2017-06-12 13:50 | 2017-06-20 | OFFSITE NOTIFICATION FOR DISCHARGE OF CIRCULATING WATER "On Sunday, June 11, 2017 at 1200 CDT, a Chemistry Technician reported water from the Circulating Water Blowdown (CW B/D) valve building had been pumped onto the ground outside the CW B/D building during a maintenance activity. The sump in the CW B/D building has a sump pump discharge hose that had been routed outside to the ground near the outfall canal rather than to the permitted outfall path. Water sample analysis results confirmed the presence of tritium. The sump pump discharge hose was rerouted to the required outfall on June 11th, 2017 at 1500 CDT. The discharge flow did not leave the site boundary before reaching the permitted discharge pathway. "In accordance with the Braidwood Station Illinois Environmental Protection Agency (IEPA) Consent Order dated March 11, 2010, the IEPA was notified of the blowdown line release on June 12, 2017 at 0914 CDT; the Illinois Emergency Management Agency (IEMA) was subsequently notified. Local agencies in the Braidwood area will also be notified. "Follow-up analyses are being performed to determine if additional IEPA or IEMA notifications will be required. The release tank values for other radionuclides (i.e., other than tritium) were interpolated based on tritium values for the release tank, dilution from the CW B/D, and sampled sump tritium values; and determined to be less than Minimum Detectable Activity (MDA). "Within 4 hours of determination that state and local agencies notification will be made, the NRC Operations Center is required to be notified. There were no public health risks associated with the event. The NRC Resident Inspector was notified. Due to the notification of government agencies, this event is being reported under 10 CFR 50.72(b)(2)(xi)." * * * UPDATE ON 6/14/17 AT 1650 EDT FROM JOHN LOGAN TO DONG PARK * * * "The Illinois Environmental Protection Agency (IEPA) and the Illinois Emergency Management Agency (IEMA) were notified on Wednesday, June 14, 2017, at 1206 CDT and 1213 CDT, respectively, of the preliminary results of estimated quantity of curies of tritium release (approximately 0.009 curies of tritium) and the estimated volume of the release (approximately 35,000 gallons). The discharge flow did not leave the site boundary before reaching the permitted discharge pathway. The NRC Resident Inspector was notified of the update to IEPA and IEMA." Notified R3DO (Stone). * * * UPDATE FROM CRAIG FOBERT TO HOWIE CROUCH AT 1656 EDT ON 6/16/17 * * * "The Illinois Environmental Protection Agency (IEPA) and the Illinois Emergency Management Agency (IEMA) were provided with a follow-up report on June 16, 2017, at 1528 CDT as required by 35 IAC 1010.204. The report includes the estimated quantity of curies of tritium released (approximately 0.009 curies), the estimated volume of the release (approximately 35,000 gallons), and actions taken in response to the on-site release (installation of groundwater monitoring wells, implementation of a sampling program to monitor the concentrations and migration, if any, of the tritium in the groundwater on-site, and the installation of a remediation system). "The NRC Resident Inspectors have been notified of the update to IEPA and IEMA." Notified R3DO (Stone). * * * UPDATE ON 6/20/17 AT 1435 EDT FROM MIKE NOLAN TO BETHANY CECERE * * * "On 6/20/2017, the Illinois Environmental Protection Agency (IEPA) Des Plaines Regional Office was sent a follow-up report pursuant to the Consent Order, dated March 11, 2010. This report contains that same information as the follow-up report required by 35 IAC 1010.204 that was submitted to the IEPA and the Illinois Emergency Management Agency on June 16. 2017. "The NRC Resident Inspector has been notified of the update to IEPA." Notified R3DO (Pelke). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OTHER UNSPEC REQMNT |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-06-12
52801 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2017-06-11 09:11 | 2017-06-11 14:35 | 2017-06-11 | EXCESSIVE BONNET LEAKAGE FROM CHEMICAL VOLUME CONTROL SYSTEM VALVE "At Indian Point Energy Center [IPEC], Unit 3 normal letdown was isolated due to a significant body/bonnet leak on the inlet valve to Reactor Coolant Filter. Shift team took action to isolate letdown and stop the leak. The Abnormal Operating Procedure (AOP) was entered, normal letdown was isolated per procedure, and excess letdown was placed in service to balance inventory at 61 percent Pressurizer Level. This was above the Technical Specification [3.4.9] level of 54.3 percent which was exceeded at 0911 [EDT], putting the unit in a 6-hour shutdown action statement. The valve body/bonnet was torqued, successfully eliminating the leakage. Pressurizer Level was restored to the normal control band and the AOP was exited at 1136. The SM [Shift Manager] estimated the leakage at 18 gallons per minute when leak was active. No EAL [Emergency Action Level] thresholds were exceeded. This occurrence is considered a safety system functional failure per 10 CFR 50.72(b)(3)(v)(A), requiring an 8-hour NRC report. Both IPEC units are stable at full power." The licensee has notified the NRC Resident Inspector and the New York State Public Service Commission. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2017-06-11
52800 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-06-10 22:56 | 2017-06-11 01:00 | 2017-06-11 | MANUAL REACTOR SCRAM DUE TO LOSS OF FEEDWATER HEATING At 2256 CDT on 6/10/17, Clinton operators manually scrammed the reactor from 99 percent power due to a loss of feedwater heating. The scram was uncomplicated and the plant is stable and in mode 3. All rods inserted and decay heat is being removed by the condenser. All offsite power is available. The cause of the loss of feedwater heating is under investigation. The NRC Resident Inspector and the State of Illinois have been notified. | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-06-11
52799 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-06-09 | 2017-06-09 17:04 | 2017-06-09 | AGREEMENT STATE REPORT - IRRADIATOR DRAWER STUCK IN INTERMEDIATE POSITION "On June 9, 2017 it was reported to the department that, following a routine irradiation of two samples, the drawer containing the irradiated material ground to a halt while being raised from the irradiation position. The drawer is currently stuck in an intermediate position. Following the halting of the device, the licensee immediately removed it from service and contacted the manufacturer to schedule servicing of the device. Area monitors indicate that there are no elevated radiation levels. The device is J.L. Shepherd Model 143-45-C irradiator. The department will dispatch inspectors to perform an investigation." WI Event Report ID No.: WI-170008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-06-19
52798 | 0 | ENGINE SYSTEMS, INC |  |  |  |  | 2017-06-08 | 2017-06-09 17:00 | 2017-06-09 | PART 21 REPORT - DEFECTIVE MOTOR OPERATED POTENTIOMETER The following information is excerpted from an Engine Systems, Inc. (ESI) report received via fax: "Component: Motor operated potentiometer without pre-position feature P/Ns: 72-07900-100-ESI 2-04E-184-103-ESI 2-00G-009-002-ESI "System: Emergency Diesel Generator "Summary: Engine Systems Inc. (ESI) began a 10CFR21 evaluation on April 12, 2017 following correspondence with Duke Energy - Catawba Nuclear Plant of a potential issue with a motor operated potentiometer (MOP) supplied by ESI. During bench testing, Duke was unable to adjust the cams of the MOP to operate the pre-position feature (also referred to as return-to-center). Further investigation revealed that the MOP supplied to Duke did not contain the desired cam arrangement. "The evaluation was concluded on June 8, 2017 and it was determined that this issue is a reportable defect as defined by 10CFR21. For installations that rely on the pre-position function to drive generator output voltage to a predetermined setpoint in an emergency event, an incorrect cam arrangement on the motor operated potentiometer could negatively affect the emergency diesel generator [EDG] set's output voltage. This may prevent the EDG from carrying its safety-related loads in an emergency event. "Discussion: A motor operated potentiometer is commonly used in the voltage regulator system of emergency diesel generator sets to allow for local or remote adjustment of generator output voltage. The assembly supplied by ESI was a replacement for obsolete Portec/NEI part number 72-07900-100. ESI initiated a Supplier Deviation Notification [SDN] (Part Number Change) to replace the obsolete part with one that would serve as a functional replacement using the same mounting footprint. To accomplish this, a Basler brand MOP was selected. The "-ESI" suffix was added to designate a modification to the Basler MOP by replacing the standard 2W, open-wound potentiometer with a 3W, precision-wound potentiometer identical to the one used in the original Portec units. The SDN indicated that the replacement MOP would have the pre-position feature. Note that the SDN would later be revised to include replacements for Cooper-Bessemer part numbers 2-04E-184-103 and 2-00G-009-002 which represented the same Portec part number 72-07900-100. "The Basler MOP selected by ESI for the assembly was model MOC2103. A review of Basler model MOC2103 indicates that it is not a return-to-center style device and instead contains a standard cam arrangement. Photos on the following page depict the differences between the two cam arrangement styles. ESI inadvertently selected the incorrect model for this application. Reviewing the qualification testing performed by ESI revealed that ESl's testing duplicated the original Portec test procedure (whereby one cam is set to close above setpoint and one cam is set to close below setpoint). However, the testing was shown to be inadequate to fully ensure the return-to-center functionality. Though the cams were properly set above and below setpoint, a further verification that the unit would return to center, even if sufficiently away from setpoint, was not performed. For installations that rely on the preposition function, it is possible that the MOPs supplied by ESI would not return the potentiometer to setpoint. Since the MOP is used to set output voltage of the emergency diesel generator, the consequences of this issue are that the EDG may not maintain voltage within its required range to support its safety-related loads. "Root cause evaluation: ESI selected the incorrect MOP to be used for this assembly. The original MOP used was a Portec/NEI P/N 72-07900-100 which became obsolete in the 1990s. ESI offered a replacement assembly (using the "-ESI" suffix) that included a Basler brand MOP, modified by replacing the factory supplied potentiometer to replicate the original Portec design. The original Portec MOP had the return-to-center feature and Basler offers some models with return-to-center and some without. ESI inadvertently selected the model without return-to-center. "As a secondary cause, ESl's functional testing did not adequately verify the MOPs ability to return to center. The test procedure has steps to set the cams and limit switches as would be performed for the return-to-center style; however, the testing did not ensure that the cams would return the potentiometer back to the center, regardless of starting position. [photos submitted with report with following captions:] "Photo 1: Desired Return-to-Center Cam Arrangement Photo 2: As-Supplied Standard Cam Arrangement Photos 3&4: Return-to-Center Cam Profile & Arrangement Photo 5&6: Standard Cam Profile & Arrangement "Evaluation of previous shipments: ESI has supplied the replacement MOP from 2009 to 2016 on five (5) separate safety-related orders. A review of each order Indicates that the incorrect MOP was selected for the assembly. "Affected Customers: ESI has supplied motor operated potentiometers with the incorrect cam arrangement to the following customers. "Part Number 72-07900-100-ESI; Customer Duke Energy - Catawba; Customer PO 196046; Qty 6; ESI Serial Numbers 3013905-1.1-1 thru 6; MOP Serial Numbers H01931980, H01995582, H01995584, H01995585, H01995586, H01995587; C-of-C Date 5/30/2015 "Part Number 72-07900-100-ESI; Customer Dremel/CFE - Laguna Verde; Customer PO 14-011/700427979; Qty 1; ESI Serial Number 3011566-3.1-1; MOP Serial Number H01798043; C-of-C Date 2/13/2015 "Part Number 2-04E-184-103-ESI; Customer APS - Palo Verde; Customer PO 500530279; Qty 3; ESI Serial Numbers 3005695-1.1-1 thru 3; MOP Serial Numbers: H00958610, H00961219, 333861; C-of-C Date 7/31/2009 "Part Number 2-04E-184-103-ESI; Customer APS - Palo Verde; Customer PO 500555659; Qty 3; ESI Serial Numbers 3008341-1.1-1 thru 3; MOP Serial Numbers H01151813, H01161548, H01161550; C-of-C Date 212/2012 "Part Number 2-00G-009-002-ESI; Customer South Texas Project; Customer PO 200410; Qty 2; ESI Serial Numbers 3015607-1.1-1 thru 2; MOP Serial Numbers H02027435, H02027436; C-of-C Date 8/19/2016 "Total Quantity 15 "Corrective Action: Customers that have installed the motor operated potentiometer must evaluate the impact on their specific system. It may be acceptable to continue to use the MOP if other provisions are in place to ensure the EDG voltage is within an acceptable range for safety-related operation. Credit may also be taken for site acceptance testing following installation of the MOP. If the MOP is deemed acceptable for the application, no further action is necessary. "For those customers that have determined the MOP is unacceptable for their application and/or would simply rather ensure they have the correct MOP, it may be returned to ESI for warranty replacement. Once a warranty order and Return Goods Authorization (RGA) is issued, supply of safety-related replacement MOP(s) is expected to be complete within 90 days. "To prevent recurrence of this issue, ESI is implementing a revision to the procurement process for this assembly to update the part number of the MOP utilized. In addition, the dedication inspection and testing activities are being revised to ensure testing properly validates the return-to-center feature. This action is currently underway and will be completed prior to any future shipments." If you have any questions, you may call: Tom Horner Quality Assurance Manager Tel: (252) 977-2720 ESI Report ID: 10CFR21-0117, Rev. 0, dated 06/09/17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | DEFECTS AND NONCOMPLIANCE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21(d)(3)(i) |  |  |  | 0 | 2017-06-09
52797 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-06-09 05:09 | 2017-06-09 12:51 | 2017-06-09 | EXHAUST FAN BREAKER FAILURE CAUSING LOW SECONDARY CONTAINMENT DIFFERENTIAL PRESSURE "On June 9, 2017 at 0509 [EDT], Secondary Containment Zone 3 (Unit 1 and 2 Reactor Building) differential pressure lowered to 0 [inches] WG [water gauge] during a routine restoration due to equipment failure. One of the two Unit 1 Zone 3 exhaust fan breakers experienced a failure that during procedural restoration caused Secondary Containment Zone 3 to experience a positive differential pressure. Required differential pressure per SR 3.6.4.1.1 could not be maintained. "Zone 3 differential pressure was recovered to [greater than] 0.25 [inches] WG following restart of Unit 2 Zone 3 Secondary Containment fans. All other Zones of Secondary Containment were unaffected by this event. "This event is being reported under 10 CFR 50.72(b)(3)(v)(C) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as a loss of a Safety Function. There is no redundant Susquehanna Secondary Containment System. "The NRC Resident Inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-06-09
52796 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2017-04-10 13:47 | 2017-06-09 10:17 | 2017-06-09 | INVALID SYSTEM ACTUATION DURING TESTING "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of several safety systems. "On April 10, 2017 at 1347 hours [EDT] with Unit 3 in Mode 6 during performance of the Train B Engineered Safeguards Integrated Test, safety system actuations occurred prior to the expected point in the test procedure when a loss of continuity resulted while the seismic clips were being removed from a fuse. The actuations were supposed to occur at a subsequent step when the fuse was to be pulled to actuate the Hi Containment Pressure signal. As a result, the following equipment actuated: 3B, 4A and 4B High Head SI pumps; 3B Containment Spray pump; Containment Isolation and Containment Ventilation Isolations; 3A and 3B Emergency Diesel Generators; Emergency Containment Coolers. Because an actual high containment pressure signal did not exist at the time of the actuation, the actuation is considered invalid. All equipment responded as expected. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-06-09
52795 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-06-08 15:27 | 2017-06-08 19:10 | 2017-06-08 | AUTOMATIC REACTOR SCRAM AFTER MAIN TURBINE CONTROL LOGIC LOSS OF POWER "At 1527 hrs [EDT] on June 8, 2017, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a loss of Main Turbine Electro-Hydraulic Control (EHC) logic power causing a High Flux Reactor Power RPS [Reactor Protection System] trip. "All control rods [fully] inserted and both reactor recirculation pumps tripped due to reaching reactor water level 2. Reactor water level lowered to -49 inches causing Level 3 (+13 inches) and Level 2 (-38 inches) isolations. HPCI [High Pressure Coolant Injection] and RCIC [Reactor Core Isolation Cooling] automatically initiated and were overridden by control room operators after RPV [Reactor Pressure Vessel] water level was restored to the normal band with feedwater. HPCI and RCIC injected to the Reactor Coolant System during reactor level stabilization. All isolations and initiations occurred as expected. No main steam relief valves opened. Pressure was controlled via main turbine bypass valve operation. All safety systems operated as expected. "Secondary Containment Zone 1, 2, and 3 differential pressure lowered to 0 inch WG [Water Gauge] due to a trip of the Reactor Building Ventilation system that resulted from Unit 1 Level 2 isolation. Differential pressure was restored to Zones 1, 2, and 3 by the initiation of Standby Gas Treatment System on the Unit 1 Level 2 initiation. "Unit 1 reactor is currently stable in Mode 3. Investigation into the loss of Main Turbine EHC logic power is underway. "The NRC Resident Inspector has been notified. A voluntary notification to PEMA and press release will occur." The suspected cause of the loss of power to the EHC logic circuit is ongoing maintenance on the system. | 0 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | Power Operation | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2017-06-08
52794 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2017-06-06 | 2017-06-08 15:22 | 2017-06-08 | AGREEMENT STATE REPORT - MOISTURE/DENSITY GAUGE LOST IN TRANSIT The following report was received via e-mail: "Preston was sending a Troxler gauge to Troxler located in North Carolina for a repair of a faulty battery pack. Preston scheduled a package pick-up by [common carrier] on May 8, 2017 from Preston's Macon hub. The licensee stated the typical expected turn-around time for a gauge repair is 3 weeks. Troxler does not send the licensee a receipt confirmation when they receive the customer's gauge. On June 6, 2017, when the licensee had not received the gauge back from Troxler, they made a call to Troxler inquiring about the repair status of the gauge. Troxler informed the licensee they had not received the gauge. The licensee contacted [the common carrier] and asked them to track down the gauge. Based on the tracking information the licensee has, the gauge was last scanned on May 9, 2017 in TN. After some search, [the common carrier] scanned the package on either 5/18 or 5/19/17 at their International Bond Cage. According to [the common carrier], the package would have been scanned daily if it were shipped internationally. [The common carrier] will continue to search for the package. In the meantime, the licensee will follow-up with a written report." Sources: 8 mCi Cs-137 S/N 750-1945 and 40 mCi Am-241:Be S/N 47-24708 Device: Troxler 3430, S/N 28005 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2017-06-16
52793 | 0 | MAINE RADIATION CONTROL PROGRAM |  |  |  |  | 2017-06-07 11:40 | 2017-06-08 12:41 | 2017-06-23 | AGREEMENT STATE REPORT - DOSE TO PATIENT WAS LESS THAN PRESCRIBED DOSE The following information was received from the State of Maine via email: "The following is a brief description of the event that occurred today in the [Maine Medical Center] (MMC) Cath Lab during an intravascular Brachytherapy (IVB) case. "The source train was deployed to treat the 1st dwell position of the cardiac stent. Following delivery of the prescribed dose to the 1st dwell position the source train became stuck during return to the afterloader and could not be freed. This required complete removal of the catheter with the source train and placement of it in the bailout box. "As a result, only 1 dwell position was treated causing the delivered dose to vary by more than 20 percent of the prescribed dose. "The prescribed dose was 1840 REM. MMC does not have the exact delivered dose estimate, but it is approximately 50 percent of the prescribed [dose] because they had planned on 2 dwell positions. "MMC will follow this up with a full written report as required by SMRRRP G.3045.D. The Licensee will be providing a full report to the State within 15 days as required." Maine Event Report: ME 17-003 A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. * * * UPDATE FROM THOMAS HILLMAN TO VINCE KLCO ON 6/23/17 AT 1500 EDT * * * The following update excerpted information received from the State of Maine via email: "A brief description of the event: During an IVB procedure the patient was intended to receive two dwells of radiation to cover a treatment area longer than the source train. After the first dwell position the source train become stuck in the catheter and did not properly retract to the after loader, when it was determined that the source was stuck (10-15 seconds), the catheter was pulled from the patient. The catheter, after loader, and source were placed in the bail-out-box. Only one of the two dwell positions was delivered. A survey of the room, the patient (was conducted to insure that source was removed from the patient), and the source was properly secured. The manufacturer, chief physicist, radiation safety and state radiation safety control were contacted. "Why the event occurred: The reported complaint of failed hydraulic return of the Jacketed Radiation Source Train (JRST) to the Transfer Device (TD) was confirmed. The delivery catheter (DC) source lumen was found not passable by the JRST as a result of a deformation at 7.3 cm distal to the strain relief. The JSRT stopped location would have been outside the patient. The precise cause of the DC deformation is not known. The location and nature of the deformation suggest compression by a device or handling during intervention. Based upon available case information, the most likely scenario is compression of the catheter during a challenging advancement into a commonly tortuous vessel - the left internal mammary artery (LIMA). From published case reports in the literature, although successful in the majority of patients, percutaneous coronary revascularization of the left internal mammary artery using the transfemoral approach is usually a technically challenging procedure. Technical difficulties involved in LIMA intervention from the femoral approach stems from the acute angle between the proximal subclavian artery and the proximal left internal mammary artery. Thus, guide catheter support is often poor. In addition, the relatively long length and tortuosity of the LIMA (graft) make guidewire manipulation and balloon delivery difficult. These technical considerations magnify the difficulty of intervention. For these reasons, it is not unusual or unexpected that operators will experience difficulty advancing devices through the tortuous LIMA -including the distal mono-rail tip design Novoste B-rail delivery catheter. The potential for deformation of the catheter during advancement and navigability challenges in that artery is recognized. The Beta-Cath System User's Manual explicitly advises that the JRST may not navigate Internal Mammary (IM) guide catheters designed specifically for accessing left internal mammary arteries. Despite these challenges, the skilled operators in this case were able to successfully place the delivery catheter and deliver the JRST. In this case it is suspected that the DC source lumen deformation was very slight, not affecting movement during the sending of the JRST since the pressure is highest in the send lumen nearer to the device. However, the return hydraulic pressure is much lower behind the JSRT on return movement as it approaches the transfer device and was apparently not sufficient to overcome resistance of the dimensional interference. This hypothesis is consistent with the results of the method used to improve the source lumen for eventual hydraulic return of the JSRT. "The effect, if any, on the individual(s) who received the administration: There was no effect on the patient. The patient is not excluded from receiving the additional course of intravascular brachytherapy, if restenosis and symptoms should occur. "What action, if any, have been taken or at planned to prevent recurrence: Based on this event, no corrective actions are felt to be necessary. "Certification that the licensee notified the individual and if not, why not: No notification was made to the patient. This decision was based on the Cardiologist's determination that the area of stenosis within the stent was covered by the 1st dwell position and the area did receive the prescribed dose of 18.4 Gy." Notified the R1DO (Arner), NMSS Events Notification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | ME | OTH | AGR |  |  |  |  | 0 | 2017-06-16
52792 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2017-06-06 10:00 | 2017-06-07 12:13 | 2018-03-20 | AGREEMENT STATE REPORT - STUCK OPEN SHUTTER ON DENSITY GAUGE The following information was provided by the State of Arkansas via email: "During routine shutter checks performed by the licensee on June 6, 2017, the licensee noted that the shutter would not close. "The gauge is identified as Berthold Model LB 300 L source holder containing 0.189 milliCuries of Cobalt-60. "The gauge remains operational in the normal use location and the RSO will place additional signs in the area. No maintenance is planned in the area that would require closing of the shutter. The RSO has performed a radiation survey to ensure that radiation exposure is maintained at less than 2 mR/hr in the vicinity of the gauge. "The licensee has contacted the technical representative who was expected to be at the facility on July 6, 2017, for other maintenance and will examine this gauge. "In accordance with RH-1502.f.2 (10 CFR 30.50(b)(2)) the malfunctioning shutter is reportable within 24 hours. "The State of Arkansas is awaiting a written report from the licensee and final disposition information for the gauge. The State's event number is AR-2017-003. " * * * UPDATE ON 3/20/2018 AT 1520 EDT FROM STEVE MACK TO DONG PARK * * * The following was received via e-mail: "A report submitted on July 3, 2017, indicated that the cause of the shutter failure was the exposure to alkaline pulp material and the carbon steel construction of the source holder. The source holder was replaced on January 9, 2018 with a comparable source holder constructed of stainless steel. The Department [Arkansas Department of Health] considers this event to be closed." Notified R4DO (Groom) and NMSS Events Notification via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2017-06-15
52791 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2017-06-06 17:51 | 2017-06-06 15:48 | 2017-06-06 | BOTH STANDBY STEAM GENERATOR FEED PUMPS OUT OF SERVICE FOR PRE-PLANNED MAINTENANCE "This notification is in accordance with Turkey Point Technical Specification (TS) 3.7.1.6, Action b.1 to report the inoperability of both Standby Steam Generator Feedwater Pumps (SSGFPs) for greater than 24 hours. "On 6/6/17 at 1751 hours [EDT] both SSGFPs will be inoperable for greater than 24 hours in support of planned valve repairs that require isolation of the common suction and discharge piping. TS 3.7.1.6, Action b.1 requires a report within four hours if both SSGFPs have been inoperable for 24 hours providing the cause of the inoperability and restoration plans. The valve repairs are currently planned for completion on or about 2300 hours on 6/9/17 which will restore the 'A' pump to service and allow TS 3.7.1.6, Action b.1 to be exited. The diesel-driven 'B' pump will remain out of service for radiator repair which is currently planned for completion on or about 0800 hours on 6/14/17. "The function of the Standby Steam Generator Feedwater System is as a backup to the Auxiliary Feedwater System and is not credited in the safety analysis." "The NRC Resident Inspector has been notified." Both pumps were taken out of service at 1751 EDT on 6/5/17. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2017-06-06
52790 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2017-04-28 05:00 | 2017-06-06 08:30 | 2017-06-06 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION FOR AN INVALID AUXILIARY FEEDWATER ACTUATION "This 60-day telephone notification is being submitted in accordance with paragraphs 10 CFR 50.73(a)(1) and 50.73(a)(2)(iv)(A) to report an invalid Auxiliary Feedwater (AFW) actuation at Watts Bar Nuclear Plant (WBN) Unit 1. "On April 28, 2017 at approximately 0500 Eastern Daylight Time (EDT), Unit 1 maintenance personnel were performing 1-IMI-3.005, '18 Month Calibration of Anticipated Transient Without Scram System Actuation Circuitry (AMSAC),' when an AMSAC actuation signal was received. Both Motor Driven Auxiliary Feedwater Pumps (MDAFWPs) were already in service when this actuation occurred. The Turbine Driven Auxiliary Feedwater Pump (TDAFWP) did not start as it had been removed from service. Additionally, steam generator blowdown isolated as required. During this event, AMSAC actuation was complete and equipment functioned as expected by its operating state. "Upon identification of the AMSAC actuation, maintenance activities were halted and a prompt investigation was initiated. WBN found that the procedure in use for the 18 month calibration had been recently revised. The procedure called for maintenance to connect an analog multi-meter set on resistance to incorrect points during performance of the procedure. When the analog multi-meter was connected to the incorrect points, a relay was energized resulting in an AMSAC actuation. The procedure was revised and the test completed. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-06-06
52789 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-06-05 16:30 | 2017-06-06 07:34 | 2017-06-06 | AGREEMENT STATE REPORT - TROXLER DENSITY GAUGE DAMAGED AT JOBSITE The following information was provided by the State of South Carolina via email: "Event Location: Highway 51 South of Pamplico, SC "Event Type: Damaged gauge "Event Description: At approximately 4:30 PM on June 5, 2017, the Department [South Carolina Department of Health and Environmental Control] was notified by [a representative] of Mead & Hunt, Inc. that it had a density gauge damaged by a trachoe while at a jobsite on Highway 51 South of Pamplico, SC. The on-call duty officer responded to the scene around 7:30 PM and met [the representative]. Upon arriving at the scene, the duty officer observed that the area around the gauge had been properly roped off. The duty officer and [the representative] approached the gauge with survey meter to identify the level of damage. The gauge was a Troxler 3440 containing 8 millicuries of Cs-137. A radiation readings of 12-16 mR/hr on the surfaces of the gauge were observed and found to be within the normal radiation profile for this gauge. The handle of the gauge was broken off causing the gauge to not properly function. The source shutter was found to be completely in the shielded position. The gauge was returned to the licensee's office in Lexington, SC. "A follow-up inspection of the gauge at the licensee's facility in Lexington, SC will be conducted on June 6, 2017." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-06-14
52788 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-06-05 13:52 | 2017-06-05 19:40 | 2017-06-05 | CONTROL ROOM AIR CONDITIONING AND EMERGENCY VENTILATION SYSTEMS INOPERABLE "At 1352 hours Eastern Daylight Time (EDT) on June 5, 2017, during control building damper inspection activities, a control building instrument air line was disconnected. This resulted in the inoperability of the three Control Room Air Conditioning subsystems required by Technical Specification (TS) 3.7.4, 'Control Room Air Conditioning (AC) System', and the two Control Room Emergency Ventilation (CREV) subsystems required by TS 3.7.3, 'Control Room Emergency Ventilation (CREV) System. As a result, this condition could have prevented the fulfillment of the safety function for these systems. "Control Room AC and CREV system operability was restored at 1407 hours with restoration of control building instrument air. Because Brunswick has a shared control room, this report applies to both Units 1 and 2 and is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "This event did not impact public health and safety. "INITIAL SAFETY SIGNIFICANCE EVALUATION: The safety significance of this event is considered minimal. The condition existed for approximately 15 minutes. Plant staff took immediate actions to return the equipment to service. For the brief time the Control Room AC and CREV systems were inoperable, performance of plant personnel and equipment in the Control Room was not adversely affected. The maximum Control Room back panel temperature during this event was approximately 70 degrees F. "CORRECTIVE ACTIONS: Control Room AC and CREV system operability was restored at 1407 hours with restoration of control building instrument air. "During subsequent investigation of the event, it was determined that at approximately 0930 hours on June 5, 2017, both subsystems of CREV were similarity rendered inoperable due to isolation of control building instrument air. Control Room AC was not affected. Operability of CREV was restored at approximately 1009 hours. This loss of the CREV system was not apparent to Operations personnel at the time of the event." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-06-05
52787 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2017-06-03 06:15 | 2017-06-03 09:29 | 2017-06-03 | OFFSITE NOTIFICATION OF A FATALITY A contract employee had just arrived on-site and sat down at his desk within the protected area. He was taken to the Brattleboro Memorial Hospital where he passed away later in the morning. A news release is planned. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Defueled; FMode1: Defueled | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-06-03
52786 | 0 | WA OFFICE OF RADIATION PROTECTION |  |  |  |  | 2017-05-31 | 2017-06-02 19:59 | 2017-06-02 | AGREEMENT STATE REPORT - PORTABLE GAUGE OPERATOR HANDLED UNSHIELDED SOURCE The following report was received from the State of Washington via email: "An operator of a portable moisture/density gauge touched and directly handled the unshielded source. "Here is how the event occurred: A worker knelt down next to a portable moisture/density gauge and pulled it up, tilted it back, and stuck his face toward the source rod. He then extended the source rod out of the gauge housing and into the air. He then took his left hand and rubbed the source rod clean with his bare hand. "This event was observed by a manager from Oregon Radiation Protection Services, who then reported the event to the Washington State Department of Health for investigation. "Incident Number: WA-17-014" The portable moisture/density gauge is a Troxler 3430 containing 0.333 GBq (9 mCi) of Cs-137 and 1.628 GBq (44 mCi) of Am-241/Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2017-06-12
52785 | -1 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2017-06-02 09:20 | 2017-06-02 17:07 | 2017-07-25 | PENETRATION ROOM FILTRATION BOUNDARY INOPERABLE "This notification is being made as required by 10 CFR 50.72(b)(3)(v) due to both trains of Penetration Room Filtration [PRF] being inoperable due to an inoperable PRF Boundary. At 0920 [CDT] on 6/2/2017, a gap was discovered between an electrical penetration room ceiling and the containment wall where seismic gap material was noted to be missing. The gap was subsequently closed and PRF testing completed sat. The condition was exited at 1345 [CDT]. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 7/25/17 AT 1725 EDT FROM MATT STANLEY TO DONG PARK * * * "On 6/2/17 at 1707 CDT Farley Nuclear Plant notified the NRC Operations Center of an entry into Technical Specification 3.7.12 Condition B for Unit 1 loss of two trains of Penetration Room Filtration (PRF). At 0920 [CDT] on 6/2/2017, a gap had been discovered between an electrical penetration and containment where seismic gap material was noted to be missing. The report was made pursuant to 10 CFR 50.72(b)(3)(v) under Event Notification 52785. Upon further engineering review and satisfactory testing to support operability, Farley has determined that the configuration did not meet the criteria for a condition that could have prevented fulfillment of a safety function, and is retracting the notification. "The NRC Resident Inspector has been notified." Notified R2DO (Blamey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-06-02
52784 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-04-03 | 2017-06-02 16:49 | 2017-06-02 | AGREEMENT STATE REPORT - ELEVATED RADIATION LEVELS AT A RADIOPHARMACY The following information was obtained from the State of Illinois via email: "On May 10, 2017, PETNET Solutions, Inc., a radiopharmacy with a cyclotron, reported high area dosimetry readings inside their facility with the highest reading being 12,276 mrem for the month of April. Readings were also elevated for the first 10 days of May. There were no neutron readings present which indicates that the readings were likely not from the cyclotron itself but from the radiopharmaceutical production process. PETNET was advised to cease cyclotron operations until their team of engineers and health physicists could determine a cause. Agency Inspectors arrived the next day, May 11, 2017, along with engineers and health physicists from PETNET to conduct an investigation at the property. Interviews with PETNET staff and an inspection of the cyclotron/hot cell did not identify any immediate problems. It was determined during the investigation that non-radiation workers opposite the adjoining wall potentially received a radiation dose during this event. The non-radiation worker involved was informed of the event, and PETNET requested permission to place TLDs and do surveys along their common wall over the next week to assess the situation. This was agreed to. In the interim the licensee estimated that the dose to the workstation in this adjoining office was 154.7 mrem. This exceeds the dose limit in regulation 32 IAC 340.310(a)(3) (10 CFR 20.1301(a)(1) equivalent). However, this dose would not represent any health effects to the individual and would be equivalent to approximately two pelvic X-rays at a doctor's office. Currently, PETNET engineers believe the root cause was related to problems in the targetry and delivery systems resulting in multiple instances of F-18 escaping from a v-vial vent. This material then accumulated in the ventilation ducts leading to the filter banks near the area dosimeters on the wall. PETNET has committed to a corrective action plan including additional maintenance on the unit, an alarming radiation detector in the cyclotron vault connected to the operator's panel and additional area dosimeters on the opposite side of the adjoining wall. IEMA [Illinois Emergency Management Agency] has committed to routine site visits until further notice." Item number: IL177005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-06-12
52783 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-06-01 | 2017-06-02 16:19 | 2017-06-02 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE FAILED TO RETRACT The following information was received from the State of Texas via email: "On June 2, 2017, the Agency [Texas Department of State Health Services] was notified by the licensee that one of its radiography crews was unable to retract a 92.5 curie iridium - 192 source into a QSA 880D exposure device. The radiographers had performed several exposures. To perform the radiography, one end of a flexible guide tube was connected to the exposure device and the other end was connected to a stiff guide tube. After completing an exposure, the source hung up in the stiff guide tube and would not retract into the exposure device. The radiographers contacted their management who responded to the site. The stiff guide tube was examined and was found to have several indentations in it that appeared to be preventing the source from passing through the tube. The recovery team straightened out the guide tubes and was able to retract the source into the fully shielded position. The licensee stated the guide tube was not damaged on this date. The licensee has removed the stiff guide tube from service. Additional information will be provided as it is received in accordance with SA 300." Texas Incident No.: I-9488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-06-12
52782 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-06-02 02:41 | 2017-06-02 11:13 | 2017-06-02 | SECONDARY CONTAINMENT DECLARED INOPERABLE "On 6/2/2017 at 0241 CDT, Clinton Power Station entered Mode 2 with secondary containment boundary doors propped open. Specifically, both doors for Reactor Water Cleanup (RT) 'B' pump room were propped open with welding cables routed through pump room doors to perform welding in the RT pump room. "At 0300 CDT, a Senior Reactor Operator identified that the doors were propped open and Secondary Containment was declared inoperable. LCO 3.6.4.1 Required Action A.1 was entered to restore Secondary Containment to Operable in four hours. "At 0324 CDT, the cabling for the welding machine was removed and the doors were closed. "Investigation determined that authorization had been granted while in mode 4, when secondary containment was not required to be operable. The doors were propped open at the beginning of the shift, prior to the mode change to mode 2 (0241 CDT). "This loss of secondary containment is reportable under 10 CFR 50.72(b)(3)(v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2017-06-02
52781 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2017-06-01 16:45 | 2017-06-01 23:41 | 2017-06-01 | LOST ABILITY TO RECEIVE METEORLOGIC DATA "Planned maintenance to restore normal power to Plant Computer Systems resulted in an unexpected loss of all Meteorological (MET) Tower Data [at 1645 CDT]. As a result, this represents a Loss of Emergency Assessment Capability and is reportable under 10CFR 50.72 (b)(3)(xiii). The isolation was restored and MET Tower Data was restored at 1845. The health and safety of the public was not affected as the plant is operating in a normal condition with no severe weather or storms in the area. Additionally meteorological data was available from the National Weather Service should this data had been necessary. "The NRC Resident Inspector has been notified." The licensee will be notifying the State of Minnesota. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-06-01
52780 | 0 | KARMANOS CANCER INSTITUTE |  |  |  |  | 2017-05-31 12:45 | 2017-06-01 12:25 | 2017-06-01 | MEDICAL EVENT - PATIENT RECEIVED LESS DOSE THAN PRESCRIBED "On May 31, 2017, the licensee's gamma knife model 'C' failed during treatment delivery. The couch retracted from the treatment position at 1245 [EDT] due to a clutch malfunction. Three out of five shots were delivered to the single planned lesion. The prescribed volume received a dose of 15 Gy versus the prescribed 20 Gy. Due to uncertainty regarding repair, the fixation frame was removed from the patient's head. Repair was completed at 1845 [EDT]." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2017-06-09
52779 | -1 | VETERANS HEALTH ADMINISTRATION |  |  |  |  | 2017-05-30 07:00 | 2017-05-31 20:08 | 2018-04-04 | EXTERNAL CONTAMINATION ON PACKAGE GREATER THAN ALLOWABLE LIMITS "Pursuant to 10 CFR 20.1906, Veterans Health Administration (VHA) National Health Physics Program is notifying NRC of the receipt of two packages of radioactive material with removable surface contamination on the outside that exceeded NRC reporting limits. "The packages were received on the morning of Tuesday, May 30, 2017, by the Robert J. Dole VA Medical Center in Wichita, Kansas. This facility is a site of use under the VA St. Louis Health Care System, St. Louis, Missouri, which holds VHA permit number 24-00144-05 under the VHA master materials license. The packages were surveyed at about 0700 CDT. The wipe tests performed on the external surfaces of the packages indicated removable contamination of about 1,450 and 1,390 dpm/cm2 as compared to the regulatory limit of 240 dpm/cm2 for beta-gamma emitters. The packages contained unit dosages of fluorine-18 fluorodeoxyglucose. The packages were shipped from Cardinal Health in Wichita, Kansas, which was also the final delivery carrier. A facility nuclear medicine technologist notified the final delivery carrier by telephone of the contaminated packages soon after discovery of the contamination. VHA National Health Physics Program, which manages the master materials license, was notified of the incident at about 1700 CDT on Wednesday May 31, 2017. "The VHA is aware that this notification does not conform to the timeliness requirements in 10 CFR 20.1906. VHA will take appropriate action regarding this apparent noncompliance. VHA will notify our NRC Region III Project Manager of this incident." * * * RETRACTION ON 4/4/18 AT 1330 EDT FROM LYNN GRAVES TO DONALD NORWOOD * * * "On July 18, 2017, the review by the facility Radiation Safety Officer (RSO) determined the event was 'suspect' due to radiation levels from a dose calibrator inducing spurious results in the well counter used for package surveys. The package did not have external radioactive contamination. "The root cause of the report of contamination was identified by the PET [Positron Emission Tomography] technologist. It was a result of counting the package wipes with a radioactive source in the adjacent dose calibrator causing crosstalk between the two instruments. Correct technique was discussed by the RSO with the PET technologist. In addition, staff training of the correct technique was provided for all department personnel. During an onsite inspection in January 2018, the root cause was verified with the inspector having a high degree of confidence that the Wichita facility did not receive an externally contaminated package on May 30, 2017." The licensee notified R3 (Parker). Notified R3DO (Orth) and NMSS Events Notification E-mail group. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Agreement State | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | AR | MAT |  | 20.1906(d)(2) |  |  |  | 0 | 2017-06-08
52778 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-06 12:12 | 2017-05-31 07:50 | 2017-05-31 | INVALID ACTUATION OF EMERGENCY DIESEL GENERATORS "This 60-day optional telephone notification is being made in lieu of an LER submittal, as allowed by 10 CFR 50.73(a)(1). This notification is made pursuant to the reporting requirements specified in 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation of one of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). "On April 6, 2017, at 1212 Eastern Daylight Time (EDT), an invalid actuation of emergency diesel generators (EDGs) 1, 2. 3. and 4 occurred. In support of maintenance associated with the onsite electrical distribution system, activities were in progress to power the 2C balance-of-plant (BOP) bus from the startup auxiliary transformer (SAT) followed by de-energization of the 2D BOP bus. However, flexible links between the SAT and the 2D BOP bus had not been installed. As a result, under voltage sensing relay (27SX) was not energized and an invalid SAT secondary side under voltage EDG auto start signal was generated. There was no actual under voltage on the SAT, no loss of power, and all emergency buses continued to be powered by the unit auxiliary transformer (UAT). "The EDGs responded properly to the auto-start signal. The actuation was complete, in that the EDGs successfully started and ran unloaded. The EDGs were returned to standby status by 1415 EDT. Since no actual under voltage condition existed which required the EDGs to start, and the start was not in response to actual plant conditions satisfying the requirements for initiation, this event has been determined to be an invalid actuation. "This event did not result in any adverse impact to the health and safety of the public." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-05-31
52777 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-05-30 20:38 | 2017-05-30 22:22 | 2017-05-30 | AUTOMATIC REACTOR SCRAM "At 2038 [CDT], Clinton Power Station received an automatic RPS [Reactor Protection System]actuation. EOP-1 [Emergency Operating Procedure] was entered on RPV [Reactor Pressure Vessel] Level 3. The cause of the scram is unknown at this time. All systems responded appropriately following the scram and the plant is currently stable." Reactor level is being maintained by normal feedwater and decay heat is being removed to the main condenser via the steam dump bypass valves. The plant is in a normal shutdown electrical lineup. The plant main generator was synchronized to the electrical grid and the plant was conducting control rod scram time testing at the time of the reactor trip. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2017-05-30
52776 | 0 | VIRGINIA RAD MATERIALS PROGRAM |  |  |  |  | 2017-05-30 | 2017-05-30 16:23 | 2017-05-30 | AGREEMENT STATE - FIXED GAUGE SHUTTER STUCK OPEN The following information was provided by the Commonwealth of Virginia via email: "On May 30, 2017, the licensee reported that the shutter of a fixed gauge failed to close during a routine test of the shutter mechanism. The gauge is a Ronan Model SA1, serial number 1093CK, with a 200 millicurie cesium-137 source (effective May 1995). It is used to measure the level of material inside a process vessel. The gauge is located approximately 10 feet from ground level. It is accessible only by a platform which has been restricted by the licensee. The licensee has contacted the manufacturer to repair or replace the gauge." VA Event Report ID No.: VA-17-007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | VA | OTH | AGR |  |  |  |  | 0 | 2017-06-07
52775 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-05-30 09:29 | 2017-05-30 14:10 | 2017-05-30 | LOSS OF EMERGENCY OPERATIONS FACILITY INTEGRATED COMPUTER SYSTEM DATA FOR PLANNED MAINTENANCE "On May 30, 2017 at 0929 (CDT), South Texas Project (STP) removed from service Integrated Computer System (ICS) connections to the Emergency Operations Facility (EOF) for planned maintenance. The ICS computers are used in the EOF to directly monitor selected plant parameters and to provide Emergency Response assessment capabilities. This planned maintenance implements a software modification and is expected to last for four days. "This is reportable under 10 CFR 50.72(b)(3)(xiii) because the EOF assessment capabilities would not be able to be restored within the facility activation time and assessment capabilities cannot be performed at a backup facility (i.e., there is no backup EOF). "While ICS connections in the EOF are out of service, if the Emergency Plan is entered and the Technical Support Center (TSC) and EOF are staffed, the EOF will not activate and Emergency Director authority will remain in the TSC. The Emergency Response Organization team members that report to the EOF and TSC have been notified regarding the status of the ICS computers in the EOF. "The planned modification that impacts the ICS computers in the EOF does not affect the health and safety of the public or station employees. The NRC Resident Inspector has been notified." The licensee notified the Matagorda County Sheriff, and the State of Texas Department of Public Safety and the Department of State Health Services. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-05-30
52774 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2017-05-28 | 2017-05-30 10:19 | 2017-07-05 | AGREEMENT STATE REPORT - STUCK SHUTTER ON A FIXED GAUGE The following report was received from the Mississippi Department of Health via email: "Licensee's RSO [Radiation Safety Officer] reported a stuck shutter on a Ronan Model SA8-C10 fixed gauge, Serial No. 1093CP, Source Model CDC.700. This was noticed during preventive maintenance, while performing shutter checks. Licensee notified the manufacturer for service. "Isotope: Cs-137 Activity: 200 mCi" * * * UPDATE AT 1524 EDT ON 7/5/17 FROM JAYSON MOAK TO MARK ABRAMOVITZ * * * The following update was received via e-mail: "Licensee reported that the gauge had been repaired by the manufacturer and returned to service. The gauge manufacturer's field engineer reported that the gauge shutter was able to be closed with channel lock pliers before the gauge was removed from the vessel. The field engineer reported that the lead ceiling portion of the shutter cavity was tight against the shutter assembly causing the shutter assembly to bind and not close. The field engineer suspects that water leached in behind the lead and froze, thereby pushing the lead deeper into the shutter cavity. The field engineer removed the expanded lead from hitting the shutter. Once the gauge had its seals replaced, the source holder was reassembled. The gauge was then wiped for removable contamination, surveyed at 30 cm and 12 in, and remounted by the field engineer for continued use. The wipe test was negative (less than 0.001uCi) for removable contamination and all fifteen (15) surveys were less than 1 mR/Hr with the gauge shutter open." Mississippi Report: MS-17001 Notified the R4DO (Farnholtz) and NMSS Resources (via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | MS | OTH | AGR |  |  |  |  | 0 | 2017-06-07
52773 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2017-05-12 | 2017-05-26 16:21 | 2017-05-26 | AGREEMENT STATE REPORT - CONTAMINATION EVENT The following information was received from the State of Illinois via email: "Advocate Condell Medical Center called to report that a patient treated with 200 mCi of I-131 on 5/10/17, subsequently released on 5/12/17, had returned to the hospital's ICU unit that same night with unrelated complications and a contamination event occurred. Her husband and her doctor both called the hospital prior to her arrival to inform them of her previous treatment with I-131. They were able to prepare for her arrival and prep the ER in plastic. She was admitted to ICU and later transferred to a regular hospital room. The only contamination is from the plastic covering the mattress, which is being stored for decay and from when the nurse drained a Foley catheter and a drop of urine ended up on the floor. Cleaning did not totally remove it. The hospital decided they did not need the room and it has been closed to allow for decay. "Additional surveys are to be conducted. The patient has since been released. The licensee will follow up with a written report." NMED Item Number: IL177004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2017-06-05
52772 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2017-04-02 21:27 | 2017-05-26 13:22 | 2017-05-26 | 60-DAY OPTIONAL TELEPHONIC NOTIFICATION OF INVALID SPECIFIED SYSTEM ACTUATION "This 60-day telephone notification is being made in accordance with the reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(1) to describe an invalid actuation of a general containment isolation signal affecting multiple Main Steam Isolation Valves (MSIVs). "On April 2, 2017 at approximately 2127 Eastern Daylight Time, during performance of a reactor vessel leak check, all four inboard MSIVs closed as a result of actuation of the Main Steam Line (MSL) high flow instrumentation. The high flow signal was spurious on two channels with no flow in the MSLs. Since an actual high flow condition did not exist at the time of the actuation, the actuation was considered invalid. The MSIVs functioned as designed on actuation of the MSL high flow instrumentation. All outboard MSIVs were closed at the time of the actuation. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-05-26
52771 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-05-26 03:21 | 2017-05-26 12:11 | 2017-05-26 | CONTROL ROOM EMERGENCY FILTRATION SYSTEM INOPERABLE "On May 26, 2017 at 0321 [CDT], Control Room staff questioned air flow and differential pressure in the Main Control Room. The CREFS [control room emergency filtration system] booster fan discharges to the Control Room supply fan suctions. With supply fan flows questionable, reasonable assurance that CREFS would fulfill its safety function could not be established. Engineering confirmed CREFS system flow rate by testing and determined the actual flow was 802 cfm, below the required flow of 810 cfm. Based on this information, CREFS was declared inoperable. "CREFS is a single train system. Per 10CFR50.72(b)(3)(v)(D), an 8-hour report is required due to the fact that, at the time of discovery, this condition could have prevented the fulfillment of the safety function of an SSC that is required to mitigate the consequences of an accident. "The NRC Senior Resident Inspector will be informed." CREFS being out of service places the plant in a 7-day LCO shutdown action statement. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-05-26
52770 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-05-24 10:52 | 2017-05-24 12:20 | 2017-05-24 | AGREEMENT STATE REPORT - FOUND MOISTURE DENSITY GAUGE The following information was received from the State of Texas by email: "On October 16, 1998, the Agency [Texas Department of State Health Services] was notified that a Humboldt model 5001 moisture/density gauge containing a 10 millicurie cesium - 137 and a 40 millicurie americium - 241 source was lost during transport from San Antonio to Laredo, Texas. The gauge was to be delivered to the Texas Department of Transportation (TXDOT). A search of the transportation companies warehouses and delivery locations along the transportation route did not find the gauge. The investigation was placed in "Inactive" status. On May 17, 2017, the Agency received an email string showing that a moisture/density gauge was for sale on the internet site 'eBay'. A search of the eBay site found that the gauge serial number matched the serial number of the gauge reported missing in 1998. The Federal Bureau of Investigation (FBI) was contacted and a request was made for assistance in gathering information on the seller. Using the information gathered by the Agency and the FBI, the Agency was able to contact the seller. The seller removed the posting off of eBay immediately. The seller stated they purchase materials from companies who are going out of business and resell them. The seller stated they did not remember when or where the gauge was purchased. The seller stated they had just moved all the materials they store in a large warehouse into two smaller warehouses and that is when they discovered the gauge. They did some research on the use for the gauge online and decided to sell it. The seller turned the gauge over to TXDOT on May 24, 2017. Dose rates taken on the gauge by TXDOT were normal. The gauge will be leak tested and returned to the manufacturer. Additional information will be provided as it is received in accordance with SA-300." Event #35040 initially reported the event on 11/16/1998 as a lost source while in transit. Texas Incident: I-7394 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2017-06-01
52769 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2017-05-23 23:30 | 2017-05-24 04:10 | 2017-05-24 | ALL FOUR EDGs AUTOSTARTED DURING TRANSFER OF SHUTDOWN BOARD TO NORMAL POWER SOURCE FOR UNIT 2 TESTING "On May 23, 2017 at 2330, while transferring 2A-A 6.9 kV Shutdown Board from its alternate power source to its normal power source in support of outage testing, a failure occurred which resulted in the loss of the Shutdown Board, emergency start of all 4 Emergency Diesel Generators (EDGs), and required the manual emergency stop of 2A-A EDG. "During transfer of the 2A-A 6.9kV Shutdown Board, the hand switch for the normal feeder breaker on the shutdown board was being maintained in the 'CLOSE' position while the alternate feeder breaker hand switch was placed in 'TRIP.' As expected, the alternate feeder breaker opened and the normal feeder breaker closed. However, the upstream supply breaker to the normal feeder breaker immediately tripped due to an overcurrent relay actuation on a single phase. As a result, the 2A-A 6.9 kV Shutdown Board deenergized, initiating a blackout signal which started all 4 of the station's EDGs. During board stripping (opening of all feeder and load breakers, to prepare the board for automatic reenergization from the EDG), the normal feeder breaker to the Shutdown Board failed to trip. This failure to trip prevented the emergency feeder breaker in the output of 2A-A EDG from closing, in accordance with interlock logic. As a result, 2A-A 6.9 kV Shutdown Board remained deenergized which prevented the cooling water supply valve for the EDG from opening due to loss of motive power. This lack of cooling caused operators to emergency stop the 2A-A EDG. "Power was restored to the Shutdown Board on May 24, 2017 at 0037. "Unit 1 is currently stable in Mode 1, at 100% power and Unit 2 is stable in Mode 5 with RCS at 164 F and 340 psig. "The cause of the breaker trip on overcurrent and the failure of the normal feeder to trip on load shedding are under investigation. "This event had no impact on the health and/or safety of the public. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-05-24
52768 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-05-23 08:30 | 2017-05-23 15:57 | 2017-05-23 | LOSS OF METEOROLOGICAL TOWER PRIMARY AND BACKUP COMMUNICATION EQUIPMENT "This notification is being made due to a loss of emergency assessment capability in accordance with 10 CFR50.72(b)(3)(xiii). On [May, 23, 2017] at 0830 (CDT), the meteorological tower primary and backup communication equipment failed, which resulted in a loss of meteorological data to the plant. Information technology and communications personnel investigated and restored the primary system to service. Meteorological data to the plant was restored at 0925 on [May 23, 2017]. "The NRC Senior Resident Inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2017-05-23
52767 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2017-03-24 14:25 | 2017-05-23 11:34 | 2017-05-23 | INVALID SYSTEM ACTUATION DURING TESTING "On March 24, 2017, at 1425 EDT, while performing Engineered Safeguards Actuation System (ESAS) quarterly High Pressure Injection/Low Pressure Injection Logic and Component testing, an unintended test signal was generated when a test switch was moved to the OFF position but went slightly past this position and engaged contacts for the Test no. 1 position. When examined, the test switch was found to be degraded which allowed the switch to move past the center position and engage the test no. 1 contacts. This resulted In a partial actuation of 'B'- train ESAS components. It also resulted in an injection to the reactor coolant system (RCS). The test signal was immediately removed by operators and the inadvertently started equipment secured. "The plant was operating at 100% power when the event occurred. There were no valid signals or plant conditions present to warrant the safety system actuation. The 'B' Emergency Diesel Generator rolled on air start but did not get up to full speed. Decay Heat Removal Pump 'B' started and the Decay Heat Removal Injection valve 4B opened, Make-Up Pump 'C' started, Make-Up Pump suction valve 14B opened, Make-Up pump discharge valves 16C and 16D opened, Spent Fuel Pump 1B tripped off, Air Handling Fan 18 tripped off and Air Handling Fan 1C trip tripped off. These components properly functioned from the inadvertent test signal and were secured prior to any adverse impact to plant operation. There was a small injection of borated water into the RCS. The plant remained stable at 100% power operation. "Pursuant to 10 CFR 50.73(a)(1) the following information is provided as a sixty (60) day telephone notification to the NRC. This notification, reported under 50.73(a)(2)(iv)(A), is being provided in lieu of the submittal of a written LER to report a condition that resulted in an invalid partial actuation of the 'B' train of the Engineered Safeguards Actuation System (ESAS) as it was not part of a pre-planned sequence. "The Licensee notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-05-23
52766 | 0 | TEXAS DEPT OF STATE HEALTH SERVICES |  |  |  |  | 2017-05-19 14:24 | 2017-05-19 16:03 | 2017-06-07 | AGREEMENT STATE REPORT - RECOVERY OF MISSING TROXLER GAUGE The following report was received as an update from the State of Texas: "On July 25, 1997, the Agency [Texas Department of State Health Services] was notified by a licensee that a Troxler model 3430 moisture density gauge serial # 24885 had been stolen from the back of a pickup truck. The gauge was not found and the Agency's file was placed in 'Inactive' status. On May 18, 2017, the Agency was contacted by the Federal Bureau of Investigation who reported the gauge had been found in an apartment in Houston, Texas, by the apartment's landlord. The gauge manufacturer was contacted and one of the manufacturer's technician retrieved the gauge and took it to its Houston location. The company that held the license is no longer licensed in the State of Texas. Additional information will be provided as it is received in accordance with SA-300." Texas Incident #: I-7173 Additional information in NMED Item Number 980180, last updated on 04/16/1998, is as follows: "The licensee reported the theft of a moisture/density gauge containing a 1.48 GBq (40 mCi) Am-Be source and a 0.296 GBq (10 mCi) Cs-137 source. The gauge was stolen from the back of a pickup truck when the operator stopped by his apartment complex. The lock had been cut from the chain securing the gauge. The licensee notified the local police. The gauge has not been recovered." * * * UPDATE FROM ART TUCKER VIA EMAIL ON 6/7/17 AT 1417 EDT * * * "On May 18, 2017, the Agency notified the HOO that a moisture/density gauge reported lost on July 25, 1997, had been recovered. The information was provided under the original incident number I-7173. This event is now being tracked under incident number I-9490." Notified R4DO (Rollins) and NMSS Events Notification via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. For additional information go to http://www-pub.iaea.org/MTCD/publications/PDF/Pub1227_web.pdf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2017-05-29
52765 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2017-05-19 08:05 | 2017-05-19 11:25 | 2017-05-19 | NONFUNCTIONAL RADIO TRANSMISSION TOWER AFFECTS TONE ALERT RADIOS "At approximately 0805 CDT on 05/19/2017, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was not functioning. This affects the tone alert radios used to notify the public in event of an emergency condition. This is considered to be a major loss of the Public Prompt Notification System capability, and is reportable under 10CFR50.72(b)(3)(xiii). "Nemaha County, NE, Richardson County, NE, and Atchison County, MO authorities within the 10 mile EPZ [Emergency Planning Zone] were notified by Cooper Nuclear Station of the condition and the affect on the tone alert radios. The first county was notified at 0834 CDT and the last was notified at 0836 CDT. Backup notification method will be utilized. Notification of other government agencies makes this condition reportable under 10CFR50.72(b)(2)(xi). "At time 1007 CDT on 5/19/2017, Cooper Nuclear Station was notified by the National Weather Service that the Shubert radio transmission tower was returned to service. "The NRC Senior Resident [Inspector] has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2017-05-19
52764 | 0 | PALISADES | 1 |  |  | [1] CE | 2017-05-19 02:06 | 2017-05-19 08:48 | 2017-05-19 | VALID REACTOR PROTECTION SYSTEM ACTUATION WHILE SHUTDOWN "Pursuant to 10CFR50.72(b)(3)(iv)(A), notifications are being performed for a valid actuation of the reactor protection system resulting in a full scram. The actuation was a result of pre-startup testing. The generator coastdown protective relay was left in service which needed to be bypassed to facilitate the testing. This resulted in a reactor scram occurring. "The reactor was subcritical with all rods inserted at the time of the actuation. All systems functioned as designed. "The licensee notified the NRC Resident Inspector." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-05-19
52763 | 0 | VOGTLE | 3 | 4 |  | [3] W-AP1000,[4] W-AP1000 | 2017-05-08 08:10 | 2017-05-18 15:14 | 2017-05-18 | FITNESS-FOR-DUTY REPORT "On May 17, 2017, at 1852 [EDT], Southern Nuclear Operating Company (SNC) contractor informed SNC that a contractor Fitness-for-Duty (FFD) collector failed to follow the process defined in both NRC Regulation 10 CFR 26.105(b) and contractor FFD procedures. The collector was fully trained, qualified, and knowledgeable of the process requirements. This determination was made based on initial department investigations and corroborated via independent investigations performed by the contractor. SNC has determined that this is reportable under 10 CFR 26.719(b)(3)." The licensee informed the NRC Resident Inspector and NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Under Construction | Under Construction |  | Under Construction | Under Construction |  | NON EMERGENCY | 2 | GA | POW |  | 26.719 |  |  |  | 0 | 2017-05-18
52762 | 0 | EMERSON AUTOMATION SOLUTIONS |  |  |  |  | 2017-03-14 | 2017-05-18 12:24 | 2017-05-18 | NOTIFICATION UNDER 10 CFR PART 21 OF BETTIS BRAND SEISMIC QUALIFIED G SERIES SPRING RETURN ACTUATORS The following report was received via fax: "Pursuant to 10 CFR Part 21, Valve Automation, Inc. (VAI) is writing to inform the Nuclear Regulatory Commission that, due to a retroactive application of a more stringent parts classification analysis, the adaptor plate contained in Bettis Brand Seismic Qualified G Series Spring Return Actuators (the 'Affected Actuators') is now classified as 'critical,' and therefore subject to certain inspection and dedication requirements which may not have been satisfied in Affected Actuators sold in the period between 2010 and 2016. "VAI has not received any information that absence of the inspection and dedication activities as a result of the prior classification has resulted in a safety hazard. In addition, VAI does not have the ability to determine whether or not a defect or non-compliance as defined in Part 21 exists. We are notifying customers and recommending remedial inspection of the Affected Actuators. "1.0 Name and address of individual providing this information: Sue Ooi Vice President Actuation Technologies Emerson Automation Solutions 19200 Northwest Freeway Houston, Texas 17065 T + 12814774170 "2.0 Identification of the basic component at issue: Adaptor plates bearing the following part numbers: VA600688 VA600692 VA600873 VA600988 "3.0 Nature of the issue: VAI is not aware of a 'defect' in the adapter plates of Affected Actuators, but due to a retroactive application of a more stringent parts classification analysis, an inspection and dedication noncompliance may exist concerning these adaptor plates. "4.0 Number and location of affected components in use: 42 Affected Actuators, sold to direct customers located in the United States. "5.0 Date the issue was discovered: March 14, 2017 "6.0 Corrective action and advice given to purchasers: Inspection Recommendation Certain measurements should be taken to remedy the inspection nonconformance. All measurements may be taken in situ with the actuator assembled to the valve. Please refer to Figure A (attached) depicting the feature to be measured. The numbered measurements in Figure A correspond to the numbered measurement inspection procedure below. Table 1 provides measurement values for reference [Figure A and Table 1 were supplied with the original submittal and may be viewed at https://www.nrc.gov/reading-rm/doc-collections/event-status/part21/ when posted]. Remedial inspection recommendations are to: 1. Confirm the thickness of the plate at the point where the bolt head & washer engage the flange surface. This location may be a milled flat section or counter sunk hole depending on the actuator size. 2. Verify full thread engagement for nuts installed on bolts for the housing flange. 3. Perform hardness testing on a small area on the outside diameter of the adaptor plate. The paint will need to be removed at the point of hardness testing. Should the adaptor plate fail to meet the above specifications, please contact us promptly. "7.0 Other advice to purchasers: VAI recommends that users review applications where any Affected Actuators are used to determine any safety considerations in the operation of the plant. "VAI is committed to the highest standards of safety and customer service in the nuclear industry, and remains dedicated to the supply of world class products to our customers. If you have any questions or require additional information related to this issue, please contact: Justin DeClue, Director of Global Quality, [Tel:] 281 477 4631." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21(a)(2) |  |  |  | 0 | 2017-05-18
52761 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2017-05-17 09:08 | 2017-05-17 12:29 | 2017-05-17 | LOW PRESSURE CORE SPRAY PUMP INOPERABLE DUE TO MINIMUM FLOW VALVE CLOSURE "This report is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. The Low Pressure Core Spray (LPCS) Pump Injection HI Flow alarm was received at 09:08 CDT on May 17, 2017, at which point the minimum flow valve was observed to go closed. The LPCS pump remained in standby during the event. To prevent damage if the pump were to auto start, the control switch for the LPCS pump was placed in pull to lock. This condition prevents LPCS, a single train safety system, from performing its design function. This is a reportable condition as an 8 hour ENS notification. "The required action of Technical Specifications (TS) 3.5.1, 'ECCS - Operating,' was entered on May 17, 2017 at 09:08 CDT when the condition was identified and the LPCS system was determined to be inoperable. Investigation into the cause of the condition is in progress. There were no related work activities in progress at the time the condition was identified." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-05-17
52760 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2017-05-16 | 2017-05-16 23:40 | 2017-05-17 | AGREEMENT STATE REPORT - LICENSEE STRUCTURE DAMAGE DUE TO TORNADO The Midwest Inspection Services building has been severely damaged by a tornado storm. All radiography cameras have been accounted for and are stored in a safe location. The vault is intact. Tornados are forecasted to continue throughout the evening. * * * UPDATE AT 1205 EDT ON 05/17/17 FROM MICHAEL BRODERICK TO JEFF HERRERA * * * The following update was received from the Oklahoma Department of Environmental Quality via email: "Shortly after 22:30 [CDT] on the evening of May 16th, Oklahoma DEQ [Department of Environmental Quality] verbally notified the HOO [NRC Headquarters Operations Officer] of an event affecting an Oklahoma radiography company. This is a follow-up report to confirm the verbal report and provide more details. "Facility Name: Desert NDT, LLC dba Shawcor (note) the facility was historically known as Midwest Inspections, and was accidentally referred to by that name in the initial report. "Facility license number: OK-32104-01 "Because of concern generated by news reports, DEQ [Oklahoma Department of Environmental Quality] contacted the facility at about 22:00 [CDT] and over the following few minutes, we were able to reach the facility manager. [The facility manager] reported that their licensed facility at Elk City had been largely destroyed by the tornado reported in the media. He indicated that the vault was mostly intact, but had damage to the ceiling. All power at the facility was out. [The facility manager] indicated they [Desert NDT] had fifteen cameras in the vault, and others were out in trucks on jobs around the region. [The facility manager] reported that they [Desert NDT] had done an inventory on the fifteen cameras in the vault, and confirmed that they were accounted for. [The facility manager] had no reports of problems with any sources dispatched on jobs. [The facility manager] explained that they [Desert NDT] did not regard the damaged vault as suitable for secure storage, but they [Desert NDT] had one radiography truck that was largely intact, and they [Desert NDT] were storing the fifteen cameras in one truck, and keeping the truck under constant surveillance by an employee who was authorized unescorted access. Media reports indicated that another storm, weaker than the first, but still having potential tornadoes was headed for the area. In a second call, the facility manager reported that because of concerns about further storms, they had moved the cameras into a storm shelter in [a secure location]. [The facility manager] indicated that the storm shelter was under surveillance, and was lockable, and would remain locked unless being directly accessed. In view of the remarkable circumstances, [Oklahoma] DEQ approved this arrangement as an interim measure. About 8:20 [CDT] on the morning of the 17th, [Oklahoma] DEQ contacted the manager again. [The facility manager] indicated that the fifteen cameras were still secured in the storm shelter. [The facility manager] reported that there was no known further damage during the night, and that the company would be conducting a confirmatory inventory of the fifteen cameras, and conducting an inventory to ensure that cameras out on jobs were safe and under control. [The facility manager] will report the results of this to [Oklahoma] DEQ when available. [The facility manager] explained that they were doing an assessment of undamaged trucks that were suitable for secure storage under Part 37, and that they planned to retain some sources at the Elk City facility using the trucks that were suitable. [The facility manager] indicated that excess sources would be moved to a licensed company facility out of state. [The facility manager] will follow up with [Oklahoma] DEQ later today. "[Oklahoma] DEQ has used GIS [Geographic Information System] to identify seven other licensed facilities that are near the storm track, and are not considered as having as much concern. We [Oklahoma DEQ] contacted all of them by phone this morning and confirmed that all is well." Notified the R4DO (Miller) and NMSS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2017-05-24
52759 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2017-05-15 | 2017-05-16 14:02 | 2017-05-23 | AGREEMENT STATE REPORT - POTENTIAL EXCESSIVE EXPOSURE OF RADIOGRAPHER The following information was received from the Wisconsin Radiation Protection Section via email: "On May 15, 2017, radiographers with Acuren Inspection, Inc. were performing radiography on a boiler at Verso Paper in Wisconsin Rapids, WI. They were utilizing an approximately 90 Ci Se-75 source, with a 17.5 HVL [Half Value Layer] collimator to perform shots through the boiler wall. The assistant radiographer would position a panel on the inside of the boiler wall and then move to the far side of the boiler. The main radiographer would then position the collimator for multiple shots from the outside of the boiler. They were in contact via radio. At approximately 7:45 p.m., following a shot, the main radiographer approached the collimator with his survey meter. As he approached, he realized the source had not yet been cranked in, and began walking back to crank it in. At that time, he was contacted via radio by the asst. radiographer. Setting down his survey meter, he had a 30-40 second conversation. Following the conversation, he forgot what he had been in the process of doing, and approached the collimator without his survey meter, and positioned it for the next shot. Turning to walk back, he spotted his survey meter on the ground halfway to the crank, remembered he had yet to crank it in, and realized he had been exposed. He was wearing a functioning alarming rate meter that did not alarm. "Acuren notified the state approximately three hours after the event on the evening of the 15th of the possible overexposure. The radiographer initially estimated he had held the source 10 seconds, and Acuren calculated this would result in approximately a 680 Rad dose to the hands. The radiographer was wearing a direct reading dosimeter on his chest which read 100 mR. Other whole body dosimetry is being processed. Following the event, the licensee had the radiographer do a mock performance 3 times. These indicated he held the collimated source approximately 3-5 second in each hand. QSA global is currently performing an independent dose calculation and the radiographer has been removed from duty. The radiographer is not currently experiencing any symptoms of acute radiation exposure. The department has dispatched inspectors to perform a site inspection." Wisconsin Event Report ID No.: WI-170007 * * * UPDATE ON 5/18/17 AT 1012 EDT FROM MEGAN SHOBER TO BETHANY CECERE * * * The following update was received from the Wisconsin Radiation Protection Section via email: "Wisconsin DHS [Department of Health Services] performed a site investigation on May 17, 2017. On the night of the event, there were approximately eight individuals supporting radiography at the temporary jobsite. Two individuals were performing radiography and the rest of the individuals were securing the boundaries. One radiographer was overexposed; no one else on the crew received an elevated dose due to the event. There was no exposure to members of the public. Inspectors confirmed that all radiography equipment (survey meters, alarming rate meters, etc.) was available and operational. "The licensee determined that the radiographer held the collimator in his hands in a way that exposed his fingers to the uncollimated beam for several seconds on two separate occasions (once for each hand). The licensee contracted with a third-party to perform a dose assessment. The assessment shows a hand exposure of 176 rem per hand. DHS is evaluating these results. "The radiographer's whole body badge was read by the dosimetry provider and showed a 152 millirem dose. This is consistent with the previously reported 100 mR direct-reading dosimeter exposure for May 15. Both the whole body badge and direct-reading dosimeter were located in the radiographer's left front shirt pocket. "Wisconsin DHS is continuing to monitor the licensee's response, including medical follow-up of the affected individual." Notified R3DO (Cameron), NMSS Events, NMSS (Rivera-Capella), and NSIR (Milligan) by email. * * * UPDATE FROM MEGAN SHOBER TO VINCE KLCO ON 5/23/17 AT 1741 EDT * * * The following information was received from the State of Wisconsin via facsimile: " The source activity on the date of the incident was 96 curies." Notified R3DO (Kunowski), NMSS Events, NMSS (Rivera-Capella), and NSIR (Milligan) by email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2017-05-24
52758 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2017-05-15 19:18 | 2017-05-16 00:27 | 2017-05-16 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "On May 15, 2017 at 1918 hours [CDT], Unit Two High Pressure Coolant Injection (HPCI) Minimum Flow Valve MO 2-2301-14 failed to open as required by procedure and HPCI was declared inoperable. When the HPCI Turbine was tripped, the Minimum Flow Valve did not open when system flow reduced to the low flow setpoint. This event is being reported as a condition that could have prevented fulfillment of a safety function in accordance with 10CFR50.72(b)(3)(v)(D). The HPCI system is a single train system and the loss of HPCI could impact the plant's ability to mitigate the consequences of an accident. In accordance with Technical Specification 3.5.1 Condition G, the Reactor Core Isolation Cooling (RCIC) system was confirmed operable." This places the plant in a 14-day LCO action statement. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-05-16
52757 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2017-05-15 18:00 | 2017-05-16 00:17 | 2017-05-16 | VALID EMERGENCY DIESEL GENERATOR SIGNAL GENERATED UPON LOSS OF 4160V POWER "On May 15, 2017 at 1800 hours EDT, the '2A3' 4.16 KV safety related bus unexpectedly de-energized. The '2A' emergency diesel generator (EDG) system received a valid start signal from the undervoltage condition on the '2A3' bus but did not start as the EDG had been removed from service for maintenance. Loss of the '2A3' 4.16 KV bus resulted in a valid actuation of the undervoltage protection relays. The direct cause of the de-energization was determined to be failed secondary side potential transformer fuses. The 'B' train safety related electrical busses were unaffected by the event. "The '2A3' 4.16 KV bus was reenergized at 2340. "This event was determined to be reportable pursuant to 10CFR50.72(b)(3)(iv)(A)." During the electrical transient, the licensee briefly entered Technical Specification 3.0.3 but plant conditions were restored, all required LCOs were satisfied, and Technical Specification 3.0.3 was exited before the plant was required to downpower. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2017-05-16
52756 | 0 | CURTISS WRIGHT FLOW CONTROL CO. |  |  |  |  | 2017-03-16 | 2017-05-15 18:55 | 2017-09-11 | PART 21 - POTENTIAL DEFECT IN GRAYBOOT SOCKET CONTACTS The following information was received via email: "This letter is issued to provide an interim notification of a potential defect in certain lots of Grayboot socket contacts supplied with EQ qualified Grayboot Connector Kits. On March 16, 2017, Curtiss-Wright, Nuclear Division, Huntsville Operations was contacted by Georgia Power Vogtle Nuclear Power Plant concerning a potential defect where the socket contact tines were in a relaxed state. "Although we have completed some testing and verification activities, additional testing is in progress now and will provide necessary information to complete our evaluation. Current testing will be completed and final conclusions made by May 31, 2017. "At this time, based on test results, evaluations and operating experience, Curtiss Wright is confident that any potentially affected Grayboot Assemblies will continue to perform their intended safety functions. As such, if the final recommendation is to replace the potentially defective socket contact, this can be accomplished during subsequent routine maintenance activities. "This notification is being made to comply with 60 day interim reporting requirements as defined in 10 CFR 21.21(a)(2). "For additional information, please contact Samuel Bledsoe, EGS Products Engineering Manager (1-256-690-7852) or Tony Gill, EGS and Trentec Quality Assurance Manager (1-256-426-4558)." * * * UPDATE PROVIDED BY TONY GILL TO JEFF ROTTON AT 1813 EDT ON 05/31/2017 * * * The following information was provided via email: "This letter is issued to provide final findings associated with a potential defect concerning GRAYBOOT socket contacts. This issue was initially identified in an interim report dated May 15, 2017. As documented previously, Curtiss-Wright, Nuclear Division, Huntsville Operations was contacted by Georgia Power Vogtle Nuclear Power Plant on March 16, 2017 concerning a potential defect wherein GRAYBOOT socket contact tines were in a relaxed state. This notification of a potential defect concerns model GB-1 GRAYBOOT kits supplied with two-tined, silver-plated, 12-14 AWG socket contacts. "Based upon this scope, potentially affected kits/parts are: 1. GB-1(12-14) GRAYBOOT kits, 2. GB-1 (12-14/ 16-18) GRAYBOOT kits, and 3. GB-1-6 GRAYBOOT 12-14 AWG socket contacts. "This issue does not affect the following: 1. Any GRAYBOOT 'A' kits/parts, 2. Any model GB-2 or GB-3 GRAYBOOT kits/parts, or 3. Any model GB-1 GRAYBOOT kits/parts with 16-18 AWG socket contacts. "Our evaluation is documented in Report No. EGS-TR-880708-15 and is available for review at our facility in Huntsville, AL. The results identify the most likely root cause is improper heat treating of the socket contacts during manufacturing. Additional testing and analysis was performed to confirm that any affected GRAYBOOT assemblies can still preform their safety-related function and do not present a substantial safety hazard . "The findings outlined in Report No. EGS-TR-880708-15 provide a high level of confidence that affected GRAYBOOT assemblies do not present a substantial safety hazard. This position is further validated by the lack of negative operating experience over the last 20 plus years from properly installed GRAYBOOT assemblies. However, this condition causes the contact to be more susceptible to damage from handling during connection and disconnection, and therefore the following actions are recommended: "1. Any affected sockets in inventory should be replaced. Affected sockets in service should be replaced during routine maintenance activities. OR "2. In lieu of replacement, it is acceptable to perform the following [steps 1-3] to confirm a separation force greater than 0.19 lbs. This is consistent with existing Curtiss-Wright dedication acceptance criteria. It is recommended that any contacts not meeting this criteria be replaced. 1. Crimp a spare pin contact to an appropriate piece of wire. 2. Connect a force gage or 0.19 lbs. of static weight to the opposite end of the wire. 3. Insert the pin into the socket and confirm that the pin does not separate from the socket under a minimum load of 0.19 lbs. "To confirm this deviation is not present in existing inventory or in future purchased lots, the following corrective actions have been or will be implemented by Curtiss-Wright: 1. Micro hardness testing was performed on all socket contact lots in inventory to verify their acceptability. Results confirmed that all lots were acceptable. 2. Acceptance criteria for dedication of socket contacts will be revised to include verification of acceptable contact hardness. This corrective action will be completed by June 9, 2017. No dedication of socket contacts will be performed until this corrective action is complete. "A list of affected utilities and associated purchase orders is being developed and will be complete and submitted by June 9, 2017. "For additional information, please contact Samuel Bledsoe, EGS Products Engineering Manager (1-256-690-7852) or Tony Gill, EGS and Trentec Quality Assurance Manager (1-256-426-4558)." Notified R1DO (Bower), R2DO (Shaeffer), R3DO (Daley), R4DO (O'Keefe) and Part 21 Operating Reactors Group via email. * * * UPDATE AT 1859 EDT ON 06/09/17 FROM TONY GILL TO JEFF HERRERA * * * The following update was received via email: "On May 31, 2017, Curtiss-Wright, Nuclear Division, Huntsville Operations issued a letter documenting final findings regarding a potential defect concerning model GB-1 GRAYBOOT kits supplied with two-tined, silver-plated, 12-14 AWG contacts. Please find that letter attached. "Pursuant to the attached letter, please find attached a list of affected purchase orders. "For additional information, please contact Samuel Bledsoe, EGS Products Engineering Manager (1-256-690-7852) or Tony Gill, EGS and Trentec Quality Assurance Manager (1-256-426-4558). List of Sites Affected: Arkansas Nuclear 1 Bruce Nuclear Power Development Brunswick Callaway Calvert Cliffs Clinton Columbia Cooper CTEAM/CRIT Davis-Besse Diablo Canyon Duane Arnold Farley FMM Fort Calhoun Gentilly Ginna Haddam Neck Harris Indian Point Kewaunee La Salle Limerick Millstone Nine Mile Point North Anna Oconee Oyster Creek Peach Bottom Pilgrim Point Beach Prairie Island Quad Cities River Bend Saint Lucie San Onofre Sizewell B South Texas Summer Turkey Point Vermont Yankee Vogtle Waterford Wolsong Zion Notified R1DO(Welling), R2DO(Suggs), R3DO(Orlikowski), R4DO(Rollins), Part-21 Reactors (via email). * * * UPDATE AT 1612 EDT ON 09/11/17 FROM TONY GILL TO BETHANY CECERE * * * The following information was received via email: "At initial issuance, the evaluation documented in Report No. EGS-TR-880708-15 presented metallurgical analysis as well as thermal, functional and seismic testing. This report has been revised to include cycle aging, functional testing and pull-out force. Test results confirm that affected socket contacts will continue to perform their intended safety function throughout their qualified life. "Based on these final findings, no further actions are recommended for the potentially affected utilities previously notified. Any potentially affected socket contacts, either in inventory or installed, are acceptable for use in their intended safety-related application. "It is recommended that all utilities confirm that installation and handling of GRAYBOOT assemblies is in accordance with Installation Instructions EGS-TR-880707-02. "For additional information, please contact Samuel Bledsoe, EGS Products Engineering Manager (1-256-690-7852) or Tony Gill, EGS and Trentec Quality Assurance Manager (1-256-426-4558)." Notified R1DO(Dentel), R2DO(Michel), R3DO(Riemer), R4DO(Groom), Part-21 Reactors (via email). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Part 21 | INTERIM EVAL OF DEVIATION | DEFECTS AND NONCOMPLIANCE | [8 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21(a)(2) | 21.21(d)(3)(i) |  |  | 0 | 2017-05-15
52755 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2017-05-15 11:50 | 2017-05-15 17:24 | 2017-05-15 | AGREEMENT STATE - SOURCE UNABLE TO BE RETRIEVED INTO SHIELDED DEVICE The following report was received from the Louisiana Department of Environmental Quality via email: "[On] 05/15/2017, [at] 11:50 [CDT], the Radiation Safety Officer of Team Industrial Services, Inc. called the Radiation Section of LDEQ [Louisiana Department of Environmental Quality] to report a source retrieval that occurred on 05/14/2017 [at approximately] 18:00 [CDT] at the INDORAMA VENTURES OLEFINS Refinery is Sulphur, LA at 4300 Hwy 108, Westlake, LA 70669. The camera was being used on a gridded walkway to radiograph some construction material situated on a tripod. The tripod became unstable causing the material to fall and crimp the guide tube. The source was in the collimator and was unable to be retrieved into the shielded exposure device. A retrieval crew was assembled and they were able to retrieve the source and return it to the shielded position. Two radiographers and a site RSO [Radiation Safety Officer] conducted the retrieval activities. The retrieval process was safely completed at [approximately] 20:30 [CDT] on 05/14/2017. "A radiography exposure device was a QSA Global Model 880D, S/N D12919 and the source was an AEA Technology Model A424-9. The exposure device was loaded with 85.7 Ci of Ir-192. The guide tube was a 7 ft. tube that utilized a collimator. The exposure device and source were returned to the office for storage until being evaluated. The crimped guide tube was tested for leakage and then sent for disposal. The area was restricted to the public and controlled for the employees of Indorama. The exposures to the retrievers were minimal." LA Event Report ID No.: LA170008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2017-05-23
52754 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2017-05-12 | 2017-05-15 11:58 | 2017-05-15 | AGREEMENT STATE - DELIVERED DOSE TO PATIENT DIFFERED BY MORE THAN 20 PERCENT The following report was received from the South Carolina Department of Health and Environmental Control (SCDEH) via email: "The licensee notified the Department [SCDEH] on May 15, 2017 that it had a medical event on May 12, 2017 involving a delivered dose that differed by more than 20 percent and dose that would have resulted from the prescribed dosage by more than 0.5 Sv (50 rem) to an organ or tissue. The patient was prescribed 145 Gray from I-125 prostate seed implants. The dose delivered was 103.53 Gray which is 28.6 percent below the prescribed dose." A Medical Event may indicate potential problems in a medical facility's use of radioactive materials. It does not necessarily result in harm to the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Agreement State | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2017-05-23
52753 | 0 | WATERFORD | 3 |  |  | [3] CE | 2017-05-14 18:23 | 2017-05-14 21:27 | 2017-05-14 | FIRE IN ADMINISTRATIVE BUILDING RESULTS IN LOCAL FIRE DEPARTMENT NOTIFICATION "On May 14, 2017 at time 1823 [CDT], Waterford 3 Steam Electric Station notified St. Charles Parish Emergency Services via 911 of a fire in the Generation Support Building (GSB), the Hahnville, Luling and Killona Fire Departments were dispatched. The GSB is an Administrative and Engineering Building outside the Protected Area and on the Owner Controlled Area. The fire was reported out at 1841. No personnel were injured due to the fire. The fire appeared to be from an external building exhaust fan. There was no internal or structural damage to the building. There was no radiological release. No Safety Related Systems were required to function." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2017-05-14
52752 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-05-14 07:30 | 2017-05-14 16:09 | 2017-05-14 | FITNESS FOR DUTY "At 0730 [CDT] on 5/14/2017, a visitor was working in the Protected Area (PA) on the turbine building roof and discovered a blue 12 ounce can of beer in their cooler. This was discovered when the visitor was removing items from their cooler into a larger community cooler. The visitor immediately notified their escort of the prohibited item. The escort then notified Security of the event. Security took possession of the item and the individual was escorted offsite. The individual stated when they packed their cooler at home they thought they had picked up a blue can of soda and did not notice it was a blue can of beer. This event is being reported per 10CFR26.719(b)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 26.719 |  |  |  | 0 | 2017-05-14
52751 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2017-05-14 09:30 | 2017-05-14 15:32 | 2017-05-14 | SINGLE FLOW BARRIER ACCESS POINT FOUND UNBOLTED "On May 14, 2017, with the Unit in Mode 4, it was identified that a single flow barrier access point (Gate C) to the 46 ft. elevation of Containment was unbolted for access to the inner crane wall to perform surveillance testing. This single flow barrier access point is required to be bolted closed to ensure the Emergency Core Cooling System (ECCS) operability basis which requires the sump barrier system to be operable in Modes 1- 4. The sump barrier system is required to prevent the transport of debris to the recirculation and containment sumps. This event is a safety system functional failure as the condition could have prevented adequate post-accident core cooling due to Design Basis Accident debris blockage of the recirculation and/or the containment sump and is reportable under 10 CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector and the New York Public Service Commission. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2017-05-14
52750 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2017-05-12 00:45 | 2017-05-12 08:20 | 2017-05-12 | MAIN STEAM ISOLATION VALVES EXCEEDED PRIMARY CONTAINMENT LOCAL LEAK RATE ACCEPTANCE CRITERIA "At 0045 [CDT] on May 12, 2017, it was discovered that a Primary Containment local leak rate test performed on Main Steam Isolation Valves (MSIV) exceeded its acceptance criteria. "During Modes 1, 2, and 3, Technical Specification Surveillance Requirement 3.6.1.3.9 requires MSIV leakage for a single MSIV line to be less than or equal to 100 standard cubic feet per hour (scfh) (47,195 sccm) and requires the combined leakage rate for all MSIV leakage paths to be less than or equal to 200 scfh (94,390 sccm) when tested at 9 psig. "As-found for the 'D' MSIV line leakage is 53,921.61 standard cubic centimeter per minute (sccm) for the 'D' Inboard MSIV 1B21F022D and 59,698.8 sccm for the 'D' Outboard MSIV 1B21F028D. As-found combined MSIV min-path leakage is 102,463 sccm. "This event is being reported as a condition of the nuclear power plant, including its principal safety barriers, being seriously degraded per 10 CFR 50.72(b)(3)(ii)(A) since the Primary Containment Isolation Valves leakage limits for MSIVs were exceeded. "The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2017-05-12
52749 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2017-05-11 08:10 | 2017-05-11 18:11 | 2017-05-11 | FITNESS FOR DUTY - UNOPENED CAN OF ALCOHOL DISCOVERED IN ADMINISTRATION BUILDING A can of alcohol (16.9 ounce foreign beer) was discovered unopened in an administration building refrigerator. Site security took possession of the can of alcohol. The owner of the can of alcohol is unknown. This licensee is making this 24 hour notification in accordance with 10CFR26.719(b)(1). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown |  | 3 | MN | POW |  | 26.719 |  |  |  | 0 | 2017-05-11
52748 | 0 | NORTH CAROLINA STATE UNIVERSITY |  |  |  | 1000 KW PULSTAR POOL TYPE | 2017-05-10 17:00 | 2017-05-11 15:24 | 2017-05-11 | RESEARCH TEST REACTOR - TECHNICAL SPECIFICATION VIOLATION "On Wednesday May 10, 2017 at approximately [1700 EDT], the Reactor Operator (RO) that was signed in on the reactor console logbook completed a ['key on'] checklist in preparation for a routine reactor startup. The RO left the control room and brought the log book to the reactor bridge for the Designated Senior Reactor Operator (DSRO) to sign off for the ['key on'] startup. The RO immediately realized his mistake concerning the procedural requirement for a reactor operator to be present in the control room at all times when the reactor is not secured (procedure OP-103), and returned to the control room. "The DSRO followed the RO to the control room and observed that the reactor key was in the on position, the control rods were all fully inserted, and reactor power was at residual levels. The reactor was shutdown, but was not secured. The DSRO determined that this constituted a violation of procedure OP-103 and could be a Reportable Occurrence as defined under Technical Specification 1.2.24 h. "The DSRO reviewed Technical Specification (TS) 6.6.2, Action to be Taken in the Event of a Reportable Occurrence. The DSRO determined that under TS 6.6.2a that reactor conditions had been returned to normal by the presence of the licensed operator in the control room. The DSRO then signed the Key On checklist authorization for reactor startup and the reactor was started. "The DSRO spoke with the Manager of Engineering and Operations (MEO) by telephone about this matter at approximately 1800 on May 10, 2017. The MEO concurred that procedure OP-103 was violated and would be reportable to the Nuclear Regulatory Commission (NRC). The DSRO and MEO agreed to discuss this matter with the Director, Nuclear Reactor Program and the Reactor Health Physicist on May 11, 2017. The MEO stated on May 11, 2017 that TS 6.1.3a, the specification implemented by procedure OP-103, was not met. It was agreed that required notifications to NRC would be made by [1700] on May 11, 2017 to meet the 24 hour notification requirement." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Non-Power Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 0 | NC | NPR | [5 empty] | 0 | 2017-05-11
52747 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2017-03-20 02:16 | 2017-05-11 13:21 | 2017-05-11 | 60-DAY OPTIONAL TELEPHONE NOTIFICATION FOR AN INVALID HIGH PRESSURE COOLANT INJECTION SYSTEM ACTUATION "Pursuant to 50.73(a)(1) the following information is provided as a sixty (60) day telephone notification to the NRC. This notification, reported under 50.73(a)(2)(iv), is being provided in lieu of the submittal of a written LER to report a condition that resulted in an invalid actuation of the high pressure coolant injection (HPCI). At Nine Mile Point Unit 1, HPCI is a flow control mode of the normal feedwater system and is not an emergency core cooling system. "On March 20, 2017 at 0216 EDT, Nine Mile Point Unit 1 reactor shutdown was in progress. The Unit 1 generator was off line, the 100 percent capacity 13 feedwater pump (13 FW) was removed from service, and the Unit 1 main turbine had been tripped appropriately per procedure while entering a planned refueling outage. At approximately 4 percent reactor power, a clearance tagging evolution was in progress to support shutdown activities. During this evolution a tag was applied that caused an unanticipated activation of a lock out (86) relay due to the failure to bypass this relay prior to the tag application. This 86 relay activation in turn resulted in a generator trip signal followed by a turbine trip signal. With the generator off line and the turbine already tripped there was no actual change in any plant parameter or condition that would have created a valid turbine trip signal and the associated HPCI initiation. "The plant configuration at the time of the main turbine trip signal had one motor operated feedwater pump, 12 Feedwater Pump (12 FW), in service and providing normal reactor level control. HPCI did initiate as designed upon receiving the generator and main turbine trip signals caused by the activation of the 86 relay. The 12 FW pump, which was providing normal reactor level control, transitioned the level control from automatic mode into HPCI mode of operation. Per design, the 11 FW pump automatically started but was not required to and did not flow water since 12 FW pump was in operation. The 11 FW pump was subsequently secured by operations. At no point in time did the HPCI system receive a valid initiation signal (due to high DW pressure, low reactor water level, or a valid turbine trip with loss of the turbine driven 13 FW pump). Operators reset HPCI and returned water level to Automatic Control at 0218. "The Licensee has notified the NRC Resident Inspector." | 4 | 0 | 0 | 4 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2017-05-11