42288 | 0 | SANJEL USA, INC |  |  |  |  | 2005-12-07 15:15 | 2006-01-26 16:11 | 2006-01-26 | FIRE INVOLVING NUCLEAR GAUGE "This is a follow-up report of an incident involving a nuclear gauge. "The gauge was a model 5192, built by Thermo Measuretech. It was a 100 mCi source of Cesium 137 Serial # B-6809. "This gauge was a sealed source, permanently mounted to a 2" high pressure pipe. It was mounted to the plumbing at the rear of Unit 4451, a cement pump unit. The fire apparently started in the building that this truck was housed in for the purposes of thawing a frozen pump. Control of the gauge was never relinquished. A fire started in the facility located approximately 2 miles East of Cut Bank, Mt. and owned by General Well Servicing. The fire is still under investigation by Sanjel's insurance carrier. "The fire started approximately 1515 on the 7th of December 2005. I was notified at approximately 1801. I notified the USNRC Emergency number @1904. "First responders were notified by the Sanjel Authorized Users about the gauge. The first responders didn't have access to a survey meter; I arrived on site at 0445 on the 8th of December 2005. I conducted a survey from upwind to the building and found no trace of radiation, but I was restricted from going into the facility by Sheriffs deputy until cleared by the Fire Chief at approximately 0730. "At 0730, I surveyed the area around the rear of the truck under the observation of the Sheriff s deputy, and surveyed the gauge. I observed readings from 1.5 mRad to what I thought I had read, 11.5 mRad. The survey was made in darkness. I questioned the local fire chief and sheriffs deputy about any personnel coming close to the gauge; I was told that the fire was primarily contained to the front of the vehicle, and the fire fighters were cautioned and restrained from getting within 30 feet of the gauge. I feel that I received the highest dose there removing the gauge/detector and pipe and conducting the survey, taking 10 minutes at 11.5 mRad x 1 (quantifier for beta/gamma sources)= 1.91 mRem/hr. "The gauge was removed @ 1200 with the permission of the State Fire Marshall and transported by covered vehicle to the Sanjel Miles City office. The area around where the gauge was mounted was surveyed, rendering no recordable readings. The path from the location of the gauge to the recovery vehicle was also surveyed rendering no noticeable readings. A second survey of the gauge was made at the recovery vehicle in daylight, showing a reading on 3 mRad on the sides of the source, 1.5mRad on the front and 2 mRad on the top, 1mRad on the bottom. This would change the highest dose received to 0.5mRem/hr. "The reason for the delay in this report is my interpretation of RIS 2005-06, 10 CFR 20.2202, and HPPOS-322 I felt this was not a reportable incident. I am reporting this after contacting Jack Witten, Tony Gaines and Bob Brown on January 26, 2006. These are my contacts at the Region IV in Arlington, TX. And being advised that this is a reportable incident under 10 CFR 30.50, (b)(ii). "The corrective action plan for this incident, is to advise Authorized Users that locations and facilities used on a temporary use must be inspected by management prior to use. As of today, 26 January 2005, the gauge has been transferred to Thermo-Electron for decommissioning due to the repair." The following information was provided to the NRC Operations Center during the initial notification at 2104 EST on 12/07/05 by the RSO for Sanjel, USA, Inc.: RSO for Sanjel, USA, Inc called to inform the NRC that his company owns a truck with a Cs-137 source mounted on the back for measuring cement density. The truck is parked inside a well servicing building in Cutbank, Montana and that building is on fire. Fire company personnel have responded and the local sheriff has set up a barrier to keep unauthorized personnel 1 mile from the site due to the hazardous chemicals stored in the building. Sanjel Technicians have informed the sheriff of the Cs-137 source on their truck. The source manufacturer is Thermal Measure Tech, model 5192, Serial # B-6809, Activity - 100 millicuries. The source is mounted on a pipe to measure the cement density pumped through the pipe, and is enclosed in a lead shield with normal on contact radiation readings of 2 mr/hr. Sanjel NRC license # is 54-27692-01. RSO is enroute to the site of the fire (8 hours away). While in route, he will keep NRC HQ notified of any updates he receives and will make a final report once he can access the situation properly. Notified R4DO (Kennedy) and NMSS EO (Pierson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2006-01-26
42287 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-01-25 | 2006-01-25 17:41 | 2006-01-30 | AGREEMENT STATE REPORT - INDUSTRIAL RADIOGRAPHY DEVICE MISSING The State provided the following information via email: "A Texas licensee reported on January 25, 2006 that an industrial radiograph crew departed Corpus Christi for Victoria, Texas, and found on arrival that the radiography device they were carrying was not on the transport vehicle. The radiation source, a 21 Curie industrial radiography source, was lost in its shielded container. Company crews are searching for the device and have not located it at this time. DSHS radiation control staff have been dispatched to aid in the search. Local law enforcement are being notified of the loss." The radionuclide is Ir-192. Texas Incident Report No. I-8292 * * * UPDATE FROM ROBERT FREE TO JOE O'HARA AT 1407 ON 1/30/06 * * * "Radiography device found by private citizen on 1/25/06 and returned 01/26/06." Notified the R4DO(Runyon), NMSS EO(Morell), IRD Manager(Wilson), TAS(Perez), and Mexico. THIS MATERIAL EVENT CONTAINS A "CATEGORY 3" LEVEL OF RADIOACTIVE MATERIAL Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours, it could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. Although IAEA categorization of this event is typically based on device type, the staff has been made aware of the actual activity of the source, and after calculation determines that it is a Category 3 event. Note: the value assigned by device type "Category 2" is different than the calculated value "Category 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-01-30
42286 | 0 | US EPA, ECOSYSTEMS RESEARCH DIV |  |  |  |  | 2006-01-25 | 2006-01-25 15:16 | 2006-01-25 | MISSING NICKEL 63 SEALED SOURCE US EPA Ecosystems Research Division RSO called to state that a 15 milliCurie sealed source of Ni-63 was misplaced. The last time an inventory was taken of this electron capture source was on 06/22/05, and was believed to have been used some time around 12/20/05. The source is used for chemical analysis in a Gas Chromatograph. The RSO believes this source to be misplaced and not stolen. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | GA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-01-25
42285 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2006-01-24 19:32 | 2006-01-25 01:33 | 2006-01-25 | INVALID HIGH PRESSURE CORE SPRAY (HPCS) INITIATION SIGNAL DURING SURVEILLANCE TESTING "50.72 (b) (3) (vi) Non-Emergency 8Hr Reportable "When I&C was performing STP-051-4256, HPCS Drywell Pressure High Channel Calibration and Logic System Functional Test (B21-N067R, B21-N667R), a human performance error resulted in an invalid HPCS initiation signal. Division III diesel generator and the HPCS pump started. The HPCS injection valve stroked open and was manually overridden closed after full open indication, thus HPCS system injection was terminated. HPCS System was unavailable due to being overridden with an initiation signal present from 1932 until 2109 [CST] for a total of 1 Hr and 37 minutes. "NUREG 1022 states that single-train systems that perform safety functions (i.e., HPCS), when lost, prevents the fulfillment of the safety function of that system." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-01-25
42284 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-10-18 | 2006-01-24 10:23 | 2006-01-24 | AGREEMENT STATE - MISSING SOURCES FOLLOWING HURRICANE KATRINA The State reported that a number of radioactive sources are missing following detailed inventories in the aftermath of Hurricane Katrina. The following two sources appear to have disappeared under suspicious circumstances (possibly associated with looting of the hospital after the hurricane): Co-57 Button IP SSM-057-100U #1111-41-2, 100 microCi 4/1/05, now 56.4 microCi Co-57 Button IP SSM-057-100U #1111-41-5, 100 microCi 4/1/05, now 56.4 microCi Material is also missing after the refurbishment of the Radiation Laboratory Room. The detectable radioactive sources were removed from the room before it was gutted. Inventory after the material was sorted out showed that the following sources were missing: 1. Co-57 button source Syncor 644-10A 200 microCi 3/1/99 now 0.4 microCi 2. Ba-133 liquid scintillation counter quench source 19 microCi 12/31/87 now 6 microCi 3. Lead pig containing approximately 0.1 microCi R-226 fixed contamination now 0.1 microCi 4. I-125 radiation therapy eye plaque seeds (886 seeds dating from 12/95 to 12/03) in lead container marked "Haik AA" now 0.6 microCi 5. I-125 radiation therapy eye plaque seeds (116 seeds dating from 4/04 to 3/05) in lead container marked "Haik BB" now 2.8 microCi All material debris from the room was placed into dumpsters for disposal in landfills. No Louisiana Event # was provided with this report. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-01-27
42283 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2006-01-23 12:40 | 2006-01-23 17:00 | 2006-02-10 | LOST AMERICIUM SOURCES The station commenced an inventory of sources in December 2005. Two sources were missing and are still unaccounted for. The licensee suspects that the sources were thrown away in radioactive trash. The two Americium-241 sources were 0.025 microCuries and 0.026 microCuries. The sources were purchased in 1981 and had since been retired from use and placed in storage. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM C. BLAIR TO W. GOTT ON 2/10/06 AT 1415 * * * "This is a RETRACTION to Event # 42283. "At 1210 CST on 01/23/2006, Cooper Nuclear Station determined that two Americium-241 sources were missing and could not be located. One source is 0.025 microCuries, the other source is 0.026 microCuries. The 10 CFR 20 Appendix C quantity for Americium-241 is 0.001 microCuries. Each missing Americium-241 source is greater than 10 times the Appendix C quantity but less than 1000 times the Appendix C quantity. "The sources were originally acquired in 1981 as internal calibration sources in a complete Stabilized Assay Meter, (SAM-2) for counting air samples in the Emergency Operations Facility (EOF). In August 1999 the SAM-2s were no longer needed in the EOF and were taken inside the radiological controlled area for storage. During the 2005 inventory the sources were discovered missing. "10 CFR 30 provides regulations for licensing byproduct material. 10 CFR 30.15 identifies quantities of certain isotopes that are exempt from the requirements of parts 20, 30 through 36, and 39 of title 10 CFR. 10 CFR 30.15(a)(9)(iii) provides a quantity of 0.05 microCuries of Americium-241 as being an exempt quantity for an internal calibration source in an ionizing radiation measuring instrument. Both of the missing sources were smaller than 0.05 microCuries and thus exempt from the requirements of 10 CFR 20. "Since the sources are exempt from the requirement to be licensed and thus exempt from the requirements of 10 CFR 20 this event is not reportable. This has no impact on the operating plant." The licensee will notify the NRC Resident Inspector. Notified NMSS (G. Morell) and R4DO (A. Gody). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2006-01-23
42282 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2006-01-23 06:15 | 2006-01-23 08:13 | 2006-01-23 | OFFSITE NOTIFICATION INVOLVING LAW ENFORCEMENT ACTION "On 1/23/2006, a contract individual on his way to work stopped to help a female individual on the side of the road. Three armed men hijacked him and his vehicle. The contract individual then proceeded to the Davis-Besse Nuclear Power Station (his intended destination), where he stopped at the Vehicle Inspection Facility at approximately 0615 hours. The three men jumped out of the vehicle and headed back toward the highway, away from the protected area. Efforts are underway to locate the individuals. The local sheriff is bringing helicopters to the area to aid in their search. There have been no indications of a threat to the facility." HOO Note: This event was originally phoned into the NRC Operations Center as a Security Information Database report #2838. This was reported by the licensee as a offsite notification under 10 CFR 50.72 based on the significant law enforcement interaction related to this report. * * * UPDATE FROM MYERS TO HUFFMAN AT 1031 EST ON 1/23/06 * * * The licensee has secured from joint Security-Law enforcement activities as of 1018 EST. Local Law Enforcement has been notified. The licensee will notify the NRC Resident Inspector. Subsequent to this notification, Davis Besse executive management (Allen and Bezila) indicated that the individual that reported the car-jacking is believed to have fabricated the story. He has been transported to a medical facility for observation. The licensee has performed confirmatory searches along with law enforcement of the OCA and considers that there is no longer any concern related to this incident and has returned to normal security posture. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 1 | 2006-01-23
42281 | 0 | MERCY HOSPITAL - SCRANTON, PA |  |  |  |  | 2006-01-20 15:00 | 2006-01-20 17:46 | 2006-01-20 | LOST IODINE SEEDS After an implantation procedure using Iodine 125 seeds was performed at 1500 at Mercy Hospital of Scranton, PA the staff became aware that there were potentially 2 seeds missing. The total activity of the 2 seeds is estimated to be 1.26 millicuries. The hospital ordered 88 seeds for this operation. 68 seeds were implanted in the patient. The number of implanted seeds was verified using an x-ray. After the operation the hospital counted 18 remaining seeds for return shipment to the seed provider thus, 2 seeds were unaccounted for. The hospital performed surveys of the operating room and was unable to locate any other seeds. At the time of the report the operating room was quarantined for further investigation. The hospital contacted the health services company that sterilized the seeds to determine if fewer seeds were provided but Anazao Heath was unable to provide an exact count of the seeds. On Monday 1/23/06 the Radiation Safety Officer plans to contact the seed provider, Amersham Health to determine an exact count of seeds shipped. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2006-01-20
42280 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-01-20 10:17 | 2006-01-20 17:07 | 2006-01-20 | PUBLIC PROMPT NOTIFICATION SYSTEMS SIRENS DISCOVERED INOPERABLE "The Public Prompt Notification System sirens were inoperable from 10:17 CST until 11:36 CST on 01/20/06. [They were inoperable for] a period of one hour and 19 minutes. The siren system was returned to operation when the antennae for operating the sirens was changed. The Tone Alert Radio System was operational during this entire time period and remains operable. The cause of the failure is not clearly understood at this time. The appropriate test equipment is being sent to the site and a complete troubleshooting plan with a test plan will be started on Monday 01/23/06. Until that time a contingency plan is in place that has personnel on call that will report to the three siren sites if an emergency is declared. They will be in communications with the local authorities to activate the sirens locally in accordance with an approved plant procedure. While performing the troubleshooting and maintenance on the siren system we will have staff standing by at the sirens that will be able to activate the sirens in accordance with an approved plant procedure." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-20
42279 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-01-20 14:00 | 2006-01-20 16:44 | 2006-01-20 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE At about 1400 hours Central Standard Time, while working at a site in Fort Worth, a 2003/2004 Chevrolet pick-up carrying a Troxler moisture density gauge belonging to the licensee was stolen. The gauge is a model number 3440 with a serial number of 28640. It has two sources. One is a 44 millicurie Americium-Beryllium source (model # A/S AmBe Model 997 Type X-LP 3021 and 3027) and the other is a 9 millicurie Cesium-137 source (model # A/S CDCW556; IPL Model HEG/137-AM). The licensee called the State an hour after the truck and gauge were stolen. The licensee filed a police report. The State of Texas is continuing to investigate the incident. Texas Incident #: I-8290 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-01-25
42278 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2006-01-20 14:40 | 2006-01-20 15:27 | 2006-02-21 | SAFEGUARDS REPORT "Safeguard material was not maintained in accordance with the security plan and therefore not in accordance with 10CFR73.71.b.1. "NRC Region 1 and the Hope Creek Resident have been contacted with additional information. "All Safeguards material has been recovered and is under proper control." The material has been in this condition since 2000 and there is no suspected compromise of the material. * * * UPDATE AT 1604 EST ON 2/21/06 FROM MIKE REED TO S. SANDIN * * * The licensee is retracting this report based on the following: The licensee completed their review of the event and concluded that it was not reportable. Contact the Headquarters Operations Officer for additional details. Notified R1DO(Henderson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 73.71(b)(1) |  |  |  | 1 | 2006-01-20
42277 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2006-01-20 08:56 | 2006-01-20 12:49 | 2006-01-20 | RPS ACTUATION "On 1/20/2006 at 0730 hrs, a Unit 2 control room annunciator was received indicating high conductivity/sodium in the main condenser. The Chemistry Dept. confirmed the sodium level was high indicating saltwater intrusion from a tube leak in the 2B2 Condenser Waterbox. Per the Secondary Chemistry Off-Normal Procedure, a rapid downpower to less than 5% power was initiated to remove the affected waterbox from service. It was decided to go ahead and remove Unit 2 from service rather than remain critical at a low power level. The downpower was planned to decrease power to approximately 25%, perform a manual transfer of plant electrics to the auxiliary transformers, and then manually trip the reactor in accordance with plant procedures. All systems worked as planned during the downpower and the reactor was manually tripped at approximately 25% power at 08:56 hrs. Standard Post Trip Actions and the Reactor Trip Recovery Procedure were carried out without incident. "All control rods fully inserted and no Steam Generator (S/G) Safety Valves lifted. Feedwater to the S/G was supplied by the Main Feedwater pumps during the shutdown and later transferred to the Auxiliary Feedwater pumps. All safe shutdown equipment operated as expected. The plant is stable in Mode 3, Hot Standby conditions, with decay heat removal being accomplished by steaming through the Atmospheric Dump Valves. The Main Feedwater pumps remain available if needed. "Unit 1 was not affected by this event." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2006-01-20
42276 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2006-01-20 11:25 | 2006-01-20 11:34 | 2006-01-20 | PRESS RELEASE ISSUED REGARDING AGREEMENT WITH DOJ RELATED TO DAVIS-BESSE REACTOR HEAD ISSUE "A press release is being made today by the First Energy Nuclear Operating Company that it has entered into a deferred prosecution agreement with the U.S. Attorney's Office related to FENOC's communication with the NRC during the fall of 2001 in connection with the reactor head issue at the DBNPS. FENOC has agreed to pay a penalty of $28 million." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-01-20
42275 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2006-01-19 13:00 | 2006-01-19 17:02 | 2006-01-19 | AGREEMENT STATE REPORT - LOST IODINE SEED "Thirteen I-125 seeds were implanted in a patient on 1/11/2006 and removed on 1/18/2006. After removal, seeds were transferred to Hot Lab at which time it was discovered that one of the seeds [1.43 millicuries I-125] was missing. All seeds were moved from patient. A search was conducted of the O.R., the patient and the traverse route. The seed has not been found at this time. The licensee stated that a doctor rinsed the item containing the sources in the sink in the O.R., and that it is possible that the missing source was rinsed down the drain. Florida is investigating." Incident Number: FL06-012 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2006-01-24
42274 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2006-01-19 13:04 | 2006-01-19 14:00 | 2006-01-19 | OFFSITE NOTIFICATION OF MINOR OIL SPILL An excavator leaked approximately three cups of oil within the site boundary. The spill created a sheen on water in the discharge canal. The spill was contained and the soil and water were cleaned up. The licensee notified the State Police, Department of Environmental Protection, and the Coast Guard. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-01-19
42273 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-01-18 | 2006-01-19 09:35 | 2006-01-19 | AGREEMENT STATE REPORT OF AN EXTREMITY EXPOSURE GREATER THAN LIMIT The State provided the following information via email: "A Nuclear Pharmacy Technician was preparing Tc-99m doses in a very busy pharmacy when his weekly extremity monitor reached an annual limit with a reading of 53,440 mrem for the calendar year of 2005. The licensee's corrective action includes additional training, possible modification of technique, and having corporate health physics staff investigate the incident. The dose was being monitored and management did not anticipate that the employee would exceed the maximum but he had a 'hard week' (12/26-01/06) where his right hand received 3,120 mrem. Corrective action will include hiring new techs since two other dose drawing techs have been 'benched' earlier in the year before their extremity doses would have exceeded the regulatory maximum. Reportedly the RSO and manager [redacted] did not receive the report until today. This is the 3rd busiest nuclear pharmacy in the world supplying ~1,000 doses/day to the greater Houston area. " TX Event Report ID: TX-06-42273 TX Incident # I-8289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-01-24
42272 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2006-01-18 10:00 | 2006-01-18 19:25 | 2006-01-18 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING FIRE PROTECTION PROGRAM NON-COMPLIANCE "This notification is being made pursuant to the Perry Nuclear Operating License section 2.C.6 (violation of the Fire Protection Program). "Incorrect configuration of Division 1 remote shutdown panel wiring was identified during performance of surveillance testing. This incorrect configuration is associated with the Reactor Core Isolation Cooling motor operated exhaust valve. In the event of a fire in the control room, the motor operated exhaust valve would have the potential for spurious operation caused by fire induced shorts prior to isolation from the control room. Repairs and operator actions could have been taken to restore the valve. However, these repairs and operator actions are not currently identified in the Fire Protection Safe Shutdown analysis or associated operating procedures. Therefore, for this issue Perry does not comply with the Perry Fire Protection Program. "Repairs have been completed and configuration has been restored." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 84 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0 | 2006-01-18
42271 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2006-01-12 | 2006-01-18 18:05 | 2006-01-20 | AGREEMENT STATE REPORT REGARDING A DAMAGED TROXLER MOISTURE DENSITY GAUGE The State provided the following information via email: "ABSTRACT: The licensee states the gauge was in use near several construction vehicles [at a work site in Clackamas, Oregon]. The gauge was located behind a nearby pickup truck attached flatbed trailer. The gauge user thought the vehicles were not occupied. A driver in the truck started the vehicle and promptly backed it into the gauge before it could be moved by the operator, resulting in damage to the index rod. No other damage was noted. The licensee says the gauge operator was in proper control of the gauge at the time the truck struck the gauge. Regardless, the licensee will provide training to the operators reminding them of the requirements to maintain proper surveillance and control of gauges while away from the licensed storage locations. An explanation of what occurred in this event was also provided to the operators as lessons learned. "Notification Reporting Criteria: WAC 246-221-250 Notification of Incidents. "Isotope and Activity involved: 8 mCi of Cesium 137, and 40 mCi of Americium 241/Beryllium. "Damaged Troxler 3430, serial number 31153. "Disposition/recovery: The licensee was able to get the source rod back into the shielded position. They had a count rate survey meter and used it to determine that readings were normal. They called the manufacturer's local representative and the RSO for Troxler in North Carolina. The licensee was instructed on how to package the gauge properly. The gauge was taken back to the licensed and secured storage area where additional gauge packaging was used to secure the damaged index rod. They took a wipe test of the gauge. The results came back normal to allow for a normal means of shipping back to Troxler in North Carolina. Shipping is scheduled for January 19, 2004. "Leak test? Leak test analysis - less than 0.005 microcuries. "Release of activity? None found. "Consultant used? Local Troxler representative and Troxler RSO. Event Report # WA-05-006. * * * UPDATE ON 01/20/06 * * * The correct Washington Event report number is WA-06-006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2006-01-23
42270 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2006-01-14 | 2006-01-18 17:38 | 2006-01-18 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via fax: "N.C. Radiation Protection Section was notified on 18 Jan 2006 by the RSO for the Charlotte Mecklenburg Hospital Authority of a misadministration during a manual brachytherapy treatment. The authorized user's written directive called for a temporary implant 'tandem and ovoid' using Cs-137 sources to deliver a total dose of 4883 RAD (approximately 49Gy) over 68 hours, with following source loading in the applicator: "Right Ovoid: 1 at 14.6 mgRaEq [milligram Radium Equivalent] (approximately 51.1 mCi or 1891 MBq) Left Ovoid: 1 at 14.6 mgRaEq Tandem: 1 at 11.2 mgRaEq (approximately 39.2 mCi or 1450 MBq), 2 at 14.6 mgRaEq "A medical dosimetrist loaded the tandem and ovoid incorrectly. The actual loading of the applicator was: "Right Ovoid: 1 at 14.6 mgRaEq (approximately 51.1 mCi or 1891 MBq) Left Ovoid: 1 at 14.6 mgRaEq Tandem: 1 at 11.2 mgRaEq (approximately 39.2 mCi or 1450 MBq), 2 at 24.8 mgRaEq (approximately 86.8 mCi or 3212 MBq) "This errant loading of applicator resulted in the patient receiving 6474 RAD (approximately 65 Gy) to the treatment area. The delivered dose was 33 percent more than prescribed. "The Cs-137 sources utilized in the procedure were: "3M Model 6503 (14.6 mgRaEq) 3M Model 6502 (11.2 mgRaEq) AEA Technology/QSA Model CDC.T1 (24.8 mgRaEq) "The licensee is conducting follow-up investigations and will make a report the Radiation Protection Section within 15 days of the discovery of the event. The report will contain root cause analysis and procedures to prevent recurrence. "N.C. Radiation Protection has not received any media attention as of this report. No press release has been issued." Event Report ID No.: NC-06-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2006-01-23
42269 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-01-18 12:45 | 2006-01-18 17:29 | 2006-01-18 | LOSS OF EMERGENCY RESPONSE CAPABILITY DUE TO WEATHER "On January 18, 2006, at 12:45 hours, Westchester County Emergency Operations Center notified Indian Point that their local emergency service agencies would not be able to accomplish route alerting in the event of an emergency at Indian Point in accordance with the Emergency Plan due to weather related conditions in Westchester County. Westchester County advised that all Westchester County emergency response agencies are fully engaged in storm related responses and have no available manpower. At the time of the Westchester County notification, 18 of 79 sirens in Westchester County were without power due to weather. Westchester County was contacted by Indian Point and the use of outbound calling was discussed. Although Westchester County stated they would use outbound calling, they indicated a concern regarding the availability of the public switch network. New York State Emergency Management office was also contacted by Indian Point regarding this issue and they in turn contacted Westchester County to offer support. In addition, the other counties (Putnam, Rockland and Orange) were contacted regarding their ability to initiate route alerting. Each of the other counties confirmed their ability to perform route alerting. In accordance with NRC reporting guidelines (NUREG1022), if a significant natural hazard causes parts of the response infrastructure to be impaired to the extent that the State and local governments are rendered incapable of fulfilling their responsibilities in the Emergency Plan for the plant, the NRC must be notified. Therefore, based on Westchester County's stated condition, an 8-hour non-emergency notification is being made in accordance with 10 CFR 50.72(b)(3)(xiii). The condition was recorded in the Indian Point Energy Center Corrective Action Program as CR-IP2-2006-00256 and actions have been initiated to investigate and correct the condition. The notification of the loss of sirens was reported at 11:57 hours, by Event Notification log No. 42266. At 16:41 hours, Westchester County advised Indian Point that local municipalities will be able to handle required route alerting responsibilities if there is an event at Indian Point." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-18
42268 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-01-21 | 2006-01-18 15:30 | 2006-01-18 | AGREEMENT STATE REPORT OF MISSING MOISTURE DENSITY GAUGE The State provided the following information via email: "RSO for Earth Consultants, claims his company has broken up and his Alternate RSO has taken their single moisture density gauge. The gauge is a CPN model 503, source model 131 serial number H300305517. This information was first provided in a letter dated 1/21/05 and he has not been able to locate his former ARSO. RHB Richmond has determined that the former ARSO is probably located in Greenfield, CA. RHB will continue its efforts to locate the former RSO and the gauge. RHB Richmond has spoken to the RSO and suggested that he report the gauge as stolen by his former ARSO to the local authorities and request license termination." These gauges typically contain 10 milliCi of Cs-137 and 40 milliCi of Am-241. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-01-23
42267 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2006-01-18 11:34 | 2006-01-18 15:06 | 2006-01-18 | LOSS OF OFFSITE PUBLIC PROMPT NOTIFICATION FOR GREATER THAN ONE HOUR "Offsite Public Prompt Notification System, Sirens and Tone Alert Radios were inoperable for greater than one hour. The Primary Console for siren operation at Houston County was found to be non functional at [approximately] 0820 CST during periodic siren tests. The backup console did successfully operate the sirens. However, at 1030 CST the transport system for actuating system failed at Webb, AL and the Backup Console for siren operation as well as Tone Alert Radios became inoperable. The inoperability of the system lasted for one hour and five minutes, being restored at 1134 CST. Initial troubleshooting indicates the problem was with the fiber coaxial cable to the demultiplexer in the transport. The problem could not be repeated, and investigation continues. Repairs for the Primary Console for siren actuation are being facilitated." The licensee notified the NRC Resident Inspector and Houston County. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-18
42266 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2006-01-18 08:48 | 2006-01-18 11:57 | 2006-01-18 | LOSS OF POWER TO OFF-SITE EMERGENCY SIRENS "On January 18, 2006, at 08:48 hours, Emergency Planning determined that greater than 15 of a total of 156 sirens were reported as unavailable due to weather related loss of power as a result of high winds. In accordance with the Indian Point reporting procedure, the loss of 16 or more sirens that can not be returned to service in one hour, constitutes a major loss of the offsite notification capability that requires an 8-hour non-emergency notification in accordance with 10 CFR 50.72(b)(3)(xiii). The condition was recorded in the Indian Point Energy Center Corrective Action Program as CR-IP2-2006-00246 and actions have been initiated to investigate and correct the condition." As of 11:40 EST on 01/18/06 there were 31 of 156 sirens out of service. The licensee notified the NRC Resident Inspector, as well as the Counties of Westchester, Putnam, Rockland, and Orange. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-18
42265 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2006-01-10 | 2006-01-18 07:34 | 2006-01-18 | AGREEMENT STATE REPORT INVOLVING A MEDICAL EVENT The State provided the following information via fax: "On January 10, 2006, a patient was to receive an Iodine-131 therapy dose of 150 mCi (2 capsules). Upon review of the dose it was determined that the dose received was only 75 mCi (1 capsule)." This incident was reported to the GA Radiation Control Program on 1/17/06. GA Incident Summary: GA-2006-03I. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2006-01-23
42264 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-01-17 08:56 | 2006-01-17 18:03 | 2006-01-17 | AUTOCLAVE STEAM LEAKAGE DURING HEATING OPERATION "On 01/17/06 at approximately 0856 hours, X-344 Operations Personnel identified visible steam out leakage on Autoclave #2. The autoclave was operating in Operational Mode II 'Heating' at time of discovery. The out leakage was determined to be a failure of the autoclave shell 'O' Ring ( 'Q' Safety System Component) which seals the autoclave enclosure. The steam was immediately valved off, autoclave placed in Non-TSR applicable Mode VII 'Shutdown', and declared inoperable by the Plant Shift Superintendent. No release of Radiological Material occurred. This incident is being reported as a Safety Equipment Failure while operating in a TSR Applicable Mode." The licensee also notified NRC Region 2 (Hartland) and the DOE Site Representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-01-17
42263 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-11-22 | 2006-01-17 15:30 | 2006-01-17 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via facsimile: "The patient was planned to receive an HDR brachytherapy dose of 750 cGy in a single fraction to a distance of 1.0 cm beyond the active dwell positions in the right lung. A catheter was inserted in the right bronchus on November 22, 2005 for the treatment. The catheter was marked at the entrance of the nostril and taped to the nose and face. The patient was then taken to CT for the treatment planning. The treatment plan was developed and approved. The patient was treated in a linear accelerator vault. Prior to treatment, a dummy wire was placed into the catheter and a megavoltage portal image was taken to confirm placement of the catheter. The radiation oncologist believed that he had verified the catheter placement from the portal image. The catheter was connected to the HDR unit and the treatment was performed. At the conclusion of the treatment, the prescribing physician and nurse entered the treatment room to remove the catheter from the patient. At that time it was discovered that the catheter was not fully inserted into the patient's lung. The mark that was put on the catheter during the planning was 15 cm outside of the nose. Apparently the catheter had become loose from the tape. According to the prescribing physician the dose used for this treatment was not enough to produce any significant sequalae in the upper thorax and neck region. The patient was informed on 11/22/05. External beam therapy will be used for the missing dose to the lung. Some procedures have been modified to prevent this from reoccurring." LA Event Report ID No: LA050009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2006-01-20
42262 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2006-01-16 18:31 | 2006-01-16 23:16 | 2006-01-16 | HPCI SYSTEM ISOLATED DUE TO ATTS CARD FAILURE "HPCI (High Pressure Coolant Injection) isolation rendered the HPCI system inoperable. An ATTS card 2E41-N658B, for HPCI steam line low pressure, failed. Concurrent with this card failure was several annunciators, one of which was 'HPCI Steam Line Diff. Press High'. One HPCI steam line low pressure card failing or tripping will not cause a HPCI isolation, but one HPCI steam line differential press high trip condition (indication of high flow) will cause an isolation. Both of these cards are fed from the same power supply. Investigation to confirm the isolation cause is in progress." Licensee indicated 2E41-F003, outboard isolation valve, auto closed and 2E41-F002, inboard isolation valve was manually closed. The licensee notified the NRC Resident Inspector. | 0 | 72 | 0 | 0 | 72 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-01-16
42261 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2006-01-16 17:03 | 2006-01-16 19:36 | 2006-01-16 | SMALL FIRE OCCURRED IN SECURITY DEPARTMENT STORAGE AREA. A small fire occurred in the Security Department storage area, located in a administration building. The licensee requested off-site assistance and the fire was extinguished in approximately 15 minutes. As a result of the fire, there was no damage to plant related equipment and station security was not compromised. An Event Review Team is being assembled to investigate the cause of the fire, which at this time is unknown. The following fire departments responded to the site: Jordan Fire Department Goshen Fire Department Oswegatchie Fire Department Cohanzie Fire Department Niantic Fire Department" The licensee stated there will not be a press release concerning this fire, nor is there expected to be a press inquiry. The licensee notified the NRC Resident Inspector, as well as State and local governments. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-01-16
42260 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2006-01-15 11:04 | 2006-01-15 12:36 | 2006-01-15 | TS SHUTDOWN DUE TO ELECTROMATIC RELIEF VALVES (ERVS) DECLARED INOPERABLE "At 1014 hours on January 15, 2006, the four Unit 1 Electromatic Relief Valves (ERVs) were declared inoperable due to concerns related to the ERV actuators. These operability concerns originated from inspections and testing performed on the Unit 2 ERVs which indicate evidence of mechanical interference issues that could prevent proper ERV operation (note that Unit 2 was shutdown on January 14, 2006 to perform ERV actuator inspections). In accordance with Technical Specification 3.4.3, Condition B, 3.5.1 Condition H, and 3.6.1.6 Condition B, Unit 1 commenced a shutdown on January 15, 2006 at 1104 hours. "This notification is being made in accordance with 10 CFR 50.72(b)(2)(i) as commencement of any nuclear plant shutdown required by the plant's Technical Specifications. "During the upcoming Unit 1 outage, actuator inspections and ERV testing is planned to confirm the operational ability of the ERVs. Note that the Unit 1 Target Rock Relief Valve and the Main Steam Safety Valves are operable and available to support reactor overpressure protection." The plant is conducting a normal shutdown per Tech Spec requirements. At 1600 CST the unit will going off line and by 2400 CST the plant is expected to be in Mode 4 (Cold Shutdown). The licensee notified the NRC Resident Inspector. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2006-01-15
42259 | 0 | VIGO COAL COMPANY |  |  |  |  | 2006-01-11 | 2006-01-14 11:44 | 2006-01-14 | COAL ANALYZER SHUTTER INSTALLED INCORRECTLY Last Wednesday, 01/11/06, an NRC Inspector discovered that the company's SABIA online, Model No. XC-5000 coal analyzer which contains a Cs-137 source could not lock the shutter closed. The online analyzer is used for elemental analysis of coal. Vigo Coal contacted SABI, located in CA and their representatives arrived at Vigo Coal Company this morning, 01/14/06. The SABIA representative found that the lever arm to the shutter of the camera was installed 180 degrees out of its proper position (reversed). The SABIA representative took the two screws out and reversed the handle, which corrected the problems. The shutter worked properly. The holes on the lever and the camera shutter now line up so a padlock can be installed to lock the camera shut. There were no personnel exposures, contamination nor safety issues associated with this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-01-14
42258 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2006-01-13 16:45 | 2006-01-13 20:58 | 2006-01-13 | LOSS OF COMMUNICATIONS - GREATER THAN 25% OF EMERGENCY NOTIFICATION SIRENS UNAVAILABLE "At 1645 on 01/13/2006, greater than 25% of the Clinton Power Station emergency notification sirens became unavailable, most likely caused by inclement weather. A total of 18 of the 44 sirens were unavailable. "At 1745, 15 of the 18 inoperable sirens were restored to an operable status. 1(one) siren remains unavailable due to a loss of communication and two others due to loss of power. "At 1745, this condition was considered to be a major loss of emergency preparedness. Restoration of the 3 remaining unavailable sirens is in progress. Appropriate compensatory measures are in place for the 3 remaining unavailable sirens." The licensee notified the local DeWitt County Sheriff office and the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-13
42257 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-01-13 08:30 | 2006-01-13 16:53 | 2006-01-13 | PRESSURIZER PORV STROKE TIMES EXCEED ANALYSIS ASSUMPTIONS "The analyses for the Callaway Cold Overpressure Mitigating System (COMS) assumes an opening time and delay time for the pressurizer Power Operated Relief Valves (PORV)s. Evaluations performed by Callaway engineering personnel have determined that PORV stroke times measured during surveillance testing do not account for all of the delay times credited in the Design Bases COMS Analyses of Record. Further reviews determined the allowed delay times could not be met by the control loop. This results in potentially non-conservative PORV lifts settings relative to those specified in the PTLR (Pressurizer & Temperature Limits Report) for satisfying Technical Specification (TS) 3.4.12.a and 3.4.12.c. "At the time the determination was made, the plant was in Mode 1. Technical Specification 3.4.12, COMS, is applicable in Mode 4 with RCS temperature less than or equal to 275 F, Mode 5 (cold shutdown) and Mode 6 (refueling) with the head on the reactor vessel. The TS allows other methods of providing cold overpressure protection (ex. Residual Heat Removal system suction relief valves). "Remedial actions have been initiated to ensure the COMS TS function is maintained when required, pending completion of corrective actions." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2006-01-13
42256 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2006-01-12 | 2006-01-13 16:24 | 2006-01-13 | AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The State provided the following information via facsimile: "The South Carolina Department of Health and Environmental Control was notified (telephone) on January 13, 2006, by the licensee, that a medical misadministration had occurred. A patient being treated with a Iridium 192 HDR after loading brachytherapy system received a fractionated dose that differed from the prescribed dose, for a single fraction, by 50 percent or more. The patient was undergoing the first of three treatments to the pelvic region. The prescribed dose for this first treatment was 700 centigray but the patient only received 233 centigray, approximately one third of the intended dose. Further details of the misadministration will be supplied by the licensee in the forthcoming written report. Updates to this event will be made through the NMED system." SC Report ID No. - SC060001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2006-01-18
42255 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2006-01-05 | 2006-01-12 17:32 | 2006-01-12 | LEAKING SEALED SOURCE DUE TO IMPROPERLY PACKAGED MATERIAL The State provided the following information via email: "On January 11, 2005 the Division learned of an event involving a leaking sealed source that was intended for the therapeutic treatment of prostate cancer. On January 5, 2006, the Chicago Prostate Cancer Center (CPCC) in Westmont, IL (IL-02015-01) received four packages [which] contained sources that had been loaded into [an] applicator as well as 'loose seeds' for reference and potential application. One of the four packages contained 10 sealed sources of Cs-131 and 42 additional sources (actual activity of 3.8 milliCi, each) [were] pre-loaded into treatment applicators by Anazao Health of Tampa Florida via IsoRay, Inc of Richland Washington who manufactured the sources. "Although the outer packaging was shown to be free from contamination, once the cardboard outer container was opened, and the secondary lead container was opened, a seed was visually detected on the outer lead container. The seed was also notably damaged. Associated contamination was subsequently found on the secondary container, and the primary lead container as well as a second 'seed' of Cs-131 that had been trapped and bent within the primary lead container. Although all the sources were accounted for, none of the 10 seeds were contained within the innermost glass vial as its lid was not engaged with the vial. Cs-131 is a very low energy gamma emitter (33 KeV) with a half life of 9.7 days. The form of Cs involved is bound to a non-volatile, insoluble material. "The Division discovered that the CPCC had experienced widespread contamination within the source preparation area as a result of the damaged sources and the failure to don proper protective gloves. The affected surfaces and items had been subsequently decontaminated and set aside as waste by the staff that was present on January 5, 2005. Contamination levels ranged from 1,000 cpm to 5,000 cpm as measured by their Geiger counter and rate meter. Items which had been touched by the medical physicist who had not been wearing disposable gloves were found to be contaminated. One of the assisting staff members experienced contamination on their hand that was later completely decontaminated. "A Division representative was dispatched from the West Chicago offices to the facility shortly after we were notified, to determine the effectiveness of the decontamination effort, the extent of contamination that may have remained and to interview the Radiation Safety Officer [redacted]. The inspector's initial investigation today showed that contamination was limited to the source handling room which is a restricted area and that indeed all the sources were accounted for and secured. She also obtained the verbal report from [the RSO]. The only remaining contamination she was able to find were two spots on a counter of approximately 1,000 cpm - 2,000 cpm and the containers which were involved. The inspector returned to the facility on the following day to interview the responsible physicist, and the assisting technician. Gamma spectroscopy performed on samples of the contaminated items indicate the presence of Cs-131 rather than any of the other nuclides used by the facility. "The Division is continuing its investigation and is acquiring additional information from the licensee. The Division has been in contact with the State of Washington regarding this matter. A formal report is due from the licensee within the next 30 days. This event was reported to the U.S. NRC Operations Center on January 12 and assigned event number 42255." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2006-01-17
42254 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2006-01-12 09:20 | 2006-01-12 16:07 | 2006-01-12 | CONTROL ROOM AIR CONDITIONING AND CONTROL ROOM EMERGENCY VENTILATION SYSTEMS INOPERABLE "At 0400 hours on January 12, 2006, 2A Control Building Standby Instrument Air Compressor was taken out of service for scheduled maintenance. Subsequently, at 0920 hours, the in-service 2B Control Building Standby Instrument Air Compressor failed, resulting in the loss of control air. As a result, the three Control Room Air Conditioning subsystems required by Technical Specification (TS) 3.7.4, "Control Room Air Conditioning (AC) System," and the two Control Room Emergency Ventilation subsystems required by TS 3.7.3, "Control Room Emergency Ventilation (CREV) System," became inoperable. As a result, this condition could have prevented the fulfillment of the safety function for these systems. The Control Room AC and CREV systems became inoperable due to loss of control air to the systems. Because Brunswick has a shared control room, Unit 1 and Unit 2 entered TS 3.7.3 Required Action B.1, for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours) and TS 3.7.4, Required Action E.1, for three Control Room AC subsystems inoperable (i.e., enter LCO 3.0.3 immediately). "Operability of two Control Room AC subsystems and one CREV subsystem was restored and LCO 3.0.3 was exited, at 1014 hours, when the 2A Control Building Standby Instrument Air Compressor was restored to service. [The licensee stated the actual maintenance was completed on 2A Control Building Standby Instrument Air Compressor at the time it was restored to service.] "No power reduction took place as a result of the LCO 3.0.3 entry. This report applies to both Units 1 and 2 and is being made in accordance with 10 CFR 50.72(b)(3)(v)(D), as a condition that at the time of discovery could have prevented fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "The safety significance of this event is considered minimal. The condition existed for approximately 54 minutes. Plant staff took immediate actions to return the equipment to service. For the brief time the Control Room AC and CREV systems were inoperable, performance of plant personnel and equipment in the Control Room was not adversely affected. The maximum Control Room back panel temperature during this event was approximately 73 degrees F. "Operability of the Control Room AC system and one subsystem of the CREV system were restored at 1014 hours when the 2A Control Building Standby Instrument Air Compressor was restored to service. Troubleshooting activities are under way to determine the cause of the 2B Control Building Standby Instrument Air Compressor failure. Initial indications are that the unloading ability of the 2B Control Building Standby Instrument Air Compressor failed." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2006-01-12
42253 | -1 | NEW BRITAIN GENERAL HOSPITAL |  |  |  |  | 2006-01-11 09:15 | 2006-01-12 10:18 | 2006-01-19 | LICENSEE DID NOT HAVE A WRITTEN DIRECTIVE BEFORE ADMINISTERING A DIAGNOSTIC WHOLE BODY SCAN. A patient had a physicians order to perform a diagnostic whole body scan but the two technologists over-looked that the patient did not have a written directive to give the patient 4.1 millicuries of Iodine-131. The patient got the correct dose of Iodine-131 for his diagnostic whole body scan. The licensee stated that they were operating under Departmental Protocol for Thyrogen Whole Body Iodine doses. * * * RETRACTION FROM C. MAJEK TO W. GOTT AT 1307 ON 01/19/06 * * * Based on discussions with NRC personnel, the licensee does not consider this to meet the criteria of a medical event. This event is retracted. Notified R1DO (C. Hott) and NMSSEO (G. Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2006-01-12
42252 | -1 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2006-01-11 12:48 | 2006-01-11 20:43 | 2006-03-03 | SHUTDOWN COOLING INOPERABILITY DUE TO SMALL DISCHARGE HEADER LEAK "On Wednesday, January 11, 2006, at approximately 1248 PST, with San Onofre Unit 2 in Mode 5 (loops not filled), Southern California Edison (SCE) declared both trains of the Shutdown Cooling (SDC) System inoperable. This action was taken following discovery and evaluation of an approximate 1.5 inch crack and minor leak (about 10 drops per minute) in a line located at the Low Pressure Safety Injection (LPSI) common discharge header (the LPSI pumps are also used as the SDC system pumps). Although both trains of the SDC system remain functional and one train is in service, SCE declared both SDC trains inoperable because the affected pipe might not be ASME Code qualified as a result of this crack. "SCE is conservatively reporting this event in accordance with 10CFR50.72(b)(3)(v)(B) as a condition that could prevent the remove residual heat. SCE is continuing to evaluate this condition. "SCE is following the actions required by Technical Specifications 3.4.8, and will repair the pipe crack during the current refueling outage, after the reactor core has been off-loaded to the spent fuel pool. SCE expects to place the plant in Mode 6 tomorrow. "At the time of this report, Unit 2 is in Mode 5 and Unit 3 is in Mode 1 at 100% power. The NRC Senior Resident Inspector, NRC Region IV, and the Nuclear Reactor Regulation Project Manager have been briefed of this event and will be provided with a copy of this report." Shutdown cooling has been running for approximately one week and the leak was initially discovered sometime on 01/10/06 during an inspection in which Boric acid accumulation was discovered . A work request was written to perform a more thorough inspection that was performed on 01/11/06. The crack is on an 8 inch line that returns to RCS Loop 2A which is normally isolated during high pressure shutdown conditions and reactor power operation. * * * RETRACTION FROM C. WILLIAMS TO W. GOTT AT 2039 EST ON 3/3/06 * * * "On January 11, 2006, Southern California Edison (SCE) reported to the NRC that both trains of Shutdown Cooling System (SDC) were inoperable at San Onofre Unit 2 due to a through-wall crack in a pipe in the common discharge header. That occurrence was reported to the NRC in accordance with 10CFR50.72(b)(3)(v)(B) for a condition that could prevent the removal of residual heat. "SCE has since analyzed the pipe integrity at the design basis conditions and determined the pipe would have remained intact and that system leakage through the crack would have remained below the allowable system leak rate. Based on these results, SCE concluded that the pipe was capable of performing its safety functions under design basis conditions. Because the system was always capable of performing its safety function, SCE is retracting the January 11, 2006 report. Nevertheless, SCE plans to submit a voluntary licensee event report to document this event and inform the NRC of the corrective actions taken. "At the time of this phone call, Unit 2 was in the middle of the Cycle 14 refueling outage and Unit 3 was at about 100 percent power. SCE has notified the NRC resident inspectors about this retraction and will provide them with a copy of this report." Notified R4DO (J. Whitten) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2006-01-11
42251 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2006-01-11 15:01 | 2006-01-11 16:39 | 2006-01-11 | OFFSITE NOTIFICATION DUE TO SMALL DISCHARGE OF UNKNOWN OILY SUBSTANCE "Approximately one gallon of an oily substance was spilled into the plant discharge cove of Lake Wylie. The source of the substance is unknown. Notification of the event has been made to South Carolina DHEC (Columbia and Fort Lawn offices) and the National Response Center (Report #784895)." The substance had been noticed earlier today in a yard drain sump, but was not removed prior to heavy rains on site forcing it into the discharge cove. The licensee will be notifying North Carolina and South Carolina Emergency Operations Centers, and the Emergency Operations Centers for York, Gaston, and Mecklenburg counties. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-01-11
42250 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2006-01-11 07:43 | 2006-01-11 14:16 | 2006-01-18 | MODIFICATION TO THE UNIT 2 PROCESS COMPUTER THAT WILL IMPACT ERDS AND SPDS "The Unit 2 Plant Process Computer System (PPCS) will be taken out of service for an approximate 2 week period to implement a planned modification. The current PPCS is being replaced and the computer outage is required to allow cutover to the new PPCS. During this time period ERDS and SPDS will not be available. Unit 2 ERDS and SPDS parameters will be monitored by control board indications. Compensatory actions have been developed. "This is an 8-hour reportable event per 10 CFR50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of plant systems will not be affected due to this planned action. "The Unit 2 PPCS outage started at 0743 CST on 1/11/2006. The licensee has informed the NRC Resident Inspectors of the modification and schedule. The NRC was previously notified of this planned outage via letter dated November 7, 2005." * * * UPDATE FROM J BAARTMAN TO W GOTT AT 2019 EST ON 01/18/06 * * * "The Unit 2 Plant Process Computer System (PPCS) was restored at 1801 CST on 01/18/06. The Unit 2 Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) have also been returned to service." The licensee notified the NRC Resident Inspector. Notified R3DO (M Phillips) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-11
42249 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2006-01-10 14:30 | 2006-01-10 17:30 | 2006-01-10 | OFFSITE NOTIFICATION TO LOCAL MEDIA DUE TO INADVERTENT SIREN ACTUATION "A single Alert Notification System siren inadvertently sounded. The Tensas Parish (Louisiana) Emergency Coordinator issued a notification to local media (KNOE - TV and radio) advising the public of the inadvertent sounding and that no emergency exists. The siren has been secured. There were no effects on plant operation." "The inadvertent siren actuation may have been due to bad weather in the area." "The NRC resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2006-01-10
42248 | 0 | PALISADES | 1 |  |  | [1] CE | 2006-01-10 14:30 | 2006-01-10 17:27 | 2006-01-10 | POSITIVE RANDOM DRUG TEST FOR NON-LICENSED EMPLOYEE SUPERVISOR "A non-licensed employee supervisor tested positive for a controlled substance (illegal drug) during a random fitness-for-duty test. The employee's access to the plant has been terminated." A work performance review is in progress. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2006-01-10
42247 | 0 | AK STEEL CORPORATION |  |  |  |  | 2006-01-09 11:30 | 2006-01-10 17:15 | 2006-01-11 | FAILURE OF SHUTTER TO CLOSE ON FIXED DENSITY GAUGE USED TO MEASURE STEEL THICKNESS At 1130 hours on 01/09, the air cylinder on a gate operating the shutter for a fixed gauge failed to close. The gauge, a SenTek device, model not identified, is generally licensed and contains a 1000 mCi Am-241 source. The device was removed from service and heavy steel plate was positioned to shield the source. Additionally, the affected area was isolated and posted. No unmonitored personnel exposures occurred. A SenTek technician arrived onsite and corrected the malfunctioning shutter as of 0900 hours 01/10/06. * * * UPDATE 1340 EST ON 1/11/06 FROM STEVE CUSTER TO S. SANDIN * * * Further investigation determined that the fixed gauge is a model THAM2 manufactured by ABB AccuRay. The initial report is required per 10 CFR 30.50(b)(2). AK Steel will be submitting a followup written report within 30 days. Notified R3DO(O'Brien) and NMSS (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2006-01-10
42246 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2006-01-10 11:00 | 2006-01-10 15:51 | 2006-01-11 | LOSS OF ENS AND COMMERCIAL LINE COMMUNICATION DUE TO FIBER OPTIC LINE BREAK "At approximately 1100 EST on 1/10/06, the capability of the ENS and commercial telephones to communicate with offsite authorities was found to be not functioning. In addition, the capability of the ERDS system to communicate with the NRC is not functioning. Communications to offsite authorities have been verified using microwave communications (RERP phone lines). The cause of the problem has been determined to be an offsite cable break within the telecommunication provider's network. All onsite communications (including onsite telephones) are functioning properly. Offsite telecommunication company personnel are working to repair the broken cable. Currently, repairs are estimated to be complete by 1800 EST. The NRC Senior Resident Inspector has been notified. "This report is being made pursuant to 10CFR50.72(b)(3)(xiii), as an event that results in a major loss of offsite communications capabilities." * * * UPDATE FROM MIKE HIMEBAUCH TO JEFF ROTTON AT 1753 ON 01/10/06 * * * "This is a follow-up to NRC Event No. 42246: Offsite repairs of the broken telecommunications cable which caused a loss of capability to communicate with offsite authorities using ENS, commercial telephones and ERDS has been completed. Proper operation of ENS, commercial telephone lines and ERDS to communicate with offsite authorities has been verified. All offsite communication systems have been returned to normal." The licensee will notify the NRC Resident Inspector. Notified R3DO (O'Brien) * * * UPDATE PROVIDED FROM JEFF YEAGER TO JEFF ROTTON AT 2050 EST ON 01/10/06 * * * "At 1850 on 1/10/06, the capability of the ENS and commercial telephones to communicate with offsite authorities was again found to be not functioning. Discussion with telecommunication personnel indicate that troubleshooting and repair to the broken cable is continuing and will take approximately 4 hours. During this time, the communications with outside authorities will be intermittent. "Therefore, this report is being made pursuant to 10CFR50.72(b)(3)(xiii), as an event that results in a major loss of off-site communications capabilities." The licensee notified the NRC Resident Inspector, and state and local emergency response organizations. Notified R3DO (O'Brien) * * * UPDATE PROVIDED FROM JEFF YEAGER TO BILL HUFFMAN AT 0406 EST ON 01/11/06 * * * "Offsite repairs of the broken telecommunications cable which caused a loss of capability to communicate with offsite authorities using ENS, commercial telephones and ERDS has been completed. Proper operation of ENS, commercial telephone lines and ERDS to communicate with offsite authorities has been verified. All offsite communication systems have been returned to normal." State and Local governments notified. The NRC Resident Inspector will be notified. R3DO (O'Brien) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-10
42245 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2006-01-09 04:55 | 2006-01-09 17:09 | 2006-01-09 | LOSS OF CHARGING SYSTEM IMPACT ON SAFE SHUTDOWN CAPABILITY At 0455 EST, the control room received a Plant Process computer alarm for the 'C' Charging pump and entered TS 3.0.3. TS 3.0.3 was entered due to both ECCS trains becoming inoperable due to the loss of the charging subsystem safety function. The 'A' charging pump (backup) was started at 0458 and had sufficient flow for only several minutes. The control room then attempted to start the 'B' charging pump (standby) at 0459 with no success. At 0500 Charging and Letdown was secured and at 0501, operators identified a potential 'B' charging pump pulse dampener bladder failure and entered AOP 2568 for RCS leakage. The 'B' Charging pump suction and discharge were isolated at 0510 and at 0544 the 'C' charging pump was vented and restored to service. The licensee exited TS 3.0.3 at 0554 and entered TS 3.5.2 A since 'B' train of ECCS was restored to operability. The licensee suspects that the nitrogen from the bladder on the discharge of the pump leaked through the 'B' charging pump to the common charging pump suction header and caused gas intrusion to the running 'C" charging pump and to the common suction header for the standby charging pumps. TS 3.5.2 Bases does not credit the charging system for Design Basis Accident (DBA) mitigation, however the charging system is credited for two beyond DBA events - ATWS and Complete Loss of Secondary Heat Sink. At 1343 EST, the control room received a Charging low flow alarm with the 'C' charging pump in service. Charging and Letdown were secured and the licensee entered TS 3.0.3 at 1344. At 1459 the licensee completed the fill and vent of the 'C' charging pump and started the pump at 1514 and placed Charging and Letdown into service. The licensee is performing an engineering evaluation to keep the 'C' charging pump running and an Operability Determination must be completed prior to declaring the 'C' charging pump operable. The licensee continues to troubleshoot the 'A' charging pump to restore to operability. Once the 'C' charging pump is declared operable, the licensee will exit TS 3.0.3 The licensee notified the NRC Resident Inspector, and both state and local emergency response organizations. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2006-01-09
42244 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2006-01-05 16:15 | 2006-01-06 10:30 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * MONITOR SETPOINT IMPROPERLY SET "During a revision to a related Nuclear Criticality Safety Evaluation (NCSE), it was determined that the setpoint for the Building [DELETED] Condensate Tank in-line uranium concentration monitor was set at a non-conservative value. "Along with other controls, the in-line uranium concentration monitor for the Building [DELETED] Condensate Tank is relied on in two Nuclear Criticality Safety Evaluations which are associated with two different facility areas/operations: 1)The monitor is relied on to maintain mass control for the condensate tank in Building [DELETED]; and 2) the monitor is relied on to maintain concentration control for tanks in the Waste Water Treatment Facility (WWTF). "There were no actual or potential safety consequences to workers, the public, or the environment. "Upon discovery of the situation, transfer operations to the condensate tank were suspended. WWTF overcheck sample results were reviewed (for condensate solutions) which confirmed extremely low uranium concentrations. The condensate tank in-line monitor was re-set to the most conservative concentration value and the monitor was recalibrated and re-tested. A review was performed for all other in-line monitor set-points to verify that the set-points were appropriate; no problems were noted with the set-points for other in-line monitoring systems." The licensee notified the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
42243 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2006-01-05 09:30 | 2006-01-05 15:44 | 2006-01-05 | UNANALYZED CONDITION INVOLVING RCIC OPERATION DURING MCR EVACUATION "During an engineering assessment, a condition was found which does not meet the assumptions of the River Bend post-fire safe shutdown analysis. 10CFR50 Appendix R states that for alternate shutdown capability (i.e. shutdown from outside the main control room), reactor coolant system process variables shall be maintained within those predicted for a loss of normal AC power, and the fission product boundary integrity shall not be affected. Generic Letter (GL) 86-10, 'Implementation of Fire Protection Requirements,' states that the following assumptions are required for evaluation of a control room fire: 1) fire-induced spurious operation of safe shutdown components has occurred; 2) offsite power is lost; and, 3) the emergency diesel generators (DGs) do not automatically start. "Based on the conservative assumptions imposed by GL 86-10, the following control room fire scenario must be addressed. A fire is assumed to cause motor-operated valve E51-MOVF063, the inboard steam supply to Reactor Core Isolation Cooling (RCIC) turbine to close. The same fire requires the main control room (MCR) to be evacuated, and during relocation to the Division 1 Remote Shutdown panel, offsite power is lost. "The post-fire safe shutdown analysis has evaluated RCIC to be available from the Remote Shutdown Panel in order to maintain reactor water level, and that the Division 1 and 3 DGs are started locally. The Division 2 DG is not analyzed to remain free of damage caused by the MCR fire. Since valve E51-MOVF063 is powered from Division 2, and there is no Division 2 power available to re-open the valve, steam would not be available to power the RCIC turbine. E51-MOVF063 is located in the drywell, making manual operation of the valve impractical. Therefore, RCIC is postulated to not be available to maintain reactor level. Establishing reactor level control is a time-critical function that is required to occur within ten minutes of MCR evacuation in order to meet one of the Appendix R safe shutdown performance goals. "This condition involves compliance with 10CFR50, Appendix R. Plant equipment remains operable. The scope of this analysis deficiency is limited to the MCR fire scenario, with three concurrent failures. The MCR Is continuously manned. The affected cables in the MCR under-floor area are protected by fire detection and automatic suppression systems, which would rapidly detect and smother a fire. Introduction of ignition sources, such as work involving welding or grinding, is strictly controlled by station procedures. "While the assumptions of the post-fire safe shutdown analysis are not met for this scenario, it has been verified that the components required to properly align the Division 1 Residual Heat Removal system in the low pressure coolant injection mode would be available at the Division 1 Remote Shutdown Panel. Control of three safety-relief valves is also available at the Division 1 Remote Shutdown Panel to depressurize the reactor vessel for low pressure injection. An analysis is under way to determine the response of reactor water level, given these conditions." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-01-05
42242 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2006-01-04 13:45 | 2006-01-04 18:29 | 2006-02-16 | UNANALYZED CONDITION RELATED TO EMERGENCY DIESEL FUEL OIL TANK VORTEX FORMATION "At 1345, 1/4/06, Callaway Nuclear Plant completed a preliminary evaluation of the potential for vortex formation at the suction of the Emergency Diesel Generator fuel oil transfer pumps. This evaluation was performed in response to industry operating experience concerning an NRC finding identified during a utility inspection. The preliminary conclusion was that the existing Technical Specification level requirements for the Emergency Diesel Generator underground fuel oil storage tanks may be non-conservative and should be increased by an additional 489 gallons. This will result in a six day fuel oil volume requirement of 69,746 gallons and a seven day fuel oil volume requirement of 80,816 gallons. "A review of indicated fuel oil storage tank levels for the last three years was conducted and it was determined that there was sufficient fuel oil contained within the underground storage tanks to satisfy the new, higher volume requirements. In those instances where the volume would have been below the new requirements, this condition was already being tracked in the Callaway Plant Equipment Out of Service Log (EOSL) to satisfy associated Technical Specification requirements. "It was conservatively decided to institute administrative controls utilizing plant procedural controls and establish new, elevated fuel oil tank level limits which will ensure vortex formation can not occur. Once the evaluation results are finalized, a review of all actions taken to date will be performed to ensure all required actions have been identified and appropriate measures taken to ensure compliance." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY SHIFT MANAGER (BRADLEY) TO ROTTON AT 1539 ON 02/16/06 * * * "The evaluation discussed in the original notification has been completed. Administrative minimum limits for fuel oil level established to maintain compliance with the original Technical Specification Emergency Diesel Generator underground fuel oil volume requirements were in fact sufficient to ensure the prevention of vortex formation at the suction of the fuel oil transfer pumps. The fuel oil transfer subsystem remained capable of performing its safety function; therefore, there are no applicable reporting criteria under 50.72 or 50.73 and Event Notification 42242 is retracted. "The licensee notified the NRC Resident Inspector." Notified R4DO (Graves). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2006-01-04
42241 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2006-01-04 11:00 | 2006-01-04 15:15 | 2006-01-04 | PARTIAL LOSS OF EMERGENCY SIRENS "On 01/04/06, while performing the Emergency Siren Monthly Test it was determined that 14 out of 143 (9.7%) of the Emergency sirens had failed. A Notification is required because of the major loss of offsite response capability, i.e., the public prompt notification system. "Calculating the percentage of failures with a total count of 143 sirens results in an approximately 10% failure rate or a 'significant number of failures.' "This information was immediately discussed with Licensing and determined that a conservative decision is to make an 10 CFR 50.72(b)(3)(xiii) reportability notification. The State of Iowa, FEMA, and Benton and Linn Counties have also been notified. "Electricians were immediately dispatched to begin to troubleshoot and repair the 14 declared INOP sirens. "Compensatory actions have been taken." The licensee notified the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2006-01-04
42240 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2006-01-04 | 2006-01-04 15:17 | 2006-02-06 | AGREEMENT STATE - TEXAS LICENSEE EMPLOYEE OCCUPATIONAL OVEREXPOSURE The State provided the following information via email: "The [Texas] Department of State Health Services (DSHS), Radiation Control received written notification from [Name Deleted], Texas Regional RSO for IRISNDT, Inc. that one of its previous employee's received exposure in excess of 5 Rem annual dose. The RSO reports that while doing an update of radiation dose reports for all licensees' Texas employees, the Texas Regional RSO noted that a past employer exposure history was not recorded for a former employee (the radiographer) of the licensee. The RSO reviewed the personnel files for the individual and could not find a past exposure history from the record from the radiographer's previous employer. The Texas RSO contacted the Corporate RSO to see if he had a record for the individual. The Corporate RSO found an exposure history record and faxed it to the Texas RSO. The previous employer's record, H&G Inspection, [address deleted] reflected a dose of 3.918 Rem in the first 6.5 months of employment. The doses were compiled with IRISNDT's records and it was immediately noted that the radiographer had an accumulated dose in excess of 5 Rem. The Texas RSO called the former employee to notify him of the overexposure that same day of record discovery. The former employee stated that he thought the dose he had been assigned was not correct and that's why he did not inform the Texas RSO. It was determined through discussions with the radiographer that the radiographer has not worked since November 2005 and was informed that he cannot work in the industry until he talks to the DSHS. IRISNDT, Inc. stated they failed to check previous records and the radiographer failed to report [previous dose] to [IRISNDT]. In the future IRISNDT, Inc. will provide a form for potential employees to complete pre-hire for dose records to be reviewed and the safety program administrator has been assigned the responsibility to call 2 times per week to follow-up on previous employer dose histories for new hires." Texas Incident No: I-8287 * * * UPDATE FROM THE STATE OF TEXAS (E-MAIL) TO HUFFMAN AT 1200 ON 2/6/06 * * * The final Texas Department of State Health Services Radiation Branch report on this incident noted that the total annual expose received by the individual involved was 5.713 Rem. The exposure breakdown was 3.918 Rem for individual's previous employer and 1.795 Rem while the individual worked at IRISNDT. The R4DO (Nease) and NMSS (Morell) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2006-01-09
42239 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-12-31 | 2006-01-03 16:22 | 2006-01-03 | CALIFORNIA AGREEMENT STATE REPORT OF A STOLEN TROXER GAUGE The State provided the following information via facsimile: "The RSO for Twining Laboratories called to inform the State of California Radiologic Health Branch that a Troxler 3430, Serial # 32684, was stolen the evening of New Years Eve (12/31/05). The gauge was located in an employees garage in San Bernadino, CA. The gauge was chained in the bed of a pickup. The tab that locks the lid of the transport box was cut and the gauge, block, and charger were taken. The employee had worked half a day on Saturday and did not want to drive his vehicle all the way back to the company's Bakersfield office." The police have been notified of the theft. Although not stated in the report, Troxler gauges typically contain an 8 millicurie Cesium-137 source and a 40 millicurie Americium-241/Beryllium source. State Report: 010306 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2006-01-06
42238 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2006-01-02 04:38 | 2006-01-02 17:58 | 2006-01-18 | REPORT OF SAFETY EQUIPMENT FAILURE "At 0453 CST on 01/02/2006, the Plant Shift Superintendent (PSS) was notified that steam was observed leaking from the C-337A Position 1 West Autoclave. A 14 ton cylinder containing 0.711 % U235 assay uranium hexafluoride had been heating (TSR [Technical Safety Requirement] Mode 5) for approximately 5 minutes when the leak was observed. The autoclave pressure containment boundary is a TSR system required to be operable per TSR 2.2.3.1, 'Autoclave High Pressure Isolation System (HPIS),' when the autoclave is in Mode 5. The autoclave was placed in Mode 2, 'Autoclave Out-of-Service' in accordance with LCO Required Actions 2.2.3.1.C. "This event is reportable as a 24 hour event in accordance with 10CFR 76.120(c)(2)(i). This is an event in which equipment is disabled or fails to function as designed when: a.) the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b.) the equipment is required by a TSR to be available and operable and either should have been operating or should have operated on demand, and c.) no redundant equipment is available and operable to perform the required safety function." The licensee noted that after steam was turned off to the autoclave, an inspection of the o-ring sealing surfaces did not identify any problems. No other sources of a steam leak could be found in the autoclave. The HPSI was declared inoperable due to a possible head-to-shell leak. The licensee will need to wait for a five day cool down time for the cylinder in the autoclave before it can be removed. Once the cylinder is removed, the autoclave can be re-pressurized in an attempt to determine the leak location. The NRC Senior Resident Inspector and DOE have been notified of this event. * * * UPDATE AT 15:03 EST ON 01/18/06 FROM SKAGGS TO KNOKE * * * "This notification is being retracted." "On January 11, 2006, the 1 west autoclave was subjected to an autoclave pressure decay test. The autoclave passed the test on both the inner and outer containment valves. This proved that the steam leak reported by operators was not from a breach of the autoclave containment boundary, and that the AHPIS was performing as designed during the heat cycle initiated on January 2, 2006. Following the pressure decay test, steam was valved into the autoclave in an effort to find the steam leak. Steam vapor was seen under the autoclave at the location reported by operators on January 2, 2006. The steam vapor was discovered to be coming from a condensate blow-down hose that had moved away from the condensate drain housing allowing steam vapor to escape. No other leaks were noted. "The successful autoclave pressure decay test provides evidence that the AHPIS was operable and available while the autoclave was in TSR Mode 5 on January 2, 2006, and thus the reporting criteria was not met. "The NRC Senior Resident Inspector for PGDP has been notified of this retraction." Notified R2DO (Ogle) and NMSS Daytime EO (Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2006-01-02
42237 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2005-12-31 14:12 | 2005-12-31 19:16 | 2006-01-06 | AUTOMATIC ACTUATION OF THE EMERGENCY FEEDWATER (EFW) DUE TO A TRANSIENT ON THE "B" MAIN FEEDWATER (MFW) PUMP "The EFW actuation occurred when the 'B' MFW pump RPM rose then dropped to ~4000 rpm. The MFW pump then recovered immediately. This transient caused EFIC [Emergency Feedwater Initiation Control] to actuate and both EFW pumps received start signals on invalid low SG level from the EFIC low range level instruments. These instruments measure level based upon a dp [differential pressure] across an orifice and are not considered reliable at 95% power and full MFW flow. All other SG level instruments indicate SG level was above EFIC setpoint during the MFW pump transient. This can be concluded by reviewing the OTSG [Once Through Steam Generator] level prior to and during the transient. Prior to the transient the EFIC low range level instruments indicated a level of ~24 inches. During the transient the EFIC low range level instruments indicated as low as 4 inches. However, the Startup Range level only lowered from ~122 inches prior to the transient to ~120 inches. "Both EFW pumps were immediately overridden and stopped once it was verified this was not an actual under feed condition to the OTSGs. No EFW injection into the OTSGs occurred due to the EFW actuation." There was no ongoing maintenance at the time which would have explained the "B" MFW pump transient. The licensee informed the NRC Resident Inspector. * * * UPDATE EVENT FROM FRED VAN BUSKIRK TO JOE O'HARA ON 1/5/06 AT 0942 * * * "On 12/31/05, an 8-hour notification (EN# 42237) was made by Arkansas Nuclear One reporting an automatic actuation of Emergency Feedwater (EFW). The report was submitted pursuant to the requirements of 10 CFR 50.72 (b)(3)(iv)(A) Valid System Actuation. The actuation of EFW occurred as a result of a "B" Main Feedwater (MFW) pump transient which caused an invalid low Steam Generator (SG) level signal from the Emergency Feedwater Initiation and Control (EFIC) instrumentation. As discussed in the original event report, the low SG level EFIC instruments do not provide valid indication at 95% power and full MFW flow. As a result of the elevated flow rate during this perturbation, an invalid indication below the low SG level setpoint was produced resulting in the system actuation. All other SG level instrumentation indicated that actual SG levels remained within the normal operating band, confirming that no low level condition existed and that this event represented an invalid actuation. Accordingly, this update revises Event Notification 42237 to be submitted pursuant to 10 CFR 50.73 (a)(2)(iv)(A) and the 60-day Optional 10 CFR 50.73 (a)(1) requirement - Invalid Actuation of EFW. EFID and EFW systems functioned as designed in response to the invalid low SG level signal. "The original event report stated that there was no EFW injection into the steam generators as a result of the actuation; however, subsequent reviews of historical Safety Parameter Display System (SPDS) data indicated that the electric EFW pump (P-7B) fed the steam generators for approximately 5 seconds during the event." The licensee notified the NRC Resident Inspector. R4DO (Shannon) notified. | 94 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-12-31
42236 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-12-29 11:45 | 2005-12-29 12:26 | 2005-12-29 | AGREEMENT STATE REPORT - TRANSPORTATION ACCIDENT INVOLVING USED TECHNETIUM 99M SYRINGES The Commonwealth of Massachusetts reported that there was a transportation accident on route 9 in Westborough, Massachusetts involving an overturned delivery truck returning used Technetium 99m medical diagnostic dose syringes. State police responded and closed the roadway. A hazardous materials team responded. A Commonwealth of Massachusetts Health Physicist also responded to the scene. Seven type A "ammo box" containers contained the used syringes. At least one of the boxes broke open. The doses were supplied by Cardinal Health of Woburn, Massachusetts. Originally it was estimated that 56 millicuries of Tc-99m was involved. In an update to the original report, the Massachusetts official determined through interviewing the driver of the vehicle, that the dose syringes were used. The responders took surveys of the area and detected no readings above normal background radiation levels. Local television news media responded to the scene. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2006-01-03
42235 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2005-11-02 19:01 | 2005-12-28 13:45 | 2005-12-28 | INADVERTENT CONTAINMENT ISOLATION SIGNAL AFFECTING CONTAINMENT ISOLATION VALVES "This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A) to provide the NRC with information pertaining to an invalid Primary Containment Isolation System (PCIS) Group 3 actuation signal that affected containment isolation valves in more than one system. "On 11/02/05 with the reactor shutdown for a refueling outage, an invalid PCIS Group 3 actuation occurred while cycling a breaker during a tagging clearance activity. The invalid actuation occurred when the circuit was de-energized. This is an expected result of opening the breaker. "The PCIS functioned successfully providing a complete Group 3 isolation. "The train actuation was complete. Both trains of the Standby Gas Treatment System started as designed. The PCIS Group 3 isolation involves valves in the following systems: Drywell Air Purge and Vent Drywell and Suppression Chamber Main Exhaust Suppression Chamber Purge and Vent Containment Air Compressor Suction Valve Exhaust to Standby Gas Treatment Containment Purge Supply and Makeup Containment Air Sampling Air Dilution Subsystem Valves Vent Subsystem Valves Containment Air Dilution Vent System" The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-12-28
42234 | -1 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-28 11:14 | 2005-12-28 13:07 | 2005-12-29 | PART 73.71 REPORT INVOLVING DEGRADED MONITORING OF PROTECTED AREA ACCESS Safeguards system degradation related to monitoring and detection of PA boundary. Compensatory measures taken. Call the Headquarters Operations Officer for details. The licensee will inform the NRC Resident Inspector. * * * AT 1236 EST ON 12/29/05 RECEIVED UPDATE FROM KEN SIMKULET TO JOE O'HARA * * * Upon further review the licensee has retracted the event notification after determining that no degradation occurred. Call the Headquarters Operations Officer for details. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 73.71(b)(1) |  |  |  | 1 | 2005-12-28
42233 | 0 | ROSEMOUNT NUCLEAR INSTRUMENTS |  |  |  |  | 2005-12-27 | 2005-12-27 18:14 | 2005-12-28 | PART 21 NOTIFICATION FOR ROSEMOUNT TRANSMITTERS The Supplier provided this notification via facsimile and is summarized below: A multi-meter used in the calibration of certain pressure instruments went out of calibration between 10/10/2005 and 11/18/2005. These instruments may not conform to the published accuracy specification of +/- 0.25% of calibrated span. Rosemont Nuclear Instruments, Inc (RNII) successfully recalibrated all affected transmitters that had not yet shipped from its facility. The instruments affected by this failure are: "(a) certain Model 1152 gage and differential pressure transmitters with model codes beginning with 1152GP, 1152DP, or 1152HP, inclusive of pressure measuring range codes 3, 4, 5, and 6 (the range code is the 7th position in the model string); and "(b) certain Model 1153 Series B and 1153 Series D gage and differential pressure transmitters with model codes beginning with 1153GB, 1153DB, 1153HB, 1153GD, 1153DD, or 1153HD inclusive of pressure measuring range codes 3, 4, 5, and 6 (the range code is the 7th position in the model string); and "(c) certain Model 1154 and 1154 Series H gage and differential pressure transmitters with model codes beginning with 1154GP, 1154DP, 1154HP, 1154DH, or 1154HH inclusive of pressure measuring range codes 4, 5, and 6 (the range code is the 7th position in the model string). "The end user must determine the impact of this potential non-conformance on its plant operations and safety and take action as deemed necessary. If an affected pressure transmitter has been successfully calibrated after receipt from RNII or will be calibrated prior to installation, no further action should be required." * * * UPDATE FROM ROSEMOUNT NUCLEAR INSTRUMENTS (D. ROBERTS) TO M. RIPLEY AT 0927 ET 12/28/05 * * * Rosemount provided the following information via facsimile: "Yesterday, Rosemount Nuclear Instruments, Inc. (RNII) submitted a notification under 10 CFR Part 21. The submission to the NRC did not include Attachment A, which lists all of the affected U.S. licensees. This fax includes the letter and the attachment. RNII has initiated communication with its customers. The notification letter and attachment A have been sent to each of the affected customers." Attachment A provides Purchase Order Numbers, Model Numbers, Serial Numbers, and Calibration Dates for instruments provided to the following affected licensees: Dominion Generation, First Energy Corporation, Progress Energy Carolinas, Georgia Power Co., and Southern Nuclear Operating Co. Notified R1 DO (M. Sykes), R2 DO (M. Lesser), R3 DO (D. Hills), R4 DO (J. Clark), NRR (C. Holden and O. Tabatabai) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MN | OTH | PAR | 21.21 |  |  |  | 0 | 2005-12-27
42232 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2005-12-27 07:30 | 2005-12-27 14:59 | 2005-12-27 | TECHNICAL SUPPORT CENTER VENTILATION INOPERABLE "During an equipment operator rounds of the onsite Emergency Response Technical Support Center the access cover for the suction plenum of VA-107, Technical Support Center Air Handling Unit, was found removed and resting on the floor under the opening exposing a 2 ft X 2 ft opening. The as-found condition would have made the Technical Support Center ventilation System inoperable with respect to maintaining Technical Support Center personnel dose limits in a design basis accident. The air handling unit is located in a mechanical room outside the Technical Support Center envelope. With the access cover removed, air from the mechanical room would be drawn into the air handling unit and discharged into the Technical Support Center, in a design basis accident, the as-found condition would allow an undesirable amount of unfiltered air into the Technical Support Center envelope. This condition does not adversely affect the charcoal filtering unit, VA-119, from drawing outside air required to maintain the Technical Support Center in a positive pressure envelope. The cause of the access cover being removed could not be determined, the access cover was re-installed at 08:15 CST and a maintenance work document generated to verify proper operation of latches. This report is being made under 10 CFR 50.72(b)(3)(xiii) since the as-found condition impaired the licensee's ability to staff the Technical Support Center during an accident. Contingency actions are in place in the Emergency Plan to deal with the evacuation of the Technical Support Center." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-12-27
42231 | -1 | AMERICAN TECHNICAL SERVICES |  |  |  |  | 2005-12-08 | 2005-12-27 13:13 | 2005-12-30 | LOST TROXLER MOISTURE DENSITY GAUGE American Technical Services (Sioux Falls, SD) sent a Troxler Moisture Density Gauge to QALTEK (Idaho Falls, ID) for repairs. The gauge was picked up by DHL Express at 14:15 CST on 12/08/2005 and has not arrived at its destination. DHL is searching for the gauge. Troxler Model 3400 Serial Number 25721 Cs-137 source #47-22091, 0.3 GBq [8 millicuries] Am-241:Be source 1.48 GBq [40 millicuries] * * * UPDATE FROM M. HUDSON TO P. SNYDER AT 1444 ON 12/30/05 * * * The licensee is retracting this report based on the following: The shipping company temporarily lost track of the item and found it in their system. The gauge was delivered with no evidence of tampering on 12/30/05 at 1130 CST. Notified R4DO (Clark), NMSS EO (Ruland), TAS (Whitney). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | SD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-12-27
42229 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2005-12-26 10:47 | 2005-12-26 15:35 | 2005-12-26 | AUTOMATIC REACTOR TRIP FOLLOWING TURBINE TRIP " A reactor trip occurred due to a Reactor Protective System (RPS) actuation from probable Main Turbine problems. The Emergency Feedwater Initiation and Control System (EFIC) actuated on the 'A' Steam Generator only due to a momentary level spike post trip. The RPS and EFIC performed as designed. Unit 1 will remain in mode 3 for troubleshooting efforts. No significant equipment issues observed. This report is being made in compliance with the 4 hour and 8 hour non-emergency notifications required by 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A), respectively." The licensee notified the NRC Resident Inspector and State authorities. All rods fully inserted. The trip was characterized as uncomplicated and all systems functioned as required. Electrical conditions are stable. The reactor is currently at no load temperature and pressure with decay heat being removed via the turbine bypass valves and cooling to the steam generators from the non-safety related auxiliary feedwater system. The trip had no impact on Unit 2. The licensee was in no significant LCO at the time of the trip. The licensee noted that one of the main steam code safeties did stick open for a short period of time but closed after secondary pressure was reduced without any overcooling. The cause of the turbine trip is under investigation. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-12-26
42228 | -1 | ROBINSON | 2 |  |  | [2] W-3-LP | 2005-12-26 12:00 | 2005-12-26 12:58 | 2006-01-11 | SAFEGUARDS REPORT The licensee reported a vulnerability in a safeguards system for the protected area for which compensatory measures had not been implemented prior to discovery of the condition. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE 1235 EST ON 01/11/06 FROM CHUCK BAUCOM TO S. SANDIN * * * After completing an investigation the licensee determined that the condition previously reported did not constitute a vulnerability and is, therefore, retracting this report. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. Notified R2DO (Joel Munday), R2IAT (Brian Bonser via email) and TAS (Matt Hahn via email). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 1 | 2005-12-26
42227 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-12-26 08:30 | 2005-12-26 11:33 | 2005-12-27 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE Licensee reported that a model 3440 Troxler moisture density gauge containing 8 millicuries of Cs-137 and 40 millicuries of Am/Be-241 was stolen from a trailer located next to a highway construction site in Lakeland, FL. The gauge was located in the locked trailer, and the gauge was locked in the transportation case with the source in the stored position. The site was surrounded by a chain link fence and the trailer was pried open. Also stolen were vehicles and equipment. Lakeland Police have been notified. The licensee noticed the theft at 0830 12/26/2005. A reward will be offered. Troxler Serial Number 33567 Cs-137 Source #750-9252 Am/Be-241 Source #47-15619 Lakeland Police Report Number 2005-100863 * * * UPDATE PROVIDED BY STATE TO JEFF ROTTON AT 1035 EST ON 12/27/05 * * * The State provided the following information via email: "Licensee reported that their worksite had been vandalized on December 25. Many items plus a contractor's vehicle were stolen. Incident was reported to this office [Florida Bureau of Radiation Control] on 1130 December 26. On December 27, licensee reported that police had discovered the stolen vehicle with the gauge at Providence & Griffin road, less than two miles from the worksite. Gauge was still locked in case and that there was no damage to case/gauge. The licensee has taken possession of the gauge and will perform a leak test. Florida continues it's investigation. FL Incident Number: FL05-183 Notified R1DO (Sykes) and NMSS EO (Holahan), and TAS (Whitney via E-mail) THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-12-29
42226 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-12-22 14:00 | 2005-12-23 13:30 | 2006-02-07 | SAFETY EQUIPMENT FAILURE "While performing semi-annual criticality accident alarm system (CAAS) testing, one unit in a pair of detectors failed to initiate the site wide alarm. Spare unit was immediately installed and all systems successfully tested. Production facility covered by this CAAS [was] in a shutdown status at the time of testing. Subsequent troubleshooting indicated a faulty electronic relay contact in the failed unit. "Testing of CAAS is conducted on a semi-annual basis in accordance with procedure, NFS-HS-A-80, Sections 5.5 & 5.6. [The] Detector pair on 2nd floor of Oxide Conversion Facility did not activate site-wide alarm as expected. Alarm indication did occur as expected at the local read-out panel, and at the central alarm panel located in an adjacent building occupied by security guards. Investigation revealed failed relay contact in Eberline Instruments Model RMS-3 read-out meter. [The] Unit [was] replaced, and [a] subsequent test [was] satisfactory. "No actual safety consequences occurred as a result of this event; however, there was a risk of potential health and safety consequence to the occupational workforce, involving significant radiation exposure from accidental criticality event with no warning to initiate prompt site-wide evacuation." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM MICHAEL TESTER TO HUFFMAN AT 1626 EST ON 2/06/06 * * * Following evaluation of this event by the licensee's Part 21 review committee, Nuclear Fuel Services has reached the conclusion that this event was the result of a design defect in the relay used in the RMS-3 read-out meter. This event is being updated to reflect the Part 21 reportability conclusion. The Eberline RMS-3 read-out meter is manufactured by Thermo Electron Corporation. Nuclear Fuel Services has been in contact with Eberline during its investigation and Eberline is aware of the conclusions. The defective relay is manufactured by Potter and Brumsfield. Immediate corrective actions included replacement of the defective equipment, and re-testing to ensure operability; long term corrective action includes design and installation of PLC based surveillance equipment to continuously monitor the function of system components by NFS Engineering Department in approximately 3 - 6 months. The licensee notified the NRC Resident Inspector. The R2DO (Bernhard), NMSS EO ( Janosko) and Part 21 coordinator (Markley) have been notified. * * *UPDATE BY HUFFMAN ON 2/7/06 * * * This event has been decontrolled to make it publicly available and permit information about this problem to be shared with all affected parties. NRC management has determined that the report does not contain information about sensitive operations at the NFS site. R2DO(Bernhard) and NMSS (Morell) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | UNSPECIFIED PARAGRAPH | [8 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) | 21.21 |  |  | 0 | 2006-02-07
42225 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-12-23 | 2005-12-23 10:31 | 2005-12-23 | AGREEMENT STATE - LOSS OF TRITIUM SIGNS "In 2004 the Port Washington Power Plant (PWPP) was demolished in preparation for the construction of a new gas-fired plant. Before demolishing began, 56 exit signs containing Tritium (H-3) were taken down, boxed up and planned for return to Isolite through a contractor. The signs were accounted for in December of 2004 but during the 4th quarter of 2005 WE Energies identified that there was no accounting for the signs disposal. An investigation began and WE Energies spoke with their contractors and sub-contractors. No paperwork was found for the disposal and it appears they were sent to a landfill with the general trash. "Due to the length of time since disposal, the signs are assumed to be in the landfill buried under general trash. No search of the landfill will be conducted. "WE Energies has taken four steps to identify and properly manage their exit signs. They are: 1. Conduct a full inventory for exit signs at all WE Energies sites. 2. Develop a procedure for the use, control, handling and disposal or their exit signs. 3. Begin replacing their exist signs containing H-3 with signs not containing H-3. 4. Implement a training program for management on the proper use and control of their exit signs. "WI DHFS is meeting with WE Energies in January to discuss this incident." Additional information on the signs is not available at this time. This information will be discussed at the January 2006 meeting. The State of Wisconsin estimates that the signs contained 20-30 Curies each. This equates to a total activity of (56x30) 1680 Curies of tritium. Wisconsin Event Report ID: 32 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-12-28
42224 | -1 | FERMI | 2 |  |  | [2] GE-4 | 2005-12-22 22:25 | 2005-12-23 02:22 | 2006-01-05 | EECW TEMPERATURE CONTROL VALVE NOT FULLY OPEN "While performing Div. 1 & 2 Emergency Equipment Cooling Water (EECW)/Emergency Equipment Service Water (EESW) Valve Lineup Verification surveillance on 12/22/05, the temperature control valve (TCV) on both divisions of EECW were found to be approximately 95% open rather than their required full open position. The system design requires that the TCV, or the associated TCV bypass valve, be in the full open position during system startup to avoid a potentially damaging pressure transient from occurring. Both divisions of EECW and all supported systems (including HPCl, both divisions Core Spray, and both divisions of RHR) were declared INOPERABLE at 2225 EST. Multiple LCO Required Actions were entered, including entry into LCO 3.0.3. At 2250 EST, Div. 1 EECW was restored to OPERABLE status by fully opening the TCV bypass valve and isolating the TCV, and LCO 3.0.3 was exited. At 2252 EST, Div. 2 EECW was restored to OPERABLE status by fully opening the TCV bypass valve and isolating the TCV, and all associated LCO Required Actions were exited. Reactor power remained at 100% throughout the event. The NRC resident inspector has been notified. This report is being made pursuant to 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition and 10CFR50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident." The licensee is investigating the cause of the valve not being fully open. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY YEAGER TO ROTTON AT 1524 ON 01/05/06 * * * "This is a retraction of NRC Event #42224. Based on further engineering review, it is concluded that no potential damage from a pressure transient would occur as a result of the TCV being approximately 95% open. System startup pressure transient concerns reflected in the operating procedures originated from a previously-experienced pressure transient resulting from void collapse against a closed TCV. System startup with the as-found TCV position still provides a sufficiently-open flow path to preclude void collapse against a closed boundary. Additionally, Engineering has determined that system operation with a 90% open TCV would have no significant impact on total system flow and the cooling function. Therefore, both divisions of EECW and all other supported systems (including HPCI, both divisions of Core Spray, and both divisions of RHR) were operable with the TCV in the approximately 95% open position." The licensee notified the NRC Resident Inspector. Notified R3DO (Ring). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2005-12-23
42223 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2005-12-22 06:30 | 2005-12-22 17:38 | 2005-12-22 | AGREEMENT STATE REPORT OF TRAFFIC ACCIDENT INVOLVING RADIOACTIVE MATERIAL A truck carrying 600 millicuries of Technetium-99m (150 ml in two containers) was involved in a traffic accident in Lawrence, Kansas. The containers were undamaged by the accident and a survey of the containers and truck determined that there was no leakage or radioactive contamination. The Technetium has been secured and taken into possession by representatives of Cardinal Health. Kansas Report # 7831227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2005-12-27
42222 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2005-12-22 06:25 | 2005-12-22 15:03 | 2005-12-22 | FITNESS FOR DUTY A licensed supervisor had a confirmed positive for alcohol during a "for cause" fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 26.73 |  |  |  | 0 | 2005-12-22
42221 | 0 | McDOWELL AND ASSOCIATES |  |  |  |  | 2005-12-21 | 2005-12-22 14:10 | 2005-12-22 | STOLEN TROXLER MOISTURE DENSITY GAUGE A licensee's employee had his 1988 Cadillac Brougham stolen while it was parked in front of his house in Westland, MI and a Troxler moisture density gauge was inside the vehicle (Model 3440, S/N 13815, containing 8 millicuries of Cs-137 and 40 millicuries of Am-241:Be). The gauge was locked in its wired down casing. The vehicle was stolen sometime between 1900 and 0400 hours on 12/21/05 and 12/22/05 respectively. The licensee contacted NRC Region III, the Westland Police (report No.0542989) and the State Police who subsequently contacted the State Homeland Security. * * * UPDATE AT 1705 ON 12/22/05 FROM J. KALISZ TO A. COSTA * * * The licensee reported that the automobile was taken away at the owner's location by a car repossession company. The gauge and its case were intact inside the car and have been recovered by the licensee. Notified R3 DO (Peterson), NMSS EO (Camper) and TAS (email). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-12-22
42220 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-12-22 05:50 | 2005-12-22 12:08 | 2005-12-22 | VALID ACTUATION SIGNAL DUE TO HIGH STEAM GENERATOR WATER LEVEL "While performing a plant shutdown due to a packing leak on #24 Feedwater Regulating Valve [see event #42217] on December 22, 2005 at 0550 hours, Indian Point Unit 2 received a 22 Steam Generator Water High-High Level signal at 73% narrow range level. This resulted in tripping the standby 21 Main Boiler Feed Pump which then resulted in a start signal being sent to both motor driven Auxiliary Feedwater Pumps. Both of the motor driven Auxiliary Feedwater Pumps were already operating and feeding the steam generators when this start signal was received. Operators restored 22 Steam Generator Level to normal. All systems responded properly." The licensee will notify the NRC Resident Inspector. | 5 | 0 | 0 | 5 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-12-22
42219 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2005-12-22 09:03 | 2005-12-22 10:20 | 2006-02-16 | HPCI DECLARED INOPERABLE "The HPCI flow control current loop was found degraded in such a manner that HPCI would not perform its intended function. HPCI was declared inoperable per TS 3.5.E.2 (14 day LCO). Repair efforts have been initiated." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM M. RAMSEY TO M. RIPLEY AT 1601 ET ON 02/16/06 * * * "On 12/22/05, the HPCI System flow indicator 'spiked' a number of times with the system in its normal standby line-up. Control Room Operators declared the HPCI system inoperable and entered a 14 day LCO per TS 3.5.E.2, to troubleshoot and repair the system as appropriate. "The safety function of HPCI system is to provide and maintain an adequate coolant inventory inside the reactor vessel to prevent fuel clad conditions from exceeding 10CFR50.46 criteria as a result of postulated small breaks in the Nuclear System process barrier. To ensure that this safety function is met, the HPCI System must be able to deliver a minimum actual flow rate of 3570 gallons per minute (gpm) to the reactor vessel. The actual flow rate was reduced below the Technical Specification value of 4250 gpm to account for potential flow instrument string inaccuracies. The delivery of 3570 gpm of actual flow demonstrates that sufficient margin to safety function is maintained during accident conditions. In automatic operation, the HPCI flow controller uses the flow signal to maintain a flow rate of 4250 gpm and is designed to automatically adjust developed flow rate in response to changes in flow signals. "System operation is tested quarterly by monitoring flow to ensure that the HPCI system can perform its safety functions. The Technical Specification surveillance requirement states that the HPCI system shall deliver at least 4250 gpm at normal reactor operating pressure when recirculating to the Condensate Storage Tank. "The event investigation revealed that the cause of the flow spikes was a malfunctioning electrical component in the power supply module within the flow controller. Power to the flow transmitter is supplied by this module. The power supply would malfunction for a few seconds and then would return to normal operation, thereby resulting in step changes in the HPCI flow signal. It is conservative to assume the actual HPCI flow rate would have been reduced by the full amount of the flow rate, for the entire duration of the flow signal. Additional conservatism also exists because the HPCI system flow is unlikely to have been able to respond to the full value of a short duration flow spike. "When calculating the average HPCI flow rate, the impact of the flow spikes decreases as a longer period is evaluated because the duration of all of the flow spikes added together is very short and comparably longer periods of stable performance exist between the individual spikes. Therefore, it is conservative to evaluate the shortest period of time that HPCI is required to perform its safety functions that is stated in the Design Bases Document as 1000 seconds. With HPCI operable, the worst case period occurred just prior to it being declared 'Inoperable'. HPCI was calculated to have developed an actual flow rate of greater than 4191 gpm during the worst case 1,000 second period. "The calculation for 'HPCI Flow Control & Indication Loop Accuracy' provides total loop accuracy of plus or minus 216.2 gpm at 4250 gpm for Design Bases Accident conditions. A calculated flow rate of 4191 gpm, minus the flow instrument loop uncertainty of 216 gpm yields a worst case actual flow rate of 3975 gpm. A flow rate of 3975 gpm is greater than the 3570 gpm assumed in event calculations. "The subject flow controller power supply module was removed and bench tested to demonstrate that sufficient operating margin existed to provide reasonable assurance that the power supply would not have failed if called upon to mitigate a design bases accident with sufficient margin. The testing simulated HPCI operation at 4250 gpm for more than 24 hours. No flow spikes were recorded during this period. Based upon these test results and the analysis provided above, if the subject power supply component had remained in service and HPCI operation was required, the system would have performed its required safety function for a duration exceeding any analyzed event. "ENS Event Number 42219, completed on 12/22/05, is being retracted." The licensee notified the NRC Resident Inspector. Notified R1 DO (J. Trapp) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-12-22
42218 | 0 | PHYSICS ASSOCIATES |  |  |  |  | 2005-12-01 | 2005-12-22 10:04 | 2005-12-22 | IMPROPER DISPOSAL OF I-131 CAPSULES On 12/01/2005, a technician at Southside Community Hospital in Farmville, VA disposed of six vials that had contained I-131. At least one patient had not received therapy that day and the vials contained at least two capsules of Iodine. On 12/08/2005, Stericycle Disposal in Baltimore, MD informed the hospital of radioactive material in two of their sharps disposal boxes. On 12/13/2005, RSO Inc. measured the radiation level on the sharps boxes of 50 mR/hr and 60 mR/hr. On 12/19/2005, RSO Inc. delivered the sharps boxes back to the hospital and the sharps radiation level was 10 mR/r and 15 mR/hr. On 12/21/2005 the vials were retrieved from the sharps boxes and the total activity was 479 microCuries. An estimate of the dose received by the drivers was performed assuming the packages were one meter from the driver. The total dose received on 12/01/2005 was less than eight milliRem. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-12-22
42217 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-12-22 02:08 | 2005-12-22 03:20 | 2005-12-22 | AFW START DURING MAIN FEEDWATER PUMP TRIP "While performing a plant shutdown due to a packing leak on #24 Feedwater Regulating Valve on 12/22/05 at 0208 at about 67% power, #22 MBFP tripped while swapping lube oil coolers. #21 and #23 motor driven auxiliary feedwater pumps auto started. All systems responded properly. Entered appropriate abnormal operating procedure (2-AOP-FW-1, Loss of Main Feedwater). Reduced power to within the capacity of one MBFP and established conditions to shutdown and realign #21 and #23 ABFPs to Auto. On 12/22/05 at 0218, #21 and #23 ABFPs were shutdown and aligned for automatic operation." The licensee notified the NRC Resident Inspector. | 58 | 0 | 0 | 67 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-12-22
42216 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-12-06 23:00 | 2005-12-21 16:27 | 2005-12-21 | INVALID SPECIFIED SYSTEM ACTUATION - "A" AUXILIARY FEEDWATER "This report is being made in lieu of an LER per the guidance of 10CFR50.73(a)(2)(iv)(A). The `A' train Motor Driven Auxiliary Feedwater pump received an invalid auto-start signal due to a failed safeguards driver board in the A train Solid State Protection System (SSPS). This was a complete actuation of the 'A' train of auxiliary feedwater, and all components functioned as designed. The pump was manually secured and no other systems were affected. The plant entered an 8 hour LCO for an inoperable train of SSPS. The safeguards driver board was replaced and the plant exited the LCO. Investigation of the cause of the card failure is in progress." The licensee notified the NRC Resident Inspector. | 0 | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-12-21
42215 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-11-15 08:05 | 2005-12-21 14:01 | 2005-12-21 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of general containment isolation signals affecting more than one system. "On November 15, 2005, while operating at 100% thermal power, at 08:05 hours CST, Browns Ferry Unit 2 incurred an inadvertent, invalid actuation of the PCIS Group 6 logic. One reactor zone ventilation exhaust radiation monitor (the B channel) was indicating downscale due to a pre-existing maintenance issue, and, during activities to formally place the channel in a tripped status in accordance with the applicable Technical Specifications, the PCIS logic fuse for the opposite (A channel) radiation monitor was inadvertently removed rather than the fuse for the B channel. The PCIS logic responded as designed to the condition of both radiation monitors being downscale, and a Group 6 logic actuation resulted. The actuation was invalid because it resulted from an error related to an equipment tagging activity; there were no actual plant conditions which required the associated equipment actuations/isolations to occur. "The following equipment actuations/isolations occurred: Unit 2 Group 6 * Initiation of the Standby Gas Treatment System * Initiation of Control Room Emergency Ventilation * Isolation of the following equipment: * reactor zone and refuel zone normal ventilation systems * drywell-torus differential pressure compressor * drywell-torus Hydrogen/Oxygen analyzers * drywell radiation continuous air particulate monitor "All equipment responded in accordance with the plant design. There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for resolution." The NRC senior resident inspector has been notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-12-21
42214 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-12-19 12:00 | 2005-12-21 12:06 | 2006-02-08 | OHIO AGREEMENT STATE REPORT: DAMAGED TROXLER MOISTURE DENSITY GAUGE "ODH was notified on 12/19/05 by the licensee that a Troxler moisture density gauge received extensive damage when it was run over by a construction vehicle at a job site. The gauge was a Troxler Model 3430, serial number 31068, containing 8 mCi (millicuries) of Cs-137 and 40 mCi (millicuries) of Am-241. Preliminary notification by the licensee is that the gauge was left unattended but is still in sight of the operator, who had gone back to their truck to verify information for the next analysis. While the operator was away from the gauge, the construction vehicle approached the location and ran over the gauge. The gauge user was unable to get back to the gauge and wave away the truck driver before the gauge was run over. The gauge casing was destroyed but initial surveys performed on site indicate that the sources remained intact. The gauge was packed into the transport case and transported to a gauge service provider for leak testing and packaging for return to the manufacturer. An investigation is being conducted by ODH." ITEM NUMBER: OH050010 * * * UPDATE FROM S. JAMES TO W. GOTT AT 1633 ON 02/08/06 * * * The State provided the following information via email: "Device was found to not be leaking and was returned to the manufacturer." Notified R3DO (Lanksbury) and NMSS (Camper). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-12-26
42213 | 0 | BEAVER VALLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-12-20 21:15 | 2005-12-20 23:34 | 2005-12-20 | MINOR CHEMICAL SPILL "Notified the Pennsylvania Department of Environmental Protection ( PA DEP) at 2115 of an onsite chemical leak, some of which ended up being discharged to the environment (Ohio River). A small hydrazine spill onsite was directed to the onsite chemical waste sump. The chemical waste sump was at that time being reprocessed to the water treating clarifier. The clarifier effluent is directed to filters and eventually to the onsite reverse osmosis unit and demineralizer train. The waste effluent of the reverse osmosis unit is directed to the clarifier settling basin, which in turn is routed directly to the Ohio river. The chemical analysis of the clarifier settling basin indicated 132 ppb hydrazine. "The information reported to the PA DEP essentially stated that BVPS had a minor onsite chemical spill that is not EPA reportable. However, since hydrazine was detected in outfall 103 (The clarifier settling basin) under the requirements of the National Pollutant Discharge Elimination System (NPDES) permit we are required to report this to the PA DEP. We do not expect harm to the environment. No offsite emergency response is required." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-12-20
42212 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-20 17:12 | 2005-12-20 18:13 | 2005-12-20 | OFFSITE NOTIFICATION - PRESS RELEASE "This notification is being made in accordance with 10CFR50.72(b)(2)(xi) due to a press release being issued. On 12/19/05 at 14:46 CST, a licensee employee was leaving the station and received a gunshot wound to the left leg/ankle while walking between the Byron Main Access Facility and the Byron Pre Access Facility. Onsite personnel provided first aid assistance, and an offsite ambulance responded to the scene. The injured individual was transported to St. Anthony's Hospital in Rockford, Illinois. The injured individual is in stable condition and is expected to make a full recovery. The Ogle County Sheriff's Office is conducting an investigation into the event. Byron Security Firing Range activities were in progress at the time of the event and were suspended immediately upon notification of the injury. A press release is being issued due to media attention related to this event. The NRC Resident Inspector has been notified, as well as NRC personnel from Region III and NRC Headquarters." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-12-20
42211 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-12-17 03:11 | 2005-12-17 03:45 | 2005-12-17 | AUTOMATIC REACTOR TRIP FROM FULL POWER DUE TO A FAILED FEED FLOW CHANNEL "'A' Steam Generator hi/hi level caused a turbine trip which in turn caused a Unit 1 reactor trip. The hi/hi steam generator level also caused both feedwater pumps to trip which caused the auxiliary feedwater pumps to auto-start. The hi/hi level also caused a feedwater isolation. Appropriate emergency procedures have been implemented and the plant is currently stable." All control rods fully inserted on the trip. Offsite power is available and powering safety related buses. The emergency diesel generators are available if required. There are no known primary to secondary leaks in the steam generators. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-12-17
42210 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2005-12-16 09:30 | 2005-12-16 16:20 | 2005-12-16 | ARIZONA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "At approximately 9:30 AM December 16, 2005, the Agency was informed by the Licensee that a Troxler Model 3411B Portable Gauge, SN 17964 had been stolen from the back of an employee's pick up truck. The theft occurred between 2:00 - 4:30 AM December 16, 2005. The gauge contains 8 mCi (millicuries) of Cesium-137 and 40 mCi (millicuries) AM:Be-241. "Phoenix PD is investigating and has issued report number 2005-52380969 "The Licensee is offering a $500.00 reward for the recovery of the truck and sources. A press release is to be made. "The Agency continues to investigate. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2005-12-21
42209 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-05-18 | 2005-12-16 14:16 | 2005-12-16 | OHIO AGREEMENT STATE REPORT - LOSS OF TRITIUM FOIL SOURCE The State provided the following information via email: "Licensee had submitted license renewal application. RFI from ODH requested info on disposition of sources to be removed from the license. One H-3 foil source from a Varian Aerograph ECD was reported as having been disposed of on May 18, 2004. When asked to produce documentation, the licensee went back to their copy of the waste shipping manifest to find reference to the H-3 source. However, this source was not referenced on the manifest as being included in the shipment on the licensee's copy. The licensee has contacted the waste broker to investigate whether this source had been included in the waste shipment. Source was purchased in the late 1970's and was removed from service and placed in storage in the late 1990's. The source is now calculated to have an activity of 232 millicuries. The licensee will file a written report to ODH as required by Ohio regulations." This source was part of an electron capture detector, Varian model 02-1681-01. Ohio Item Number: OH050008 Notified the R3DO (Burgess), NMSS (Karas) and TAS (via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-12-21
42208 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-15 13:04 | 2005-12-15 17:15 | 2005-12-15 | LOSS OF 38 OUT OF 67 EMERGENCY SIRENS DUE TO WEATHER "During performance of weekly testing on ANS Sirens 38 of 67 sirens failed. Suspect due to inclement weather. Retested at 15:43 (EST) and currently 4 of 67 are inoperable. " Licensee notified Mecklenburg county. NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-12-15
42207 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2005-09-12 | 2005-12-15 12:26 | 2005-12-15 | ILLINOIS AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The State provided the following information via email: "On December 14, 2005 the licensee's Radiation Safety Officer, [name deleted], called the Division and forwarded information describing a medical misadministration that involved a brachytherapy dose that was greater than 10 percent from the intended treatment. The misadministration had occurred some months ago. The event was discovered as a result of a review of past treatments during an attempt to understand, what appeared to be, anomalies for certain cases. "In a particular case on September 12, 2005, a patient began treatment for cervical cancer with a 'Fletcher Suit' manual brachytherapy afterloader using Cs-137 sealed sources. A transposition error was made in the digitization of the patient's lateral film used to construct the applicator's position and thus the positions of the radiation sources relative to the locations of the dose calculation points. Therefore, the digital locations used for mapping and treatment planning of points 'right A' and 'left A' relative to the sources were incorrectly determined. "These calculated points used in the treatment planning were located in a region of lower dose rate within the tumor than the true anatomical 'A points', at which the prescription should have been defined. As a result, the prescription/final treatment plan used incorrect lower dose rate points and called for the use of an erroneously high source loading. Based on a retrospective analysis, instead of the calculated average dose rate of 0.545 Gy/hr for the erroneous 'A points', the actual delivered averaged dose rate to the true 'A points' was 0.74 Gy/hr. This resulted in an average dose of 54.3 Gy delivered to the true points A instead of the planned 40.0 Gy. The dose to the other points, namely rectum and bladder, were calculated correctly because their location did not involve the digitization step in which the transposition error occurred. These doses, which were calculated correctly, were all within acceptable limits. Only the tumor dose was in excess of the intended dose. "This event occurred because of a misunderstanding concerning use of the new treatment planning system (TPS) that was being introduced into the clinic. The TPS allows digitizing either a right or left lateral film for locating the sources, bladder and rectal points for calculating doses. However the location of target point 'A', which is used for dose prescription, must be determined manually. Therefore a separate program is used which requires digitizing the source applicator on AP and lateral films to localize these points. In this additional step, the orientation of the lateral film on the digitizer was reversed left to right from what the program required, resulting in sign reversal of the anterior-posterior coordinate of the left and right 'A points'. This error was discovered in December, when looking into why positions of calculated points sometimes appeared unusual. This error was not caught at the time of the original implants. "Once this potential source of dose discrepancy was discovered, the licensee reviewed all the patients whose dosimetry plans were determined with the new TPS since treatments were first initiated some three months ago. Three total patients were identified. The magnitude of the effect was found to also depend upon the orientation of the applicator in the patient. Only the case described above had those adverse complications which resulted in a medical event. A review of the two additional dosimetry plans showed that due to the orientation of the apparatus in the patient, the dose to the true prescription point was less than 5% greater than the planned dose. The clinical consequences for the patient concerned in this report are being evaluated by physicians. "Four Cs-137 sealed sources with a total activity of 178 mCi were inserted into the patient. The planned averaged point A dose was 40.0 Gy and the actual administered dose was 54.3 Gy. Other than the 'point A' dose, no other dose calculation points were outside of the treatment specifications. The physicians are reviewing the revised dosimetry plans to determine if there will be any increased risk of complications for this patient. The clinical consequences for the patient concerned in this report are being evaluated by physicians. The dose at the various calculation points were: "Dose points/Planned Dose (Gy/hr)/Actual Dose (Gy/hr) Right A/0.56/0.74, Left A/0.530.74, Right B/0.18/0.18, Left B/0.17/0.17, r-rectum/0.33/0.37, s-rectum/0.35/0.39, t-rectum/0.31/0.32, u-rectum/0.21/0.21, B-bladder/0.47/0.43. "This matter will be included during an pending routine inspection which will be conducted in the next 30 days. "Corrective Actions: Action Number / Corrective Action: 1 PROCEDURE MODIFIED 2 PERSONNEL RECEIVED ADDITIONAL TRAINING "Patient Information: Patient Number: 1 Patient Informed: N Date Informed: Therapeutic BRACHY, MANUAL AFTERLOADER Organ: CERVIX Dose: 5430 rad 54.3 Gy % Dose Exceeds Prescribed: 36 % Dose is Less Than Prescribed: Effect on Patient: UNKNOWN Administered By: PHYSICIAN Dose to Family: 0 rem 0 Sv Dose to Newborn: 0 rem 0 Sv Dose to Fetus: 0 rem 0 Sv Source of Radiation: Due to the nature of the event, this matter was reported to the U.S. NRC Operations Center on December 15, 2005. It was assigned event number 42207 Source Number: 1 Form of Radioactive: SEALED SOURCE Radionuclide or Voltage (kVp/MeV): CS-137 Source Use: BRACHYTHERAPY Activity: .178 Ci 6.586 GBq Manufacturer: Model Number: Serial Number: Device/Associated Equipment: Device Number: 1 Device Name: MANUAL AFTERLOADER Model Number: Manufacturer: UNKNOWN Serial Number: Reporting Requirement: 32 IAC 335.1080 - Any administration of radioactive materials that results in a 'reportable event' (misadministration), licensee shall notify the agency by telephone NLT next day after licensee ascertains and confirms that a 'reportable event' has occurred. Mode Reported: Written" Illinois Item No. IL-050073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2005-12-20
42206 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-12-15 09:30 | 2005-12-15 12:19 | 2005-12-20 | LOSS OF EMERGENCY SIREN POWER "On December 15, 2005, at 0930 hours, it was determined that approximately 17 of 65 Oconee Nuclear Station emergency sirens, located in Pickens and Oconee Counties, failed to send a feedback signal when checked. It is postulated that these sirens are inoperable due to a loss of power attributed to severe icing conditions currently being experienced in both counties. At the time of discovery, current weather conditions were a steady light rain with a temperature of 33 degrees F. "Duke is currently attempting to restore power to the affected sirens but does not expect to have all of the inoperable sirens back in service until later in the day. During the loss of siren period, a compensatory means of notifying the public has been put into place to include routing of local law enforcement personnel to the affected areas for public notification should an emergency occur at the station. Because more than 25% of the sirens were unavailable as a result of this event, this event constitutes a major loss of notification capability; consequently, this event is reported as an eight -hour notification in accordance with 10CFR50.72(b)(3)(xiii) reporting criteria. "The licensee notified the NRC Resident Inspector and applicable station personnel. "Initial Safety Significance: None. Compensatory measures have been put into place to ensure that the members of the public located in the affected areas are appropriately notified by local law enforcement personnel. All three Oconee units remain operable in Mode 1 (100 percent Power) and are unaffected by this condition. "Corrective Action(s): Duke will attempt to have all of the inoperable sirens restored as soon as possible and will maintain the compensatory action in-place until full restoration has been completed." * * * UPDATE ON 12/16/05 AT 1620 FROM JOHN COLLINS TO JOE O'HARA* * * "On December 15, 2005, at 0930 hours, it was determined that approximately 17 of 65 Oconee Nuclear Station emergency sirens, located in Pickens and Oconee Counties, failed to send a feedback signal when checked. It is postulated that these sirens are inoperable due to a loss of power attributed to severe icing conditions currently being experienced in both counties. At the time of discovery, current weather conditions were a steady light rain with a temperature of 33 degrees F. "Throughout the day and night of December 15th, additional sirens were lost. A maximum number of 40 sirens were eventually lost. "On December 16th, 2005, at 0815 Emergency Planning contacted Oconee and Pickens County to assess the siren outage due to ice storm on 12-15-05 and the results of the assessment were that Pickens County still had 17 sirens out of service and Oconee County still had 9 sirens out of service due to the ice storm. The ONS resident NRC inspector was notified this morning at 0818 of the siren issue and all of his questions and concerns were answered. Duke Power Company Community Affairs was also notified. "On December 16th, 2005, at 1509, Emergency Planning contacted Oconee and Pickens County. The results were that Pickens County still has 11 sirens out of service and Oconee County still has 2 sirens out of service due to the ice storm. This reduces the total number of sirens out of service to less than the threshold considered a major loss of offsite response capability per the 10CFR 50.72 notification requirements. "Duke is currently attempting to restore power to all the affected sirens. Power is expected to be restored to the entire service area by Sunday. "During the loss of siren period, a compensatory means of notifying the public was put into place to include routing of local law enforcement personnel to the affected areas for public notification should an emergency occur at the station. "Initial Safety Significance: 12-16-05, Safety Significance has not changed. None. Compensatory measures have been put into place to ensure that the members of the public located in the affected service areas are appropriately notified by local law enforcement personnel. All three Oconee units remain operable in Mode 1 (100 percent power) and are unaffected by this condition. "Corrective Action(s): Duke will attempt to have all the inoperable sirens restored as soon as possible and will maintain the compensatory action in-place until full restoration has been completed." The R2DO(Decker) had been notified. ***** UPDATE ON 12/20/05 AT 1610 EST FROM RANDY TODD TO MACKINNON ****** "This update (December 20, 2005) is to report that all sirens have now been returned to service and tested. "Duke has completed repairs to restore and test all sirens. Full restoration has been completed." R2DO (Paul Fredrickson) notified. NRC Resident Inspector will be notified of this update by the licensee. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-12-15
42205 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2005-12-14 06:30 | 2005-12-14 16:30 | 2005-12-14 | AGREEMENT STATE REPORT - STOLEN RADIOACTIVE MATERIAL The State provided the following information via facsimile: "Event type: Theft of Nuclear Pharmacy delivery vehicle en route to hospital "Notifications: Local Police Department. "Event description: The SC Department of Health and Environmental Control was notified on Wednesday (a.m.), December 14, 2005, by the pharmacist/RSO for the facility that one of their delivery vehicles had been stolen at gunpoint. The vehicle was en route to a hospital to deliver radiopharmaceuticals. The vehicle was carrying approximately 795 millicuries of Technetium 99m, 42 millicuries of Thallium 201 and one Iodine 123 capsule at 0.36 millicuries. The Port Royal Police Department was contacted and responded to the incident. The search is still ongoing at this point. The event is still under investigation and updates will be made through the national NMED system as they become available." Contact the NRC Headquarters Operations Officer for additional details South Carolina Event Report ID No.: SC050007 THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2005-12-19
42204 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-13 13:45 | 2005-12-13 18:10 | 2005-12-13 | OFFSITE NOTIFICATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS. "At 1345 CST as part of post maintenance testing of the Comanche Peak Alert and Notification (siren) System, a polling of the system was initiated from the onsite microwave building. In response to this polling, only 5 of the system's 72 sirens initially responded. Troubleshooting determined that the 450 MHz radio system repeater used by both the siren system and the site emergency response teams was malfunctioning. Malfunction of this radio repeater made functionality of the systems intermittent and full function of neither was assured. "The siren system and emergency response radio system have been returned to service by switching to the backup radio repeater at 1522 CST. "There are no events in progress that required siren operation or dispatch of the site's emergency response teams. "The NRC Resident Inspector has been notified of the siren and emergency response radio system failures." | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2005-12-13
42203 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-12 18:30 | 2005-12-13 18:06 | 2005-12-13 | VIOLATION OF SPENT FUEL HANDLING CONDITIONS "This report is being made pursuant to a reporting requirement specified in Certificate of Compliance Number 1015, Appendix B2.1, which states that if any fuel specification or loading conditions of this section are violated that the affected fuel assemblies be placed in a safe condition; that the NRC Operations Center be notified within 24 hours and that a special report be submitted within 30 days. "On 12/12/2005, fuel handlers were loading a NAC-UMS canister with spent fuel assemblies from the McGuire Unit Two fuel pool. As the fuel handlers were attempting to retrieve a fuel assembly from pool location PP-34, they inadvertently picked assembly Z50 from pool location RR-34. Once retrieved, the assembly was transferred to the canister where it was lowered into the canister. As the assembly was being lowered into the canister, a camera operator noticed that the fuel ID did not match the one specified in the loading procedures. The assembly was never disengaged from the grappling tool used to move it to the canister. From a fuel specification perspective, the initial enrichment was 3.636 weight percent U-235, the final burnup was 40,254 MWD, and the discharge date was 2/22/2002. At this time, the decay heat for this assembly has been conservatively determined to be greater than the decay heat allowed per assembly. The fuel specifications not being met for this condition were minimal cooling time of five years (Table B2-4) and the allowable decay heat per assembly (Table B2-1). "Immediate corrective actions included returning the fuel assembly to its original storage location in the fuel pool." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW | [5 empty] | 0 | 2005-12-13
42202 | 0 | LEWIS-GALE MEDICAL CENTER |  |  |  |  | 2005-12-13 | 2005-12-13 16:50 | 2005-12-13 | MEDICAL EVENT On 12/09/05 a patient was to receive 220 millicuries of I-131 (three capsules). The three capsules were transported in two small pigs. On Tuesday,12/13/05, one of the capsules was discovered in one of the two pigs indicating the patient only received two of the capsules. The patient will be notified. The licensee notified Tara Weidner at NRC Region 1. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-12-13
42201 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2005-11-06 01:19 | 2005-12-13 15:42 | 2005-12-13 | INVALID CONTAINMENT ISOLATION SIGNAL GENERATED "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1), to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A), 'Any event or condition that resulted in manual or automatic actuation of any system listed in paragraph (a)(2)(iv)(B).' General containment isolation signals affecting containment isolation valves in more than one system is identified in paragraph (a)(2)(iv)(B). "On November 6, 2005, at 0119 hours, with Unit 2 in Mode 5 'Refueling,' an invalid containment isolation signal was generated when maintenance personnel disconnected an electrical lead. The event occurred due to an error in a work package and resulted in the initiation of Group 2 and 3 isolation signals. The containment isolation signals affected containment isolation valves in more than one system. All affected containment isolation valves operated as designed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-12-13
42200 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2005-12-12 18:30 | 2005-12-13 14:00 | 2006-07-11 | STOLEN MOISTURE DENSITY TROXLER GAUGE The licensee provided the following information via facsimile: "On the evening of December 12, 2005 at approximately 6:30 pm CST, a Troxler model 3440 moisture density gauge, serial number 503557, containing 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be was stolen from the back of a pickup truck at a Home Depot parking lot in Birmingham, Alabama. The licensee, Goodwyn, Mills & Cawood, Inc., notified the Birmingham Police Department and the Alabama Office of Radiation Control. The Alabama Office of Radiation Control advised the Alabama Emergency Management Agency of the event. Goodwyn, Mills & Cawood, Inc. is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 1404. The licensee representative stated that the transport case was not locked and chained in the bed of the truck as required. The licensee representative did state that the gauge shutter was locked. A pressure meter was stolen in addition to the gauge. The Agency advised the licensee to consider issuing a press release and a reward. The licensee has been able to view surveillance tapes from Home Depot which appear to indicate that the gauge was stolen by individuals riding around the parking lot looking for unsecured items to steal in the back of trucks. The licensee has provided the Birmingham Police Department with a picture of the gauge and is checking with the local businesses and pawn shops. This is all the information that this Agency has at this time and is current as of 11:20 am CST." Alabama Event 05-70. * * * UPDATE AT 0931 EDT ON 7/11/06 FROM DAVID A. TUBERVILLE TO S. SANDIN * * * The following information was received as an update via fax: "SUBJECT: Found Gauge Containing Radioactive Material. - Alabama Event 05-70 - UPDATE. "On the morning of July 10, 2006, the Alabama Office of Radiation Control was contacted by Alabama Emergency Management Agency concerning a container found behind a convenience store in Irondale, Alabama that had radioactive material markings. The Irondale Fire Department was at the scene. The item was determined to be a Troxler model 3440 moisture density gauge within its transport container. It was determined that this gauge is the one that was stolen on the evening of December 12, 2005 from the back of a Goodwyn, Mills & Cawood, Inc. pickup truck at a Home Depot parking lot in Birmingham, Alabama. Goodwyn, Mills & Cawood, Inc. is authorized to possess and use radioactive material under their Alabama Radioactive Material License No. 1404. The licensee was notified of the found gauge and took possession of the device that morning. The licensee representative advised the Alabama Office of Radiation Control that the device was intact and confirmed that the device was the one stolen on December 12, 2005. The licensee representative was advised to perform a leak test and obtain the results before placing the gauge back in service. Also, the licensee representative was requested to submit a written report to the Agency describing the event with results of the leak test. "It was noted that the serial number for the gauge found (14822) did not match with the serial number of the gauge stolen (503557). The serial numbers were confirmed with the licensee representative who indicated that the 503557 serial number was inaccurate. The correct serial number for this incident should be 14822." Notified R1DO (Meyer), NMSS (Morell) and ILTAB via email. THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2005-12-16
42199 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2005-12-13 03:39 | 2005-12-13 06:42 | 2005-12-13 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSER VACUUM "Point Beach Unit 1 was manually tripped at 0339 CST on 12/13/05 due to a loss of condenser vacuum caused by a mechanical failure of the running circulating water pump. All plant systems responded normally, including an auxiliary feedwater actuation." The trip was uncomplicated. All rods fully inserted. MSIVs were isolated due to the loss of condenser vacuum so decay heat is being removed by the atmospheric dump valves. The licensee indicated that there are no known steam generator tube leak issues. All systems functioned as required. The licensee was not in any significant LCO at the time of the trip. The trip had no impact on the electrical lineup or on Unit 2 operations. The cause of the circ water pump failure is still under investigation but there is evidence of sheared bolts on the pump coupling. The licensee noted the turbine condenser rupture disks blew due to high pressure. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-12-13
42198 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-12-09 21:30 | 2005-12-12 17:30 | 2005-12-12 | STOLEN SEALED CALIBRATION SOURCE - 2 MILLICURIES OF AM-241 "The North Carolina Radioactive Materials Branch was notified at 16:00 [EST] today [12/12/05] of the theft of an Am-241 sealed calibration and reference source from a Siemens Medical Solutions USA, Inc. (N.C. Radioactive Materials License No. 068-0895-1) service vehicle. The theft occurred on 09 December 2005 between 21:30 and 23:00 in Statesville, NC. "The information for the missing source is as follows: Isotope: Am-241 Activity: 2 millicuries Make: AEA Technology Model: AMC.P3 Serial No.: 0182LX "The theft occurred at a restaurant parking lot in Statesville, NC. The source was contained within a locked tool-box stored inside of the locked service vehicle. The passenger side window was broken and the toolbox was taken, along with other items, from the vehicle. "The licensee notified the Statesville, NC police department [Report No. 05-4284] and the police have conducted a preliminary investigation into the break-in/theft. The licensee has drafted a press release and is offering a $1,000 reward for the return of the source. "The Radioactive Materials Branch continues to monitor the situation and will update the NRC when new information becomes available." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-12-15
42197 | 0 | FROEHLING & ROBERTSON |  |  |  |  | 2005-12-12 07:15 | 2005-12-12 09:30 | 2005-12-13 | STOLEN MOISTURE DENSITY GUAGE A Troxler moisture density gauge (Model 3430, Serial number 36310) was stolen in front of a residence in Roanoke, VA. The technician wanted to get an early start on his Monday morning tasks, went into work at 14:00 Sunday, and took the truck home. The gauge was properly attached to the truck with two chains and two locks. The gauge was stolen sometime between 14:00 Sunday (12/11/2005) and 07:15 Monday (12/12/2005). The technician called 911 and made police report #143498. Sources: 9 milliCurie Cs-137 and 40 milliCurie Am-241/Be * * * UPDATE AT 16:20 ON 12/13/2005 FROM BRIODY TO ABRAMOVITZ * * * The licensee found the stolen Troxler gauge on a river bank approximately two miles from the scene of the theft. The gauge was still in the case and no apparent damage was observed. Notified NMSS (Morell), R1DO (Dimitriadis), and TAS (via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-12-12
42196 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-12-11 09:04 | 2005-12-11 10:02 | 2005-12-11 | INFORMATION ONLY- ACCIDENTAL WEAPON DISCHARGE On 12/11/2005, at 0904 EST, a security officer unintentionally discharged a weapon on site inside the protected area. The guard was cleaning the weapon at a security location between the turbine building and the reactor building and inadvertently pulled the trigger. The bullet entered a chair and was stopped by the chair. It did not impact any plant equipment or anything else and therefore has no ongoing safety significant implications. The security guard was removed from the protected area and has been sent for a fitness-for-duty test. An investigation will be conducted. The incident is considered a security logable event by the licensee. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW | [5 empty] | 1 | 2005-12-11
42195 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2005-12-09 14:00 | 2005-12-09 19:48 | 2005-12-12 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The licensee provided the following information via facsimile: "On December 9, 2005 approximately between 11:50 a.m. and 12:15 p.m. [the gauge operator] lost a Nuclear Gauge (Troxler Moisture Density Gauge, Model 3430, s/n 35182, 8 millicuries Cs-137 and 40 millicuries Am-241:Be). "[The gauge operator] was out at Del Webb Somersett, Village 8 to perform compaction tests with the Nuclear Gauge. [The gauge operator] arrived on the job-site and parked his truck at the intersection of Hidden River Way and Del Webb Parkway. He got his equipment ready to so he could begin to test the soil compaction. He took the gauge out of the safety box, and left it in the bed of his truck with the tailgate down. "The contractor, ran into rock while excavating, and it was taking longer than normal to lay the pipe backfill. On and off for the next two hours [the gauge operator] watched from his truck. Lunchtime rolled around and the gauge operator left the jobsite for lunch. He did not put the gauge back in the safety box, or put his tailgate back up. "This is the route that [the gauge operator] took to go to lunch. He took Del Webb Parkway East to Somersett Parkway. He took Somersett Parkway all the way to Mae Anne. After turning left onto Mae Anne he drove to KFC located in the Wal-Mart complex near McCarran Blvd. He went through the drive-thru at KFC, got his lunch and drove back to the job-site by the exact same route. When back on Del Webb Parkway he ran over a piece of steel and got out of his truck to see what he ran over. When he got out, he saw that the tailgate was down on his truck and that the gauge was gone. This was approximately 12:15 p.m. When [the gauge operator] saw the gauge was gone he got in his truck and retraced all of his steps looking for the gauge. He did not find it. The workers on the job site were asked if they had seen the gauge and no one had." The licensee notified the Reno Police Department and Washoe County Sheriff's Department. Event Report ID NV-05-006. * * * UPDATE TO ABRAMOVITZ RECEIVED VIA FAX AT 10:04 ON 12/12/05 * * * "The gauge has been found and is now in the possession of the licensee. Some gauge electronics appeared to be missing, but the source appears to be intact. The gauge has been leak tested." Nevada has updated the Event Report ID Number from NV-05-006 to NV-05-009. Notified NMSS (Morell), R4DO (Johnson), and TAS (via E-mail). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2005-12-14
42194 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-09 15:44 | 2005-12-09 18:11 | 2005-12-12 | RCS PRESSURE BOUNDARY LEAKAGE IDENTIFIED "At 1450 hours on 12/5/05, Unit 2 entered abnormal operating procedure 18004-C 'RCS Leakage' due to increasing containment atmospheric radiation levels as identified on 2RE2562A. Per procedure, an RCS leak rate determination was commenced and completed as of 1629 hours, 12/8/05 (identified = 0.032gpm, unidentified = 0.254gpm, total = 0.286gpm). While making preparations for a containment entry for leakage inspection, a second leak rate [determination] was completed at 2020 hours, 12/8/05 (identified = 0.070gpm, unidentified = 0.267gpm, total = 0.337gpm). At 2240 hours, 12/8/05, the team performing the containment leak inspection reported no leakage identified outside the bioshield. Another leak rate [determination] was completed at 0245 hours, 12/9/05, the team performing the containment leak inspection reported that by using a robotic camera, water was observed coming down the inside wall of the bioshield in the area of loop 2. At 0433 hours, 12/9/05, a shutdown of Unit 2 was initiated to allow further investigation / repair of the RCS leak inside containment. Unit 2 was placed in Mode 3 at 1313 hours, 12/9/05. At 1544 hours, 12/9/05, the containment leak inspection team reported pressure boundary leakage at a welded connection where a 3/4 inch bypass line is welded to the RCS loop upstream of the RHR loop suction valve 2HV8701B. [Plant Vogtle personnel are] presently preparing to commence shutdown to Mode 5 for repair of the leak." Technical specification 3.4.14 applies and requires no pressure boundary leakage. The plant is currently removing decay heat by steaming from the steam generators through the steam dump valves to the condenser. All safety related electrical buses are available. Emergency diesel generators are available and in standby. The licensee notified the NRC Resident Inspector. * * * UPDATE RECEIVED BY PHONE ON 12/12/2005 AT 13:50 FROM JIM POLICKOSKI TO ABRAMOVITZ * * * Two corrections were communicated. The date of the initial event was "at 1450 hours on 12/8/05." The technical specification quoted is changed to 3.4.13. Notified the R2DO (Henson). | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-12-09
42193 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-12-09 09:01 | 2005-12-09 13:15 | 2005-12-09 | TRIP OF A STARTUP BUS BREAKER RESULTS IN START OF EMERGENCY DIESEL GENERATORS "At 0901 on December 9, 2005, a trip of the 10 Startup Bus Breaker occurred at Limerick Generating Station in the 220 KV substation. This de-energized one of the required offsite sources and the associated 10 Startup Bus and 101 Safeguard Bus, causing a valid actuation signal for the D11, D13, D22 and D24 Diesel Generators. All diesels started and their associated 4 KV buses swapped to the 201 Safeguard Bus as required. The cause of the 10 Startup Bus Breaker trip is under investigation. Units 1 and 2 remain at 100% power." No safety related loads were lost. The diesel generators were still running at the time of the call but, the licensee was shutting down the diesels per procedure. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-12-09
42192 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-12-08 15:00 | 2005-12-09 10:55 | 2005-12-09 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via email: "On December 8, 2005, the California Radiologic Health Branch received notification from the Office of Emergency Services that one moisture density gauge (Troxler Model 3440, SN 31824, containing up to 9 mCi Cs-137 and up to 44 mCi Am-241) had been stolen from MFG, Inc. The gauge, along with a few other items, was stolen from the licensee's storage unit in Santa Ana, CA. The transport case was still in the storage unit, but the gauge was missing. The California Radiologic Health Branch is following up with the licensee to obtain more information." THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE FROM D. KRAJEWSKI TO P. SNYDER AT 1835 ON 12/8/05 * * * The State of California representative called to correct the earlier report due to additional information they received. The transport case housing the gauge was also stolen with the gauge. The State provided the following information via e-mail: "The door to the facility had been pried open. The lock to the wooden storage box (which housed the gauge / gauge transport case) was still fastened, but the side of the wooden storage box had been pried open and the transport case and the gauge were gone. The California Radiologic Health Branch is following up with the licensee to obtain more information and to get a copy of the latest leak test." Notified R4DO K. Kennedy and NMSS EO M. Wayne Hodges. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-12-14
42191 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-12-07 15:00 | 2005-12-08 17:13 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * APPARENT LOSS OF NATURAL THORIUM SHIPMENT "A drum of thorium shavings appears to have been lost during shipment. On 11/11/2005 Nuclear Fuel Services (NFS) shipped a 55 gallon drum of thorium shavings to LR International Inc. The drum was then to be shipped to Highways International of Holland. "On or about 11/22/05 [a contact point] at Highways International informed [NFS] that the shipment had not arrived. [NFS] checked the [shipping company] tracking number and it showed that the shipment had been delivered on 11/21/05. "[NFS] contacted LR International who said that they did not accept large shipments at their Wood Dale Road location and that they had directed the driver to [a trucking company] in Bensenville, IL. [NFS] contacted [the trucking company] who said that they had not received a shipment, but would check again." After contacting the shipping company and other contact points more in the ensuing time period on 12/7/05 NFS determined that the shipment was lost. The shipment consisted of 10 kilograms of natural thorium with a calculated activity of 2200 microCurie. The licensee informed the agreement state of Tennessee. The state of Tennessee representative told the licensee that they would contact the agreement state of Illinois. The licensee notified the NRC Resident Inspector. This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore it is being categorized as a less than Category 3 source. * * * UPDATE FROM DROKE TO KNOKE AT 17:40 EST ON 12/13/05 * * * The licensee provided the following RETRACTION via facsimile: "On December 8, 2005, Nuclear Fuel Services, Inc. (NFS), made a telephone notification to the State of Tennessee and the NRC Operations Center based on SRPAR 1200-2-5-.140 and 10 CFR 20.2201(a)(1)(ii), respectively. At that time, an NFS shipping package containing 10 kgs of Thorium was suspected to be lost, stolen, or missing; in that, the carrier stated the package had been delivered to a forwarding agent in Illinois on November 21, 2005, and the forwarding agent stated that they could not locate the package. Although the referenced regulations allow NFS up to 30 days to make the notification after learning of the potentially missing material, and the material has to still be missing at that time, NFS chose to inform the regulatory agencies soon after management became aware of the matter. "NFS has now been informed by the forwarding agent that the package of Thorium has been located at their facility, and arrangements are being made to return the package to NFS. The FBI has also confirmed that the package has been located. Because it has been less than 30 days since NFS first learned that the package of Thorium may be missing, and because the package has now been located, NFS believes that the earlier telephone notification was not required and is therefore requesting that it be retracted." Notified R2DO (Decker), R3DO ( Burgess) and NMSS (Essig). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2008-05-11
42190 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-12-08 11:15 | 2005-12-08 14:38 | 2005-12-08 | FITNESS FOR DUTY A non-licensed contract employee supervisor had a confirmed positive for alcohol during a fitness-for-duty. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 90 | 100 | 0 | 90 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2005-12-08
42189 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2005-12-08 13:41 | 2005-12-08 13:41 | 2005-12-08 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM DUE TO PLANNED SOFTWARE MODIFICATION There will be a "loss of U3 ERDADS data retrieval capability to Emergency Response Data System (ERDS) link due to a planned software modification to the U3 ERDADS computer. The expected duration of the loss of capability is 3 hours." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM M.A. NEWTON TO P. SNYDER AT 2022 ON 12/8/05 * * * "Unit 3 ERDADS data retrieval capability to ERDS link due a planned software modification to Unit 3 ERDADS computer has been restored. The total duration for this loss of capability was 6 hours." The system was returned to service at 2004. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-12-08
42188 | 0 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2005-12-05 09:00 | 2005-12-05 10:45 | 2006-01-06 | PLANT PROCESS COMPUTER SYSTEM (PPCS) WILL BE TAKEN OUT OF SERVICE FOR APPROXIMATLEY 2 WEEKS. "The Plant Process Computer (PPCS) will be taken out of service for an approximately 2 week period to implement a planned modification. The current PPCS is being replaced and the computer outage is required to allow cutover to the new PPCS. During this time period ERDS and SPDS will not be available. ERDS and SPDS parameters will be monitored by control board indications. Compensatory actions have been developed. "This is an 8-hour reportable event per 10 CFR50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of plant systems will not be affected due to this planned action. "The PPCS outage is expected to commence around 0600 CST on 12/5/05. The licensee has informed the NRC Resident Inspectors of the modification and schedule. The NRC was previously notified of this planned outage via letter dated November 7, 2005." The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE PROVIDED BY JOHNSON TO ROTTON AT 0324 EST ON 12/16/05 * * * "The Plant Process Computer System was restored at 2330 CST on 12/15/05. The Safety Parameter Display System (SPDS) has been returned to service. The Emergency Response Data System (ERDS) portion of the system will be turned over once the testing has been completed." The licensee will notify the NRC Resident Inspector. Notified R3DO (Burgess). * * * UPDATE PROVIDED BY ELLISON TO ROTTON AT 1716 EST ON 01/06/06 * * * "This notification is an update to previously made notification, EN# 42188. As of 14:30 CST on 1/6/06 the Unit 1 Emergency Response Data System (ERDS) has been accepted for use and is considered fully operational." The licensee notified the NRC Resident Inspector. Notified the R3DO (Ring) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-12-05
42187 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-12-02 17:00 | 2005-12-03 12:25 | 2005-12-03 | REACTOR POWER OPERATION IN EXCESS OF OPERATING LICENSE CONDITION "This notification is being made pursuant to Braidwood Station Unit 1, Operating License Condition 2.G, which requires a 24 hour notification to the NRC Operations Center for reactor power operation in excess of 3586.6 megawatts thermal (100 percent rated power), i.e., a violation of Operating License Condition 2.C (1)- Braidwood Station will, following this notification, provide a written report within thirty days in accordance with the procedures described in 10 CFR 50.73(b), (c), and (e). "Braidwood Station, Unit 1 experienced a Feedwater temperature transient on November 18, 2004, which caused reactor power to momentarily increase and peak at approximately 101.2% as indicated on the excore nuclear instrumentation system. The duration that reactor power remained above 100% was approximately one minute. Subsequent to the event, a number of peer reviews were conducted to validate that power did not exceed 102%. The results of these reviews questioned the methodology used to determine the power level at the time of the transient. Industry was consulted regarding methodologies appropriate for power level measurement during transient conditions. At 1700 on December 2, 2005, an independent Exelon task force concluded, using a conservative methodology, that reactor power level during this transient did exceed 100% for approximately one minute and was limited to a peak of approximately 103.5% and that the appropriate reports, as specified in the Operating License, should be initiated. "This overpower transient, caused by the loss of a Feedwater heater string, is bounded by the Feedwater design basis transient described and analyzed in UFSAR, Section 15.1.1, "Feedwater System Malfunctions Causing a Reduction in Feedwater Temperature, therefore, the event did not place Braidwood Unit 1 in an unanalyzed condition that significantly degraded plant safety. No safety limits were exceeded and there was no impact on the health and safety of the public. The licensee has notified the Resident Inspector." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2005-12-03
42186 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-03-08 | 2005-12-02 14:18 | 2007-11-20 | AGREEMENT STATE REPORT - MISSING RADIOACTIVE MATERIAL The State provided the following information via email: "Date of Event: March 8, 2005 (reported to DOH December 1, 2005) Location of Event: Pacific, Washington "In a phone call made Thursday, December 1, by DOH staff to set up a time to meet with a licensee for a routine inspection, we were informed that a part of the licensed material they store had been stolen. The material stolen was 2,719 pounds magnesium metal plate that contained 2 and 3 percent Thorium-232. The plate thickness varied between 1.125 inches to 2.25 inches, with most measuring 1.25 inches. The plate dimensions varied. The longest and most numerous pieces were 72 inches long. The width varied from 3.38 inches to 65 inches with most measuring 8.25 inches. The largest plate weighed 590 pounds with three plates weighing around 250 pounds. Most pieces weighed 50 pounds. This is approximately one third of the licensee's inventory of this material. The size of the material left behind was larger than that taken and could be the reason the entire inventory was not stolen. "Bolt cutters were used to cut off the locks to the storage building where the plate was stored. The material was loaded onto trucks and driven off the premises. "The theft was reported to the local police when the theft was discovered by the licensee. The police report number of 05378 was given to this case. An insurance claim has also been filed. The licensee replaced the locks in a manner that will prevent them from being cut through again. Each door has two locks for a total of four locks. "No media notified. "Isotope and Activity involved: Thorium-232, activity less than 6 millicuries. Activity was calculated based on the entire weight of 3% thorium alloy. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Not known. Lost, Stolen or Damaged? (mfg., model, serial number): Stolen. Disposition/recovery: There has been no recovery to date. Leak test? N/A Vehicle: (description; placards; Shipper; package type; Pkg. ID number) N/A Release of activity? Not known. Activity and pharmaceutical compound intended: N/A Misadministered activity and/or compound received: N/A Device (HDR, etc.) Mfg., Model; computer program: N/A Exposure (intended/actual); consequences: N/A" Washington Event Report # WA-05-070 This source is not amongst those sources or devices identified by the IAEA Code of Conduct for the Safety & Security of Radioactive Sources to be of concern from a radiological standpoint. Therefore is it being categorized as a less than Category 3 source. * * * UPDATE AT 11:49 ON 11/20/2007 FROM ARDEN SCROGGS TO MARK ABRAMOVITZ * * * The State provided the following information via email: "The licensee has been unable to recover any of the stolen Magnesium Thorium Plate, they have not obtained any additional information regarding this incident of 32 months ago and now regard this as a 'dead issue.'" Notified R4DO (Clark), FSME (Burgess), Canada (E-mail), and ILTAB (E-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-12-07
42185 | 0 | FRAMATOME ANP RICHLAND |  |  |  |  | 2005-11-15 | 2005-12-02 12:50 | 2005-12-02 | PART 21 NOTIFICATION - SAFETY LIMIT MINIMUM CRITICAL POWER RATIO CALCULATION "(i) Name and address of the individual informing the Commission: Jerald S. Holm, Framatome ANP, 2101 Horn Rapids Road, Richland, WA 99354 "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: The Safety Limit Minimum Critical Power Ratio (SLMCPR) for Susquehanna Unit 1 Cycle 14. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: Framatome ANP "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such a defect or failure to comply: The mean bow and standard deviation from recent channel measurements during a Susquehanna Unit 1 Cycle 14 (SQ1C14) mid-cycle outage exceed the values in the current database used in licensing analyses for Susquehanna Unit 1. "The majority of data acquired at Susquehanna Unit 1 during the mid-cycle outage were in the exposure range of 35 to 45 MWd/kgU. In that range, the new measurements exceed both the mean and the standard deviation of bow from the existing database. Preliminary results from the measurements indicate that the mean from the new data is approximately 60% higher and the standard deviation is approximately 50% higher. "The SLMCPR Technical Specification limit for Susquehanna Unit 1 Cycle 14 was too low (by about .01) when calculated with the channel bow values from the Framatome ANP channel bow database, since channel bows measured for Cycle 14 exceeded those in the channel bow database. Therefore a safety limit could have been violated. "(v) The date on which the information of such a defect or failure to comply was obtained: This issue was determined to be a deviation on November 15, 2005. "(vi) In the case of a basic component which fails to comply, the number and the location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: Susquehanna Unit 1 Cycle 14. "The other plants supported by Framatome ANP analyses, or using Framatome ANP supplied channels, are not impacted. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for this action; and the length of time that has been or will be taken to complete the action: A new SLMCPR for the remainder of the Susquehanna Unit 1 Cycle 14 (denoted Cycle 14a) operation has been provided by Framatome ANP which bounds channel bow experienced during Susquehanna Unit 1 Cycle 14. "Susquehanna Unit 1 also applied a conservative interim CPR penalty (.04) during Cycle 14 operation when slow settling of the control blades was encountered. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: In order to assure that other plants are not impacted in the future by unanticipated channel bow, recommended surveillance actions will be provided in January 2006 to all customers using Framatome ANP channels. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2005-12-02
42184 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-12-02 10:00 | 2005-12-02 11:45 | 2005-12-02 | OFFSITE NOTIFICATION - ELEVATED LEVELS OF TRITIUM FOUND IN GROUNDWATER "This notification is being made pursuant to 10 CFR 50.72(b)(2)(xi) for a press release issued by Exelon Nuclear at 10:00 AM CST on December 2, 2005 regarding elevated levels of tritium found in groundwater on the Braidwood Station site property near the plant's north boundary. An environmental monitoring program at the Braidwood Generating Station has found higher than normal concentrations of tritium close to an underground pipe inside the plant's northern boundary, and the station has begun a remediation program. An Exelon Nuclear environmental team is drilling test wells on and just beyond the Braidwood property line in order to determine how much tritium may have moved beyond the plant boundaries and ultimately to clean up the tritium. Exelon Nuclear has notified NRC regional personnel, appropriate state agencies, local and state elected officials and four property owners who are potentially affected. "The tritium was found in shallow groundwater 8 to 15 feet deep on company property. It poses no health or safety risk to the public and does not threaten drinking water wells in the area. Tritium is a naturally occurring isotope of hydrogen that emits a very low level of radiation and is a natural part of water. It is found in more concentrated levels in water used in nuclear reactors. The closest private residential wells to the site showed no tritium above natural background levels. A sample of water from a pond 50 yards north of the plant property line showed tritium levels of about 2,400 picocuries per liter, above background levels but less than one-eighth of the federal drinking water limit. The residential and pond test samples were taken with the consent of property owners and the results received on Dec. 1. "The underground pipe that passes near the monitored site in the past has carried water containing tritium from the plant to the Kankakee River, where it was periodically discharged under federal guidelines as part of normal plant operations. No tritiated water is currently in the pipe and no tritium is currently being introduced into the ground. Braidwood has not released levels of tritium that exceeded federal limits." The licensee notified the NRC Resident Inspector, State and local agencies and has issued a press release. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-12-02
42183 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-12-02 00:49 | 2005-12-02 05:05 | 2005-12-02 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) FAILURE ON UNIT TWO "At 0049 hours on 12/2/2005 the Unit 2 [safety parameter display system] SPDS system failed. The cause of the failure is under investigation and is expected to exceed 8 hours. "ERDS remains operable but several points are not available. For example 23 of 58 ERDS points are unavailable while SPDS is out of service, The ERDS system can transmit the remaining points. "Loss of Emergency Assessment Capability - A review of the ability of the Emergency organization to function without SPDS was performed. Alternate sources for many of the points in SPDS were identified and are contained on an Emergency Plan format in PICSY (plant integrated computer system). Those points not available from PICSY can be obtained from the control room. With these compensatory actions and the communications in place between the facilities, there will not be a major loss of emergency assessment capability. "Since the Unit 2 SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The NRC Resident Inspector was notified by the licensee. * * * UPDATE (Gordy Robinson verbal notification to Joe O'Hara at 0719 EST on 12/2/2005): * * * " As of 0530 EDT on 12/02/05, Unit 2 SPDS was restored to Operable status following replacement of the CPU Board for the Remote Data Concentrator (RDC). NRC Resident was notified." R1DO (Todd Jackson) notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-12-02
42182 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-12-01 18:30 | 2005-12-01 19:34 | 2005-12-01 | UNANALYZED CONDITION - EMERGENCY DIESEL CAPABILITY "This report addresses a concern with the capability to field flash the diesel generator after the diesel engine has started in response to a fire in the Control Room. Step C9 in procedure OFN RP-017 opens NB0212 to drop power to NB02 and force an automatic start of the 'B' Train emergency diesel engine. Step C10 states to verify that the diesel engine is running and provides an RNO action to start the diesel if it is not running. "Step C10.d in OFN RP-017 has the operator check NB02 voltage on breaker NB0201 NORMAL. There is no RNO action if the voltage is not normal. "A fire in control room panel RL015 has the potential to cause a loss of diesel generator field flashing. For example, a short to ground on conductor 51 in cable 14KJK03AH with a simultaneous short to ground on conductor N1 in cable 14NEB11AA could blow the fuse(s) associated with the speed control relays (LSR and HSR). Loss of power to these relays will prevent field flashing, which will prevent voltage generation from the diesel generator, even though the diesel engine may be running. "Step C10.b in OFN RP-017 has the operator place the master transfer switch (KJHS0109) in LOC/MAN. Based on drawing E-13KJ03A, this action will isolate the control room start circuit by opening the contact between G7 and H7, and effectively isolate the short circuit potential. However, the fuse may have already blown before this action is taken. The circuit is not provided with redundant fusing, so it may be necessary to replace one or both fuses (FU5 and FU6) in panel KJ122 to re-establish power to the speed relays. "Wolf Creek has implemented the following compensatory measures: "Staged 4 spare fuses in the emergency locker in the B Train Diesel Generator Room. Revised OFN RP-017, Control Room Evacuation. Continued hourly fire watch in the control room (established due to another concern). " The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-12-01
42181 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-12-01 10:00 | 2005-12-01 18:46 | 2005-12-01 | AGREEMENT STATE REPORT - POTENTIAL PERSONNEL OVEREXPOSURE "Brief Description of Incident: Licensee's October Landauer [dosimetry processor] report reported a whole body exposure of 11,016 milliRem (Deep) and 10,465 milliRem (Shallow) to an individual who is a cyclotron operator. Landauer reported that this appears to have been a single exposure event, not a continuous exposure over the course of the month. Landauer is assessing the badge at this time to determine if it is a static or a dynamic exposure. The licensee reported a single contamination event that occurred 10/5/05 and resulted in skin and clothes contamination. The licensee is evaluating their documentation of this contamination event at this time. The licensee also reported that ring badges are exchanged weekly but that the badges in use during this contamination event are missing or have not been reported yet. The licensee reported that the individual in question was wearing an electronic dosimeter during the contamination event and recovery time span and had a recorded dose of 19 milliRem on 10/5/05. More information will follow as it becomes available. "Additional Notes: Licensee reported a contamination event (details to be reported later) that occurred 10/5/05 resulting in contamination of the cyclotron operator's skin, clothes and lab coat. The individual left his/her badge on the lab coat overnight so the RAM on the lab coat could decay (110 min half life). Landauer reported the dose today (12/1/05) and has not evaluated if it is a static or dynamic exposure yet, but did report to the licensee that the reported dose appears to be from a single event. The individual who purportedly received this dose has been placed in non-RAM worker status." North Carolina Incident No. 05-40 HOO Note: The radioisotope identified in the report is F-18 (FDG) which is accelerator produced. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-12-06
42180 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2005-12-01 14:45 | 2005-12-01 15:50 | 2005-12-01 | AUTOMATIC REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL While reducing power in order to enter containment, and following a manual main turbine trip due to high vibration, an automatic reactor trip on low steam generator level was received as a result of the turbine trip transient. Containment was being entered to investigate the source of an RCS identified leakage, which was less than the Technical Specification limit. In conjunction with the reactor trip, an automatic actuation of the Auxiliary Feedwater System was received as expected. All control rods fully inserted on the automatic trip. The current decay heat removal path is via the steam dumps to the main condenser. No primary or secondary relief valves lifted during the transient. There are no known primary to secondary leaks. All safety related buses are powered from offsite power. With the exception of one diesel out of service for planned maintenance, all emergency diesel generators are available and in standby. Unit 2 was not affected. The licensee notified State and local agencies and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-12-01
42179 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-11-30 15:00 | 2005-11-30 21:54 | 2005-11-30 | CONTROL ROOM EMERGENCY VENTILATION AC SYSTEM INOPERABLE "On November 30, 2005, at 1500 hours, the Control Room Emergency Ventilation Air Conditioning (CREV AC) system was declared inoperable due to failure of the associated air conditioning compressor. As a result, Technical Specification 3.7.5 Condition A was entered. "The CREV AC system maintains a habitable control room environment and ensures the operability of components in the control room emergency zone during accident conditions. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the CREV system is a single train system, and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident." The licensee informed the NRC Resident Inspector. | 97 | 96 | 0 | 97 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-11-30
42178 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-11-30 03:24 | 2005-11-30 17:14 | 2005-11-30 | INVERTER INOPERABLE FOR GREATER THAN ALLOWED TIME PER TECHNICAL SPECIFICATIONS "This report is being made pursuant to the requirements of License Condition 2.G of the Seabrook Station Operating License. Inverter 1F was inoperable for greater than the 24 hours allowed by Technical Specification 3.8.3.1.h. The inverter was inoperable for a total of 35 hours 59 minutes. The inverter was declared to be inoperable at 0323 on November 29, 2005 and was not returned to operable status until 1522 on November 30, 2005, this exceeded the 24 hour TS limit. The NRC approved a Notice of Enforcement Discretion at 0220 on November 30, 2005, which allowed an extension of 18 hours (until 2123 11/30/05). The inverter was declared operable prior to the expiration of the extension. This event will be documented in a License Event Report pursuant to the requirements of 10CFR50.73." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2005-11-30
42177 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2005-11-28 15:10 | 2005-11-30 16:03 | 2005-11-30 | AGREEMENT STATE REPORT INVOLVING RADIOACTIVE I-131 SPILL "On November 29, 2005 the corporate radiation safety officer contacted the Division by telephone concerning an event that occurred at a nuclear pharmacy operated by Medi-Physics, Inc, dba GE Healthcare (license number IL-01052-01) located at 1053 W. Grand, Chicago, IL. During the call, the Division was advised that, 100 mCi of Na I-131 was spilled at 15:10 on November 28, 2005, when a vial was dropped to the floor and broke outside a fume hood in the iodine room located within the restricted area of the facility. Contamination was detected on the operator's pants and shoes and on various surfaces in the room. However, no personal contamination was detected following removal of the individual's lab coat, shoes, and other clothing. Bioassay results taken shortly after the incident and the next day indicated thyroid uptake was minimal. "A response team from the licensee's main offices performed remediation that evening to contain and shield much of the activity and employ other measures to prevent the spread of contamination. As a result of these efforts, contamination was confined within the iodine room of the restricted area of the pharmacy. Air monitoring results show that there was no elevation of airborne radioactivity in the restricted area or in the effluent air at the release point from the facility that was above regulatory limits. A recovery drum was used to collect and hold waste and materials generated as a result of the clean up. The dose rate on the surface of the container was approximately 350 µSv/h (35 mR/h) and the dose rate at the nearest outside wall in an unrestricted area was 4 µSv/h (0.4 mR/h). "The area will be monitored on an ongoing basis until routine conditions are restored. Although measured dose rates are only slightly elevated at the workstations within the room, access to the room has been limited to monitoring activities, in the interest of ALARA. Prescriptions for radioiodine are temporarily being referred to the company's alternate radiopharmacy." IL Report Number: IL050070 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2005-12-05
42176 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-11-29 08:45 | 2005-11-29 23:36 | 2005-11-29 | FAULTY SWITCH RENDERED CRITICALITY ACCIDENT ALARM SYSTEM INOPERABLE "At 0845 CST, on 11/29/2005 the C-337 process building Criticality Accident Alarm System (CAAS) was being tested when a building horn control switch in C-300 Central Control Facility which supplies voltage to actuate the building CAAS evacuation horns was found to not be properly made up. This switch caused the building CAAS horns not to sound when a cluster was actuated. The test which revealed this problem, was the initial 'as found' test, which means the failure most likely occurred prior to today's testing. The C-337 CAAS system is a TSR system which is required to be operable in the current operating mode unless LCO actions are in place. The C-337 CAAS system was last tested on 11/05/2005 and indications are that the switch problem has existed since that time. "During testing the CAAS alarm was received in C-300, but the evacuation horns did not automatically sound. Per procedure if a criticality alarm had occurred the C-300 operator would have actuated the horn switch manually which would have sounded the evacuation horns. To ensure that not only the C-337 switch was properly repaired, but also to verify all other building horn control switches were in the proper state, a plant wide LCO was implemented and switch outputs were checked to verify the proper voltage output." The NRC Senior Resident has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2005-11-29
42175 | 0 | STEELE MEMORIAL MEDICAL CENTER |  |  |  |  | 2005-11-29 15:20 | 2005-11-29 18:27 | 2005-11-29 | POTENTIAL OVEREXPOSURE DUE TO SURGICAL REMOVAL OF PROSTATE WITH SEED IMPLANTS During surgery to remove a patient's prostate gland, the surgeon announced that there were radioactive seed implants present. The surgeon warned surgical staff in the operating room after the surgery commenced to don lead apron shielding and the prostate gland was covered with a lead apron. The prostate was placed in a plastic container submerged in 5 inches of water in a 5 gallon container with the lead apron over the container based on a consultant's recommendation. The container is in an area with limited access and labeled as a radiation hazard. The hospital does not have a nuclear medicine department or any devices to measure radioactivity. The seed implants were supposedly implanted 90 days ago at a hospital in California with approximately a 30 day half life. The hospital will be ordering a lead shipping container for proper disposal later. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 4 | ID | HOS |  | 20.2202(b)(1) |  |  |  | 0 | 2005-11-29
42174 | 0 | HOSP ONCOLOGICO ANDRES GRILLASCA |  |  |  |  | 2005-11-29 | 2005-11-29 15:40 | 2005-11-29 | MEDICAL EVENT INVOLVING ADMINISTRATION OF LESS THAN THE PRESCRIBED DOSE On 11/22/05 a female patient undergoing treatment for cervical cancer received the third fraction of a five (5) fraction treatment plan using a HDR Brachytherapy source. Each fraction was scheduled to deliver 600 cGy to the intended treatment site for a total delivered dose of 3000 cGy. During the third treatment, the delivered dose was 200 cGy, instead of 600 cGy, due to a miscalculation in the distance factor. The treating physician does not believe there will be any adverse effects upon the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PR | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-11-29
42173 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-11-28 22:20 | 2005-11-29 01:24 | 2005-11-29 | AUTOMATIC REACTOR TRIP FOLLOWING MAIN FEED PUMP TRIP "At 22:19 CST, Main Feedwater Pump B tripped on over current. A secondary plant runback from 100% power was automatically initiated. During the secondary plant runback, the reactor automatically tripped on Steam Generator B low-low level at 22:20 CST. "All three Auxiliary Feedwater pumps automatically started due to low-low Steam Generator level. The plant has been stabilized at Hot Shutdown (RCS temperature approximately 547 degrees F, RCS pressure approximately 2235 psig). Investigation into the cause of the trip is on-going. "This event is being reported under 10CFR50.72(b)(2)(iv)(B) for actuation of the reactor protection system (RPS) when the reactor is critical and 10CFR50.72(b)(3)(iv)(A) for valid actuation of the Auxiliary Feedwater System." All control rods fully inserted on the automatic trip. Steam generator water levels have recovered to indicate in the narrow range. The current decay heat removal path is auxiliary feedwater to the steam generators steaming through the power operated relief valves. There are no known primary to secondary leaks. All safety related buses are powered from offsite power. Emergency diesel generators are available and in standby. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-11-29
42172 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-11-28 07:22 | 2005-11-28 13:25 | 2006-03-02 | AGREEMENT STATE REPORT INVOLVING A STOLEN NUCLEAR GAUGE "At 0830 on November 28, 2005, RHB-Brea received a call from the licensee that one of their gauges (CPN, MC1-DRP, #MD20306488 containing 10 mCi Cs-137 and 50 mCi Am-241:Be) was stolen out of their construction trailer that was located at a temporary job site (KB Homes - "The Cove" construction site, located at the corner of Warren Road and Cottonwood in San Jacinto, CA). Three of the four construction trailers at this job site had been broken into over the same time period - the security metal plates (covering the locks to the doors) had all been pried open and the locks to the doors were cut off and were removed from the site. The theft occurred sometime between 1130 on November 23, 2005 (when the gauge user secured the gauge inside the construction trailer) and 0722 on November 28, 2005 (when the gauge user returned to the job site and discovered the theft). The last leak test for this gauge was performed on January 4, 2005 and was negative for removable contamination. The licensee contacted the San Jacinto Police Department to report the theft. They will also post a $1000 reward for the gauge in the local paper." "CA NMED #: XCA-824" * * * UPDATE FROM D. KRAJEWSKI TO W. GOTT AT 1925 ON 03/02/06 * * * The gauge was located about a week ago and returned to the owner Leighton and Associates. The gauge was not damaged. A leak test was performed and the results are pending. Local law enforcement are still investigating. Notified R4DO (Whitten), NMSS EO (Flanders), emailed to ILTAB and Mexico. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-12-01
42171 | -1 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-11-27 05:30 | 2005-11-27 11:11 | 2006-01-26 | LOSS AND RESTORATION OF BACK-UP INSTRUMENT AIR TO FEEDWATER CONTROL VALVES "Event: "At 0530 hours on 11/27/2005, while in Mode 3 following a Unit 2 refueling outage, it was discovered that the nitrogen backup supply to 2FDW-315 and 2FDW-316 was valved out. 2FDW-315 and 2FDW-316 are the emergency feedwater (EFW) control valves which function to regulate steam generator level on a loss of main feedwater event. Motive force to these valves is normally supplied by instrument air and nitrogen provides backup to instrument air in the event that instrument air becomes unavailable. At 0530 hours on 11/27/2005, both EFW flow paths were declared inoperable and Technical Specification 3.7.5, Conditions B and E were entered. Condition E of TS 3.7.5 specifically deals with the inoperability of two EFW flow paths. The Required Action is to initiate actions to restore one EFW flow path to operable status, immediately. "Initial Safety Significance: "2FDW-315 and 2FDW-316 are the control valves for the Unit 2 'A' and 'B' steam generators, respectively. These valves must be able to function in order to control steam generator level during an event where main feedwater is lost. The motive force for these valves is normally instrument air. However, in the unlikely event where main feedwater is lost, and instrument air is unavailable, these valves rely on a nitrogen backup to supply their motive force. The events where this nitrogen backup is credited are a station blackout (SBO) and a loss of instrument air. While nitrogen backup to 2FDW-315 and 2FDW-316 was unavailable between 0530 hours and 0710 hours on 11/27/2005, it is reasonable to assume that the ability to remove decay heat would have been available. In the case of a loss of instrument air, 2FDW-315 and 2FDW-316 fail open, with the motor driven EFW pumps providing EFW supply to both steam generators. In this case, the Emergency Operating Procedure (EOP) provides guidance to realign EFW through the electric powered startup control valves. Should this realignment attempt fail, the EOP provides further guidance to control EFW flow by manually throttling closed on 2FDW-315 and 2FDW-316. In the event of an SBO, power to the instrument air compressors would be lost, resulting in a loss of instrument air header pressure. The motor driven EFW pumps would be unavailable, however, the turbine driven EFW pump would automatically start and provide EFW flow. As with the loss of instrument air event, 2FDW-315 and 2FDW316 would fail open. The EOP provides guidance to dispatch operators to manually throttle closed on these valves to control flow to the steam generators. Additionally, while not credited for this event, Oconee has diesel driven air compressors which auto start on low instrument air pressure and supply the instrument air header. Also, in the event of a SBO, the Standby Shutdown Facility (SSF) is manned within 10 minutes of event initiation. The SSF is a SBO coping facility with a dedicated diesel generator and the pumps and valves necessary to supply and control steam generator feed in the event of an SBO. "Corrective Action(s): "At 0702 hours on 11/27/2005, nitrogen was realigned to 2FDW-316 and TS 3.7.5, Condition E was exited. At 0710 hours on 11/27/2005, nitrogen was realigned to 2FDW-315 and TS 3.7.5 Condition B was exited." The licensee is investigating the cause of the valve line up problem. The licensee notified the NRC Resident Inspector. * * * RETRACTION OF EVENT RECEIVED BY JOE O'HARA FROM TRACY ROLAND AT 1333 0N 1/26/06 * * * "After detailed review of this event, it was concluded that Technical Specification 3.7.5 limiting conditions for operation were met at all times during this event. Control valves 2FDW-315 and 2FDW-316 fail open on loss of air/nitrogen by the spring return design of the actuators. Therefore, the required flow path would not have been lost due to the failure of normal air supply and the isolation of nitrogen supplies to the actuators. It has been further concluded that all throttling functions of these control valves could have been performed manually by use of a local handwheel on each valve actuator. Appropriate procedure guidance exists to operate the system with these valves failed open until the operators can access the local handwheel and take local control. Therefore, the valves and the associated flow paths were operable during this event. As a result of this determination, no reportability criteria under 50.72 and 50.73 apply to this event and the associated event report is hereby retracted." The licensee notified the NRC Resident Inspector. R2DO(Payne) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2005-11-27
42170 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-11-25 21:20 | 2005-11-26 04:09 | 2005-11-26 | OIL SPILL ON PLANT SITE "On 11/25/05 at approximately 2120 hours, an oil spill occurred on plant site. During normal shift rounds, Power Operations observed oil coming from the overflow of an oil storage tank associated with the X-530 345KV under ground oil pumping station. A pump failed to shut off as required, allowing oil to be pumped to the storage tank until operator intervention shut down the pump. "At 0020, 11/26/2005 hours, The Plant Shift Superintendent notified the National Response Center and the Ohio EPA that a Reportable Quantity (RQ) of insulating oil (Polybutene) was released to the ground. No material left the immediate area and clean-up of the spill is currently in progress. "UE2-RA-RE1030, Appendix D, section P requires a 4 hour NRC event when other government agencies are notified." The licensee reported this event to the National Response Center as report number 780580. The licensee notified NRC Region 2 (Hartland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2005-11-26
42169 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-11-25 16:24 | 2005-11-25 18:10 | 2005-11-25 | UNUSUAL EVENT DECLARED DUE TO DANGEROUS LEVELS OF CARBON DIOXIDE FOLLOWING A CARDOX RELEASE "At 16:09 CST, the Control Room received a fire alarm on the Main Generator and actuation of the fire protection system. The Main Generator is protected by Carbon Dioxide for fire protection purposes. There was no evidence of a fire at the Main Generator. Air sampling of the Cardox Storage Tank Room indicated Carbon Dioxide levels at life threatening levels. An Unusual Event was declared at 1624 CST based on Emergency Action Level Chart P 'External Events and Chemical Spills' for a release of toxic or flammable gas on site AND portable monitors indicate toxic or explosive concentrations at life threatening levels of the gas near the spill area." There were no personnel injuries reported and the licensee is conducting a survey to account for personnel. Ventilation of the affected areas is in progress to reduce the toxic gas levels. The licensee informed state/local agencies and the NRC Resident Inspector. * * * UPDATE AT 2105 EST ON 11/25/05 FROM SCOTT CIESLEWICZ TO S.SANDIN * * * "[The] declaration of Unusual Event has been terminated [at 1915 CST on 11/25/05]. The Control Room received a fire alarm on the Main Generator and actuation of the fire protection system. The Main Generator is protected by Carbon Dioxide for fire protection purposes. There was no evidence of a fire at the Main Generator. [The] source of Carbon Dioxide gas has been isolated. The area with [the] life threatening concentration of Carbon Dioxide has been ventilated. [The] plant no longer has any areas with [a] toxic concentration of Carbon Dioxide at the life threatening levels. Normal plant operation continues." The licensee is continuing their investigation into the cause of the Cardox discharge. The licensee informed stat/local agencies and the NRC Resident Inspector. Notified R3DO(Skokowski), NRR (Gillespie), IRD (Leach), DHS (Akers) and FEMA (Ligett). | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Startup; FMode1: Startup | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-11-25
42168 | 0 | NUCLEAR LOGISTICS INC |  |  |  |  | 2005-11-23 | 2005-11-23 15:54 | 2005-11-23 | PART 21 FROM NUCLEAR LOGISTICS INC CONCERNING POTENTIALLY DEFECTIVE MICROLOGIC TRIP UNITS The following information is provided on a potential defect in accordance with 10CFR Part 21, paragraph 21.21(b). NLI [Nuclear Logistics Inc] does not have the capability to perform the evaluation to determine if a defect exists. NLI has supplied safety related breakers with the Micrologic trip units only to First Energy-Beaver Valley and PSEG-Hope Creek. Both of these plants are aware of the issue and the corrective actions described below. The basic component that contains a potential defect is the Micrologic trip device installed in Square D series NT and NW low voltage switchgear breakers. The nature of the potential defect is as follows: - Under certain combinations of operating conditions, the trip unit spuriously trips the breaker. The conditions that cause the spurious trip are starting a motor directly by breaker closure (no starter in the circuit) and system transients that have not been defined. The reported spurious trips are as follows: - PSEG-Hope Creek has Square D NW series breakers installed. One spurious trip was identified in over 1000 motor starts using these breakers in 7 safety related applications that start motors directly. - First Energy-Beaver Valley has Square D NT and NW series breakers installed. One NT breaker installed in a non-safety application had multiple spurious trips upon motor starting. - There are no other reported spurious trips of breakers at PSEG-Hope Creek or First Energy-Beaver Valley. Spurious trips in other facilities have been reported to Square D. - NLI is not aware of the installation of Micrologic trip devices in safety related applications in other nuclear plants in the United States. The following actions and corrective action that has been taken: - Root cause analysis and testing has been performed by Square D and NLI. It was determined that the spurious trip was due to a combination transient voltages during motor start and a breaker configuration that lasts approximately 100ms during breaker closure. - The NT breaker was determined to be more sensitive to the spurious trip than the NW breaker. - The reported spurious trip rate for the Micrologic trip units installed worldwide is estimated at approximately 0.05%. - A modification was developed and tested to prevent the susceptibility of the trip unit. This modified design will be implemented on the existing breakers and all future units. NLI is working with the impacted utilities to replace the existing trip units. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2005-11-23
42167 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-11-23 12:30 | 2005-11-23 14:39 | 2005-11-23 | AGREEMENT STATE REPORT - RADIOACTIVE CONTAMINATION ON RADIOGRAPHY CAMERA The State reported that a licensee, Kooney X-Ray Inc., shipped a radiography camera (Model #150; S/N 197) to QSA Global in Baton Rouge, LA, for replacement of the iridium-192 camera source. When the camera arrived and was inspected at QSA Global, low-level radioactive contamination was found on the camera. A wipe test (swipe area not specified) revealed a contamination level of 0.0059 microcuries. The acceptance limit for QSA Global is 0.0050 microcuries. QSA Global believes that the contamination is from depleted uranium shielding in the camera S-tube and not from the currently installed iridium-192 source. Kooney X-ray has requested that QSA Global return the camera. Kooney plans to have the camera S-tube repaired as necessary. The State reported that the contamination was confined to the camera and this event did not result in any personnel or uncontrolled contamination on any other items. Texas Report Number 8278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-28
42166 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2005-11-23 11:10 | 2005-11-23 13:13 | 2005-11-23 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via email: "On the morning of November 23, 2005 at 11:10 am, [the] Radiation Safety Officer for S&ME, Inc. of Pelham, Alabama notified the [State] that their 2003 Ford F-150 truck with a CPN model MC-3 moisture density gauge was stolen in the Lakeshore Drive area of Birmingham, Alabama. S&ME, Inc. is authorized to possess and use radioactive material under their Alabama Radioactive Material License No.1273. The event had occurred less than one hour from [the licensee's notification] call and the Birmingham Police Department had been notified and were in route. The stolen gauge was identified as a CPN model MC-3, serial number M300405612, with 10 millicuries of Cs-137 (sealed source serial number 1148GC), and 50 millicuries of Am-241:Be (sealed source serial number 7139NE). [The licensee] indicated that the gauge transport case was chained to the bed of the pickup. [The licensee] indicated that the truck contained other valuable equipment including a cement mixer. [The licensee] is presently in route to the site of the event. This is all the information that [the State] has at this time." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2005-11-28
42165 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-11-22 12:05 | 2005-11-22 15:54 | 2007-04-02 | IMPROPER CRITICALITY SPACING FOR WASTE DRUM "At 1205 CST, on 11-22-05 the Plant Shift Superintendent was notified that during waste drum remediation activities, a drum was discovered that was in violation of one leg of double contingency. Drum #39666W has been determined to contain up to (deleted) g (grams) U235 exceeding the allowed (deleted) gram limit for NCS Spacing Exempt drums. This drum was previously located in an NCS (Nuclear Criticality Safety) Spacing Exempt storage area in violation of NCSA WMO-001 requirements. The drum was moved to the C-335 storage area under an approved Remediation Guide which established a safety basis for the movement of drums that had been roped off and posted per earlier direction. This drum is currently stored in a Temporary Fissile Storage Area maintaining a minimum 2 foot edge-to-edge spacing under NCSA WMO-001, which maintains double contingency." SAFETY SIGNIFICANCE OF EVENTS "While the (deleted) gram U235 limit was exceeded for this drum; DAC-832-2A1280-0001 demonstrates that drums containing less than (deleted) grams U235 in an NCS Spacing Exempt array are subcritical. The storage area is roped off and posted to prevent the addition of fissile material to the area; therefore another upset would be required before a criticality is possible." POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR) "This drum is currently stored in the Temporary Fissile Storage Area under NCSA WMO-001, meeting double contingency. In order for a criticality to occur, two independent, unlikely, and concurrent events would have to occur." CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.) "Double contingency is maintained by implementing two controls on mass." ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS) "The drum has been determined to contain (deleted) grams U235. Calculations performed demonstrate that drums containing less than (deleted) grams U235 each, in an NCS Spacing Exempt array are subcritical." NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES "Although the drum contains greater than the WMO-001 limit of (deleted) grams U235 for NCS Spacing Exempt drums, it has been shown to be less than (deleted) grams U235 based on independent sample results. Calculations performed demonstrate that drums containing less than (deleted) grams U235 each, in an NCS Spacing Exempt array, are subcritical. Therefore, an additional process upset (i.e., spacing upset) would be necessary in order to have a criticality. Therefore, while the drum contained greater than (deleted) grams U235 in the spacing exempt array, the array has been shown to be subcritical for drums containing less than (deleted) grams U235 thus maintaining one leg of double contingency." CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED "At the time of discovery, the drum was being stored according to NCS approved spacing controls. The drum will continue to be handled according to approved controls until the U235 mass can be reduced to meet the NCS Spacing Exempt criteria per NCSA WMO-001. The NRC Senior Resident Inspector has been notified of this event." See Related Event Report #40700. * * * UPDATE 1802 EST ON 2/13/06 FROM K. BEASLEY TO S. SANDIN * * * "At 1100 [CST], on 02-13-06 the Plant Shift Superintendent was notified that two additional waste drums were discovered that exceed the allowed [deleted] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drums are currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. "The NRC Senior Resident Inspector has been notified of this event." Notified R2DO(Ayres) and NMSS (Camper). * * * UPDATE ON 3/20/06 AT 1859 EST FROM B. WALLACE TO HUFFMAN * * * "At 1430, on 03-20-06, the Plant Shift Superintendent was notified that an additional waste drum has been discovered that exceeds the allowed (deleted) gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drums are currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. "The additional drum was determined to contain (deleted) grams U235. Calculations performed demonstrate that drums containing less than (deleted) grams U235 each, in an NCS Spacing Exempt array are subcritical." The licensee notified the NRC Resident Inspector. R2DO (Ernstes) and NMSS EO (Pierson) notified. * * * UPDATE ON 4/20/06 AT 1750 EDT FROM B. WALLACE TO HUFFMAN * * * " At 1130, on 04-20-06 the Plant Shift Superintendent was notified that an additional waste drum has been discovered that exceeds the allowed (deleted) gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drums are currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. "The additional drum (#41663) was determined to contain (deleted) grams of U235." The licensee notified the NRC Resident Inspector. R2DO (Lesser) and NMSS EO (Janosko) notified. * * * UPDATE ON 4/21/06 AT 2040 EDT FROM WALKER TO HUFFMAN * * * "At 1333, on 4-21-06 the Plant Shift Superintendent was notified that seven additional waste drums had been discovered that exceed the allowed (deleted) gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drums are currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. "Seven additional drums (41160W,41161W,41162W,41158W,41159W,40605W.41681W) were determined to contain in excess of the (deleted) gram limit of U235 but less than the (deleted) gram safety limit." The licensee notified the NRC Resident Inspector. R2DO (Lesser) and NMSS EO (Janosko) notified. * * * UPDATE ON 4/28/06 AT 1802 EDT FROM WALKER TO A. COSTA * * * "At 1430, on 04-28-06 the Plant Shift Superintendent was notified that an additional waste drum has been discovered that exceeds the allowed [DELETED] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. "[This] one additional drum, # 43170W was determined to contain in excess of the [DELETED] gram limit of U235 but less than the [DELETED] gram safety limit." The licensee notified the NRC Resident Inspector. Notified R2DO (Landis) and NMSS EO (Giitter). * * * UPDATE ON 10/11/06 AT 1551 EDT FROM WALLACE TO HUFFMAN * * * At 0900, on 10-11-06 the Plant Shift Superintendent was notified that an additional waste drum (#41470W) has been discovered that exceeds the allowed limit (but less than the safety limit) for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. The licensee notified the NRC Resident Inspector. Notified R2DO (Decker) and NMSS EO (Essig). * * * UPDATE ON 10/24/06 AT 1130 EDT FROM K. A. BEASLEY TO MACKINNON * * * At 1000, on 10/24/06 the Plant Shift Superintendent was notified that an additional waste drum has been discovered that exceeds the allowed [Deleted] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. The NRC Senior Resident Inspector has been notified of this event. Notified R2DO (Brain Bonser) and NMSS (Sandra Wastler). * * * UPDATE ON 12/08/06 AT 1604 EST FROM K. A. BEASLEY TO KOZAL * * * At 1140 on 12/08/06 the Plant Shift Superintendent was notified that an additional waste drum (42171W) has been discovered that exceeds the allowed [Deleted] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NSCA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. The licensee notified the NRC Resident Inspector. Notified R2RDO (Lesser) and NMSS EO (Janosko). * * * UPDATE ON 12/18/06 AT 1250 EST FROM B. W. WALLACE TO KOZAL * * * At 1250 on 12/18/06 the Plant Shift Superintendent was notified that 4 additional waste drums (39639W, 42118W, 42488W, & 43521W) had been discovered that exceeds the allowed [Deleted] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NSCA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. The licensee notified the NRC Resident Inspector. Notified R2RDO (Moorman) and NMSS EO (Ruland). * * * UPDATE ON 3/23/07 AT 1602 EDT FROM C. PITTMAN TO JOE O'HARA * * * "At 1345 on 3/23/07 the Plant Shift Superintendent was notified that an additional waste drum (43561W) had been discovered that exceeds the allowed [Deleted] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NSCA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency." The licensee notified the NRC Resident Inspector. Notified R2RDO (Lesser) and FSME EO (Brach). * * * UPDATE 1155 EDT ON 4/2/07 FROM CALVIN PITTMAN TO MARK ABRAMOVITZ * * * The following information was received as an update: "UPDATE 4/02/07 at 0845, on 4/02/07 the Plant Shift Superintendent was notified that an additional waste drum (43557W) has been discovered that exceed the allowed [Deleted] gram limit for NCS Spacing Exempt drums and had previously been located in an NCS Spacing Exempt storage area in violation of NCSA WMO-001. The drum is currently stored in a Temporary Fissile Storage Area under NCSA WMO-001, which maintains double contingency. The licensee informed the NRC Resident Inspector. Notified R2DO(Henson) and FSME(Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2005-11-22
42164 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-11-19 | 2005-11-22 11:45 | 2005-11-22 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via email: "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention) The licensee called the Washington State Department of Health, Office of Radiation Protection emergency line Saturday November 19, 2005 to report a damaged portable gauge. The Office of Radiation Protection Emergency Response Duty Officer called the supervisor of the Radioactive Materials Section with the information who drove to the incident site to access the situation and monitor for radiation. Radiation readings were normal for a Troxler gauge. "The Licensee provided a statement of the event by the operator. In it the operator said when all the contractor personnel left the area for lunch no equipment was running. Thinking everything was OK; the operator walked to her car for lunch and left the gauge in place. The gauge was not in use. When contractor personnel began returning to the site the operator followed. The operator heard equipment start up and was approximately 50 feet away when a moving piece of equipment backed over the gauge. "The operator called the company RSO and 911 to notify the local fire department. The area was cordoned off to keep personnel away. The operator then removed the shipping and emergency papers and made calls to the State Department of Health who responded to the scene of the incident. The gauge was taken to the licensee's lab in nearby Fife, Washington before being taken to their licensed storage location in Bellevue, Washington. "To prevent reoccurrence, gauge operators have been instructed by the RSO to be with in a few feet of the gauge when it is in an exposed location. The Licensee has suspended for a week without pay the operator in this incident. Notification Reporting Criteria: WAC 246-221-250 Notification of Incidents. Isotope and Activity involved: 8 mCi of Cesium 137, and 40 mCi of Americium 241 Beryllium. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None expected. "Lost, Stolen or Damaged? (mfg., model, serial number) : Troxler, model 3430, serial number 26287. "Disposition/recovery: The gauge was placed back in the manufactures transport case and returned to the licensed storage location in Bellevue, Washington. A licensed technical service provider was contacted and the gauge is being held for pick up and disposal by the service provider. "Leak test? None reported post incident. Last Leak Test performed on September 8, 2005. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) NA Release of activity? None found. "Activity and pharmaceutical compound intended: NA Misadministered activity and/or compound received: NA Device (HDR, etc.) Mfg., Model; computer program: NA Exposure (intended/actual); consequences: NA Was patient or responsible relative notified? NA Was written report provided? NA Was referring physician notified? NA Consultant used? No." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-11-25
42163 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2005-11-21 | 2005-11-22 10:03 | 2005-11-22 | IOWA AGREEMENT STATE REPORT - MISSING STATIC ELIMINATOR The licensee notified the State that on 11/21/05, a static eliminator was discovered missing. The eliminator is a Model P-2021 NRD Static Eliminator, Serial No. A2DT581, containing Po-210 with an original activity of 10 milliCuries. The licensee continues to investigate the loss. * * * UPDATE FROM STATE (N. FARRINGTON) TO M. RIPLEY 1040 EST 11/22/05 * * * The licensee notified the State that the missing static eliminator was found 11/22/05 in the area where it was supposed to be in, but unexpectedly under a workbench, and therefore originally missed. Notified R3 DO (Skokowski), NMSS (G. Morell), and TAS (email). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2005-11-25
42162 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2005-11-21 14:15 | 2005-11-21 18:54 | 2005-11-21 | POSTULATED FIRE SCENARIO AFFECTING REACTOR MAKEUP FROM A CHARGING PUMP "On November 21, 2005, continued engineering evaluation determined that the Beaver Valley Power Station Unit No. 1 (BV-1) charging pump used to provide make-up to the Reactor Coolant System (RCS) may not perform its credited safety function during all postulated fire scenarios. This potential issue was first identified by a condition report on November 18, 2005. The BV1 Primary Plant Component Cooling Water System (CCR) is not credited during any postulated fire scenario. However, two postulated fire scenarios were identified where the absence of CCR could lead to elevated temperature of the water entering the charging pump suction, which could result in pump cavitation and subsequent pump damage. One scenario involves continued normal letdown entering the Volume Control Tank (VCT) at elevated temperatures raising VCT outlet water temperatures above 250 degree Fahrenheit which then goes to the charging pump suction. Another scenario involves elevated suction temperatures during a minimum flow scenario when charging flow to the RCS may be normally isolated by procedure. "Hourly fire tours were immediately initiated as interim measures on November 18, 2005 in applicable areas to reduce the risk of an initiating fire to support continued plant operation. Plant procedure changes are being developed which will address these two scenario issues. These plant procedure revisions, expected shortly, will return the plant into compliance with the current fire protection licensing and design bases. Preliminary engineering evaluation also determined that the complete loss of RCS make-up during the two identified scenarios will not lead to core damage. "This event is reportable pursuant to 10 CFR 50.72(b)(3)(v)(A) since the make-up function to the RCS may not be available during a postulated fire event which is credited for maintaining the reactor in a safe shutdown condition. The Beaver Valley Power Station Unit No. 2 (BV-2) Component Cooling Water System is credited and evaluated in its fire design bases. BV-2 operator action currently exists to protect the BV-2 charging pump during a fire event. "The NRC resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2005-11-21
42161 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2005-11-21 10:42 | 2005-11-21 17:42 | 2005-12-20 | DIVISION 3 EMERGENCY DIESEL GENERATOR DECLARED INOPERABLE "The Division 3 Emergency Diesel Generator (EDG) was declared INOPERABLE following a trip during a routine monthly surveillance run. As soon as the Division 3 EDG was at full load it tripped off line (output breaker tripped). The Division 3 EDG supplies electrical power to the High Pressure Core Spray System in the event of a loss of offsite power. "No problems occurred on the Division 3, 4160 volt, safety related bus. "This event is being reported in accordance with 10CFR50.72(b)(3)(v)(B), Event or Condition That Could Have Prevented Fulfillment of a Safety Function for a single-train system failure. "The NRC Resident inspector has been notified." * * * THIS EVENT IS BEING RETRACTED ON 12/20/05 AT 1557 * * * "Subsequent trouble-shooting and testing determined that the cause of the engine trip on 11/21/05 was an invalid high coolant temperature trip signal. This trip is bypassed during a Loss of Coolant (LOCA) initiation of the system, therefore, it was determined that the EDG would have been able to perform its safety function during a LOCA. Following a Loss of Offsite Power (LOOP), reactor water level is expected to reach Reactor Pressure Vessel (RPV) Water Level Low Low (Level 2) within 30 seconds of the initiating signal. Once Level 2 is reached, both the EDG and the LOCA Trip bypass signals are actuated. It was determined that the bypass would have occurred prior to the high coolant temperature trip. Based on the above, it was determined that the Division 3 EDG would have been fully capable of performing its safety function under both LOCA and LOOP. The Division 3 EDG was restored to an operable condition at 0214 on 11/22/05. "The NRC Senior Resident Inspector has been notified." Notified R3DO (H. Peterson). | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2005-11-21
42160 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-05-22 | 2005-11-21 15:16 | 2005-11-21 | AGREEMENT STATE REPORT - STOLEN TRITIUM EXIT SIGNS The State provided the following information via facsimile: "Safety Light shipped 15 self illuminating exit signs to Fagen, Inc. on April 14, 2003 with serial numbers 220369 - 220383. The signs were [Safety Light Corp] model SLX-60 with 11.5 curies [of Tritium (H-3)] in each. Fagen, Inc. was the contractor for Kaapa Ethanol, LLC In Minden, Nebraska. Fagen, Inc. staff suspect that five signs were stolen on May 22 or 23, 2003 from a trailer that they kept supplies in. They [Fagen, Inc] then ordered six additional signs (five for the ones suspected stolen and one needed for an additional area needing a sign). Safety Light shipped the six signs on June 17, 2003 with serial numbers 211313-211318. Kaapa Ethanol, LLC took over the plant in January of 2004. When Kaapa did a complete inventory of the signs in 2005 they could not locate all of the signs. After a number of emails and phone calls it was determined that in addition to the unreported five signs that were missing in May of 2003, one additional sign from the April 14, 2003 order and three from the June 17, 2003 order were also missing. They believe that the signs were taken/stolen the first week of January 2004. Kappa Ethanol staff does not believe that the nine missing signs were ever installed." Serial numbers of stolen exit signs: 220369, 220370, 220371, 220372, 220373, 220380, 211315, 211316, 211317. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2005-11-24
42159 | 0 | UNITED STATES AIR FORCE |  |  |  |  | 2005-09-06 | 2005-11-21 14:12 | 2005-11-21 | LOST NICKEL-63 SOURCE A representative for the Air Force Master Material License reported that a device containing a 10 millicurie Nickel-63 source is lost. The device containing the source is a Ion Track Vapor Tracer. The device was last inventoried in storage at Patrick Air Force Base at Cape Canaveral, Florida. The date of the last confirmed inventory of the device and source was in 2002. The Air Force has exhausted all its efforts to locate the source and declared it permanently lost following the an inventory in August 2005. The source serial number is s/n 01024892704. Other sources kept at the same storage location as the missing device have been moved to a more secure location. The licensee does not believe that the device was stolen. The licensee has notified NRC Regional Inspector (R. Browder). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-11-21
42158 | 0 | STS CONSULTANTS LTD |  |  |  |  | 2005-11-20 09:00 | 2005-11-20 10:25 | 2006-11-08 | STOLEN TROXLER MOISTURE DENSITY GAUGE A Troxler Model 3420 moisture density gauge (nominally 40 milliCi Am-241/Be and 8 milliCi Cs-137) was stolen from the back of an employee technician's pickup truck while parked in a parking garage in Minnetonka, MN. The gauge was in its case inside a gang box. The gang box was double-locked and secured to the truck by cables or chains attached to the gang box handles which were found cut. The licensee's license number, the gauge serial number, and the address of the parking garage were not available at the time of the report. The licensee stated that the theft has been reported to the local police department. There are no current plans for either a reward or a press release. * * * UPDATE FROM C. VERKE TO W. GOTT AT 1522 ON 11/08/06 * * * Minnesota became an Agreement State after the original report was made. The State provided the following information via facsimile: "On November 20, 2005 the Troxler gauge, serial number 29535 was taken from a locked pickup truck. The locked transport case had been attached to the pickup truck bed by two chains. The pickup truck was in a secured garage of an apartment building in Minnetonka. The police report states that the garage had been ransacked and this was not the only item taken. The stolen gauge was noticed by the owner of an automotive repair business approximated 9 months later in the back area of the business. He thought that someone would come and claim it. At a point approximately 3 months later, when no one had picked it up, the business owner asked a friend of his who was having his vehicle worked on and was a member of the Metropolitan Transit Company if he knew what it was. At this point, the Minnetonka police were called, discovered the owner and returned it to senior project manager at STS Consultants, Ltd. "The supervisor of the Radiation Control unit for the Minnesota Department of Health, Environmental Health Division was notified on the recovery of the gauge by NRC Region 3. He requested that a follow-up inspection be conducted. "On November 6, 2006, the inspectors went to STS Consultants, Ltd. to survey a recovered Troxler gauge, serial number 29535, that had been stolen one year ago. Upon arrival they met with the senior project manager. The senior project manager showed the inspectors the gauge that was already out of the transport case. He was getting ready to do the leak testing. Meter readings were taken using a Ludlum 2241-3 meter, serial number 220224. Wipes were read with a Radiation Alert Inspector serial number 5588 on 11/7/06. The project manager did perform the leak test while the inspectors were there. The gauge will be sent in for repair and calibration. The gauge will be sent to a company in Sheboygan, Wisconsin. "When the senior project manager received the gauge back from the Minnetonka police department, he found: The transport case locks were broken; The serial number of the gauge had been ground off; and The trigger mechanism on the handle did not function properly. He did discover the Am-Be source holder was still intact. With the trigger mechanism not working, he was not sure if the Cs 137 source was still intact. "As a result of the meter readings and wipe results, the conclusion by the inspectors was that there was no contamination or leakage from the two sources contained within the gauge. There was no indication of any further follow-up needed." Notified NMSS EO (G. Morell), R3DO (J. Cameron), emailed to ILTAB and faxed to Canada (CNSC). THIS MATERIAL EVENT CONTAINS A "LESS THAN CAT 3" LEVEL OF RADIOACTIVE MATERIAL Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-11-20
42157 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-11-19 15:51 | 2005-11-19 20:21 | 2005-11-19 | UNPLANNED DIESEL GENERATOR STARTS ON A VAILD BUS UNDERVOLTAGE SIGNAL "On November 19, 2005 at 1551 Pacific Standard Time Diablo Canyon Unit 2 [was] in Mode 1 (Power Operation) at approximately 100% power when the 230kv offsite power supply breaker (#212) opened. Diesel generators 2-1, 2-2, and 2-3 auto-started on a valid bus undervoltage signal. "The immediate cause of the event was the opening of the 230kv breaker (#212) due to a valid (but unintentional) startup transformer 1-1 sudden pressure switch activation due to maintenance being performed on the Unit 1 Startup Transformer 1-1. "All equipment performed as expected." None of the diesel generators picked up load since the buses remained energized. The safety buses were powered by offsite power. Unit 1 is in a refueling outage and was not adversely affected. The diesel generators are currently being returned to a standby condition. The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-11-19
42156 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2005-11-18 20:00 | 2005-11-19 11:54 | 2006-02-16 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE OF A RADIOGRAPHER At 2000 on 11/18/05 during a radiography job at P2S in Sand Springs, OK, a radiographer received a 23 Rem calculated dose. He went out to change the camera film when he thought his assistant had fully retracted the source. The radiographer was in front of the camera for approximately 3 minutes. The licensee stated that the cause of the overexposure was miscommunication. When the radiographer was on his way to the camera he set down his radiation detection instrument and answered a cell phone call. At the same time the assistant who was responsible for retracting the source was sending a text message on his cell phone. The radiographer's alarming rate meter was turned off. The camera was a SPEC Model 150 with a 66 Curie Iridium-192 source. The camera was tested after the event and found to be in good operating condition. Both the radiographer and the assistant have been suspended pending further investigation. The dosimeters of the individuals have been sent to be read and readings should be available on 11/21/05. The licensees radiation safety officer made the report to the state after taking both individuals to the hospital for blood tests as a precautionary measure. On 11/21/05 the state will investigate this incident further at the jobsite. * * * UPDATE FROM STATE (M. BRODERICK) TO M. RIPLEY 1515 ET 02/16/06 * * * The results of a chromosome analysis performed on a blood sample indicated that the best estimate of the radiographer's exposure as a result of the event was 4 Rem (with a 95% confidence interval of 0 - 17 Rem). The licensee states that the blood analysis results are in agreement with the radiographer's dosimetry, and the radiographers dose for the year is calculated to be 6.9 Rem. Notified R4 DO (D. Graves) and NMSS EO (G. Morell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2005-11-23
42155 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2005-11-18 21:19 | 2005-11-18 23:33 | 2005-11-18 | LOST POWER TO CIRCULATING WATER DILUTION PUMP ELEVATING DISCHARGE TEMPERATURES TO BAY At 2235 the licensee notified the New Jersey Environmental Protection (NJEP) Agency that their circulating water discharge temperature to Barnegat Bay was elevated. This is due to the fact that the licensee lost power to their non-safety related circulating water dilution pump. The licensee is currently working to restore power to the dilution pump and reducing reactor power to minimize the temperature difference between the discharge water and Bay water. The licensee notified the NRC Resident Inspector. | 89 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-11-18
42154 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-11-17 17:45 | 2005-11-18 19:53 | 2005-11-18 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via email: "Event Report # WA-05-062 "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "STATUS: new "Licensee: USKH, Inc. "City and state: Spokane, Washington "License number: WN-I0409-1 "Type of license: Portable Gauge "Date of event: 17 November 2005, Called in 5:45 PM. "Location of Event: Spokane, Washington "ABSTRACT: The license's Radiation Safety Officer reported that sometime between 2 and 5 PM a Troxler, Model 3411B, moisture density gauge, Serial Number 5541, was stolen out of the operator's transport vehicle parked in a Diamond Parking lot adjacent to the 'Flour Mill' where the company's offices are located at 621 W. Mallon Avenue, Suite 309, Spokane, Washington. A police report was filed on 17 November 2005 but Spokane police declined to investigate the scene. "Bolt cutters were used to liberate the gauge/transport box from 2 separate chains with a padlock on each attaching the box to the rear of the operator's pick-up truck. The parking lot (of over 75 vehicles) has an attendant who did not observe the theft. "The operator appears to have violated at least one DOH requirement that may have contributed to the theft to the device. Department of Health Order, dated 2 December 2002, requires that when the licensee's portable gauge is not physically under the control of the operator that the device must be covered or carried in such a way that the passer-by cannot see the device. "Another potential contributing factor to the theft, is that the operator was planning on transporting the gauge to his residence to recharge and take it to the work site the next morning because the work site was halfway between the operator's residence and the primary storage location. Preliminary information indicates that the work site is within 50 miles of the primary storage location. This is still under investigation. The licensee will be cited for at least one violation as a result of the event, and corrective actions will be discussed with the licensee. "The event is currently under investigation. This report will be updated to include any new findings. No media attention noted at present. "What is the notification or reporting criteria involved? WAC 246-221-240 Reports of stolen, lost or missing radiation sources "Activity and Isotope(s) involved: 296 megaBq (8 millicuries) Cesium-137 and 1480 megaBq (40 millicuries) Americium 241/Beryllium. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) N/A "Lost, Stolen or Damaged? STOLEN (mfg., model, serial number) noted above "Disposition/recovery: pending "Leak test? Unknown "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) pick-up truck with no cap "Release of activity? N/A "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided? Pending "Was referring physician notified? N/A "Consultant used? N/A" Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-11-23
42153 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2005-11-17 23:00 | 2005-11-18 01:16 | 2005-11-18 | LOSS AND RECOVERY OF COMMUNICATIONS The Emergency Notification System (ENS) was lost due to the loss of offsite telephone communications. Troubleshooting to determine the cause is in progress. Offsite telephone communications were restored at 0040 EST on 11/18/05. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-11-18
42152 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-11-17 16:51 | 2005-11-17 20:53 | 2006-01-13 | BOTH TRAINS OF SHIELD BUILDING VENTILATION DECLARED INOPERABLE DUE TO MISSING CLAMPS "At 1651 on 11/17/2005 both trains of Shield Building Ventilation were declared out-of-service because it was identified that Shield Building penetrations 31 and 36NW flexible boot seals were not clamped per the design drawing. Since there is no documentation to show that Shield Building Ventilation would be able to perform its function during a design basis event with no clamps installed, Shield Building Vent was declared inoperable. Clamps have been installed and the penetrations were returned to the design configuration. At 1810 CST Shield Building Ventilation was declared Operable." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM MALONEY TO HUFFMAN AT 1105 EST ON 1/13/06 * * * The licensee has performed an engineering review and determined that the boot seals would have been capable of performing their design basis function without the clamps installed. Consequently, this event is no longer considered reportable and is being retracted. The NRC Resident Inspector has been notified by the licensee. R3DO (O'Brien) has also been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2005-11-17
42151 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-11-17 08:30 | 2005-11-17 16:25 | 2005-11-17 | INITIAL PART 21 NOTIFICATION - PRIME MEASUREMENT PRODUCTS, MODELS 763 & 763A PRESSURE TRANSMITTERS AND MODEL 764 DIFFERENTIAL PRESSURE TRANSMITTERS The following information was received via facsimile: "On 11/2/05 SGT LLC, primary contractor for Steam Generator replacements at Callaway Plant, received notification from PRIME Measurement Products, (formerly ITT Barton) of a manufacturing defect in Model 763, 763A, and 764 pressure transmitters involving use of Zener diodes that were not in compliance with purchase specifications. Subsequently, on 11/3/05 SGT LLC notified AmerenUE Callaway Plant of the potential manufacturing defects involving the aforementioned transmitters. These transmitters provide input to steam generator level indication and control functions. "The notification provided by PRIME stated the purchasing specifications required JANTX components, but in some cases commercial variations of the required parts were used to manufacture some transmitters. This condition was potentially reportable under 10 CFR 21, depending on the specific application at facilities using these instruments manufactured by PRIME Measurement Products. The following is a summary of the information obtained from PRIME Measurement Products: 1. This notification involves 76 specific transmitters manufactured between 2/10/04 and 9/19/05. 2. Each transmitter contains two Zener diodes which may not comply with purchase specifications. 3. The JANTX Zener diodes are different in appearance with respect to the commercial variations. Some JANTX Zener diodes used in the recent past have bodies that are solid orange or light blue in color or clear glass. The commercial Zener diodes in question have a clear glass body. The commercial Zener diode is larger (0.095" diameter X 0.275" long) than the smaller JANTX Zener diode (0.072" diameter X .155" long). 4. The existence of the commercial Zener diode can be confirmed by removal of the transmitter electronics cover and observing the Zener diodes at locations CR2 and CR3, as shown on manufacturer supplied circuit board drawings. 5. The Zener diodes are not field replaceable, as it is necessary to electronically reestablish the calibration zero which will likely necessitate replacement of a calibration resistor. This calibration resistor is located in a temperature sensitive portion of the electronic circuit and requires thermal performance validation. 6. PRIME believes that transmitters with commercial Zener diodes that are currently installed in a plant can be relied upon to continue to operate and perform their safety-related function in the event of an accident. This belief is based on the facts that the commercial Zener diodes installed in any transmitter have been shown to be functional at the accident maximum sustained temperature and because the radiation effects on commercial Zener diodes are known to be within the margin of the original Barton qualification. "SGT LLC purchased 22 of the suspect transmitters for use in the Callaway Plant Steam Generator replacement project. Additionally, 6 suspect transmitters had been supplied directly to Callaway Plant. Physical inspections by SGT LLC and Callaway Plant staff determined 21 of the transmitters had the commercial Zener diodes installed. These transmitters were returned to PRIME where the commercial Zener diodes were replaced with qualified Zener diodes and proper transmitter operation was verified. The affected transmitters have since been returned to Callaway as fully qualified for safety related use in nuclear applications. "On 11 /16/05, Callaway Plant personnel completed evaluations and determined the use of commercial Zener diodes constituted a defect per 10 CPR 21, requiring initial notification to the NRC within two days. Per the information provided by PRIME, all other affected customers have been notified. "The concern was identified while Callaway Plant was shutdown for a refueling outage when the transmitters were installed, and prior to being returned to service. Therefore, no other reporting criteria apply. "The NRC Resident Inspectors have been notified of this issue." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Hot Standby; FMode1: Startup | NON EMERGENCY | 4 | MO | POW |  | 21.21 |  |  |  | 0 | 2005-11-17
42150 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2005-11-17 | 2005-11-17 16:18 | 2005-11-18 | AGREEMENT STATE REPORT INVOLVING LOSS OF PALLADIUM-103 SOURCES On the morning of 11/17/05, Deaconess Health Systems inadvertently discarded a package of twenty-four (24) TheraSeed Palladium-103 Model 200 Implants. Each implant contains a 2.01 mCi Pd-103 source used in the treatment of prostate cancer. The error occurred due to a change in packaging which was not recognized by the recipient. The discarded material was buried at the East Oak Landfill. The licensee does not intend to attempt recovery due to the relatively short half-life, i.e., 17 days, and the small of amount of material involved. The landfill utilizes a portal alarm which did not activate since the material was discarded in it's shielded shipping container. * * * UPDATE FROM STATE (K. SAMPSON) TO M. RIPLEY 0940 EST 11/18/05 * * * The State provided the following additional information via facsimile: "At approximately 1:00 PM on November 17, 2005 the licensee discovered the loss of 24 Theraseed 200 brachytherapy seeds. Each seed contained 2.01 mCi of Pd-103 at the time of the loss. According to the RSO, the manufacturer of the seeds had recently changed the packaging of the material. Prior to the change, the seeds were all packaged in one lead foil tray. However, the licensee had recently received them packed in three trays stacked one atop another in a single box. In this instance when the box was opened only two trays were removed, the box was discarded with the third tray still inside it. Trash receptacles in the hospital were searched, but the missing materials were not found. The local waste hauler and landfill were contacted and it was determined that the trash had already been delivered to the landfill that morning and had been covered. In light of the short half life of Pd-103 and the low energy of the gamma it emits, and the fact that the sources were still within their shielded tray, it was decided not to attempt to locate them at the landfill." Note also that the name of the licensee on the Oklahoma license is Deaconess Health System, LLC doing business as Deaconess Hospital. Notified R4 DO (J. Clark), NMSS EO (G. Morell) and TAS DO (A. Danis via email) Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2005-11-22
42149 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-11-17 10:15 | 2005-11-17 11:57 | 2005-11-17 | SECURITY LOGABLE REPORT INFORMATION CALL - ACCIDENTAL WEAPON DISCHARGE The licensee called to report an accidental weapons discharge inside one of their bullet resistant enclosures (BRE) in the protected area. A security officer had returned from the weapons range. He noticed that his weapon had excess lubrication on it and wanted to functionally test it. The weapon was discharged inside the BRE. No other officers were present. The officer was not injured. The licensee was performing a prompt investigation on the issue. The individual guard was placed on administrative access restriction and sent for a fitness for duty test. The weapon was quarantined. This was a violation of the licensee's procedures and was logged by the licensee as a security logable event. The licensee notified NRC, G. Smith, in Region 1. The licensee also notified the Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 1 | 2005-11-17
42148 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-11-17 00:47 | 2005-11-17 08:55 | 2005-11-17 | LOSS AND SUBSEQUENT RECOVERY OF EMERGENCY RESPONSE DATA SYSTEM Emergency Response Data System (ERDS) was unavailable from 00:47 until 01:51 due to an Emergency Response Data Acquisition and Display System (ERDADS) failure. The problem has been corrected and ERDADS is currently able to supply data to ERDS. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-11-17
42147 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-11-10 17:00 | 2005-11-16 23:33 | 2005-11-16 | WASHINGTON AGREEMENT STATE REPORT - LEAKING SHIPMENT CONTAINER "Licensee: Pacific EcoSolutions LLC (PEcoS) - Richland, Washington "City and State: Richland, Washington "PEcoS Radioactive Materials license Number: WN-I0393-1 "Type of License: Industrial- Radioactive Waste Processor "Date and Time of Event: The licensee (PEcoS) notified the Department of Health on November 10, at approximately 5:00pm. "Location of Event: The leaking container was found on a shipment that arrived at the PEcoS facility at 2025 Battelle Blvd. Richland, Washington "Involved Persons: Pacific EcoSolutions LLC (PEcoS) - Richland, Washington, ADCO Services, Inc.-Tinley Park, Illinois "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "On Thursday November 10, 2005 the Department of Health was notified by the licensee that a shipment from ADCO Services, Inc. arrived at their facility. During offloading of the packages one drum on the shipment was found to be leaking liquid. The leak was not contained to the inside of the closed trailer. Evidence of the leak was also seen on the underside of the trailer's wood floor and undercarriage. The I beam of the trailer was visibly stained. There was no evidence that the container had tipped over. "The shipping papers for this load indicated that the shipping date from ADCO was 29 October 2005 and that the drum contained approximately 21.0 millicuries of tritium. The physical and chemical form is listed as solid NETA Plates. The container was shipped as Radioactive Material - Limited Quantity. The generator of the waste was identified as Agouron Pharmaceuticals located in San Diego, California. "The shipment arrived in Richland and was parked at a local hotel for approximately 5 days prior to arriving at the PEcoS facility. The department identified the location where the trailer was parked and have obtained samples of parking lot material and performed paper smear surveys. The licensee also obtained samples and performed smear surveys. Initial results showed contamination levels in the parking lot and on the frame of the trailer as 3,000 4,000 dpm/100 cm2. The contamination on the trailer floor prior to removal was approximately 118,000 dpm/cm2. "Discussions with ADCO indicated that a container from the same lot of drums was found leaking at the time of shipment preparation. That drum was over-packed (put into a larger drum and filled with sorbent material) and shipped. ADCO had also indicated that the drums from this generator were new and not reconditioned. According to ADCO, the generator of this waste is no longer in business. It was sold to another pharmaceutical company. ADCO also indicated that the containers from this company was picked up in California and trucked to the Illinois facility. The drums were at the Illinois facility for approximately 4-5 months after arrival. "This shipment entered the state of Washington through the Spokane Port of Entry, however personnel at the Port who conducted an inspection of the truck, including the undercarriage did not observe any leakage. "Corrective Actions: "The shipper (ADCO) has been notified that they are not to ship to the state of Washington until further notice. They must submit a root cause analysis, and a quality assurance program acceptable to the department that assures further shipments into the state of Washington will be in full compliance with all applicable state and federal regulations, as well as the PEcoS license. "No known media attention yet. "Notification Reporting Criteria: WAC 246-221-160. "Isotope and Activity involved: Tritium, 7.9039 E+2 MBq (21.362 millicuries). "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None "Lost, Stolen or Damaged? Not Applicable. "Disposition/recovery: Unknown "Leak test? Not Applicable "Vehicle: Not Applicable. "Release of activity ? Exact amount unknown "Activity and pharmaceutical compound intended: Not applicable. "Misadministered activity and/or compound received: Not applicable. "Device (HDR, etc.) Mfg., Model; computer program: Not applicable. "Exposure (intended/actual); consequences: Not applicable. "Was patient or responsible relative notified? Not applicable. "Was written report provided to patient? Not applicable "Was referring physician notified? Not applicable "Consultant used? No." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-11-21
42146 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-11-16 15:30 | 2005-11-16 18:56 | 2005-11-16 | POTENTIAL FAILURE TO MEET REQUIRED RESPONSE TIMES FOR SHUTDOWN OUTSIDE CONTROL ROOM "After a timed walk down of an Off Normal Operations procedure for shut down outside the Control Room, it appears that required response times were not met. This is due to a new assumption that all actions would not function due to plant configuration. Some valve circuits are not protected with a second fuse that is isolated from the control room portion of the circuitry. The only fuse in the circuit may blow during the early part of the event, prior to manipulating the isolation switch on the breaker. Since the fuse could blow, there would be no control power to electrically manipulate the valve and that would cause the operator to go to the 'Response not Obtained' column adding time to the actions taken. "This issue was previously identified at Wolf Creek in 1985 in IE INFORMATION NOTICE NO. 85-09. However, additional research needs to be accomplished as to why some circuits have only one fuse. "Compensatory actions include: "1) A change to the procedure to direct additional actions. "2) An hourly fire watch has been added to the control room." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-11-16
42145 | 0 | LOUISIANA DEPT. OF ENVIRONMENTAL QT |  |  |  |  | 2005-08-24 | 2005-11-16 14:10 | 2005-11-16 | AGREEMENT STATE REPORT - LOST DENSOMETER The following was received via facsimile: "On Wednesday 8/24/05 a densometer (serial number W28901) with a 9.25 mCi source of Cs-137 (serial number DA433) was secured to an iron truck after performing a job. There were multiple trucks that were convoyed in and there were no reports of anything falling off. The path that was taken was Texas 302 to 301 to loop 390 to Highway 79 to I-20 to Industrial drive exit. The truck had a bad transmission and was taken to Peterbuilt for repair that same day. The repaired truck was returned to the Bossier City yard on Thursday 8/25/05. On Saturday 8/27/05 during an inspection of the truck for a job on 8/28/05, it was noticed that the 2 inch densometer was missing. The mounting bracket which held the densometer does not appear to have been compromised however, the lock and densometer were missing. The route that was taken was checked, but the devise could not be located. An award was placed in the local paper on 9/2/05. As of this date the devise has not been located. To prevent reoccurrence, the densometer holder has been relocated from the rear bumper to the front center portion of the bed of the unit. The densometer is secured by means of a hammer union, bar, and lock." Louisiana Report Number: LA050008. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | MAT | [5 empty] | 0 | 2005-11-16
42144 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-11-15 13:30 | 2005-11-16 12:43 | 2005-11-16 | REPORTABLE INCIDENT DUE TO DEVIATION FROM TECHNICAL SPECIFICATION REQUIREMENTS "At 1216 CST, on 11-15-05 the C-333, Unit 4, Cell 8, Process Gas Leak Detection (PGLD) system was declared inoperable by the Plant Shift Superintendent (PSS) in order to perform maintenance. Due to the inoperability of the system, a [Technical Specification Requirement] TSR required continuous smoke watch was put into place according to LCO 2.4.4.1. At 1330 CST a Tornado Warning was issued by the National Weather Service (NWS) for the area affecting the plant and surrounding area that remained in affect until 1400 CST. Based on the NWS warning, radar indications, and visual observations from on-site spotters, the PSS ordered the activation of the plants Take Cover Signal and [Public Address] PA announcements were made instructing the plant population to shelter in their designated 'take cover areas'. Upon activation of the Take Cover Signal, the individual performing the TSR required smoke watch at C-333, Unit 4, Cell 8, discontinued the smoke watch and reported to the 'take cover area' as required by plant emergency procedures. At this time, the PSS entered TSR 1.6.4, 'Conditions Outside TSR' due to discontinuing the TSR required smoke watch. TSR 1.6.4 requires that in an emergency, if a situation develops that is not addressed by the TSR, operations personnel should use their training and expertise to take actions to correct or mitigate the situation. In compliance with the TSR, the PSS instructed the Cascade Coordinator to reduce the operating pressure in the area affected by the Unit 4, Cell 8, PGLD outage, which would place the equipment in a non-applicable TSR mode of operation. Operating pressures were being reduced when the National Weather Service lifted the Tornado Warning at 1400 CST. At this time, the PSS lifted the Take Cover order and the TSR required smoke watch was put back into place at Unit 4, Cell 8 at 1405 CST. At this time the plant came into compliance with TSR LCO 2.4.4.1 and exited TSR 1.6.4. "This event is being reported under the requirements of TSR 1.6.4, 'If emergency action is taken, both a verbal and written notification shall be made in accordance with 10 CFR 76.120'." The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2005-11-16
42143 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-11-16 04:22 | 2005-11-16 09:17 | 2005-11-16 | INCORRECT READING OF HPCI POSITION INDICATING LIGHTS ON CONTROL ROOM PANEL. "At 0422, during a panel tour in preparation for shift turnover, a Reactor Operator identified that both position indicating lights for HPCI-MO-19 were not illuminated. For current plant conditions the closed position indication should have been illuminated. The position indication for this valve is powered from 125 VDC, which also provides control power for the valve operation. Without control power, the valve would not open upon HPCI system initiation. HPCI was declared inoperable. Per the discussion in NUREG 1022, inoperability of a single train system is reportable as an 8 hour report. Per Technical Specifications, RCIC was verified to be operable immediately, and restoration of HPCI to an operable condition is required within 14 days." The licensee indicated that the valve position was always in the correct posture although the panel light did not reflect it true position. This is a 14 day LCO. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-11-16
42142 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2005-10-13 12:00 | 2005-11-15 16:27 | 2005-11-15 | AGREEMENT STATE REPORT FROM MISSISSIPPI "During routine inspection of general licensed devices at Shell Lubricants, it was discovered that the company could not account for two (2) Metorex X-Ray Fluorescence Analyzers. The facility has changed ownership since the last inspection and records were not well maintained of receipt/transfer and leak tests. The licensee conducted a search of the facility after the inspection and did not locate the devices. They also contacted personnel that had been previously employed in the facility as well as the maintenance supervisor, who had no information of the location or disposal of the devices. The Metorex Models were a HEPS X-ray Fluorescence Analyzer, containing a 60 millicurie Curium-244 source, Serial No. 206734, and a LEPS X-ray Fluorescence Analyzer, containing a 40 millicurie Iron-55 source, Serial No. 206777. "Describe clean-up actions taken by DRH: After determining all other radioactive devices were accounted for, DRH helped search for the lost devices, but could not locate them. "Case Closed: No "Enforcement action taken: Investigation ongoing. Licensee cited violations for lost devices and failure to maintain records of receipt/transfer. Also required to send DRH a report about lost devices and corrective actions." Mississippi Report Number: MS-05-004 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2005-11-18
42141 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-11-14 | 2005-11-15 12:00 | 2006-02-01 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The State provided the following information via email: The State of Texas received a call from the Radiation Safety Officer for Terra-Mar Inc. on Tuesday, November 15, 2005, reporting the theft of a moisture/density gauge, Troxler Model # 3430, Serial # 32220, with a 40 milliCurie AmBe source, Serial # 47-28552 and an 8 milliCurie Cs-137, Serial # 750-7360. The licensee went to the gauge storage area of the site on Monday, November 14, 2005, and discovered that the gauge was missing. The licensee checked with personnel to see if any one had removed it from the storage area. When no one acknowledged removing the gauge, the licensee contacted Texas Department of State Health Services (DSHS), Dallas-Ft Worth Department of Public Safety, and the Irving Police Department that the gauge was possibly stolen. The licensee will send in the police report and a written statement to DSHS. The last leak test performed on the missing gauge was performed on July 9, 2005. Texas Report Number: I-8277 * * * UPDATE FROM S. SIMMONS TO J. KNOKE AT 13:28 EST ON 12/12/05. The licensee provided more detail surrounding the missing Troxler gauges and added security measures for the storage area of other gauges. Contact the Headquarters Operations Officer for further information. "The incident report No. from DFW Airport DPS is 050-5143. The DFW DPS is investigating the apparent theft and has assigned a detective to the case. A copy of the police report was sent to DSHS. "On November 17, 2005, licensee installed an additional keyed padlock on the nuclear storage doors and placed a heavy duty chain and lock through the case handles of the remaining gauges. The licensee has also changed the combination code to the entry door of the building. Only the site RSO and one authorized user have access to the building and gauge storage area." Notified R4DO (Johnson) and NMSS (Morell) **** UPDATE ON 02/01/06 AT 1500 VIA E-MAIL FROM S. SIMMONS TO MACKINNON ***** "On Monday, January 30, 2006, I received a call from the RSO for Terra-Mar US Labs, informing the agency that an employee of the company had found the stolen gauge. The gauge was recovered at "First Cash Pawn" located at Wisdom Camp Rd., Duncanville, TX. The agency immediately responded by dispatching an inspector to verify that the gauge was in fact the property of the licensee. Once accomplished, the licensee was notified to recover the property. The gauge is now in possession of the licensee. Law enforcement officials are investigating the possibility of criminal prosecution. Case Close. " R4DO (Runyan), NMSS EO (Greg Morell), TAS (e-mail) & MEXICO (e-mail) notified. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-18
42140 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-11-14 11:41 | 2005-11-14 19:09 | 2005-11-14 | CLADDING FAILURE TO ONE SPENT FUEL ROD FOUND DURING INSPECTION OF SPENT FUEL IN THE SPENT FUEL POOL "On November 14, 2005, WBN was operating at 100% power and an inspection of spent fuel stored in the spent fuel pool (SFP) was being performed. The inspection confirmed that an opening existed in one rod (P9) located in G45 fuel assembly. This assembly is a 17 x 17 Vantage +/Performance + (V+/P+) fuel assembly and it has been used in the core during two previous cycles. The inspection noted some rod cladding failure different than what could be expected. "TVA is making a non-emergency notification in accordance with 10 CFR 50.72(b)(3)(ii)(A). For this event, the cladding failure could be considered to exceed expected values. "TVA's investigation of the cause of the rod failure is currently ongoing." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-11-14
42139 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2005-11-14 07:20 | 2005-11-14 17:43 | 2005-11-14 | FAILURE TO TAKE FITNESS FOR DUTY TEST A contract employee general foreman who was suspected of being under the influence of alcohol in the protected area did not arrive for fitness for duty testing for cause as directed. Because individual failed to submit to testing, his authorized access to ANO site was terminated and his site access badge was disarmed. Contact the Headquarters Operations Officer for additional details. NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AR | POW |  | 26.73 |  |  |  | 0 | 2005-11-14
42138 | 0 | WATERFORD | 3 |  |  | [3] CE | 2005-11-11 20:34 | 2005-11-12 04:48 | 2005-11-14 | MANUAL REACTOR TRIP AFTER LOSS OF ALL CONDENSER CIRCULATING WATER PUMPS "Waterford 3 manually tripped the reactor at 20:34 [CST] on 11/11/05 due to lowering main condenser vacuum caused by a loss of all circ water pumps. Subsequently an Emergency Feedwater Actuation Signal (EFAS) was received due to low steam generator levels. The plant is currently being maintained in mode 3 with both Steam Generators being fed from the Auxiliary Feedwater system with Steam Generator levels in the normal operational band for mode 3. The EFAS has been reset. The plant will be maintained in Mode 3 while a Post Trip Review is performed. This report is submitted as required by 10CFR50.72." All control rods fully inserted on the manual trip. The main steam isolation valves are shut and the heat sink is through the atmospheric dump valves. The electrical grid is stable and plant power is from the startup transformer. No primary or secondary relief valves or safety valves lifted. The site was able to restart the B & D circ water pumps. There is no significant steam generator tube leakage. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM PICKENS TO HUFFMAN AT 13:55 EST ON 11/14/05 * * * "This notification is an update to an immediate notification that was called into the NRC Operations Center at 04:48 (eastern time) on November 12, 2005 (Event # 42138). The event was reported as an 8-hour event. This update to the original notification is to communicate that, based on further review, the event notification should have been made within 4 hours since it was reportable within 4 hours as well as the 8-hour reporting criteria and therefore the call should have been made within the 4 hour period. The condition is reportable under four hour reporting criteria 50.72(b)(2)(iv)(B) for a manual trip of the plant in anticipation of receiving a RPS Trip with the Reactor critical. The condition is reportable within eight hour reporting criteria 50.72(b)(3)(iv)(A) for the automatic actuation of EFAS upon low steam generator levels. This update does not report a change to the event description reported. As mentioned in the original report, Waterford 3 manually tripped the reactor at 20:34 on November 11, 2005 due to lowering main condenser vacuum caused by a loss of all circulating water pumps. Subsequently an Emergency Feedwater Actuation Signal (EFAS) was received due to low steam generator levels. The plant was then maintained in Mode 3 with both steam generators being fed from the Auxiliary Feedwater System with steam generator levels in the normal operational band for Mode 3. The EFAS had been reset at the time of the original notification. The plant was maintained in Mode 3 while a Post Trip Review was performed. Further details of the event will be reported under the 60 day LER reporting criteria." The licensee notified the NRC Resident Inspector. R4DO (Clark) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2005-11-12
42137 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-11-11 15:02 | 2005-11-11 16:50 | 2005-11-11 | MANUAL REACTOR TRIP DURING STARTUP FOLLOWING FAILURE OF ROD CONTROL POWER CABINET "During a reactor startup, while withdrawing the second shutdown bank, a failure of the 2BD rod control power cabinet occurred. Shutdown Bank B group 2 rods failed to withdraw. After gathering data and indications for troubleshooting, a manual reactor trip was initiated. All rods fully inserted. The Unit was and remains in mode 3. There were no other required or actual ESF actuations." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-11-11
42136 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-11-11 12:00 | 2005-11-11 15:30 | 2005-11-11 | REPORT OF DEGRADED CONDITION DUE TO DEFECTIVE STEAM GENERATOR TUBES "This is a 4-hour report as required by Technical Specification (TS) 5.5.9, Table 5.5.9-2, reported via the ENS in accordance with 10 CFR 50.72(b)(3)(ii)(A), 'Any event or condition that results in the nuclear power plant, including its principal barriers, being seriously degraded'. "Greater than one percent of steam generator (SG) 1-1 and SG 1-2 tubes were determined to be defective and require plugging. Diablo Canyon performs 100% bobbin inspection of SG tubes, thus, no expanded bobbin inspection scope was required. "On November 11, 2005, during the Unit 1 thirteenth refueling outage (1R13), final analysis of eddy current data of SG 1-1 and SG 1-2 indicated that greater than one percent of the total tubes inspected in two SGs were defective placing them in Category C-3. Thirty seven (37) defective tubes in SG 1-1 and forty one (41) defective tubes in SG 1-2 were detected and are being plugged. Most of the pluggable indications are due to circumferential outside diameter stress corrosion cracking at the hot leg tube support plates and at the hot leg top of tubesheet. Results of SG tube inspections that fall into Category C-3, requires a 4-hour non-emergency report to accordance with Diablo Canyon TS 5.5.9, Table 5.5.9-2 and 'Notification to the NRC pursuant to 10 CFR 50.72(b)(2)' (a 4-hour requirement, replaced by 10 CFR 50.72(b)(3)(ii), now an 8-hour requirement). "An NRC teleconference in accordance with TS 5.6.10.d to report the preliminary SG tube inspection results was conducted on November 9, 2005, at 1100 PST. "A Special Report in accordance with TS 5.6.10.a to report the number of tubes plugged in each SG, and TS 5.6.10.c describing the cause of the tube degradation and corrective measures taken to prevent recurrence will be submitted prior to returning Diablo Canyon Unit 1 to power operation." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-11-11
42135 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-10-27 17:00 | 2005-11-10 15:28 | 2006-08-21 | MATERIAL ACCOUNTABILITY DISCREPANCY AT PLANT HATCH "This is a non-emergency Event Notification made in accordance with 10 CFR 20.2201(a)(1)(ii) to inform the NRC of a nuclear material accountability discrepancy amounting to, in the aggregate, a portion of a spent fuel rod used at Plant Hatch (HNP). In the process of reviewing records and physically verifying the contents of the spent fuel pool (SFP) as a part of activities associated with SNC's [Southern Nuclear Company] response to Bulletin 2005-01, SNC has identified discrepancies between fuel segments located in the SFP and segments indicated in plant records. "The segments originated in the early 1980s during fuel reconstitution and inspection activities. The discrepancies call into question the location of segments of single spent fuel rods in each of three bundles. Characterization of three segments located in the SFP provided rod serial numbers which, in turn, were used to determine the bundles from which these segments originated. These bundles were then inspected, and the length of fuel in the location corresponding to each rod segment's intended location was determined. The aggregate in-bundle length found in these rod locations was combined with the lengths of the segments located in the SFP and compared to the design active fuel length of the three rods. This comparison results in a material discrepancy of approximately 55 inches, based on the length measurements. In addition to this discrepancy, historical records indicate two segments (totaling 13 inches of fuel length), which may not be within the inventory of segments identified to date in the SFP. When this amount is added to the length associated with the three rod locations, a discrepancy of approximately 68 inches results. When the planned supplemental inspection of select bundles and SFP locations is completed and photographs are evaluated to aid in the determination of special nuclear material present, this 68 inch estimate may increase or decrease. "On June 16, 2005 SNC formed a team to identify and characterize material in the SFPs at Hatch in order to account for special nuclear material (SNM) at the level of detail requested by Bulletin 2005-01. A work scope was established and specialized resources were contracted to support the work activities. During the performance of these work activities, a number of items of interest were characterized as being either SNM or non-SNM items. On October 28, 2005, SNC submitted the interim status report to NRC. "On November 4, 2005 the Hatch Plant Review Board (PRB) reviewed the SNM Issue Resolution Team's assessment of data produced by the records searches and physical cataloging of SNM in the SFPs. Based on that review, the PRB concurred that a discrepancy exists in material accounting for a portion of a spent fuel rod in each of three bundles and records, as noted above, which in the aggregate approximates 68 inches of fuel rod length. This length is equivalent to about 45% of the length of one intact fuel rod. Further physical examination of the SFP will include additional examination of SFP floor areas that have not been examined to date and selected fuel bundle inspections. The SFP floor areas are limited to a small number of locations that are under equipment or objects stored on the SFP floor. This expanded work scope is expected to be completed by December 15, 2005. "Based on the nature of the fuel rod segments and radiation monitoring, a high degree of confidence exists that the segments are in a restricted area of the plant or otherwise under the control of a licensed facility such that the public health and safety has not been adversely affected. In addition, there is no evidence of theft or diversion. "This notification satisfies the 30-day notification requirement of 10 CFR 20.2201(a)(1)(ii). A subsequent written report will be made in accordance with 10 CFR 20.2201(b). "The licensee has informed the NRC Resident Inspector regarding the discrepancies. "SNC will be making a press release describing the current status of this issue. Accordingly, this notification also satisfies the 4-hour notification requirement of 10 CFR 50.72(b)(2)(xi) with respect to issuance of the press release associated with this issue." * * * UPDATE AT 15:48 ON 8/21/2006 FROM FRANK GORLEY TO ABRAMOVITZ * * * "This is an update of non-emergency Event Notification 42135 that was previously made on November 10, 2005, in accordance with 10CFR 20.2201. This non-emergency Event Notification is made in accordance with 10 CFR 74.11 and informs the NRC of the loss of special nuclear material (SNM) from the historic breakage of several fuel rods used at Plant Hatch (HNP) in the early 1980s amounting to, in the aggregate, approximately 18 inches of a spent fuel rod. This amount is based on the available information, potentially affected by incomplete historic documentation. While reviewing records and physically verifying the contents of the spent fuel pool (SFP) in 2005 and 2006 associated with its response to Bulletin 2005-01, SNC identified discrepancies between fuel rod segments located in the SFP and segments indicated in plant records. This discrepancy was the subject of Event Notification 42135 and LER 2005-003 transmitted by letter NL-05-2262 dated 12/09/2005, including Rev. 1 of the LER, dated 04/14/2006 (transmitted by letter NL-06-0689). "Additional locations in and around the fuel racks and additional fuel bundles were inspected between November 11, 2005, and July 21, 2006. Fuel vendor disorientation and plant SNM offsite shipping records reviews and quantity reconciliations were also recently completed. Based an the results of this expanded work scope, SNC concluded that some SNM material has been lost. This material either resides in some unidentified location in the SFP, resides in the bottom of the SFP as particles or small pieces, or was inadvertently shipped to a licensed low level waste processing facility. "One SNM fragment, referred to as Item 30, was dropped during the physical activities in the pools and has not yet been recovered. This 4-1/2-inch fuel segment had been characterized and quantified and was dropped in the SFP during handling. A search was performed to look for item 30, but the intact segment was not found. During this search, a cladding segment with no appreciable SNM inside was located and identified as Item 32. It may be a portion of Item 30. Item 30's fuel length of 4-1/2 inches is included in the total characterized as lost. "Based on the nature of the fuel rod segments, fragments, pellets, pellet chips, and small particles, and the barrier provided by in-plant radiation monitoring Instrumentation, a high degree of confidence exists that the lost SNM is either still in the SFP or was inadvertently shipped offsite to a licensed low level waste processing facility. Throughout its investigation and review, SNC has identified no evidence to indicate the possibility of theft or diversion of the missing quantity of SNM material. "This notification satisfies the one-hour notification requirement of 10 CFR 74.11 (b). A subsequent written report will be made in accordance with 10CFR74.11(c). The licensee has informed the NRC Resident Inspector regarding the discrepancies and the conclusion regarding the lost material. SNC will be making a press release describing the current status of this issue. Accordingly, this notification also satisfies the 4-hour notification requirement of 10 CFR 50.72(b)(2)(xi) with respect to issuance of the press release associated with this issue." Notified the R2DO (Lesser), PAO (Brenner), and NRR EO (Jung). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOST/STOLEN LNM>10X | LOST/STOLEN SNM |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(xi) | 20.2201(a)(1)(ii) | 74.11(a) |  | 0 | 2005-11-10
42134 | 0 | BIG ROCK POINT | 1 |  |  | [1] GE-1 | 2005-11-10 13:21 | 2005-11-10 14:30 | 2005-11-10 | OFFSITE NOTIFICATION TO THE EPA The licensee notified the EPA that it had inadvertently made some demolition cuts on the steel containment shell coated with paint containing PCBs (Polychlorinated Biphenyls). This was not in accordance with the general conditions of the demolition agreement with the EPA. The steel was being cut with a torch and the paint along the cut line had been abated by the licensee to prevent burning paint with PCBs. However, some cuts were inadvertently not made along the abated lines. The amount of paint involved has been characterized as in the range of grams. The licensee has notified both the NRC regional inspector and headquarters project manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-11-10
42133 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-10-21 15:30 | 2005-11-10 13:56 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * POTENTIAL DEGRADATION OF GLOVEBOX OVERFLOW DRAINS UNDER CERTAIN VACUUM CONDITIONS The NRC Resident Inspector questioned the impact of glovebox enclosure vacuum on the design and function of the glovebox overflow drains. Enclosure vacuum was not considered in the set-point analysis for these drains such that, under certain circumstances, the drains may not function as intended. The degraded safety scenario would involve high uranium concentration solution entering the glovebox (which is considered unlikely as the solution is typically low level caustic solution). The vacuum on the glovebox enclosure would have to exceed that which could result in the overflow drains being incapable of performing their functions. (The licensee notes that vacuums on enclosures have not been observed which would cause the drains to not be capable of performing their function). The solution in the enclosure would have to exceed the height necessary for criticality. The licensee suspended operations in the affected enclosures on 10/21/05. A review was performed for all glovebox enclosures (during the week of 10/24/05). Modifications were made to all Building [DELETED] enclosure overflow drains to account for the absolute worst case enclosure vacuum for the facility (week of 10/24/05). The licensee notified the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
42132 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-11-09 18:35 | 2005-11-09 21:43 | 2005-11-09 | EMERGENCY RESPONSE DATA ACQUISITION SYSTEM TEMPORARILY INOPERABLE "On 11/09/2005 at 18:35 hours, it was identified that St Lucie Units 1 & 2 had lost both of the computer trains associated with Emergency Response Data Acquisition and Display System (ERDADS). This is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as a major loss of emergency assessment capability. Other means to monitor critical data and communicate this data to government agencies exist in each unit. The system was returned to an operable status at 19:45 hrs." The cause of the computer problem was software related. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-11-09
42131 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-11-08 16:15 | 2005-11-09 15:50 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * EXCEEDED MASS LIMIT REQUIREMENTS Licensee reported an administrative IROF [Item Relied On For Safety] failure for the Environmental Safety Program. During the transfer of NaOH based uranium solution from Tank # XX-0023 to Tank # XX-0011 the licensee failed to identify a mass limit more restrictive for Tank # XX-0011 prior to transfer. The licensee exceeded the mass limit requirements due to the two tanks not being identical. Tank #XX-0011 was quarantined and the accident sequence for the tank transfer re-evaluated. This event did not involve or violate any criticality controls, and no release occurred. The licensee notified the NRC Resident Inspector. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
42130 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2005-11-03 | 2005-11-09 10:56 | 2005-11-09 | AGREEMENT STATE NOTIFICATON - MISSING SHIPMENT OF RADIOACTIVE MATERIAL On November 3, 2005, reported that a radioactive shipment was missing its contents. On November 3, 2005, at approximately 2:30 pm, Spectratek Services received a call from Protechnics in Kilgore, TX. They stated a seven piece shipment of four (4) fiberboard boxes and three (3) 20-gallon drums had been received. The contents of one of the 20-gallon drums were not in the drum. The drum was to have contained an ammo box with two 25 pound lead shipping containers, each containing 40 millicuries of Antimony-124 used in oil and gas well completion studies. All packages had security seals in place when they arrived at the Protechnics facility in Kilgore. Notification was made to the Protechnics corporate office, the freight company, and the NM Radiation Control Bureau. Interviewing all employees involved in packaging the shipment resulted in written statements from them. The inventory has been double-checked and it appears the material balance is correct. Security camera tapes have been reviewed showing the packaging area for 10/31/2005 (the day of the shipment). The tapes show the radioactive material being loaded into the containers and the containers being closed and they also show the shipment being loaded onto the freight carrier's trailer. Members of the FBI and Homeland Security made visits while conducting their investigation. The investigation is ongoing. Notification was made to the inspector with the Environmental Monitoring Program, Radiation Branch, Department of State Health Services in Texas. State of Texas also notified NRC. See EN-42118. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-14
42129 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-11-08 08:44 | 2005-11-08 17:37 | 2005-11-08 | DESIGN BASIS FOR LONG TERM COOLING NOT CORRECTLY MODELED "While investigating an issue related to containment coatings and their potential to clog the containment sump strainers, errors were discovered in the calculations that were used as the basis for responding to GL98-04. The errors involved the improper application of a correlation that was used to derive head loss across a screen that was assessed to be partially fouled with debris and the incorrect application of the results to a partially submerged screen that would be susceptible to air intrusion. Further investigation revealed that the flow path for a partially blocked strainer was not correctly modeled for the containment sump strainer and containment sump valve (SI-850A&B). The SI-850 valves have a rising disk and are located inside and at the bottom of the containment sump strainer. These errors in the modeling fidelity potentially impact the analytical basis for demonstrating compliance with the acceptance criteria in 10 CFR 50.46 (b)(5), Long-term Cooling. "Immediate actions - Operability analyses were performed. These operability analyses demonstrated that adequate NPSH would be available to the ECCS pumps to ensure long-term cooling. "Long-term action - The containment sump strainer will be modified, as committed to in Point Beach letter NRC 2005-0109, "Nuclear Management Company Response to Generic Letter 2004-02, Potential Impact of Debris Blockage on Emergency Recirculation During Design Basis Accidents at Pressurized Water Reactors, for Point Beach Nuclear Plant," dated September 1, 2005. This modification will result in a larger strainer surface area and a greater clearance in the vicinity of the SI-850 valves. These modifications will be supported by design analysis and testing that will demonstrate the strainers comply with the long-term cooling capability requirement of 10 CFR 50.46 (b)(5)." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-11-08
42128 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-11-08 10:00 | 2005-11-08 16:50 | 2005-11-08 | EMPLOYEE REFUSED TO TAKE A RANDOM DRUG TEST. On 11/08/05 at 1000 CST a licensed employee was selected for a random drug test. The employee refused to take the drug test. The employee last Friday tendered his resignation and his last day of work was supposed to be 11/11/05. Upon refusing to take the drug test his plant access was denied and he moved up his last day of work to today, 11/08/05. Licensee will write a condition report and review his past work. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector was informed of this report by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 26.73 |  |  |  | 0 | 2005-11-08
42127 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-11-08 13:07 | 2005-11-08 14:38 | 2005-11-08 | ALERT DECLARED DUE TO LOSS OF MAIN CONTROL BOARD ANNUNCIATOR PANELS "An Alert was declared at 13:19 CST for Unit 2 due to a loss of all main control board (MCB) annunciator capability. I&C [instrumentation & controls] personnel were working on a light bulb which tripped a breaker thus losing all MCB annunciator capability. The condition was recognized and an Alert was declared. The deficiency was corrected and the breaker supplying the annunciator system was reclosed, restoring all annunciator capabilities. The total time without annunciator capability was 14 minutes. The Alert was terminated at 13:39 CST. Unit 1 [was not affected by this event and] is currently Mode 1, 100%." Unit 2 is currently defueled. The licensee notified the NRC Resident Inspector along with State, local, and other government agencies. The licensee will be issuing a press release. Notified NRR Jim Dyer. External notifications also included HHS (Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Refueling; FMode2: Refueling | ALERT | 2 | AL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-11-08
42126 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2005-11-08 04:00 | 2005-11-08 14:10 | 2005-11-08 | MARYLAND AGREEMENT STATE REPORT - MISSING TECHNETIUM-99m At 0400 EST on 11/08/05 a delivery person left Mallinckrodt, Inc., located in Beltsville, MD to make deliveries. When he arrived at Cardiology Associates of Frederick, Maryland license MD21-039-01, he was missing the 5 doses of Technetium-99m that were supposed to be delivered to them. The delivery person had made 6 delivery stops before arriving at Cardiology Associates of Frederick. Mallinckrodt, Inc., is calling and sending personnel to the first 6 delivery stops to try to find the missing 5 doses of Technetium-99m. The 5 doses were divided into 2 lots. Lot 1 number is 95143 which contained 4 doses of Tc-99m for cardiolite studies. Activity of each one of the doses as of 0400 hours was 61 millicuries, 73 millicuries, 78 millicuries, and 82 millicuries. The second lot number is 95138 it had one dose with an activity of 62 millicuries (as of 0400 hours) of Tc-99m. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2005-11-11
42125 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-11-08 03:58 | 2005-11-08 07:10 | 2005-11-08 | REACTOR TRIP DUE TO REACTOR COOLANT PUMP BUS UNDERVOLTAGE At 03:58 on 11-08-05, D.C. Cook Unit 2 experienced an automatic, reactor trip due to Reactor Coolant Pump Bus Undervoltage. The cause of the reactor trip its under investigation. This requires a 4-hour report under 10CFR50.72(b)(2)(iv)(B). "All four reactor coolant pumps have remained running. "The Unit 2 Turbine Driven Auxiliary Feedwater Rump (TDAFP) started automatically due to low-low levels in at least two steam generators which is expected for a reactor trip from 100% power. The 'B' train Emergency Diesel Generator (2AB EDG) automatically started and loaded "B" train emergency bus T21A. These automatic actuations of the reactor protection system, TDAFP start, and 2A13 EDG start require an 8-hour report under I OCFR50.72(b)(3)(iv)(A). "'B' train emergency bus T21B was declared inoperable after it failed to be energized automatically on the start of the 2AB EDG. The cause of this failure is under investigation. "The 'A' train Emergency Diesel Generator (2CD EDG) had been inoperable for scheduled maintenance during the time of the event. It was restored to operable status at 06:06." All control rods fully inserted. Steam generators are discharging steam to the main condenser using steam dumps. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-11-08
42124 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2005-11-04 23:00 | 2005-11-07 18:04 | 2005-11-08 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE The State provided the following information via email: "At approximately 8:00 AM November 7, 2005, the Agency was informed that the Licensee had a pickup truck stolen with a Troxler Model 3430 gauge, SN 28101. The theft occurred at approximately 11:00 PM November 4, 2005. The truck is a silver 2002 Nissan. The Troxler gauge was locked in a 16 gauge steel box with a hardened and anti-theft designed lock and hasp. The steel box is bolted to the frame of the truck. The truck license number is Arizona 997MWT. The gauge contains 8 mCi of Cesium-137 and 40 mCi Am:Be-241. "Mesa PD is investigating and has issued report number 2005-308-1094 "The Licensee is offering a $500.00 reward for the recovery of the truck and sources. A press release is to be made. "The Agency continues to look for the source." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | MAT | [5 empty] | 0 | 2005-11-08
42123 | 0 | INDIANA DEPARTMENT OF TRANSPORTATIO |  |  |  |  | 2005-11-07 | 2005-11-07 08:02 | 2005-11-10 | STOLEN TROXLER MOISTURE DENSITY GAUGE Sometime between 11/05/05 and 11/07/05 a Troxler Model 3440, Serial Number 15460, moisture density gauge was stolen from the licensee's field office in Rensselaer, Indiana. The licensee discovered that the office at that location was broken into and the gauge was stolen along with several other items. The gauge was kept inside the locked office and was chained to the floor. The police were notified and a police report will be made. The item contained a 8 millicuries Cesium-137 source and a 40 millicuries Americium-241/Beryllium source. The licensee will notify the NRC Region 3 office. * * * UPDATE FROM KONIECZNY TO HUFFMAN AT 13:53 EST ON 11/10/05 * * * The licensee reports that the gauge was returned to the field office location sometime during the night by individuals unknown. It was discovered in front of the field office door by the first person reporting to the office around 7:00 am CST on 11/10/05. The gauge has been examined and appears to be undamaged. R3DO (Madera), NMSS EO (Morell), and TAS (Whitney via e-mail) notified. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-11-07
42122 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2005-11-06 09:35 | 2005-11-06 12:45 | 2005-11-06 | TEMPORARY LOSS OF OFFSITE NOTIFICATION SIRENS "At 0935 on November 6, 2005, all offsite notification sirens for Crystal River Unit 3 were lost. One siren failed and sent a feedback signal which in turn disabled all remaining sirens. The failed siren was bypassed at 1124, thereby restoring the remaining 39 sirens to service. The failed siren will be repaired promptly. During the loss of siren function, backup means of notifying the public were available, including route alerting using local law enforcement and use of the Code Red autodialing system. This is reportable as an immediate notification (eight-hour report) in accordance with 10CFR50.72(b)(3)(xiii)." The siren system is maintained by the county. Compensatory measures for the remaining area is either: dispatching a police car, or fire truck, or using the Code Red autodialing system for the affected area. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-11-06
42121 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2005-11-05 12:50 | 2005-11-05 16:18 | 2005-11-11 | AGREEMENT STATE - MISSING Am-241 SOURCE The University of Utah moved its Radiation Health Department between buildings. An Am-241 source on a disk in a glass vial was last inventoried and leak checked on May 12, 2005 i.e. prior to the move. The inventory on November 3, 2005 (Thursday) found one source missing. The sources are kept in a locked room and stored in a locked pig. The university is performing an inventory on November 5, 2005 (Saturday) and may perform additional inventories. This information will be placed in NMED on Monday, November 7, 2005. Source: Am-241, 477 milliCuries * * * UPDATE AT 19:37 ON 11/5/2005 FROM GALLOWAY TO ABRAMOVITZ * * * The Source is model # SWA-259, purchased January 1977 and is the size of a nickel. * * * UPDATE AT 13:18 ON 11/7/2005 FROM GALLOWAY TO KNOKE * * * Received notification from the licensee that a Radiation Safety Analyst found the missing Am-241 source at 11:07 MST on 11/07/05. An updated description was given as 1.5 inches long and wrapped in a sheet of lead. The RSO was present when the source was found. Notified R4DO (Shaffer), NMSS (Morell), and TAS email (Perez). * * * UPDATE FROM GALLOWAY TO HUFFMAN AT 19:17 EST ON 11/9/2005 * * * The State of Utah has determined that the update on 11/7/05 reporting that the missing source had been located was incorrect. Further investigation by the University of Utah authorities has determined that the original source description was correct. The source is a nickel-sized slug in a glass vial and not the 1.5 inch source discussed in the 11/7/05 update. Recollection by individuals that had used the source confirmed the source appearance and the discolored "darkened" vial that held the source. The source number was also corrected to SNA-259 The licensee has informed both campus police and the FBI of the missing material. Notified R4DO (Whitten), NMSS (Collins), and TAS (Perez) via email. * * * UPDATE FROM GALLOWAY TO HUFFMAN AT 14:38 EST ON 11/11/2005 * * * The State provided the following information via email: The State of Utah reports that the source has been found. This time verified and sure. It was found in a secure facility. It had rolled under a pallet in the secured waste facility. The investigation as to how it got there is continuing. Notified R4DO (Shaffer), NMSS (Collins), and TAS (Whitney) via email. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2005-11-09
42120 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2005-11-04 16:08 | 2005-11-04 22:20 | 2005-11-17 | TEMPORARY LOSS OF THE RUNNING RHR PUMP DURING A BUS TRANSFER "PCIS Group 4 isolated during Reactor Protection Power Supply bus transfer. The isolation was not expected by control room operators prior to the power supply transfer. The isolation resulted in the trip of the running RHR pump. "Operators verified proper isolation and reset the power supply. Shutdown cooling was re-established. The total time out of service was 18 minutes. The time to boil was calculated to be 68 hours prior to the event." The temperature at the RHR heat exchanger inlet at the beginning of the event was 90 degrees. The temperature at 22:20 was 92 degrees. The other RHR pump was available during this event. The plant is in refueling with the cavity flooded. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1606 EST ON 11/17/05 FROM MICHAEL PLETCHER TO S.SANDIN * * * "This notification updates the reporting criteria for Event No. 42120. The event was determined to not be reportable per 10CFR50.72 (b)(3)(iv)(A) since it was not due to a valid signal or the result of an intentional manual initiation. This report also satisfies the 60 day telephone notification provisions in 10CFR50.73 (a)(1). "This notification is being made in accordance with 10CFR50.73 (a)(2)(iv)(A) due to an invalid Primary Containment Isolation System (PCIS) Group 4 actuation that impacted the availability of the Residual Heat Removal (RHR) shutdown cooling system. "On November 4, 2005, with the reactor shutdown for refueling, an invalid actuation of PCIS Group 4 occurred during transfer of 'A' RPS Bus power supply. The actuation occurred because a breaker supplying power to the 'B' logic was tagged open resulting in completing the PCIS actuation logic. The Group 4 actuation resulted in a complete isolation of the single train RHR shutdown cooling suction path by isolation of RHR-17 and RHR -18 isolation valves. "The shutdown cooling path was isolated for approximately 18 minutes and the time to boil was approximately 68 hours at the time of the event." The licensee informed the NRC Resident Inspector. Notified R1DO (Barkley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-11-04
42119 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2005-11-03 14:00 | 2005-11-04 14:38 | 2005-11-04 | DEFICIENCY FOUND IN INTEGRATED SAFETY ANALYSIS PROGRAM "BACKGROUND: "Framatome ANP routinely vacuum transfers LEU powder into 55-gallon drums for storage in the BLEU facility 55-gallon drum warehouse. A change was implemented recently to also vacuum transfer LEU powder from 45-gallon drums into 55-gallon drums, also for storage in the BLEU facility 55-gallon drum warehouse. "EVENT DESCRIPTION: "On day shift November 3, 2005 at approximate 2:00 PST, a process operator vacuum transferred LEU powder enriched to (deleted) wt% 235U from a 45-gallon to a 55-gallon drum in the BLEU facility at the Richland site. This transfer was performed according to an approved standard operating procedure (SOP). This was the first such transfer under a recently approved nuclear criticality safety analysis (NCSA) part of the Integrated Safety Analysis (ISA) "When the operator was preparing the newly filled 55-gallon drum for transfer to and storage in the warehouse, the Nuclear Inventory Management System (NIMS) would not print a label for the drum. Operations personnel contacted an NCS specialist about this issue. While troubleshooting this problem, the NCS specialist discovered that the LEU powder contained hydrogenous additives. He recognized that the Richland site ISA did not implement IROFS to prevent transfer of powder containing hydrogenous additives from 45-gallon to 55-gallon drums. "At this point, the drum was sampled and locked in place pending further evaluation. The 45-gallon to 55-gallon transfer process was also placed out of service pending further evaluation. "SAFETY SIGNIFICANCE OF EVENT: "The safety significance of this event is very low. In accordance with the NCSA a 55-gallon drum filled with LEU powder, enriched to (deleted ) 235U with a bulk density of (deleted ) and containing (deleted ) wt% moisture, that is fully reflected by water has a keff of (deleted). A moisture value of (deleted) wt% is required in such a drum to reach a keff of 1.0. "The drum involved in this event actually contained 115.4 kg of LEU powder enriched to (deleted) wt% 235U with a bulk density of (deleted) and containing (deleted) total moisture equivalence (moisture and moisture equivalent approved additives determined by follow up laboratory analysis). Based on total moisture equivalent content alone, the material in the drum would have to have more than (deleted) times the limit (deleted) and more than (deleted) times the actual amount (deleted) before criticality could occur in the drum. The actual enrichment and bulk density of the material involved in this event provide additional margin compared to the values required for criticality discussed in the previous paragraph. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): "Criticality could only occur if moderation control on the material placed in the drum is lost. This could hypothetically occur if powder containing over (deleted) times the allowed limit (deleted) were placed into the drum. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): "The process parameter controlled in this portion of the process is moderation. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "Within the 1SA the NCSA, E04-NCSA-323 version 3.0 accident sequence 1.4.1 description bounds this event. It states, "UO, powder containing greater than (deleted) wt% H2O equivalent is transferred to a 55-gallon drum from the BLEU powder preparation south addback station." "Defense 1 for this accident sequence states, 'Moderation control: Any 45-gallon drum of UOX powder that does not have at least two independent determinations that it has (deleted) wt% or less moisture must be stored in a specially designated, locked storage grid to prevent accidental drum movement.' This is IROFS 1105 and was maintained throughout this event. At HRR, per SOP, if a drum contains greater than (deleted) wt% moisture and/or > (greater) wt% moisture equivalent additives, it is locked in a storage location. Only trained key custodians may unlock these storage locations for further processing or handling of the drum, Based on the moisture and moisture equivalent approved additive content of the powder, the drum involved in this event was not such a drum. "Defense 2 for this accident sequence states, 'Moderation control: The programmable controller interfaces with NIMS to verify acceptable moisture content before it permits transfer valve to open.' This is IROFS 6002 and was maintained throughout this event for moisture content of the powder. As implemented, this IROFS does not verify that the powder to be transferred contains no hydrogenous additives. However, as an uncredited defense, before permitting the transfer valve to open, NIMS does verify that the powder contains s (deleted) wt% AZS and (deleted) wt% ALS, which is (deleted) wt% moisture equivalent approved additives. Therefore, on a total moisture and moisture equivalent basis, NIMS does verify that the powder contains less than (deleted) wt% total moisture equivalence. This is approximately (deleted) times less than the (deleted) wt% total moisture equivalence required to approach a keff value of (deleted). "Defense 3 for this accident sequence states, Moderation control provided by an AEC [active engineered control]. An in-line moisture monitor is interlocked to shut off the vacuum blower and stop the rotary valve to prevent a significant amount of Uox powder containing greater than (deleted) wt% H2O from being transferred to the drum. This is IROFS 4704 and was maintained throughout this event for moisture content of the powder. This IROFS, however, will not detect dry hydrogenous additives. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "After discovery of the deficiency, the drum was sampled and locked in place pending further evaluation. The 45-gallon to 55-gallon transfer process was also placed out of service pending further evaluation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2005-11-04
42118 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-11-04 | 2005-11-04 12:33 | 2005-11-09 | AGREEMENT STATE - LOST/MISSING SHIPMENT "On Monday, October 31, 2005 a shipment of RAM was packaged in Albuquerque, NM by Spectrotech, Svcs. And offered for ground shipment to Kilgore, TX. There were 7 packages, 4 fiberboard boxes and 3 twenty gallon drums, the latter being yellow III, TI=5.0. When the shipment arrived at Kilgore, TX subsite #004 on the RAML03835, Thursday afternoon November 3, 2005, two vials of liquid (Antimony) Sb-124 with 40mCi/each were missing along with the inner shipping container, an ammo box. A tamper seal on the 20 gallon drum was still intact, but this type did not contain a unique serial number. The inventory at Spectrotech has been verified as correct and video surveillance indicates that the materials were packaged and offered for shipment to Conway shipping for ground service. The corporate RSO reported the missing material to the answering service at 1830 hrs, Thursday, 11/03/05. Sb-124 is used for sub-surface field studies in the oil and gas industry. All parties are continuing the investigation." Texas Incident Number: I-8275 Texas Report Number: TX-05-42118 *** UPDATE ON 11/09/05 TO KNOKE *** On 11/09/05 the State of New Mexico also notified NRC. See EN-42130. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-09
42117 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2005-08-30 | 2005-11-04 09:14 | 2005-11-04 | LOSS OF RADIOACTIVE MATERIAL "I am calling per 10 CFR 20.2201(a)(ii) to notify you of a possible loss of radioactive material at the VA Medical Center, New Orleans, Louisiana, a permittee under the VA license. This incident occurred on or around August 30, 2005, and was discovered October 7, 2005. This possible incident resulted from the flooding of the radioactive waste storage room at the medical center and involved the loss of radioactive materials. "The materials which are considered lost are Iodine 131 and Iodine 125. The unsealed materials were in waste containers and may have washed out of the containers when the waste room was flooded. The dilution of the small amount of activity in the floodwaters precludes any possible public dose or health and safety concern. "These circumstances are considered a possible incident since a technical evaluation to estimate the loss is not based on quantitative measurements or surveys. Also, the tags and waste records attached to the containers were obliterated by the floodwaters. Attempts to estimate the activity began on October 7, 2005, and an estimate of the original activity was submitted by the permittee in a preliminary report to the National Health Physics Program on October 24, 2005. "A best estimate based on review of storage records, radioactive decay, and observations and measurements in the waste room is that, perhaps, as much as 200 microcuries Iodine 131 and 600 microcuries Iodine 125 in storage August 30, 2005, cannot be specifically located or identified as being present in the waste storage room on October 7, 2005." Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-11-04
42116 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2005-11-03 16:00 | 2005-11-04 03:32 | 2005-12-30 | TS REQUIRED COMPONENTS INADVERTENTLY RENDERED INOPERABLE DUE TO INADEQUATE REVIEW OF WORK CLEARANCE "At 0200 on 11/03/05 a clearance was authorized that defeated the DW [Drywell] pressure high and Rx [Reactor] vessel low isolation features to valves in the Nuclear Closed Cooling System and Instrument Air Systems. The required T.S. [Technical Specification] actions after this discovery are that the plant should have been in Mode 3 at 1600 on 11/3/05. The clearance was removed and the circuit restored to operability at 0142 on 11/4/05. The time of discovery for the loss of safety function was 2345 on 11/3/05." The clearance was to perform pre-planned maintenance activities. The licensee plans on entering this incident into their corrective action program and will issue a Condition Report. The licensee informed the NRC Resident Inspector. * * * RETRACTION ON 12/30/2005 AT 10:07 FROM KENNETH RUSSELL TO ABRAMOVITZ * * * "An 8-hour notification was made on November 3, 2005, in accordance with 10CFR50.72(b)(3)(v)(D), Accident Mitigation. This report was made when it was discovered that a clearance had unintentionally deenergized a portion of the containment isolation logic. This logic would have prevented a containment isolation valve for the nuclear closed cooling system and a containment isolation valve for the instrument air system from closing on a signal due to high drywell pressure or reactor vessel low level as designed. "The condition was determined not to be a loss of containment (leakage) function since each containment penetration also has an inboard containment check valve which is leak tested and is credited for preventing leakage. The check valves in both penetrations were successfully tested to be in conformance with 10 CFR 50 Appendix J Option B criteria in March 2005. The containment isolation (instrumentation) function was also not lost. Only the logic for Group 2A outboard valves was deenergized. This was a small portion of the outboard logic and had no impact on the inboard logic. Since neither the containment function nor the containment isolation function was lost, there was no loss of safety function for an accident mitigation function and EN# 42116 is retracted. "As discussed in EN# 42116, a Technical Specification violation occurred and is reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications." The licensee will be submitting a written LER for the 10CFR50.73(a)(2)(i)(B) event. The licensee notified the NRC Resident Inspector. Notified the R3DO (Hills). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-11-04
42115 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2005-11-03 17:00 | 2005-11-03 17:35 | 2005-11-08 | SAFEGUARDS REPORT Discovered vulnerability in a safeguards system that could allow access to a controlled access area. Compensatory measure have been initiated. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. *** UPDATE AT 11:47 EST ON 11/08/05 FROM EWERS TO KNOKE *** "This is a retraction to a notification made in accordance with 10CFR73.71 on November 3, 2005, regarding a security safeguards breach of a vital area at Millstone 2, (NRC Event No. 42115). Upon further investigation and review, it has been determined that there was no breach of the security barrier in that the required barriers were visually inspected and found to be intact. Therefore, this event has been determined to be not reportable in accordance with 10CFR73.71." The NRC Resident Inspector has been notified. Notified R1DO (Miller) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 0 | 2005-11-08
42114 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-11-03 10:30 | 2005-11-03 15:05 | 2005-11-23 | ECCS LEAKAGE OUTSIDE CONTAINMENT "A 0.02 GPM leak was identified on the inlet valve (1CV89) to the 11 seal injection filter. This leak equates to 4500 cc/hour. The leakage is outside containment and quantified IAW Leakage Monitoring and reduction program procedure SC.RA-AP.ZZ-0051. This leakage exceeds the 3800cc/hour limit as stated in UFSAR section 6.3.2.11 and GDC-19 to ensure control room habitability. Therefore ECG section 11 section 11.2 specifically 11.2.2.b applies for being in a degraded or unanalyzed condition. The 1CV89 valve was recently replaced as a scheduled activity during the current 1R17 refueling outage. The 1CV89 packing has been adjusted and the leakage has stopped. The leakage was to the floor to the liquid waste system. There was no personnel contamination or injuries due to the leakage. "Current Plant Conditions: RCS temperature is 340 degrees, RCS pressure is at 1400 PSIG and stable, plant heat-up and pressurization is in progress IAW integrated operating procedures." The leakage occurred from 10:30 to 12:30 EST. The valve has been tested and declared operable. Primary coolant activity is 0.828 microCuries per cc. There is no known steam generator tube leakage. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (SAUER) TO HUFFMAN ON 11/23/05 AT 15:10 EST * * * "On 11/03/05 at 1505, PSEG Nuclear made an 8 hour report in accordance with the 10CFR50.72(b)(3)(v) --(Event number 42114) - for ECCS leakage outside containment. "Upon further investigation, it has been determined that the leak was within the guideline limits for the control room and off-site radiological exposure. Additionally, at the time of discovery, Salem Unit 1 was in Mode 4 coming out of its seventeenth refueling outage and 73 of the 193 fuel assemblies in the core were new fuel assemblies. Therefore, the actual core nuclide inventory would have been much less than the core nuclide inventory assumed in the design basis analysis. Therefore, the event of November 3, 2005 reported under 10CFR50.72(b)(3)(v) is being retracted." The licensee will notify the NRC Resident Inspector. R1DO (Doerflein) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2005-11-03
42113 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2005-11-02 21:00 | 2005-11-03 11:35 | 2005-11-03 | CONTRACT SUPERVISOR TESTED POSITIVE FOR THE PRESENCE OF ALCOHOL DURING A RANDOM DRUG TEST A contract supervisor tested positive for the presence of alcohol during administration of the Random Drug Testing Program. The individual's unescorted access authorization was terminated, his badge was confiscated, and appropriate management notifications were made. The NRC Resident Inspector was notified of this event by the licensee Contact the Headquarters Operations Officer for details | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.73 |  |  |  | 0 | 2005-11-03
42112 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-11-02 | 2005-11-02 14:30 | 2005-12-05 | AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGE The State provided the following information via email: "A portable gauge licensee reported a Troxler Electronics Model 3411 portable moisture/density gauge, serial number 16176 was stolen when the transport vehicle was stolen. The transport vehicle is a 1989 Honda CRX and was parked at the gauge user's residence at the time of the theft. The Licensee reported the gauge was stolen between the hours of 10:00 PM Monday, November 1, 2005 and 7:00 AM Tuesday, November 2, 2005. A police report has been filed by the licensee with the Edmonds police department. "No media attention to date. "Isotope and Activity involved: 1.48 GBq (40 mCi) Am-241:Be and a 0.296 GBq (8 mCi) Cs-137 source. Source serial numbers: Cs-137 (50-5267), Am-241Be (47-11584). "Disposition/recovery: The police have been notified of the theft, the gauge has not yet been recovered. "Gauge was last leak tested on October 5, 2005. Analysis was done by Troxler and found to be acceptable. "The licensee reported that all the proper levels of security were being used at the time the vehicle was stolen with two locked cables or chains." Washington Event report # WA-05-061 * * * UPDATE PROVIDED FROM STATE (SCROGGS) VIA EMAIL TO ROTTON AT 1854 EST ON 12/05/05 * * * "The Licensee reported that the vehicle stolen on November 2, 2005 was recovered at 7:30 PM that day. The gauge in the vehicle was not damaged and the security cables securing the gauge to the vehicle were intact. The licensee also reported that an attempt was made to remove the security cables. "The licensee must perform a new leak test on the gauge to verify that the gauge is in proper condition prior to being used in the field." Notified R4DO (Kennedy), NMSS EO (Pierson), Canada (CNSC), TAS (Hahn via email). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-11-07
42111 | 0 | CONTINENTAL STRUCTURAL PLASTICS |  |  |  |  | 2005-10-03 | 2005-11-02 15:40 | 2005-11-02 | LOST GENERALLY-LICENSED DEVICE Between 10/01/05 and 10/03/05, Continental Structural Plastics lost a small static eliminator. The device was attached to the barrel of an air gun and was being used to ionize plastic parts. The company searched for the material but was unable to locate it. It is thought that the material may have been inadvertently disposed of in the trash. The device is a NRD Model P2021-8000 Nuclecel static eliminator containing a Po-210 ionization source. The company did not know the source strength, however these devices contain sources which are less than 10 milliCuries. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-11-02
42110 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-10-07 10:37 | 2005-11-02 12:46 | 2005-11-02 | INVALID SYSTEM ACTUATION "The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of the 10CFR50.73(a)(2)(iv)(B) system checked above. NUREG1022 Revision 2 identifies the Information that needs to be reported as discussed below. "(a) The specific train(s) and system(s) that were actuated. "On October 7, 2005, at 10:01 EDT, a procedure was started to calibrate the Unit 2 Refueling Floor Vent Exhaust radiation monitors 2D11K611C and K611D. Monitor K611C was tested and restored, and K611D was being tested in the tripped condition. At 10:37, the K611C monitor received a momentary, spurious high radiation signal, or spike. As per design, the high radiation signal resulted in the following automatic actions: Group 2 primary containment isolation valves closed, secondary containment isolated, and both Unit 1 and 2 A and B trains of Standby Gas Treatment initiated. The initiation signal was invalid because it did not result in response to an actual high radiation condition, nor did it trip as a result of any other requirement for initiation of the safety function, such as a downscale or inoperable trip, for example. "(b) Whether each train actuation was complete or partial. "The four Standby Gas Treatment (SBGT) trains auto started and both Unit 1 and 2 secondary containment fully isolated. This is a complete actuation. The primary containment isolation valve Group 2 isolation was outboard valves only. This is a partial actuation. "(c) Whether or not the system started and functioned successfully. "The above systems functioned successfully." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-11-02
42109 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-11-01 23:00 | 2005-11-02 01:13 | 2005-12-21 | TECH SPEC REQUIRED SHUTDOWN DUE TO DEGRADATION OF CONTAINMENT COATINGS "On November 2, 2005 at approximately 00:00 Central Standard Time (CST), Point Beach Nuclear Plant (PBNP) Unit 2 commenced a reactor shutdown required by Technical Specification 3.0.3. "During a review of the containment coatings in both Unit 1 & 2 containments, it was discovered that the containments have not been maintained with the analysis of record performed by Sergeant and Lundy (S&L). The S&L analysis performed for Unit 2 was based on the known condition of coatings when the analysis was performed. There was no explicit margin for further degradation. Subsequent discoveries of degraded or unqualified coatings cannot be accommodated by the existing analysis as written. "An Operability Recommendation (OPR) was performed for Unit 2 and approved on 10/30/05 at 2000. Following this OPR, a further review of containment coatings in the Unit 2 containment was performed and showed a potential for approximately 11 square feet of unqualified coatings [in] the Zone of Influence (ZOI) for the containment sump. The OPR allowed for a maximum of 5.68 square feet of loose material in the ZOI. A Unit 2 containment walk-down was performed on the evening of November 1, 2005. This revealed that the unqualified coatings in the ZOI were approximately 11 square feet. This information placed Unit 2 in an unanalyzed condition, which lead the operators to enter Technical Specification 3.0.3 at 2300 on November 1 due to both trains of Emergency Core Cooling System (ECCS) being declared inoperable for sump recirculation capability. "Actions are currently underway to remove enough unqualified coatings to be within the assumptions made in the OPR and restore Containment Sump recirculation capability. When this is completed, the technical specification shutdown will be terminated, and Unit 2 will make preparations to return to full power. "Unit 1 is currently in Mode 5 and ECCS is not required. However, the condition is also applicable to Unit 1 containment. Actions have been underway since the identification of the original issue to remove unqualified containment coatings. The Plant Manager has placed a hold on entering Mode 4 on Unit 1 pending completion of corrective actions." Presently there are 2 workers and a Radiation Protection technician inside containment. The licensee said that workers will go inside containment and remove the degraded coating. This will take approximately 45 minutes and have a total exposure to personnel of 85 millirem. The licensee notified the NRC Resident Inspector. *** UPDATE FROM C. STALZER TO J. KNOKE AT 03:15 ON 11/02/05 *** At 01:06 CST the licensee exited from Technical Specification 3.0.3. requirements and plans to hold power on Unit 2 at 97% power pending further assessment and evaluation. The licensee will notify the NRC Resident Inspector. Notified the R3DO (Kozak). * * * RETRACTION FROM E. SCHULTZ TO W. GOTT AT 1712 ON 12/21/05 * * * "On November 2, 2005, at 01:13 [ET] PBNP submitted Emergency Notification #42109, to report a TS required shutdown due to potential of an unanalyzed condition that significantly degrades plant safety and an event or condition that potentially could have prevented the fulfillment of a safety function. The condition related to the discovery of degraded containment coatings in the zone of influence (ZOI) for the containment sump. "A subsequent evaluation concluded that the degraded coatings would not have significantly affected sump recirculation flow capability. Additionally, the zone of influence was identified to be approximately one-third that assumed for the design-basis calculation. Based on the conservatism in the sump blockage analysis, the degraded coatings in the Unit 2 containment within the original ZOI did not affect the conclusion that equipment needed for accident mitigation would have operated as designed. "Therefore, the Emergency Notification made on November 2, 2005, documenting that this condition created the potential of an unanalyzed condition that significantly degrades plant safety, and potentially could have prevented the fulfillment of a safety function, is retracted. The Technical Specification required shutdown is also retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (H. Peterson). | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | ACCIDENT MITIGATION |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2005-11-02
42108 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-08-10 | 2005-11-01 19:09 | 2005-11-01 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE The State provided the following information via email: "[Licensee employee] called RSO to let him know that [a radiographer trainer] had 12.5 rem deep dose equivalent for Quarter 3 - July 1-31, 2005. "On Wednesday, 8/10/05, [name deleted], RSO for Turner Industries called DSHS Radiation Control (RC) to report that [licensee employee] has informed him that [name deleted] radiographer trainer for his company, had a 12.5 rem deep dose equivalent reading for Quarter 3-July 1-31, 2005 monitoring period. "[The radiographer trainer] wrote a statement to RC stating that he has worked as an x-ray radiographer for the last 6 years with Turner Industries, is very conscientious & checks his dosimeter often throughout the work day. He stated that he was closely supervised by the RSO for the monitoring period in question & did training for a new trainee. "An on-site investigation was conducted by [name deleted], a RAM inspector for RC. [The RAM inspector] interviewed [the radiographer trainer] & [another employee] regarding this investigation. Both [the radiographer trainer and the other employee] felt that this was a result of an altercation [the radiographer trainer] had with a contract radiographer & felt that this was the result of a retaliation against [the radiographer trainer] for not allowing the contract radiographer to enter [the radiographer trainer's] shooting bay. [The radiographer trainer] went on vacation & from 6/27-07/5/05.The RSO & [the radiographer trainer] felt that the contract radiographer had access to [the radiographer trainer's] film badge & a radiography camera & could have easily carried out this retaliation without being noticed. "The RC inspector reviewed past monitoring records for [the radiographer trainer] & found that his results were consistent with someone receiving 50-60 mrem /month & 500-650 mrem/year in this line of work. The inspector concluded that the overexposure appeared to be very suspicious & agreed that the overexposure be readjusted to reflect the normal monthly results for [the radiographer trainer]. "Additional Documents Supplied: "Personnel monitoring records for the past year for [the radiographer trainer] were obtained & sent in to RC by the RAM inspector. The investigation determined that the dose appeared to be to the dosimeter only. No violation recommended. RC has issued a letter concurring with the licensee's investigation results & has sent a copy of this letter to DSHS RC." Texas Incident # I-8250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-04
42107 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2005-11-01 | 2005-11-01 15:34 | 2005-11-01 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGN Hardi Lighting shipped one exit sign model NEXT-1-10WR with serial number C018515 to H and H Chevrolet on April 27, 2005. The sign contained 7.09 Curies of H-3, Tritium. The facility received the sign and paid for it. Upon receiving two letters from the Nebraska Department of Health and Human Services concerning the sign, the facility replied on October 10, 2005 indicating that they did not have the sign. H and H Chevrolet personnel have made three searches of the facility and cannot locate the sign. They believe that the sign was disposed in a trash container and sent to the landfill. Nebraska Incident Number: NE050008 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2005-11-04
42106 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-10-29 | 2005-11-01 15:27 | 2005-11-02 | AGREEMENT STATE REPORT - RADIOACTIVE MATERIAL MISSING IN SHIPMENT The State provided the following information via facsimile: A single package originally containing two pigs arrived on 10/29/05 at the FedEx hub at the Memphis Airport damaged, with one of the two pigs missing. The missing pig contains 10 special form capsules of Am-241/Be with a total activity of 500 milliCuries. The pig is small (described as the size of a shotgun shell). The package was being sent by AEA Technology QSA of Burlington, MA to CPN Corp in California. FedEx stated that the package arrived in Memphis on Saturday morning 10/29, however, it was not determined that one of the pigs was missing until the morning of 10/30. On 11/1/05, the Tennessee Radiation Control Program was at Fed Ex hub to assist in the search for the pig, and AEA Technology QSA (now known as QSA Global, Inc.) confirmed that the container did contain 2 pigs. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE FROM STATES TO M. RIPLEY 1615 EST 11/02/05 * * * The following information was provided from the States of Tennessee and Massachusetts via email: "The following is an summary/update from [the Tennessee State inspector's ] visit: The container/sources have not been found. FedEx said they have thoroughly searched and continue to search all possible areas where the source could have been lost. They are tracking all the details of the package from the time it arrived through their system until it was last seen. They are attempting to determine the root cause of the damage to the package and loss of part of its contents. Interviews are being conducted of individuals who played a role in the handling/processing of the package. The damage to the package was such that it looks like a mechanical device (closing metal grate/gate?) was involved in tearing the package. Radiation surveys have been and are being performed by Fed-Ex in any areas that they think the source could have been lost. There is a suspicion that the container and the sources have been swept up and disposed of at the landfill. AEA Technology (now QSA Global) provided the following information via the State of Massachusetts: "The W1 lead pot (i.e., pig) is 2.5 inches tall X 1 inch diameter, it is painted white and has tape securing the cap. AEA performed measurements on the W1 lead pot and found the surface measurements were: 36 mr/hr gamma and 70 mr/hr neutron. They performed measurements on a pig with the same amount of Am-241/Be lost in TN - 500 mCi of Am241/Be" Notified R1DO (C. Anderson), NMSS EO (J. Gitter), TAS (L. English). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-11-04
42105 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2005-10-31 22:23 | 2005-11-01 02:14 | 2005-11-01 | CONTAINMENT EVACUATION AND SMOKE INHALATION TREATMENT DUE TO SMALL FIRE "On October 31, 2005, at 22:23 fire and smoke was reported in the Unit 1 Reactor Containment Building. Unit 1 is currently shut down for a refueling outage. Investigation into the cause of the fire continues. The fire appears to have been caused by slag from cutting/grinding work contacting a temporary ventilation hose. The containment evacuation alarm and fire alarm was sounded. The fire was reported extinguished at 22:25. The fire team and first aid team responded. First aid team reported several people were overcome by smoke inhalation. The Unit 1 control room called '911' to request ambulance and EMT assistance. Eight people have been transported to local hospitals for treatment of smoke inhalation. None of the people transported offsite were contaminated. 29 CFR 1904.8 requires notification of the Occupational Safety and Health Administration (OSHA) within eight hours of this event because it resulted in the hospitalization of three or more employees as a result of a work related incident. This NRC notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to the notification of offsite governmental agencies via '911' as well as the OSHA notification." Unit 2 is at 100% power and was not impacted by this event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-11-01
42104 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-10-31 22:27 | 2005-10-31 23:02 | 2005-11-02 | UNUSUAL EVENT DECLARATION: LOSS OF OFFSITE POWER DUE TO LOSS OF STARTUP TRANSFORMER "Unusual event category 10A on Unit 4. Loss of offsite power to Unit 4 due to loss of Unit 4 Startup Transformer. Auto AFW actuation. Auto starting and loading of both Unit 4 Emergency Diesel Generators." The licensee stated that the plant is stable in Mode 3 at approximately 700 psi and 380 deg F. The plant was experiencing electrical grid instabilities at the time of the trip of the Startup Transformer. The exact cause of the transformer trip is being investigated. The grid instabilities were associated with the plant's Northwest Bus, therefore, Unit 3 is not affected and continues to operate at approximately 60% power. The licensee notified the State of Florida and will notify the NRC Resident Inspector *** UPDATE FROM D. FUNK TO J. KNOKE AT 02:15 ON 11/02/05 *** "The licensee terminated from their Unusual Event (EAL 10A) at 0200 EST on 11/02/05. Unit 4 A & B 4 KV busses are now powered from off-site power using Unit 4 startup transformer." The power / mode for Unit 4 is now 0% power / Mode 5. The licensee will notify the NRC Resident Inspector and has notified State, local and other government agencies. Notified R2DO (Ayres), NRR EO (Case), IRD-MOC (Wilson), DHS (J. Frost) and FEMA (S. Kimbrell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-10-31
42103 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2005-10-31 01:00 | 2005-10-31 17:34 | 2005-11-02 | AGREEMENT STATE REPORT - MISSING RADIOGRAPHY CAMERA At 0100 on 10/31/05 the licensee discovered that a SPEC 150 Radiography Camera (camera s/n 204) with a 64 Curie Ir-192 (s/n 217221B) source was stolen from the company's office. The camera was in a locked space. The camera was last used on 10/28/05, and was logged in at 0100 on 10/29/05. A dispatcher saw the camera at 1500 on 10/28/05. At 0100 on 10/31/05, a radiographer went to the space to get the gauge and discovered that it was gone. The Tulsa Police Department was notified. Category 2 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for a short time (minutes to hours). It could possibly be fatal to be close to this amount of unshielded radioactive material for a period of hours to days. These sources are typically used in practices such as industrial gamma radiography, high dose rate brachytherapy and medium dose rate brachytherapy. *** UPDATE FROM M. BRODERICK TO J. KNOKE AT 10:20 EDT ON 11/2/05 *** The Department of Environmental Quality in Oklahoma provided information that the missing radiography camera was recovered at 07:30 CST. Due to local media coverage in the area, a private citizen called the number published by the TV media and volunteered information. The citizen indicated he saw the camera near the freeway entrance of 33 West Avenue and I-44 in West Tulsa, OK. The camera, which was found in a grassy area (weeds) near a privacy fence (wall), was intact with the source in the shielded position. The licensee (IRIS-NDT) has surveyed the site and said the readings were consistent with a source inside a camera. The Tulsa police department is still pursuing the investigation. The licensee offered a reward of $1,000 for information leading to the recovery of the camera. Notified R4DO (Farnholtz), NMSS (Burgess), TAS (English), IRD (Wilson, Blount, and Leach) DHS (Holtz), NRC (Doherty), FEMA (Liggett), and HHS (Turner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2005-11-03
42102 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-10-31 13:18 | 2005-10-31 17:37 | 2005-10-31 | AUTOMATIC REACTOR SCRAM DUE TO TRIP OF MAIN TURBINE "At 1318 [CST] on 10/31/05 with Unit 3 at 100% power, a full reactor scram signal (RPS) was received due to a turbine trip. Unit 2 was also at 100% power and was unaffected by the event. Reactor water level lowered to approximately minus 6 inches as expected and was recovered with normal feedwater flow. All expected PCIS isolations, Group 2 (RHR Shutdown Cooling), Group 3 (RWCU), Group 6 (Ventilation), and Group 8 (TIP) were received along with the auto start of CREVs and 3 SBGT trains. "This event is reportable as a 4-hour and 8-hour non-emergency notification along with a 60-day written report in accordance with 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(A) as 'any event or condition that results in valid actuation of RPS or PCIS'." The licensee stated that the turbine trip was most likely caused by bus transfer evolutions in the 500 kv switchyard. The licensee stated that all control rods fully inserted, the electrical grid is stable, the EDGs and ESF systems remain available, and that decay heat is being removed via the turbine bypass valves to the main condenser. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-10-31
42101 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-10-31 12:02 | 2005-10-31 15:38 | 2005-10-31 | MEDIA INTEREST "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 31, 2005, at approximately 12:02 PM Mountain Standard Time (MST) the Palo Verde Nuclear Generating Station was informed of a request to conduct a media interview with a clearinghouse that provides newsworthy input to local media regarding an emergency preparedness exercise to commence tomorrow. No press release is planned by Palo Verde, but the interview is indication of media interest. The State of Arizona and Maricopa County will be performing an ingestion pathway emergency preparedness exercise on November 1, 2005 through November 3, 2005. The exercise will be evaluated by the Federal Emergency Management Agency (FEMA). "Although this exercise will involve significant participation by State and County agencies, Palo Verde participation is expected to be limited to a small control cell of personnel to simulate communication with the State and County. "There has been some media interest. "There have been no official press releases posted by Maricopa County or the State of Arizona, although the Governor's calendar for November 1, 2005 indicates that the Honorable Janet Napolitano will participate. "Resident NRC inspectors are not expected to participate in this exercise, but Palo Verde understands that two NRC Region IV personnel (Messrs. T. Andrews and W. Maier) are expected to support FEMA evaluation of the exercise. "Palo Verde Unit 1 is in a refueling outage with all fuel assemblies offloaded to the spent fuel pool. "Units 2 and 3 are operating in Mode 1 at approximately 100% power, at normal operating temperature and pressure." The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-31
42100 | 0 | EPSILON PRODUCTS COMPANY |  |  |  |  | 2005-10-31 | 2005-10-31 15:34 | 2005-10-31 | DEFECTIVE GAUGE The shutter of an OMART Level Gauge (Model SHD s/n66437 80 millicuries Cs-137) failed in the closed position. The manufacturer has been notified and will pick up the gauged for repairs. The gauge shutter failed in a safe position. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 21.21 |  |  |  | 0 | 2005-10-31
42099 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2005-10-31 09:00 | 2005-10-31 12:48 | 2005-10-31 | OFFSITE NOTIFICATION Haddam Neck uncovered evidence of Spent Fuel Pool leakage below ground. The leakage was discovered when removing soil east of the Spent Fuel Building. Consequently, the site notified the Connecticut Department of Environmental Protection. The quantity of water leaked is unknown. Estimates based on historic Spent Fuel Pool evaporation data indicate that the leak was small - on the order of a few gallons per day. Based on readings from down-gradient monitoring wells, there is no travel beyond the property line. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-31
42098 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-10-30 19:50 | 2005-10-30 23:28 | 2005-10-30 | OFFSITE NOTIFICATION "On October 30, 2005, at 1950 an altercation occurred between two contract personnel. The event occurred inside the protected area, but outside the radiation controlled area. The event took place in a temporary building used as a dress out area for the Unit 1 refueling outage. One of the two people suffered a minor cut to his arm. There was no contamination related to this incident. FPL Security escorted the two individuals off site and revoked their plant access. The local St. Lucie County Sheriff department was called and is investigating the event. One person has been arrested for simple battery and is in custody of the St. Lucie County Sheriff Department. This NRC notification is being made in accordance with 10 CFR 50.72(b)(2)(xi) due to the notification of the St. Lucie County Sheriff Department." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-30
42097 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-10-30 01:50 | 2005-10-30 03:05 | 2005-10-30 | SPDS UNAVAILABLE FOR GREATER THAN ONE HOUR The Unit 2 SPDS (Safety Parameter Display System) was unavailable from 0050 EDT to 0300 EST on 10/30/05. The cause of the unavailability is believe to have been related to software updates. The condition has been corrected and the system is back in service. This item is reportable per the licensee's procedures whenever SPDS is out of service for more than one hour. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-30
42096 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2005-10-29 13:25 | 2005-10-29 14:51 | 2005-10-30 | UNUSUAL EVENT - MAIN TRANSFORMER FIRE "NUE declared on Hatch Unit 1 due to a fire on the main transformer lasting greater than 10 minutes. Unit 1 reactor scram on main turbine trip. Group 2 PCIV (Primary Containment Isolation Valves) isolation on low reactor water level (+3 inches). All group 2 valves closed as required. Fire extinguished at 1358 hours. Plant is stable." All control rods fully inserted on the reactor scram. The plant is in hot shutdown steaming through the turbine bypass valves to the main condenser. No safety systems are affected. Emergency electrical buses are on normal offsite power and emergency diesel generators are available if required. The onsite fire brigade responded to the fire and the fire suppression system for the main transformer functioned as expected. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM E. BURKETT TO W. GOTT AT 1950 ON 10/29/05 * * * The licensee is still in a NUE. The fire is out. The fire reflashed at 1603 when the deluge system was secured to inspect the transformer. The deluge system was restarted immediately. Offsite fire support have responded. Cleanup efforts are in progress. The licensee notified the NRC Resident Inspector. Notified IRD (Blount), R2DO (Cahill), and NRR EO (J. Hannon). * * * UPDATE FROM E. BURKETT TO P. SNYDER AT 2010 ON 10/29/05 * * * The licensee is still in a NUE. This call is to add an offsite notification per 10 CFR 72.75 (b)(2) to another government agency. The site chemistry department notified the National Response Center (Coast Guard) at 1636 that the site had discharged an unknown quantity of oil into the Altamaha River and was implementing site spill control and countermeasures procedures. The licensee also notified the Georgia Environmental Protection Division. The licensee notified the NRC Resident Inspector. Notified IRD (Blount), NRR EO (J. Hannon), and R2DO(Cahill). * * * UPDATE FROM E. BURKETT TO W. HUFFMAN AT 0021 EDT ON 10/30/05 * * * The licensee reports that the fire is confirmed extinguished (i.e., no risk of reflash) based on long term monitoring of the transformer including thermography measurements. The Unit remains in an Unusual Event until assessment activities related to the transformer fire have been completed. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM E. BURKETT TO W. HUFFMAN AT 0105 EDT ON 10/30/05 * * * Based on the results of assessment activities related to the transformer fire, the licensee has exited the Unusual Event at 0050. The licensee notified the NRC Resident Inspector. The R2DO (Cahill), EO (Hannon), IRD (Blount), DHS (Doyle), and FEMA (Bisco) have been notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-10-29
42095 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-10-29 09:30 | 2005-10-29 13:54 | 2005-11-09 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE On 10/29/05, a Troxler Moisture Density Gauge (model 3440, s/n 032146, 8 millicuries Cs-137, 40 millicuries Am-241: Be) was stolen from the back of the operators truck at the job site on Four Acre Road in Jacksonville, FL. The gauge was chained and locked to the operator's truck. The operator left the truck at the job site while she reviewed the job site. She returned to the truck and drove back to the office. At the office she noted that the gauge was gone. The Jacksonville Police Department was notified. The company intends on placing an ad in the local newspaper. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. *** UPDATE AT 15:20 EST ON 11/09/05 FROM FURNACE TO KNOKE *** "The Troxler gauge was recovered intact and undamaged on 11-8-2005 by Jacksonville Police Department and returned to the licensee. Information on the location of the gauge was supplied by an individual asking the manufacturer (Troxler) about the possibility of a reward. The Troxler representative called this office with information. The individual was arrested for a prior warrant in Tennessee." Notified the R1DO (Miller), NMSS (Greg Morell), and TAS Email (Perez) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-11-02
42094 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2005-10-29 01:26 | 2005-10-29 04:39 | 2005-10-29 | MANUAL REACTOR TRIP FOLLOWING LOSS OF FEEDWATER PUMPS "This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.72 (b)(3)(iv)(B)(6). During a plant shutdown for a refueling outage at 0126 [EDT] on October 29, a manual reactor trip was initiated in anticipation of Critical Operation on Emergency Feedwater. CR3 [Crystal River Unit 3] experienced an automatic Emergency Feedwater Actuation based upon a loss of both Main Feedwater Pumps. Main Feedwater Pumps tripped on a loss of the running Main Feedwater Booster Pump, which was automatically tripped on low Feedwater De-aerator Tank level. The redundant Main Feedwater Booster Pump was shutdown as part of the plant shutdown sequence. The low Feedwater De-aerator Tank level occurred due to a loss of the operating Condensate Pump while the redundant Condensate Pump was tagged out of service for scheduled maintenance." The cause of the failed condensate pump that initiated the event sequence is still under investigation but the licensee indicated that it appears to be due to a mechanical failure. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-10-29
42093 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2005-10-28 23:32 | 2005-10-29 01:44 | 2005-10-29 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE CONTROL RODS "On 10/28/2005, Susquehanna Unit 1 operators began the process of shutting down the unit for a maintenance outage to address control cell friction. It was expected that during this evolution, "slow to settle" control rods would be encountered, and rather than delay the continuance of the shutdown to perform operability testing, it was determined that these control rods would conservatively be declared inoperable. Based on previous testing data and trending analysis of operability testing performed during the cycle, PPL [Pennsylvania Power and Light] believes that the subject control rods would have passed operability tests. "Accordingly, at 2332 EDT, Technical Specification 3.1.3.f was entered which requires the unit to be taken to Mode 3 in 12 hours when nine or more control rods are inoperable. Entry into this specification was also required per 3.1.3.e when it was determined that four inoperable rods resided within one Banked Position Withdrawal Sequence (BPWS) group. The inoperable control rods are fully inserted and disarmed, shutdown margin requirements are met, and the control rod system was always fully capable of performing its safety function. "At the time when the ninth control rod was declared inoperable, Unit One was operating at 18% power. Unit Two is continuing operation at 100% power. "PPL is reporting this event as a Technical Specification required shutdown per 10CFR 50.72(b)(2)(i). "The NRC Resident Inspector was notified by the licensee." Unit 2 is not affected by this problem and will continue to operate at 100% power. * * * UPDATE FROM LICENSEE (ILLIADIS) TO NRC HUFFMAN AT 1011 EDT ON 10/29/05 * * * "At 0744 the plant reached All Rods In and at 0805 entered Mode 3 in accordance with plant procedures to fulfill the requirement of Technical Specification 3.1.3. As stated in the original EN# 42093, it was expected that during this evolution, "slow to settle"' control rods would be encountered, and rather than delay the continuance of the shutdown to perform operability testing, it was determined that these control rods would conservatively be declared inoperable. This action was taken on a total of 41 control rods that failed to settle at position 00 during the shutdown. There are 4 additional control rods that were declared inoperable previously during the cycle and subsequently settled to 00. Of the 41 control rods that failed to settle at the time of the shutdown, 6 have settled to 00 at the time of this update. "Based on previous testing data and trending analysis of operability testing performed during the cycle, PPL continues to believe that the subject control rods would have passed operability tests. The inoperable control rods are fully inserted, shutdown margin requirements are met, and the control rod system was always fully capable of performing its safety function. "There were no ECCS initiations and no challenges to containment." The licensee notified the NRC Resident Inspector. R1DO (Silk) notified. | 18 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-10-29
42092 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-09-21 | 2005-10-28 17:50 | 2005-10-28 | AGREEMENT STATE REPORT - MISSING PORTABLE ALLOY ANALYZER The licensee provided the following information via email: "On 09/21/05 while preparing for Hurricane Rita, the owner's truck was stolen from in front of his office in Houston, Texas, 77087. Since his office is a trailer, the owner thought it best to put his Niton Alloy Analyzer [6 millicuries Cd-109 s/n U1238 NR5498] in his truck to bring home in case his office was destroyed by the hurricane. Houston law enforcement was notified as soon as owner discovered the truck missing. His truck was recovered 10/13/05, but the analyzer was not." Texas Incident No: I-8273 Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-02
42091 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-08-15 16:00 | 2005-10-28 17:50 | 2005-10-28 | AGREEMENT STATE REPORT The licensee provided the following information via email: "The written prescribed dose for this treatment was 550 cGy with the plan of repeating another procedure one week afterwards for a total prescribed dose of 1100 cGy. This dose, to be given in 2 fractions, was to be delivered to the vaginal cavity using High Dose Rate (HDR) afterloader device. The first fractionation of 550 cGy was delivered incorrectly, approximately 4.5 cm anterior to the correct position. This resulted in the intended target area receiving 1451 cGy in one treatment. "The medical physicist discovered the error in the brachytherapy vision software (planning system). When digitizing the calculation point of the coronal plane, the sagittal plane viewing plane was in an incorrect position that resulted in the calculation point being entered incorrectly. There was no other medical physicist to second check the plan at that time due to personnel shortage issues. "The prescribing physician determined that the clinical effect of the dose is negligible and there is no impact to the patient's well being." Texas Incident number: I-8253 Event Report ID No: TX-05-41932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-11-02
42090 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-10-18 | 2005-10-28 15:56 | 2005-11-21 | AGREEMENT STATE REPORT - MISSING PAPER THICKNESS GAUGE On 10/18/05 while conducting leak checks of their equipment, the licensee discovered a NDC Model 104F Paper Thickness Gauge (80 millicuries Am-241 s/n 11480) missing. The device was not located in a search of the facility. The device was part of the production line. The licensee notified the Arkansas Department of Health at 1430 CDT on 10/28/05. * * * UPDATE FROM MACK TO HUFFMAN ON 11/21/05 AT 12:37 EST * * * On 10/31/05, authorities from the State of Arkansas performed a search of the licensee's facility but were still unable to locate the missing gauge. The State determined that the gauge had not been used in support of the production process at the facility for quite a while and had been retired in place on the production line by the licensee. The State also determined that the last inventory of the gauge had been in 2001. The licensee has provided the State with corrective actions related to this event. The State considers this gauge lost and is closing out this report. The R4DO (Smith), NMSS( Karas), and TAS (Danis via e-mail) have been notified on this update. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2005-11-02
42089 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-10-28 01:15 | 2005-10-28 11:25 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * DISCARD OF CAUSTIC SOLUTION TO WASTE TANK WITHOUT SAMPLE AND ANALYSIS A low level caustic discard solution was transferred to caustic waste tanks without sample and analysis. An in-line uranium concentration monitor was also present which would have stopped the transfer of high concentration solution. The solution in the tank was sampled. The solution concentration was very low and would have met analysis requirements. There was no actual or potential health and safety consequences to workers, the public or the environment. The safety significance was very low due to the very low mass (8.91 grams U-235 at 65 weight %) and concentration (0.033 grams U-235/liter) [solution volume discarded without sampling was 270 liters]. This event was entered into the Problem Identification , Resolution and Correction System (PIRCS). An investigation is underway. The licensee informed the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
42088 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-10-27 13:28 | 2005-10-27 17:38 | 2005-12-19 | UNANALYZED CONDITION "As part of an ongoing Appendix R assessment, it has been determined that Operator actions credited in the Fire Hazards Analysis (FHA) potentially would not be met in fire zones credited for post fire safe shutdown per 10 CFR 50 Appendix R. Specifically, the FHA credited the availability of two in plant operators to conduct two separate series of operator actions that are required to be performed simultaneously within the first 20 minutes. However, the site Fire Plan requires one of these in plant operators to respond to a plant fire as a Fire Brigade member. Since no barrier was put in place to compensate for the lack of the credited operator; this event is reportable as an unanalyzed condition that significantly degraded plant safety." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BOB MURELL TO W. GOTT AT 1314 ON 12/19/05 * * * "Further review has determined that adequate operator resources are and have been available to perform the required post fire safe shutdown actions. Therefore, this event is not an unanalyzed condition that significantly degrades plant safety and is being retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (H. Peterson) | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-10-27
42087 | 0 | CONAM INSPECTION |  |  |  |  | 2005-10-27 15:00 | 2005-10-27 17:25 | 2005-10-27 | POTENTIAL EXTREMETY DOSE IN EXCESS OF 250 RAD At about 3 PM on 10/27/05 following industrial radiography at the Sunoco Refinery in Philadelphia, PA, a radiographer approached the front of the radiography camera to disassemble the guide tube from the camera body. The radiographer thought that he had fully retracted the source but noticed that the source was exposed during the disassembly. The source was a 21.8 curie Iridium 192 source. The radiographer contacted the radiation safety officer after he realized he had been overexposed. The radiographer received a calculated dose to his extremities of between 330 and 360 Rad. The licensee stated that the individual's self indicating dosimeter was off scale. The individual's thermo-luminescent dosimeter will be sent for a whole body exposure reading. Whole body calculated dose was less than 5 Rem. The radiographer was being sent for medical treatment. The licensee has removed the radiographer from his duties pending further investigation. The licensee will determine corrective actions and perform stand-down training for the employees in the Trainer, PA field office concerning the occurrence. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2005-10-27
42086 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2005-10-26 14:00 | 2005-10-27 13:46 | 2005-10-27 | AGREEMENT STATE REPORT - LOOSE SURFACE CONTAMINATION AND CONTAMINATED PERSONNEL "At 6:40 PM, October 26, 2005, the Agency's Duty Officer received a call from the dispatch center to contact Pharmacy Services of Peoria (IL-01874-01) at their Peoria facility regarding a contaminated package they had transported back from Proctor Hospital, Peoria, IL (IL-01188-01) earlier that afternoon. Pharmacy Services of Peoria reported that the package was contaminated on the surface with Tc-99m. Direct measurements yielded 3 milliR/hr and 4.9 million DPM. The package was immediately set aside in their waste area and secured. The driver was surveyed and contamination was found on one hand. His hand was decontaminated until readings were approximately 0.04 milliR/hr and no removable contamination remained. The pharmacy vehicle was subsequently surveyed and decontaminated to the extent practicable below releasable limits. Pharmacy Services of Peoria went on to state that he had contacted the hospital as well when the contamination was discovered that afternoon. "The Duty Office then contacted, a technician of Proctor Hospital who indicated that a syringe of Tc-99m had partially vented which resulted in the contamination of her glove and the exterior of the retrieved pharmacy container. She stated that following notification from the pharmacy around 2 pm that afternoon, she had surveyed the hot lab for contamination and discovered loose radioactive contamination on the counter, the floor and the gloves she had been using at the time. She successfully decontaminated the floor and changed the counter absorbent covering. No other contamination had been found in the Department. "On October 27, 2005 a Division representative called both individuals to follow-up and discuss reporting requirements. Pharmacy Services of Peoria advised that the courier had visited one other facility that afternoon following the collection of the briefcase containing empty lead containers at Proctor Hospital. Representatives from the pharmacy had called the second facility the previous afternoon to advise them of the potential for contamination. The second facility investigated and then reported back that their monitoring had revealed no contamination of the items dropped off. The pharmacy subsequently visited the site themselves later that same day to retrieve some empty containers and confirmed no contamination was present on any of the packages involved. He went on to report that the driver involved was monitored when he reported for work on the morning of the 27th and no additional removable contamination was discovered on his hands and as a further precaution the vehicle that had been used was set aside for the day and would not be driven. "When the technician of Proctor Hospital was contacted she reported that she believed the contamination on the package resulted from a procedure where she was preparing a diagnostic tracer from a kit. Based on the initial amount involved and the subsequent diagnostic procedure she believed that no more than 0.5 milliCi of Tc-99m could have been involved. Circumstances in the hot lab and with available personnel lead to an uncommon situation where the package to be retrieved by the pharmacy courier was in the dose preparation area leading to its eventual contamination. Although routine procedure is to monitor all items removed from the radioactive work area of the hot lab, this was not performed on this occasion as it was unusual for the package to be in the dose preparation area. The licensee indicated that similar circumstances are very unlikely to be repeated so the potential for second occurrence is negligible." State Report: IL050052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2005-11-01
42085 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-10-26 | 2005-10-27 11:04 | 2005-12-16 | SOURCE DISCOVERED AT METAL SCRAP YARD The State provided the following information via facsimile: Gauge containing a Sr-90 sealed source was discovered at a metal scrap yard in Girard, Ohio. The gauge is a Betamike model manufactured by Taylor Instruments (Model 015020; Serial 781-35). The activity as of 8/70 was 100 mCi (millicuries). The activity as of 10/27/05 was calculated to be 44 mCi (millicuries). The Ohio Department of Health dispatched an inspector to the scrap yard on October 26. The gauge is secure and a leak test of the source showed no removable contamination. Radiation levels are 5 Mr/hr (milliRem per hour) on contact and 1 Mr/hr at 30 cm. Disposal options for the device are being investigated. Ohio Report OH05-134 * * * UPDATE FROM S. JAMES TO W. GOTT AT 1114 ON 12/16/05 * * * "The source was packaged and removed for disposal by a contractor to the USEPA." Notified NMSSEO (B. Karas) and R3DO (S. Burgess) Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-11-01
42084 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2005-08-31 18:05 | 2005-10-27 09:39 | 2005-10-27 | INVALID ACTUATION OF AN EMERGENCY DIESEL GENERATOR "This telephone notification to report an invalid actuation is provided in accordance with 10 CFR 50.73(a)(1), which states, 'In the case of an invalid actuation reported under Sec. 50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER.' The specific reporting requirement in 10 CFR 50.73(a)(2)(iv)(A), states, 'Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).' For this report, the affected system was the emergency AC electrical power systems as listed in 10 CFR 50.73(a)(2)(iv)(B)(8). Specifically, the Train A emergency diesel generator (EDG) automatically started due to an invalid system actuation. "On August 31, 2005, at approximately 1805 hours (EDT), with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, operating in MODE 1 at approximately 100% power, the Train A EDG automatically started from the standby condition. The EDG did not automatically connect to the associated emergency bus (E-1), because no E-1 bus undervoltage (UV) signal was present. The automatic start was caused by a failed solenoid-operated valve (SOV) in the air start system for the EDG (valve number DA-23A). The SOV failed-open, which is the designed failure-mode condition for this valve. This admitted air to the EDG air-start distributor, which started the Train A EDG. No additional failures or abnormalities were noted. The Train A EDG successfully started and achieved the required speed and voltage, but as stated previously, the EDG did not load because no UV signal was present on the associated bus. "The Train B EDG remained operable during this event. Also, the EDGs each have two starting SOVs that are in parallel in the starting air system. A start signal or a loss of power to either valve is sufficient to start the associated EDG. "The failed SOV was replaced. The Train A EDG was tested after replacement of the SOV and returned to service at 1016 hours on September 1, 2005. "The invalid EDG start was entered into the corrective action program for HBRSEP, Unit No. 2. The investigation of this event has been completed. The results of the investigation determined that the EDG start was caused by a short-circuit failure of the coil for the SOV. Additional corrective actions for this condition, beyond replacement of the failed SOV, are in progress and are being tracked via the corrective action program." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-10-27
42083 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2005-10-25 15:00 | 2005-10-26 17:55 | 2005-10-26 | VIOLATION OF ANSI STANDARD FOR UF6 CYLINDERS "Metropolis Works, Metropolis, Illinois (MTW) is reporting a failure to follow procedure related to the installation of valves in UF6 cylinders." "A violation of ANSI Standard N14.1 (2001) 'Uranium Hexafluoride Packaging for Transport', Section 6.14.6 was reported 26 October, 2005. This is a reportable event because it is a violation of an applicable national standard and also an action outside the licensee's procedures. ANSI N14-1 (2001) 6.14.6 states, 'No material of any kind other than the specified solder shall be used on the threads to facilitate installation {of cylinder valves into the UH6 type 48Y cylinders}.' Contrary to that standard, MTW site maintenance personnel did use Teflon spray to facilitate installation of cylinder valves into type 48Y cylinders. Use of a thread lubricant, such as Teflon, can be expected to increase the degree the valve threads are engaged for a given torque. Teflon is a fluorinated compound and is not a chemical hazard in contact with UF6. "This issue was discovered when USEC inspectors noted white residue around cylinder valves previously replaced by the licensee when those valves were later replaced by the cylinder manufacturer. Analysis of the residue showed it was Teflon. USEC notified the licensee of the finding 25 October 2005. Interviews with maintenance workers disclosed that Teflon had been used when replacing some cylinder valves. The licensee is investigating the quantity and type of cylinders that might have been subjected to Teflon during valve replacement. Notification of all customers that might have received cylinders with valves installed with Teflon is in progress. "The licensee notified NRC Region 2 (D. Hartland)." Notified R2DO (Ernstes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | IL | FUE | [5 empty] | 0 | 2005-10-26
42082 | 0 | HONEYWELL INC |  |  |  |  | 2005-07-22 | 2005-10-26 17:36 | 2005-10-26 | MISSING AIR IONIZER A generally licensed NRD model P-2021-3000 air ionizer (s/n A2DV726) was discovered missing following the demolition of a wall. During the installation of a new cleaning bench on July 22 and 23, a wall was demolished. The nitrogen line and the attached blow-off gun containing the device was attached to that wall and the assumption is the ionizer was in the demolition debris. The debris was moved to a Waste Management dumpster for a short time and then sent to a landfill in Blaine, MN. The landfill was searched, but the device was not found. These devices generally have an initial activity of 10 mCi of Po-210, but the caller did not know the activity of the lost device. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-10-26
42081 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-10-26 10:20 | 2005-10-26 12:22 | 2005-10-26 | LOSS OF POWER AT THE EMERGENCY OPERATIONS FACILITY "Due to an electrical fault in the Susquehanna Emergency Operations Facility (EOF), the power to the building has been removed. Testing and repairs are underway and expectations are that power will be restored in approximately 6 hours. The EOF is located approximately 30 miles from the Susquehanna plant and the loss of power does not effect plant operation. "Until repairs are complete communications and accident assessments will be made in the on site Technical Support Center (TSC). The Pennsylvania Emergency Management Agency, Luzerne and Columbia Counties have been notified by the Susquehanna Emergency Planning Organization. "The NRC and PEMA will be notified upon power restoration." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 10/26/05 AT 1500 EDT FROM JIM HUFFORD TO ARLON COSTA * * * "As of approximately 1300 hours on 10/26/2005, power was restored to the Susquehanna Emergency Operations Facility (EOF) and the facility is considered operable. The NRC Resident Inspector will be updated." Notified the R1DO (Silk). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-26
42080 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2005-10-26 03:33 | 2005-10-26 06:10 | 2005-10-26 | LOSS OF THE TONE ALERT PROMPT NOTIFICATION SYSTEM FOR GREATER THAN ONE HOUR "This notification is being made due to Nine Mile Point site losing the Tone Alert Radio System for more than 1 hour as of 0333 ET on 10/26/05. This is an 8 hour Non-Emergency per 10 CFR 50.72 (b)(3)(xiii) (Loss Comm/Asmt/Resp). Cause for the loss is unknown and under investigation at this time. Emergency planning has verified route notification is available as a compensatory measure. Nine Mile Point will provide a follow-up notification when the system is returned to Service." The licensee will inform the NRC Resident Inspector. * * * UPDATE AT 09:18 EDT ON 10/26/2005 FROM BRIAN FINCH TO ABRAMOVITZ * * * "This notification is being made due to Nine Mile Point site losing the National Weather Service Tone Alert Radio for more than 1 hour as of 03:33 ET on 10/26/2005. This is an 8 hour Non-Emergency per 10 CFR 50.72 (b) (3) (xiii) (Loss Comm/Asmt/Resp). Cause for the loss is unknown and under investigation at this time and cause will be documented in CR-20054275. Emergency planning had verified route notification is available as a compensatory measure. "Nine Mile Point Unit 1 & Unit 2 are at 100% power before and after event. "Notified via RECS line by the Oswego County Warning Point the National Weather Service Tone Alert Radio has been returned to service @ 0630 October 26, 2005. "A copy of this Notification Worksheet will be provided to the Resident Inspector. This event has been captured on Condition Report 2005-3679." The licensee will notify the NRC Resident Inspector. Notified the R1DO (Silk). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-26
42079 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-10-26 02:33 | 2005-10-26 05:20 | 2005-10-26 | LOSS OF THE TONE ALERT PROMPT NOTIFICATION SYSTEM FOR GREATER THAN ONE HOUR "The James A. Fitzpatrick Station was notified by Oswego County at 0403 EDT that the tone alert Prompt Notification System had been out of service for greater than one hour. The out of service time started at 0233 EDT on 10/26/05. Actions have been initiated to repair the system. The cause of the failure is unknown at this time." The licensee informed local authorities and will inform the NRC Resident Inspector. * * * UPDATE AT 1015 EDT FROM JIM COSTEDIO TO ABRAMOVITZ * * * "Oswego County notified the James A. Fitzpatrick nuclear station that as of 0630 on 10/26/05, the Tone Alert Prompt Notification System had been restored to service." The licensee notified the NRC Resident Inspector. Notified the R1DO (Silk). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-26
42078 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2005-10-25 21:40 | 2005-10-25 22:05 | 2005-10-26 | UNUSUAL EVENT DECLARED DUE TO A SMALL FIRE AT THE MAIN TURBINE AREA "Small Class B fire on the Unit 3 High Pressure Turbine. Fire is currently out, presented no challenges, and lasted 13 minutes" The fire occurred underneath the high pressure turbine bearing and was caused by oil soaked insulation. The fire was extinguished by the site's fire brigade and resulted in no injuries to plant personnel. Plant safety and emergency systems were not affected by the fire and all plant systems functioned as required. Currently, the fire brigade is being debriefed and it is anticipated that the site will terminate the Unusual Event shortly. The licensee notified the State, local authorities and the NRC Resident Inspector. * * * UPDATE AT 23:54 EDT ON 10/25/2005 FROM MICHAEL COEN TO RIPLEY * * * "Small class B fire on the Unit 3 High Pressure Turbine. Fire is currently out, presented no challenge, and lasted 13 minutes. Terminated Unusual Event at 2330." The plant is in mode three both before and after the event. The plant startup schedule has not been determined. The licensee will notify the NRC Resident Inspector. Notified the IRD Manager (Blount), FEMA (Chris Leggett), R2DO (Ernstes), and NRR EO (Hannon). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-10-25
42077 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-10-25 11:25 | 2005-10-25 13:14 | 2005-10-25 | PROTECTIVE ACTION PREVENTED - DISCOVERY OF SUSPICIOUS ITEM "At 1130 [CDT], on 10-25-2005, the Plant Shift Superintendent was notified of a suspicious item located on top of a concrete sully stone about 10' from the south side of C-212 office complex, inside the Controlled Access Area (CAA). This stone is part of the CAA Vehicle Barrier System (VBS). The item was identified as a 1.5" x 1' cylindrical PVC type tube with caps on both ends. The Shift Security Commander [deleted] was notified to investigate the item in question. After investigation it was determined that item was indeed suspicious and in a suspicious location. At 1200, Security Commander [deleted] initiated a Plant lockdown. At 1241, Security notified Paducah City Police Department captain [deleted] and the Paducah Police bomb squad was dispatched to the plant. The bomb squad arrived at the plant at 1253 along with FBI agent [delete] and ATF agents [deleted] and [deleted]. FBI and ATF had been notified by the Paducah Police Department. The bomb squad utilized a robotic device to evaluate the contents of a nearby dumpster which revealed no suspicious items. The robotic device was then utilized to engage the suspicion item with a water cannon and the item was broken apart and no detonation was encountered. The suspicious item was determined to be a container containing an epoxy resin manufactured by Atlas Minerals and Chemicals. Preliminary investigation reveals that this is not currently used by US EC maintenance organization for work at the plant; however an investigation of the event is ongoing. At 1433, the incident was terminated and the plant lockdown was discontinued. At no time was the suspicious device located close to any process systems located in the plant. "This is being reported as an event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." The licensee notified the Federal, State and local law enforcement agencies as well as the NRC Resident Inspector. (See NRC's Security Incident Database event no. 2769 and PGDP Event Report No. PAD-2005-0018). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | PROTECTIVE ACTION PREVENTED | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(b) |  |  |  | 1 | 2005-10-25
42076 | 0 | HUNTINGTON TESTING AND TECHNOLOGY |  |  |  |  | 2005-10-25 09:25 | 2005-10-25 17:00 | 2005-10-26 | RADIOACTIVE SOURCE LOST IN SHIPMENT At 1651 ET on 10/24/05, the licensee dropped off two shipping containers at the FedEx shipping facility near the Huntington Tri-State Airport in Huntington, WV for shipment by FedEx to AEA Technology in Burlington, MA . Each container contained an 8.7 Curie Ir-192 source. On 10/25/05, the licensee was notified by AEA that only one of the two sources had arrived. AEA reported that two packages did arrive per schedule (0925 ET 10/24/05): one package was one of the radioactive material shipping containers containing one of the two expected sources, however the other was an attaché case containing only the licensee's shipping papers. The FedEx Response Center was notified and FedEx is searching for the missing shipment. The shipping containers are both AEA Type 650L containers, each measuring 8" x 10" x 13 " with Yellow 2 radioactive material markings. The Transportation Index for each container is 0.2. The container received by AEA contained an AEA source changer S/N 202 containing an 8.7 Curie Ir-192 source S/N 20284B. The container lost in shipment contains an AEA source changer S/N 190 containing an 8.7 Curie Ir-192 source S/N 20285B. * * * UPDATE 1120 EDT ON 10/26/05 FROM REGION I (JOHN KINNEMAN) TO S.SANDIN * * * Region I was notified by AEA that the misdirected shipment arrived at their Burlington, MA facility this morning in good condition. Notified R1DO (Silk), NMSS (Holahan) and TAS (Danis). Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-10-25
42075 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-10-25 10:00 | 2005-10-25 13:01 | 2005-10-25 | LOSS OF COMMUNICATION BY FRONT END PROCESSOR AND SPARE TRAIN TO FTS-2001 COMMUNICATIONS LINK "At 1000 EDT on October 25, 2005, it was discovered that no good data is being transmitted via the FTS-2001 communications link. The communications link itself is functioning properly; however, the front end processor and the spare train for Unit 4 are not on-line. The estimated time of repair for restoration of data flow is approximately 1700 EDT on 10/25/05." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-25
42074 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-10-24 23:00 | 2005-10-25 02:16 | 2005-10-25 | INOPERABLE START-UP TRANSFORMERS; HIGH SWITCHYARD VOLTAGE DUE TO HURRICANE WILMA "At 2300 on October 24, 2005, both unit 3 and unit 4 start up transformers were declared inoperable and Tech Spec 3.8.1.1.e action statements were entered. With both units being energized from their respective start-up transformers, the high voltage limit is 241.5kV in accordance with 0-ONOP-004.6, Degraded Switchyard Voltage. System Operations reported switchyard voltage at 243.5 kV and 242.5 kV for unit 3 and unit 4 respectfully. System Operations was requested to lower switchyard voltage to within limits. At 0015 on October 25, 2005, switchyard voltage being lowered to within the switchyard limits and both start-up transformers were declared operable. The high switchyard voltage is due to hurricane Wilma's impact on the Florida service area that has [led] to low system load with cooler weather conditions." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Hot Standby | Hot Standby |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2005-10-25
42073 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-10-24 13:14 | 2005-10-24 16:47 | 2005-10-24 | LOSS OF EMERGENCY RESPONSE DATA ACQUISITION AND DISPLAY SYSTEM "On 10/24/2005 at 12:14 hours, Saint Lucie Units 1 & 2 lost both of the computer trains associated with Emergency Response Data Acquisition and Display System (ERDADS). This is reportable in accordance with 10 CFR 50.72(b)(3)(xiii) as a major loss of emergency assessment capability. Other means to monitor critical data exist in each unit. Troubleshooting and restoration work is in progress." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Hot Standby |  | Cold Shutdown | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-24
42072 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2005-10-21 09:00 | 2005-10-24 12:41 | 2005-10-28 | UNANALYZED CONDITION DUE TO RELOCATION OF A FIRE DOOR BOUNDARY "This event is being reported as 10CFR50.72(b)(3)(ii)(B), an unanalyzed condition that significantly degrades plant safety. A postulated fire water system line break did not take into consideration the movement of a fire door boundary. Consequently, the break may affect safe shutdown of the plant. The door boundary was moved in May 1999. "While assessing a calculation to update fire pump curves (CR 04-00422-04) it was found that the calculation does not appear to have been updated for the tornado depressurization event modifications (DCP 99-05014). Specifically, door DG-112 was moved to the control complex wall from the diesel generator wall. This door movement isolates the rattle space that was previously credited as a relief path for this internal flood. "A full break is postulated for this line as the result of a safe shutdown earthquake. As the result of the postulated pipe break, both fire protection pumps are expected to auto start resulting in a break flow rate into the hallway of approximately 6,000 gpm. Standard Perry design practice is to assume a 30 minute duration for the pipe break flow isolation unless justified otherwise. "The line in question was isolated at 2027 on 10/21/05. The valves are being maintained closed under administrative controls." The licensee notified the NRC Resident Inspector. **** RETRACTION ON 10/28/05 AT 1748 EDT FROM H. KELLY TO P. SNYDER **** "An 8-hour notification was made on October 24, 2005 under 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition that significantly degrades plant safety. The report was made due to a postulated break for a non-safety non-seismic fire water pipe that could possibly affect safe shutdown of the plant. "An evaluation was completed on October 28, 2005. This evaluation confirmed that the current plant configuration is consistent with the design basis. The evaluation used for the original event notification assumed a full break of the involved piping. Perry design basis for this moderate energy system is a leakage crack. The postulated leakage from the crack in the piping remains within design basis and does not significantly degrade plant safety. Since Perry remains in compliance with design basis and there is no unanalyzed condition that significantly degrades plant safety, there is no reportable condition. Therefore, ENF 42072 is retracted." The licensee notified the NRC Resident Inspector. Notified R3DO (Lipa). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-10-24
42069 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-10-23 23:00 | 2005-10-24 00:26 | 2005-12-20 | NON-EMERGENCY EVENT DECLARED FOR LOSS OF ERDADS SYSTEM AFFECTING BOTH UNITS "On 10/23/05 at 2300, the Unit 1 and Unit 2 emergency response data acquisition and display system's emergency response data system (ERDS) link to the NRC failed. Troubleshooting and restoration work is in progress." The NRC Resident Inspector has been notified. ****** UPDATE ON 11/14/05 AT 1646 EST BY JOONG KO TO MACKINNON ******* "This notification is an update to previously made notification, EN# 42069. ERDS link to the NRC failed on 10/23/05, and during continuing troubleshooting efforts, Saint Lucie discovered both unit's NRC modem had failed. Due to the failure, Saint Lucie will be rescheduling Quarterly ERDS Link Test with the NRC." NRC Resident Inspector was notified of this update by the licensee. R2DO ( Mike Ernstes) notified. * * * UPDATE ON 12/20/05 AT 1157 EST BY D. WILLIAMS TO GOTT * * * "This notification is an update to previously made notification, EN# 42069. The ERDS link modems have been repaired and the Quarterly ERDS Link Test has been successfully completed on the morning of 12/20/05." NRC Resident Inspector was notified of this update by the licensee. R2DO (T. Decker) notified. | 0 | 25 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-24
42068 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-10-23 05:05 | 2005-10-23 05:30 | 2005-10-23 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING "Hurricane Warning for St. Lucie Plants 1 & 2. U-2 will be going to Mode 4 prior to Hurricane force winds on site. U-1 in refueling outage, outage risk safety assessment will be green prior to hurricane force winds on site. " The licensee indicated that all emergency diesel generators are operable on both units. The licensee indicated that they needed to restore A train component cooling water on Unit 1. The licensee is in EAL# 11A for Hurricane Warning - Unusual Event. The licensee will notify the NRC Resident Inspector. UPDATE FROM NRC (WILSON) TO NRC (KNOKE) AT 17:00 ON 10/23/05 The NRC entered into Monitoring Mode due to hurricane force winds expected to be at the site within 12 hours. * * * UPDATE ON 10/24/05 AT 2012 FROM J. HURCHALLA TO A. COSTA * * * "At 18:19 on 10/24/05 St. Lucie notified the Sate to Florida that the emergency plan declaration of Unusual Event due to hurricane Wilma had been terminated. The termination of the emergency plan declaration was made at 17:00 on 10/24/05 based on National Weather Service public advisory #39. "Currently Unit 1 is in mode 5 for a refueling outage and will continue in this mode. Unit 2 is in mode 3 and preparations are being made for restart on 10/25/05." The licensee notified the NRC Resident Inspector. Notified R1DO (Ernstes), NRR (Berkow), IRD (Wilson and Blount), OPA (Brenner), DOE (Bartlett), DHS (Frost), EPA (McCrossen), FEMA (Roland), USDA (Smeltzer), and HHS (Pyles). The NRC exited the Monitoring Mode earlier at 1315. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-10-23
42067 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-10-22 22:54 | 2005-10-22 23:24 | 2005-10-22 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WILMA "Declaration of an Unusual Event due to Turkey Point Nuclear Site in a confirmed hurricane warning due to the projected path of Hurricane Wilma." The licensee indicated all 4 EDG's were available if required, and all safety systems were also available if required. The licensee will notify the NRC Resident Inspector. UPDATE FROM NRC (WILSON) TO NRC (KNOKE) AT 17:00 ON 10/23/05 The NRC entered into Monitoring Mode due to hurricane force winds expected to be at the site within 12 hours. * * * UPDATE ON 10/24/05 AT 1904 EDT FROM BOB MEIXELL TO A. COSTA * * * "Notification of termination [at 1839 on 10/24/05] of Unusual Event at Turkey Point. All tropical storms and Hurricane watches an warnings have been terminated as of 1700 EDT for the Florida Peninsula and the Florida Keys." The licensee notified the NRC Resident Inspector. Notified R1DO (Ernstes), NRR (Berkow), IRD (Wilson and Blount), OPA (Brenner), DOE (Bartlett), DHS (Frost), EPA (McCrossen), FEMA (Roland), USDA (Smeltzer), and HHS (Pyles). The NRC exited the Monitoring Mode earlier at 1315. | 60 | 100 | 0 | 60 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-10-22
42066 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-10-20 14:20 | 2005-10-20 14:30 | 2005-10-20 | PLANNED UPGRADE OF SAFETY PARAMETER DISPLAY SYSTEM "On October 20, 2005, the Safety Parameter Display System (SPDS) is being removed from service to perform planned upgrades to the system. The removal of SPDS from service for Hope Creek also affects the transmission of data via the Emergency Response Data System (ERDS). Appropriate compensatory measures are in place while SPDS is out of service. The SPDS is expected to be returned to service in approximately 8 days. This is a voluntary/courtesy notification." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-20
42065 | 0 | INDIANA STATE DEPARTMENT OF HEALTH |  |  |  |  | 2005-10-19 16:00 | 2005-10-20 12:47 | 2005-10-20 | RADIOACTIVE SOURCE FOUND IN SCRAP YARD A scrap yard operator contacted the Indiana State Department of Health to request investigative assistance after their radiation monitor alarm sounded while monitoring a batch of trash. A Health Physicist was dispatched to the scrap yard and discovered a Cesium-137 source in the trash. Upon further investigation it was determined that the source belonged to a general licensed company which was no longer in operation. The company owned two like sources, but only source CS4464 (S/N 4699931) containing 14 millicuries of Cesium-137 was found. The found source is not leaking and it has not caused any injury to personnel. The Indiana State Department of Health has contacted Region III and will continue looking for the other missing source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-10-20
42064 | 0 | KLEINFELDER |  |  |  |  | 2005-10-19 14:30 | 2005-10-19 17:34 | 2005-10-19 | DAMAGED TROXLER MOISTURE DENSITY GAUGE On Wednesday, 10/19/05 at approximately 14:30 hours, a technician left a Troxler Model 3440 moisture/density gauge (S/N 21953) in an area where a pickup truck eventually ran over it. The location of the incident was at 275 So. Main Street in Meridian, ID. The RSO conducted a visual examination and noted that the source rod had remained inside the gauge in the shielded position. A survey meter checked the damaged gauge for radiation levels, and it read <1.2 mR/Hr. The radionuclides for the source are 40 milliCuries of Am-241/Be and 8 milliCuries of Cs-137. The Corporate RSO was called and informed of the incident. The gauge is being transported back to Troxler in Rancho Cordova, CA. for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | ID | MAT | [5 empty] | 0 | 2005-10-19
42063 | 0 | BYRON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-10-19 00:57 | 2005-10-19 02:39 | 2005-10-19 | AUTOMATIC REACTOR TRIP DUE TO LOW 2 STEAM GENERATOR WATER LEVEL "Unit 2 reactor trip on low 2 S/G level. 2A CD/CB (condensate and condensate booster pump set is driven by a single motor) tripped while 2D CD/CB was out of service. The auto turbine runback was unsuccessful and turbine was runbacked manually. ESF actuations: AF (Auxiliary Feedwater) activation and FWI (Feedwater Isolation)." Only indication on the condensate and condensate booster pump trip was an over current flag. All rods fully inserted into the core. Both the motor driven and the diesel driven auxiliary feedwater pumps are operating. All Emergency Core Cooling systems and the Emergency Diesel Generators are fully operable if needed. The NRC Resident Inspector was paged by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-10-19
42062 | 0 | IVEYCOOPER SERVICES, LLC |  |  |  |  | 2005-10-17 | 2005-10-18 17:43 | 2005-10-18 | PART 21 REPORT INVOLVING A RADIOGRAPHIC SEALED SOURCE WITH A POTENTIAL SAFEY CONCERN The following information was provided via fax: "On October 17, 2005 I became aware of a condition involving a radiographic sealed source that may prove to be a safety concern to users of the sources. The manufacturer was promptly notified of the condition and a resolution was provided to IveyCooper via memo. The attached supplier corrective action has been generated and transmitted to Industrial Nuclear for 'Root Cause' and 'Action to Prevent Recurrence' dispositions. It provides details of the discovered condition. I am providing this notification in accordance with the requirements of 10CFR21. "Date: 10/17/05 "Supplier: Industrial Nuclear Company, 35 Flagship Dr., North Andover, MA 01845 "Due Date: 12/17/05 "Material: Model 702 Radiographic Source "Quantity: 8 at IveyCooper, unknown quantity at other licensees "Description of Nonconformance: Roll pins of source connectors protrude from the source connector bodies on sources purchased from Industrial Nuclear Company in North Andover, MA. The protruding pins may increase risk of disconnect or source hanging in guide tube. Per the manufacturer roll pins should not extend past the outer plane of the connector barrel. A dial caliper was used to determine the amount of stick-out. Note: Two of the sources had been in use since January 05. No operational problems had occurred during use. "Corrective Action Taken: Per memo from Industrial Nuclear Company the roll pins were filed to a flush condition using a hand file. Sources were secured and locked within the exposure device during the operation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | TN | OTH | PAR | 21.21 |  |  |  | 0 | 2005-10-18
42061 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-10-10 | 2005-10-18 14:51 | 2005-10-18 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER GAUGE The following information was received via email: "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "STATUS: new "Licensee: Lakeside Industries "City and State: Issaquah, Washington "License Number: WN-I0233-1 "Type of License: Portable Gauge "Date of Event: October 10, 2004 "Location of Event: Port Angeles, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "In a written report dated October 14, 2005 the Licensee's RSO reported that a Troxler model 3440 moisture/density gauge had been damaged when a single drum of a roller struck and rolled over a portable gauge before the roller operator could stop. "The gauge operator had stepped 15 feet away from the gauge prior to the incident. It was then the roller rounded a corner and the roller operator's view of the gauge was obstructed by some large concrete blocks. The gauge was in the back scatter mode when struck. "The gauge housing was left intact with only some deep scratches in the base. The source rod was bent, the index rod broken, with slight damage to the plastic top shell and no apparent damage to the electronics. The Cesium source was in the shielded position and the Americium source intact. (Photographs submitted with the report substantiate this description). "Based on this information, the RSO, trained in the service and repair of Troxler gauges, instructed the operator to remove the gauge from the site and return it to the licensed storage area. When the RSO arrived, he took readings of the gauge with a Troxler 3105 survey meter and the readings were the same as the replacement gauge he brought with him. "The damaged gauge is now stored at Lakeside Industries' licensed storage facility in Centralia, Washington awaiting repair or disposal by a license service provider. "To prevent reoccurrence, gauge operators have been instructed by the RSO to be no more than 5 feet from the gauge when it is in an exposed location. "Notification Reporting Criteria: WAC 246-221-250 Notification of Incidents. "Isotope and Activity involved: 8 mCi of Cesium 137, and 40 mCi of Americium 241 Beryllium. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None expected. "Lost, Stolen or Damaged? (mfg., model, serial number): Troxler, model 3440, serial number 23475. "Disposition/recovery: Stored at a licensed storage facility awaiting repair or disposal by a licensed service provider. "Leak test? None reported post incident. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) NA "Release of activity? None reported. "Activity and pharmaceutical compound intended: NA "Misadministered activity and/or compound received: NA "Device (HDR, etc.) Mfg., Model; computer program: NA "Exposure (intended/actual); consequences: NA "Was patient or responsible relative notified? NA "Was written report provided? NA "Was referring physician notified? NA "Consultant used? No." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-10-21
42059 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2005-10-18 09:30 | 2005-10-18 14:14 | 2005-10-21 | UT EXAMINATION DISCOVERED AN UNACCEPTABLE SPRAY LINE TO PRESSURIZER WELD Ultrasonic Testing (UT) during the current refueling outage revealed three (3) indications unacceptable to ASME Section XI code on the 4 inch line "3RCS-004-224-1" Reactor Coolant System Pressurizer Nozzle to safe end weld. Two indications are circumferential, 6.4 inches and 7.7 inches in length, and the third is .25 inches long axis. This condition has existed since construction, i.e., circa 1984. There is no indication of any past RCS leakage from any of these weld defect indications. A weld overlay repair is currently in progress with five of seven passes completed which will meet ASME code requirements for all modes of operation. The licensee will inform state/local agencies and has informed the NRC Resident Inspector. ***** UPDATE ON 10/21/05 AT 1112EDT FROM DAVID DODSON TO MACKINNON ***** "An Update of Event Notification 42059 is being made to correct previous information regarding the ultrasonic examination results for the condition reported on October 18, 2005. The results of examination have been shown to reveal the presence of 3 flaws (2 circumferential flaws indicative of lack of fusion, one totaling 16.75 inches, the other 7.7 inches, and 1 axial planar flaw of 0.25 inches). NRC verbal approval of the associated weld repair process was provided 10/21/05. No further updates are expected." R1DO (John Kinneman) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-10-18
42058 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-10-17 18:16 | 2005-10-17 19:18 | 2005-10-17 | MANUAL REACTOR TRIP DUE TO LOW STEAM GENERATOR LEVEL "At 1816 EDT on 10/17/2005 Vogtle Unit 1 was manually tripped from 100% power due to lowering Steam Generator level on Loop 2. The Main Feedwater Regulating Valve for Loop 2 failed closed and operator attempts to re-open it were unsuccessful. The operators initiated a manual reactor trip when it was apparent that Steam Generator level would not be restored. Following the manual reactor trip, an automatic actuation of the Motor Driven and Turbine Driven Auxiliary Feedwater Pumps occurred due to low level in the Steam Generators. The Main Feedwater Regulating Valve for Loop 1 did not close as expected for the feedwater isolation signal (P-4 / Tavg 564 degrees F) that resulted from the manual trip. The Loop 1 Main Feedwater Regulating Valve was manually closed by the operators. All control rods are fully inserted." This incident did not affect Unit 2. Unit 1 is stable in Mode 3 and removing heat by dumping steam to the condensers. All safety related systems or equipment are available and functioning as required. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-10-17
42057 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-10-15 09:30 | 2005-10-15 13:25 | 2005-10-15 | DIESEL OIL SPILL IN EXCESS OF REPORTABLE QUANTITIES OF HAZARDOUS WASTE "On 10/15/2005, at 09:30 am CDT, Wolf Creek Generating Station Operations personnel discovered a diesel fuel oil spill on acreage controlled by Wolf Creek generating Station, at the Makeup Water Screen House. The spill was not currently active and had occurred at an unknown previous date and time. The spill amount is estimated to be in excess of "Reportable Quantities of Hazardous Waste" per 40 CFR 302.4, which is greater than 1.4 gallons. The actual spill amount is not known, however there is no puddling or runoff. The spill has been reported to the Kansas Department of Health and Environment. This [incident] requires a report to the NRC per 10 CPR 50.72 (b) (2) (xi)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-15
42056 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2005-10-15 07:02 | 2005-10-15 08:54 | 2005-10-19 | AUXILIARY FEEDWATER ACTUATION ON A MANUAL REACTOR TRIP "Auxiliary Feedwater actuation due to low steam generator level following a manual reactor trip. "At 0702 on 10/15/05, a manual reactor trip was initiated due to decreasing level on the 3C steam generator. Auxiliary Feedwater system actuated as expected due to post-trip steam generator level decrease. 3C steam generator level was restored using Auxiliary and Main feed. The cause of the loss of steam generator level control is under investigation. "The plant is stable in Mode 3 with the Auxiliary Feedwater system in standby." All control rods fully inserted. The decay heat removal path is normal feedwater through the steam generators and out the atmospheric relief valves. There are no primary to secondary steam generator tube leaks. Safety related electrical busses are powered via normal offsite power. Emergency diesel generators are available if needed. There was no impact on Unit 4. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1147 ON 10/19/05 FROM E. TREMBLAY TO P. SNYDER * * * "Updated to include notification under 10 CFR 50.72 (b)(2) for manual reactor trip." The licensee notified the NRC Resident Inspector. R2DO (Ernstes) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2005-10-15
42055 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2005-10-14 06:00 | 2005-10-14 11:31 | 2005-10-14 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "The Radiation Safety Officer at Chicago Testing Laboratory's (IL-02065-01) Elk Grove facility reported the theft of a Troxler gauge. The gauge is a model 3440 with s/n 16643. It contains 8 milliCuries of Cs-137 and 40 milliCuries of Am-241:Be. The construction gauge was stolen from the bed of a company truck early this morning between 0400 and 0630 while it was parked at the residence of the operator in Blue Island, IL. Blue Island police have investigated the reported theft. Several other pieces of construction equipment were stolen from the truck as well. The gauge was stored in its manufacturer's large yellow DOT Type A container. The gauge is designed to be used in the construction industry to determine compaction and density of soil, roadbeds, asphalt and concrete. The sealed sources have withstood direct impact from compactors and were designed with that possibility in mind. "Local police have been advised to be aware of the theft and to notify the Agency's dispatch center should the gauge be located. They were cautioned that should the gauge appear to be damaged, crushed or dismantled to not approach the device and to secure the scene pending our notification/arrival." Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Illinois Report number: IL050051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2005-10-19
42054 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-10-12 22:24 | 2005-10-12 23:55 | 2005-10-13 | AUTOMATIC SCRAM DUE TO REACTOR HIGH PRESSURE SIGNAL "Unit 2 Reactor automatically scrammed at 2224 [EDT] as a result of an RPS actuation due to Reactor High Pressure. All control rods inserted. The plant is stable. No ECCS or SRV actuation occurred. This report is made pursuant to 50.72(B)(2)(iv)(B). An investigation into the cause is currently in progress." Electric plant lineup is in a normal stable lineup. Reactor water level is being maintained via main feedwater system and removing decay heat via the steam bypass valves to the main condenser. This event had no effect on Unit 1. The licensee notified the NRC Resident Inspector, Pennsylvania Emergency Management Agency (PEMA), and the Berks, Chester, and Montgomery County emergency agencies. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-10-13
42053 | 0 | PALISADES | 1 |  |  | [1] CE | 2005-10-12 17:09 | 2005-10-12 21:55 | 2005-10-13 | PARTIAL LOSS OF PLANT PROCESS COMPUTER "Portions of the Palisades Plant Process Computer (PPC) including the Emergency Response Data System (ERDS) became inoperable due to failure of a plant inverter (EY-210). The failed inverter supplies power to portions of the PPC. The inverter failed for unknown reasons. Options for bypassing the inverter and inverter repairs are being evaluated." The licensee notified the NRC Resident Inspector. * * *UPDATE PROVIDED BY MULFORD TO ROTTON AT 0511 EDT ON 10/13/05 * * * At 0500 the Palisades Plant Process Computer (PPC) including ERDS was declared operable after bypassing plant inverter EY-210 per plant procedure and restoring power to equipment. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-10-12
42052 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2005-10-12 14:40 | 2005-10-12 16:53 | 2005-10-12 | TECHNICAL SPECIFICATION SHUTDOWN BASED ON LOSS OF TWO CHANNELS OF CONTAINMENT ISOLATION RADIATION MONITOR On 10/12/05 at 14:40 EDT, Unit 1 experienced a loss of Channel A of the CIS (Containment Isolation Signal) Radiation Monitor which, when combined with the previous existing inoperability of Channel D of the CIS radiation monitor, required Unit 1 to enter technical specification LCO 3.0.3. If the action statement [for the CIS], LCO 3.3.2.1, cannot be met, within 1 hour, action shall be initiated to place the unit in Hot Standby with the next 6 hours, Hot Shutdown within the following 6 hours, and cold shutdown within the subsequent 24 hours. Unit shutdown is in progress. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (C. MARPLE) TO NRC (HUFFMAN) AT 2145 EDT ON 10/12/05 * * * At 2101 EDT on 10/12/05, the Unit 1 exited Technical Specification 3.0.3 when Channel D of the CIS radiation monitor was returned to service. The down-power of Unit 1 was halted at 97% power. The licensee notified the NRC Resident Inspector. R2DO(Decker) informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-10-12
42051 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2005-09-08 10:08 | 2005-10-12 14:25 | 2005-10-12 | INVALID SYSTEM ACTUATION "This telephone notification is provided in accordance with 10 CFR 50.73 (a)(1), to report an invalid actuation reportable under 10 CFR 50.73 (a)(2)(iv)(A), 'Any event or condition that resulted in manual or automatic actuation of any system listed in paragraph (a)(2)(iv)(B).' General containment isolation signals affecting containment isolation valves in more than one system is identified in paragraph (a)(2)(iv)(B). "On September 8, 2005, at 1008 hours, with Unit 2 in Mode 4 'Cold Shutdown,' fuse 2-902-3-AA-F7 in the 902-3 panel blew which resulted in a partial Group 2 Primary Containment Isolation. The containment isolation signal affected containment isolation valves in more than one system. All affected containment isolation valves operated as designed. "The fuse was successfully replaced and all affected components were restored to operable status." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-10-12
42050 | 0 | PALO VERDE |  | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-10-11 16:02 | 2005-10-11 22:32 | 2005-10-11 | TECH SPEC REQUIRED SHUTDOWN OF BOTH UNIT 2 AND 3 "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On October 11, 2005 Palo Verde Nuclear Generating Station (PVNGS) Units 2 and 3 at approximately 1602 and 1655 Mountain Standard Time (MST), respectively commenced reactor shutdowns required by Technical Specification 3.0.3. "Engineering personnel were unable to demonstrate that the original design of the Emergency Core Cooling System (ECCS) could perform its safety function for its mission time under certain postulated accident scenarios. Specifically, the Refueling Water Tank (RWT) is designed with baffles to prevent a vortex from developing and air binding the Safety Injection pumps during a Loss of Coolant Accident (LOCA). On a LOCA, the High Pressure Safety Injection pumps take a suction from the RWT and inject borated water into the Reactor Coolant System (RCS). At 7.4 percent RWT level, the source of borated water by design automatically shifts from the RWT to the containment sump. However, for small break LOCA there may be insufficient containment pressure to ensure inventory is not continuing to be drawn from the RWT. This may allow the baffles in the bottom of the RWT to uncover. With the RWT baffles uncovered, a vortex may develop, leading to potential air binding of the Safety Injection pumps before the operator manually isolates the RWT. "At approximately 1333 Mountain Standard Time, based on the inability to demonstrate that the ECCS can perform its safety function under certain accident scenarios, Palo Verde Units 2 and 3 entered Technical Specification 3.0.3. "Engineering continues to evaluate this condition. "There were no RPS/ESF actuations, and none were required. "There were no structures, systems or components that were inoperable at the start of event that contributed to the event. "This condition did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. This condition did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified of this condition and this ENS notification." | 0 | 0 | 0 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | Power Operation | Power Operation |  | Hot Standby | Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2005-10-11
42049 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2005-10-10 09:35 | 2005-10-10 15:55 | 2005-10-11 | AGREEMENT STATE REPORT INVOLVING A DAMAGED TROXLER MOISTURE DENSITY GAUGE At approximately 0930 CDT on 10/10/05, a Troxler moisture density gauge, Model 3430 containing both a 8-9 mCi Cs-137 and 44 mCi Am-241:Be source, was run over by a bulldozer at the new NASCAR track construction site south of I-80 Exit 168 near Newton, IA. The State of Iowa responded to the incident and determined that the source was not breached and that there was no spread of contamination. The damaged gauge was boxed up and transported by the licensee to their office in Des Moines. The State has requested that the manufacturer, i.e., Troxler, examine the gauge at the licensee's facility before shipment to a Troxler repair facility. The State of Iowa does not plan a press release. * * * UPDATE FROM D. FLATER TO M. RIPLEY 0715 ET 10/11/05 * * * The State reported that the serial number of the damaged gauge is 32198. Notified R3 DO (B. Burgess) and NMSS EO (T. Essig) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2005-10-13
42047 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-10-08 10:00 | 2005-10-08 18:33 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * CRITICALITY ALARM SYSTEM INOPERABLE IN THE NDA/LOADING DOCK AREA DUE TO DETECTOR FAILURE "The NDA RMS-3 detector pair had stopped communicating with the RadNet computer in early September. The RadNet program is not required to actuate the criticality alarm, but is used for detector monitoring and diagnostics. This pair of readouts is in a remote location and are not monitored frequently. On 10/8/05 while performing monthly meter checks and semi-annual calibration the following was noted: 1) NDA East background 10-20 µR/hr, NDA West 0.2 - 0.4 Mr/hr; both had green normal lights. 2) Conducted internal source check, NDA West - normal. 3) Conducted internal source check NDA East- only read 1.1 Mr/hr when >10 Mr/hr is expected, source check took much longer than is normal. 4) Attempted to calibrate East detector, when exposed to 20 Mr/hr indicated 200-300 µR/hr, when exposed to 100 Mr/hr indicated 4 Mr/hr. Normal alarm setpoint is 20 Mr/hr. 5) Attempted to communicate with NDA East RMS-3 with a local computer, but it would not communicate. 6) Replaced detector, no change noted. 7) Replaced RMS-3 internals with a spare RMS-3. This RMS-3 started communicating with the RadNet program normally and was calibrated normally. When the NDA East RMS-3 was turned off for replacement, the NDA West also started communicating with the RadNet program. "NDA East detector was last calibrated on 8/18/05 due to the replacement of NDA West detector. Locally source checked when communications initially failed on 9/9/05." A valid signal from both detectors is required in order to initiate a criticality alarm. The source check performed on 9/9/05 may not have confirmed detector operability since it utilized a RadNet generated input signal. The licensee noted that no known condition requiring operation of the criticality alarm system had occurred in this portion of the facility, i.e., the [DELETED] corridor of the Bldg. [DELETED] complex, during the interval when the criticality alarm system was inoperable. At 1800 hours following replacement of the NDA East RMS-3 internals, all recalibrations and tests confirming operability of the entire criticality alarm system had been completed satisfactorily. The licensee informed the NRC Resident Inspector. * * * UPDATE 0938 EST ON 11/4/05 FROM RIK DROKE TO S. SANDIN * * * The licensee is retracting this report based on the following: "On October 8, 2005, Nuclear Fuel Services, Inc. (NFS) made a 24-hour telephone notification to the NRC Operations Center based on Title 10 CFR Part 70.50 (b) (2). This section requires a 24-hour report for an event in which equipment is disabled or fails to function as designed when: (1) the equipment is required by regulation or license condition to prevent releases exceeding regulatory limits, to prevent exposure to radiation and radioactive materials exceeding regulatory limits, or to mitigate the consequences of an accident; (2) the equipment is required to be available and operable to perform the required safety function; and (3) no redundant equipment is available and operable when it is disabled or fails to function. The report was made on a Saturday by a maintenance team engaged in repair and calibration of the NFS Criticality Accident Alarm System (CAAS), when it was observed that a single detector in the network did not respond to a calibration check as expected. The detector and read-out meter were immediately removed from service, replaced with a properly calibrated unit, and system operability restored. "On Monday, October 10, 2005, when the NFS Nuclear Measurements Department staff returned to work, and were able to evaluate the CAAS technical basis documentation, it was determined the SNM process and storage area monitored by the out-of-calibration CAAS detector was monitored as well by several other detectors in adjacent areas. Upon further testing of the subject detector in the laboratory, it was demonstrated a redundant electrical circuit in the unit especially designed for nuclear criticality monitoring purposes (which is independent of detector calibration) would have enabled the unit to initiate an alarm in the event of a criticality event. Therefore, for two entirely separate reasons, redundant equipment was available and operable to perform the required safety function during the period of time the subject detector was out of calibration. This information was discussed and reviewed with the NFS Resident NRC Inspector during the week of October 10, 2005. Based on this information and discussion with the NRC Inspector, it is requested that this event report be retracted." The licensee informed the NRC Resident Inspector. Notified R2DO (David Ayres) and NMSS (Trish Holahan). * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
42046 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-10-08 07:20 | 2005-10-08 08:20 | 2005-10-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE CONTROL ROOM CHILLER TRAIN "'B' Train Control Room Chiller inoperable due to being aligned to Unit 1 Nuclear Cooling Water Train 'B.' This is a normal alignment for Unit 1 ESF 'B' Train testing. When we attempted to start 'A' Train Control Room Chiller, it failed to start. This placed Unit 2 in Tech Spec 3.0.3 at 0320 on 10/08/05. Unit load reduction started at 0720 on 10/08/05." The licensee stated that the load reduction was terminated at 0815 on 10/08/05 based on a Notification of Enforcement Discretion (NOED) granting a 24-hour extension. The licensee notified the NRC Resident Inspector. | 0 | 88 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-10-08
42045 | 0 | BRAUN INTERTEC |  |  |  |  | 2005-10-07 10:00 | 2005-10-07 18:05 | 2005-10-07 | RADIOGRAPHY CAMERA SOURCE TEMPORARILY UNABLE TO RETRACT When performing radiography at Marathon Petroleum located in St. Paul Park, MN, a radiography source was unable to be fully retracted due to a dent in the guide tube tip caused by a collimator set screw. The camera is an AEA Model 660B Serial # B1839 which contains a 22 curie Iridium-192 source. The licensee personnel called their radiation safety officer (RSO) who assessed the situation. The RSO using shielding and other equipment was able to unscrew the guide tube tip with the collimator attached to allow the source to retract. There were no personnel overexposures. The licensee checked their remaining guide tube tips to ensure that the same problem did not exist on the other tips. The Licensee notified Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2005-10-07
42044 | 0 | GUARDIAN AUTOMOTIVE |  |  |  |  | 2005-10-06 21:00 | 2005-10-07 16:38 | 2005-10-07 | LOST GENERAL LICENSED MATERIAL On 10/6/05 Guardian Automotive lost the barrel of an air gun used to ionize automotive parts in a manufacturing process. The company searched for the material but was unable to locate it. It is thought that the material may have been inadvertently disposed of in the trash. The material consisted of a 2 to 3 inch long by less than 1 inch in diameter section of an air gun with a 5.41 millicurie (maximum) Po 210 source inside. The gun was made by NRD LLC. The model number of the air gun is P-2000. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-10-07
42043 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-10-06 09:30 | 2005-10-06 15:53 | 2005-10-06 | FITNESS FOR DUTY REPORT INVOLVING A LICENSED EMPLOYEE A licensed employee had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.73 |  |  |  | 0 | 2005-10-06
42042 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-10-06 11:00 | 2005-10-06 13:57 | 2005-10-14 | OFFSITE NOTIFICATION - OIL SPILL TO NAVIGABLE WATERS There was an "oil spill to navigable waters (Lake Wylie), requiring DHEC [Department of Health and Environmental Control] SC [South Carolina] notification." The oil was in an onsite yard drain. The site staff was not aware of the oil in the drain. Before the yard drain was emptied, rains caused the yard drain to overflow resulting in oil entry into the lake. "Site hazmat response [was] initiated. An offsite agency will be called in to assist in the clean up. At this time the source of the spill is unknown. [The] oil spill does not appear to be ongoing." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 11/14/05 AT 1605 EDT FROM EVERETT TO COSTA * * * "Catawba Nuclear Station Environmental, Department determined that an update to the 10/06/05 oil spill was required and the update was given at 13:58 on 10/14/05. The original notification to the Department of Health and Environmental Control (DHEC) identified oil in navigable waters, but did not identify the underground line used to transfer diesel fuel from a sump to an underground used oil tank as the potential oil source. "Catawba is in the process of developing plans to excavate the suspect piping area in order to evaluate the piping and repair/replace as necessary. These plans will include mitigation strategies for materials contaminated by the spill event. The suspect piping has been isolated and the oil removed from the affected navigable waters." The licensee notified the NRC Resident Inspector. Notified R2DO (Decker). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-06
42041 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-10-05 15:20 | 2005-10-05 21:22 | 2005-10-05 | TRITIUM DETECTED IN TRANSFORMER YARD MONITORING WELL "On October 5, 2005, at approximately 1520 hours a condition report was written to report that tritium was detected in monitoring well MW-111 located in the Indian Point [Unit] 2 transformer yard. The sample indicated 2.11E-4 micro curies per cc [cubic centimeter]. Other [nearby] sampling wells showed negative. Follow up samples and an investigation are in progress. The sampling that was done was part of an ongoing investigation to verify and quantify previously identified leakage, potentially from the spent fuel pool. Courtesy calls have been made to local officials to notify them of these findings." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2005-10-05
42040 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-09-29 02:00 | 2005-10-05 16:29 | 2005-10-05 | OHIO AGREEMENT STATE REPORT - PORTABLE DENSITY GAUGE DAMAGED "Portable density gauge was damaged by [an] intoxicated driver while [the] gauge was in use at approximately 2:00 AM. Licensee personnel were able to retract [the] source rod into [the] damaged case. [The] shielding appeared to be intact. Readings on [the] damaged gauge at one meter with [the] rod retracted were 0.2 to 0.3 Mr/hr. [The] Gauge was placed in [a] transport case and returned to [the] licensee's storage location. Licensee performed [a] leak test and is awaiting results. Initial survey of [the] area around [the] damaged gauge indicated no contamination or evidence of leakage of [the] source. Gauge to be surveyed, packaged and prepared for shipment by local service provider (Cline Technical Services). Gauge is a Troxler Model 4640-B with 8 mCi (millicuries) Cs-137 source." Corrective Action: Equipment returned to manufacturer for repair or disposal. Manufacturer: Troxler Model Number: 4640-B Serial Number: 1122 Item Number: OH050006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-10-10
42039 | 0 | BOEING COMPANY |  |  |  |  | 2005-09-07 13:00 | 2005-10-05 14:27 | 2005-10-05 | EXIT SIGNS CONTAINING TRITIUM BELIEVED TO HAVE BEEN TAKEN TO LOCAL LANDFILL On 09/07/05 during an inventory check it was discovered that 9 exit signs were missing from Building 102C, used as a storage building, at Boeing Company located in Berkeley, MO (suburb of St. Louis). They were last seen in May of 2005. The person that looks after the signs took an extended sick leave for several weeks during July. Three of the Exit signs were made by Self Powered Lighting and the other 6 were from SRB. The original total activity of the 9 Exit Signs was 119 curies and the current total activity of the Exit Signs is now 54 curies. It is believed that the Exit Signs were discarded in a dumpster and then the dumpster was taken to the local landfill. Exit Signs were made between 1988 and 1996. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-10-05
42038 | -1 | PHILADELPHIA VA MEDICAL CENTER |  |  |  |  | 2005-10-03 | 2005-10-05 13:17 | 2006-02-03 | MEDICAL EVENT - SOME BRACHYTHERAPY SEEDS ADMINISTERED TO WRONG SITE "l am calling per 10 CFR 35.3045 to notify you of a possible medical event at the VA Medical Center, Philadelphia, Pennsylvania. On October 3, 2005 a permanent implant prostate brachytherapy procedure was performed at the medical center. A written directive prescribed 90 Iodine 125 seeds to be implanted in the patient's prostate. "However, 45 of the seeds were implanted mistakenly in bladder. The seeds were recovered from the bladder prior to completion of the procedure in the operating room. "The written directive was revised by the authorized user prior to completion of the procedure in the operating room to document the actual number of seeds implanted in the prostate (45). "Based on dosimetry calculations performed October 4, 2005, a medical event may have occurred since the dose to the prostate and other tissues may differ from that originally prescribed in the written directive by values greater than those given in 10 CFR 35.3045. "These circumstances appear to be similar to a previously reported event (Event No. 39586), which NRC ultimately decided did not represent a medical event. "However, the NHPP has decided conservatively to perform an on-site review at the medical center next week to assess the particular circumstances of this event." At the time of this report the licensee did not know why the event happened but will be investigating to determine the cause and the significance on 10/13/2005. The licensee stated that the patient was notified of the situation. * * * RETRACTION AT 14:05 EST ON 2/3/2006 FROM GARY WILLIAMS TO ABRAMOVITZ * * * "Based on our discussions with NRC Region III, the circumstances for event do not meet the definition in 10CFR35.3045 as a medical event." Contacted the R1DO (Meyer), R3DO (Riemer), and NMSS EO (Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2005-10-05
42037 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-10-03 20:15 | 2005-10-04 14:57 | 2005-10-04 | FITNESS FOR DUTY "A non--licensed contractor supervisor had a Medical Review Officer (MRO) determined positive for alcohol during a "for cause" test. The employee's access to the plant has been terminated." The NRC Resident Inspector was notified of this event by the licensee. Contact the Headquarters Operation Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MO | POW |  | 26.73 |  |  |  | 0 | 2005-10-04
42036 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2005-09-20 | 2005-10-04 07:30 | 2005-10-04 | AGREEMENT STATE REPORT - MEDICAL UNDEREXPOSURE On Thursday morning, 9/20/05, a technologist gave a cancer patient receiving Iodine-131 therapy only one capsule of a prescribed 2-capsule dose. Consequently, only 93 milliCuries of an ordered 150 milliCuries was delivered to the patient. The referring endocrinologist was notified and determined that his patient had received adequate amount for the patient's therapy. On Thursday afternoon, the licensee's Manager of Nuclear Medicine telephoned the Department and reported that the technologist involved in the event had also been responsible for a previous misadministration and had been fired. The capsule that was not administered was found in the lead container while preparing for a subsequent procedure on another patient. Georgia report number: GA-2005-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2005-10-07
42035 | 0 | OK DEPT OF ENVIRONMENTAL HEALTH |  |  |  |  | 2005-10-03 11:00 | 2005-10-03 18:43 | 2005-10-05 | AGREEMENT STATE REPORT ON A SOURCE OF UNKNOWN ORIGIN FOUND AT METAL PROCESSOR The State representative reported that scrap metal received by a metal processor in Sand Springs, OK, set off the facility's gate radiation monitor. Investigation into the alarm determined that the radiation was coming from a foil source of unknown origin. The source dimensions are 3 inches by 1/2 inch with a contact reading (using a Ludlum Model 3) of 200 mR/hr. The scrap metal processor notified the State which dispatched inspectors to the site. The State found that the source also had loose surface contamination. Investigation has determined that four individuals had handled the source. The State was able to contact one of those individuals and a survey of the individual revealed no indication of contamination. The State has not yet been able to contact the other three people involve in handling the source. The source has been wrapped in lead shielding material and secured in a safe location. The State plans to perform a Gamma Spec analysis of the source to determine the isotope. The investigation into the origin of the source has been unproductive so far. It appears that the scrap metal came from a intermediary scrap metal dealer. * * * UPDATE ON 10/5/05 @ 15:20 FROM SAMPSON TO ABRAMOVITZ * * * The source (foil) was determined to be Radium-226. The Curie content was not determined but was estimated to be in the micro Curie range. The loose contamination was not found on any other surfaces, only on the test swipe. The four individuals who contacted this source were contacted and an estimate of their dose is in progress. Notified R4DO D. Graves. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2005-10-06
42034 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-10-03 12:48 | 2005-10-03 14:34 | 2005-10-03 | OFFSITE NOTIFICATION MADE TO PENNSYLVANIA EMERGENCY MANAGEMENT AGENCY (PEMA) "At 12:48 PM EST, the Main Control Room was notified that an individual needed medical assistance at the South Building. The individual was experiencing chest pains. An ambulance was requested to the site, and arrived on site at 13:17 PM. The individual is not contaminated and was transported offsite to a local hospital at 13:35 PM. PEMA was notified of the incident. "This requires a voluntary report due to the offsite notification on an emergency vehicle responding to the site." The NRC Resident Inspector was notified of this voluntary notification. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-03
42033 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-10-03 07:51 | 2005-10-03 08:08 | 2005-11-16 | AGREEMENT STATE REPORT - TWO STOLEN MOISTURE DENSITY GAUGES "Two Troxler Gauges stolen from storage container at temporary jobsite. NCDOT Gauge Manager called NC Radioactive Materials Branch at 7:45 AM to alert AGENCY. Only two gauges were stolen, and a torch was used to cut the security lock from the container. "Location of job site: NC Highway 98 Bypass in Wake Forest, NC. "Troxler Model 3450, Serial #298 - 8 mCi (milliCuries) CS-137, 40 mCi Am-241. "Troxler Model 4640B, Serial #952 - 8 mCi Cs-137." The Agreement State notified: NC PIO, FBI, SBI, Troxler, and the NCHP. NC Incident # 05-34. * * * UPDATE ON 10/3/2005 @ 11:25 FROM JEFFRIES TO ABRAMOVITZ * * * "Troxler 3450 S/N 298 Cs-137 8 mCi S/N 750-5221 and Am-241:Be 40 mCi S/N 472355 "Troxler 4640B S/N 952 Cs-137 8 mCi S/N 50-9198 "Chain link fence was cut with bolt cutters. Gauges were stored in rear of tractor trailer storage unit. Torch and bolt cutters used to remove lock on trailer. Gauges with cases no longer on site. Both gauges had trigger locks and were locked in respective cases." Contacted the R1DO (Rogge), the NMSSEO (Morell), and E-mailed TAS. * * * UPDATE AT10:05 EST ON 11/16/05 FROM JEFFRIES TO KNOKE * * * The State provided an update indicating one of the Troxler gauges (4640B, s/n 952) was recovered in a scrap metal yard. The source and shielding were intact and in place. Investigation is continuing. Notified R1DO (Barkley), R2DO (Evans), NMSS (Burgess), and TAS (Whitney email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-10-06
42032 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-10-01 10:59 | 2005-10-01 15:03 | 2005-10-06 | OFFSITE NOTIFICATION CONCERNING AN INDUSTRIAL ACCIDENT "On 10/01/2005 at approximately 1059 hours CDT, an industrial safety accident occurred at Browns Ferry that involved the serious injury of a contract employee working on the Unit 1 Recovery Project. During transportation of a Small Article Monitor (SAM) into the Reactor Building access area, the equipment fell injuring two contract personnel, one seriously. Both personnel have been transported to an offsite medical facility. Neither were contaminated. "An accident investigation has been initiated by TVA. The BFN NRC Senior Resident Inspector has been notified. No other government agencies have been notified as of the time of this report. No plant systems were affected as a result of this event. BFN Units 2 and 3 remain at 100% power at this time. [Unit 1 is defueled]. "TVA has received media inquiries concerning this event. As a result, this event is considered reportable under 10CFR50.72(b)(2)(xi), 'Any event or situation, related to the health and safety of the public or on-site personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include on-site fatality or inadvertent release of radioactively contaminated materials.' " * * * UPDATE FROM VAUGHN TO HUFFMAN AT 1435 EDT ON 10/02/05 * * * "The accident investigation is being conducted by L.E. Myers Company, the contract company that employs the two injured workers. TVA is providing oversight for the accident investigation. OSHA and the State of Alabama have been notified of the event." The licensee will notify the Resident Inspector of this update. R2DO (Payne) notified. * * * UPDATE FROM VAUGHN TO SNYDER AT 1239 EDT ON 10/06/05 * * * "The L.E. Myers Co. employee who was seriously injured on 10/01/05 while moving a Small Article Monitor (SAM) unit passed away early Thursday, 10/06/05. TVA has informed the NRC Senior Resident Inspector at Browns Ferry, and the accident investigation conducted by L.E. Myers Co. is ongoing with TVA oversight." The licensee notified the NRC Resident Inspector. Notified R2DO (Bonser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-10-01
42031 | 0 | WHITE SANDS MISSLE RANGE |  |  |  |  | 2005-09-30 15:30 | 2005-10-01 14:40 | 2005-10-01 | STUCK SOURCE IN PANORAMIC DRY-SOURCE IRRADIATOR The licensee reported their irradiator had a 13 kCi Co-60 source stuck in the exposure cell. The remote area monitor registered a reading of 70 mR/hr for the area near the source. No personnel radiation exposure occurred. The irradiator building was vacated and an exterior barrier was positioned so personnel exposure would be limited to <2mR/hr. The source is from MDS Nordion, C132 - Type 72. The irradiator is a panoramic, dry-source storage which uses pneumatic air as the driving force. The licensee, who had just completed maintenance on the device, was conducting operational tests when the source stuck. The source, which is lodged in the exposure head inside the exposure cell, is prevented from being retracted by a piece of metal called a "head switch". The licensee unsuccessfully tried to free the source by applying high pressure air. The next step the licensee is considering is the possible use of a robot. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSHIELD STUCK SOURCE | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 36.83(a)(1) |  |  |  | 0 | 2005-10-01
42030 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-09-30 06:05 | 2005-09-30 14:59 | 2005-09-30 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a "for-cause" test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | OTHER UNSPEC REQMNT |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2005-09-30
42029 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-09-30 09:45 | 2005-09-30 13:08 | 2005-09-30 | POTENTIAL VULNERABILITIES DISCOVERED DURING DESIGN BASIS FIRE REVIEW "During a design basis fire in area A-8 (2000 level auxiliary building), [the licensee determined that] a number of Train A components, including the Train A motor driven auxiliary feedwater pump (control and power cables), are affected. Also, the turbine driven auxiliary feedwater pump (control cables) may not be available. In addition, the following spurious actuations could occur: "1.Pressurizer PORV BBPCV0455A opens and block valve BBHV8000A fails to close (Train A). 2. Steam Generator A ARV ABPV0001 spuriously opens and cannot be controlled from the control room (Train A). 3. Steam Generator C ARV ABPV0003 spuriously opens and cannot be closed from the control room (Train A). 4. Both VCT outlet valves BGLCV0112B and BGLCVO112C fail to close and normal letdown isolates, causing a reducing inventory in the VCT and possible hydrogen intrusion into the charging pump suction (Trains A & B). 5. Normal charging pump power cables pass through this fire area and may be damaged, causing the NCP to trip. 6. RHR suction valve from the RWST, BNHV8812A, loses power and containment sump valve EJHV8811A opens, causing the RWST to drain to the containment sump (Train A). 7. BIT inlet valve EMHV8803B fails to open from the control room hand switch (Train B). "Actions taken or planned: 1) Detection / Suppression systems available in area A-8 are functional. 2) Hourly fire watch established IAW AP 10-104, Breech procedure." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2005-09-30
42028 | 0 | HALLIBURTON ENERGY SERVICES |  |  |  |  | 2005-09-26 | 2005-09-30 11:26 | 2005-09-30 | NUCLEAR GAUGES LOST OFFSHORE DUE TO HURRICANE RITA On 9/30/05, Rowan Companies of Houston, TX reported to the licensee that two generally-licensed slurry density gauges sank along with the drilling rig they were installed on due to Hurricane Rita. The rig was abandoned prior to the hurricane's approach and so the event date is an estimate. The rig is the Rowan Odessa owned by Rowan Companies. The rig was located at Ship Shoal 250 (distance offshore and depth of water not provided). Rowan Companies performed aerial searches of the area in an attempt to find the rig. Both gauges are Halliburton 10-SD gauges with Cs-137 sources manufactured by Isotope Products. The first device has serial number V32-0246 with a current source activity of 11.11 milliCuries (source serial number DB-076). The second device has serial number W2C-097 with a current source activity of 9.4 milliCuries (source serial number DB-140). The licensee notified NRC Region 4 (J. Whitten). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-09-30
42027 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2005-09-30 05:10 | 2005-09-30 11:39 | 2005-09-30 | EMERGENCY ASSESSMENT CAPABILITY INOPERABLE FOR GREATER THAN ONE HOUR "On 9/30/2005, an unplanned loss of the Emergency Response Data Acquisition and Display System (ERDADS) output to the Unit 2 control room occurred for greater than one hour. This event is considered a loss of emergency assessment capability in accordance with the guidance provided in St. Lucie Plant procedures. Maintenance activity is ongoing to restore ERDADS capability to the Unit 2 Control Room. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-09-30
42026 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-09-28 | 2005-09-29 19:21 | 2005-09-29 | CALIFORNIA AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "The licensee called Granada Hills office on 09/28/05 to report a damaged Humboldt moisture density gauge, Model 5001, S/N 1976, at a job site in Panorama City area in Los Angeles, CA. This information was forwarded to RHB-Berkeley on 09/29/05. According to the report provided by the RSO, the gauge was set off to the side of the area being tested while holes were being made for testing and during that time a 966 E rubber tire loader ran over the gauge. This caused the tip of the rod that contained the source to snap off. According to the RSO, he picked up the source rod tip with pliers and inserted it into the gauge shield. An aluminum rod was also placed into the hole to keep the source rod tip in place in the shielded area. A leak test was performed and the swabs were sent overnight for testing to Pacific Nuclear Technology. Licensee is awaiting for the leak test results. The licensee will be providing RHB with additional information." Although not stated in the report, these gauges typically contain 40 millicuries of Am-241/Be and 10 millicuries of Cs-137. California Report # 092805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-10-04
42025 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-09-29 15:34 | 2005-09-29 18:13 | 2005-09-29 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE "During venting of the HPCI discharge line, a steady stream of water was not obtained. Venting was conducted for approximately 30 minutes. "HPCI was declared inoperable as Surveillance Requirement SR 3.5.1.1 (for verifying ECCS injection subsystem piping is filled with water from the pump discharge valve to the injection valve) was unable to be satisfied. "This unplanned HPCI System inoperability is reportable under 10 CFR 50.72(b)(3)(v)(D) as a single train failure that could have prevented the fulfillment of a safety function of structures or systems designed to mitigate the consequences of an accident." The licensee stated that the cause of the venting problem is still under investigation. The HPCI inoperability places the licensee into a 14 day LCO. The NRC resident has been notified. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-09-29
42024 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2005-09-29 13:10 | 2005-09-29 14:49 | 2005-09-29 | MANUAL REACTOR TRIP DUE TO LOSS OF CIRCULATING WATER PUMPS The licensee reported that high wind and wave action at the site has resulted in sea weed and related debris buildup at the Unit 3 intake structure. The traveling screens were unable to keep pace with the debris buildup and two out of six circulating water pumps tripped on high differential pressure across the traveling screens. Based on procedural requirements, the licensee is required to manually trip the plant due to the loss of the two circ water pumps. The reactor trip was characterized as uncomplicated with all systems functioning as required. All rods fully inserted. No primary or secondary relief valves lifted. Auxiliary feedwater automatically started as expected and is supplying cooling water to the steam generators. Decay heat is being discharged to the condenser via the turbine bypass valves. The plant is stable in hot standby at no-load temperature and pressure. The plant trip had no impact on Unit 2. The debris buildup on the Unit 2 intake is being monitored but is less of a problem due to the orientation of the Unit 2 intake structure. The NRC Resident Inspector has been notified by the licensee. The licensee has also notified State and local authorities and has made a press release. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-09-29
42023 | 0 | ST. VINCENT HOSPITAL |  |  |  |  | 2004-03-11 | 2005-09-28 17:16 | 2005-09-28 | MEDICAL EVENT INVOLVING TREATMENT TO WRONG LOCATION "As a result of a retrospective review of HDR brachytherapy cases, a medical event was discovered. This event occurred on March 11, 2004, which involved a single esophageal HDR brachytherapy treatment. In this case, a 62 year old female patient, was treated with a Nucletron High Dose Rate (HDR) brachytherapy remote afterloader for esophageal cancer . The physician Authorized User (AU) prescribed a dose of 500 cGy at 0.5 cm from the surface of a N/G tube (naso-gastric tube) for an active length of 8.0 cm using a 8.49 Curie Iridium-192 source. The treatment plan called for 17 indexer step positions at 5.0mm spacing to begin at dwell position 23 and terminating at dwell position 39. The medical physicist entered 17 indexer step positions with 5.0 mm spacing at dwell positions 1 through 17 and treatment was delivered. "As the intended delivery site was to be delivered an intended dosage of 500 cGy for one fraction for a total of 500 cGy, the dose delivered to the unintended site was 500 cGy while the intended treatment site was not treated. "This patient is now deceased. It is not believed this medical event was a significant contributing factor in the cause of death when consideration of the prognosis of the disease is given. "Although this medical event occurred March 11, 2004, it was discovered 17:45 ET on September 27, 2005, as a result of a retrospective review." The licensee has notified Region 3 (Madera and Mulay) about this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2005-09-28
42022 | 0 | SAINT-GOBAIN PERFORMANCE PLASTICS |  |  |  |  | 2005-09-26 | 2005-09-28 15:02 | 2005-09-28 | MISSING TWO KRYPTON-85 THICKNESS GAUGES Saint-Gobain Performance Plastic located in Hoosick, NY, said that they are missing two 500 millicurie Kr-85 thickness gauges (500 millicuries in 1967, half life 10.4 years) from their Saint-Gobain Performance Plastic company in New Haven, CT, which was closed in late 2003 or early 2004. The Kr-85 thickness gauges license number is 20-01382-02 (license expired in 1994 and were licensed through LFE Industrial System Corp.). Caller stated that the krypton thickness gauges were not licensed through the State of New York but to CT which is an NRC non-agreement state. On 09/26/05 the two krypton thickness gauges were discovered missing while putting together an ionizing radiation report for the State of CT for the radioactive materials that were located in their New Haven facility. The two krypton thickness gauges were made by LFE Tracer Units (now known as EGS Gauging located in MA) and each contained 500 millicures of Kr-85 as of 1967. Based on a total of activity 1000 millicuries for the two Kr-85 thickness gauges at the end of 1968 as of 2005 the total activity of the two thickness gauges would be around 85 millicuries (37years, half life 10.4 years). Model number of the two gauges are S-6A and their serial numbers are 24A & T9A. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-09-28
42021 | 0 | WYLE LABORATORIES |  |  |  |  | 2005-09-23 | 2005-09-27 17:39 | 2006-01-25 | MATERIAL DEFECT REPORT The licensee provided the following information via facsimile: "Pursuant to 10 CFR Part 21, this letter notifies the NRC of the existence of a possible defect in Bussmann KWN-R fuses. "The defect is a poor solder connection of the fuse link assembly to the rejection ferrule. The defect applies potentially to all KWN-R fuses. "An evaluation was performed and determined that this defect can create a substantial safety hazard or contribute to circumstances that would exceed safety limits as defined in the technical specifications of a license issued pursuant to 10CFR50. Safety-related circuits that include fuses with this defect may not be able to perform their safety-related function as required during a design basis event. Therefore, this potential defect is reportable per 10 CFR Part 21. "DESCRIPTION OF ANOMALY: The customer reports that the fuse lost electrical continuity while in service. The customer cut the fuse open and found the fuse element intact and a lack of electrical continuity across the soldered connection of the element to the rejection ferrule of the fuse. According to the customer, the fuse had been in service since 3/31/05 carrying 2 - 3 amperes, and there were no overcurrent events which caused the fuse to open. "DISPOSITION - COMMENTS - RECOMMENDATIONS: The customer returned the fuse to Wyle for failure analysis. Wyle forwarded the fuse to the manufacturer for evaluation. The manufacturer found a poor solder connection on the rejection cap. Apparently the cap did not get hot enough to reflow solder during the manufacturing process. The manufacturer stated the issue could be isolated to this particular fuse due to placing it in an incorrect bin, but the issue may extend to other fuses due to a process problem. Based on the evaluation, a potential defect exists in other KWN-R fuses. "As a screening test to ensure a good soldered connection, the manufacturer recommends performing a Current Carrying Capacity Test for 30 minutes at 110% of rated current after warm up at 100% of rated current. "This anomaly impacts qualification of KWN-R fuses. Only KWN-R fuses that pass the 110% Current Carrying Capacity Test are qualified." * * *UPDATE PROVIDED BY BATEMAN TO ROTTON AT 0942 EST ON 01/25/06 * * * The manufacturer provided the following information via fax: "This letter provides an update to the referenced letter that Wyle submitted to the NRC on the above subject [on 09/27/05] "The KWN-R fuses affected are limited to [less than or equal to] 30 amps. KTN-R fuses [less than or equal to] 30 amps are added to the referenced Part 21 notification since these fuses are manufactured using the same process as the KWN-R fuses. "Thus far, poor solder joints have been found in 3, 6, and 10 amp KWN-R fuses. In addition to the date codes previously mentioned (L05, M37, M17), poor solder joints have also been found in date codes L11, L19, M07, M20, M40. "Poor solder joints have also been found in 3, 4, 5, and 15 amp KTN-R fuses of the 1987-1991, vintage (no date code on fuses). "When performing the 110% Current-Carrying Capacity Test, the fuses should be warmed up at 100% until their temperature and the voltage drop across them are stable before applying 110% current to avoid blowing the fuses. "A mechanical drop test has been added to the KWN-R and KTN-R manufacturing process. This drop test should be added to the screening process. The drop test consists of: 1. Measure and record the fuse resistance. 2. Drop the fuse though a 3 foot pipe onto a laminated workbench onto the non-rejection end of the fuse. 3. Measure the fuse resistance after the drop. 4. Acceptance Criteria: Fuse resistance should be the same resistance after the drop (+/- 10%) and within the manufacturer's specified range." Notified R1DO (Perry), R2DO (Payne), R3DO (Lipa), R4DO (Spitzberg), and NRR (Tabatabai) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | AL | OTH | PAR | 21.21 |  |  |  | 0 | 2005-09-27
42020 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-09-27 10:00 | 2005-09-27 17:15 | 2006-06-06 | POSTULATED FAULTS HAVE ELECTRICAL CURRENT IN EXCESS OF THE MAXIMUM LISTED INTERRUPTING RATINGS. "NMC (Nuclear Management Company) has identified certain equipment in the PBNP electrical distribution system that will not assure, under certain conditions, interruption of a three phase bolted fault short circuit. These postulated faults have electrical current in excess of the maximum listed interrupting ratings for designated circuit breakers and associated bus bar bracing. This condition affects the 13.8 Kv, 4.16 Kv, and 480 V power panels, motor control centers (MCCs), and switchgear. Although the probability of bolted faults is considered low, the Point Beach bolted fault analysis is based on the worst case assumption of three phases firmly tied together and grounded. A postulated bolted fault itself would only impact equipment in a single safety train. However, the PBNP Appendix R analysis relies on breaker coordination and fault current interruption to prevent loss of safe shutdown equipment due to common enclosure/power supply associated circuit concerns. The degraded breaker coordination resulting from a bolted fault condition does not satisfy the requirements of the Appendix R safe shutdown analysis. "This condition is reportable because the PBNP Appendix R analysis is based on the occurrence of a single fire in a single fire area. The postulated condition could result in a loss of safe shutdown equipment functionality beyond that previously analyzed. "Compensatory measures (i.e., fire rounds - 6 times per day) have been implemented for cases where the unprotected cable length was routed beyond the original fire area. As part of the long-term corrective action, transformer tap setting changes to reduce bus voltages are being evaluated." The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE RECEIVED FROM RYAN RODE TO JOE O'HARA AT 1855 ON 04/06/06 * * * "This is a supplemental emergency notification based on additional information identified regarding degraded voltage conditions at PBNP. On 09/27/2005 NMC reported a condition where certain equipment in the PBNP electrical distribution system would not assure, under certain conditions, interruption of a three-phase bolted fault short circuit. Licensee Event Report (LER) 266 & 301/2005-005-00 was subsequently submitted on November 18, 2005. The original Event Notification Report was associated with bolted fault conditions that potentially resulted in additional unanalyzed fire losses due to direct fire damage or uncleared faults on associated circuits. The synopsis of the LER addressed these issues, and also identified: "1. A non-conservative Technical Specification for degraded voltage time delay relay settings and their setting tolerance range in calibration procedures that could have resulted in certain safety system motors and switchgear tripping on overcurrent. Such an event could have prevented the fulfillment of the motors' safety function to mitigate the consequences of an accident. "2. Under a design basis loss of coolant accident concurrent with a reduced voltage condition, safety-related motors and switchgear may trip their protective devices on overcurrent without the degraded voltage relays being actuated. Affected equipment included certain safeguards 480V AC switchgear, 480 V AC motor control centers, both auxiliary feedwater pump motors, and one component cooling water pump motor. "Corrective actions for the above issues included placing calibration procedures on administrative hold, implementation of compensatory measures consisting of fire rounds for affected zones, and administrative controls to assure that a more restrictive limit for the degraded voltage allowable value was in place for the affected Technical Specification (s), as well as implementing administrative controls on the management of 480 V loads. "Long-term corrective actions are evaluation and implementation of analytical changes resulting from the completed analysis, plant modification changes as needed to address minimum bus voltage and submittal of a license amendment request. "Additional reviews into the extent of condition of this issue have revealed additional potential concerns associated if a station battery charger load test is conducted under reduced or degraded grid voltage conditions. If a battery charger load test is conducted during a degraded grid voltage condition and a loss-of-coolant accident occurs with a coincident safety injection signal but a loss of off-site power does not occur, the battery chargers are not stripped from their alternating current supply. The additional potential electrical load on the AC supply has not been analyzed. "Compensatory measures, in the form of administrative controls associated with battery charger testing, are being implemented. A supplement to LER 266(301)/2005-005-00 will be submitted. "The senior resident inspector has been informed of this supplemental report." Subsequent conversations between the Headquarters Operations Officer and the Shift Manager and Shift Technical Advisor at Point Beach have confirmed that this is not an "emergency" notification as quoted in the first paragraph of the event update. This is an event notification only. R3DO (Stone) notified. * * *UPDATE RECEIVED FROM ROBERT BLACK TO PETE SNYDER AT 1847 EDT ON 06/05/06 * * * "On April 6, 2006, NMC provided a supplemental notification to EN# 42020 regarding a condition where certain equipment in the PBNP electrical distribution system would not assure, under certain conditions, interruption of a three-phase bolted fault short circuit. The supplemental notification resulted from additional reviews into the extent of condition of this issue, which indicated additional potential concerns associated with a station battery charger load test being conducted under reduced or degraded grid voltage conditions. "A subsequent evaluation of this supplemental condition concluded that its significance is minor. "The April 6, 2006, supplemental notification concerned 480 VAC vital bus loading due to battery charger load during charger testing and battery charger load while recovering a battery after battery discharge testing conducted under reduced or degraded grid voltage condition. The potential impact of this testing was evaluated to be associated only with the D-109 station battery charger and not several chargers as originally determined. An evaluation of the risk significance of this issue indicates that because of the combination of simultaneous events that would need to occur, the significance is minor. Because of the minor risk significance and that the issue concerns only a single piece of equipment (D-109 station battery charger), the guidance in NUREG-1022 indicates that this condition does not meet the reportability criteria in 10 CFR 50.72(b)(3)(ii)(B). Therefore, the supplemental notification made to EN #42020 on April 6, 2006, is hereby retracted. The underlying condition will continue to be addressed through the plant's corrective action process." The licensee notified the NRC Resident Inspector. Notified R3DO (M. Phillips). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-09-27
42019 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-09-20 | 2005-09-27 15:36 | 2005-09-27 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via email: "On September 20, 2005, a Troxler moisture density gauge, S/N 8161 was run over by a compactor at a job site in Brentwood. According to the report (fax on 9/21/05 and letter dated 9/21/05) provided by the licensee, the gauge shell and base were in pieces. The rod was in one piece but was bent out of shape. The RSO was not available on 9/20/05 and he was immediately notified of the incident. The technician transported the damaged gauge to the Pacific Nuclear Technology (PNT) of Antioch for disposal. The leak test performed on 9/20/05 at PNT indicated no contamination. "The inspector learned of this incident on 9/27/05 and contacted the licensee and PNT to get further information. According to PNT, the rod was not in the shielded position when it was transported to their location. RHB will perform an investigation to try to determine the cause of this incident." Incident number: 092105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-09-30
42018 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2005-09-24 | 2005-09-27 14:39 | 2005-10-26 | TENNESSEE AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Troxler 3430 portable gauge was stolen from the home of an employee of B&W Engineering between mid-day Saturday, 9/24/05 and Monday morning, 9/26/05. The retractable source rod on the gauge was locked, the gauge was in a yellow plastic shipping container which was also locked. The locked gauge in the locked shipping container were located in a locked storage shed behind the employee's home located in Memphis, TN. The gauge is owned by B&W Engineering, Memphis TN. The Radiation Safety Officer for B&W Engineering said that he had contacted the North Memphis Police Dept., but they told him that the employee from whom the gauge was stolen would have to file a police report personally. TN Dept. of Environment & Conservation contacted Tennessee Emergency Management Agency (TEMA) and reported the occurrence to them. TEMA said they would contact the Shelby Co. Emergency Management Agency as soon as they hung up. TN Dept. of Environment & Conservation then called Memphis Police Dept., North Precinct and reported the occurrence to them. TN Dept. of Environment & Conservation then reported the occurrence to the Arkansas Radiation Control Program, they said they might issue a press release. TN Dept. of Environment & Conservation then reported the occurrence to the Mississippi Division of Radiological Health. TN Dept. of Environment & Conservation reported to occurrence to Duncan White , NRC Region l. TN Dept. of Environment & Conservation then received a call back from the Memphis Police Dept. who said that they would contact the RSO for B&W and try to file a police report regarding the theft. Troxler Model 3430 contains 8 millicuries of Cs-137 ands 40 millicuries of Am-241/Be. Incident Report number TN-05-109 * * * UPDATE 1540 EDT ON 10/25/05 FROM BILLY FREEMAN TO A. COSTA VIA EMAIL * * * On the morning of 10/25/05, the Memphis Police Department notified the TN Division of Rad Health that the stolen gauge had been recovered during a narcotics search of a private residence. A preliminary assessment performed by on-scene law enforcement concluded that the device appeared intact and without evidence of damage. The licensee was contacted and will make arrangements to recover the Troxler Model 3430, S/N 23422 within the next several hours. The TN Division of Rad Health representative requested the licensee contact their office after retrieving the device to discuss the condition of the gauge. Notified R1DO (Silk), NMSS (Janosko) and TAS (Sandler) via email. * * * UPDATE AT 09:04 EDT ON 10/26/2005 FROM BILLY FREEMAN TO ABRAMOVITZ * * * The licensee stated "that he had retrieved the gauge and returned it to their B&W Engineering shop. He said the gauge appeared to be unharmed; that they tested/calibrated the gauge and the results indicated it was working properly/as it was prior to the theft; that they had surveyed it with a radiation survey meter and the results were the same as prior to the theft; and finally, that they had taken a leak test smear and sent it in for analysis." Notified R1DO (Silk), NMSS (Burgess) and TAS (Sandler) via email. Less than the quantity of a IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2005-09-30
42017 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2005-09-26 13:00 | 2005-09-26 18:48 | 2005-09-26 | OFFSITE NOTIFICATION "A flatbed truck carrying one sea-land container overturned on Horn Rapids Road just outside the plant entrance. The sea-land container is loaded with TNF-11 loaded with uranium oxide powder. Survey results indicate no contamination outside of the container. Sea-land container integrity is visually good. "The driver was not injured and no other vehicles were involved. AREVA responded using our own forces. Local law enforcement, state and county officials were notified." There is media interest from three local television stations and the Tri-City Herald. * * * UPDATE FROM C. MANNING TO W. GOTT AT 2011 ON 09/26/05 * * * The container is back on Framatome property. * * * UPDATE FROM C. MANNING TO W. GOTT AT 2028 ON 09/26/05 * * * There has been no written press release. The container is being moved into a warehouse where additional surveys will be conducted. The internals will be inspected in the morning. There is a heavy bulkhead inside the sea-land container and appropriate equipment needs to be staged before opening the container. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2005-09-26
42016 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2005-09-26 13:45 | 2005-09-26 16:00 | 2005-09-26 | ALABAMA AGREEMENT STATE REPORT - IODINE-125 CONTAMINATION "[The State of Alabama Department of Public Health] Received a call from Baptist Medical Center -Princeton, Birmingham, Alabama, that they had found I-125 contamination during the post-operative clean-up of an I-125 prostate seed implant therapy. Licensee indicated that they were not sure that there was a leaking seed inserted into the patient. None of the seeds remaining after the procedure were leaking. The licensee performed a thyroid scan on the patient on 9/22/05, which showed that there was an uptake. Potassium iodide was administered at that time. The Seeds are Model ProstaSeed I125-SL, distributed by Mantor Brachytherapy. The applicator is MICK Model 200TP. The licensee is performing dose assessment to include in their written report." Event ID Number: AL-05-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2005-09-29
42015 | 0 | US GEOLOGICAL SURVEY |  |  |  |  | 2005-09-26 | 2005-09-26 15:31 | 2005-09-28 | SOURCE LOST IN SHIPMENT "This memo is to report a missing/lost Cs-137 (s/n A5-509 100 milliCuries) source and describe the events of its loss under the US Geological Survey License 05-01399-08 as required in 10CFR20.2201. Two well logging sources (Cs-137 and Americium-Beryllium) were shipped by FedEx Overnight on September 21, 2005 from Denver, Colorado to arrive in Salisbury, Maryland on September 22, 2005. "The Cs-137 never arrived at its destination. The status of the sources during transportation was being monitored by the licensee. FedEx was called on September 21, and 22, 2005, about both sources. FedEx assured the license that the sources were in transport and they had only been delayed by normal transportation delays. On Monday, September 23, 2005, when the Cs-137 source still was not at its final destination, the licensee had FedEx put a trace on the Cs-137 source. Later on September 23, 2005, the licensee was informed by FedEx that the Cs-137 source could not be found, that FedEx would continue looking for it and the source had made it to Baltimore-Washington Airport but did not make it to the next scheduled scan point. "The Americium/Beryllium (AmBe) source arrived in Salisbury on September 24, 2005 after being delayed in Memphis, TN. A well logging supervisor picked up the AmBe source at the FedEx location in Salisbury, MD and noticed that both Declaration of Dangerous Goods Forms (Cs-137 and AmBe) had been erroneously placed on the AmBe package. This apparently happened in route since FedEx checked both declarations when the shipments were picked up in Denver and placed them back on their respective package." * * * UPDATE FROM D. LILES TO W GOTT AT 1717 ON 09/28/05 * * * The package containing the Cs-137 source was located at approximately 1530 CT 09/28/05, in Memphis, TN. The package will be delivered to the Salisbury, MD facility on 09/29/05. Notified NMSS (Reamer), R1DO (Cahill), and R4DO (Spitzburg). Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | CO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-09-26
42014 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-09-24 | 2005-09-26 11:30 | 2005-09-26 | AGREEMENT STATE REPORT INVOLVING MISSING I-131 SHIPMENT "The Ohio Department of Health was notified by Doctors OhioHealth Corporation on September 26 of a missing 25 millicurie I-131 capsule. The I-131 capsule was to be delivered to the Doctors OhioHealth Corporation Columbus, Ohio location for a thyroid therapy September 26, 2005, at 9 a.m. "The capsule was delivered on Saturday by AirNet but not to the Doctors OhioHealth Corporation location. The person who signed for the I-131 on Saturday, September 24 is not employed by Doctors OhioHealth Corporation. Security at Doctors OhioHealth Corporation and AirNet are trying to locate the I-131 capsule as of 9:30 a.m. Monday September 26th, 2005. The I-131 was sent to Doctors OhioHealth Corporation from Anazao Health in Tampa, Florida via AirNet. The Ohio Department of Health is currently attempting to track the missing I-131 capsule." OH Reference Number: 05-114. Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. *** UPDATE ON 09/26/05 AT 1147 EDT BY MIKE SNEE TO MACKINNON **** "The I-131 capsule was located by AirNet in the Hazmat trailer at Rickenbacher Airport in Columbus, Ohio. The material was never delivered to the hospital as originally reported. AirNet will deliver the material to the hospital today, September 26." R3DO (David Hills) and NMSS (Tom Essig) notified of the update. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-09-29
42013 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-09-25 14:10 | 2005-09-25 19:49 | 2005-11-11 | DEGRADATION IN FIRE BARRIER DISCOVERED DURING AN INSPECTION "During an inspection of structural steel in the Emergency Filtration Train (EFT) building, it was determined that a portion of the steel did not have adequate fire retardant material protecting the steel. This condition would have compromised the 3 hour-fire barrier between the 2 divisions of the Emergency Service Water (ESW) System, impacting # 11 Emergency Diesel Generator ESW Pumps, # 13 and # 14 ESW Pumps. This condition could have resulted in the inability to establish and maintain cold shutdown conditions in the event of a fire in this area. A fire impairment was entered and an hourly fire watch was established to address this condition. All ESW divisions are presently operable." The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTION FROM SCHREIFELS TO HUFFMAN AT 15:45 EST ON 11/11/05 * * * "Monticello is retracting the event notification based on further investigation of the issue. The station has completed calculations that confirm the affected steel beams are not required to maintain fire barrier integrity. Further, the fire severity in the zone will not cause the steel beams to fail. Therefore, the ability of the station to establish and maintain cold shutdown conditions in the event of a fire in this area was not impacted. Based on this information, Monticello has determined there was no unanalyzed condition as reported in Event Notification # 42013. The degraded fire retardant material has been replaced." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-09-25
42011 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-09-24 21:21 | 2005-09-24 23:41 | 2005-09-24 | WEATHER RELATED LOSS OF EMERGENCY SIRENS "Due to weather from Hurricane Rita, 15 of the 43 emergency sirens are inoperable. This places the number of required sirens less than the required operability rate of 75%. A recovery effort is in progress." Alternate notification methods with LLEA (state and local governments) are being set up. The licensee expects to return the sirens to service by tomorrow. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-09-24
42010 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-09-23 00:40 | 2005-09-23 04:38 | 2005-09-23 | MANUAL REACTOR SCRAM DUE TO DEGRADING MAIN CONDENSER VACUUM "At 0040 hours Central Daylight Time, Cooper Nuclear Station was manually scrammed due to degrading main condenser vacuum. Subsequent to the scram, reactor vessel level lowered to minus 20 inches wide range which corresponds to approximately 140 inches above the top of fuel. A Primary Containment Isolation System (PCIS) group 2 isolation occurred as expected due to the level transient. All automatic actions occurred as expected. "This report includes both a 4 hour and an 8 hour report. The 4 hour report is being made pursuant to 10CFR50.72(b)(2)(iv)(b), Actuation of RPS when the reactor is critical. The 8 hour report is being made pursuant to 10CFR50.72(b)(3)(iv)(a), Actuation of PCIS group 2 due to expected RPV low level following the scram. "The NRC Resident Inspector has been informed of the event." All control rods fully inserted following the scram. All safety-related equipment including Emergency Diesel Generators are operable. Offsite power is stable and available. RPV water level is currently being maintained at approximately 35 inches with feedwater supplied by the condensate pumps. The cause of the degrading main condenser vacuum is unknown and under investigation. The RWCU Heat Exchanger is in service to remove decay heat. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-09-23
42009 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-09-22 14:30 | 2005-09-22 19:58 | 2007-04-05 | CALIFORNIA AGREEMENT STATE REPORT: MISSING/STOLEN TROXLER MOISTURE DENSITY GAUGE The Riverside County gauge operator at the Jefferson Street Bridge Construction site located in La Quinta, CA was called to a meeting with the on-site construction inspector. The gauge operator placed a Troxler Model # 3440 moisture density gauge unsecured into the back of his open bed pickup truck with its tail gate down. The gauge handle was not locked, not in its case and not placed in a metal shipping case attached to the bed of the pickup truck. The gauge operator did not placed a cover over the gauge. He drove 1.75 miles to where he met with the on-site construction inspector and a water district official. He talked with them between 8 to 10 minutes. After he completed talking with them he found that the gauge was not in the back of the pickup truck. It either fell out of the back of the pickup truck or it was stolen while he was talking. Three different people retraced the route that he had taken several times without finding the gauge. A police report was made with the La Quinta Police, report number 0509-4479. The Riverside County Transportation Department was instructed to make a press release and offer a $500 reward for the missing gauge. Also the press release instructs people not to touch the gauge and to call the police if they find the gauge. The Troxler gauge contains 8 millicuries of Cs-137 and 40 millicuries of Am-241/Be. The gauge was last leak checked in June of 2005. **** UPDATE ON 09/27/05 AT 1928 EDT FROM MARK M. GOTTLIEB TO BILL GOTT ***** The activity of the Cs-137 is 9 millicuries instead of 8 millicuries and the activity of the Am-241/Be is 44 millicuries instead of 40 millicuries. R4DO (B. Spitzberg), NMSS (Bill Reamer) notified. E-mailed to Mexican Govt Rep and NRC TAS. * * * UPDATE FROM STATE OF CALIFORNIA (KRAJEWSKI) TO HUFFMAN AT 1124 EDT ON 4/5/07 * * * The State reported that the licensee has recovered the gauge from the Police Department in Indio California. The police apparently found the gauge in a warehouse along with other stolen items and traced the gauge back to the licensee through its stolen items database. The gauge is intact and was found with the source in the retracted position. As stated in the original report, the gauge was not in its case. The licensee has taken possession if the gauge and will have the gauge leak tested and examined by a Troxler representative. R4DO (Cain) and FSME (Morell) notified. ILTAB & Mexico notified by e-mail. Less than the quantity of a IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-09-27
42008 | 0 | FLUKE BIOMEDICAL RMS |  |  |  |  | 2005-09-07 | 2005-09-22 15:33 | 2005-09-23 | PART 21 REPORT ON FLUKE RADIATION METER The following information was received via facsimile: 1.0 Name and address of individual informing the Commission: Zisimos Giatis Quality Assurance Manager Fluke Biomedical Radiation Management Services 6045 Cochran Road Solon, Ohio 44139 2.0 Identification of the Basic Component supplied which fails to comply or contains a defect: Customer Complaint 0065 identifies the inability of the customer to insert the detector into the sample volume to the depth defined in primary isotopic calibration report 958.350. The report and manual for the device state the detector is to be inserted to a depth that results in 0.125 inches of the detector body extending outside of the detector mounting flanges. This dimension was expanded to 0.25 inches for the detectors supplied with a removable rear end cap. The customer advised that when installing the detector per the above, the face of the detector would "bottom out" against the sample volume cap before being fully inserted, leaving a gap of approximately 0.3 inches in front of the detector mounting flanges. 3.0 Identification of the firm supplying the Basic Component which fails to comply or contains a defect: Fluke Biomedical Radiation Management Services 6045 Cochran Road Solon, Ohio 44139 (Formerly Victoreen, Inc.) 4.0 Nature of the defect or failure to comply and the Safety Hazard created: Because the insertion depth is a critical component of the sample volume, and thus the efficiency of the detector, the detector CPM to µCi/cc conversion constant cannot be validated. The conversion constant supplied for the sample geometry will result in the detector either overstating or understating the radioactivity being monitored. 5.0 The date on which the information of such defect or failure to comply was obtained: The problem was discovered September 7, 2005. 6.0 Affective Facilities Diablo Canyon Nuclear Plant, California Jose Cabrera, Spain KEPCO, Republic of Korea KAERI, Republic of Korea Con Ed, Indian Point 2 7.0 Corrective Action: The primary calibration will be repeated and a revised insertion depth will be provided to the affected customers. The estimated time frame to complete this task is 6 months. 8.0 Advice related to the defect or failure to comply about the Basic Component that has been, is being, or will be given to purchasers: At the Diablo Canyon plant, the accident range gas channel is not required for plant operation, and has been declared inoperable. International customers are being advised that the response of their accident range gas monitors may be questionable and to verify the insertion depth used in their plant. * * * UPDATE ON 9/23/05 @ 14:00 BY FAX FROM FLUKE BIOMEDICAL TO ABRAMOVITZ * * * "Entergy (Con Ed) Indian Point 2 will be notified of the situation, although their sampler is no longer being used." Notified the R1DO (Henderson), NMSS (Moore) and Part 21 (Tabatabai). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2005-09-22
42007 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-09-16 08:45 | 2005-09-22 13:54 | 2005-09-22 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "Notification received from Governor's Office of Emergency Services at 8:40 a.m. regarding report of a stolen moisture density gauge. The RSO reported the theft of the gauge was noticed at 7:00 a.m. today. The cables were cut from the security device in his truck. It is unclear if the truck was located at a worksite or residence. The gauge is a HSI1500EZ unit - Cs-137 10 mCi [milliCurie] & Am-241 40 mCi model. The Tracy police have been notified." California NMED # XCA-787 Less than the quantity of a IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-09-27
42006 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2005-09-21 18:22 | 2005-09-22 00:50 | 2005-09-22 | PARTIAL LOSS OF EMERGENCY SIREN CAPABILITY IN HARRISON COUNTY IOWA DUE TO A TRANSFORMER FIRE "Fort Calhoun Station was informed that 6 of the 18 emergency sirens located in Harrison County Iowa were rendered inoperable due to a fire affecting a transformer. Harrison County Sheriff department implemented the alternate notification method. Local utility responding to restore power anticipates a 4 hour outage duration. Power was reported to be restored at 2208 CST. Sirens will be verified on Thursday September 22, 2005." There was no indication of malevolent intent reported with respect to the cause of the fire. The licensee informed local authorities and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-09-22
42005 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2005-09-21 08:30 | 2005-09-21 15:57 | 2005-09-23 | FITNESS FOR DUTY A licensed operator had a confirmed positive for drugs during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. ***** UPDATE ON 09/23/05 1729 EDT FROM BRIAN FINCH TO MACKINNON ***** CORRECTION: At the time of the original report on 9/21/05 the Headquarters Operations Officer incorrectly described the results of the random fitness-for-duty test as a confirmed positive. The licensee noted the discrepancy and provided the following additional information which includes the test results for the sample taken on 9/21/05. On 09/23/05 the test results for the sample submitted on 9/21/05 were received and confirmed positive for drugs. The NRC Resident Inspector will be notified of this event update. NRC R1DO (P. Henderson) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2005-09-21
42004 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-09-20 22:40 | 2005-09-21 02:37 | 2005-11-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN COMMENCED DUE TO INOPERABILITY OF RESIDUAL HEAT REMOVAL CONTAINMENT SUMP ISOLATION VALVES "At 2240 09/20/2005 an engineering evaluation concluded that the Residual Heat Removal Containment Sump Isolation Valves were inoperable based on their inability to open against a higher differential pressure than had been previously evaluated. Historically Wolf Creek has operated with the Component Cooling Water isolated to the Residual Heat Removal Heat Exchangers. If the pumps started during accident conditions there is a potential that the pump heat generated could cause system pressure to increase to the suction relief valve setting of 450 psig. Testing of the valves has shown that they are capable of opening with 207 psid across the valve. "Technical Specification 3.0.3 was entered at 2240 9/20/2005 due to the inoperability of both Residual Heat Removal trains. Power reduction was commenced at 2340. Component Cooling Water was aligned to the Residual Heat Removal Heat Exchangers at 0004 9/21/2005 restoring operability of the Residual Heat Removal trains. At 0017 9/21/2005 actions were commenced to restore power to 100%. "This event is reportable under 10 CFR50.72(b)(2)(i) Technical Specification required shut down (4 hour) and 10 CFR50.72(b)(3)(v)(B) Event or Condition that could have prevented fulfillment of a Safety Function (8 hour). "The NRC Resident has been contacted." *** UPDATE AT 15:39 EST ON 11/08/05 FROM DEES TO KNOKE *** "Evaluation of the Residual Heat Removal Containment Sump Isolation Valves concluded that the valves were operable and the Residual Heat Removal trains were capable of fulfilling their safety function. Therefore, this event is not reportable under 10 CFR 50.72(b)(3)(v)(B)." Based on the information above, 10 CFR 50.72(b)(3)(v)(B) has been deleted from the original event notification. The licensee notified the NRC Resident Inspector. Notified the R4DO (Whitten). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-09-21
42003 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2005-09-20 05:00 | 2005-09-20 12:48 | 2005-09-20 | DEGRADED CONDITION - SMALL LEAK ON RHR INJECTION DRAIN LINE "After shutting down for refueling outage, a small leak was discovered on a 1-inch drain line for the 'A' Loop RHR injection line. This leak is at a weld. "Tech Spec 3.4.4 was entered for RCS Operational Leakage due to potential Class I pressure boundary leakage. "This report is being made IAW 10CFR50.72(b)(3)." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-09-20
42002 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-09-19 07:22 | 2005-09-19 16:25 | 2005-09-20 | FITNESS FOR DUTY A licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 9/20/05 TO CORRECT ERROR * * * The text should read: A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 26.73 |  |  |  | 0 | 2005-09-19
42001 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-09-19 11:04 | 2005-09-19 11:26 | 2005-09-20 | UNUSUAL EVENT DECLARED DUE TO HURRICANE RITA "Turkey Point nuclear power plant is under a hurricane warning from the National Hurricane Center, starting at 11:00 EDT for Tropical Storm Rita." On-site facilities are not being activated at this time. No off-site assistance is requested. All 4 Emergency Diesel Generators are available and fully operable if needed. The electrical grid is stable. The licensee has notified the State and local agencies. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM D. FUNK TO W GOTT AT 1917 ON 09/19/05 * * * Tropical storm force winds are expected between 0700 and 2100 on 09/20/05. Maximum expected sustained wind speed is 53 MPH. The licensee notified the NRC Resident Inspector. Notified R2DO (C Ogle) and R2 IRC (J. Hufham) * * * UPDATE FROM C. MONTGOMERY TO M. RIPLEY 1410 EDT 09/20/05 * * * "As of 1353 EDT 09/20/05, Turkey Point nuclear power plant is no longer in an Unusual Event due to a hurricane warning from the National Hurricane Center for Hurricane Rita." The licensee notified the NRC Resident Inspector, and State and County officials . Notified R2 DO (Ogle), IRD Mgr (Wilson), NNR EO (Benner), FEMA (Liggett), HERO (Gott), DHS via DOE Nuclear Event Notification Desk (J. Everett) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-09-19
42000 | 0 | GEOTEST, INC |  |  |  |  | 2005-09-19 07:30 | 2005-09-19 10:10 | 2005-09-19 | STOLEN TROXLER MOISTURE DENSITY GAUGE An employee of GeoTest notified his company that a moisture density gauge was stolen from his job site in Jefferson County, MO. The gauge is a Troxler (Model 3440, S/N 36277) with 40 millicuries of Am-241/Be and 8 millicuries of Cs-137. The employee had the gauge locked inside a cabinet that was inside a locked trailer at the job site. The licensee notified the LLEA (Police Dept in Herculaneum, MO) and they are investigating the incident. The licensee is not expecting any media attention, and is not offering a reward. Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-09-19
41999 | 0 | GEOMECHANICS |  |  |  |  | 2005-09-19 07:00 | 2005-09-19 08:32 | 2005-09-23 | STOLEN HUMBOLDT SCIENTIFIC MOISTURE DENSITY GAUGE An employee of Geomechanics notified his company that a Humboldt Scientific gauge was stolen from his truck. The moisture density gauge is a Humboldt Scientific (Model 5001, S/N 4731) with 40 millicuries of Am-241/Be and 10 millicuries of Cs-137. The source serial numbers are NJ04997 and 5850CM respectively. The employee was parked overnight in a Holiday Inn Express parking lot in Charleston West Virginia when the theft occurred. The gauge was locked in a container, which was chained to the bed of the truck. The licensee notified the LLEA and they are investigating the incident. The licensee is not expecting any media attention, and is not offering a reward. Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. **** UPDATE 09/23/05 at 1530 EDT from Clay Carney and Walter Lorence to MacKinnon **** Operations Officer for the State of West Virginia Homeland Security tied the NRC Headquarters Operation Officer with Geomechanics Radiation Safety Officer. The Emergency Director for Boone County, West Virginia, has found the stolen Humboldt Moisture Density gauge intact and in its case. A State of West Virginia police officer is on scene guarding the missing gauge. Geomechanics will be sending a consultant from Applied Health Physics out of Pittsburgh, PA to check the gauge out and bring it back to Geomechanics. Notified NRC R1DO(P. Henderson) & NMSS EO (Scott Moore) and emailed to TAS (L. English). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-09-19
41998 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2005-09-18 | 2005-09-18 23:49 | 2005-09-19 | CONTAMINATION EVENT IN UNCONTROLLED AREA The licensee observed a puddle of water on a blacktop surface in an area outside the Uranium Oxide (UO2) building under conditions where no water would ordinarily be expected. The puddle was characterized as about 4 feet by 8 feet in size. The area was barricaded and samples were taken for analysis. The sample analysis has still not been completed, however, the puddle has evaporated and radiological survey of the blacktop area with a GM tube type probe indicated an on-contact radiological contamination count rate of 4000 CPM (counts per minute). The licensee has covered the blacktop surface with a tarpaulin now that the area is dry and a decontamination plan is under development. The location of the contamination is within the facility's security zone that is not a contamination-controlled area. There was no release or potential of release outside the facility. There was no personnel contamination associated with this event. The licensee believes the contamination is from Uranium but is still awaiting lab results. The source of the contamination is still unknown. The license was performing fire protection deluge testing at approximately the time the puddle was discovered but the connection between this testing and the generation of the contaminated water is not known. The licensee plans to contact the Region. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 70.50(b)(1) |  |  |  | 0 | 2005-09-19
41997 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-09-17 11:29 | 2005-09-17 16:07 | 2005-09-17 | REACTOR SCRAM DUE TO MAINTENANCE "On 09/17/2005 at 1129 CDT, Browns Ferry Unit 3 reactor automatically scrammed due to the trip of the main generator turbine on low main condenser vacuum. Prior to the trip, the unit was operating at reduced power (74 percent) and maintenance was in progress to repair in place a secondary plant moisture separator level control valve. This maintenance activity resulted in the low condenser vacuum condition. "Plant response to the scram was as expected. Post-scram transient RPV low water level caused a valid automatic initiation of primary containment isolation (PCIS) valves group 2 (containment sumps and shutdown cooling valves), group 3 (reactor water cleanup system), group 6 (ventilation systems, including initiation of standby gas treatment and control room emergency ventilation systems), and group 8 (traversing in-core probe system). "This event is reportable to the NRC via ENS within four hours under 10CFR50.72(b)(2)(iv)(B) (RPS actuation while critical), and within eight hours under 10CFR50.72(b)(3)(iv)(A) (RPS and containment isolation actuation)." Browns Ferry Unit 2 was not affected. The reactor shutdown and all control rods fully inserted. Condenser vacuum has been restored and decay heat is being removed using the bypass valves. | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-09-17
41996 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-09-15 11:40 | 2005-09-15 14:41 | 2005-09-15 | EMERGENCY PREPAREDNESS SIREN MODIFICATIONS "This is an information only notification. "Commencing approximately 1 PM Mountain Standard Time, September 15, 2005, the Palo Verde Nuclear Generating Station will be performing modifications to Emergency Preparedness sirens within the 5-mile radius of the emergency planning zone (EPZ) to implement corrective action to prevent recurrence of damage due to vandalism that has occurred and been reported in previous ENS notifications [Recent Event Notifications: 41960, 41912, 41874, 41810, 41486, 41466, 41451]. "Palo Verde's reporting criterion includes a loss of capability to inform greater than 5% of the population (more than 106 people) within 5 miles. Six of the 12 sirens within the 5-mile radius meet this criterion. Only one of these 6 sirens will be out of service at a time for modification. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. The MCSO has been informed of the status of siren modification for each of the 6 sirens so that the contingency can be promptly implemented if an event requiring siren activation were to exist, thus no loss of capability to inform the population will occur." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW | [5 empty] | 0 | 2005-09-15
41995 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-09-14 21:38 | 2005-09-14 23:38 | 2005-10-30 | HIGH PRESSURE COOLANT INJECTION SYSTEM FAILED SURVEILLANCE TESTING "On 9/14/05 at 2138, the High Pressure Coolant Injection (HPCl) system was declared inoperable. The HPCI Pump In Service Surveillance Test was in progress with system flow and speed being adjusted to establish surveillance test conditions. Speed and flow oscillations were observed when turbine speed approached 3900 rpm. Since speed and flow oscillations prevented the establishment of surveillance test conditions, HPCI was declared inoperable. Evaluations of these speed and flow oscillations are ongoing. "Loss of the HPCI is reportable under 10CFR50.72(b)(3)(v) as loss of a single train safety system required to mitigate the consequences of an accident. No additional Emergency Core Cooling Systems or Safety Related equipment was inoperable during this time period." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM LICENSEE (BREADY) TO NRC (HUFFMAN) AT 11:38 EST ON 10/30/05 * * * "Evaluation of the HPCI system speed and flow oscillations concluded that the HPCI system was capable of mitigating the consequences of an accident. Therefore this event is not reportable under 10 CFR 50.72(b)(3)(v) as a loss of a single train safety function and is being retracted." The licensee will notify the NRC Resident Inspector. R1DO (Silk) notified. | 100 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-09-14
41994 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-08-15 | 2005-09-14 13:18 | 2005-09-14 | AGREEMENT STATE REPORT - LOSS OF CASE CONTAINING TECHNETIUM-99m The licensee provided the following information via email: "A customer of Cardinal Health called Cardinal on Tuesday, 16 August 2005, to inform Cardinal that they had not received part of their nuclear medicine order for Monday, 15 August. Only one of the two cases ordered had been delivered. The missing case contained 6 doses of diagnostic technetium-99m (a maximum total activity of 9.36 Megabecquerels [253 millicuries] as of ~ 06:30 am on 15 August). Cardinal Health indicates the doses were prepared early the morning of 15 August. The driver who delivered to the customer location on 15 August stated that only one case had been picked up from the pharmacy for that customer. Survey of delivery vehicle confirmed absence of missing radioactive material. The customer is sure that they did not receive the shipment. ORP performed a Cardinal facility site investigation on 19 August. Cardinal Health has not yet been able to explain what actually happened. Cardinal Health and ORP continue to investigate the event (Event Report # WA-05-047)." Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-09-19
41993 | 0 | VA COMMONWEALTH UNIVERSITY |  |  |  |  | 2005-09-13 15:30 | 2005-09-14 14:24 | 2005-09-14 | UNPLANNED CONTAMINATION DUE TO A PIPE CRACK Licensee personnel noted a pipe crack in the waste water system which allowed contaminated water to drip onto the air handling equipment for the laboratory. The leaking sink was in the laboratory receiving area for waste disposal. The waste water penetrated the air handler and contaminated the unit. The air handling unit was shut down and access control for contamination was initiated for the entire area. Contamination was measured up to 20K dpm but no one has been injured nor contaminated. Most of the beta activity comes mainly from P-32, C-14 and S-35. Area decontamination procedures are currently underway. The licensee will provide a detailed written report of this incident to the U.S. NRC. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 30.50(b)(1) |  |  |  | 0 | 2005-09-14
41991 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-09-14 08:32 | 2005-09-14 14:11 | 2005-09-15 | LOSS OF OFFSITE EMERGENCY PREPAREDNESS SIRENS "On September 14, 2005, at approximately 0832 hours [EDT], Brunswick began losing the function of several offsite emergency preparedness sirens as a result of adverse weather conditions associated with Hurricane Ophelia. There are a total of 36 sirens located in Brunswick and New Hanover Counties, NC. The maximum number of sirens that were inoperable was twenty (20). As of 1330 [EDT], eleven (11) sirens in Brunswick County and four (4) sirens in New Hanover County remain inoperable. The Brunswick and New Hanover County Emergency Operations Centers are aware of the condition of the sirens and maintenance activities are in progress to restore siren capabilities. Other communications with local, state, and federal emergency response organizations have not been affected. "The initial safety significance of this condition is considered minimal. Unit 1 and 2 are currently operating in Mode 1 under normal parameters. State and county emergency response officials are aware of the condition and compensatory measures are in place to provide warning to the affected areas if required." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0028 EDT ON 9/15/05 FROM KENON CHISM TO S. SANDIN * * * "On September 14, 2005, under Event Notification 41991, Brunswick Plant reported the loss of a number of offsite emergency preparedness sirens as a result of adverse weather conditions associated with Hurricane Ophelia. Maintenance activities continue for restoration of the siren capabilities lost. As of 2340 hours (EDT) on September 14, 2005, nine (9) sirens remain inoperable, six (6) sirens in Brunswick County and three (3) sirens in New Hanover County." The licensee will inform the NRC Resident Inspector. Notified R2DO (Munday). * * * UPDATE AT 1639 EDT ON 9/15/05 FROM DANIEL HARDIN TO J. ROTTON * * * "On September 14, 2005, at 1411 hours, the Brunswick plant provided a notification (reference Event Number 41991) in accordance with 10 CFR 50.72(b)(3)(xiii) for the loss of function several offsite emergency preparedness sirens as a result of adverse weather conditions associated with Hurricane Ophelia. This update is to notify the NRC Operations Center that as of September 15, 2005, at 1600 hours, all but 3 of 36 sirens have been restored and the condition no longer meets the criteria of 10 CFR 50.72(b)(3)(xiii). "Restoration efforts for the remaining sirens are in progress." The licensee notified the NRC Resident Inspector. Notified R2DO (Munday) | 100 | 93 | 0 | 100 | 93 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-09-14
41990 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-06-01 | 2005-09-14 12:30 | 2005-09-14 | AGREEMENT STATE REPORT - TRITIUM SOURCES DISPOSED AT LANDFILL Nineteen Tritium Exit Signs were inadvertently disposed in Robeson County Landfill in St. Pauls, North Carolina in mid June 2005, totaling 403 Curies of Tritium gas (H-3). The incident location is at 22828 NC Way 87 W. Fayetteville, NC. 28306-7332. A survey of the landfill has not yet been performed and there are no significant exposure hazards. No one has been injured by the event. (NC Incident No.05-32). Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. These are IAEA Category 5 sources and are not dangerous: No one could be permanently injured by this amount of radioactive material. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-09-19
41989 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2005-09-13 16:00 | 2005-09-14 10:30 | 2005-09-15 | AGREEMENT STATE REPORT INVOLVING A STOLEN/RECOVERED INDUSTRIAL RADIOGRAPHY CAMERA At 1600 EDT on 9/13/05 an Acuren Inspection vehicle was discovered missing from their satellite office located in Augusta, GA. The vehicle contained a TechOps industrial radiography camera, model and serial number unknown containing an Ir-192 source (source strength not available at time of the report). The vehicle was recovered four (4) hours later at 2000 EDT by law enforcement. The individual believed responsible for the theft, an employee, was arrested at 0300 EDT on 9/14. The corporate RSO (Radiation Safety Officer) is enroute to Augusta to examine the recovered vehicle and radiography camera. The State of Georgia will update this report as additional information becomes available. * * * UPDATE ON 09/15/05 @ 1525 FROM ELIZABETH DRINNON TO CHAUNCEY GOULD * * * The model of the camera is AEA 660B serial # B2655. The source model AEA 424-9 serial number 21291B, containing iridium 192. The strength of the source at the time of the theft was 18.5 curies. Notified Reg 1 RDO (Trapp), NMSS EO (Hodges), IRD (Wilson), TAS (English), TAS(Sandler), and DHS (Cartledge) IAEA Category 3 sources, if not safely managed or securely protected, could cause permanent injury to a person who handled them, or were otherwise in contact with them, for some hours. It could possibly - although it is unlikely - be fatal to be close to this amount of unshielded radioactive material for a period of days to weeks. These sources are typically used in practices such as fixed industrial gauges involving high activity sources (for example, level gauges, dredger gauges, conveyor gauges and spinning pipe gauges) and well logging. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2005-09-19
41988 | 0 | IOWA DEPARTMENT OF PUBLIC HEALTH |  |  |  |  | 2004-08-07 | 2005-09-14 09:56 | 2005-09-14 | AGREEMENT STATE REPORT INVOLVING FIRE DAMAGE TO GAUGE SOURCES The State representative reported that a fire occurred at the Mid-America coal fired electrical power plant in Salix, Iowa on August 7, 2004. Two Thermo-Electron level and flow gauges used on the facility's coke tower were damaged by the fire. Each of the two gauges contained a 50 millicuries Cesium-137 sealed source. The facility RSO isolated access to the gauge location until they could be inspected by representatives of Thermo-electron. On August 11, 2004, Thermo-electron representatives arrived onsite and performed leak tests of the gauge sources. The sources were determined to be intact. Thermo-electron took possession of the gauges. The gauges have subsequently been repaired and returned to the licensee for reinstallation at its facility. It has been determined that no radiation was released as a result of this event. The State has notified NRC Region 3 (Lynch) of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IA | OTH | AGR |  |  |  |  | 0 | 2005-09-19
41987 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-09-14 02:13 | 2005-09-14 04:48 | 2005-09-14 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL DURING PLANNED MAINTENANCE "An automatic reactor scram on low reactor water level occurred following a momentary loss of the UPS (Uninterruptible Power Supply) system. The power loss resulted in a lock-out of the RFP (Reactor Feed Pump) controls. The HPCI system started on low reactor level but did not inject, reactor level had risen above the initiation set-point. The RCIC did not receive an initiation signal. Overall plant response was as expected." Prior to the transient the licensee was in the process of transferring UPS electrical loads to the alternate power supply. The momentary loss of UPS power locked-out the RFP controls during a downtrend in the reactor water level from the normal 201-203 inch operating band. Before Operators could establish manual control, reactor water level reached the 177 inch scram setpoint. Following the scram, reactor water level continued to decrease to the HPCI and RCIC initiation setpoint of 126 inches before recovering. HPCI received a start signal but RCIC did not for reasons under investigation. The unit will remain in mode 3 pending the results of the post-scram investigation and restart. The licensee informed the NRC Resident Inspector and is planning on issuing a press release. * * * UPDATE ON 09/14/05 @ 1918 BY TIM PAGE TO CHAUNCEY GOULD * * * On September 14, 2005 at approximately 0213. an automatic reactor scram on low reactor water level occurred following a momentary loss of the UPS (Uninterruptible Power Supply) system. The power loss resulted in a lock-out of the RFP (Reactor Feed Pump) controls. A level transient occurred causing reactor water level to lower, resulting in an automatic reactor scram on low reactor water level. The HPCI system auto initiated on low reactor water level but did not inject as reactor water level had risen above the initiation setpoint. The RCIC system auto initiated (and sealed-in) and injected into the reactor vessel. Both systems operated as designed. In addition, a Primary Containment Isolation System (PCIS) Group 2 isolation occurred, resulting in multiple system isolations. This included isolation signals to Reactor Water Cleanup, Reactor Building Ventilation, Containment Atmosphere Dilution. Torus Vent and Purge, Drywall Floor and Equipment Drain Sumps, Drywall Containment Atmospheric Monitors, Recirculation System Sample Lines, Traversing In-Core Probes, LPCI Inboard Injection Valves, Residual Heat Removal Drain to Radwaste, and auto initiation of Standby Gas Treatment. (Note that two Reactor Water Cleanup PCIS valves did not close due to their respective circuit breakers being in the open position for planned maintenance activities.) The above event meets the reporting criteria of 10 CFR 50.72(b)(2)(iv)(B) for RPS actuation while the reactor was critical, as well as 10 CFR 50.72(b)(3)(iv)(A) for the valid actuation of systems listed in 10 CFR 50.72(b)(3)(iv)(B), including general containment isolation signals affecting containment isolation valves in more than one system, the HPCI system, and the RCIC system. The NRC Resident Inspector has been briefed. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-09-14
41986 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-09-12 | 2005-09-13 18:07 | 2005-09-13 | AGREEMENT STATE REPORT - RADIOGRAPHY SOURCE DISCONNECT The State provided the following information via facsimile: "On 13 September 2005 at approximately 1:00 PM, I received telephone notification from David L. Ezzell, the Corporate RSO for Midwest Inspection Services, informing the Department of a source disconnect that occurred on 12 Sept 05. The source was a 33 Ci Ir-192 radiography source that was being used in Sterling Colorado. The radiography crew identified the source disconnect when approaching the end of the guide tube following a shot. The crew contacted their corporate RSO who proceeded to the location and retrieved the source at approximately 2:45 PM that day. Mr. Ezzell stated that there was no apparent reason for the disconnect and the examination of the connector portion of the pigtail (once the source was returned to the radiography exposure device) did not show damage. A written report providing a detailed description of the events and circumstances is to be submitted by Mr. Ezzell within the next few days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-09-16
41985 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-09-11 | 2005-09-13 13:20 | 2005-09-13 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "Matt Falke notified Office of Emergency Services on Sunday 9-11-05 of the theft of his Soil Moisture Density Gauge from a secured container located in the bed of his truck parked in the driveway of his home. Matt Falke thought he had called RHB [Radiological Health Branch] but in fact was speaking with OES who transferred him [to] the DHS Duty Officer of the day. Bill Potter of OES sent RHB actual notification on Monday, Sept 12 of the event. Local police and Modesto and Sacramento FBI field offices have been notified. The device has been identified as a CPN 503DR Hydroprobe containing 50 mCi of AmBe241 [Americium-241-beryllium] with a serial number H33024767. Matt Falke is checking the local Flea Market today to see if the item will be offered for sale and is putting a reward offer in the local newspaper." Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-09-16
41984 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2005-09-12 17:09 | 2005-09-12 23:27 | 2005-09-12 | OVERPOWER OF REACTOR DUE TO CALIBRATION ERROR ON STEAM DUMP CONTROL SYSTEM "On September 12, 2005 at 1709 hours, one feedwater train bypass valve (TV-1CN-100) unexpectedly opened at Beaver Valley Power Station Unit No. 1, causing the temperature of the feedwater going to the three steam generators to reduce. Reactor power then increased due to cooler feedwater temperature entering the steam generators. Reactor power increased to approximately 103 percent. The control room crew commenced reducing plant load and reactor power. Approximately 4 minutes later, TV-1CN-100 automatically closed as designed following an automatic opening signal. Reactor power decreased below 100% at approximately the same time. Currently, the plant is stable with reactor power at 93 percent. "A calibration procedure of the Steam Dump Control System was ongoing at the time of the event. Preliminary investigation determined that this event occurred due to removal of an instrument card within the Steam Dump Control System which caused TV-1CN-100 to inappropriately open. Actuation of TV-1CN-100 was not initiated by a valid actuation signal. "This event is being reported as a voluntary notification since the reactor power exceeded maximum licensed steady state power level of 102 percent." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2005-09-12
41983 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-09-12 23:14 | 2005-09-12 23:27 | 2005-09-15 | UNUSUAL EVENT DECLARED DUE TO HURRICANE OPHELIA WARNING "On September 12, 2005, at 2300 hours, a hurricane warning was issued, which resulted in the declaration of an unusual event for both units. Unit 1 and 2 are currently operating at 100 percent of rated thermal power. The plant area is not currently experiencing any hurricane force winds. The wind speed at the site is approximately 24 miles per hour. State and county emergency response organizations have been notified. The resident inspector has been notified. "There is no significant impact to the safety of the plant at this time. "The plant is currently in Abnormal Operating Procedure 0AOP-13.0, 'Operation During Hurricane, Flood Conditions, Tornado, or Earthquake,' and Plant Emergency Procedure 0PEP-02.6, 'Severe Weather,' in preparation for hurricane conditions." On-site facilities are not being activated at this time. No off-site assistance is requested. Request suspension of additional follow up notification unless plant conditions change. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable. * * * UPDATE AT 0758 EDT ON 9/14/05 FROM BRUCE HARTSOCK TO S. SANDIN * * * "Commenced reduction in power on Unit 2 in anticipation of exceeding 74 mph winds. Prediction revised to maximum of 64 mph onsite. Power reduction stopped. Plant stabilized. Power will be restored." Notified RCT (Hasselberg) and R2IRC (Casto). * * * UPDATE AT 0028 EDT ON 9/15/05 FROM KENON CHISM TO S. SANDIN * * * "As of 2300 hours (EDT) on September 14, 2005, the Hurricane Warning south of Cape Fear, North Carolina, has been discontinued; therefore, the Unusual Event has been terminated. Entry into the Unusual Event was reported by Event Notification 41983. Both Unit 1 and Unit 2 continue to operate at 100 percent power. There has been no damage affecting safety equipment or causing operational constraints as a result of Hurricane Ophelia." The licensee notified state/local agencies and will inform the NRC Resident Inspector. Notified R2DO (Munday), NRR (Mayfield), IRD (McGinty), FEMA (Snyder), and DHS (Gomez). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-09-12
41981 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2005-09-09 07:00 | 2005-09-12 15:07 | 2005-09-12 | AGREEMENT STATE REPORT - LOST MOISTURE/DENSITY GAUGE The licensee reported a missing [moisture/density] gauge from its storage location at the Calvert Gateway construction site at Town Center Boulevard and Md Route 4 in Dunkirk, MD. The following are the gauge specifications: Campbell Pacific Nuclear (CPN) MC-3 Portaprobe Moisture/Density gauge, SE Gauge No. 15, S/N: M300405608, Radioactive Materials: Cesium-137, sealed source, 8 millicuries; Americium-241:Be, sealed source, 40 millicuries. The Anne Arundel County Police was notified (Report No.05-737156). Less than the quantity of a IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2005-09-15
41980 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-09-08 13:00 | 2005-09-12 14:07 | 2005-09-12 | AGREEMENT STATE REPORT ON DAMAGED TROXLER GAUGE The State provided the following information via email: "On September 8, 2005, we received a call from the RSO that their [Troxler] gauge had been run over by a front loader. The gauge user was standing approximately 3' away from the gauge when this occurred. Although the gauge handle had originally been in the shielded position, the front loader drove the rod down into the ground when it ran over the gauge. The RSO met the gauge user at the site of the incident (Dooley Elementary in Long Beach). The RSO contacted Kent Prendergast, Senior HP for RHB-Richmond, who directed them to try to retract the source, which they were able to do. They placed the gauge in the gauge transport case and brought it directly to Maurer Technical Services (6163-30) in Laguna Hills. Maurer Technical are CPN manufacturer representatives who repair, leak test, and calibrate gauges. The gauge was a Troxler, model 3430, #35001. "At 8:10 A.M, September 12, 2005*, Maurer reported the source rod was not able to be locked, the gauge was not repairable, but the sources appeared to be intact and was in the shielded position when it was brought in by the licensee. A leak test was performed. The gauge will be shipped to Troxler Labs once it is confirmed that the leak test is negative. There was no exposure to the workers at the site from this incident since the Cs-137 source ended up being extended into the soil and the soil shielded the source. I estimate the gauge user and RSO received from 5-10 millirem during the retrieval of the source. There are no corrective actions required because of this event. "This event is also reportable within 24 hours by California Code of Regulations, title 17, Section 30295(b)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-09-15
41979 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-09-11 11:00 | 2005-09-11 11:29 | 2005-09-11 | FLORIDA AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGE A CPN gauge was stowed and locked inside a trailer inside a locked shed in Orlando, Florida. An employee visited the work site and noticed the locks on the storage shed and trailer were broken. EarthTech reported the gauge stolen and reported the theft to the Florida Bureau of Radiation and the local police. The local police are currently at the scene. These gauges typically contain 10 milliCuries Cs-137 and 50 milliCuries of Am-241:Be. Less than the quantity of a IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE FROM J. WILLIAMSON TO M. RIPLEY 2030 EDT 09/11/05 * * * The gauge is a CPN model MC-3, serial number M330206877. The State also provided the licensee's license number and Radiation Safety Officer contact information. Notified R1 DO (F. Costello), NMSS EO (L. Kokajko) and TAS (B. Sandler) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-09-14
41978 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-06-29 10:10 | 2005-09-09 04:58 | 2005-09-11 | WASHINGTON STATE AGREEMENT STATE REPORT "This is an update and close of an event in Washington State as reported to and investigation by the Washington State Department of Health, Office of Radiation Protection (ORP). "STATUS: closed "Licensee: Mikron Industries "City and State: Kent, Washington "License Number: WN-R0483 "Type of License: General License Registration "Date and time of Event: 29 June 2005, 10:10 a.m. "Location of Event: Kent, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health, office of Radiation Protection (ORP) on-site investigation; media attention): "ORP was notified, by telephone on 29 June 2005 by a Mikron Industries representative, the company was unable to locate 34 generally licensed Po-210 static eliminators. The devices were received between 15 May 2003 until 21 October 2004. Of the 34 devices, two are NRD Model P-2021 8101 (each originally containing 370 MBq [10 millicuries] Po-210); the remaining thirty-two are NRD Model P-2035 (each originally containing 1480 MBq [40 millicuries] of Po-210). The company seems not to know any more then that the devices are missing. ORP staff will make a site visit 30 June 2005 to help the company with their investigation. "ORP staff performed site visits on 30 June and 8 July, 2005. Staff determined from November 2003 until about March 2005 the facility had not properly controlled the licensed material. The facility had not satisfactorily tracked receipt and disposal of the devices. During the visits, staff were able to locate 28 of the 34 missing devices. They had been set aside in work and storage areas. Recovered devices will remain secured on-site until analysis of leak tests will allow for return to the device manufacturer. ORP will follow up with Mikron to ensure proper disposition of the recovered devices. Mikron has instituted management control to ensure proper disposition of devices from now on. "Notification Reporting Criteria: WAC 246-221-240 (24 hour notification) "Isotope and Activity involved: 34 devices total. 32 devices originally contained 1480 MBq [40 mCi] of Po-210, 2 devices originally contained 370 MBq [10 mCi] of Po-210. Total initial activities were 48.1 GBq [1300 mCi], decayed activity as of 29 June 2005 is 98.8 GBq [267 mCi]. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Unknown but likely not. "Lost, Stolen or Damaged? (mfg., model, serial number): "34 missing NRD Models (2) P-2021 8101 & (32) P-2035 Static Eliminator Devices. "Model Serial Number / status "P-2021 8101 A2EA576 Found "P-2021 8101 A2EA577 Found "P-2035 A2EA554 Found "P-2035 A2EA556 Found "P-2035 A2EA557 Found "P-2035 A2EA558 Found "P-2035 A2EA559 Found "P-2035 A2EA560 Found "P-2035 A2EA561 Found "P-2035 A2EA562 Found "P-2035 A2EA563 Found "P-2035 A2EA564 Found "P-2035 A2EA565 Found "P-2035 A2EA566 Found "P-2035 A2EA567 Found "P-2035 A2EA568 Found "P-2035 A2EA569 Found "P-2035 A2EA570 Found "P-2035 A2EA571 Found "P-2035 A2EA574 Found "P-2035 A2EA575 Found "P-2035 A2DU458 Found "P-2035 A2DU459 Found "P-2035 A2DU462 Found "P-2035 A2DH035 Found "P-2035 A2DH037 Missing "P-2035 A2DH039 Found "P-2035 A2DH040 Found "P-2035 A2DH041 Missing "P-2035 A2DA168 Missing "P-2035 A2DA169 Missing "P-2035 A2DA170 Missing "P-2035 A2DA171 Missing "Disposition/recovery: "Disposition of the missing devices is unknown. "Leak test? "Initial, manufacturers leak tests are likely to have been performed. Succeeding, periodic leak tests are unknown. The 30 June 2005 site visit May determine leak test status. Leak tests taken during site visits have been sent for analysis. Event Report "WA-05-039 "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) N/A "Release of activity? Unknown "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: see above "Exposure (intended/actual); consequences: unknown "Was patient or responsible relative notified? N/A "Was written report provided to patient? N/A "Was referring physician notified? N/A "Consultant used? No" Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-09-14
41977 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2005-09-09 10:00 | 2005-09-09 16:35 | 2005-09-09 | UNPLANNED CONTAMINATION EVENT "An unplanned contamination event occurred on 8 September 2005. This is a reportable event in accordance with 10CFR40.60 sub paragraph(1) based on an unplanned event that resulted in additional radiological controls being required for more than 24 hours. The 24 hour period ended at 1000 on 9 September 2005 [the reported event date]. The additional control imposed was the wearing of air purifying respirators on the second floor of the Feed Materials Building. The location of the events was the Feed Materials Building second floor. The Feed Materials Building converts milled uranium oxide material to uranium hexafluoride by using a dry process. Air samples from the second floor were analyzed and the airborne radioactivity averaged approximately 6.5E-11 microCuries/ml. The airborne contaminant was natural uranium ore concentrate and the physical form is a light microscopic dust. The processes in the area of the elevated levels of airborne radioactivity have been secured and potential leakage paths are being investigated." The licensee stated that bioassay sampling of exposed individuals will be performed within the routine sampling frequency, but prior to 09/30/05. The licensee notified NRC Region 2 (D. Collins). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2005-09-09
41976 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-08-31 | 2005-09-09 12:07 | 2005-09-09 | TEXAS AGREEMENT STATE REPORT - LOST NUCLEAR GAUGES "Agency received notification of two found devices. The devices were found to belong to Alcoa Alumina Atlantic in Point Comfort. An on-site investigation at the licensee's facility was performed on 09/06-09/07/05, by two TX Radiation Control (RC) inspectors, who subsequently found that there was actually an inventory total of six devices that were missing from the Alcoa facility (all Texas Nuclear, Model 5192 gauges, with 20 milliCuries of Cs-137). The licensee stated that the six device/gauges were removed from the plant equipment [area] over the period of October 2003-October 2004, and placed into storage. They maintain that they do not know how or when two of the devices/gauges were taken from the facility as scrap metal for recycling, and do not know the location of the other four devices/gauge. "The devices/gauges that have been found are: one (Serial Number B1683) at Nucor Steel Texas Division, Highway 79, Jewett, Texas 75846 (TX RAM L02504), and two (Serial NumberB1686) at GSD Trading USA, Inc. scrap yard, Houston, Texas. Nucor Steel has bee directed by TX Radiation Control to hold on to all scrap metal received from Alcoa. GSD has been surveying all scrap metal received from Alcoa for radiation detection. Impoundment orders were issued from TX Radiation Control on 09/09/05, for TX Radiation Control's RSO, to take possession of all radioactive devices containing Cs-137 at Nucor Steel and all radioactive material, excluding RAM exempt under 25 TAC §289 and naturally occurring material (NORM) possessed under a general license that is found at the GSD facility. All materials taken in possession by RC's RSO will be temporarily stored at RC headquarters in Austin, Texas. "The four devices/gauges that were determined to be missing are: Manufacturer: Texas Nuclear, Model 5192 with the respective Serial Numbers: B1682, B1684 B1685, & B1687. Efforts are still being made to recover the remaining missing four gauges. "Texas Incident No. I-8258" Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-09-14
41975 | 0 | WASHINGTON HOSPITAL CENTER |  |  |  |  | 2003-04-09 | 2005-09-09 11:43 | 2005-09-09 | PATIENT COUGH CAUSED RADIATION DOSE TO BE ADMINISTERED NO MORE THAN 6 MILLIMETERS FROM THE CORRECT SITE. A patient was having a hearing loss due to pressure (tumor inside the brain). The patient was being treated using a gamma knife. Toward the end of the patient's final treatment, toward the end of the 11 stage of the treatment plan, the patient coughed. The cough caused a pin used to stabilize the patient's skull to become dislodged (shifted). This resulted in the patient being administered a dose not directly to the tumor (dose administered no more than 6 millimeters from the correct area). No harm was caused to the patient. All physicians involved in the case were notified. The licensee has been discussing this event for the last couple of years and they were asked to report this event to the NRC Headquarters Operation Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | DC | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-09-09
41974 | 0 | SCHLUMBERGER TECHNOLOGY CORP |  |  |  |  | 2005-08-29 | 2005-09-09 11:25 | 2005-09-09 | TRITIUM SOURCES ON GULF OIL PLATFORM LOST DUE TO HURRICANE KATRINA The Radiation Safety Officer for Schlumberger Technology Corporation reported that two Tritium Neutron Pulse Generators (Schlumberger Model 7158) with 1.6 Curie tritium sources (total of 3.2 Curies) were lost from an oil platform (Oil Platform Ensco-29) in the Gulf of Mexico. The platform was severely damaged and most equipment lost due to Hurricane Katrina storm damage. The licensee has reported this item to Region 4. This is less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-09-09
41973 | 0 | ST VINCENT HOSPITAL |  |  |  |  | 2005-09-07 | 2005-09-07 16:34 | 2005-09-07 | FIVE MEDICAL EVENTS WERE DISCOVERED TO HAVE OCCURRED AT ST.VINCENT HOSPITAL IN INDIANAPOLIS, IN The five events occurred between 3 patients and are explained in the following write-up. "Events 'A', 'B', and 'C' involve the same patient who received three high dose rate (HDR) brachytherapy administrations on three different occasions with a GYN cylinder application. The dates of treatment occurred on December 19, and 26, 2002 and January 2, 2003. In this case, a 70 year old female, was treated with a Nucletron High Dose Rate (HDR) brachytherapy remote aflerloader unit for endometrial cancer. The physician Authorized User (AU) prescribed a dose of 500 cGy at 0.5 cm from the surface of a 3.0 cm diameter vaginal cylinder for an active length of 6.0 cm using a 8.01, 7.506 and 7.030 Ci iridium-192 source on the three dates of treatment. The treatment plan called for 25 indexer step positions at 2.5 mm spacing. The medical physicist entered 25 indexer step positions at 5.0mm spacing rather than 2.5mm spacing and treatment was delivered. "A simulated plan was calculated on August 23, 2005, to reproduce the initial treatment plan and actual treatment delivered. The simulation reveals that the patient may have received as much as 360 cGy to an unintended delivery site with each of the three fractions, for a total of 1,080 cGy for the entire course of treatment. The simulation further indicates that the intended treatment site may have received as much as 28% under dosage during the same treatment period. A thorough review of the patients chart indicates that the patient reported having had some "excoriation" of the unintended site initially following treatment but this area had healed prior to a follow up exam on February 6, 2003. "This patient was last seen by her radiation oncologist January 3, 2004, with no evidence of clinical complications or abnormalities. "As a result of this review and discovery, St. Vincent Hospital will notify the referring physician and the patient of this event. No further clinical complications are anticipated or expected. "Event 'D' occurred on December 18, 2002, involved an HDR brachytherapy which also involved a GYN cylinder application. "In this case, a 56 year old female, was treated with Nucletron High Dose Rate (HDR) brachytherapy remote after loader for cervical. Cancer. The physician Authorized User (AU) prescribed a dose of 500 cGy at 0.5 cm from the surface of a 2.50 cm diameter vaginal cylinder for an active length of4.0 cm. using a 8.089 Ci iridium-1.92 source. The treatment plan called for 17 indexer step positions at 2.5mm spacing. Although the first two fractions were delivered in accordance with the written directive without incident (November 19 and November 26, 2002), for the third and final fraction (December 18, 2002) the medical physicist entered 17 indexer stop positions with 10.0 mm spacing rather than 2.5 mm spacing and treatment was delivered. "A simulated plan was calculated on August 23, 2005, to reproduce the initial treatment plan and actual treatment delivered. The simulation suggests the patient may have received as much as 200cGy to an unintended site and as much as 60% under dosage to the intended site during delivery of the final fraction. For the entire course of treatment, the calculated dosage through simulation indicates that 1200 cGy rather than 1500 cGy was delivered to the intended site. This represents a twenty percent (20%) under dosage for the overall treatment. A thorough review of the patient chart indicates no abnormal findings during follow up clinical exams and our Radiation Oncology Physicians verify these treatment parameters are within acceptable therapeutic and clinical dosages. "This patient is currently in active follow-up with her radiation oncologist. This patient was last seen May 5th, 2005 with no evidence of complications or clinical abnormalities. As a result of this review and discovery, St. Vincent Hospital will notify the referring physician and the patient of this event. No further clinical, complications are anticipated or expected. "Event 'E' occurred on August 7, 2003, involved an HDR brachytherapy which also involved a GYN cylinder application. "In this case, an 85 year old female, was treated with Nucletron High Dose Rate (HDR) brachytherapy remote after loader for cervical cancer. The physician Authorized User (AU) prescribed a dose of 500 cGy at 0.5 cm from the surface of a 2.00 cm diameter vaginal cylinder. For an active length of 6.0 cm using a 4.74 Ci iridium-1.92 source. The treatment plan called for 13 indexer step positions at 5.Omm spacing. In the delivery of the first fraction, on August 7, 2003, the medical physicist entered 13 indexer step positions with 2.5mm spacing rather than 5.0mm spacing and treatment was delivered. The delivery of the second and third fractions, August 21 and September 4, 2003, the written directive was followed accurately and treatment occurred without incident. "A simulated plan was calculated on August 23, 2005, to reproduce the initial treatment plan and actual treatment delivered. The simulation suggests that for the initial treatment fraction, the patient may have received as much as 60% over dosage to the proximal portion of the intended site and as much as 44% under dosage to the distal portion of the intended site. The calculated dosage through simulation indicates that 800 cGy was delivered to the proximal portion of the intended treatment site and approximately 280 cGy was delivered to the distal portion of the intended treatment site. "In accordance with the written directive, the intended site was to receive a dosage of 500 cGy for three fractions for a total of 1500 cGy throughout the course of treatment. The calculated simulation reveals the proximal site received 1800 cGy (20% over dosage) and the distal site received 1280 cGy (15% under dosage) over the course of the three treatments. A. thorough review of the patient chart indicates no abnormal findings during follow up clinical exams and our Radiation. Oncology Physicians verify these treatment parameters are within acceptable therapeutic and clinical dosages. "This patient is currently in active follow-up with her radiation oncologist. This patient was last seen August 15, 2005 with no evidence of complications or clinical abnormalities. "As a result of this review and discovery, St. Vincent Hospital will notify the referring physician and the patient of this event. No further clinical complications are anticipated or expected, "It is believed that the conditions and practices which contributed to the five medical events listed above were identified during the course of investigating the previous medical event of April, 2004. It is further believed that St. Vincent Hospital has implemented corrective action since the event of April, 2004 that has eliminated (or significantly reduced the risk of) recurrence of these conditions/practices." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-09-07
41972 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-07-28 | 2005-09-07 12:42 | 2005-09-07 | WELL LOGGING SOURCE LODGED NEAR THE BOTTOM OF A 240 FOOT SHAFT On July 28, 2005, a 100 milliCurie Cs-137 sealed source (New England Nuclear, Model 572, serial number 1623) became lodged near the bottom of a 240 foot shaft The logging probe and source had descended to that depth after breaking loose from the logging cable at the surface of the well. Repeated efforts to retrieve the source failed, Retrieval efforts were discontinued when a 4 foot section of an overshot device twisted off at approximately 210 feet down-hole. The licensee submitted a written description of the event on August 23, 2005 and provided supplemental information on September 1, 2005 and September 2, 2005. Authorization to abandon the well formally approved on September 6, 2005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-09-12
41971 | 0 | CONOCO PHILLIPS |  |  |  |  | 2005-09-06 15:10 | 2005-09-07 15:10 | 2005-09-07 | FAILURE OF OHMART "DENSITY PROFILER" GAUGE The licensee's RSO reported that a "density profiler" gauge failed, and the 10 milliCurie Cs-137 source broke away from the gauge. The source is now at the bottom of a 10 foot deep well, which is inside a drum at the Alkalization Unit. The gauge is manufactured by Ohmart, model MDTS and s/n 67524GK. The density profiler gauge has a source on the end of a tape, and the tape reels in and out of the instrument. When the tape broke, the Cs-137 source fell to the bottom of the well. No personnel exposure occurred. The RSO surveyed the area and found readings of 3 milliRem/hr at contact and 1.8 milliRem/hr at 1 foot. The licensee contacted the manufacturer who will be sending a technician out to repair the gauge. Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | MT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2005-09-07
41970 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2005-09-06 14:05 | 2005-09-06 21:45 | 2005-09-06 | QUALITY ASSURANCE FITNESS FOR DUTY BLIND SAMPLES TESTING "This event was determined to be reportable per 10 CFR26 Appendix A Section 2.8(e)(4): The licensee shall investigate any unsatisfactory (blind) performance testing result. A record shall be made of the investigation findings and the corrective actions taken by the laboratory. "Event Description: Two known positive Fitness for Duty QA blind samples (both had the same lot number) were sent to the drug testing laboratory and both results came back negative." The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.73 |  |  |  | 0 | 2005-09-06
41969 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2005-09-06 | 2005-09-06 14:02 | 2005-09-06 | LOST/STOLEN PORTABLE GAUGE The State provided the following information via facsimile: "The South Carolina Department of Health and Environmental Control was notified on September 6, 2005, by the licensee, that a portable gauging device had been lost or stolen from a Forest Drive work site in Columbia, South Carolina. The technician stated he may have inadvertently left the gauge at the Forest Drive work site as he traveled to a second work site. When the technician returned to the Forest Drive location the gauge was missing. The licensee is in the process of notifying the police. The gauge is a CPN International, Inc. model MC series Portaprobe serial number M350702733 containing 10 mCi [milliCuries] of cesium-137 and 50 mCi of Am-241:Be. Updates to this event will be made through the national NMED system." South Carolina Report ID: SC050006 A police report was filed. Source is less than the quantity of an IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2005-09-09
41967 | 0 | PALISADES | 1 |  |  | [1] CE | 2005-09-01 10:25 | 2005-09-01 11:23 | 2005-09-01 | REACTOR TRIP DUE TO MAIN GENERATOR HYDROGEN LEAK "The Palisades reactor was manually tripped from approximately 100% power at 1025 hours EDT due to a hydrogen leak from main generator. At 1027 hours, an automatic actuation of the auxiliary feedwater system occurred, as designed, to maintain steam generator levels. The atmospheric steam dump valves opened and reseated per design on reactor trip. Reactor decay heat is being removed via steaming through the turbine bypass valve to the main condenser. The source of the hydrogen leak was determined earlier to be a cracked weld that could not be repaired on line. The main generator must be purged in order to repair the weld. "This is reportable under 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A)." All control rods fully inserted. There are no known Steam Generator tube leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-09-01
41966 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-08-31 14:28 | 2005-08-31 17:38 | 2005-08-31 | UNIT 3 EXPERIENCED AN AUTOMATIC REACTOR TRIP DURING ROUTINE TESTING "Event: At 1428 hours on 8/31/2005, Oconee Unit 3 tripped. A routine test of the alternate power source for the Control Rod Drive System was in progress when power to the Control Rod Drive system was interrupted, which resulted in a reactor trip. AC power transferred to the Start-up source (switchyard). Normally the Main Steam Header pressure control setpoint is automatically increased for post-trip RCS temperature control. This did not occur. As a result the RCS cooled down to approximately 536F (versus a normal post-trip temperature of approximately 555F), reducing RCS pressure to the actuation setpoint for Engineered Safeguards Channels 1 and 2. This started the High Pressure Injection pumps in ECCS mode, caused partial containment isolation and initiated start-up of both Keowee Hydro Units (emergency power). Because Start-up power was available, Keowee did not supply power but remained in stand-by. At 1433 hours Operators terminated ECCS injection. "Initial Safety Significance: Because RCS pressure decreased below normal post-trip levels which resulted in an ECCS actuation, this is considered an abnormal transient. Unit 3 has been stabilized and at this time the actual event is considered to have low safety significance. The exact cause of the loss of power to the Control Rod Drive system is unknown, but is under investigation. It is suspected that that loss also resulted in the failure of the Main Steam Header Pressure to shift to the post-trip Main Steam pressure control setpoint. "Corrective Action(s): Operations stabilized Unit 3. A post-trip investigation is in progress, per site procedures and directives." All control rods fully inserted as a result of the reactor trip. No primary or secondary reliefs or PORVs lifted. Pressurizer level decreased off-scale low and was recovered prior to securing the High Pressure Injection pumps (the licensee estimates approximately 3000 gallons was injected). Current RCS temp is 542F (Tave) with RCS pressure in the normal post-trip band. Decay heat is being removed by the Steam Generators to Condenser through the Turbine Bypass Valves. Main Feedwater remained in service during the transient. The licensee informed the NRC Resident Inspector and does not plan a press release at this time. * * *UPDATE FROM LICENSEE (NIX) TO NRC (HUFFMAN) @ 2156 EDT ON 8/31/05 * * * "During this event, the Engineering Safeguards (ES) System was manually bypassed at 14:33 on 8-31-05 to restore both High Pressure Injection (HPI) System trains to a normal lineup following an ES-initiated safety injection. Manually bypassing ES for both trains of HPI required entry into Tech Spec 3.0.3 at 15:33 on 8-31-05. Tech Spec 3.0.3 requires shutdown of Unit 3 to Mode 3 by 03:33 on 9-1-05 and to Mode 4 by 09:33 on 9-1-05. This condition was discovered to apply at 21:15 on 8-31-05. "Initial Safety Significance: Units 1 and 2 remain at 100% power with no issues following the Unit 3 ES Actuation and Keowee Hydro Unit emergency start. Unit 3 remains in Mode 3. No other safety systems have actuated or exhibited abnormal behavior. Therefore, the safety significance of this condition is LOW. "Corrective Action(s): Restore ES System to Automatic for the HPI System." The licensee reported this under 10 CFR 50.72(b)(2) (i), Technical Specification Shutdown. The licensee will notify the NRC Resident Inspector. R2DO (Lesser) notified. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION | PLANT S/D REQD BY TS | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(i) | 0 | 2005-08-31
41965 | 0 | NATIONAL RESPONSE CENTER |  |  |  |  | 2005-08-31 13:30 | 2005-08-31 16:13 | 2005-08-31 | POTENTIAL RELEASE OF RADIOACTIVE MATERIAL AT SCENE OF VEHICLE ACCIDENT The U.S. Coast Guard National Response Center (NRC) was informed by a representative of Cardinal Health Nuclear Pharmacy Services located in Dublin, OH, that one of their commercial trucks operating in Kansas City, MO, was involved in a fatality (driver) accident. The reporting party (representative) noted that there was a potential release of approximately 200 millicuries Technetium-99m due to the accident, however, this could not be confirmed since the police are treating the location as a crime scene. The U.S.C.G. NRC notified NRC Region III Office and various federal agencies including DOT, EPA and HHS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | TRA | [5 empty] | 0 | 2005-08-31
41964 | 0 | DOW CHEMICAL |  |  |  |  | 2005-08-30 14:00 | 2005-08-31 10:27 | 2005-08-31 | SAFETY EQUIPMENT FAILS TO FUNCTION PROPERLY The RSO called to state that the Bromine Monitor at their facility failed to function properly. The shutter on the monitor failed to close, thus leaving it in an unsafe condition. The licensee taped a piece of metal (the same metal as the shutter) across the instrument to render it in a safe condition. The equipment was removed from service and no personnel received exposure from the event. The equipment is made by AEA Technology, Model number CUCD2, s/n 5738LY. The radionuclide is 10 microCuries of Cd-109 (cadium-109). A qualified technician has been dispatched to repair the Bromine Monitor. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2005-08-31
41963 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-08-30 08:30 | 2005-08-30 14:25 | 2005-08-30 | A STATE LICENSEE REPORTED ONE OF THEIR TROXLER MOISTURE DENSITY GAUGES HAD BEEN STOLEN A Troxler moisture density gauge was stolen from the company truck while parked at the private residence of a Wingerter Laboratory employee. The gauge was checked out from the company at 0630 and taken to his residence to pick up job related paperwork. While at the job site the RSO was notified at 0830 that the gauge was missing. The driver said he made no stops while driving from his residence to job site. The Troxler gauge (model 3440, serial #19973) contained 8 mCi (milliCuries) of Cs-137; 40 mCi of AM-241/Be. Wingerter is offering a $1000 reward for the return of the gauge in local newspaper. Florida incident #FL05-120 This is less than the quantity of a IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-09-02
41962 | 0 | MICHIGAN STATE UNIVERSITY |  |  |  |  | 2005-08-30 10:30 | 2005-08-30 13:27 | 2005-11-17 | LICENSEE REPORTED AN UNACCOUNTABLE CALIFORNIUM-249 SOURCE The licensee reported that a 0.958 microCurie (as of 02/05/83) source of Californium 249 was unaccounted for when the device was inspected prior to usage. The source is a solid electrode deposit on a platinum foil which is used to calibrate nuclear physics instrumentation. The last inventory was conducted on 07/25/05, but it was only a visual check of the container. The last activity identification of the device was on 05/11/04. They have searched and are continuing the search to find the material. No evidence of contamination has been detected in the area at this time. This is a IAEA Category 5 material. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. *** UPDATE FROM ROSSI TO KNOKE AT 13:05 EDT 0N 09/07/05 *** The licensee made a correction to the 3rd sentence in the first paragraph to read as follows: "The last inventory was conducted on 07/25/05, which was a physical inventory of the source." Notified R3DO (Cameron) and NMSS (Hickey), and emailed TAS (Danis). * * * UPDATE FROM K. ERICKSON TO W. GOTT AT 0855 ON 11/17/05 * * * The licensee located the lost material on November 10, 2005. The source was in the restricted area of the facility but was not in the normal storage location. The source in now in the appropriate locked storage location. The licensee notified Regions 3 (S. Bakhsh). Notified R3DO (Stone), NMSS (G. Morell), email Canadian Nuclear Safety Commission, and TAS (Whitney). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-08-30
41961 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-08-29 17:45 | 2005-08-29 19:22 | 2005-08-29 | EMERGENCY RESPONSE DATA SYSTEM (ERDS) WAS OUT OF SERVICE FOR APPROXIMATELY 20 MINUTES The licensee's ERDS was unavailable for 20 minutes. After another attempt was made to activate ERDS, it was successful when the phone modem was cycled and the connection was established. The NRC resident Inspector was notified.. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-29
41960 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-08-29 10:30 | 2005-08-29 15:14 | 2005-08-29 | OFF SITE NOTIFICATIONS DUE TO INOPERABLE EMERGENCY EVACUATION SIREN "On August 29, 2005 at approximately 10:30 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department identified an inoperable single siren (#18). The siren was vandalized by stealing the internal battery. The affected siren is estimated to impact approximately 131 members of population in the emergency planning zone (EPZ) within 5 miles. This call is being placed due to the relatively large segment of the population affected and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area's) when sirens are inoperable. "Maricopa County and State agencies have been informed to implement the MCSO notification if a need arises. "There are no events in progress that require siren operation." The NRC Resident Inspector has been notified | 78 | 91 | 99 | 78 | 91 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-08-29
41959 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-08-29 12:18 | 2005-08-29 14:29 | 2005-08-29 | PARTIAL LOSS OF EMERGENCY SIRENS ASSOCIATED WITH HURRICANE KATRINA "Due to winds associated with hurricane Katrina, power has been loss to 17 of the 43 emergency sirens. This places the number of required sirens less than the operability rate of 75%. Additional sirens may be lost as the storm passes through the area. A recovery plan will be developed and implemented once weather conditions allow. "Notification per ENS [the Emergency Notification System] could not be accomplished and notification was made per commercial phone lines. This event notification documents loss of ENS also which was verified by NRC." The licensee has notified State and local authorities and the NRC Resident Inspector of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-29
41958 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-08-29 10:45 | 2005-08-29 14:18 | 2005-09-04 | SAFETY PARAMETER DISPLAY SYSTEM AND EMERGENCY RESPONSE DATA SYSTEM PLANNED UPGRADE OUTAGE "On August 29, 2005 at about 1045 PDT, San Onofre Nuclear Generating Station, Unit 3, removed a portion of the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) from service for a planned upgrade to ensure long-term reliability and improve the human-machine interface. This work is expected to complete within seven days. "The SPDS emergency assessment function at San Onofre is implemented by a combination of the Qualified Safety Parameter Display System (QSPDS) and the Critical Function Monitoring System (CFMS). The QSPDS portion, which provides emergency assessment capability to plant operators in the control room, will remain functional. The CFMS portion, which receives input from the QSPDS, implements the ERDS and communicates data to the Technical Support Center and Emergency Offsite Facility. Only the CFMS and ERDS are impacted by this upgrade. "This planned CFMS outage is being reported in accordance with10CFR50.72(b)(3)(xiii) as a courtesy notification even though only a portion of the SPDS will be removed from service and preplanned compensatory measures will be in place for the duration of the work. "At the time of this report, Unit 2 and Unit 3 were operating at about 99 percent and 100 percent power, respectively. The NRC Resident Inspectors will be notified of this occurrence and will be provided with a copy of this report." * * * UPDATE ON 09/04/05 AT 0249 FROM C. WILLIAMS TO P. SNYDER * * * "The CFMS upgrade work was completed on September 3, 2005 at 2255 PDT. The SPDS and ERDS have been returned to service. "The NRC Resident Inspectors will be notified of this occurrence." Notified R4DO (Smith). | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-29
41956 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-08-28 11:00 | 2005-08-28 11:04 | 2005-08-28 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE SUPPRESSION CHAMBER VACUUM BREAKER "At 0325 on 8/28/05 the `B' Drywell to Suppression Chamber vacuum breaker indication began cycling from closed to intermediate open. Attempts were made to close the vacuum breaker from the control room were not successful. Attempts to establish a differential pressure between the drywall and suppression chamber airspace were also not successful at getting the vacuum breaker to close and stay closed. Technical Specification 3.6.4.1 was entered at 0325 and a plant shutdown was initiated at 1100 to comply with Technical Specifications. With the vacuum breaker open or partially open, the pressure suppression function of the suppression chamber could be compromised in the event of a postulated loss of coolant accident and therefore this safety function is degraded. The inoperability of this vacuum breaker is reportable in accordance with 50.72(b)(3)(v), The cause of the open vacuum breaker is currently not known. The plant will be taken to cold shutdown to facilitate torus entry to effect repairs. "There was no other equipment that was unavailable that contributed to this event. All other safety related equipment is currently operable." The licensee is starting a normal shutdown. The licensee notified the NRC Resident Inspector and will be notifying the LAC Township. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(A) |  |  | 0 | 2005-08-28
41955 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-08-28 02:25 | 2005-08-28 04:50 | 2005-08-28 | FAILURE OF NOAA WEATHER SERVICE RADIO "Failure of the NOAA Weather Service radio was reported by Plant Hatch Site Security after receipt of an alarm message in the Security Secondary Alarm Station. The NOAA Weather Service radio was out of service for greater than 15 minutes as of 0225. The NOAA Weather Service radio was out of service for 1 hour and 16 minutes, from 0209 to 0325 on August 28, 2005. "The NOAA Weather Service radio has been restored to service by the Jacksonville Weather Service after repair's were done by their local telephone provider. As of 0325 the NOAH Weather Service radio is operable. Discussions with Jacksonville Weather Service indicate they do not know, at this time, what the problems were, or how they were resolved by their telephones service provider." The licensee notified State and local agencies and the NRC Resident Inspector. | 100 | 98 | 0 | 100 | 98 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-28
41954 | 0 | WATERFORD | 3 |  |  | [3] CE | 2005-08-27 22:04 | 2005-08-27 23:22 | 2005-09-08 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING At 2204 CDT, an Unusual Event was declared due to a Hurricane warning in St Charles Parish, LA. The licensee does not have any Limiting Conditions for Operation on safety related equipment. No electrical grid disturbances currently exist. The licensee will be notifying the NRC Resident Inspector. The licensee notified the State and Local government agencies. * * * UPDATE FROM J. PIERCE TO M. RIPLEY 1144 EDT 08/28/05 * * * "Waterford 3 will commence a plant shutdown to Mode 4 on August 28, 2005 at 1100 CDT. The goal is to be approximately 325 deg F reactor coolant system temperature with both trains of Shutdown Cooling in service [expected at approximately 0100 CDT 08/29/05] . This is approximately 2 hours before hurricane force winds are expected on site." Notified R4DO (Jones), NRR EO (Kuo), IRD Mgr. (Wilson), DHS (York), and FEMA (Canupp). * * * UPDATE FROM J. PIERCE TO J. ROTTON 1131 EDT 08/29/05 * * * As a result of Hurricane Katrina, all offsite power was lost at 0800 CDT. The emergency diesel generators successfully started and loaded. Notified R4DO (R. Bywater), NSIR (Leach, Wilson), NRR EO (Kuo, Jung), FEMA (Kuzia), DHS (Stransky). * * * UPDATE FROM LICENSEE (LEWIS) TO NRC (HUFFMAN) AT 2302 EDT ON 8/29/05 * * * The Hurricane warning for St Charles Parish, LA, has been discontinued by the National Weather Service. Initiating condition, D UE-5, is no longer applicable. Waterford 3 remains in an Unusual Event for initiating condition C UE-1, loss of all offsite power. An agreement to relax 60 minute notification updates to State and local authorities remains in effect. The licensee has notified State and local authorities as well as the NRC Resident Inspector. Offsite power is available to the licensee switchyard. However, the voltage is too high for plant specification and the licensee remains disconnected from offsite power and on the emergency diesel generators. * * * UPDATE FROM LICENSEE (LEWIS) TO NRC (KNOKE) AT 0001 EDT ON 8/31/05 * * * Waterford 3 remains in an Unusual Event for initiating condition C UE-1, loss of all offsite power. An agreement to relax 60 minute notification updates to State and local authorities remains in effect. The communications system for Public Automatic Branch Exchange (PABX) is working internally, but not externally. Other areas where communications are lost are Emergency Operations Facility (EOF), Operations hotline, Reactor Auxiliary Building (RAB), and the Emergency Notification System (ENS). Waterford has use of an industrial hotline to a circuit in the Parish of St Charles, however, this is very limited in its capability. The Civil Defense communication system is still inoperable. * * * UPDATE AT 1903 ON 9/6/05 FROM WAIG TO GOULD * * * NRC exited monitoring mode at 1800 CDT on 9/6/05. Notified R4 IRC (Waig), R4DO (Powers), IRD (Leach), DHS (Cartlidge), FEMA (Kuzia). * * * UPDATE FROM LICENSEE (LEWIS) TO NRC (KNOKE) AT 19:12 EDT ON 09/07/05 * * * At 17:57 CDT the licensee exited from the Unusual Event. Offsite power was restored and communications were reestablished with (1) a functional operational hotline, (2) a dedicated open line to NRC Headquarters Operations Center, and (3) having the plant PABX circuits routed through Little Rock, AK area code. The plant is holding in Mode 5 until further notice, however, this may change when the decision to (or not to) repair a check valve in the Safety Injection system is made. Notified R4DO (Powers), IRD (McGinty), NRR EO (Hackett), DHS (Sullivan), and FEMA (Kuzia). * * * UPDATE FROM LICENSEE AT 08:45 EDT ON 09/08/05 * * * This report has been updated to reflect the correct time of the licensee exiting their unusual event classification. Unusual event was exited at 1740 CDT not 1757 CDT. Notified R4DO (Powers), IRD (McGinty), NRR EO (Jung). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | LA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-08-27
41953 | 0 | MATERIAL TESTING, INC |  |  |  |  | 2005-08-27 08:00 | 2005-08-27 10:16 | 2005-08-27 | TROXLER MOSITURE/DENSITY GAUGE STOLEN A corporate executive of the licensee stated that about 0800 EDT one of their employees notified him that a Troxler gauge (Model 3411B, s/n 7989) was stolen from the back of his pickup truck. The Troxler gauge, which was correctly chained and boxed in the employee's truck per company regulations, had the chain cut and box removed. The gauge contained 50 milliCuries of Am-241/Be and 10 milliCuries of Cs-137. The LLEA (Newark Police) was notified, however, the report number was not known. The licensee is not offering a reward at this time, and does not expect to make a press release. Less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-08-27
41952 | 0 | EPSILON PRODUCTS |  |  |  |  | 2005-08-27 00:30 | 2005-08-27 02:59 | 2005-08-28 | FIXED GAUGE (OHMART) FAILED TO PROPERLY RETRACT SOURCE The licensee's RSO reported that a Ohmart fixed gauge (s/n HLM-CR-3) containing a 1200 millicurie Cs-137 source (Capsule # M4695) malfunctioned by failing to fully retract the source. The RSO believes the shutter may have sheared the cable and left the source outside the shielded (fully closed) position. A protective barrier for a less than 2 milliRem/hr area was set up to protect personnel, and work in this area was discontinued. The RSO did not know whether any personnel received an exposure due to this incident, however, the licensee's APS manager was going to the site to determine this. A representative of the Ohmart company is also going to the site to repair the faulty equipment. * * * UPDATE 08/27/05 AT 1925 FROM W. APPLEGATE TO P. SNYDER * * * The Ohmart Vega manufacturers representative is onsite to assess the circumstances and is expected to take action tomorrow to correct the problem. Epsilon Products is continuing their "around the clock" investigation of this issue. Notified R1DO (Cook) and NMSS EO (Brach). * * * UPDATE 08/28/05 AT 1320 FROM W. APPLEGATE TO P. SNYDER * * * The source has been retracted back into the holder and secured. The manufacturers representative will stay on-site while the source is packaged and readied for shipment to Ohmart for further evaluation. The temporary barriers have been removed and the area has been returned to normal background radiation levels. Notified R1DO (Cook) and NMSS EO (Brach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2005-08-27
41951 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2005-08-26 18:24 | 2005-08-27 00:19 | 2005-08-27 | RPS ACTUATION - REACTOR SCRAM ON HIGH STEAM GENERATOR LEVEL "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On August 26, 2005, at approximately 18:24 Mountain Standard Time (MST) Palo Verde Unit 1 experienced an automatic reactor scram on high steam generator #1 level. All rods inserted, as required. Unit 1 was at normal operating temperature and pressure prior to the trip. The main turbine was not yet synchronized to the grid; turbine chest warming was in progress. The main turbine automatically tripped in response to the reactor trip. A reactor startup had been completed and operators were transferring feedwater from a motor driven auxiliary feedwater pump to the steam driven 'A' main feedwater pump at approximately 1.2% reactor power. Steam generator #1 level decreased from a normal level of approximately 40% narrow range (approx. 77% wide range) to approximately 12% narrow range (approx. 66% wide range). An operator took manual control of feedwater to increase level. Upon returning feedwater control to automatic after level was restored, steam generator #1 level continued to increase, resulting in a reactor trip on high steam generator level at approximately the Technical Specification reactor trip and Main Steam Isolation Signal (MSIS) setpoint of 91.5%. The MSIS (ESF actuation) functioned as required. No other ESF actuations occurred or were required. No emergency classification was required per the Emergency Plan. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. The maximum power level during the feedwater transient was approximately 8.5%. "Unit 1 is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The maximum RCS pressure was approximately 2251 psia (normal 2250). The maximum steam generator pressure was approximately 1188 psia (normal 1165). The event did not adversely affect the safe operation of the plant or the health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-08-27
41950 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-08-22 | 2005-08-26 13:59 | 2005-08-26 | AGREEMENT STATE - VEHICLE ACCIDENT WITH SPILLED SOURCE The State provided the following information via facsimile: "A well logging licensee notified the [Colorado Department of Health] on 8/26/05, that one of their well logging vehicles was involved in a roll-over accident in Colorado on Monday, 8/22/05, resulting in the spill of a small quantity of Scandium-46. No other vehicles or personnel were involved. "The licensee, ProTechnics, of Trinidad, Colorado, License Number CO-545-01, stated that the accident occurred in a remote area on state highway 550, south of Ouray, Colorado. Emergency vehicles responded to the scene, and the driver was taken to a local hospital with minor injuries. The licensee sent additional personnel to the site with survey meters, and they assisted with the clean up. They reported that the shipping container was ejected from the vehicle, and broke open. They reported that they were able to clean up all of the spilled material, except for one spot that was reading 15 [millirem per hour] on contact. The spot was located in a remote area, several feet to the side of the road. "No other details are available at this time. "The Department has initiated an investigation of this incident, and arrangements are being made to perform a confirmatory survey of the area." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-08-31
41949 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-08-26 | 2005-08-26 13:27 | 2005-08-26 | AGREEMENT STATE - TRITIUM EXIT SIGNS FOUND IN RECYCLABLES The State provided the following information via facsimile: "Wisconsin Radiation Protection Section [RPS] was contacted by Cascade Asset Management Company on August 25th. Workers at Cascade found several exit signs containing Tritium with a shipment of recyclable material. WI RPS staff were dispatched to investigate. Six intact signs and pieces of other signs were found in a trash barrel. Wipes were taken of the signs and barrel, and are being analyzed for contamination. The signs were placed in bags, sealed and placed in a remote part of the building. An investigation into the origin of the signs is under way." Wisconsin Event Report ID No.: 30 This is less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-08-31
41948 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2005-08-25 16:30 | 2005-08-25 20:39 | 2005-09-27 | HIGH PRESSURE COOLANT INJECTION INOPERABLE DUE TO FLOW OSCILLATIONS "This report is being made in accordance with 10CFR50.72 (b) (3) (v) due to the High Pressure Coolant Injection (HPCI) system being declared inoperable. HPCI was declared inoperable on 8/25/05 at 1630 EST due to oscillations at below rated flow during the scheduled operability testing. HPCI was restored to standby line-up when testing was completed and remains available for use. This event is an eight hour notification. Efforts are on going to determine the cause of the oscillations on the Flow Controller. This event had no adverse effect to the health and safety of the public. "The resident NRC inspector has been notified of this event." * * * RETRACTION FROM D. NOYES TO W. GOTT AT 1711 ON 09/27/05 * * * "This follow-up notification is being made to retract the notification made to the NRC Operations Center on 8/25/05 at 2039 hours (notification #41948). "The initial report was made in accordance with 10 CFR 50.72(b)(3) due to the HPCI system being declared inoperable. The system was declared inoperable due to oscillations in turbine speed, pump discharge pressure, and pump flow during a quarterly surveillance test of the HPCI pump. "Further investigation and evaluation of this has been performed. The cause of the noted oscillations was the position of a hand operated valve that is located in the HPCI system full flow test line. The hand operated valve is located downstream of an in-series motor operated valve that automatically closes if an automatic HPCI system initiation signal occurs. The full flow test line is not part of the HPCI injection pathway to the reactor vessel. As a result, the position of this valve would not have impacted the ability of the system to perform its design function. After adjusting the position of the hand operated valve, the surveillance test of the HPCI pump was completed with satisfactory results. "The evaluation has determined that the HPCI system was capable of performing the designed safety function. Therefore, the HPCI system was not inoperable and event notification #41948 is retracted." The licensee notified the NRC Resident Inspector. Notified R1DO (C. Cahill) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-08-25
41947 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2005-08-25 10:59 | 2005-08-25 15:58 | 2005-08-25 | POSITIVE RANDOM FITNESS FOR DUTY TEST - ALCOHOL A licensed employee was determined to be under the influence of alcohol during a random fitness-for-duty test. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2005-08-25
41946 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2005-08-25 11:41 | 2005-08-25 12:07 | 2005-08-25 | UNUSUAL EVENT DECLARED DUE TO FIRE IN PROTECTED AREA "At 1125 on 8/25/05, the 'B' condensate pump tripped. Upon investigation, the turbine building operator noticed smoke coming from the pump motor. There was no visible flame at this time. In response, the 'A' condensate pump was started. Due to a suspected malfunction of the 'A' condensate pump discharge valve, a low water level condition developed in the deaerator storage tank. The order was then given to manually trip the reactor. However, before the operator could complete this action, the low level condition automatically tripped the feedwater pumps and the main turbine which by design tripped the reactor at 1133. "A Notification of Unusual Event (NUE) was declared at 1141 due to a fire in the protected area lasting for more than 15 minutes. The fire was initially extinguished at 1200. Subsequently, a small flame was noted within the pump motor housing upon removal of an inspection cover at 1253. The fire was ultimately extinguished at 1317. "The plant is currently stable in mode 3. According to current indications, all safety systems operated as required. The fire was fully contained within the pump motor housing and did not cause any collateral damage. No radioactivity was released to the environment and there were no injuries." The licensee requested offsite assistance from the Fairfield Fire Department. All control rods fully inserted from the automatic trip. Decay heat was being removed via emergency feedwater into the steam generators through the steam dumps into the main condenser. Normal offsite power was available and electrical power was in normal alignment. The licensee notified the NRC Resident Inspector. The licensee notified state and local government agencies. * * * UPDATE ON 8/25/05 AT 1346 EDT FROM R. SWEET TO SNYDER * * * At 1327 the licensee terminated the Unusual Event. The licensee was continuing to investigate the cause of the automatic reactor trip and the fire. Notified R2DO (D. Ayers), NRR EO (I. Jung), IRD Manager (P. Wilson), FEMA (K. Sweetser), and DHS (Krause). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-08-25
41945 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2005-08-24 23:37 | 2005-08-25 02:23 | 2005-08-25 | EMERGENCY DIESEL GENERATOR AUTOMATIC START DUE TO BUS SUPPLY BREAKER TRIP 4160 volt Bus 1D normal supply Breaker 1D tripped open. The associated No. 2 EDG automatically started and is supplying the 1D 4160 volt Bus. Plant equipment responded as expected. Troubleshooting is in progress to determine the cause of the breaker trip. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-08-25
41944 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-08-24 23:02 | 2005-08-24 23:43 | 2005-08-25 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING "On 8/24/2005, at 2302 an Unusual Event was declared at St. Lucie Plant based upon the 2300 EDT Tropical Storm Katrina Forecast/Advisory. A Hurricane Warning has been issued for the southeast Florida coast from Vero Beach southward to Florida City. A Hurricane Warning means that Hurricane conditions are expected with the warning area within the next 24 hours. The St. Lucie Plant falls within this Hurricane Warning area." The licensee entered the Unusual Event based on EAL '5-B.' Currently Unit 2 'B' Train of Component Cooling Water is out if service for planned maintenance. The licensee notified the state and the NRC Resident Inspector. * * * UPDATE FROM J. ABERNETHY TO ROTTON AT 1824 EDT ON 08/25/05 * * * The licensee terminated the Unusual Event at 1815. Updated National Weather Service data removed the hurricane warning in the area. The licensee notified state and local governments. The licensee notified the NRC Resident Inspector. Notified R2DO (Ayers), NRR EO (Kuo), IRD Manager (Wilson), FEMA (Erwin), and DHS (Haselton). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-08-24
41943 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-08-24 23:04 | 2005-08-24 23:26 | 2005-08-26 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING The licensee declared an Unusual Event in accordance with their emergency procedures due to hurricane force winds expected within 24 hours. The licensee does not have any Limiting Conditions for Operation on safety related equipment. No electrical grid disturbances currently exist and the licensee is currently testing their diesel generators in accordance with their emergency procedures. All emergency diesel generators are operable. The licensee notified state and local government agencies and the NRC Resident Inspector. * * * UPDATE FROM D. MORRIS TO W. GOTT AT 0141 EDT ON 08/26/05 * * * The licensee terminated the Unusual Event at 0110. Updated National Weather Service data removed the hurricane warning in the area. The licensee notified state and local governments. The licensee notified the NRC Resident Inspector. Notified R2DO (Ayers), NRR EO (Kuo), IRD Manager (Wilson), FEMA (Irwin), and DHS (Biasco). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-08-24
41942 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-08-23 15:45 | 2005-08-24 15:47 | 2005-08-24 | OFFSITE NOTIFICATION TO STATE OF NEW JERSEY DUE TO CHEMICAL SPILL "This is a 4-hour notification to report a notification made to the New Jersey Department of Environmental Protection [NJDEP] for a chemical spill to the ground that could not be cleaned up within 24 hours. The spill was discovered at 1545 on 8/23/05, when water containing approximately 30 ppm hydrazine was discovered north of the condensate polisher building. The source of the spill was secured. Efforts to clean-up the affected soil commenced in parallel but could not be completed within 24-hours therefore necessitating notification of NJDEP per NJAC 7: 1E. The full volume of the discharge is unknown, however approximately 500 gallons of water have been removed. The operations shift manager made a report to the state of New Jersey to report the discharge at 1530 [on 08/24/05] when it was realized that the clean up could not be fully completed in less then 24 hours. There was no effect on plant operation. There was no one injured during the event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-08-24
41941 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-08-23 13:49 | 2005-08-23 19:01 | 2005-08-23 | TWO EMERGENCY SIRENS INOPERABLE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On August 23, 2005 at approximately 13:49 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department identified a siren (#42) inoperable due to a failed battery charger. At approximately 14:00 a faxed notice was found indicating siren #15 had failed its response check. The fax was sent approximately at 07:00 but was not noticed till later since out of service siren notifications are generally made via phone or e-mail. Upon investigation, siren #15 was found inoperable due to a circuit board failure. Siren #15 is estimated to impact approximately 144 members of population in the emergency planning zone (EPZ) within 5 miles, and siren #42 is estimated to impact 496 members of the population in the EPZ, beyond 5 miles but within 10 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles and 10% of the population beyond 5 miles but within 10 miles. This call is being placed due to the relatively large segment of the population affected and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." | 0 | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Cold Shutdown | Hot Standby | Power Operation | Cold Shutdown | Hot Standby | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2005-08-23
41940 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2005-08-23 06:13 | 2005-08-23 13:37 | 2005-08-25 | LOSS OF POWER TO TECHNICAL SUPPORT CENTER (TSC) "This report is being made pursuant to 10CFR50.72(b)(3)(xiii), which is an 8-hour Non-Emergency Report due to the loss of emergency assessment capability. This report documents the loss of power to the Peach Bottom Technical Support Center (TSC). The loss of power was due to an apparent fault of the Normal power supply, which occurred at 0613 on 08/23/05. The Alternate power supply to the TSC was secured for planned maintenance activities. The restoration of the Alternate power supply to the TSC is in progress. The Peach Bottom NRC Resident was notified." No work was being performed on the normal power feed to the TSC when power was lost to the TSC. Normal power has been restored to the TSC but power has not been restored to the TSC compressors (breaker problem). * * * UPDATE ON 08/25/05 AT 1717 EDT FROM ROSS MOONITZ TO GERRY WAIG * * * "As of 1600 on 8-24-05, TSC ventilation was restored via temporary air compressors and the TSC is now fully operational." The licensee has notified the NRC Resident Inspector. | 100 | 95 | 0 | 100 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-23
41939 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2005-08-22 16:05 | 2005-08-22 20:10 | 2005-08-22 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO CORE PROTECTION CALCULATOR SYSTEM (CPCS) SOFTWARE NOT CONSISTENT WITH SYSTEM DESIGN REQUIREMENTS. "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On August 22, 2005, at approximately 1605 hours Mountain Standard Time (MST), Palo Verde Nuclear Generating Station (PVNGS) Unit 2 commenced a reactor shutdown required by Technical Specification 3.0.3. "Westinghouse notified Palo Verde that the current version of the Common Q based Core Protection Calculator System (CPCS) software is not consistent with the system design requirements and Technical Specification Bases regarding the system response to analog input module errors. In that a failed sensor input or failure of the two analog input modules in a given CPCS channel (four total channels) would not result in a CPCS channel trip. At Palo Verde, the CPCS provides the reactor trip functions for Low Departure from Nucleate Boiling Ratio (DNBR) and High Local Power Density (LPD). A failed input sensor would be the most likely cause for both of the redundant input modules to indicate errors simultaneously because the two redundant input modules within a safety channel are connected to a single sensor. A similar scenario would occur if both analog input modules simultaneously failed. In both cases the result would be a failure of the channel without initiating a trip signal. "Operations evaluated the non-conforming condition and declared all four channels of the CPCS inoperable. Limiting Condition for Operability (LCO) 3.3.1 only addresses up to two automatic RPS trip channels inoperable, therefore Operations entered LCO 3.0.3 at approximately 13:26 MST. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. The required offsite power sources are operable and the electrical grid is stable. "The Common Q based CPCS is installed at the following nuclear power plant site in the United States: Palo Verde Unit 2. At this time, this condition is not transportable to Palo Verde Units 1 and 3." All Emergency Core Cooling systems and their Emergency Diesel Generators are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 55 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-08-22
41938 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2005-08-20 | 2005-08-22 16:01 | 2005-11-21 | AGREEMENT STATE REPORT ON A STOLEN MOISTURE DENSITY GAUGE The State provided the following information via facsimile: The State of Nevada reported that a moisture density gauge (CPN Model MC-3, s/n M37037489 with a 50 millicurie Am-241:Be source and a 10 millicurie Cs-137 source) was stolen from a licensee technician's truck. The gauge was locked in the technician's truck at his home. The technician found that the lock had been cut and the gauge stolen sometime over the weekend. The licensee has reported the incident to the Las Vegas Metro Police Department. Nevada State Report Number NV-05-007. * * * UPDATE PROVIDED BY MATUS TO ROTTON AT 1737 EST ON 11/21/05 * * * The State provided the following information via facsimile: "The gauge was recovered on 11/18/05 from an impounded vehicle at Ewing Brothers Tow Service in Las Vegas, NV and released to the licensee." Notified R4DO (Smith), NMSS EO (Holahan), and TAS (Danis via email) This is less than the quantity of an IAEA Category 3 source. Sources that are 'Less than IAEA Category 3 sources,' are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2005-08-25
41937 | -1 | LANCASTER GENERAL HOSPITAL |  |  |  |  | 2005-08-22 15:05 | 2005-08-22 15:05 | 2005-09-07 | PART 21 - GAMMA KNIFE MICROPHONE CLIP Lancaster General Hospital has been using a Leksell Model No. 23005 Type "B" Gamma Knife since 2000. The Gamma Knife unit has a metal clip which is velcroed to the patient's couch and it holds a microphone in which the patient can talk. A patient knocked the clip off, causing the clip to become detached from the couch (it was velcroed to the couch) and the microphone. The clip ended up in the Gamma Knife shielding. Due to the metal clip being stuck in the Gamma Knife shielding, the micro switches inside the Gamma Knife would not allow the jaws of the shielding to open. This prevented the patient from receiving the third treatment. Therefore the patient received only 2 out of 5 scheduled treatments (patient was under dosed) due to the clip failure. See event number 41928 called in by Lancaster General Hospital on 08/18/2005 for background information. *** UPDATE FROM MONTAGNESE TO KNOKE AT 12:07 EDT ON 09/07/05 *** The licensee discussed this event with Region 1 (Gabriel and Henderson). It was determined that this event did not meet 10 CFR 21.21 requirements and notification to the NRC under Part 21 was unnecessary. The notification for this medical event (EN 41928) is still in effect. Notifications were provided to R1DO (Holody), R2DO (Moorman), R3DO (Cameron), R4DO (Powers), NMSS (Morell) and Part 21 NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2005-08-22
41936 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-08-21 12:00 | 2005-08-22 13:39 | 2006-10-31 | AGREEMENT STATE REPORT FROM CALIFORNIA: STOLEN AND RECOVERED CPN MOISTURE DENSITY GAUGE "RHB received notification this morning that an MC-3 CPN moisture-density gauge with 10 mCi [millicuries] (nominal) Cs-137 AND 50 mCi (nominal) Am-241 was stolen from the back of a truck in the City of Garden Grove, sometime yesterday. The RSO had very few details, and intends to forward a copy of the police report as soon as he receives it. The "Other Contact" listed above is the gentleman who was transporting the gauge when it was stolen. The truck was parked at the individual user's home over the weekend, when the gauge was stolen. I asked whether they would be offering a reward, and the RSO said he would discuss that with company management. "CPN MC3 M37027389 "Cs-137 370 MBq (10mCi) "Am-241/Beryllium 1.85 GBq (50 mCi)" State of California Assignment Number for the event: 082205. * * * UPDATE FROM STATE (D. KRAJEWSKI) TO M. RIPLEY AT 1927 EST ON 10/31/06 * * * The State provided the following information via email: "On October 31, 2006, I received an e-mail from [NAME DELETED] from Converse Consultants [EMAIL ADDRESS DELETED] that the gauge (CPN, MC-3, SN # M37027389) was recovered by the Santa Ana Police Department [NAME DELETED] in the parking lot of an apartment complex. The gauge was returned to Converse Consultant who transported the gauge to Maurer Technical to have it leak tested and to get an estimate for repair. The handle of the gauge was in the 'safe' (shielded) position with the source retracted, but horizontal portion of the handle was broken off. The gauge had been repainted. The case was recovered also, but the gauge was not found in the case." Notified R4 DO (D. Powers), NMSS EO (R. Pierson), Mexico (fax), and ILTAB (email) Less than the quantity of a Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-08-25
41935 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-08-19 | 2005-08-20 19:16 | 2005-08-20 | LICENSE REQUIRED 24 HOUR NOTIFICATION OF UNUSUAL FISH KILL "Section 4.1 of Appendix B of the Operating License for Units 2 and 3 requires Southern California Edison (SCE) to report to the NRC within 24 hours any unusual or important environmental events, which includes unusual fish kills. "Between August 19 and August 20, 2005, SCE removed an unusually large number of fish from the Units 2 and 3 intake structure. At approximately 1000 PDT on August 20, 2005, SCE estimated the quantity to be approximately 11,070 pounds (approximately 6420 pounds from Unit 2 and 4650 pounds from Unit 3). While the NRC has not specified a reporting limit for an unusual fish kill, SCE has internally defined this quantity as 4500 pounds. This unusual influx of fish is unrelated to plant operation and a heat treat of the intake structure was not being performed. However, there is a heat treat of the San Onofre Unit 2 intake structure scheduled for later today." The licensee stated that the fish kill was apparently the result of a large school of anchovies that swam to close to the intake. The licensee notified the NRC Resident Inspector. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2005-08-20
41934 | -1 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-08-19 | 2005-08-19 20:32 | 2005-09-02 | VIOLATION OF MAXIMUM CORE POWER LEVEL PER OPERATING LICENSE REQUIREMENTS "Pursuant to the reporting requirements of Item 2.H of the [Vogtle Electric Generating Plant] VEGP Unit 1 and Unit 2 operating licenses, [Southern Nuclear Company] SNC is notifying the NRC of overpower events in violation of the maximum core power level of 3565 MWt authorized by Item 2.C.(1) of the licenses. "Based on a review of operating data dating back to January 2, 2002, SNC has identified occurrences where the daily average core power exceeded 3565 MWt by as much as 0.4 MWt for Unit 1 and 0.9 MWt for Unit 2." The temperature signal from the steam generator blowdown, used as input into the computer calorimetric, was determined to be out of calibration in each unit. The licensee is evaluating this situation for a causal effect. The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1434 EDT ON 9/2/05 FROM STEVE WALDRUP TO S. SANDIN * * * The licensee is retracting this report based on the following: "On 8/19/05, VEGP notified the NRC Operations Center (Notification # 41934) of overpower events in violation of the maximum core power level of 3565 MWt authorized by Item 2.C.(1) of the Unit 1 and Unit 2. operating licenses. "The non-conservative measurement of a plant parameter used in the calorimetric heat balance resulted in underestimating the calculated reactor thermal power. Correcting the calculated reactor thermal power for non-conservatism resulted in the conclusion that the licensed power level was exceeded. This led to the notification described above. "Further engineering evaluation identified conservatisms in the heat balance calculation that were demonstrated to more than offset the non-conservatism discussed above. It was therefore concluded that the maximum core power level did not exceed the power level authorized by Item 2.C.(1) of Unit 1 and Unit 2 operating licenses." The licensee notified the NRC Resident Inspector. Notified R2DO (Mark Lesser). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW | [5 empty] | 0 | 2005-08-19
41933 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2005-08-19 15:30 | 2005-08-19 18:48 | 2005-08-19 | NRC BULLETIN 91-01 VIOLATION OF CRITICALITY SPACING REQUIREMENTS "Criticality spacing configuration requirements for Integrated Fuel Burnable Absorber (IFBA) rod caskets were violated in the IFBA loading dock (Dock 9). IFBA rod caskets are used for transport of IFBA rods from the IFBA loading dock to the Quality Control (QC) Inspection Area. Criticality spacing requirements for the caskets are posted on the lid of each container. The requirements state that loaded caskets are required to remain in the same horizontal array with 12-inch spacing between all other containers not in the same array. As such, stacking of loaded caskets is prohibited. Contrary to this requirement, Westinghouse operations personnel identified several caskets loaded with IFBA rods that were stacked in the IFBA loading dock (Dock 9). It is believed that this spacing condition was present for less than 24 hours, although this has not yet been confirmed. "Notification is being made based on the loss of spacing of the caskets in conjunction with the failure to limit the potential pathway for moderator introduction into the caskets (see discussion below for more detail). "Double Contingency Protection The criticality safety analysis considers criticality not credible for normal and credible process upset conditions. However, the criticality safety analysis (ISA-12) also establishes that criticality is possible if large quantities of rods were stacked and interstitial moderation was provided and retained among the stacked fuel rods. "Introduction of interstitial moderation is limited by the casket covers and through limitation of available sources. While no liquid moderator was present in any of the caskets, the potential pathway for moderator introduction was not addressed by either the criticality safety posting (deficiency in the criticality safety analysis) or operating procedures. In addition (as discussed under the Reason for Notification), the caskets were improperly spaced in a stacked configuration. "It was determined that the criticality safety analysis is deficient and that less than two unlikely, independent, and concurrent changes in process conditions would be required before a criticality accident would be possible. A criticality is judged to be credible through the introduction of moderation and the incorrect configuration of the caskets. "In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (b.3), this event satisfies the criteria for a 4-hour notification. "Summary of Activity: IFBA casket loading operations were discontinued. Operations Management reviewed the procedural requirements prohibiting stacking of caskets with all of the operations personnel. The program to train and re-certify all Operations personnel is continuing, per schedule. The program to assess and reconstitute the plant's criticality safety basis is continuing, per schedule. "Conclusions: Problem was self identified by Westinghouse Operations personnel. As stated previously it is believed that the improper spacing configuration was present for less than 24 hours. Less than double contingency protection remained. No liquid moderator was present in any of the caskets. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed. The plant programs for training and recertification of operations personnel and for assessment and reconstitution of the plant's criticality safety basis are appropriate corrective actions for this type of event and are continuing according to plan." There is no NRC Resident Inspector at the site. The loading operations are estimated to be discontinued for 3 to 7 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2005-08-19
41932 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-08-15 16:00 | 2005-08-19 16:20 | 2005-08-19 | AGREEMENT STATE - MEDICAL EVENT The State provided the following information via facsimile: The State received a telephone call from an RSO with The University of Texas Southwestern Medical Center (UTSWMC) at Dallas on August 16, 2005 at 4:00 p.m. to report a patient misadministration of a therapy dose at UTSWMC Moncrief Medical Center. The event occurred on August 15, 2005 around 4:00 pm. The patient was scheduled to receive 1100 centiGray in two fractions for cancer treatment. Each fraction was supposed to be 550 centiGray to the vaginal vault. The first dose was oriented interior 4 1/2 cm, i.e. too close. The true target point of the vaginal vault received a dose of 1451 centiGray. The second dose was not administered and the patient is not returning for further treatment. Source was an Ir-192 HDR (high dose rate) afterloader. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-08-22
41931 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2005-08-18 14:40 | 2005-08-18 19:03 | 2005-08-18 | HIGH PRESSURE CORE SPRAY SYSTEM INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to mitigate the consequences of an accident. During a scheduled 24 hour surveillance run of the 1B diesel generator, with the diesel generator paralleled to its associated Bus 143, an electrical fault occurred in the Division 3 AC system. This resulted in a trip of the normal System Auxiliary Feed breaker ACB 1432 to the bus. The diesel generator was manually tripped when it was subsequently identified that its associated cooling water pump was not running. With the 1B diesel generator tripped, the Division 3 AC system is de-energized. The consequence is a loss of the Unit 1 High Pressure Core Spray System. High Pressure Core Spray is a single train system that performs a safety function, and therefore, loss of the system is reportable as an 8 hour ENS notification under SAF 1.8. "The required actions of Technical Specification 3.5.1 for the High Pressure Core Spray System were entered on 8/18/05 at 14:40 when the system was made inoperable. All other Emergency Core Cooling Systems are operable at this time. The High Pressure Core Spray system is also unavailable, and On Line Risk for Unit 1 is Yellow. The system has been quarantined, and an investigation is currently in progress to determine the cause of the electrical fault." Unit 2 is not affected by this event, and Unit 1 is in a 14 day LCO to repair the EDG. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-08-18
41930 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-08-15 | 2005-08-18 12:19 | 2005-08-18 | AGREEMENT STATE REPORT - SOURCE OF UNKNOWN ORIGIN FOUND IN RAILCAR The State provided the following information via email: "On 8/15/05 a sealed source was discovered on a rail car in Norfolk and Southern rail yard in Dayton, Ohio. Rail car was parked on spur line adjacent to a scrap yard. Source was discovered when rail car was being moved. Dayton HAZMAT unit was called who, in turn, notified the ODH Bureau of Radiation Protection. Bureau staff member responded to site and found source to be made of stainless steel and aluminum, 4" diameter and 18" long. Labeled as a GL device with the following information: Thermo System, Inc. St. Paul, Minn, Kr-85, 10 mCi, June 1974, Model # 8054, SN 31112. Dose rate at contact with the source was 0.8 milliR/hr and 12 microR/hr at 3 feet, as measured with Ludlum model 19 microR survey instrument. Source was stored overnight in locked trailer at rail yard. Source was taken for disposal by a disposal contractor on 8/16/05. Bureau has been unable to date to trace source back to original owner or determine how the source came to be on the rail car." This event involves material that is less than IAEA Category 3 sources. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. Ohio Report Number OH2005-092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-08-23
41929 | 0 | SCHLUMBERGER INC. |  |  |  |  | 2005-08-17 12:00 | 2005-08-18 14:25 | 2005-09-19 | MATERIAL EVENT - LOST TRITIUM SOURCE A shipment of a pulse neutron generator containing a 1.5 curie tritium source was determined to be lost by the shipper (Federal Express) and reported to the licensee on 8/17/05. The neutron generator originated in New Jersey and was shipped to Texas where it was used under a well logging source license. Upon completion of use, the generator was to be returned to New Jersey from Texas. The shipment in question originated in Webster, Texas, and was destined for the licensee's Princeton Technology Center in Princeton Junction, New Jersey. The shipping date was 7/12/05. The licensee stated that the neutron generator failed to arrive as scheduled and that on or about 7/15/05 the shipper initiated an internal incident report to investigate the shipment. The neutron generator was tracked to the shipper's Trenton, New Jersey site. The licensee also reported that the shipper reported finding packaging related to the neutron generator shipment but that the contents were missing. The tritium source in the neutron generator is less than the quantity of an IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are IAEA Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * * UPDATE FROM T. BRACKE TO M. RIPLEY 1640 EDT 09/19/05 * * * * The licensee stated that the device and source have not yet been found. The shipper has, however, exhausted their search of their facilities in Webster, TX, Houston, TX, Trenton, NJ and Woodbridge, NJ. Notified R1 DO (J. White) and NMSS EO (M. Burgess) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-08-18
41928 | 0 | LANCASTER GENERAL HOSPITAL |  |  |  |  | 2005-08-18 10:00 | 2005-08-18 14:08 | 2005-08-18 | MEDICAL EVENT The licensee reports that a patient was scheduled to receive five Gamma Knife treatments to a single tumor in the head. Two treatments were successfully administered. Prior to the third treatment, it was determined that the shield "jaws' on the Gamma Knife were stuck closed and the Knife was considered inoperable. Consequently, the patient did not receive the final three prescribed treatments. The licensee has requested repairs on the Gamma Knife from an authorized service representative. The licensee believes that a microphone clip, used to communicate with the patient while under treatment, may have fallen into the Gamma Knife and jammed the "jaws." The licensee plans to continue treatment of the patient pending repair to the Gamma Knife. The licensee also planned to notify the State of Pennsylvania. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-08-18
41927 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2005-08-18 09:49 | 2005-08-18 11:10 | 2005-08-18 | AUTOMATIC SCRAM DUE TO LOSS OF A POWER BOARD "Unit 1 scrammed from 100% power due to a loss of power board 11 coincident with 1/2 scram present already on RPS channel 12 due to [instrumentation and control] (I&C) testing. A loss of power board 11 causes a loss of 11 RPS trip bus which in turn produces a 1/2 scram. Loss of power board 11 is currently under investigation. In addition during the scram, HPCI injected into the reactor vessel on a turbine trip signal to maintain reactor water level. "Currently, the reactor is in hot shutdown with reactor water levels being maintained in the normal level band at 74 inches with feedwater in automatic. Reactor pressure is currently 920 psig and being maintained in automatic with turbine bypass valves. "Plan is to stay in hot shutdown and complete scram recovery procedures." All control rods fully inserted. No safety relief valves actuated. Electrical busses were being supplied by normal offsite power. Emergency diesel generators are available. The decay heat removal path is currently normal feedwater to the reactor vessel through the turbine bypass valves to the condenser. There was no impact on Unit 2. The licensee is going to suspend any high risk maintenance activities on Unit 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-08-18
41926 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-08-17 16:15 | 2005-08-17 19:35 | 2005-08-17 | OFFSITE EMERGENCY SIRENSOUT OF SERVICE DUE TO SEVERE WEATHER "On August 17, 2005 at 1615 [EST], Brunswick lost eight off site emergency preparedness sirens for greater than an hour due to severe weather and lightning strikes. The Brunswick County Emergency Operations Center is aware of the loss and has established Backup Route Alerting. Other communications with local, state, and federal response organizations have not been affected. "Safety Significance is minimal. Backup Route Alerting was established as a compensatory measure and the sirens were promptly returned to service. The down time was only 1 hour and 44 minutes. "All affected sirens were restored operable at 1759 [EST] 8/17/05." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-17
41925 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2005-08-04 11:30 | 2005-08-17 18:57 | 2005-08-17 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via facsimile: "This event involved an HDR brachytherapy unit [Nucletron Corporation Model 105.999, serial number 31062; with sealed source Nucletron Corporation Model 105.002, serial number D36A-7277]. The maximum activity that can be utilized in the unit is 444 gigabecquerels (12 Curies) of Ir-192. The male patient was receiving palliative treatment for metastatic disease. On August 4, 2005, the patient received the second of the three prescribed treatments to the left bronchus. The licensee's Medical Physicist discovered the error on August 10, 2005. The error was a contiguous shift lengthwise of 3 centimeters from the area that was being treated. The intended fraction was 7 Gray. The patient and the referring physician were notified on August 11, 2005. The licensee is still in the process of evaluating the event. The licensee is to submit a written report to the Utah Division of Radiation Control. The treating physician determined that there will be no adverse affect to the patient as a result of this event and that diseased tissue may have been treated. The Division of Radiation Control is still investigating this event." Event Report ID Number: UT-05-0006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2005-08-22
41924 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2005-08-17 10:00 | 2005-08-17 17:14 | 2005-08-17 | FITNESS FOR DUTY A non-licensed Entergy headquarters acting supervisor (badged at Indian Point) had a confirmed positive for alcohol during a follow-up fitness-for-duty test. The employee's access authorization has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2005-08-17
41923 | 0 | WESTINGHOUSE HEMATITE |  |  |  | URANIUM FUEL FABRICATION | 2005-01-07 15:00 | 2005-08-17 16:02 | 2005-08-17 | BULLETIN 91-01 REPORT ON FAILURE TO FOLLOW CRITICALITY CONTROLS Licensee performed plant walk downs in the site process buildings in January 2005 and determined that verbatim compliance with the nuclear criticality safety controls for safety arrays were not maintained. Items placed in storage after survey for contamination were subsequently found to exceed fissile exempt limits. Specifically, the Uranium-235 (U-235) mass was not determined prior to placement in storage. The failure to determine the U-235 mass prior to placement in storage constituted a violation of an administrative control in the approved safety evaluation. All corrective actions related to this condition have been completed. Mass analysis of the storage items in question revealed that all items were well below U-235 mass limits. The licensee states that this event has minimal safety significance. NRC Region 3 has been notified. The licensee also plan to inform the State of Missouri. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | MO | FUE | [5 empty] | 0 | 2005-08-17
41922 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-08-16 14:30 | 2005-08-17 12:47 | 2005-08-17 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "A notification was made by the RSO on August 16, 2005, concerning a portable moisture density gauge that was run over at the Menasha coal plant, a temporary job site. The approximate time of the incident was 2:30 pm. The gauge was a Troxler 3440 containing 10 milliCuries of Cs-137 and 50 milliCuries of Am-241. The RSO reported that the radiation readings were verified as normal by comparing the reading at 1 meter to the Transportation Index. Visual observation confirmed that the source rod is in the normal position and the shielding is intact. Other individuals on the job site including the truck driver that ran over the gauge were surveyed. The area where the gauge was damaged was surveyed after the gauge was moved a few feet away and no radiation readings above background were noted. The gauge was transported back to the licensee's facility in Neenah [WI]. DHFS staff were dispatched to confirm that there was no contamination on August 17, 2005. The licensee has taken a wipe smear and is sending it to Troxler for counting. The gauge is locked in the transport case and has been placed in storage." WI report number: 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-08-22
41921 | 0 | GEO-EXPLOR INC |  |  |  |  | 2005-08-16 | 2005-08-16 16:18 | 2005-08-22 | LOST/MISSING MOISTURE DENSITY GAUGE The employee placed the CPN Moisture Density Gauge (s/n: 18098458 Am/Be, Cs-137) into its case and placed the case in the back of the pickup truck. Before the employee chained the case to the truck he was required to move away from the back of the truck. He later drove away without chaining the case to the truck or closing the back gate. About 0.3 miles down the road he noticed that the gate was open and the gauge was missing. He returned to the work site but did not see the gauge along the way and could not find the gauge at the work site. The incident was reported to the local police. The company is notifying the local news media and is offering a reward. Less than the quantity of a Category 3 source. Sources that are "Less than Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE FROM RODRIGUEZ TO HUFFMAN AT 1510 EDT ON 8/22/05 * * * The licensee states that an individual retrieved the gauge from the road after it had fallen off the truck. The gauge was stored in an office building where the individual worked. The individual that recovered the gauge could not find any identifying information on the gauge container as to the owner or a contact telephone number. However, the individual did hear about the lost gauge through media coverage and was, therefore, able to track down and contact the licensee. At 12:30 EDT on 8/22/05, the licensee has recovered the gauge from the individual that found it and observed that it was in its properly stored and safe configuration. It has been examined in detail and is not damaged in any way. The licensee stated that he also planned to notify the responsible NRC Region 1 inspector (Beardsley) about the recovery of the gauge. R1DO (Cook), NMSS EO (Morell), and TAS (Perez via email) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-08-16
41920 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-08-09 12:00 | 2005-08-16 16:30 | 2005-08-16 | FLORIDA AGREEMENT STATE REPORT "Licensee reports that a doctor wrote the prescription for I-131 thyroid scan when he meant it to be a I-123 scan. Event occurred on 8/09/05 and was discovered on 8/11/05. This office was notified 8/15/05. The doctor and patient have been notified. No adverse medical consequences for the patient are expected. Any further action is referred to Radioactive Materials. " Total Activity of the Iodine-131 was 6.05 millicuries. Florida Incident Number FL05-113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-08-19
41919 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-08-16 07:00 | 2005-08-16 15:00 | 2005-08-22 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE An employee parked the truck containing the Troxler Moisture Density Gauge (Model 3411B, s/n 7573, Am/Be 40 milli Curies, Cs-137 8 milli Curies) overnight at his apartment complex. The gauge was secured by a lock and chain. The truck was parked at 2200 CDT on 08/15/05. When the employee returned to the truck at 0700 on 08/16/05 the chain was cut and the gauge was gone. The theft was reported to the police. TX report number: TX-I-8252. Less than the quantity of an IAEA Category 3 source. Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. For some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. * * * UPDATE FROM CHRIS MOORE TO J. KNOKE AT 16:46 EDT ON 08/18/05 * * * An individual called the owner of the lost Troxler gauge, indicating it was discarded on her property. The gauge was initially picked up by the local fire department, and then by the owner. The gauge was surveyed and had readings of less than 1 mr/hr. The gauge was found to have no damage, however, all the associated paperwork was missing. Notified the R4DO (Sanborn), NMSS (Holonich) and TAS (Perez) of the update. Faxed Mexico the update. Note: Event modified on 8/22/05 to correct the name of the individual from the State of Texas that provided the update to this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-08-19
41918 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-08-14 19:10 | 2005-08-14 20:42 | 2005-08-14 | FIRE ALARM IN TRAINING BUILDING DUE TO LOSS OF POWER "This is a Voluntary Report based on a State Notification that does not meet the criteria of 10CFR50.72(b)(2)(xi). "At approximately 19:10 hours, the Susquehanna Control Room was notified that offsite fire departments had responded to the Susquehanna Learning Center. This was due to a fire alarm received by the corporate office from the building due to a loss of power to the facility. Offsite fire department personnel along with our Training department inspected the building and found no indications of fire. "The Susquehanna Learning Center is located outside of the protected area and approximately one eighth mile from the main access road on State Route 11. "Pennsylvania Emergency Management Agency was advised." The loss of power to the training building was the result from lightning in the area. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2005-08-14
41917 | 0 | BAYHEALTH MEDICAL CENTER |  |  |  |  | 2005-08-13 09:31 | 2005-08-13 16:22 | 2005-08-13 | LOST/STOLEN CS-137 SOURCE The Cs-137 source (116.4 microCuries) is kept in a lead container, in an unlocked lead-lined drawer, in a key coded cipher locked room. At 06:48 on 08/12/05, the daily quality control dose calibration was performed. At 09:31 on 8/13/05, the source and its lead container were discovered missing. Security personnel have reviewed video surveillance tapes for nearby corridors but the hall outside the source's room is not surveilled. The video tapes indicate that the only personnel within the area were Security personnel. Staff and technicians with access to the room were interviewed and none had knowledge of the incident. Cardinal Health was contacted and verified that the source had not accidentally been returned to Cardinal Health. The door to the source's room is labeled and locked. The RSO has been notified and the Dover Police will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-08-13
41916 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2005-08-12 15:50 | 2005-08-12 17:22 | 2005-08-12 | OFFSITE NOTIFICATION MADE DUE TO EMERGENCY SIREN ACTUATION "On 8/12/05 at 1550, Fort Calhoun Station was notified by an off-duty employee that an emergency siren was sounding in Washington County, Nebraska. No actual emergency exists and no testing is currently in progress. The siren's location is approximately 1/2 mile East of the P32/P35 county road intersections on county road P32. "The local sheriff, radio station (KFAB), and NRC senior resident have been notified. "The cause of the inadvertent siren activation is unknown at this time. "This event is considered to be reportable per 10CFR50.72(b)(2)(xi)." This siren is within 10 miles from the plant. The local sheriff will provide compensatory notifications if required. The licensee notified the NRC Resident Inspector. * * * RETRACTING EVENT BY LICENSEE (MARASCO) TO ABRAMOVITZ AT 2135 ON 8/12/2005 * * * The licensee determined that their corporate communications department had been performing a test of the emergency sirens but had not notified the site. Notified the R4DO (Bywater) and e-mailed R4 (Graves and Dricks). The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-08-12
41915 | 0 | THOMAS JEFFERSON UNIVERSITY HOSP |  |  |  |  | 2005-08-12 13:30 | 2005-08-12 15:34 | 2005-08-16 | PATIENT OVEREXPOSURE - I-131 CONTAMINATION FOUND UNDER THUMBNAIL On 8/11/05 a patient was being treated with an I-131 (liquid) source for a hyperthyroid problem (148 milliCuries). Per procedure, the patient returned 24-hours later for a whole body count. A small (estimated 5 microCurie) I-131 fixed contamination site was found under the patient's right thumbnail. Initial estimates for the localized dose are 800 Rad. There was no other contamination nor did surveys show any contamination on individuals or equipment. The patient and doctor were notified. Decontamination is continuing. The hospital is continuing to investigate the cause of the contamination. * * * UPDATE ON 08/15/05 @ 1114 BY LARRY MARTINO TO CHAUNCEY GOULD * * * The initial report was incorrect and the correct version is as follows: THE NUCLEAR MEDICAL TECHNICIAN HAD AN OVEREXPOSURE - I-131 CONTAMINATION FOUND UNDER THUMBNAIL On 8/11/05 a patient was being treated with an I-131 (liquid) source for a hyperthyroid problem . Per procedure, the patient returned 24-hours later for a whole body count. After completing this treatment, a small (estimated 5 microCurie) I-131 fixed contamination site was found under the nuclear medicine technician's right thumbnail. Initial estimates for the localized dose are 800 Rad. There was no other contamination nor did surveys show any contamination on individuals or equipment. The technician and treating physician were notified. Decontamination is continuing. This report was made under 10CFR20.2202(a)(1)(iii) a shallow-dose equivalent to the skin or extremities of 250 rads or more. The hospital is continuing to investigate the cause of the contamination. Notified Reg 1 RDO (Ray Lorson), RI (George Pangburn) and NMSS EO(Michele Burgess) *****Update on 08/16/05 at 1455EDT by John Keklak to MacKinnon **** "License number 37-00148-06 "On 08/12/05, a Nuclear Medicine Technologist underwent a thyroid count (as per procedure) the day after administering a therapy dosage of I-131 sodium iodide (liquid) to a patient. The thyroid count results prompted a skin contamination survey that located I-131 skin contamination under the edge of the Technologist's right thumbnail. Following decontamination, some I-131 remained fixed. Initial conservative dose estimates indicated localized skin dose in the range of 800 Rad, current (8/16/05) best estimates indicate dose of about 130 Rad. No other contamination was found on this technologist, other personnel, equipment, or room surfaces. Most likely cause was a loss of integrity of the protective glove the technologist was wearing while handling the sodium iodide. "The hospital is continuing to investigate the event" R1DO (R. Lorson), R1 (Penny Lanzisera) and NMSS EO (M. Burgess) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2202(a)(1) |  |  |  | 0 | 2005-08-12
41914 | 0 | DAIMLER - CHRYSLER |  |  |  |  | 2005-08-10 12:00 | 2005-08-10 18:18 | 2005-08-12 | GENERAL LICENSED SOURCE DAMAGED WHEN LEAD SHIELDING MELTED ON A NUCLEAR GAUGE The RSO from a Daimler - Chrysler foundry reported that excessive heat inside the foundry had caused the lead shielding to partially melt. The device was a GN Technologies (now Thermo Electron Corp) model 5201 with source serial # GV8072 gauge serial # B3021. The gauge, which was on a foundry cuppola out of the area of any foot traffic, contained 100 millicuries of Cs-137. The radiation level on the top of the gauge measured 250 mr/hr at 1 ft from the source. The area near the gauge was roped off to isolate it from the public. They will shut the gauge off and the manufacturer's rep will remove it. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN |  |  |  |  | 0 | 2005-08-12
41913 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2005-08-12 00:19 | 2005-08-12 03:26 | 2005-08-12 | PLANT ENTERED LCO ACTION STATEMENT 3.8.1 TO BE IN MODE 5 DUE TO UNIT 1 "B" DIESEL GEN. BEING DECLARED INOPERABLE "On August 12, 2005, at approximately 00:19 hours Mountain Standard Time (MST), Palo Verde Nuclear Generating Station (PVNGS) Unit 1 commenced a reactor shutdown required by Technical Specification 3.8.1. "Limiting Condition for Operability (LCO) 3.8.1 requires two diesel generators (DGs) each capable of supplying one train of the onsite Class 1E AC Electrical Power Distribution System be available. On August 9, 2005, at approximately 04:20 MST, Unit 1 Diesel Generator 'B' failed to maintain the proper steady state output voltage (4080-4300 VAC) during monthly operability surveillance testing per '40ST-9DG02'. Diesel Generator 'B' was declared inoperable and the Unit entered LCO 3.8.1 action 'B'. An engineering action plan was initiated in an attempt to identify the cause of the generator output voltage fluctuation and correct the problem. To date, troubleshooting efforts have unable to isolate the problem. On August 12 at 0420 MST the 72 hour Completion Time associated with LCO 3.8.1 Action 'B' will expire and at 00:19 MST Unit 1 commenced a reactor shutdown in compliance with LCO 3.8.1 Action 'H'. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. The required offsite power sources are operable and the electrical grid is stable." The NRC Resident Inspector will be notified. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-08-12
41912 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-08-11 08:45 | 2005-08-11 15:56 | 2005-08-11 | ONE EMERGENCY PREPAREDNESS SIREN OUT OF SERVICE "On August 11, 2005 at approximately 08:45 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department identified an inoperable single siren (#15). While reviewing the siren monitoring computer log, an Information Services Technician received a 'no response' signal on siren #15. Upon investigation, siren #15 was found inoperable. The siren was vandalized by destroying the siren controller case and stealing the internal battery. The affected siren is estimated to impact approximately 496 members of population in the emergency planning zone (EPZ) beyond 5 miles but within 10 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 10% of the population beyond 5 miles but within 10 miles. This call is being placed due to the relatively large segment of the population affected and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "The County was informed at 09:05 MST to implement the MCSO notification if a need arises. "There are no events in progress that require siren operation." The licensee notified the NRC Resident Inspector. | 95 | 100 | 99 | 95 | 100 | 99 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2005-08-11
41911 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2005-08-11 10:48 | 2005-08-11 14:33 | 2005-08-11 | MANUAL REACTOR TRIP ON A CONDENSATE PUMP BUS LOCKOUT "On 8/11/2005, a manual reactor trip was initiated due to lowering steam generator level caused by a partial loss of main Feedwater. The partial loss of feedwater was caused by the differential lock out of the non-vital 2A2 4160 V bus which resulted in loss of the 2A Condensate Pump that tripped the 2A Main Feedwater Pump. All rods inserted and no Steam Generator Safety Valves lifted. The differential lock out of the non-vital 2A2 4160 V [bus] deenergized the 2A3 vital 4160V bus, starting the 2A Emergency Diesel Generator and the 2A3 loads were sequenced on the Emergency Diesel Generator per design. Subsequently, the Auxiliary Feedwater System was automatically initiated due to lowering steam generator levels. All safe shutdown equipment operated as expected. The plant is stable in Mode 3, Hot Standby conditions, with decay heat removal being accomplished by steaming to the Main Condenser and Feedwater to the steam generators supplied by the Main Feedwater system. The Offsite power grid is available and stable. The '2C' Auxiliary Feedwater Pump was out of service for routine surveillance and it had no effect on the cause of the trip nor had any effect on the trip recovery. St. Lucie is investigating the cause of the lockout on the 2A2 4160V bus. Unit 1 was not affected by this event." At the time of this report, the 2A Emergency Diesel Generator was still loaded while investigations were underway. Steam generator level is being maintained using main feed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-08-11
41910 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-08-10 17:45 | 2005-08-10 22:05 | 2005-08-10 | SECURITY OFFICER SHOOTS SELF IN FOOT DURING TRAINING "A PINSG Security Officer was shot in the foot in the owner controlled firing range at Monticello Nuclear Plant. This occurred outside the protected area. The Security Officer's injury was accidental and self inflicted." See HOO for additional information. See also EN #41909. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-08-10
41909 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-08-10 17:40 | 2005-08-10 21:09 | 2005-08-10 | SECURITY OFFICER SHOOTS SELF IN FOOT DURING TRAINING "[A Prairie Island Nuclear Generating Station] Security Officer was shot in the foot on the owner controlled firing range. This occurred outside the protected area. The security officer's injury was accidental and self inflicted." See HOO for additional information. See also EN #41910. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-08-10
41908 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-08-01 09:45 | 2005-08-10 15:53 | 2005-08-18 | OHIO AGREEMENT STATE REPORT - STOLEN AND RECOVERED NUCLEAR GAUGE The State provided the following information via email: "At approximately 9:45 AM on Monday, 8/1/05, a Humbolt Model 5001, S/N 4634 portable gauge [10 milliCuries Cs-137 and 40 milliCuries Am-241] was stolen from a company vehicle while parked at a fast food restaurant in Dayton, Ohio. The gauge was discovered missing when the employee returned to the vehicle. The gauge was discovered in a roadside ditch about one mile from the restaurant approximately 45 minutes later by a line crew from a local power company. The gauge was intact with no apparent damage. The licensee's RSO responded to the scene and took area measurements which indicated that the integrity of the source had not been compromised. The gauge was taken back to the licensee's offices, where it was leak tested. A police report was filed. The Ohio Department of Health is inspecting the licensee to determine if proper security measures had been followed prior to the theft." Ohio Report No. OH050003 * * * UPDATE FROM THE STATE OF OHIO TO NRC (HUFFMAN) AT 12:19 EDT ON 8/18/05 * * * The State provided the following information via email: "Inspection by Bureau determined that licensee's employee failed to follow procedures for securing device in vehicle. Gauge was only secured in vehicle by bungee cords, with no locking mechanism or fixed restraint system. In addition, vehicle was left unattended and unobserved while employee was in fast food restaurant for prolonged period." R3DO (Riemer) and NMSS (Hickey) notified. TAS informed via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-08-15
41907 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2005-08-10 08:15 | 2005-08-10 12:34 | 2005-08-10 | SPURIOUS ACTIVATION OF OFF-SITE EMERGENCY PLAN SIRENS "While performing silent activation tests on two new electronic sirens associated with the Alert and Notification System this morning, a siren cancel signal was sent out to stop the siren test on the two sirens. Mechanical sirens 2Z4 and 2Z8 [not the new electronic sirens] located in the areas around Oakland Heights Elementary School in Russellville and the HWY 7T curve read the signal as an activation and subsequently activated. Pope County 911 called the Arkansas Department of Health (ADH) to advise that they had received calls concerning the activation. The normal siren verifiers for those sirens called ADH to report the sounding. ADH contacted ANO regarding the siren activation and issued a press release to four local radio stations." The signals sounded for 5 - 10 minutes. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-08-10
41905 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2005-07-18 | 2005-08-09 15:57 | 2005-08-09 | AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via facsimile: "Treatment delivered to two (2) of seven (7) lesions on a patient on 18 July 2005, were discovered to be 50 percent less dose than that prescribed. (15 Gy (Grey) per lesion prescribed; two lesions received only 7.5 Gy each) This was discovered [on 3 August 2005], during an internal audit of treatments, conducted by medical physicist not originally involved with treatment. To date the investigation does not identify a problem with the equipment or the dose programs involved in planning. Initial indicators point to a potential communication problem between the original medical physicist and oncologist. At this time the investigation is pending due to the unavailability of the medical physicist due to vacation. Resumption of the investigation is to commence on or about 9 August 2005 when persons involved have returned from vacation." RI Event Report ID: RI-05-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2005-08-12
41903 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-08-02 | 2005-08-08 15:22 | 2005-08-08 | AGREEMENT STATE REPORT - STUCK WELL LOGGING SOURCE The State provided the following information via facsimile: "On August 2, 2005, Precision Energy Services had a 2 Curie source of Cs-137 and a 20 Curie source of Am/Be 241 get stuck down hole at a depth of 11,300 feet. The well depth is 12,000 feet. Precision Energy Services is trying to retrieve the well logging tool that has the two radioactive sources in it." The well is offshore in Louisiana waters. State lease #18076, Well #1. LA Event Report ID: LA050007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-08-11
41901 | 0 | LEE SUMMIT MISSOURI FIRE DEPT |  |  |  |  | 2005-08-08 06:00 | 2005-08-08 09:45 | 2005-08-08 | TRUCK ACCIDENT INVOLVING DAMAGE TO TECHNETIUM-99 SHIPMENT A call was received from a Captain in the Lee Summit, Missouri, Fire Department stating a truck carrying Technetium-99 had been involved in a single car accident. He stated that the approximately 7 to 9 lead pigs were ejected from the truck and that some of the pigs opened releasing "syringes." He stated that no fluids had leaked out of any of the syringes. He noted that the shipper, Cardinal Health, had responded to the scene and surveyed the material and found no contamination. However, he had no contact information on Cardinal Health or a contact number. He also had notified the State of Missouri Radiological Health Division. The NRC Operations Center was able to contact a responsible party at Cardinal Health that confirmed the general details of the accident. The Cardinal Health representative stated that surveys on site were still in progress but no contamination had been found. The material has been secured and loaded onto another truck for removal from the accident scene. The Cardinal Health representative stated that there would likely be a follow-up report to this event from Corporate Offices in Ohio when investigation into the incident were completed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2005-08-08
41900 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2005-08-07 | 2005-08-07 20:06 | 2005-08-07 | SPDS UNAVAILABLE FOR GREATER THAN ONE HOUR "Unit SPDS was unavailable for greater than 60 minutes due to a plant computer system failure. SPDS was unavailable from 1507 on 08/07/05 until 1900 on 08/07/05." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-08-07
41899 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2005-08-06 04:03 | 2005-08-06 04:42 | 2005-08-06 | ALERT DECLARED DUE TO LOW INTAKE WATER LEVEL The licensee declared an Alert (EAL HA3) at 0403 ET 08/06/05 due to low water level in the north half of the intake structure as a result of heavy grass accumulation due to a storm in the area. Intake level recovered to above the EAL value for an Alert, and the event was de-escalated to an Unusual Event (EAL HU3) at 0406 ET. One Circulating Water Pump associated with the north intake was immediately secured and reactor power was reduced to 43%. When the second Circulating Water Pump associated with the north intake was secured, intake water level returned to normal. As a result of the grassing, trash racks collapsed and traveling screen shear pins sheared at the north intake. The traveling screens were subsequently restored to service. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM E. DEMONCH TO M. RIPLEY AT 0800 ET 08/06/05 * * * The licensee terminated the Unusual Event at 0755 ET 08/06/05. The licensee notified the NRC Resident Inspector. Notified R1 DO (H. Gray), NRR (J. Dyer, C. Haney), NSIR IRD (T. McGinty), R1 (Dapas, Holian, Bellamy, Bores), HHS (J. Tribble), USDA (J. Jones), DHS (M. Inzer), FEMA (Liggett), EPA/NRC (P. Layman), DOE (M. Wyatt). | 43 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-08-06
41898 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-08-05 22:28 | 2005-08-06 00:20 | 2005-08-06 | AUTOMATIC REACTOR TRIP APPARENTLY DUE TO LIGHTNING STRIKE The Unit 2 reactor automatically tripped due to an overpower-delta temperature (OpDeltaT) trip signal. The licensee states that an actual OpDeltaT condition did not exist at the time of the trip. The trip signal is believed to have been generated by lightning strikes from an electrical storm that was passing through the area at the time. The trip was uncomplicated and all systems functioned as required. All control rods fully inserted; no safety relief valves lifted; decay heat is being discharged to the main condenser using normal feedwater to supply the steam generators; the reactor temperature and pressure are at normal hot standby range. No obvious grid disturbance was seen during the trip and Unit 1 was not impacted (Unit 1 was being ramped offline at the time for secondary side maintenance work). The licensee noted that Auxiliary Feedwater did auto-start as expected due to a trip from full power and was subsequently secured. The licensee is still investigating the cause of the OpDeltaT trip signal but noted that other Unit 2 instrumentation was found failed after the transient including the Unit 2, A-loop, wide range T-hot and T-cold indications and the Unit 2, B-loop, T-cold indication. The licensee plans to remain in Mode 3 until the investigation is complete and instrument repairs completed. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-08-06
41897 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-08-05 17:54 | 2005-08-05 22:46 | 2005-08-19 | LOSS OF BOTH CONTROL ROOM EMERGENCY VENTILATION SYSTEMS DURING TESTING During maintenance testing of the 'B' Control Room Emergency Ventilation system (CRV) the 'A' Air conditioning unit was running. The 'A' A/C unit (V-EAC-14A) tripped on a low service water flow condition while performing step 0255-11-III-4 which manipulated service water valves for the test. The 'B' loop of the CRV system was in a 30 day LCO due to the maintenance testing. When the 'A' A/C unit tripped and the 'B' unit inoperable due to testing, both CRV trains were inoperable and that placed the unit in a 24 hour Tech Spec LCO, 3.17.A.3.a. The compressor unit V-EAC-14A was reset following restart of the 13 Emergency Service Water pump 8 minutes after the trip and exited the 24 hour LCO. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM R. SCHREIFELS TO J. KNOKE AT 12:35 EDT ON 8/19/05 * * * "The notification was initiated due to both trains of the Control Room Ventilation system being inoperable and was reported under 50.72 (b)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. "Monticello is retracting the event notification based on further investigation of the event. Successful completion of subsequent testing indicated that the 'B' train was still capable of performing its required safety function when the 'A' train tripped. Therefore Monticello has determined there was no loss of safety function as reported in Event Notification #41897. Additional investigation is ongoing and any identified issues will be entered into the station's corrective action program." The licensee notified the NRC Resident Inspector. Notified R3DO(S. Burgess). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-08-05
41896 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-08-05 17:08 | 2005-08-05 21:50 | 2005-08-06 | RPS ACTUATION DUE TO LOW REACTOR WATER LEVEL CAUSED BY LOSS OF REACTOR FEED PUMPS "At 1708 on 08/05/2005, Unit 2 reactor scrammed from 100% power when reactor water level reached Level 3 Reactor Scram setpoint due to loss of 2C and 2B Reactor Feed Pumps. All rods inserted [fully]. Unit 3 was also at 100% power and was unaffected by this event. Reactor water level reached level 2 (-45) HPCI & RCIC initiation setpoint and was recovered by HPCI and RCIC injection. All expected PCIS isolations, Group 2 (RHR S/D cooling), Group 3 (RWCU), Group 6 (ventilation), and Group 8 (TIP) were received along with the auto start of CREV, 3 SGT trains, HPCI and RCIC with injection into Reactor Vessel. Recirc Pumps tripped at -45" as expected. Four MSRVs lifted momentarily to stabilize reactor pressure. "This event is reportable at 4 hour and 8 hour Non-Emergency Notification along with a 60 day written report in accordance with 10CFR50.72(b)(2)(iv)(A), 10CFR50.72(b)(2)(iv)(B), 10CFR50.72(b)(3)(iv)(A) and 10CFR50.73(a)(2)(iv)(A) as 'Any event or condition that results in a valid actuation of RPS and PCIS as described in (l) and (2) below.'" Decay heat is being removed via steam to the main condenser using the bypass valves maintaining pressure at 895 psi. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY HUNTER TO JEFF ROTTON AT 1524 ON 08/06/05 * * * "Upon further evaluation by the trip investigation team, it has been determined that no MSRV's lifted during this event. Reactor pressure data indicated no increasing pressure spike during the transient. The post-scram pressure trends indicated the maximum reactor pressure was normal operating pressure at the start of the transient followed by a gradual decline. The initial report which stated that 4 MSRV's had lifted was in error." The licensee will notify the NRC Resident Inspector. Notified the R2DO (Landis). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-08-05
41895 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-08-05 18:40 | 2005-08-05 21:24 | 2005-08-06 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABILITY OF ALL EMERGENCY DIESEL GENERATORS "Event reportability is in accordance with 10 CFR 50.72(b)(3)(v)(D), 'Accident Mitigation,' and 10 CFR 50.72(b)(2)(i), 'TS Required Shutdown,' due to potential COMMON CAUSE FAILURE of all four Emergency Diesel Generators. On 05 August 2005, at 14:31 hrs, DG2 was started for data gathering purposes, and it experienced a trip and lockout on differential current. Investigation revealed that set points for the installed DG differential current protective devices may be set too conservatively. Since each DG has the same relay with the same set point, all DGs were declared inoperable. Preparations are in progress to place both units in Cold Shutdown. "The site has insufficient operable backup AC sources. The current effect on the plant is minimal due to all normal AC sources being available and operable. However, due to the potential for losing a normal AC source resulting in insufficient power being available to some emergency systems, both units will be placed in cold shutdown until all emergency diesel generators can be restored to operable. "Corrective actions are in progress to correct differential current protective device problem in order to restore availability of DG2 and operability of all four DGs." The licensee plans on commencing a down power on both units (Unit 2 first) within several hours. Technical Specifications require both units to be in Hot Shutdown within 12 hours (approximately 0700 on 08/06/05) and Cold Shutdown within 36 hours. Neither unit has any other significant systems LCOs. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (BAIN) TO NRC (HUFFMAN) AT 10:38 EDT ON 8/06/05 * * * "This is a follow up message to the initial event reported in accordance with 10 CFR 50.72(b)(3)(v)(D), 'Accident Mitigation' and 10 CFR 50.72(b)(2)(i), 'TS Required Shutdown' due to the potential COMMON CAUSE FAILURE of all four Emergency Diesel Generators. Unit 2 entered Mode 3 (Hot Shutdown) at 04:46. Unit 1 entered Mode 3 (Hot Shutdown) at 05:31. Both units are continuing to cool down in preparation for entering Mode 4 (Cold Shutdown)." The licensee notified the NRC Resident Inspector. Notified R2DO(Landis), NRR EO (Haney), and IRD (McGinty). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2005-08-05
41894 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2005-08-05 01:00 | 2005-08-05 15:10 | 2005-08-05 | AGREEMENT STATE - STOLEN TROXLER MOISTURE DENSITY GAUGE At 0945 MDT on 08/05/05, the licensee reported that a Troxler Moisture Density Gauge had been stolen between 2300 MDT on 08/04/05 and 0100 MDT on 08/05/05. The gauge was locked in its transfer case and chained in the back of the truck. The truck was parked in the 1st row of the casino parking lot at the New Mexico State Fairgrounds. Casino police contacted the New Mexico State Police. The Troxler was a model 3430, Serial number 29090 and contained 50 millicuries Am-241/BE and 10 millicuries Cs-137. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2005-08-10
41893 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2005-08-05 | 2005-08-05 14:31 | 2005-08-07 | MISSING TROXLER GAUGE Kansas Department of Transportation workers transited from one worksite to another with a Troxler Moisture Density Gauge in their vehicle. When they arrived at their destination, they discovered that their Model 3440 Troxler Moisture Density Gauge (44 milliCuries Am/Be; 8 milliCuries Cs-137) was missing. Someone noticed a gauge on Fort Riley Blvd in Manhattan, KS, and notified the police and fire department. The DOT personnel had used Fort Riley Blvd to get to the second job site. When emergency personnel arrived at the scene, the gauge was gone. The KS DOT notified local law enforcement. The gauge was in its transportation container and the source was locked. KS Report Number: KS-050016 * * * UPDATE FROM D. WHITFILL TO W GOTT AT 1257 ON 08/08/05 * * * The Troxler Moisture Density Gauge was found late (2200 - 2300) on 08/05/05 near the location it was reported lost. Kansas Department of Transportation has custody of the gauge and it is not damaged. Notified R4DO (D. Powers) and NMSS (S. Moore) and emailed to TAS (R. Warren). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2005-08-10
41892 | 0 | AMERICAN RADIO-LABELED CHEMICALS |  |  |  |  | 2005-07-29 | 2005-08-04 13:36 | 2005-08-10 | MISSING NUCLEAR MATERIAL American Radio-Labeled Chemicals Inc. was expecting a shipment of 1 Curie Sulfur-35 on 07/22/05. It was being shipped from South Africa. The shipping company, DHL, picked up the shipment on 07/21/05 in Chicago, IL. On 07/22/05, American Radio-Labeled Chemicals contacted DHL since the shipment had not been delivered. At that time, DHL could not locate the shipment. DHL found the shipment in a dangerous goods warehouse in Ohio on 07/29/05. However, on 08/04/05, DHL indicated that it again does not know the location of the shipment. DHL is investigating the incident. * * * UPDATE FROM LICENSEE TO ABRAMOVITZ AT 13:18 EDT ON 8/10/2005 * * * The package was delivered to the licensee today. The package was not damaged and surveys verified source integrity. Notified the R3DO (Lanksbury), NMSS (Hickey), and TAS (e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-08-04
41890 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-08-03 14:50 | 2005-08-03 16:44 | 2005-08-05 | MISSING TROXLER GAUGE After leaving the construction site at the intersection of Highway 74 and Unionville Indian Trail Road, the workers discovered that their Troxler Moisture Density gauge was missing. They returned to the construction site and the gauge was not there. The gauge was a Model 3450 Troxler (s/n 885) with 40 milliCuries Am/Be (s/n 78-515) and 8 milliCuries Cs-137 (s/n 77-261-0). The RSO is investigating. The Troxler was in the "Safe Position" but was not locked. NC Report number: 05-29. * * * UPDATE ON 8/5/05 @ 1056 BY ACCATTIATO TO GOULD * * * The missing Troxler gauge was found (08/05/05 @ 0900) on the highway by a member of the public in Rock Hill, SC just over the boarder between NC and SC. The case of the device was damaged, however, the source was not in the exposed position. It is currently in the possession of the licensee and State inspectors are at the site to inspect the gauge. Informed Reg 1 RDO (Harold Gray), NMSS EO (Trish Holahan), and TAS (Roberta Warren) by fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-08-08
41889 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-08-03 09:08 | 2005-08-03 12:51 | 2005-08-03 | POSITIVE RANDOM FITNESS FOR DUTY TEST On August 3, 2005, a non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The individuals unescorted access was suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2005-08-03
41888 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-08-02 18:00 | 2005-08-02 21:43 | 2005-08-02 | POTENTIAL PART 21 ISSUE WITH STRUTHERS-DUNN RELAYS "On 8/2/2005 Duke Energy Corporation was informed by the manufacturer of Struthers-Dunn relay, part number 219BBXP, of a manufacturing defect with the subject relay. Duke contacted the manufacturer as follow up to recent relay failures of this type. There has not been a Part 21 notification to date. The defect is in the relay coil. Some coils that were made in China over an approximate 18-month period did not have their coil core annealed. The annealing step in the manufacturing process was apparently skipped. The missed annealing step results in the relay coil potentially drawing almost twice its rated current. As a result, the coil can fail after an extended period of time in the energized state. Potentially affected relays of this type were purchased commercial grade and dedicated by Duke Energy Corporation for use in safety related applications. This relay type is utilized in valves in the Catawba Nuclear Service Water System. An investigation is in progress as to whether the relays in service at Catawba have the date code to indicate they have the manufacturing defect. Duke is also investigating if this relay type is in service at the other Duke nuclear units. This manufacturing defect may be reportable under 10 CFR 21 if other utilities purchased identical relays and dedicated them for use in safety related applications. "The following is a summary of information obtained from Struthers-Dunn concerning the affected relays: (1) Relays manufactured between January 2003 and June 2004 (date codes 0301B through 0424B on the cover). (2) Any 219 series relay with 120 AC and 240 AC coils. (3) 'Made in China' marked on the cover. (4) Also 'Made in USA' marked on the cover with a 'B' in the date code could be affected. " The Catawba NRC senior resident inspector has been notified." The relays used in the Catawba Nuclear Service Water System are normally energized. The licensee will be notifying the North Carolina and South Carolina Warning Points and York, Gaston and Mecklenburg County agencies. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW | [5 empty] | 0 | 2005-08-02
41886 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2005-08-02 08:40 | 2005-08-02 14:42 | 2005-09-29 | ECCS SYSTEMS INOPERABLE DUE TO EXCESSIVE REACTOR EQUIPMENT COOLING SYSTEM LEAKAGE "This notification is being made pursuant to 50.72(b)(3)(v)[D- Accident Mitigation] as a loss of safety function due to unplanned inoperability of HPCI and both Low Pressure ECCS systems caused by inoperability of both REC subsystems. "At 08:40 CDT, Cooper Nuclear Station [CNS] declared both REC (Reactor Equipment Cooling) subsystems inoperable due to excessive leakage from REC system. CNS was in the process of tagging out the north east quad fan coil unit (FCU) for planned maintenance to replace an REC drain valve on the FCU. After commencing draining the FCU, the building operator noted excessive leakage at the drain. A check of REC system out-leakage determined that allowable REC leakage limits had been exceeded. Both REC subsystems were subsequently declared inoperable. REC is a support system for HPCI, RCIC, and all Low Pressure ECCS systems; therefore HPCI, RCIC, and all Low Pressure ECCS systems were declared inoperable. "At 09:08, the REC drain valve was closed terminating the REC system leakage. REC, HPCI, RCIC, and all Low Pressure ECCS systems were subsequently declared operable." The licensee notified the NRC Resident Inspector. *** UPDATE FROM E. McCUTCHEN TO J. KNOKE AT 15:35 EDT ON 09/29/05 *** " This notification is being made to retract Event Notification 41886 that reported a loss of safety function due to the unplanned inoperability of HPCI and both Low Pressure ECCS systems caused by inoperability of both REC (Reactor Equipment Cooling) subsystems. Upon further evaluation, CNS determined that ECCS safety functions were not lost. The evaluation provided reasonable assurance that initiation of Service Water Backup system to ECCS area coolers would have maintained the ability of ECCS to perform their safety functions if the REC Surge Tank had reached its low level alarm." The licensee will notify the NRC Resident Inspector. The unit is operating at 100% / Mode 1. Notified R4DO (Spitzberg) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-08-02
41885 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-08-01 20:00 | 2005-08-02 01:25 | 2005-08-02 | POTENTIALLY INOPERABLE SAFETY INJECTION PUMPS "As part of an ongoing calculation review project, design data is being evaluated on safety related motors. On 07/15/2005 at 2245, design data was accepted for 1P-15A Safety Injection motor. This data determined that during a design basis accident with degraded safeguards bus voltage, the 1P-15A Safety Injection Pump could trip and lockout on over current prior to the safeguards bus stripping on under voltage. The Safety Injection Pump lockout would then prevent an auto start of the Safety Injection Pump during Emergency Diesel Generator load sequencing. 1P-15A Safety Injection Pump was declared out of service at that time. No other safety related motors were affected by this data. "The 1P-15A Safety Injection Pump time over current set point was adjusted, based on the revised motor data, returning 1P-15A to service on July 17 at 2230. 2P-15A Safety Injection Pump time over current set point was also conservatively reset. "On 08/01/2005 at 2000, additional design motor data was accepted, which impacted the time over current set point for 1P-15B and 2P-15B Safety lnjection motors. Review of this data determined that a similar potential exists that during a design basis accident with degraded safeguards bus voltage, 1P-15B or 2P-15B Safety Injection Pump could trip and lockout on over current prior to the respective safeguards bus stripping on under voltage. The Safety Injection Pump lockout would then prevent an auto start of the Safety Injection Pump during Emergency Diesel Generator load sequencing. 1P-15B and 2P-15B Safety Injection Pumps have been declared out of service as a result of accepting this new data. "Based on the combined effect of all received design motor data, a condition existed prior to 07/15/2005, which could have impacted the design function of Unit 1 or Unit 2 Safety Injection Pumps during a design basis accident with degraded safeguards bus voltage. Both Unit 1 and both Unit 2 Safety Injection Pumps had the potential for this effect to prevent auto start on the Emergency Diesel Generator Loading Sequence per design. Therefore, this condition is being reported under 10 CFR 50.72(b)(3)(v)(D) due to the potential to prevent fulfillment of a safety function to mitigate an accident. "Previous corrective action has been completed for Unit 1 and Unit 2 P-15A Safety Injection motors therefore, they remain Operable and capable of fulfilling design safety function." The licensee is currently in a 72 hour Tech. Spec. LCO 3.5.2 (A) action statement for ECCS train B on both Units. Repairs are expected to take six to eight hours. Safety Injection train A equipment is being protected by administrative requirements put in place by the licensee. Operations personnel have been briefed of the potential impacts. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-08-02
41884 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-06-30 | 2005-07-29 17:05 | 2005-09-02 | AGREEMENT STATE EVENT - HIGH DOSIMETRY BADGE READING The licensee provided the following information via email: "On July 28, 2005 the RSO for Longview Inspection, a radiography company located in Everett Washington, notified [the Washington State Radioactive Materials] department of a potential overexposure. In a written report sent that night, events were described as follows: Two Level 2 radiographers were dispatched to Kent Washington to perform radiography work on an above ground pipeline. Each radiographer was properly equipped with survey meters, self-reading pocket dosimeters, rate alarm dosimeters, and OSL [Optically Stimulated Luminescence Dosimetry]] badges. "During the course of the on site work, radiographer #1 crawled under the pipe to search for pipe numbers. At that time, it is believed that his OSL badge was knocked off his shirt pocket where he had it clipped. Both radiographers continued to work taking shots in the area unaware of the missing OSL badge. The alarm rate and pocket dosimeters were worn in a pouch on his hip and not in his shirt pocket with the OSL badge. "At the conclusion of the work, while both radiographers performed their break downs, equipment checks and daily radiation reports to complete the job, radiographer #1 discovered his OSL badge was missing. The immediate area was searched and the OSL badge was discovered under a sheet of plywood pulled into place to crawl upon while under the pipe. "They returned to their shop in Everett, Washington and notified the RSO of the mishap. The two radiographers reported that their rate alarms had not sounded constantly and periodic checks of the pocket dosimeter did not indicate any abnormal doses. Both men stated that they were working side by side the whole day . Since it was the end of the month wear period, the RSO sent all the radiographers' OSL badges in for processing. He forwarded the dosimetry report to us with his written report of the incident. "The report on the OSL found under the pipe had millirem readings of 5367 - Deep dose, 5638 Eye dose, and 6237 Shallow dose. The radiographer #2 had readings that were consistent with the doses reported for the wear period with other radiographers in the company. "The RSO reported that he suspended the radiographer #1 who had lost the OSL badge under the pipe, until the RSO receives approval from the department to resume radiographic operations." Washington State Report #WA-05-044 * * * UPDATE AT1815 EDT ON 9/2/05 FROM A. SCROGGS VIA EMAIL * * * The following information was provided as an update and closeout for WA-05-044: "On August 17, the department received the RSO's final report. In it the RSO stated it had been determined the recorded exposures had not been received by the radiographer. This conclusion was based on: - Self-reading dosimeters for both radiographers had not gone off-scale, - Both radiographer alarming rate-meters had not continuously alarmed, - The OSL dosimeter for the second radiographer showed normal readings, and association with each individual indicated each could be trusted. "The RSO calculated an exposure of 32 mRem for the day and had the dosimetry service assign a 300 mRem exposure to the individual for the month. The radiographer was allowed to return to work after the department reviewed the reported findings. "The RSO stated that all facility radiography staff were reminded to ensure they are properly equipped prior to performing each radiographic activity." Notified R4DO (Linda Smith) and NMSS (Tom Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-08-03
41883 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-07-21 | 2005-07-29 17:07 | 2005-07-29 | AGREEMENT STATE REPORT - ABANDONED WELL LOGGING SOURCE The licensee provided the following information via facsimile: "On July 21, 2005, D & S Wireline lost a 3.0 Ci source of Am-Be 241 with serial number NV5161NE downhole. The source was manufactured by Gamma Industries on November 10, 1981. D & S stopped trying to retrieve the source on July 26, 2005. The well logging tool is at a depth of 3210 feet. A cement plug and whipstock have been put on top of the tool to keep from reentering the well." Louisiana Report Number LA050006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-08-03
41882 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-07-28 21:25 | 2005-07-29 16:55 | 2005-07-29 | FAILURE OF SAFETY EQUIPMENT ON C-310 CYLINDER VALVE CLOSURE SYSTEM "At 2125, on 7-29-05 the Plant Shift Superintendent was notified that the nitrogen bottle pressure for the C-310 Cylinder Valve Closure System was reading 0 psig. The function of this system is to close the cylinder valve in the case of an actuation of the UF6 Release Detection and Isolation System at the UF6 Withdrawal Station. TSR 2.3.4.1 requires this system to be operable while operating in mode 2. At the time the nitrogen bottle pressure was discovered to be reading 0 psig, withdrawal positions 3 and 4 were operating in mode 2. The UF6 Release Detection and Isolation System was declared inoperable by the PSS and withdrawal positions 3 and 4 were placed in mode 3 as required by TSR LCO 2.3.4.1. "This event is reportable under 10 CFR 76.120(c)(2) as an event in which equipment required by the TSR is disabled or fails to function as designed. "The NRC Senior Resident Inspector has been notified of this event." The nitrogen bottle normally maintains a pressure of 1500-2000 psig. The system malfunction was found on the daily equipment check by the operator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2005-07-29
41881 | 0 | SAINT VINCENT HOSPITAL |  |  |  |  | 2003-07-21 | 2005-07-29 15:55 | 2005-07-29 | MEDICAL EVENT - DOSE BOTH GREATER THAN AND LESS THAN PRESCRIBED "An independent review of HDR (High Dose Rate) treatment records occurred on July 28, 2005. During this review, a Medical Event was discovered which meets reporting requirements of 10 CFR 35.3045. "On July 21, 2003, an 87 year old male received what was to be the first of two High Dose Rate (HDR) treatments for esophageal cancer using a remote afterloading unit. The physician Authorized User prescribed a dose of 500 cGy (centiGray) at 0.5 cm from the surface of the NG (naso-gastric) tube for an active length of 5.5 cm using a 5.551 Curie iridium-192 source. The treatment plan called for 12 indexer step positions at 5.0 mm spacing. The medical physicist entered 12 indexer step positions with 2.5 mm spacing and treatment was delivered. On August 14, 2003, the second fraction occurred without incident. "A simulated plan was calculated on July 29, 2005, to reproduce the initial treatment plan and actual treatment delivered. The simulations suggest the patient may have received as much as 74% over dosage to a portion of his esophagus and as much as 92% under dosage to a portion of his esophagus. "The patient returned to the facility on July 14, 2005, for treatment and is currently under our care." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-07-29
41880 | 0 | SAINT LUKE HOSPITAL |  |  |  |  | 2005-07-26 11:00 | 2005-07-29 11:52 | 2005-07-29 | MEDICAL EVENT - DOSE LESS THAN PRESCRIBED DURING MEDICAL TREATMENT A patient being treated for liver cancer was scheduled to be administered two SIR-spheres treatments (SIR-spheres utilizes radioactive micro-spheres that contain yttrium-90). The first treatment was prescribed as 0.46 GBq (GigaBecquerels) of Y-90. Due to difficulty in determining how much of the Y-90 remained in the vial and the injection catheter, the licensee has determined that only 0.25 GBq were administered in the first treatment dose. The patient will be given a second treatment that takes into consideration the actual amount administered on the first treatment. The licensee notes that the fraction of Y-90 administered differs from the prescribed dose by 46%. The regulatory criteria under 10 CFR 35.3045(a)(1)(iii) states that the reportability criteria is 50% or greater. The licensee has elected to conservatively report this event since it is close to the regulatory criteria. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-07-29
41879 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2005-07-25 09:18 | 2005-07-28 16:00 | 2005-07-28 | UNPLANNED CONTAMINATION EVENT DUE TO FILTER FAILURE "An unplanned contamination event occurred on 25 July 2005. This is a reportable event in accordance with 10 CFR 40.60 sub paragraph (1) based on additional radiological controls being required for more than 24 hours. The additional control imposed was the requirement to wear air purifying respirators in the Feed Materials Building. The location of the event was the Feed Materials Building. The Feed Materials Building is where milled uranium oxide material is converted to uranium hexafluoride. Located on the sixth floor, the Ash Vacuum Cleaner filters failed which allowed spar and dust filter fines containing uranium to exit the discharge from the Ash Vacuum Cleaner. Due to the proximity of the Ash Vacuum Cleaner discharge and the inlet to the building ventilation, some the material was picked up by the ventilation system and distributed throughout the Feed Materials Building. A dust plume was noted coming from the discharge line of the Ash Vacuum Cleaner at approximately 0918. At approximately the same time, personnel in the building noted dust being emitted from the building ventilation system registers. The Ash Vacuum Cleaner was secured at approximately 0920. Personnel recognized the potential for airborne radioactivity and immediately required respiratory protection for all personnel in the building. Special bioassay samples were required for 19 people who were present in the building during the occurrence. The results of the special bioassays indicated no uptake of radioactivity by the personnel sampled. Fixed air samplers analyzed after the event on all floor indicated air activity in the range of 5x10 E-11microcuries/ml to 60x10 E-11microcuries/ml. Air samples and contamination surveys performed downwind were background levels. Cleanup of the granular material in the Feed Material Building commenced immediately. "The isotope release was U-238, the chemical form is UF4, and the physical form is granular." The Feed Materials Building has now been cleaned of contamination that was due to this event. The licensee has notified NRC Region 2 (Hartland), NRC HQ (Raddatz) and NRC Regional Inspector (Gibson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(1) |  |  |  | 0 | 2005-07-28
41878 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-06-03 17:05 | 2005-07-28 10:21 | 2005-07-28 | HALF SCRAM ON VOLTAGE REGULATOR FAILURE "On June 3, 2005 at approximately 1705, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100% reactor power, a failure of the 'A' Reactor Protection System (RPS) motor generator voltage regulator occurred, resulting in a loss of power to the 'A' RPS bus, a half scram and multiple system isolations. The voltage transient caused by Technical Specification required RPS testing revealed the voltage regulator failure. Appropriate actions were taken in accordance with Abnormal Operating Procedure (AOP)-59, Loss of RPS Bus. All equipment operated as designed as a result of the loss of power to the RPS bus. "At 1744, the 'A' RPS bus was placed on the alternate power supply and the half scram was reset. The Primary Containment Isolation System (PCIS) isolation signal was reset at 1805 and restoration of the various isolated systems commenced shortly thereafter. The reactor remained at 100% reactor power throughout the event and Limiting Conditions for Operation were entered for the affected equipment as required. "The above event meets the reporting criteria of 10 CFR 50.73(a)(2)(iv)(a) since the loss of RPS bus resulted in general containment isolation signals affecting containment isolation valves in more than one system. The following systems or components isolated as a result of the loss of RPS bus: "Reactor Water Cleanup, Reactor Building Ventilation, 'A' Containment Atmosphere Dilution, Torus Vent and Purge, Drywell Equipment and Floor Drain Sumps, 'A' Drywell Containment Atmospheric Monitors, Recirculation System Sample Line, Main Steam Line Drains, Residual Heat Removal drain valve to radwaste, Standby Gas Treatment (auto Initiated). "Since the signal was invalid (the result of loss of power vs, an actual containment isolation condition), this event meets the criteria in 10 CFR 50.73(a)(1) for being reported as a 60 day telephone notification In lieu of a written LER. "The event was entered into the corrective action program. The loss of the 'A' RPS bus was caused by the failure of a uni-junction transistor (UJT) in the voltage regulator of the 'A' RPS motor generator, which resulted in an overvoltage condition and resultant protective trip. The voltage regulator was replaced with a spare from stock with a UJT from a different manufacturer. Other corrective actions include changing manufacturer's of the UJT (the former vendor no longer makes this UJT), and replacing the 'B' motor generator and alternate power supply voltage regulators with ones having new UJTs." The licensee notified the NRC Resident Inspector and the state Public Service Commission. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-07-28
41877 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-07-27 21:25 | 2005-07-28 05:57 | 2005-09-09 | TWO TRAINS OF CONTROL ROOM EMERGENCY VENTILATION SYSTEMS (CREVS) INOPERABLE AND NOT RESTORED WITHIN 24 HOURS "At 2125 on 7/27/05, Door 33021 (B Engineering Safety Feature Switchgear to B Emergency Diesel Generator) (B ESF Switchgear to B EDG) was found not to be latched. Reviewing history; the door was first discovered not to latch at 1215 on 7/26/05, by Security. The Control Room was notified at 2125 on 7/27/05 by an Equipment Operator, who found the door unlatched. Door was subsequently latched closed at 2155 on 7/27/05. "Due to this door not being able to be verified latched, T/S LCO 3.7.10.B should have been entered at 1215 on 7/26/05. This renders 2 trains of Control Room Emergency Ventilation Systems (CREVS) inoperable, and if not restored within 24 hours, a plant shutdown is required; being in Mode 3 (Hot Standby) in 6 hours and Mode 5 (Cold Shutdown) in 36 hours. The plant should have been in Mode 3 at 1815 on 7/27/05. This time was not met. As stated previously, the door was verified to be latched at 2155 on 7/27/05. A plant shutdown is not being made due to the LCO 3.7.10.B being satisfied at 2155 on 7/27/05. "Door 33021 (B ESF Switchgear to B Emergency Diesel Generator) was repaired at 0022 on 7/28/05. "This issue has been entered in the licensee corrective action program." The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION FROM R. REIDMEYER TO M. RIPLEY 1419 EDT 09/09/05 * * * "Upon further review, it was concluded that this event is not reportable. The design functions of this door are pressure boundary and fire protection. Based upon the following criteria, this event was determined to be not reportable: "1) Pressure boundary: Actual duration of door inoperability did not result in a violation of Control Room Emergency Ventilation System Technical Specification Action completion time limits. "2) Fire protection: Only one fire suppression system was impacted and the inoperability of a fire protection suppression system for a single area is not reportable with regards to the Fire Protection Program. "The loss of one fire suppression system was bounded by Callaway licensing basis." The licensee will notify the NRC Resident Inspector. Notified R4 DO (Powers) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-07-28
41876 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2005-07-27 20:00 | 2005-07-27 21:08 | 2005-07-27 | OFFSITE NOTIFICATION CONCERNING POWER REDUCTION TO TAKE PLANT OFFLINE "The New York State Public Service Commission was notified that Ginna is coming offline due to chemistry concerns. EPRI level 3 guidelines [for sodium and chloride levels] were exceeded during line-up of the blow down system during maintenance. Required action is to reduce power to less than 5% reactor power and perform system cleanup." The licensee notified the NRC Resident Inspector. | 45 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-07-27
41875 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2005-07-27 15:00 | 2005-07-27 16:03 | 2005-07-27 | IMPROPERLY LABELED RADIOACTIVE MATERIAL SHIPMENT The licensee reported that three main steam line radiation monitors (unused) were recently shipped from a site storage warehouse to a salvage vendor (ATS Corporation in Woodridge, Illinois). When the material arrived at the vendor, it was discovered that each of the monitors contained a 100 nanocurie Americium-241 source (a total of three 100 nanocurie sources). The vendor informed Calvert Cliffs of the radioactive sources in the shipment. Apparently, the licensee was unaware of the sources in the monitors when the material was sent to salvage. Calvert is sending a representative to the vendor to retrieve the sources. Calvert will also be issuing a 30 day Hazardous Material Incident Report in accordance with 49 CFR 171.21 for making the shipment without properly marking the packaging as containing radioactive material. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-07-27
41874 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-07-26 16:35 | 2005-07-26 19:35 | 2005-07-26 | INOPERABLE SINGLE EMERGENCY SIREN "On July 26, 2005 at approximately 09:07 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Department was notified of an inoperable single siren (#42). While reviewing the siren monitoring computer log, an Information Services Technician received a no response signal on siren #42. Upon investigation, siren #42 was found inoperable. The siren was vandalized by destroying the battery case and stealing the internal battery. The affected siren is estimated to impact approximately 144 members of population (6.8%) in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles (or 10% within 5 to 10 miles) for greater than 1 hour. This call is being placed due to the relatively large segment of the population affected and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "The County was informed at 09:38 MST to implement the MCSO notification if a need arises. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-07-26
41873 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-07-26 16:00 | 2005-07-26 18:50 | 2005-07-28 | AGREEMENT STATE REPORT - POSSIBLE LOST TRITIUM GENERATORS Schlumberger called the State of Louisiana to report a missing shipment of four tritium generators. Each unit contains 3 to 5 Ci (curies) of tritium. The shipment was picked up by Federal Express on July 15, 2005 in Shreveport, LA. It was to arrive at its destination on July 17, 2005 at Princeton, NJ. Federal Express notified Schlumberger yesterday that as of that date the shipment had not arrived at its Memphis transportation hub. The units are sealed in the sense that they need software to be used. The State of Louisiana is following up. * * * UPDATE TO NRC (HUFFMAN) FROM STATE REP (NOBLE) @ 12:12 EDT ON 7/28/05 * * * Federal Express has located the shipment of tritium generators and redirected the shipment to the final destination in New Jersey. The State was told that the shipment was misdirected due to a package labeling problem. The State considers this report closed. R4DO (Graves) and NMSS EO (Essig) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-07-29
41872 | 0 | WINCHESTER MEDICAL CENTER |  |  |  |  | 2005-07-22 10:00 | 2005-07-26 16:10 | 2005-07-27 | MEDICAL EVENT - ADMINISTRATION OF LOWER DOSE THAN PRESCRIBED On July 22, 2005 a patient was administered a dose of 2.64 rem from a 66 mCi (millicurie) source of Sm 153 versus the intended dose of 4.28 rem for bone pain therapy. This was discovered later when the medical technologist questioned the dose and raised a question with the supervisor. When the technologists checked the calibration setting of the instrument used to measure the source they discovered that the calibration setting was incorrect. With the incorrect calibration setting a source of 66 mCi of Sm 153 was used versus the intended 107 mCi source. The prescribing physician will notify the patient's doctor who will contact the patient. There was no known adverse affect on the patient. The hospital took a corrective action of retraining and adding a check on their administration sheet that requires the technologist to check the instrument calibration setting. * * * UPDATE TO NRC (HUFFMAN) FROM LICENSEE (WILLIAMS) AT 15:11 EDT ON 7/27/05 * * * The following follow-up calculations related to the dose were provided by the licensee: Whole body dose (assuming a qualify factor of 10) - 0.108 millisieverts per megabecquerel Bony Surfaces dose (assuming a qualify factor of 10) - 67.56 millisieverts per megabecquerel Bone Marrow dose (assuming a qualify factor of 10) - 15.37 millisieverts per megabecquerel R1DO (Meyers) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-07-26
41871 | 0 | HARBINSON AND WALKER |  |  |  |  | 2005-04-25 | 2005-07-26 14:27 | 2005-07-27 | LOST SOURCE FROM A LEVEL MEASURING DEVICE Licensee reported that two 50 millicurie Cs-137 sources, used in level measuring devices, were found to be missing from a magnesium oxide producing facility that had been closed for two years. It was determined that two sources were missing after a review of their registration around the April-May time period. Since then, they located one of the two sources, brand new, in a crate on a shelf at the facility. They located the non-nuclear part of the device (the receiver) on a hopper which was at a scrap yard on site, but the sending unit (the nuclear part) was missing. They continued looking for the sender, but could not find it. * * * UPDATE ON 07/27/05 @ 1745 BY ASHLEY TULL TO CHAUNCEY GOULD * * * The single source which is still lost is a TN Technologies Model 5200 gauge containing 200 millicuries Cs-137 not 50 millicuries. Notified Reg 3 RDO (Mark Ring) and NMSS EO (Joe Giitter) * * * UPDATE ON 07/27/05 @ 2142 BY JOHN CROOKS TO CHAUNCEY GOULD * * * Two NRC Inspectors visited the closed facility with a radiation detector and located the missing device in a parts warehouse at the facility. It was on a shelf and had turned rusty and was unidentifiable. The device was isolated in another building with the other device that had been found. Notified Reg 3 RDO (Mark Ring), NMSS EO (Joe Giitter) and TAS(E-MAIL) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-07-26
41870 | 0 | PROFESSIONAL INSPECTION AND SERVICE |  |  |  |  | 2005-07-26 | 2005-07-26 10:29 | 2005-07-26 | DAMAGED TROXLER GAUGE A track hoe ran over a Troxler Moisture Density Gauge (s/n 032770) with a 8 milliCurie Cs-137 (s/n 7508116) and a 40 milliCurie Am-241/Be (s/n 47-28967) source. The gauge was imbedded upside down in the ground. The source was still in the gauge and the shutter is half open. The area is roped off to limit access. The RSO made the report, is on scene, and is preparing to take radiation surveys. The RSO had not decided on how to remove the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2005-07-26
41869 | -1 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-07-25 18:15 | 2005-07-25 18:38 | 2005-08-16 | SPECIAL NUCLEAR MATERIALS INVENTORY DISCOVERS A FUEL PIN MISSING " As a result of NRC Bulletin 2005-01 "Material Control and Accounting at Reactors and Wet Spent Fuel Storage Facilities", Oconee has been conducting an inventory of Special Nuclear Materials (SNM), other than complete fuel assemblies, stored in the spent fuel pools at Oconee. One canister, documented as containing 383 fuel pins, was found to actually contain 382 fuel pins. At this time it is uncertain if this is a record keeping error or an actual "lost" pin. "Initial Safety Significance: "The inventory process for other canisters is not complete, and it is possible that the pin may be in another container. These containers being inventoried have been stored underwater in the spent fuel pool for years. The affected canister was filled in 1982. Oconee has no reason to believe that this pin or any other SNM has been stolen or unlawfully diverted. For reference, one fuel assembly contains 208 fuel pins. "Corrective Action(s): "The inventory process is continuing. This notification is being trade per 10 CFR 74.11." The NRC Resident Inspector will be notified. ****** RETRACTION on 08/16/05 at 1537 EDT by Stephen C. Newman to MacKinnon ***** "On July 17, 2005 at 1838 [ET] Oconee reported that during an inventory of Special Nuclear Material (SNM), other than complete fuel assemblies stored in the spend fuel pools at Oconee, one canister, documented as containing 383 fuel pins, was found to actually contain 382 fuel pins. At that time it was uncertain if this is a record keeping error or an actual "lost" pin. Further investigation has located the suspect fuel pin in a different canister; consequently, this issue no longer meets the reporting requirements as previously stated and this report is being retracted. "Initial Safety Significance: There is no initial safety significance. "Corrective Action(s): No additional corrective actions planned at this time." R2DO (C. Julian), NMSS EO (M. Burgess) and IRD Manger (M. Leach) notified. NRC resident Inspector was notified of this retraction by the licensee. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOST/STOLEN SNM |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 74.11(a) |  |  |  | 0 | 2005-07-25
41868 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2005-07-25 | 2005-07-25 17:35 | 2005-07-29 | AUTOMATIC REACTOR TRIP CAUSED BY FAILURE IN SWITCHYARD "At 1525 the plant experienced a load reject generator trip due to a catastrophic failure in the 345 Kv switchyard. A reactor scram occurred as a result. The degraded AC power system prevented a fast transfer from occurring. Degraded bus voltage caused the emergency diesel generators (EDGs) to start. A residual bus transfer restored power to the 4 Kv busses. The [main steam isolation valves] (MSIVs) closed on a low-low reactor water level of 82.5 inches. [Reactor Core Isolation Cooling] and [High Pressure Coolant Injection] (HPCI) also started on the low-low reactor vessel water level. "The [Safety Relief Valves] were cycled twice for pressure control. OT 3100 Reactor Scram procedure was executed. EOP-3 was entered due to elevated torus water temperature and both loops of [Residual Heat Removal] (RHR) are in torus cooling. Water level has restored and is being maintained by feedwater. The MSIVs have been reopened and the scram reset. EDGs were secured." The plant is currently shutdown and stable with all control rods fully inserted. Decay heat removal is being accomplished with HPCI in pressure control mode. The licensee is transitioning to feeding with normal feedwater and steam exhausting through drains. Both trains of RHR are providing torus cooling. Electric power is being provided by offsite power. The licensee is currently investigating the event in the switchyard. The licensee notified the NRC Resident Inspector and will issue a press release. * * * UPDATED ON 07/29/05 BY MACKINNON * * * Corrected incorrect entry for Scram Code from N (N/A) to A/R (Automatic/with Rod Motion). R1DO (Glenn Meyer) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ECCS INJECTION | OFFSITE NOTIFICATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2005-07-25
41867 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-07-25 | 2005-07-25 13:30 | 2005-07-25 | AGREEMENT STATE REPORT INVOLVING FIRE DAMAGED GAUGES The State provided the following information via facsimile: "Fire broke out in the Coker 1 unit at Citgo. The FA201A and 201B vessel structures (24,000 cu. Ft.) holding Coker feed (heavy black oil) product were impacted by the fire / heat from fire. Each of the above-mentioned vessels have three nuclear gauges (Am-241 / Be, 500mCi activity) attached in linear formation to them. The gauges are used for product level measurements. Three of the six total number of gauges sustained fire / heat from fire that impacted the functioning of the housing of devices, specifically the shutters. According to Citgo licensee: "1) Of the three shutters impacted, two cannot be closed (and therefore, unlocked) and remain open as they usually are during regular production, the third could be closed but not locked. "2) All six gauges are scheduled to be removed by the manufacturer for maintenance, repair, etc. as needed. "3) The gauges are Kay-Ray (Thermo Measure Tech) brands. "4) The three gauges with functional impact are: Gauge Housing - all are model number 7100B; Sealed Source model number MRL2723C and serial numbers -- 17235, 26053, and S95M2201." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-07-28
41865 | 0 | U.S. ARMY |  |  |  |  | 2005-05-17 | 2005-07-22 19:43 | 2005-07-22 | LOST M88 ACADA CHEMICAL DETECTOR The following information was discussed with the U.S. Army (Gizicki), and faxed to HOC: "On 23 Dec 04 a Stryker vehicle (sn CV007-01) containing one ea M88 ACADA detector (NSN 6665-01-438-3673 with possible s/n Y14-D-19158 ) was shipped from Ft. Lewis, WA to General Dynamics Land System (GSLS) in Sterling Hts, MI. The M88 ACADA is hard mounted in the Stryker vehicle. The M88 ACADA contains 30 millicuries of Ni-63 in sealed source form. The particular vehicle with the M88 was to be retrofitted and tested for shipment to Iraq. "The stryker vehicle was received at GDLS Sterling Hts. on 28 Feb 2005. The Stryker vehicle with the M88 was driven from GDLS, Sterling Hts, MI to GDLS Shelby, MI on 28 Feb 05 in order to be equipped with other components and inspected. On 25 March 2005 the Stryker was shipped to Fort Huachuca, AZ where the vehicle was to be further tested. The Stryker vehicle was shipped from EPG Ft. Huachuca, AZ to Yuma Proving Grounds, AZ on 25 March 2005 for additional testing. The vehicle was then shipped from Yuma PG to Ft. Lewis, WA where it was received on 4 April 05. "On 13 April 05 the M88 ACADA was discovered missing at Ft. Lewis WA. The Licensee was notified on 17 May 05 of the missing M88 detector. Between May 17 and 11 July 2005 an extensive search for the missing M88 occurred at GDLS (Sterling Hts., MI, Shelby MI and Auburn, WA sites), Yuma PG, AZ, Ft. Huachuca, AZ, and Ft. Lewis, WA. The missing M88 could not be found and presumed lost or stolen. The Army is currently conducting their own investigation of the lost device through the Army CID office." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-07-22
41864 | 0 | AREVA |  |  |  |  | 2005-06-15 | 2005-07-22 16:22 | 2005-07-22 | PART 21 REPORT - PRESSURIZER HEATERS FROM FRAMATOME AREVA provided the following information via facsimile. "Reportable Defect "(i) Name and address of the individual informing the Commission: Gayle Elliott, 3315 Old Forest Road, Lynchburg, VA 24501. "(ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States which fails to comply or contains a defect: The components that contain the defect are pressurizer heaters. "(iii) Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: Framatome ANP, Inc. supplied pressurizer heaters with internals manufactured by Thermocoax. "(iv) Nature of the defect or failure to comply and the safety hazard which is created or could be created by such a defect or failure to comply: This issue concerns installed pressurizer heaters that were supplied by Framatome ANP. The heaters in question had a deficiency that may have resulted in a portion of the heated length being located inside the pressurizer heater nozzles (sleeves). Evaluation indicates that the failure mode could cause heating of the pressure boundary base metal (pressurizer heater nozzle) above the design temperature specification. "(v) The data on which the information of such a defect or failure to comply was obtained: This issue was determined to be a deviation on June 15, 2005. "(vi) In the case of a basic component which fails to comply, the number and the location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: Framatome ANP supplied 36 Thermocoax pressurizer heaters to Arizona Public Service for Palo Verde Unit 3 and 30 heaters to Entergy for Waterford Unit 3. "(vii) The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for this action; and the length of time that has been or will be taken to complete the action: All of the heaters supplied for Palo Verde Unit 3 have been removed from service and will not be reinstalled in the plant. All of the pressurizer heaters delivered for Waterford 3 (except for five) have been removed from service. The remaining five pressurizer heaters are currently installed in the pressurizer, however, Entergy has taken steps to preclude electrically energizing of these heaters and, therefore, the adverse conditions that could be created by the defect are precluded. "(viii) Any advice related to the defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: See (vii) above." Also see related Event # 41783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2005-07-22
41863 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-07-22 09:12 | 2005-07-22 14:50 | 2005-07-22 | FITNESS FOR DUTY REPORT INVOLVING A CONTRACT ACTING FOREMAN A non-licensed contract acting foreman had a confirmed positive for alcohol during a random fitness-for-duty test. The contractor's access to the plant has been terminated. Contact the Headquarters Operation Officer for additional details. The licensee informed the NRC Resident Inspector and Region 2 (Wallo). | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2005-07-22
41862 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2005-07-20 | 2005-07-22 12:47 | 2005-07-22 | AGREEMENT STATE REPORT INVOLVING POTENTIALLY ABANDONED SOURCES The following information was received from the State of Mississippi via email: "Description of Incident: Received notification 7-20-05 from Mississippi Emergency Management Agency (MEMA) that another State Agency (DEQ) had discovered the abandonment of a AEA Model 680 Cobalt-60 exposure device and a SPEC Model 150 exposure device containing Iridium-192. Division of Rad Health (DRH) personnel responded to location and determined that no devices were missing from the licensed storage facility. It had been assumed from other emergency responders that a overpack (Model 680-OP) for the Cobalt device may have contained radioactive material and was missing from the container. The event generated television and newspaper media attention. DRH personnel explained that the overpack was only used when the device was transported on public roads. All radioactive material was accounted for and secured in the storage area. Also, DRH and DEQ personnel went to Struthers Industries location at the 34th Street facility located in Gulfport, MS, where all radioactive material ( a Model 680 Cobalt 60 exposure device and a Model 660 Iridium 192 device) was accounted for and still secured in the locked storage vault. There was security concerns due to the companies being in bankruptcy and the new owners not knowing about the radioactive devices. DRH had investigated the security of the sources on 6-28-05 and found the sources safe, but met with the president of company who assured DRH he would properly dispose of the devices. On 7-21-05 AEA Technology was contacted to remove the sources. The sources were put in approved overpacks. Leak tests had been performed on the sources and determined that the sources were not leaking. AEA personnel also removed all radiation signs and associated equipment at the 2 locations. DRH personnel did closeout surveys along with AEA personnel to ensure no radioactive sources were left behind. All radioactive material that was licensed by the 2 licenses (MS-750-01 and MS-259-01) were accounted for and removed by AEA personnel. It has not been determined by DRH personnel if devices were abandoned and the investigation is ongoing by DRH personnel. "Isotope(s)/Activity: Cobalt 60 (2 devices/sources) @ 23 curies in each device, Iridium 192 (2 devices/sources) @ 5 curies in each device "Date of Incident: 7-20-05 "Date Reported To DRH: 7-20-05 "Describe clean-up actions taken by DRH: After determining all radioactive devices were accounted for, DRH contacted AEA Technology about the removal of the devices. DRH personnel stayed at location until all sources and devices were removed and caution signs and associated radiography equipment was removed. "List radiation measurements taken by DRH: Highest readings were @ 30 mR/hr at surface of the Co-60 exposure devices. The readings on the Iridium-192 devices were less than 5 mR/hr. "List any other actions required of DRH: Event is under investigation by DRH, EPA, MS DEQ, and FBI. "List any actions taken to notify NRC, other Agreement States: NRC Ops Center notified by E-mail 7-22-05; NMED notified 7-22-05 by E-mail. Event was reported to EPA due to other hazardous materials that were discovered at the site. Also investigated by FBI and inquiries made from Homeland Security. "Enforcement action taken: Investigation ongoing as to if devices were abandoned or if the owner was still in process of disposing of the devices." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2005-07-27
41861 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-07-22 03:16 | 2005-07-22 08:01 | 2005-07-22 | T/S SHUTDOWN DUE TO DC SUBSYSTEM DECLARED INOPERABLE "During performance of 2-SR-3.8.6.2(I-A) QUARTERLY CHECK FOR SHUTDOWN BOARD A BATTERY, the DC subsystem was declared inoperable due to cell voltage not meeting Technical Specification (TS) acceptance criteria. Concurrently a second DC subsystem was inoperable in support of scheduled maintenance activities. As a result of these subsystems being inoperable, Unit 2 entered TECHNICAL SPECIFICATION LCO 3.0.3. at 0220 and commenced a shutdown at 0316. In accordance with 10CFR50.72(b)(2)(i) this notification is being made. "Plant conditions are stable at this time and no other plant systems were affected. At 0450 one DC subsystem was returned to an operable status. As a result of this, Unit 2 exited LCO 3.0.3, shutdown activities were terminated and unit 2 has been returned to 100 % power." The licensee notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-07-22
41860 | 0 | MONTGOMERY REGIONAL HOSPITAL |  |  |  |  | 2005-07-20 11:00 | 2005-07-21 14:30 | 2005-07-21 | MEDICAL EVENT - DELIVERED DOSAGE EXCEEDED PRESCRIBED DOSAGE "On Wednesday July 20, 2005 it was discovered, during a routine audit of the Nuclear Medicine records, that two patients were administered I-131 in amounts exceeding 30 microcuries without a written directive. Furthermore, the doses fell more than 20% outside the prescribed dose range as set by the Authorized User (AU) physician. Below I will discuss the particulars of each administration. "1. Patient #1: 25 year old female was administered 31 µCi of I-131 Sodium Iodide (Nal) on 18 July 2005 without a written directive prepared or signed by the AU previous to administration. The purpose of the study was to ascertain the thyroid uptake fraction and image the thyroid tissue. The prescribed does range, as set by the AU, was 8 to18 microcuries. This dose was 72% higher than the maximum dose allowed by the AU for this diagnostic procedure. (The patient's actual 24-hour thyroid uptake fraction was 27.5%). "2. Patient #2: 61 year old female was administered 42 µCi of I-131 Nal on 14 July, 2005 without a written directive prepared or signed by the AU previous to administration. The purpose of the study was to ascertain the thyroid uptake fraction and image the thyroid tissue. This dose was 133% higher than the maximum dose allowed by the AU for this diagnostic procedure. (The patient's actual 24-hour uptake fraction was 14%). "Dose Estimates From These Procedures "1. Patient #1: Using data found in NUREG CR-6435 "Radiation Dose Estimated from Radiopharmaceuticals" we estimate the following doses for the (a) Whole Body: 1.209 rem, and (b) Thyroid (target organ) 40.3 rad "2. Patient #2: Using data from NUREG CR-6345 and from other sources we estimate the following dose for the (a) Whole Body: 1.638 rem, and (b) Thyroid: 17.6 rad." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-07-21
41859 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-07-07 | 2005-07-20 16:00 | 2005-08-05 | AGREEMENT STATE REPORT - SCRAP METAL CONTAMINATION State of California provided the following information via email: "[The] US Customs Service, Port of Oakland contacted RHB-Berkeley on the morning of 07-07-2005, reporting that a load of scrap metal bound for China had set off a radiation alarm. Mr. Kent Prendergast and Mr. Mark Gottlieb of RHB-Berkeley responded. Measurements were made of the trailer and the following readings were obtained using a Bicron FieldSPEC-N, sn 02f3/777, portable MCA: "Dose Rates: Surface = 260 µR (microR)/hr; 1 foot from surface = 38 µR/hr; 1 foot to the left = 35 µR/hr; 1 foot to the right = 45 µR/hr; 1 foot above = 19 µR/hr. The radionuclide was identified as Am-241. "On 07-08-2005, the Pleasant Hill Recycling Center was visited. The Port of Oakland determined that the load of scrap metal had originated there. [The Recycling Center] President and the Manager were interviewed. They stated that the load was lead scrap which had been accumulating for several years. They said that it would be very difficult to identify the source of the Am-241 if possible at all. They were uncertain if the scrap would be returned to them or handled by the Port of Oakland. [The Recycling Center President had] made contact with a health physics consultant as directed by the Port of Oakland to dispose of the Am-241. The area where the lead was stored was surveyed with both a Ludlum Model 3-98 survey meter with an external thin window, thin crystal Nal probe Mode 44-3, and a Ludlum Model 19 µR meter. The results of the survey were negative. "Based on measurements and calculations performed on 7-19-05 and 7-20-05, the activity of the Am-241/ Be source at the Port of Oakland is from 50 mCi to 150 mCi." * * * UPDATE FROM K. PRENDERGAST TO W. GOTT AT 1630 ON 08/05/05 * * * California Radiation Control Program personnel with the assistance of U.S Customs, inspected the scrap metal and found 9 Am-241 sources. They have taken custody of the sources and will conduct analysis to identify and determine where the sources originated. Notified R4DO (D. Powers) and NMSS EO (S. Moore) and emailed TAS (R. Warren) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-07-26
41858 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-07-20 19:17 | 2005-07-20 22:17 | 2005-07-20 | EMERGENCY SIRENS FAILED FOR ONE HOUR "At 2017 CDST on July 20, 2005, it was determined that greater than 25% of Braidwood Station Emergency Sirens, which are maintained by others, had been failed for one hour. The initial failure occurred at 1917 CDST on July 20, 2005, and was apparently caused by storm activity in the area. At 2041 CDST on July 20, 2005, Braidwood Station was notified by the Corporate Emergency Planning organization that the number of failed Emergency sirens was less than 25% of the total number of sirens, and that sirens were in the process of being restored at that time. "This notification is required by 10CFR 50.72(b)(3)(xiii)" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-07-20
41857 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2005-07-15 | 2005-07-20 16:43 | 2005-07-20 | PART 21 NOTIFICATION OF NON-COMPLIANCE WITH ANSI AND QA MANUAL REQUIREMENTS The following report was submitted by the licensee via facsimile: "1. During review of quality records for installation of valves in Uranium Hexafluoride cylinders it was determined that this site was not in compliance with ANSI N 14.1 - 1971/2001, 'Uranium Hexafluoride Packaging for Transport.' Specifically, personnel were not recording the torque during valve installation as required by paragraph 6.12.6 of ANSI N 14.1 and Section 10 of Honeywell UF6 Cylinder Quality Assurance Manual. The ANSI standard specifies both a torque and minimum thread engagement for the valves. Even though both parameters are required by the Honeywell procedure this site was using only the thread engagement for determination of proper valve installation. The issue was identified on July 15, 2005. No full cylinders with questionable valve installation have been shipped since this date. All recipients of cylinders pertaining to this matter were notified of the compliance issue on July 20, 2005. Currently there have been no reports of issues related to valves installed by MTW Honeywell. "2. Since identification of the problem the following additional actions have been taken: "a. Honeywell has started a review to determine the correlation between thread engagement and torque. Thus far, fourteen cylinders have had valves installed to the proper thread engagement. In every case thus far the thread engagement has correlated with the torque specified by the ANSI standard within the required range of - 200 to 400 ft-lbs. Twenty six more cylinders will have valves installed to the required thread engagement and the torque will be verified. This statistical sample size gives a 99% confidence level of representing the total Honeywell population of Uranium Hexafluoride cylinders in service. Honeywell Metropolis presently has approximately 900 Uranium Hexafluoride cylinders in service. In addition Honeywell has changed approximately 106 valves in recipient cylinders and they will be notified of the cylinder numbers and the issue concerning valve torque. "b. In accordance with the ANSI N 14.1 standard cylinders have been and will continue to be pressure tested to 100 psig after valve installation to assure the valve and valve joint do not leak. "c. A technical evaluation was made concerning the failure mode if the valves were significantly over-torqued. This evaluation concluded that failure of the valve would occur prior to failure of the cylinder fitting and that failure would be obvious upon visual inspection. As noted previously there have been no reported issues related to valves installed by Honeywell. The probability of valves being significantly under torqued while achieving proper thread engagement appears to be very remote. "d. Only six personnel are presently authorized to perform valve installations and have been re-trained to ensure they understand and comply with the applicable procedures. In addition as a temporary measure direct supervision will be provided to assure compliance with Honeywell procedures that meet ANSI N 14.1 requirements. "3. Based on the above review and actions Honeywell does not consider that a safety hazard exists with the transport and use of cylinders on which valve replacement was performed by Honeywell." The licensee has notified Region 2 (J. Hanson, D. Hartland and J. Sharkey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 21.21 |  |  |  | 0 | 2005-07-20
41856 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-07-20 04:51 | 2005-07-20 12:47 | 2005-07-20 | MINIMUM RECIRCULATION VALVES WILL NOT AUTOMATICALLY OPEN IN LOCAL OPERATING MODE "While performing a test start of P-38A Motor Driven Auxiliary Feedwater Pump utilizing the local control station, it was discovered that AF-4007, the mini-recirculation valve for P-38A would not automatically open in the local mode of operation. The mini-recirculation valve provides a minimum flow path for pump operation to prevent pump damage. After this condition was discovered, a review of procedures associated with initiating safe shutdown via local operation disclosed that the procedure did not address manually opening the mini-recirculation valve prior to local pump start. As a result, pump damage could occur due to no flow though the pump prior to aligning a flow path into a steam generator. This condition is also applicable to AF-4014, the mini-recirculation valve for P-38B Motor Driven Auxiliary Feedwater Pump. "P-38A and P-38B Motor Driven Auxiliary Feedwater pumps would only be used in a safe shutdown local control condition if steam generator level could not be maintained using the normal means of 1P-29 and 2P-29 Turbine Driven Auxiliary Feedwater Pumps. "The station has taken compensatory actions to brief the operators about the condition. Additionally, temporary procedure changes are in progress to direct the operator to manually open each Motor Driven Auxiliary Feedwater Pump's associated mini-recirculation valve prior to a local start of the P-38A or P-38B Motor Driven Auxiliary Feedwater Pump. "The associated mini-recirculation valve will operate when P-38A or P-38B Motor Driven Auxiliary Feedwater Pump is started from the control room. Follow up testing has verified P-38A Auxiliary Feedwater Pump operability." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-07-20
41855 | -1 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2005-07-19 | 2005-07-19 18:22 | 2005-07-20 | RADIOACTIVE PACKAGE WITH REMOVABLE SURFACE CONTAMINATION EXCEEDING A LIMIT "Licensee: Department of Veterans Affairs, National Health Physics Program License # 03-23853-01VA "Permittee: VA Gulf Coast Veterans Health Care System, Biloxi, Mississippi "Date of event: July 19, 2005, about 1000 CDT "Date and Time NHPP notified: July 19, 2005, 1700 CDT "A radioactive package was received from the commercial radiopharmacy at about 1000 hours CDT. The nuclear medicine technologist followed routine procedures for opening radioactive packages and performed a wipe test on the outside of the package. The wipe test results were 13,000 dpm / 300 cm2. Slight contamination was located on the inside of the package. The technologist immediately notified the radiopharmacy of the contamination. The radiopharmacy is Cox Nuclear Pharmacy in Biloxi, MS. "NHPP representatives will follow-up with the permittee on July 20, 2005. A copy of this text has been sent to Kevin Null, NRC Region III "Event Number: 41855" **** RETRACTION ON 07/20/05 AT 1010 EDT FROM GARY WILLIAMS TO MACKINNON **** "The basis for retracting the event is that the package had approximately 49 DPM per cm2 removable radioactive contamination on the outside, which is less than the reporting requirement under 49 CFR 173.443. "This retraction was coordinated with NRC Region III." R3DO (Patrick Louden), R1DO (Rich Conte) and NMSS EO (Michele Burgess) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | MS | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2005-07-19
41854 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2005-07-18 | 2005-07-19 10:04 | 2005-08-05 | ALABAMA AGREEMENT STATE REPORT - IMPROPER USE AND SHIPMENT OF NUCLEAR GAUGE The State provided the following information via facsimile: "Description of Event: A dredging company using GL devices in Alabama illegally, removed and shipped a device containing a 200 milliCuries cesium 137 source to Ronan Engineering Company in Kentucky for repair. The shutter was not locked in the closed position. The owner had painted over the marking and labeling on the source holder so that they were illegible. The dredging company has hired a consultant to reconstruct the incident and try to determine any possible exposures received. "Additional information will be submitted after the investigation is completed." The following, additional information was obtained from the State via telephone: Dredging Company: Inland Dredging, Co. based in Dyersberg, TN, doing work in the vicinity of Jackson, AL The gauge is currently at Ronan Engineering Co., Florence, KY Event date is unknown, but the State was notified on the evening of 7/18/05. * * * UPDATE PROVIDED BY DAVID WALTER (STATE OF ALABAMA) TO JEFF ROTTON VIA FAX AT 1623 EDT ON 08/05/05 * * * The State provided the following information via facsimile: "The general licensee stated that they had closed the shutter and placed a bolt through the mechanism to lock it closed. [The general licensee] then removed the device and prepared it for delivery to Ronan Engineering Company via truck. [The general licensee] contends that the shutter handle was broken during shipping. [The general licensee] further states that they had removed the paint from the identification placard on the source head. When [the general licensee] prepared the unit, they stated they bolted the source head to the detector head. This resulted in minimal access to the beam port. Ronan performed a survey of the device, and found maximum exposure readings of 1.5 mrem/hour at 1 meter. "During shipping, the device went through five transport terminals, and appears to have been transferred to different trucks in each terminal. "An Alabama licensee authorized to service industrial gauges has been contracted to investigate the incident. This company is traveling to Ronan to obtain further information, and has set up interviews with personnel at the transport terminals." Notified the R1DO (Gray) and NMSS EO (Moore). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2005-07-22
41853 | 0 | RAPID CITY REGIONAL HOSPITAL |  |  |  |  | 2005-01-06 07:00 | 2005-07-19 11:00 | 2005-07-19 | PART 21 NOTIFICATION CONCERNING MALFUNCTION OF A HIGH DOSE RATE BRACHYTHERAPY REMOTE AFTERLOADER DEVICE The RSO at the Rapid City Regional Hospital reported a malfunction of a high dose rate brachytherapy remote afterloader manufactured by Nucletron - Old Delft (Headquarters in Maryland). The unit was a Microselect V-2 with 18 channels. While treating a patient, the source had been deployed successfully through 16 channels. When attempting to deploy the source into the 17th channel, an alarm was received indicating a problem and locked-out the source in its safe shielded position. Attempts to correct the problem were unsuccessful and the treatment was terminated. No excess exposure resulted from the problem. A service representative from Nucletron serviced and repaired the device on January 7, 2005. The "Flag" wire on the device was determined to be broken and the "V" block was replaced. The device flag is a component that monitors the position of the source and will lock out the device when it does not respond properly. It was noted by the RSO that the device had been in service for about 5 years without any problem of this nature. This problem was discussed with NRC Region 4 inspector (Rick Munoz) on 7/13/05 during a routine inspection of the hospital. Additional discussions were conducted with NRC HQ (Greg Morell) on 7/19/05. The hospital RSO will followup this verbal notification with a written report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | SD | HOS |  | 21.21 |  |  |  | 0 | 2005-07-19
41852 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-07-19 03:45 | 2005-07-19 10:53 | 2005-08-05 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "On 7/19/05 at 0345, maintenance technicians were performing a voltage check during an I&C surveillance when a lead slipped, making inadvertent contact within the panel. This resulted in shorting of a power connection and blowing a fuse. This fuse supplied initiation and trip logic components associated with the High Pressure Coolant Injection (HPCI) system, the 'A' Core Spray system, and the 'A' Residual Heat Removal (RHR) system. Loss of the HPCI system is reportable under 10 CFR 50.72(b)(3)(v) as a loss of a single train safety system required to mitigate the consequences of an accident. "Hope Creek entered Technical Specification (TS) 3.0.3 for HPCI inoperability with one Core Spray and one RHR system inoperable. Actions to replace the fuse and restore operability of the HPCI system were completed at 0909 on 7/19/05, allowing exit from TS 3.0.3. Actions to commence staffing for a shutdown and implement required procedures were implemented, however a power reduction was not initiated based on successful restoration. "The remaining retest activities associated with fuse restoration were completed for the 'A' Core Spray Loop and the 'A' RHR system at 0923 on 7/19/05, clearing the remaining Limiting Conditions for Operation associated with the fuse failure. No additional Emergency Core Cooling Systems or safety related equipment was inoperable during this time period." The licensee notified the NRC Resident Inspector and Lower Alloways Creek Township. * * * UPDATE PROVIDED BY DARON ZAKARIAN TO JEFF ROTTON AT 1331 EDT ON 08/05/05 * * * "Event # 41852, which was made by Hope Creek on July 19, 2005, at 1053, is being retracted. "Although HPCI was declared inoperable in accordance with the instrumentation Technical Specification due to the instrumentation that was inoperable as a result of the blown fuse, a subsequent review of the HPCI control circuitry determined that HPCI remained capable of automatically performing its safety function in response to any event for which it is credited. Since HPCI was able to perform its safety function, it is not reportable in accordance with 10 CFR 50.72(b)(3)(v) and this notification can be retracted." The licensee will notify the NRC Resident Inspector. Notified the R1DO (Gray). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-07-19
41851 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2005-07-19 02:00 | 2005-07-19 09:42 | 2005-07-19 | LOSS OF EMERGENCY SIREN POWER On July 19, 2005, at approximately 0650 hours, it was determined that of all of the Indian Point Energy Center emergency sirens were out of service and had been out of service since approximately 0200 on July 19, 2005. This results in a degraded emergency siren notification system which is reportable under 10 CFR 50.72(b)(3)(xiii). Both Units 2 and 3 were at 100 percent power and remain at 100 percent power. The loss of sirens was caused by a loss of power to the main radio transmitter. The loss of normal power is still under investigation. The loss of emergency backup occurred when the non-safety related backup diesel tripped. The transmitter remained operable on the backup battery supply until it was expended. Immediate corrective action was completed at approximately 0745 by restoring backup battery power and verification of system operability, (two sirens remain inoperable). Availability of battery power will be assured until corrective action to restore normal power is complete. The loss of the [non-safety related backup] diesel is being investigated. The emergency plan has route alerting and public radio announcements available as necessary to notify the public in lieu of the non-operational sirens. The counties and state were notified of the loss of sirens and restoration. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-07-19
41850 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-07-18 11:30 | 2005-07-18 15:53 | 2005-07-18 | ELECTRICAL ALIGNMENT RESULTS IN SINGLE FAILURE VULNERABILITY "Event: Keowee Hydro Station provides emergency power to the three Oconee units via two independent emergency power paths designated as the Overhead Path and the Underground Path. Either of the two Keowee Hydro Units (KHU) can be dedicated to either path, and Keowee Operations rotates which unit is aligned to which path, nominally on a monthly basis. On 7-18-05, as part of a corrective action from a previous event, Oconee reviewed power configurations for Keowee components/circuits with alternate power sources and discovered an alignment which presented a single failure vulnerability which could impact both paths. "A review of Keowee Operating Procedures revealed that KHU-1 was designated as the normal source for control relays associated with the overhead path regardless of which unit was aligned to the underground path. KHU-1 was currently aligned to the underground path. It was determined that a postulated single failure of that DC power source would prevent KHU-1 from starting (which would affect the underground path) and would also prevent the main output Air Circuit Breakers from closing in the overhead path. "As a result, Operations declared entry at 1130 hours [EDT] into Technical Specification (TS) 3.8.1 condition C for the Overhead power path being inoperable (a 72 hour allowed completion time). A review of available information indicates that this condition has existed whenever KHU-1 was dedicated to the underground path. This condition is being reported as an unanalyzed condition per guidance in NUREG 1022 section 3.2.4. "Initial Safety Significance: The postulated single failure has not occurred. If the postulated single failure occurred during a design basis event, it is expected that, without credit for Operator intervention, both KHUs would fail. Operations would have been able to realign the KHU-2 to the Underground path and/or to have started and aligned a combustion turbine at Lee Steam Station. Such actions would be adequate for LOOP and station blackout scenarios, but would not be adequate for LOCA/LOOP scenarios. Therefore, the potential single failure condition being reported could have potentially resulted in a loss of safety function. "Corrective Action(s): The immediate corrective action was to realign the affected DC control circuit power source to KHU-2, which was aligned to the overhead Path. The TS condition was exited at 1200 hours [EDT] when this realignment was complete." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2005-07-18
41849 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-07-18 08:30 | 2005-07-18 12:52 | 2005-07-18 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGES The State provided the following information via email: "At 0830 on July 18, 2005, [NAME DELETED], RSO for the licensee called to report that two model MC-3 gauges (each containing nominally 10 mCi of Cs-137 and 50 mCi of Am-241) were stolen from the secured temporary job storage site in Yucaipa, CA . There were three gauges at this site, but the model MC-1 gauge (an older gauge) was not taken. The licensee last saw these gauges when the job-site was shut down for the weekend, approximately 1700 on July 15, 2005. This morning [07/18/05], in preparation for returning to work, it was noted that two gauges were missing at approximately 0630-0700 hours [PDT]. The RSO is in transit to the job-site, to meet the local police, and will provide more details as he gets them. The licensee intends to post a reward in the Press-Enterprise newspaper in the Riverside area." State 5010 Report No.: 071805 * * * UPDATE FROM STATE (GREGOR) TO M. RIPLEY 1839 EDT 07/18/05 * * * The State provided the following information via email: " The window in which the gauges were stolen was 7/16-18/05 instead of 7/15-18/05 as indicated on our form. Also, we have been informed that there was other construction equipment stolen in addition to the two gauges. We have been informed in the past by law enforcement in the area that there is a ring who apparently raids construction sites stealing construction materials for resale in Mexico. Don't know if this is the situation in this case." Notified R4 DO (L. Smith), NMSS EO (Dan Gillen), TAS and Mexico CNSNS (email) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-07-21
41848 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2005-07-18 09:52 | 2005-07-18 11:15 | 2005-07-18 | AUTOMATIC REACTOR SCRAM "Unit 1 reactor automatically scrammed at 09:52 as a result of an RPS Actuation following a main turbine trip caused by unit protection relaying. All control rods inserted. The plant is stable. No ECCS or SRV actuations occurred. This report is made pursuant to 50.72(b)(2)(iv)(B). An investigation into the cause is currently in progress." The plant is currently stable in mode 3. No safety relief valves actuated. The current decay heat removal path is normal feedwater to the reactor steaming through the turbine bypass valves to the condenser. No other safety systems actuated. Electric power to the safety busses was supplied via normal offsite power. No bad weather conditions are present. Current reactor pressure is 900 psi with temperature at about 540 degrees. Currently troubleshooting is ongoing to investigate the cause of the trip. The licensee currently plans to stay in mode 3 until the investigation is complete. No safety related systems are currently out of service. There was no estimated restart date. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-07-18
41847 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-07-17 22:31 | 2005-07-18 00:18 | 2005-07-18 | UNANALYZED CONDITION OF MAINTENANCE BUS TIE BREAKERS "During review of 10CFR50 Appendix R, III.G.2 compliance, it was discovered that a fire in a divisional switchgear room affecting maintenance tie breakers 64T or 65T, may result in the opposite division diesels [tripping]. The postulated fire could affect cables associated with a maintenance tie breaker which could in turn cause associated bus tie breakers in the opposite division to close (B9, C9, E9, F9). The III.G.2 scenario would also include a Loss of Offsite Power event which would require the [Emergency Diesel Generators] (EDG's) to be running. Postulating multiple hot shorts could result in both 9 breakers in a single division closing and paralleling the EDG's out of synch resulting in potential damage to the EDG's. "Compensatory action: Eliminated this failure mechanism by racking out the four tie breakers (B9, C9, E9, F9) that could be affected. This does not affect operability of the EDG's." The licensee notified the NRC Resident Inspector. | 74 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-07-18
41846 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-07-15 09:22 | 2005-07-15 16:26 | 2005-07-15 | FITNESS FOR DUTY A non-licensed employee supervisor was determined to be under the influence of alcohol during a random fitness-for-duty test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2005-07-15
41845 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2005-07-15 10:30 | 2005-07-15 12:33 | 2005-07-18 | ENVIRONMENTAL EVENT - UNUSUAL FISH KILL "Unusual fish kill on both unit's intake trash racks. Approximately 80-100 Skate (Cow Nosed Rays) dead on intake racks. The apparent cause was low oxygen levels in the bay water. This event appears to be an unusual environmental event per CCNPP's NPDES permit paragraph N, page 12 for impingement. This event is reportable per Tech Spec Appendix B Section 4.1 for significant environmental events." The licensee contacted the Maryland Department of the Environment. The licensee will notify the NRC Resident Inspector. * * * * UPDATE AND CORRECTION FROM K. ALLOR TO M. RIPLEY 1415 EDT 07/18/05 * * * * "Update: Unusual fish kill on both unit's intake trash racks. Approximately 80-100 Skate (Cow Nosed Rays) dead on intake racks. The apparent cause was low oxygen levels in the bay water. This event initially appeared to be an unusual environmental event per CCNPP's NPDES permit paragraph N, page 12 for impingement. Upon further review, the unusual environmental event threshold was not met since the fish kill was not substantial enough to cause a modification to plant operations. This event is reportable per Tech Spec Appendix B Section 4.1 for significant environmental events. "Correction: The Maryland Department of the Environment notification will follow within 30 days per the NPDES permit [and therefore being reported per 50.72(b)(2)(xi), Offsite Notification, by the licensee]." The licensee notified the NRC Resident Inspector of this update. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  |  | 50.72(b)(2)(xi) |  |  | 0 | 2005-07-15
41844 | -1 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2005-07-14 16:10 | 2005-07-14 20:43 | 2005-08-16 | STATION BLACKOUT TEMPERATURE ANALYSIS HIGHER THAN RCIC GOVERNOR DOCUMENTATION "During fact gathering in response to an NRC inspection inquiry, it was determined that documentation does not exist that demonstrates that the Reactor Core Isolation Cooling (RCIC) Electronic Governor Module (EGM) would be able to operate during the required Station Blackout (SBO) coping mission time at the postulated post SBO RCIC room temperature of 206.4F. Current documentation supports operation up to 150F. "The EGM is a skid-mounted module that provides speed control signals for the RCIC Woodward Governor. Failure of the EGM would result in a loss of speed control for the RCIC turbine. This could result in an overspeed, underspeed or no change condition. Overspeed of the turbine would result in a mechanical overspeed trip. This device is not in the EQ program but is Augmented Quality. "RCIC continues to perform its Technical Specification required functions as defined in the Bases of Technical Specification (TS) 3.5.3. The TS function is to respond to transient events by providing makeup coolant to the reactor. The RCIC Room temperatures for the postulated TS transient events is less than the currently documented component qualification temperature. The RCIC is not an ESF system and no credit is taken in the safety analysis for RCIC system operation but is retained in the TS based on its contribution to the reduction of overall plant risk per Criterion 4 of 10 CFR 50.36. The RCIC system design requirements ensure that the criteria of 10CFR50 Appendix A, GDC 33, are satisfied. "Due to the lack of supporting documentation for the EGM, the beyond design basis regulatory SBO rule requirements of 10 CFR 50.63 may not be met. This condition could potentially result in an unanalyzed condition that could significantly degrade plant safety and is therefore reportable under 10 CFR 50.72(b)(3)(ii). "An analysis of the RCIC Room Heat Up Rate calculation is being performed as there are conservatisms built into the calculation that when removed will result in a lower temperature than 206.4F. Additional actions in progress include, establishing appropriate protected pathways to minimize the potential for a Loss Of Off-Site Power which could result in a SBO, performance of temperature qualification testing at SBO temperatures for the EGM, and performance of an extent of condition review for remaining RCIC components to ensure temperature qualification is met for the SBO rule. In parallel with temperature qualification testing, a modification to relocate the EGM to an area outside the RCIC room that has a lower SBO profile temperature is being pursued in the event that temperature qualification is not successful." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM D. COVEYOU TO W. GOTT AT 1427 EDT ON 8/16/05 * * * "A 8-hour notification was made on July 14, 2005, in accordance with 10 50.72(b)(3)(ii)(B), Unanalyzed condition. The report was made because documentation did not support the continued operation of Reactor Core Isolation Cooling (RCIC) Electronic Governor Module (EGM) during the required Station Blackout (SBO) coping mission. "Since the initial report, the post SBO room heatup calculation was evaluated and determined that the decay heat removal function during the SBO coping mission was met. The decay heat removal function during SBO coping period is achieved by either High Pressure Core Spray (HPCS) or RCIC systems. In addition, the other RCIC functions (i.e., Remote Shutdown, and Safe Shutdown Fire) were evaluated and determined to be met. Since the RCIC functions and the decay heat removal and vessel inventory functions during the SBO coping mission were maintained, the plant was not in an unanalyzed condition and this issue is not reportable. "Since the condition is not reportable EN 41844 is retracted. "The licensee notified the NRC Resident " Notified R3DO (K. O'Brien) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-07-14
41843 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-07-13 21:50 | 2005-07-14 17:04 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FIRE ALARM COMMUNICATION SYSTEM FAILURE "On Wednesday, July 13, 2005, at approximately 9:40 pm, NPD established a storm watch for the facility criticality alarm system during a violent thunderstorm. At approximately 9:50 pm, a lightning strike at the Mt. Athos facility activated the criticality monitoring system and damaged the fire alarm system. "Storm watch procedures were in place and personnel were evacuated to a safe location. After repairs were complete, at approximately 1:00 am, during functional testing of the [DELETED] criticality alarm system, a power surge occurred. Tests indicated that while the [DELETED] facility safety alarms were functional, communications from the alarm panel, which includes the fire alarms to the NPD [DELETED] Alarm Station [DELETED], were lost. It is uncertain whether the lightening strike or the power surge damaged the communications capability. "By 9:00 am on July 14, 2005 the system was repaired and fire detection was functional." "Evaluation of the Event: "10 CFR 70.50(b)(2) states that the NRC must be notified of an event within 24 hours followed by a 30-day written report if the following condition is met. An event in which equipment that meets all of the following three conditions is disabled or fails to function as designed: [10CFR70.50(b)(2)] "(1) The equipment is required by regulation or license condition to prevent releases exceeding regulatory limits, to prevent exposures to radiation and radioactive material exceeding regulatory limits, or to mitigate the consequences of an accident and "(2) The equipment is required to be available and operable when it is disabled or fails to function; and "(3) No redundant equipment is available and operable to perform the required safety function. "License SNM-42, Chapter 1, Section 1.9.2 requires that: 'Fire detectors be installed and maintained in controlled areas. These detectors will alarm in the continuously manned NPD [DELETED] alarm station.' The system malfunction prevented the [DELETED] controlled area fire detection from alarming in the NPD [DELETED] alarm station. "Evaluations have been performed to determine that the fire detection system in this area is not an IROFS and that regulatory limits will not be exceeded by a fire. "The equipment was required to be available and operable when it failed to function. Also, redundant equipment was not available; however, compensatory measures were utilized. Radiation Protection personnel were dispatched to monitor the local alarms and system activations. Compensatory measures [personnel at the local alarm panel] were in place by approximately 1:00 am. "Notification Requirements "The event is reportable due to: "Although the fire system monitoring is not an IROFS, it is required by the license to mitigate the consequences of an event in a controlled area. Also, it was required to be functional when the communications loss occurred and a redundant system was not available to perform the required safety function. Based on this, notification is required to the NRC within 24 hours followed by a 30-day written report. "Status of Corrective Actions: "The system has been repaired, tested, and is functioning properly. A new surge protector will be installed on the Honeywell System when it is received." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
41842 | 0 | GLOBAL X-RAY & TESTING CORP |  |  |  |  | 2005-07-14 08:45 | 2005-07-14 16:42 | 2005-07-14 | RADIOGRAPHY CAMERA SOURCE TEMPORARILY STUCK Radiography was being performed on an offshore pipeline aboard the pipe lay barge "American Horizon" at Mustang Island 746/726. The source failed to return to the camera after an exposure. The Radiation Safety Officer (RSO) was dispatched to the barge and was able to retrieve the source and return it to the camera. The RSO picked up 35 milliRem during this evolution. It is suspected that the source wire was broken. The camera and source are being returned to the manufacturer for inspection and repair. Camera: AEA Technology model 880D Serial number D1644 Source model A424-9 Source serial number 22601B Source Ir-192 62.5 Curies | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | EXCESSIVE RELEASE | [8 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) | 20.2202(a)(2) |  |  | 0 | 2005-07-14
41841 | -1 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-07-13 22:45 | 2005-07-13 22:59 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * EMERGENCY DECLARED DUE TO CRITICALITY ALARMS At 2230 EDT the facility received multiple Criticality Alarms believed to be due to lightning strikes on site. The Emergency Operations Center has been activated and is in the process of staffing. Most alarms have been reset to normal. The licensee has sent teams to take local radiation readings. Local state and local agencies have been notified. The NRC Resident Inspector has been notified and is onsite. * * * UPDATE FROM POWELL TO ROTTON AT 2330 ON 07/13/05 * * * BWXT secured Alert based on surveys of affected areas being normal. * * * UPDATE FROM POWELL TO GOTT AT 0010 ON 07/14/05 * * * "Emergency has been terminated. EOC will maintain a minimal staffing for follow-up. A Post Incident Review Team has been appointed to assess the incident." * * * UPDATE AT 0026 ON 17/14/05 * * * NRC secured monitoring. Notified R2 IRC (Plisco, D. Collins), R4DO (B. Spitzberg), IRD (Wilson), NMSS (Strosnider, Gillen). Commission Staff (Castleman, Thoma, Hatchett, Piccone), EDO/EDO staff (Virgilio, Dyer, Kane, Miller), IRD (Wilson, Leach, McGinty), PAO (Brenner), DOC (Outlaw), DHS (S. York), FEMA (Dunker), DOE (Bailey), EPA(NRC) (Allison), HHS (White). * * * RETRACTION AT 0959 ON 07/15/05 FROM L. MORRELL TO W. GOTT * * * "On Wednesday, July 13, 2005, at 10:45 p.m. BWX Technologies, Inc. declared an Alert per the BWXT Emergency Plan and internal emergency procedures. BWXT contacted the NRC Operations Center to report that an Alert had been declared due to a criticality alarm that resulted from a lightning strike. The decision to declare an Alert was based on the fact that radiation indicator alarms on the criticality panel went into a high alarm and it was not immediately determined that high radiation levels did not exist. EOC personnel conservatively determined that an Alert should be declared and implemented the notification process while an evaluation into the exact cause of the alarm was implemented. Further evaluation of the situation confirmed that the activation of the alarms was not caused by high levels of radiation but by the lightning strike, which caused damage to electronic components within the alarm system. Therefore, the Alert criteria were actually not met. BWXT is requesting that the Alert declaration that was made on July 13, 2005, be withdrawn." The licensee notified the NRC Resident Inspector. Notified R2DO (P. Fredrickson) and NMSS (S. Moore). * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | VA | FUE |  | 70.32(i) |  |  |  | 0 | 2008-05-11
41840 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-06-26 15:20 | 2005-07-13 20:37 | 2005-07-26 | AGREEMENT STATE - MEDICAL SOURCES STOLEN "The theft occurred on June 26, 2005, at approximately 3:20 p.m. [The driver] had taken receipt of the cargo at the airport in Dallas (DFW), Texas, and he made the first delivery at a Cardinal pharmacy in Tyler, Texas. After the first delivery, he proceeded to the next stop, which was about one mile away. When he went to the back of the truck, he noticed that the canopy door had been pried open, but was still locked. When he looked inside, he noticed the box containing products for the Cardinal pharmacy was missing. The driver promptly notified [his] supervisor, who then contacted the Tyler Police and the Tyler Fire Department. The driver was personally interviewed that day by [Trade wind Enterprises - the shipper] and the Tyler Police Department. Efforts were made to locate the missing cargo, but police and the driver have been unable to locate the cargo or identify the person or persons involved in the theft. "The materials stolen consisted of 6 boxes of sodium iodide capsules [I-123]." The activity in the missing capsules was 6.8 milliCuries." Police Report case: 1-05-029925 * * * UPDATE P. EGIDI TO P. SNYDER ON 7/26/05 AT 1656 * * * The State provided the following information via facsimile: "Material found. Issue closed." R4DO (Graves) and NMSS EO (Giitter) notified. E-mailed to TAS (Hahn) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-07-18
41839 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-07-09 09:36 | 2005-07-13 17:06 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SMALL FIRE IN WASTE (CALCINER) FURNACE The [DELETED] calciner was loaded with low-level contaminated scrap materials. The door gasket had a small leak and the operator attempted to stop the leak. This inadvertently caused an increase in the leakage. Air contacted the hot gases leaking from the calciner and the gases were ignited. No IROFS were degraded or failed. There was a brief flame in enclosure [DELETED] from the calciner door. A prefilter in the vent duct caught fire, the HEPA filter was damaged and part of the vent duct melted. Immediately following the event, the calciner was shutdown. There were very small potential consequences due to the fact that containment was not lost. No elevated airborne, surface contamination, or effluent radioactivity levels were detected. There were no actual health and safety consequences. The equipment is still shut down pending completion of the investigation. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2008-05-11
41838 | 0 | ENGINEERING CONSULTING SERVICES |  |  |  |  | 2005-07-13 15:30 | 2005-07-13 16:28 | 2005-07-13 | DAMAGED MOISTURE DENSITY GAGE A CPN moisture density gage was run over at a job site. The source was retracted during the event. There is damage to the handle . The sources are intact (0.4 mR/hr @ 1 meter). The gage is being sent to the manufacturer for repairs. Serial number: ND90404949 Model number: MC1DRP Sources: Cs-137 10 milliCurie Am-241:Be 50 milliCurie | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2005-07-13
41837 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2005-07-13 09:17 | 2005-07-13 13:03 | 2005-07-14 | TURBINE TRIP/REACTOR TRIP "On July 13, 2005, at approximately 0917 hours, Unit 1 received a Reactor Protection System (RPS) trip and a Main Turbine trip. All control rods fully inserted into the core. Plant response to the reactor shutdown resulted in a reactor coolant level transient that caused a Low Level 2 signal and subsequent High Pressure Coolant Injection (HPCI) system initiation. The HPCI system started but did not inject into the vessel because reactor coolant level was already recovered by the Reactor Feedwater system. Proper operation of the RCIC system has not been conclusively determined. Both Reactor Recirculation pumps tripped, as expected, from the low reactor coolant level and high pressure transient. "Additionally, primary containment isolation system actuation signals for valve groups 2, 3, 6, and 8 were received and the valves, that were open, closed as required. The Reactor Building Ventilation System isolated and both trains of the Standby Gas Treatment (SBGT) System automatically started and operated successfully. "The RPS trip was reset and the HPCI turbine secured. Both trains of the SBGT system were secured. At 1119 hours, the plant exited the scram recovery procedure and entered General Plant Operating procedure 0GP-05, "Unit Shutdown." Investigation into the cause of the RPS and Main Turbine trip is still in progress. "The plant is currently in Mode 3 (i.e., Hot Shutdown) and activities are in progress to transition to Mode 4 (i.e., Cold Shutdown). The resident inspector has been notified. "INITIAL SAFETY SIGNIFICANCE EVALUATION "The initial safety significance of this condition is considered to be minimal. The plant responded as designed to the transient, with the exception of the verification of RCIC system performance, and the plant was safely shut down. "CORRECTIVE ACTIONS "An event investigation team has been assembled to determine the cause of the event. Plant response to the event is being evaluated and identified issues will be addressed prior to plant restart." During the transient, four safety relief valves lifted and reset. The plant is currently in a normal shutdown electrical lineup. Reactor vessel level is being maintained using normal feedwater. The bypass valves are available for cooldown. There was no effect on unit-2. * * * UPDATE FROM LICENSEE TO ABRAMOVITZ AT 1741 ON 7/14/05 * * * "On July 13, 2005, at approximately 0917 hours, Unit 1 received a Reactor Protection System (RPS) trip and a Main Turbine trip. All control rods fully inserted into the core and the plant safely shut down. A non-emergency notification (Event Number 41837) was made to the NRC Operations Center at 1303 hours. This follow-up notification discusses plant recovery from the Unit 1 event. "After investigation team review of plant data, it was determined that the RCIC system performed appropriately (i.e., was not required to start) in response to the reactor coolant level transient. Reactor coolant level decreased to near, but did not exceed, the RCIC System actuation instrumentation setpoint. The investigation team determined that the direct cause of the RPS/Main Turbine trip is the shorting to ground of one phase of the Unit 1 Main Generator No-Load Disconnect Switch, which electrically connects the generator to the Main Transformer. The switch grounding caused a generator ground fault that resulted in a backup generator lockout and fast closure of the turbine control valves. Fast closure of the turbine control valves provided the trip input to the RPS. "Unit 1 is now making preparations to go to mode 4, cold shutdown. Unit 1 and Unit 2 are currently in Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1 'AC Sources - Operating,' for one of two required Unit 1 offsite AC circuits inoperable. The resident inspector has been notified. "CORRECTIVE ACTIONS "Further testing of RCIC System Low Reactor Level actuation instrumentation will be performed to further verify satisfactory RCIC System performance during the event. Activities are in progress to address the damaged No-Load Disconnect Switch and to determine the cause of the switch failure." Notified the R2DO (Fredrickson). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-07-13
41836 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-05-17 00:42 | 2005-07-12 16:42 | 2005-07-12 | INVALID ACTUATION OF THE "B" RESIDUAL HEAT REMOVAL (RHR) PUMP. "July 12, 2005 Telephone Report in Accordance with 10 CFR 50.73(a)(2)(iv)(A) Invalid Actuation of the "B" Residual Heat Removal (RHR) Pump. "SPECIFIC TRAINS AND SYSTEMS THAT WERE ACTUATED "During a maintenance activity involving replacement of a safeguards relay, "B" Train RHR Pump 2P-10B was started inadvertently. The RHR pump is part of the emergency core cooling system (ECCS). "DESCRIPTION OF WHETHER EACH TRAIN ACTUATION WAS COMPLETE OR PARTIAL "On May 17, 2005, Unit 2 was in a shutdown condition (MODE 6) for routine refueling outage. At approximately 0042, Unit 2 RHR Pump 2P-10B was inadvertently started. Since RHR Pump 2P-10A had already been running for normal shutdown decay heat removal, the inadvertent start of the B RHR pump resulted in both RHR pumps running. Operations observed an increase in RHR flow but initially attributed the flow change to the RHR Heat Exchanger (HX) Bypass Flow Control Valve, which was operating in automatic. "At the time of the inadvertent pump start, technicians were landing a wire as part of performance of a procedure to replace a safeguards relay. During this activity, the technicians heard a breaker close in the 480 VAC safeguards bus. Primary Plant Computer System (PPCS) computer data indicates that this breaker closure corresponded to the 2P-10B RHR Pump start. The technicians were not aware that this breaker closure was caused by their activity. The inadvertent RHR pump start was identified at 0525. "The investigation of this event determined that a current path was created during the relay replacement, which caused starting of 2P-10B. No other ECCS components were actuated during this event. A review of the activity could not determine the specific wire that was lifted landed to cause the pump start. Rather several wire combinations were noted, each of which could have caused what is commonly referred to as a 'sneak' current path. These current paths can result in the RHR pump starting circuit being energized. "DESCRIPTION OF WHETHER OR NOT THE SYSTEM STARTED AND FUNCTIONED SUCCESSFULLY "This event was not safety significant. The RHR pump started and functioned successfully. The RHR pump was the only ECCS component in the system affected. Since the pump was aligned in the standby mode to provide normal decay heat removal cooling, its start appropriately resulted in additional cooling flow being pumped to the reactor core. The RHR pump was secured and returned to standby mode following discovery of this condition. "As corrective action, a procedure change was initiated to add a precaution statement to ensure the associated safeguards relay cabinet is deenergized to the extent possible prior to similar maintenance activities to prevent inadvertent safeguards actuations. This item is documented in the PBNP corrective action process system (CAP 064616)." The NRC Resident Inspector was notified of this event report by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-07-12
41835 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-06-29 | 2005-07-12 14:49 | 2005-12-19 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVER EXPOSURE The State provided the following information via email: "Texas Radiation Control received a telephone call from [the licensee's RSO] . The RSO was contacted by Landauer regarding an exposure to a 'film badge' in excess of 1,000 (one thousand) rads. "The badge was being worn by [name deleted]. His exposure for the previous quarter was 350 millirem and for 2004 he received a total exposure of 290 Mr. The badge had been returned for evaluation with 4 other badges, which had no problems with excessive exposure. "[The individual] only performed four tracer study jobs during the monitoring period and worked with a 34 mCi Ir-192 source. [The RSO] believes the badge was not worn. The licensee will be requesting the exposure be deleted. "Texas Incident Investigation Program has contacted the licensee and requested additional information. A written report will be submitted within 30 days. The Event has received no media attention." Texas Incident No.: I - 8242 ***** UPDATE ON 12/19/05 AT 1830 EST from Latischa M. Hanson (via e-mail) entered by MacKinnon ****** "The licensee believes that the badge worn by (name deleted) during the first quarter of 2005 was intentionally exposed. The licensee states that the reported dose was in excess of the reporting capabilities of 1000 rad & concluded that the reported dose was not accurate. The licensee reported that (name deleted) terminated employee at the end of the first month of the quarterly monitoring period & that the employee worked with sealed sources during the first week & radiation work was performed afterward until time of termination. All jobs were short duration & neither the individual nor his single co-worker (supervisor) reported any unusual occurrences that would have resulted in a higher than normal dose. Based on the amount of the extremely high dose, the licensee concluded that the employee was not the recipient of 1000 rem (rad) dose & that the dose should be considered erroneous. Permanent dose record for (name deleted) reported by the licensee is as follows: 1st quarter 2005 - 0.349 rem; 2nd quarter 2005 - 0.100 rem. Licensee corrective action: "No corrective actions taken or planned since reported dose appears to be incorrect. The licensee has calculated a dose of 0.100 rem for the 2nd quarter & consequently assigned this to (name deleted) permanent personnel monitoring record. This is based on the individual's previous cumulative six-month period dose of 0.593 rem, which averages to (approx) 0.100 rem/month." R4DO (Shaffer) & NMSS EO (Essig) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-07-15
41834 | 0 | MEDTRONIC |  |  |  |  | 2005-06-16 12:00 | 2005-07-11 15:14 | 2005-07-11 | STOLEN AIR IONIZER CONTAINING A GENERAL LICENSED POLONIUM-210 SOURCE Between June 16th and the 22nd a 10 millicurie Po-210 air ionizer was stolen from their facility. Medtronic alerted their security and filed a Police report on the stolen Po-210 air ionizer. The Model number of the air ionizer is P2021-8000 and the serial number is A2EM605. On June 15, 2005 Medtronic received the air ionizer from NRD located in Grand Island, NY (The air ionizer is leased through NRD). Medtronic stated that all future devices will be stored in a locked cabinet. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-07-11
41833 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-05-02 | 2005-07-11 10:00 | 2005-07-11 | AGREEMENT STATE REPORT INVOLVING A POTENTIAL EXTREMITY OVEREXPOSURE The following information was received via facsimile: "A radio pharmaceutical worker received an extremity dose for 2004 of 51 Rem according to her ring badge. 20 Rem of this dose occurred on April 26 - May 2. The licensee thought this may have been an erroneous reading so this is currently considered a potential extremity overexposure until further investigation." The radiation source is described as mostly Tc-99m with a dose received to the left ring finger of 51050 mRem. The time and date of discovery for this event was 1100 hours on 7/7/05. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-07-14
41832 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2005-07-10 03:18 | 2005-07-10 06:42 | 2005-07-10 | TURBINE TRIP RESULTING IN RPS ACTUATION AND AUTOMATIC REACTOR SCRAM "This non-emergency 4-hour and 8-hour report is pursuant to 10CFR50.72(b)(2) and 10CFR50.72(b)(3). On 7/10/05 at 0318 hours, Unit 2 experienced a turbine trip and subsequent reactor scram. An RPS actuation occurred, as expected, following the turbine trip. RPS responded normally and reactor power is 0%. Reactor water level went below 1 inch, as expected, following a reactor scram from 100% power. At a reactor level of less than 1 inch, PCIS Group 2 and 3 isolations occurred. Reactor water level has been restored above 1 inch to the normal level using the normal reactor feedwater system. All safety systems responded as designed. "An investigation is in progress to determine the cause of the turbine trip and to initiate appropriate corrective actions." During the scram the RCS experienced a high pressure condition which caused both recirculation pumps to trip and 3 SRVs to lift and reseat. The licensee is presently depressurizing primary system in order to restart one of the recirculation pumps. Current RCS parameters: Pressure - 320 psig; Temperature - 428 F; and Level - +23 inches. All rods fully inserted. Prior to the turbine trip the licensee was conducting a routine weekly "Mechanical Trip Valve Test." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-07-10
41831 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-07-09 22:54 | 2005-07-10 01:20 | 2005-07-10 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO INOPERABLE EP SIRENS "At 2154 hours on July 9, 2005, power was lost to the #11, Otter Creek and #12, Jacob's Creek Emergency Plan Sirens. At 2254 hours on July 9, 2005, the #11 and #12 sirens are still without power. Siren #4, WC Lake South, was previously determined to be inoperable at 1210 hours on July 6, 2005, due to being struck by lightning. With 3 of the 11 Emergency Plan sirens out of service for greater than 1 hour a major loss of emergency assessment capability exists. "Lyon Coffey Electric is currently working to restore power to the #11 and #12 Emergency Plan sirens. "The NRC Senior Resident Inspector has been notified. "At 2359 hours power has been restored to the #11 and #12 sirens restoring emergency assessment capability." The licensee contacted the dispatcher at the LLEO as an informational call. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-07-10
41829 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-07-08 19:15 | 2005-07-08 22:49 | 2005-07-08 | STARTUP TRANSFORMERS DECLARED INOPERABLE BASED ON POTENTIAL UNDERVOLTAGE CONDITION "PTN (Turkey Point) received a notification from System Operations that switchyard voltage limits (based upon System Operations Contingency Analysis) was forecasted to exceed switchyard voltage limits if Unit 3 had tripped. This condition existed from 1434 to 1448 on July 8, 2005. "At 1915 on July 8, 2005, PTN determined that both Unit 3 and 4 Startup Transformers were inoperable at 1434 on July 8, 2005, and entered Technical Specification 3.8.1.1 action e. This action was to notify the NRC within 4 hours; and to restore at least one of the inoperable Startup Transformers to OPERABLE status within 24 hours. At 1448 on July 8, 2005, both Startup Transformers were declared OPERABLE and PTN exited Technical Specification 3.8.1.1 action e." The licensee stated that the potential for low grid voltage at the Turkey Point Nuclear Plant was based on offsite conditions and was a postulated condition. Low voltage conditions did not actually occur. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | FL | POW | [5 empty] | 0 | 2005-07-08
41828 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-07-08 09:15 | 2005-07-08 16:20 | 2005-07-08 | OFFSITE NOTIFICATION RELATED TO IMPROPERLY PACKAGED RADIOACTIVE WASTE MATERIAL SHIPMENT "At 09:15 CDT Cooper Nuclear Station was notified by Chem Nuclear Limited Liability Company (LLC) of Barnwell South Carolina waste disposal site, of a condition discovered during the off loading of the first Trans Nuclear Radioactive Material (TN RAM) shipping cask (#05-10). This shipping cask was utilized for the shipment of the first TN RAM liner from the current fuel pool cleanup project. Per conversation with the Chem Nuclear LLC representative a small 1/4" by 1/4" piece of metal debris was discovered between the outer wall of the inner TN RAM liner and the interior wall of the TN RAM cask. This was discovered after the inner liner was off loaded into the disposal trench. The radiation level of this debris was 70 R/hr contact. The debris was removed from the TN RAM cask interior and placed in a 30 gal drum for temporary storage. Barnwell has requested a decision from NPPD on the disposal of this item. There were no violations of the DOT limits specified for the external dose rates of the TN RAM cask during the CNS Shipment. "Cooper Nuclear Station representatives are being sent to Barnwell, South Carolina to assist in the determination of the cause and appropriate corrective actions. "This is a potential violation of the Department of Health and Environmental Controls (DHEC) of the State of South Carolina acceptance criteria for unpackaged material outside of a disposal liner. This was also a potential violation of the Certificate of Compliance for the NRC Certified Type B TN RAM Cask. "This is being reported per 10 CFR 50.72(b)(2)(xi) since Chem Nuclear LLC has notified DHEC of the State of South Carolina." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-07-08
41827 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-07-06 | 2005-07-08 15:45 | 2005-07-08 | WISCONSIN AGREEMENT STATE REPORT - MEDICAL EVENT The State provided the following information via email: "On July 6, 2005, a brachytherapy procedure to treat a bile duct carcinoma using 22 iridium-192 sources totaling 53.9 milliCuries in a ribbon with spacing of 0.5 centimeter between each source was performed. The ribbon was routed through the nasal gastric system to the treatment site (bile duct). A radiograph was taken of the source placement in the bile duct before releasing the patient to a hospital room. The radiograph verified the sources to be in the prescribed location. "On July 7, 2005, a verification image was taken at 0850 and found that the radioactive sources had moved approximately 5 centimeters toward the gastrointestinal tract. The location of the sources was outside of the intended site. An attempt to reposition the source ribbon by the authorized user was unsuccessful. The authorized user amended the written directive and removed the sources at approximately 1300. The sources were placed in storage. "The licensee notified the department on July 8, 2005. The Wisconsin Radiation Protection Section will investigate the medical event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-07-13
41826 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2005-07-07 15:30 | 2005-07-07 15:52 | 2005-07-07 | OFFSITE NOTIFICATION RELATED TO VEHICLE ACCIDENT INVOLVING LOW-LEVEL RADIOACTIVE DEMOLITION DEBRIS This licensee reported that a flatbed truck transporting demolition debris (concrete/rebar/soil etc) from Haddam Neck was involved in a traffic accident in the State of Virginia (at mile marker 64 on Interstate 81). The material was low-level radioactive contaminated material that was shipped as DOT exempt and did not involve any reportable quantities. The shipper was RACE, LLC. The radioactive material was in an intermodal container on a flatbed truck. The truck overturned and damaged the intermodal spilling approximately a "pickup truck" full of debris. The Virginia State Hazmat team has responded to the scene of the accident. In addition, RACE has sent a team with a health physicist. No one has been contaminated. RACE will be supplying a backup intermodal and truck to transfer and transport the debris. The licensee has notified NRC Region 1 (Roberts). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-07-07
41825 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-07-07 11:52 | 2005-07-07 15:27 | 2005-07-07 | OFFSITE NOTIFICATIONS DUE TO EMPLOYEE FATALITY "On July 07, 2005 at approximately 1105 [hrs. CDT] a report was received in the Wolf Creek Generating Station Control Room of a non-work related medical emergency involving an employee. Onsite medical personnel responded and commenced first aid including CPR. An ambulance was dispatched and the individual was transported offsite to a local hospital. "Hospital personnel notified Wolf Creek personnel at 1152 that the individual had passed away. At this time no press release is planned. "OSHA has been informed of the fatality." The licensee notified the NRC Senior Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-07-07
41824 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-07-07 10:17 | 2005-07-07 12:51 | 2005-07-07 | LICENSE CONDITION REPORT DUE TO EXCEEDING TECHNICAL SPECIFICATION INOPERABILITY TIME "FPL Energy Seabrook Station has discovered that a condition existed that was prohibited by the Technical Specifications. The Train B Containment Building Spray Pump (CBS) was inoperable for a period of time longer than permitted by the Technical Specifications. A failed relay driver board would have prevented the Train B CBS pump from automatically starting in response to high containment pressure. Following an LOP coincident with a high containment pressure, the initial start signal from the Train B EDG emergency power sequencer would not have initiated a CBS pump start, but an automatic start signal generated at a later time in the LOP sequence would have started the pump. The failed relay driver board only inhibited automatic starting of the Train B CBS pump. The Train B EDG remained capable of providing power to other Train B loads including the automatic start of the CBS pump at the later sequence. "This event is being reported in accordance with Seabrook Station Operating License condition 2.G as a failure to operate the facility in accordance with the Technical Specifications." The licensee discovered the condition during surveillance testing and the condition has been repaired. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2005-07-07
41823 | 0 | H AND G INSPECTION COMPANY |  |  |  |  | 2005-06-02 | 2005-07-06 15:15 | 2005-07-06 | PERSONNEL OVEREXPOSURE The dosimeter (film badge) for a dismissed employee at H and G Industrial Company, an industrial radiographer, was read and indicated 1000 Rads exposure. 1000 Rads is the maximum dose this type of dosimeter can read. The employee was dismissed on 06/02/05. The dosimeter was sent for reading on about 06/17/05 and the readings were reported today 07/06/05. The employee was contacted and has agreed to take a blood test. The employee shows no signs of receiving this amount of exposure. The employee thinks that another employee took his dosimeter and exposed it. Self reading dosimeters used for this time period indicate an exposure of 200 millirem. None of the assistants who worked with this employee received an abnormal exposure. The licensee continues to investigate. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2005-07-06
41822 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-07-05 20:30 | 2005-07-06 15:09 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SAFETY EQUIPMENT FAILURE "On Tuesday, July 5, 2005, at approximately 8:30 pm, Radiation Protection personnel discovered that the [DELETED] Alarm System was unable to detect information from the [DELETED] Honeywell alarm panel, which includes alarms for criticality monitoring and fire protection. This failure was identified when Radiation Protection personnel were performing a check of the criticality alarm system as part of a post storm watch evaluation of the alarm system. As a compensatory measure, Radiation Protection personnel were immediately dispatched to the local alarm panel at the [DELETED] to monitor the alarms. Phone and radio communications are available to alert security if any alarms or other abnormal conditions occur. "The cause of the failure is currently being evaluated. The system is currently being repaired and compensatory measures will remain in place until system is determined to be functioning." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
41821 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2005-05-12 15:48 | 2005-07-05 17:12 | 2005-07-05 | INVALID ACTUATION OF THE DIVISION 2 SHUTDOWN SERVICE WATER (SX) SYSTEM PUMP. "The following 60-day report is being made under 50.73 (a)(2)(iv)(A) for an invalid actuation of the Division 2 Shutdown Service Water (SX) system pump that occurred at 1548 hours on May 12, 2005. As allowed by 10CFR50.73(a)(1) this notification is being made via telephone. NUREG-1022, Revision 2 identifies the information that needs to be reported as follows: "(a) The specific train(s) and system(s) that were actuated. "On May 12, 2005, the Division 2 SX system pump automatically started during the performance of surveillance testing procedure, 9069.01, SX Operability, while preparing to secure the pump and restore the Plant Service Water (WS) system feed to the Division 2 SX piping. As part of the restoration of the system to its normal standby lineup, the handswitch for the 1SX014B (WS to SX cross-tie) valve was being held in the Open position while the handswitch for the Division 2 SX pump was held in the Off position. While monitoring system pressure to allow releasing the handswitch for the SX pump, system pressure had not increased above the automatic initiation setpoint when the operator's hand relaxed on the grip of the handswitch of the pump enough to allow the pump to start. The inadvertent actuation of the Division 2 SX pump was not in response to plant conditions requiring the pump to automatically start. "(b) Whether each train actuation was complete or partial. "The automatic start of the Division 2 SX pump was complete, but was limited to Division 2 only. Divisions 1 and 3 were in standby and were not affected by the opening of the Division 2 WS to SX cross-tie valve. "(c) Whether or not the system started and functioned successfully. "The automatic start of the Division 2 SX pump was a successful start and functioned successfully. "The NRC Resident Inspector was notified of this notification." | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-07-05
41819 | 0 | HOWDEN BUFFALO |  |  |  |  | 2005-05-05 16:15 | 2005-07-01 18:32 | 2005-07-02 | PART 21 NOTIFICATION OF FAILED SURFACE COATINGS ON FANS Howden Buffalo provided the following information via facsimile: "In accordance with subject regulation and Howden Buffalo internal procedures, Howden Buffalo is submitting a report of a defect or failure to comply for basic components supplied to a nuclear facility. "Duke Energy, Oconee Plant, reported insufficient adhesion of Carboline topcoat to Carboline primer, resulting in separation of the topcoat on two fans and one other fan inlet bell. The items were manufactured, painted, and supplied to Duke Oconee during the period February 2002 thru March 2002, as basic components in a nuclear safety related application. The three affected items were part of ten complete fans delivered to Duke Oconee both before and after the affected units. "Howden Buffalo conducted an initial investigation that included both Duke Power Materials Engineering & Lab Services and Carboline. Our investigation concluded that coating materials were not defective however, application of Carboline primer was not in accordance with Carboline recommendations for sufficient curing of the primer, resulting in accumulation of VOC's from the uncured primer and ultimate separation of the topcoats. "Howden Buffalo has reviewed internal plant procedures for application of Carboline primer and topcoat, including surface preparation, and found that the procedures failed to incorporate Carboline updated requirements for sufficient curing of the primer. All internal procedures are now revised to incorporate Carboline requirements in their entirety. Howden Buffalo procedures for supplying Carboline coating as a basic component were applicable during the period of October 2001 thru March 2005. Howden Buffalo is contacting each of these customers to a) advise of a potential defect in the Carboline coating, b) recommend inspection criteria, and c) provide contact information. "Summary evaluation: Review of documentation for this sales order, including all paint surveillance records, does not support a conclusion that this defect is limited only to the fans delivered for this order. Root cause of paint failure would appear to be insufficient training in procedures for surface preparation and preparation and application of primer and paint. Environmental limitations for temperature and relative humidity may not have been correctly considered for drying time requirements. Notification to NRC and to all customers of safety-related coating is required." Howden Buffalo item number: 540059-080 Reactor building cooling unit fans serial numbers 004, 005, and 006 Nature of defect: Insufficient adhesion of Carboline topcoat to Carboline primer - topcoat flaking from two fans and one fan inlet bell. Affected safety related orders: Duke (Oconee) shipped 11/2/01 Exelon (Dresden) shipped 3/28/03 Edison Material Supply (SONGS) shipped 7/28/04 Amergen Energy (Oyster Creek) shipped 10/31/02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2005-07-02
41818 | 0 | MOUNTAINSIDE HOSPITAL |  |  |  |  | 2005-07-01 12:00 | 2005-07-01 18:13 | 2005-07-02 | RADIOACTIVE SOURCES NOT REMOVED PRIOR TO SHIPMENT A Mountainside Hospital representative informed us that a nuclear medicine camera was mistakenly transported with 28 Gadolinium-153 sources inside the camera. The total source activity is 20 millicuries and the calculated source strength is approximately 2 milliRem/hr at 1 meter. The representative contacted the driver transporting the camera, who was at the Pennsylvania/Ohio border, notified him that radioactive sources were inside the camera and requested he return the camera and sources back to Mountainside Hospital. Established a conference call with R1 (George Pangburn, Pam Henderson, John White), NMSS (Bill Brach, Joe Holonich), and NSIR (Phil Brochman). *** UPDATE FROM R. SASSO TO J. KNOKE AT 14:23 ON 07/02/05 *** A Mountainside Hospital representative informed us that the camera and sources have arrived back at the hospital without incident. The licensee removed all 28 shielded sources from the camera and detected no activity on the camera or truck. This confirmed that all sources have been removed. The R1DO (White) and NMSS EO (Holonich) were notified. An update was also emailed to R1 (George Pangburn, Pam Henderson, John White), NMSS (Bill Brach, Joe Holonich), and NSIR (Phil Brochman). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NJ | HOS | [5 empty] | 0 | 2005-07-01
41817 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2005-06-30 11:05 | 2005-07-01 08:46 | 2005-07-01 | AGREEMENT STATE REPORT - LOSS OF X-RAY FLUORESCENCE SURVEY DEVICE After completing an x-ray fluorescence (XRF) survey for a client, the licensee placed the XRF device on the roof of his vehicle. The licensee left the work area and upon entering the main flow of traffic he pulled over and realized that the device was no longer on top of the roof of his vehicle. He conducted a search along the path he had traveled. The Montgomery County Fire and Rescue responded and proceeded to search the previously identified stretches of roadway and did not find the device. This incident was also reported to the Montgomery County Police Department. The Maryland Department of the Environment is investigating this incident. The lost instrument is an LPA-1 XRF (S/N 1189) device, gray in color, manufactured by Radioactive Monitoring Devices (RM3) of Watertown, MA. The radioactive source is a Cobalt-57 isotope with an activity of (12) twelve millicuries. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2005-07-06
41816 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-06-30 19:31 | 2005-07-01 00:08 | 2005-07-01 | UNANALYZED CONDITION RELATED TO THE STANDBY FEEDWATER PUMPS AND CONTROL CIRCUITS "During an NRC Triennial Fire Protection Audit the Inspector identified a fuse coordination issue between 130VDC supply circuit and breaker trip circuit fuses for the Standby Feedwater (SBFW) Pump switchgear. The coordination ratio was found to be too low to support requirements for fire related safe shutdown equipment under Generic Letter 81-12. Impacted equipment is SBFW Pumps A & B and control circuits required for Appendix R Alternative Shutdown auxiliary equipment. This event is being reported as an unanalyzed condition that significantly degraded plant safety under 10CFR50.72(b)(3)(ii)(B). "The impacted equipment has been declared inoperable and a team is currently working on design changes to change fuse sizes for the breaker trip circuit/supply circuit to meet the requirements of Generic Letter 81-12." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-07-01
41815 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-06-30 19:29 | 2005-06-30 19:49 | 2005-07-01 | PRIMARY CONTAINMENT INOPERABLE DUE TO SMALL CRACK IN TORUS The licensee has determined that the small weep hole crack in the torus (x in shape) is in a position which requires the plant to initiate a normal shutdown to cold shutdown conditions. The crack is located about 5 feet below the waterline and just below the HPCI exhaust pipe discharge. Due to the location of this crack the licensee's engineering staff showed via analysis that it would be prudent to restrict the number of thermal cycles the crack receives. The plant is in a 1 hour Technical Specification LCO shutdown action statement. At 19:50 the licensee commenced the Technical Specification shutdown to cold shutdown conditions. As an additional item, one of the four Emergency Diesel Generators was deemed inoperable at the time of the event, and continues to be in a LCO action statement. The licensee made notifications to the State and local agencies, and will notify the NRC Resident Inspector. *** UPDATE ON 06/30/05 AT 22:24 EDT FROM T. PAGE TO J. KNOKE *** "With the plant operating at 100% on June 27, 2005 during RCIC Torus Suction piping inspection per ST-24H, inspectors discovered a TORUS leak in the vicinity of a TORUS Support between Bays A and P. The leak was quantified as slight weepage with streaking and a small puddle below leak. This was captured in the plant corrective action program on CR-JAF-2005-02593. Subsequent non destructive examination determined that the leakage was from a small through wall crack. The condition was discussed with the NRC Staff at that time. Initial evaluation at that time determined that there was reasonable expectation of operability, an Operational Decision Making Instruction (ODMI) was prepared and implemented to monitor the leakage while further engineering evaluation was conducted. On June 30,2005 further engineering analysis determined that operability of the primary containment was not assured and at 19:29 on June 30, 2005 the Shift Manager declared Primary Containment Inoperable and entered Technical Specification LCO 3.6.1.1 Condition A, Primary Containment Inoperable, and declared an Unusual Event under EAL 9.1.2. Preparations were made for a reactor shutdown and the shutdown was commenced at 20:00. "At the time of the event the A Train of EDGs was out of service for a planned maintenance LCO. At this time the NRC Resident has been informed." The A Train EDG is not available nor operable if needed. The R1DO (White) and NRR EO (Carpenter) have been notified. **** UPDATE ON 07/01/05 AT 1720 EDT FROM N. AVRAKOTOS MACKINNON *** An Unusual Event was terminated at 1716 EDT due to achieving cold shutdown. R1DO (John White), NRR EO (Cynthia Carpenter), IRD Manager (M. Leach), FEMA (Todd Kuzia) and DHS (Craig) notified. NRC Resident Inspector, State and Local officials were notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | PLANT S/D REQD BY TS | OFFSITE NOTIFICATION | DEGRADED CONDITION | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(i) | 50.72(b)(2)(xi) | 50.72(b)(3)(ii)(A) | 0 | 2005-06-30
41814 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-06-30 09:30 | 2005-06-30 16:16 | 2005-06-30 | NON-LICENSED SUPERVISOR FAILED FITNESS FOR DUTY TEST FOR DRUGS A non-licensed employee supervisor had a confirmed positive for illegal drugs during a random fitness-for-duty tests. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2005-06-30
41813 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-06-30 08:00 | 2005-06-30 11:52 | 2005-06-30 | ALERT NOTIFICATION RADIO TRANSMITTER DISCOVERED INOPERABLE "During daily maintenance check of alert notification siren system, a siren technician discovered that the radio transmitter used to communicate with the sirens was not available. Investigation revealed that an encoder that utilizes a T1 phone line to send signals from a siren encoder to the transmitter had failed. This failure produced a signal to key the transmitter. After the transmitter is keyed for approximately 15 seconds the transmitter will lock out and therefore not be available for use. Since the transmitter was unavailable this rendered all offsite sirens inoperable. This notification is made under 10CFR50.72(b) because of a significant loss off offsite public notification capability. "This failure was promptly diagnosed, corrected, and the system tested satisfactorily within approximately 62 minutes from time of discovery of 0800 Eastern Time. "The tone alert radio portion of the alert notification system was available for notification during this event." The NRC Resident Inspector and Burke County was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-30
41812 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-06-29 14:40 | 2005-06-29 17:32 | 2005-06-29 | LOSS OF EMERGENCY SIRENS DUE TO POWER OUTAGE "At 1440 hrs [EDT] on 06/29/05, the Emergency Plan Coordinator for PSEG informed the Hope Creek Control Room that 31 offsite sirens were inoperable due to an unplanned power outage. The Hope Creek ECG [Emergency Communications Guide] requires an eight-hour report to be made if greater than 17 offsite sirens are inoperable for more than one hour. All safety systems are available and operable with the exception of the 'C' Safety Auxiliary Cooling Water Pump, and the 'C' Residual Heat Removal Pump, which is cleared and tagged for a scheduled system outage. At 1555 [hrs.], [we were] notified by [the] Emergency Plan coordinator that power was restored to a majority of the sirens in New Jersey. [Nine] sirens in New Jersey are still inoperable, [one] siren in Delaware is still inoperable." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-29
41811 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-06-28 07:00 | 2005-06-29 16:45 | 2005-06-29 | CALIFORNIA AGREEMENT STATE REPORT - LOST AND RECOVERED IR-192 IMPLANTATION SEEDS The State provided the following information via email: "On Tuesday, June 28, 2005, I received a call from Waste Management of Orange that the radiation alarm had sounded. They separated the radioactive waste from the other waste and placed the radioactive waste in their secure holding area until I could arrive. Around 11:30 a.m. I went out to the facility and took surveys and tried to identify the radionuclide - my batteries on the MCA were running low, but based on the peaks I thought it could be either Ga-67 or Ir-192. The load had been picked up from Chapman Hospital so I contacted them and brought the waste back to the hospital where the RSO was going to do a positive identification. This morning I stopped at the hospital and took some readings outside the waste storage area and did another identification scan using the Bicron Field spec. I contacted the Imaging Director [name deleted]. He said they did find an Ir-192 ribbon (which contained 6 seeds). They put this ribbon with the 19 other ribbons that were being returned to the manufacturer. A 48 year old female patient received 20 ribbons (each with 6 seeds) on 6-20-05. The total activity was 58.19 mCi (activity per ribbon with 6 seeds = 2.9 mCi). The Oncology Physician [name deleted], feels the ribbon could have been dislodged before she was discharged on 6-24-05. This ribbon could have been in the bedding under the patient for some period of time. He will do an evaluation to determine the effects of the ribbon being under the patient for a given time and the effects of a lower dose being administered. [The Imaging Director] states that the found ribbon was placed in with the other 19 ribbons that will be going back to the manufacturer. He has counted and accounted for the 20 ribbons that were originally sent and confirms all 20 are now accounted for. The facility will send me a report about this incident and will outline their corrective actions to avoid disposal of such ribbons in the future." California Report No. 062805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-07-04
41810 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-06-29 04:43 | 2005-06-29 13:23 | 2005-06-29 | EVACUATION SIREN INOPERABLE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On June 29, 2005 at approximately 08:55 Mountain Standard Time (MST), the Palo Verde Emergency Preparedness Program Manager was notified of an inoperable single siren #36. An alarm indicates that the inoperability started at 04:43 AM MST. The siren was vandalized by destroying the battery case and stealing the internal battery. The affected siren is estimated to impact approximately 215 members of population (10.1 %) in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles (or 10% within 5 to 10 miles) for greater than 1 hour. This call is being placed due to the relatively large segment of the population affected and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriffs Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "The County was informed at 09:25 AM MST to implement the MCSO notification if a need arises. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2005-06-29
41809 | 0 | INDIANA DEPT OF TRANSPORTATION |  |  |  |  | 2005-06-28 18:00 | 2005-06-29 07:55 | 2005-06-29 | STOLEN TROXLER DENSITY GAUGE A Troxler Moisture Density Gauge Model 3440, S/N 18795 was stolen from a locked closet in the licensee's trailer field office located in East Chicago, IN, between 1800 [CDT] on 6/28/05 and 0600 on 6/29/05. The Model 3440 contains two (2) radioactive sources; 8 millicuries Cs-137 (S/N 508385) and 40 millicures Am-241/Be (S/N 4714253). The licensee contacted the local police and they are investigating the incident. The licensee is not planning to issue a press release. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-06-29
41808 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2005-06-28 14:00 | 2005-06-28 18:20 | 2005-06-28 | TECHNICAL SUPPORT CENTER VENTILATION INOPERABLE "This 8 Hour Non-Emergency report is pursuant to 10CFR50.72(b)(3)(xiii). Main Control Room personnel were notified that normal and emergency Technical Support Center (TSC) ventilation was inoperable. The loss of ventilation in the TSC constitutes a Major Loss of Emergency Preparedness Capability because it significantly impaired the fulfillment of the Peach Bottom emergency plan in the event of a potential radiological release. Peach Bottom maintenance personnel immediately began investigating the inability to place TSC ventilation in service and were able to restore both normal and emergency ventilation. The initial failure of both normal and emergency TSC ventilation is still being investigated. Normal plant operation is unaffected by the loss of TSC ventilation." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-28
41807 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-06-28 13:00 | 2005-06-28 17:38 | 2005-06-28 | OFFSITE NOTIFICATION TO ILLINOIS DEPARTMENT OF NATURAL RESOURCES "A 1300 CDST on 06/28/05, it was discovered that a minor fish kill took place in Braidwood Nuclear Station's cooling lake, due to increased temperature. As Summer air temperatures increased, the cooling lake temperature increased above 95°F, the threshold at which species susceptible to increased temperature begin to perish. It was communicated to the Illinois Department of Natural Resources, that approximately 1000 fish, the majority of which were Gizzard Shad, had perished. "This notification is made in accordance with Exelon Reportability manual SAF 1.9, ENV 3.26, Braidwood Station Facility Operating License Appendix B Section 4.1 'Unusual or Important Environmental Events,' and 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-06-28
41806 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-06-28 | 2005-06-28 17:06 | 2005-06-28 | AGREEMENT STATE REPORT LOST / MISSING SOURCE The State provided the following information via facsimile: "The North Carolina Radioactive Materials branch was made aware of the loss [of] a Po-210 static elimination source from the Energizer facility in Asheboro, NC today. "The agency interviewed the Staff Environmental Coordinator this afternoon via telephone. The information for the missing source is as follows: Isotope: Po-210 Activity: 20 millicuries as of 3 March 2004 (decay corrected to 2.38 mCi at time of loss) Make: NRD LLC Model: P-2031-1000 Serial No.: A2DP844 "The licensee continues to search for the missing source. North Carolina Radioactive Materials Branch continues to monitor the situation and will dispatch health physicists to investigate as necessary." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-07-01
41805 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2005-06-28 13:00 | 2005-06-28 16:24 | 2005-06-28 | OFFSITE NOTIFICATION DUE TO MINOR FISH KILL "At 1300 CDST on 06/28/05, it was discovered that a minor fish kill took place in LaSalle County Nuclear Station's cooling lake, due to increased temperature. As summer air temperatures increased, the cooling lake temperature increased above 95°F, the threshold at which species susceptible to increased temperature begin to perish. It was communicated to the Illinois Department of Natural Resources, that approximately 300 fish, the majority of which were striped bass, had perished. "This notification is made in accordance with Exelon Reportability manual SAF 1.9, ENV 3.26, LaSalle County Station Facility Operating License Appendix B Section 4.1 'Unusual or Important Environmental Events,' and 10CFR50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-06-28
41804 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2005-04-29 00:43 | 2005-06-28 15:30 | 2005-06-28 | INVALID SYSTEM ACTUATION "This report is being made under 50.73 (a)(2)(iv)(A). "On April 29, 2005, at approximately 0043 Mountain Standard Time, Palo Verde Nuclear Generating Station Unit 2 experienced an invalid 1/2 leg Engineered Safety Feature Actuation Signal (ESFAS) actuation (B train) when operations personnel prematurely implemented a tag out causing loss of vital power to the 'B' train ESFAS cabinet. The following alarms were received; Recirculation Actuation Signal B, Auxiliary Feedwater Actuation Signal-1B, Containment Spray Actuation Signal B, Main Steam Isolation Signal B, Containment Isolation Actuation Signal B, Safety Injection Actuation Signal B, Auxiliary Feedwater Actuation Signal-2B (all Leg 1-3), and Emergency Diesel Generator (EDG) Start Signal B. At the time of the event Unit 2 was in the 'B' train work window for refueling outage 2R12 and not all 'B' train equipment actuated - EDG B, Low Pressure Safety Injection B, Containment Spray B, and the B train Recirculation Actuation Signal sump valves were tagged out of service for maintenance. During the performance of the 'Inadvertent Plant Protection System - ESFAS Actuations' procedure, Operations personnel determined that all 'B' ESFAS equipment operated as expected considering the 'B' train equipment that was tagged out for maintenance." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-06-28
41803 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-05-17 16:02 | 2005-06-28 13:17 | 2005-06-28 | INVALID SYSTEM ACTUATION - AUXILIARY FEEDWATER PUMP STARTED DURING SURVEILLANCE "Per 10 CFR 50.73(a)(1), this telephone notification is made under 10 CFR 50.73(a)(2)(iv)(A) for an invalid actuation. The train D steam-driven Auxiliary Feedwater Pump was inadvertently started while performing post-maintenance testing on another component. "The test was conducted using applicable steps in a surveillance procedure for the solid state protection system. A procedure step for isolating the auxiliary feedwater pump steam turbine was incorrectly performed so that the steam turbine was not isolated, as intended, and started when the test actuation signal was initiated. The steam-driven turbine and pump functioned successfully as a result of the invalid signal. "The signal was determined to be invalid in that it was not initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. The pump start was not an intentional manual initiation. The invalid actuation is reportable in that it did not occur while the system was properly removed from service and did not occur after the safety function had already been completed" The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-06-28
41802 | 0 | EASTERN ASSOCIATED COAL CORPORATION |  |  |  |  | 2005-06-24 16:55 | 2005-06-28 08:20 | 2005-06-28 | NUCLEAR DENSITY GAUGE SOURCE SEPARATED FROM GUAGE Following troubleshooting to remedy density measurement problems, the Cs-137 source (100 milliCuries) and source holder were found missing from its liquid line gauge mounting. It was then determined that the source and holder had become separated from the gauge and had fallen into a sump directly beneath. The gauge is a Ronan Model SA-1-C5, S/N EE823. The licensee isolated the area and performed surveys with no contamination or abnormal radiation readings noted. The licensee contacted the manufacturer and subsequently contracted with a consultant (Jendco, Inc. of Pittsburg, PA) who retrieved the source and source holder from the sump without incident. The source was found intact and undamaged. The gauge was re-assembled and returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | WV | MAT | [5 empty] | 0 | 2005-06-28
41801 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-06-27 11:50 | 2005-06-27 16:41 | 2005-08-09 | MINIMUM SWITCHYARD VOLTAGE REQUIREMENTS NOT MET "At 1150 on June 27, 2005 Quad Cities Station was notified that the calculated post-LOCA switchyard voltage is below the minimum acceptable value required to ensure offsite power will remain available following a design basis accident. The appropriate Technical Specification Actions have been taken for both Units. The ability of the Emergency Diesel Generators to fulfill their design function is not affected by this condition. This event is being reported in accordance with 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function given the predicted post-LOCA switchyard voltage. "Actual Switchyard voltage at the time of this notification is 356 Kv. The required minimum post-accident switchyard voltage for current conditions is 352.9 Kv for Unit-1 and 351 Kv for Unit-2, while the projected post-accident voltage which prompted this notification is 349.8 Kv. At 1320 hrs on June 27, the projected post-accident voltage was 351.3kV. This prediction satisfies the minimum Unit 2 voltage requirement, but is still below the minimum voltage for Unit 1. "This notification is similar to the condition reported on April 29, 2005 (EN #41652) and June 11, 2005 (EN #41766)." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM J. COX TO W. GOTT 1906 ET 08/09/05 * * * "The purpose of this report is to retract ENS report #41652 (April 29, 2005), ENS report 41766 (June 11, 2005), and ENS report #41801 (June 27, 2005). The reports were made following notification that the switchyard predicted voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. For each event, both sources of offsite power were declared inoperable, the appropriate Technical Specification required actions were taken for the units, and an ENS notification was made for a condition that could have prevented the fulfillment of a safety function. "Each Quad Cities unit has two sources of off-site power. For a specific unit, one source is from the switchyard through the unit's Reserve Auxiliary Transformer (RAT) and the second source is from the switchyard through the opposite unit's RAT. Following further analysis of the loading on the RATs during an accident, it was determined that only one source of offsite power to each unit should have been considered inoperable. The analysis determined that because the RAT for the non-accident unit (i.e., the offsite source supplied through the opposite unit) would be carrying a much smaller load, it would not be subject to a degraded voltage condition and resultant isolation from the grid. Therefore, an accident on one unit would not affect the operability of the source of offsite power supplied through the opposite unit's RAT. As a result, only the source of offsite power supplied through the unit's RAT was inoperable. With one source of offsite power available at all times, there was no condition present that could have prevented fulfillment of a safety function, and therefore, these events are not reportable." The licensee notified the NRC Resident Inspector. Notified R3 DO (R. Lanksbury) | 85 | 97 | 0 | 85 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-06-27
41800 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-06-27 03:16 | 2005-06-27 04:19 | 2005-06-27 | DECLARATION OF AN UNUSUAL EVENT DUE TRANSFORMER FIRE >10 MINUTES UNUSUAL EVENT (EAL #16 - Fire) declared at 0327 on 6/27/05 due to uncontrolled fire in the Unit 4 Main Transformer lasting longer than 10 minutes. Unit 4 experienced an automatic reactor trip from 100% on a turbine trip due to a fire in the Main Transformer. The fire was extinguished after approximately 25 minutes. On-site fire brigade and Miami-Dade fire department responded. The cause of the fire is under investigation. The reactor is stable in Mode 3. No safety systems were affected. All rods fully inserted, no ECCS actuations, no relief valves lifted and no personnel injuries occurred. Offsite power is still available and no emergency diesels auto started, however, there was an auxiliary feedwater actuation. Hazardous Material response is being implemented due to discharge of transformer oil. There may be a possible press release on this event. The NRC Resident Inspector was notified along with State and local agencies. * * * UPDATE ON 06/27/05 @ 05:13 BY SPEICHER TO GOULD * * * The NOUE was terminated at 05:00 due to the fire being extinguished and the emergency no longer existing. The NRC Resident Inspector was notified. Notified RDO 3 (Evans), EDO (Case), IRO (Frant), FEMA (Bagwell), DHS (Reed) * * * UPDATE 0915 EDT ON 6/27/05 BY S. SANDIN * * * Received a call from a member of the Turkey Point Communications Group. The licensee does not plan on issuing a press release at this time. Notified R2DO (Evans). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | OFFSITE NOTIFICATION | IMode2: Power Operation; FMode2: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(xi) | 0 | 2005-06-27
41799 | -1 | PILGRIM | 1 |  |  | [1] GE-3 | 2005-06-26 10:55 | 2005-06-26 15:30 | 2005-08-12 | EMERGENCY DIESEL GENERATORS INOPERABLE DUE TO HIGH AMBIENT TEMPERATURE "The report is being made in accordance with 10 CFR 50.72(b)(3) due to both Emergency Diesel Generators (EDGs) being declared inoperable. [This is a 24-hour LCO.] The EDGs were declared inoperable due to indicated outside air temperature exceeding the established operability limit of 95F for two short periods of time. Indicated outside air temperature went above 95F during the following time frames: 10:55 to 11:00 and 12:15 to 12:20. Indicated outside air temperature subsequently decreased to less than 95F following these spikes. Both EDGs are currently operable. Outside ambient temperatures are continuing to be monitored. Offsite power is available. "Further evaluation of this event is ongoing." The licensee notified the NRC Resident Inspector. * * * EVENT RETRACTION FROM LICENSEE (NOYES) TO ABRAMOVITZ AT 12:06 ON 08/12/2005 * * * "The initial report was made in accordance with 10 CFR 50.72(b)(3) due to both Emergency Diesel Generators (EDGs) being declared inoperable. The EDGs were declared inoperable due to indicated outside air temperature exceeding the established operability limit of 95F for short periods of time on 6/26/05. Outside indicated air temperature subsequently decreased to less than 95F following these short timeframes. Both EDGs were operable when the notification was made, and outside ambient temperatures continued to be monitored. Offsite power was available. Further evaluation of this event has been performed. The initial report used temperature indication that was conservative with respect to actual conditions. The evaluation determined that the air temperature outside the EDG Building was a maximum of 91 F on 6/26105. This evaluation was based on other temperature reading taken during the periods of interest. Additionally, further evaluation has determined that both EDGs were not inoperable even at the higher temperatures initially indicated. Therefore, the EDGs were not inoperable during the periods reported and event notification #41799 is retracted." Notified the R1DO (Caruso). The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2005-06-26
41798 | -1 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-06-26 04:17 | 2005-06-26 14:52 | 2005-08-23 | EDG INOPERABLE DUE TO LOOSE ELECTRICAL CONNECTION "On June 25, 2005, at about 1335 PDT, during a test of Unit 3 Emergency Diesel Generator (EDG) 3G003, Emergency Supply Fan 3A276 did not start. SCE's investigation found a loose electrical connection at the thermal overload auxiliary switch contact for that fan. A similar condition was found on Emergency Supply Fan 3A277. SCE declared 3G003 inoperable and initiated a common cause investigation required by the EDG Technical Specifications. SCE tightened the affected electrical connections and after successfully start testing 3G003, declared 3G003 operable at 0406 PDT on June 26, 2005. "On June 26, 2005, at about 0417 PDT, SCE found similar loose connections for EDG 3G002. Components affected were the EDG radiator fan and an EDG Emergency Supply Fan. Because SCE could not conclusively determine if the loose connections would have caused 3G002 to be inoperable, SCE conservatively declared 3G002 inoperable. (SCE currently plans to start test the Unit 2 EDGs today to confirm the Unit 2 EDGs remain operable.) "Because it appears that both Unit 3 EDGs could have been inoperable at the same time, SCE is reporting this occurrence in accordance with 10CFR50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. "At the time of this occurrence, Unit 2 was operating at about 99 percent power and Unit 3 was at about 100 percent power. SCE has notified the NRC Resident Inspectors about this occurrence and will provide them with a copy of this report." * * * RETRACTION FROM LICENSEE (HOLT) TO NRC (HUFFMAN) AT 1850 EDT ON 8/23/05 * * * "On June 26, 2005, SCE reported to the NRC that both Unit 3 emergency Diesel Generators (EDGs) were conservatively declared inoperable at the same time. SCE reported that occurrence to the NRC in accordance with 10CFR50.72(b)(3)(v)(D) for the loss of a safety function. "SCE has since determined that both EDGs were operable in the as found condition and that a report to the NRC was not required and SCE is retracting that report. "For EDG 3G003, even though one of two emergency supply fans did not function, SCE confirmed by calculation that the remaining emergency supply fan was sufficient. That is, 3G003 was capable of performing its specified safety function with only one emergency supply fan operating. For EDG 3G002, the electrical connections that were reported to be 'loose' did not prevent circuit continuity and did not degrade the operability of the EDG. 3G002, therefore remained operable. "Because the EDGs were operable, no report was required. SCE is retracting the June 26, 2005 report. SCE will, however, submit a voluntary licensee event report to document this event and inform the NRC of the corrective actions taken. "At the time of this phone call, Unit 2 was operating at about 99 percent power and Unit 3 was at about 100 percent power. SCE has notified the NRC resident inspectors about this retraction and will provide them with a copy of this report." R4DO (Smith) was notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-06-26
41797 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2005-06-25 20:42 | 2005-06-26 01:03 | 2005-06-26 | OFFSITE ASSISTANCE REQUESTED DUE TO SWITCHYARD CIRCUIT BREAKER FAILURE "On June 25, 2005 at 2042, Clinton Power Station received indications of loss of the Reserve Auxiliary Transformer (RAT). Upon investigation, it was discovered that Gas Circuit Breaker (GCB) 4522 had suffered catastrophic failure resulting in a lockout of the North Bus, which supplies the RAT. "Offsite assistance was requested, as a precautionary measure, from the Local Law Enforcement Agency, Medical, and Fire Departments. The onsite Operations Fire Brigade extinguished the fire in the GCB 4522. "Clinton Power Station remained online at full electrical load during the event and is stable. Restoration and recovery is now in progress. "The NRC Resident Inspector has been informed." The licensee stated that local law enforcement (Dewitt County Sheriff) departed the site at 2130 CDT and that nothing of a suspicious nature was found. The incident is considered to be solely the result of a component failure. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-06-26
41796 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2005-06-24 15:30 | 2005-06-24 20:11 | 2005-06-24 | SAFETY PARAMETER DISPLAY SYSTEM FAILURE IN EMERGENCY OPERATIONS FACILITY "At 1530, on June 24, 2005, Training personnel reported a problem with the Safety Parameter Display System (SPDS) screens at the Emergency Operations Facility (EOF). Subsequent investigation determined that data was being updated, but the SPDS screens would not respond to keyboard or touch screen commands. SPDS was declared inoperable at 1630. "The SPDS computer system is designed to monitor and display a concise set of parameters from which the safety status of both units can be readily and reliably determined. The system provides plant status information to the Unit-1 and Unit-2 control rooms, the Technical Support Center (TSC), and the Emergency Operating Facility (EOF). "The controls and displays in the computer room, both Control Rooms and the TSC were unaffected by this condition. "A bad communications card was found and replaced at the EOF. SPDS operability was restored at 1735." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-24
41795 | 0 | ENGINEERING CONSULTANT SERVICES |  |  |  |  | 2005-06-24 15:15 | 2005-06-24 16:15 | 2005-06-24 | NUCLEAR DENSITY GAUGE DAMAGED AT JOBSITE At approximately 1515 EDT on 6/24/05, a CPN Nuclear Gauge, Model NC1DRP, S/N MD00505618 containing two (2) sources, i.e., 10 millicuries Cs-137 and 50 millicuries Am-241:Be, was run over by a loader at a jobsite near the intersection of Olley Lane and Little River Turnpike in Fairfax County, VA. The area was isolated and rad surveys conducted by the RSO confirmed that the source was not exposed (a radiation level of .4mR/hr was measured at a distance of 1 meter). The RSO will package the damaged gauge and return it to the manufacturer for evaluation. No assistance from any HAZMAT/Fire Department personnel was requested or needed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | OTH | GEN |  |  |  |  | 0 | 2005-06-24
41794 | 0 | GE ENERGY |  |  |  |  | 2005-04-26 | 2005-06-24 13:35 | 2005-06-24 | PART 21 NOTIFICATION - CRITICAL POWER DETERMINATION FOR GE14 AND GE12 FUEL WITH ZIRCALOY SPACERS The following is a portion of a facsimile received on June 24, 2005 from GE Energy, reference - MFN 05-058 Rev 1: ATTACHMENT 2 - 60-Day interim Report Notification per §21.21(a)(2), and Transfer of Information per §21.21(b) (i) Name and address of the individual informing the Commission: J. S. Post, Manager, Engineering Quality &Safety Evaluations, GE Energy - Nuclear, 3901 Castle Hayne Road, Wilmington, NC 28401. (ii) Identification of the facility, the activity, or the basic component supplied for such facility or such activity within the United States, which may fail to comply or contain a defect: The affected and potentially affected plants are identified in Attachment 1. This concern is limited to plants that have fresh or once-burned GE14 or GE12 fuel with Zircaloy spacers. GE12 fuel with Inconel spacers is not affected. (iii) Identification of the firm constructing the facility or supplying the basic component, which may fail to comply or contain a defect: Global Nuclear Fuel-Americas, LLC, Wilmington, NC. (iv) Nature of the defect or failure to comply and safety hazard, which could be created by such defect or failure to comply: During review of GE14 ATLAS critical power tests results, it was discovered that springs on the Zircaloy test spacers used in the GE14 and GE12 critical power testing were deformed, possibly during the testing. This resulted in a potentially non-conservative critical power determination for fuel bundle corner pin locations. This non-conservatism potentially impacts the calculated margin to the Operating Limit Minimum Critical Power Ratio (OLMCPR), the Safety Limit MCPR (SLMCPR), the Rod Withdrawal Error (RWE) analysis, and the R-factors used in the on-line 3D core simulator. GE has completed the evaluation of the impact on the critical power determination, and has completed the evaluation of the impact on the R-factors. GE has performed a preliminary evaluation of the impact on the margin to the OLMCPR, the impact on the SLMCPR, and the impact on the RWE event. Potentially affected plants have been informed and have taken appropriate compensatory actions. (v) The date on which the information of such a potential defect or failure to comply was obtained: This concern was identified in the GE safety evaluation program on April 26, 2005. (vi) In the case of a basic component which may contain a defect or failure to comply, the number and locations of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: The basic component that may contain a defect is the critical power determination for fresh and once-burned GE14 and GE12 fuel with Zircaloy spacers. GE12 fuel with Inconel spacers and other GNF fuels are not affected. In the US, only GE14 is affected since all GE12 designs in the US have Inconel spacers. (vii) The corrective action which has been, is being, or will be taken: the name of the individual or organization responsible for the action; and the length of time that has been or will be taken to complete the action (note, these are actions specifically associated with the identified Potential Reportable Condition evaluation): GE has completed the evaluation of the impact on the critical power determination and has completed the evaluation of the impact on the R-factors. GE has performed a preliminary evaluation of the impact on the margin to the OLMCPR, the impact on the SLMCPR, and the impact on the RWE event. Plants that may have non-conservative process computer calculated OLMCPR margins have taken compensatory action as necessary based on the magnitude of the non-conservatism to prevent inadvertently exceeding the OLMCPR during plant operating maneuvers. Additional corrective actions planned are as follows: 1. Complete the current-cycle analyses to confirm the non-conservative MFLCPR impact (September 20, 2005). 2. Complete the analysis for previous cycle(s) extending to the previous three years of operation to determine which plants may have a non-conservative MFLCPR (December 15, 2005). 3. Complete the analyses to confirm that no plant has a SLMCPR impact greater than or equal to the reportable threshold of 0.01 (September 20, 2005). 4. Determine and provide the necessary data for plants that perform their own SLMCPR calculations, or that operate with fresh fuel batches of non-GE fuel along with second cycle affected GE14 fuel (September 30, 2005). 5. Complete the evaluation to confirm that the RWE analyses do not impact the OLMCPR (September 20, 2005). 6. Provide bundle R-factor and software updates for the on-line 30 core simulator (beginning in August 2005, and extending through the balance of 2005). (viii) Any advice related to the potential defect or failure to comply about the facility, activity, or basic component that has been, is being, or will be given to purchasers or licensees: Affected plants should continue to work with their GE Customer Account Leader to obtain information as plant-specific calculations are completed. ATTACHMENT 1 - Affected and Potentially Affected Plants for Current Operating Cycle [ABSTRACTED] (a) Impact on MFLCPR: Transfer of Information; preliminary analysis indicates MFLCPR impact, GE does not have sufficient information to determine if the OLMCPR could have been exceeded Clinton, Brunswick 1 & 2, Nine Mile Point 2, Fermi 2, FitzPatrick, Dresden 2, LaSalle 1 & 2, Limerick 1 & 2, Peach Bottom 2 & 3, Quad Cities 2, Perry 1, Cooper, Duane Arnold, Monticello, and Hope Creek. (b) Impact on SLMCPR: Transfer of Information; GE does not have sufficient information to determine if there is an impact on the SLMCPR greater than or equal to 0.01 Browns Ferry 2 & 3 (c) Impact of Rod Withdrawal Error (RWE) on OLMCPR: Transfer of Information; GE does not do the analysis for RWE (info provided via telephone during notification to Ops Center) Browns Ferry 2 & 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2005-06-24
41793 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-06-24 08:45 | 2005-06-24 09:59 | 2005-06-24 | OFFSITE NOTIFICATION - FUEL OIL SPILL ON LAKE WYLIE NEAR PLANT INTAKE "At 0741 the control room was notified that a barge that was being used to support drilling activities near the plant intake on Lake Wylie had partially sunk. The barge was supporting a diesel fuel engine used for drilling operations. The fuel oil tank (maximum capacity of 6 gallons) was submerged under the surface of Lake Wylie. At 0840 the duty hazmat personnel on the scene notified the control room that there was fuel oil on the surface of the lake. At approximately 0845 the York County South Carolina 911 telecommunicator was called and informed of the fuel oil spill on Lake Wylie. This notification is being made as a 4-hour non-emergency notification as a result of notifying an offsite agency of the fuel oil spill on Lake Wylie. Efforts are currently underway to secure / contain the fuel oil. No offsite assistance has been requested." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-06-24
41792 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-06-23 23:21 | 2005-06-24 02:57 | 2005-06-24 | LICENSEE DECLARED AN UNUSUAL EVENT DUE TO DETECTION OF A FLAMMABLE GAS IN THE GENERAL SERVICES BUILDING An NOUE was declared at the site at 2327 PDT due to the discovery of flammable gas in the General Services Building (office space) which is attached to the turbine and reactor building. The source and type of gas has not been identified and investigation is ongoing by HAZMAT trained personnel. The highest level of flammability measured is 50% of LEL (Lower Explosive Limit). The building has been evacuated. The NRC Resident Inspector will be notified and State local and other Gov agencies have been notified. * * * UPDATE FROM D. FUJIYOSHI TO M. RIPLEY 0527 EDT 06/24/05 * * * "EAL # 9.3.U.3 - Report or detection of toxic or flammable gases that could enter or have entered within the Protected Area Boundary in amounts that could affect the health of plant personnel or safe plant operation. "The event has been terminated based on a thorough survey of the building by HAZMAT personnel. The building in question has been determined to be free of any flammable gases. "Probable source of gas is from a sewage treatment plant. The gas was carried by a stable breeze to the building's air intake. Immediately prior to the event, initial reports of odorous gas from several building occupants was confirmed using portable instrumentation. The highest flammable gas levels were found at a building air intake. Dissipation of gas concentration was accomplished using normal building ventilation." The NRC Resident Inspector will be notified and State local and other Gov agencies have been notified. Notified R4 DO (R. Bywater), NRR EO (M. Case), IRD Manager (S. Frant), DHS (Ceasar), and FEMA (Sullivan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 4 | WA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-06-24
41791 | -1 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2005-06-23 15:49 | 2005-06-23 22:08 | 2006-07-28 | OFFSITE POWER SOURCE DECLARED INOPERABLE DUE TO LOW VOLTAGE "At 15:49 hours Central Daylight Savings Time, June 23, 2005, entered DOA 6500-12, Low Switchyard Voltage. Bulk Power Operations reported predicted post Unit trip with LOCA switchyard voltage for Unit 2 is 342.5 KV and for Unit 3 is 342.3 KV. This rendered both Unit 2 and Unit 3 offsite electrical power sources inoperable. This predicted voltage is the value required to support Loss Of Coolant Accident (LOCA) loading. Entered applicable Technical Specification required actions for both Units due to both offsite power sources being declared inoperable for Unit 2 and Unit 3. "As of 1744 hours, restored Unit 2 offsite electrical power source to operable status by performing Transformer 86 Tap Changer adjustment per applicable procedure. TR 86 [transformer 86] supplies Unit 2 offsite electrical power. "As of 1948 hours, switchyard voltage was restored to operable limits. This restored Unit 3 offsite electrical power source to operable status. "This notification is provided in accordance with 10CFR50.72(b)(3)(v)(D) to report a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The licensee will notify the NRC Resident Inspector and the state. * * * UPDATE FROM P. SALGADO TO M. RIPLEY 1258 EDT 07/28/06 * * * "The purpose of this report is to retract ENS report 41791 (June 23, 2005) for Dresden Nuclear Power Station (DNPS). The report was made following notification from Bulk Power Operations that the predicted post Unit trip with LOCA switchyard voltage rendered both Unit 2 and Unit 3 offsite electrical power sources inoperable. Both offsite electrical power sources were declared inoperable, the appropriate Technical Specification required actions were taken and an ENS notification was made in accordance with 10CFR 50.72(b) (3)(v)(D) for an event that could have prevented fulfillment of a safety function. "In July 2006, DNPS performed a reanalysis of the June 23, 2005 event. The reanalysis determined that the computer model used to determine the required switchyard voltage for the June 23, 2005 event conservatively assumed that the Reserve Auxiliary Transformers (RATs) were supplying all plant 4 kilovolt (Kv) electrical loads and the second source of offsite power for each unit was based on a post unit trip. During normal plant operation the 4kV electrical loads are split between the RATs and the Unit Auxiliary Transformers (UATs). The reanalysis used the split bus configuration and the actual switchyard voltages at the time of the June 23, 2005 event. The reanalysis concluded that the voltages were greater than required, ensuring that the second source of offsite power for each unit would remain operable following a postulated design basis accident. Therefore, there was no condition present on June 23, 2005, that could have prevented fulfillment of a safety function and this event is not reportable under 10CFR 50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified R3 DO (R. Lanksbury) | 0 | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-06-23
41790 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-06-23 13:46 | 2005-06-23 18:50 | 2005-06-23 | UNIT EXPERIENCED AN AUTOMATIC REACTOR SCRAM DUE TO A LOSS OF FEEDWATER FLOW "On June 23, 2005 at 1348 PDT Columbia Generating Station experienced a Reactor Protection System (RPS) actuation and closure of all Main Steam Isolation Valves (MSIV) while operating at approximately 25% power. Currently, Reactor Pressure Vessel (RPV) level is being controlled using the Reactor Core Isolation Cooling (RCIC) system and RPV pressure is stable at approximately 800 psi. There was no automatic ECCS system injection. At this time, the plant is stable and indications show that the RPS actuation and closure of MSIVs was initiated in response to a valid low RPV water level signals that occurred because of a loss of feedwater flow. Determination of the cause of the loss of feedwater flow is ongoing at this time." All control rods fully inserted. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-06-23
41789 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2005-06-23 08:23 | 2005-06-23 18:33 | 2005-06-23 | UNIT 2 AUX FEEDWATER TRAIN SEPARATION NOT MAINTAINED DURING OPERATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On 6/23/05 at approximately 08:23 MST, it was identified that the door between the 'A' and 'B' Train Aux Feedwater Pump rooms was open and unattended. The door was immediately closed and secured. This door is required to be maintained secured in the closed position (except for personnel ingress/egress) during Modes 1 through 4 to provide a barrier for protection from fire or internal flooding. Station procedures require compensatory measures to be established when this door is maintained open in Modes 1-4. The compensatory measures include stationing an individual with the responsibility to close the door in the event of internal flooding. Since this compensatory measure was not established, this condition is considered to be reportable as an unanalyzed condition per the criteria of 10CFR50.72(b)(3)(ii)(B). "Investigation is in progress to determine the duration and reason that this door was inappropriately open." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-06-23
41788 | 0 | PALISADES | 1 |  |  | [1] CE | 2005-06-23 08:20 | 2005-06-23 10:40 | 2005-06-23 | NON-LICENSED SUPERVISOR FAILED RANDOM FITNESS FOR DUTY TEST A non-licensed employee supervisor tested positive for illegal drugs during a random test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2005-06-23
41787 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2005-06-21 23:40 | 2005-06-22 05:56 | 2005-06-23 | MULTIPLE SPECIFIED SYSTEMS ACTUATIONS DUE TO LOSS OF AC SAFETY RELATED BUSES "At 23:40 CDST, LaSalle Unit 2 experienced a trip of the 4160 Volt AC feed breaker to 480 Volt AC Safety Related buses 235X & 235Y. As a result of this feed breaker trip, containment isolation valves closed in multiple systems. The systems which isolated included Containment Monitoring System, Drywell Floor Drains and Drywell Equipment Drains, Reactor Recirculation Flow Control Hydraulic System, Drywell Instrument Nitrogen System, Reactor Water Cleanup System, and Reactor Recirculation Sample System. This event is reportable under 10 CFR50.72(b)(3)(iv)(A). In addition to the- above mentioned system isolations, the following plant responses occurred due to the loss of these 480 Volt AC buses: Reactor Building Ventilation was lost due to the closure of the secondary containment isolation dampers; Multiple Division 1 containment isolation valves lost their AC power source, a 1/2-SCRAM occurred due to the loss of the 2A Reactor Protection System Motor-Generator set, the DC charger feed to the Division 1 DC Battery/Bus was lost, and the battery is currently maintaining availability of DC power to the bus. Troubleshooting has determined that the cause of the breaker trip was due to a defective neutral ground current protective relay. This relay has been replaced and the buses have been re-energized. System restoration is currently in progress." The plant is in multiple LCOs, however, the limiting LCO is a 12 hour requirement to reestablish operability to the DC Battery. The half scram has been restored and all ECCS systems can function correctly when required. The licensee informed the NRC Resident Inspector. * * * UPDATE FROM JEFF WILLIAMS TO GERRY WAIG AT 1217 EDT ON 06/22/05 * * * "The following is an update to EN# 41787. Restoration of all required safety systems with the exception of the Reactor Core Isolation Cooling (RCIC) system has been completed. The associated ECCS systems were filled, vented and restored to an available status at 0630 CDST and full operability established at 0803 CDST. The Division 1 DC battery was fully recharged and returned to an operable status at 0803 CDST. Restoration of the RCIC system and investigation into the cause of the relay failure is currently in progress." The licensee has notified the NRC Resident Inspector. Notified R3DO (Bruce Burgess) of the update. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-06-22
41786 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-05-10 16:55 | 2005-06-21 16:35 | 2005-06-21 | EMERGENCY SAFETY SYSTEM ACTUATION DAMPERS INOPERABLE "During integrated ESFAS System Testing coming out of RF 14, it was noted [on 5/10/05] that 4 dampers receiving an SI signal did not reposition full closed as required. The dampers serve to isolate the Condenser Air Removal Ductwork in the Turbine Building from the Filtration train in the Auxiliary Building. Failure of these dampers to close was determined on 05/27/2005 to constitute an unanalyzed condition in that this path is assumed isolated in the accident analysis. "The dampers receive a signal to close but are powered from an AC source requiring a Diesel Generator to supply power from a safety related motor control center. The problem occurs when a signal for loss of offsite power is inserted coincident with an SI signal. The dampers start to close, but there was no seal in circuit so that motion to the closed condition would continue once the affected Diesel Generator reenergized the safety related bus and power supply. "The plant was in Mode 5 at time of discovery, but has operated at power with this configuration since the initial startup of the unit. The dampers could have been closed as evidenced by troubleshooting at the time relying on operator action once the Diesel Generator had reenergized the bus. There is no requirement for Sl and Auxiliary Building isolation in Mode 5. A modification was completed to the circuitry prior to entering Mode 4 where automatic isolation is required. "The Reportability Evaluation was completed on 5/27/2005 but was not reported within the required 8 hours. The reportability of 8 hours was discovered during review on 06/21/2005 of the completed evaluation. Licensing personnel were immediately contacted." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-06-21
41785 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-06-20 03:08 | 2005-06-20 05:41 | 2005-06-20 | BOTH STANDBY GAS TREATMENT TRAINS BRIEFLY INOPERABLE DURING TESTING "During the performance of the monthly 10-hour run testing of the 'B' Standby Gas Treatment (SBGT) train it was discovered that the flow-indicating controller was not controlling flow at the required setpoint. The 'B' SBGT train was declared inoperable at 0308 on 20 June 2005. As part of the testing, the 'A' SBGT train Mode Select switch was in Manual with the inlet damper closed rendering the 'A' SBGT train inoperable. During the short period of time (approximately 4 minutes) between the discovery of the 'B' SBGT controller failure and the return of the 'A' SBGT train to an operable condition, both SBGT trains were inoperable which is a condition that could prevent the fulfillment of the safety function of the SBGT system to control the release of radioactive material. This is an 8-hour reportable event per 50.72(b)(3)(v)(C). "The 'A' SBGT train was restored to operable status at 0312 when its inlet damper was reopened and its Mode Select switch was returned to AUTO per the surveillance test." The licensee will inform the NRC Resident Inspector. | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2005-06-20
41784 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-06-17 16:54 | 2005-06-17 19:25 | 2005-06-17 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM "On 6/17/2005, at 08:54 am CDT, the Wolf Creek Generating Station experienced an unexpected loss of the safety parameter display system (SPDS). Troubleshooting efforts have been, at this time, unsuccessful in restoring functionality of the SPDS. Because SPDS has been lost for longer than a short period of time, the Wolf Creek Nuclear Operating Corporation is making this ENS notification pursuant to the criteria within 10 CFR 50.72(b)(3)(xiii). There is no other loss of emergency assessment capability concurrent with the ongoing loss of SPDS. Plant personnel have entered the applicable off-normal procedure and are taking local readings of equipment normally monitored by SPDS. "It is unknown at this time when SPDS is expected to be restored." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-17
41783 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2005-06-17 11:00 | 2005-06-17 18:39 | 2005-08-01 | POTENTIAL DEGRADED CONDITION DUE TO PRESSURIZER HEATER ELEMENT NON-CONFORMANCE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On June 15, 2005, Palo Verde Nuclear Generating Station was informed by Framatome that Thermocoax pressurizer heater elements provided for, and installed in Unit 3, were in non-conformance with specifications. Specifically, the active heating portion of the element was approximately 8 inches lower than design. The result of this error is that the active (heating) portion of the element extended into the nozzle area of the pressurizer heater sleeve and the heating effect on the pressurizer sleeve exceeded design, and possibly code-allowable temperature. "Unit 3 operators entered Technical Requirements Manual LCO 3.4.103, Structural Integrity, Condition A for a ASME Code Class 1 component not conforming with requirements. The pressurizer can not be isolated and RCS temperature was already more than 50 degrees F above the minimum temperature required by NDT consideration when the condition was discovered. TLCO 3.0.100.3 is not applicable in Mode 5 and Technical Specification 3.4.9, Pressurizer, is not applicable in Mode 5. The RCS is in Mode 5 at approximately 190 degrees F and 350 psia. "Engineering personnel are evaluating the code acceptability and potential for significant degradation resulting from the temperatures experienced by the pressurizer heater sleeves. On June 17, 2005, at approximately 11:00 AM MST, Palo Verde was informed that based on x-ray results of a PVNGS failed Thermocoax heater that revealed the active portion of the heater is longer than previously assumed, the metal temperatures exceeded ASME code allowable values. Stress levels are still under evaluation. "This report is conservatively being placed per 10CFR50.72(b)(3)(ii)(A) based on the potential that the RCS pressure boundary may be seriously degraded, and 10CFR21(d)(3)(i) based on a defect in the pressurizer heater, a basic component, that may affect its safety function necessary to assure the integrity of the reactor coolant pressure boundary. "An investigation of this condition will be conducted in accordance with the PVNGS corrective action program." The Thermocoax heater elements were installed in November 2004, when all heaters in the Unit 3 pressurizer were replaced. Due to the increased failure rate all Thermocoax heater elements have been replaced in the last 30 days with General Electric style pressurizer heater elements that were used previously. The heaters, which were also provided to SONGS 2&3 and Waterford 3, had a design variance (480 VAC single phase instead of 480 VAC 3-phase) which made them unique to Palo Verde. The impact of this variance is currently being evaluated. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 8/1/05 AT 1143 EDT FROM R. BUZZARD TO P. SNYDER * * * The licensee is retracting this event based on the following: "This is a retraction of ENS 41783, placed with the Headquarter Operations Center on 06/17/2005 at 1839 EDT. "On June 15, 2005, Palo Verde Nuclear Generating Station was informed by Framatome that the Thermocoax pressurizer heaters provided for, and installed in Unit 3, were in non-conformance with the applicable design specification. Specifically, the heating section of the heater was manufactured approximately 8 inches longer than cited in the specification. The result of this error was that the heating section extended into the pressurizer lower head. "Engineering analysis concluded that the pressurizer lower head exceeded design and ASME Code allowable temperatures. This condition was reported on June 17, 2005 (ENS 41783). "Further Engineering analysis concluded that the RCS pressure boundary (pressurizer lower head) was not significantly degraded. APS has requested NRC approval for a relief request (reference letter to the NRC dated June 19, 2005). The proposed alternative discussed in this relief request provided an acceptable level of quality and safety since no significant creep effects were introduced into the Unit 3 pressurizer lower head as a result of the design non-conformance. Therefore, APS has requested that the proposed alternative be authorized pursuant to 10 CFR 50.55a(a)(3)(i). The NRC provided verbal approval for Unit 3 to continue operation. "Based on the above information the "Degraded Operation" ENS notification made on June 17, is being retracted. "The heater supplier, FRAMATOME ANP, INC, reported the defect in accordance with10CFR Part 21 on July 22, 2005 (ENS 41864)." The licensee has retracted both the 10CFR Part 50.72(b)(3)(ii)(A) degraded condition notification and their 10 CFR Part 21 notification. Retraction of the 10 CFR Part 21 notification is based on the fact that the vendor reported the same condition. The licensee notified the NRC Resident Inspector of the retraction. Notified R4DO (D. Powers). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | UNSPECIFIED PARAGRAPH |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) | 21.21 |  |  | 0 | 2005-06-17
41782 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2005-06-17 11:20 | 2005-06-17 15:02 | 2005-06-17 | AUTOMATIC REACTOR SCRAM DUE TO EHC MALFUNCTION "At 1120 hours (CDT) on June 17, 2005, the Unit 1 reactor automatically scrammed from 85% power due to a valid high reactor pressure signal. The maximum reactor pressure was approximately 1044 psig during the event. All control rods inserted to their full-in position. Initial indications are that the reactor pressure increase was caused by a malfunction in the Electro-Hydraulic Control (EHC) system, which resulted in closure of the main turbine control valves. The main turbine bypass valves (nine) opened as expected in response to the pressure increase. No reactor pressure vessel safety or relief valves were required to actuate during the event. Reactor water level decreased to approximately -20 inches, which resulted in automatic Group 2 and 3 isolations as expected. All systems responded properly to the event. Unit 1 is in Mode 3 with a cooldown in progress and reactor water level in the normal level band. An investigation into the Unit 1 scram is in progress. "Unit 2 remains at 94% power. "This report is being made in accordance with 10CFR 50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A)." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-06-17
41781 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-06-16 19:02 | 2005-06-16 22:16 | 2005-06-16 | UNIT COMMENCED A TECH SPEC REQUIRED SHUTDOWN DUE TO AN ELECTRICAL PROBLEM AFFECTING A SAFETY RELATED BATTERY "At 1302 [CDT], 6/16/05, during investigation of an electrical ground affecting safety related battery NK04, a channel failure alarm actuated for SA075B, Main Steam and Feedwater Isolation Actuation control panel. Work at KJ122, 'B' Emergency Diesel Generator [EDG] local control panel, was suspended and troubleshooting efforts commenced to determine the cause of the SA075B alarm. Concurrently, SA075B was declared Inoperable at 1302 [CDT] and Engineered Safety Feature Actuation System Technical Specification Action statement 3.3.2.S was entered which allowed 6 hours to restore the train to Operable status, or be in Mode 3 within the following 6 hours. As of 1902 [CDT], all repairs and retests had not been completed. A reactor shutdown was commenced at 1902 [CDT] in accordance with Technical Specification 3.3.2.S, which is reportable per 10CFR50.72(b)(2)(i)." The licensee is continuing their investigation to identify cause of the electrical ground but does not anticipate exiting the LCO Action Statement before completing the Unit shutdown. Safety related battery NK04 is currently operable with the faulted loads isolated. The "B" EDG remains Inoperable at this time for troubleshooting. The licensee informed the NRC Resident Inspector. | 67 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-06-16
41780 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-06-16 09:23 | 2005-06-16 13:44 | 2005-06-16 | BOTH RHR LPCI DIVISIONS INOPERABLE DUE TO VALVE FAILURE "On June 16, 2005 at 0923 EDT, with the plant in Mode 1 at 100% reactor power, both divisions of Residual Heat Removal (RHR) were declared inoperable for the Low Pressure Coolant Injection (LPCI) mode of operation due to a failure of E1150-F017B, Division 2 LPCI Outboard Injection Valve. While performing the Division 2 RHR Pump & Valve Operability Surveillance following a planned Division 2 RHR system outage, E1150-F017B closed properly but failed to open during its required stroke time test. With this valve closed and unable to automatically open, LPCI injection into the RPV from both divisions of RHR would be prevented if LPCI Loop Select Logic selected the Division 2 loop for injection. Therefore, this failure rendered both divisions of RHR inoperable for the LPCI function. LCO 3.5.1.J was entered, which requires immediate entry into LCO 3.0.3. The cause of the failure was subsequently identified and E1150-F017B was returned to its normally open position. At 1146 EDT, Division 1 RHR was declared operable for the LPCI function, and LCO 3.5.1.J and LCO 3.0.3 were exited. The plant remained at 100% power throughout the event. "The NRC resident inspector has been notified. This report is being made pursuant to 10CFR 50.72(b)(3)(v)(D)." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-06-16
41779 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-06-15 14:00 | 2005-06-15 18:38 | 2005-06-15 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE THROTTLE VALVE CLOSURE "On June 15, 2005 at 1400 PDT Columbia Generating Station experienced a Reactor Protection System (RPS) actuation while operating at full power. Currently, reactor level is being controlled with the feedwater system and reactor pressure is being controlled via the turbine bypass valves to the condenser. All safety systems functioned as expected and there was no ECCS system injection. The initial attempt to trip the main turbine from the control room was unsuccessful and it was subsequently tripped locally. At this time the plant is stable and indications show that the RPS actuation originated from closure of turbine throttle valves. Determination of the cause of the RPS actuation is ongoing at this time." All rods fully inserted and no relief valves lifted. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-06-15
41778 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-06-08 | 2005-06-15 18:21 | 2005-06-15 | RADIOGRAPHY SOURCE DISCONNECT/ RETRIEVAL AND POTENTIAL OVEREXPOSURE "Consultant for Lamco was conducting a source retrieval on June 8, 2005 and personnel monitor fell near the 70 Curie radiography source. She picked it up when she realized it and had it returned to the supplier for processing. After receiving the results on June 13, 2005, she called to report the results. The personnel monitor received 9.477 rem, deep dose equivalent. The consultant estimated she received 1.5 rem based on her direct reading dosimeter after the source recovery was completed." Texas Incident # I-8236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-06-20
41777 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-06-15 08:02 | 2005-06-15 16:06 | 2005-06-15 | EMERGENCY OFFSITE FACILITY DECLARED INOPERABLE DUE TO AIR FILTRATION FAN FAILURE TO START "On 06/15/2005 at 08:02 [CDT] the Callaway Plant declared the Emergency Offsite Facility (EOF) Inoperable due to the EOF air filtration fan not starting when the system was switched from Normal to Filtration Mode. This was discovered during a scheduled emergency plan drill. "Repair of the ventilation system is being pursued in a priority manner. Compensatory measures have been put in place. The Backup Emergency Offsite Facility (EOF) is available to support the Emergency Plan. "The resident inspector was notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-15
41775 | 0 | HUMBOLDT BAY | 3 |  |  | [3] GE-1 | 2005-06-14 20:00 | 2005-06-15 | 2005-06-15 | NOTIFICATION OF UNUSUAL EVENT DUE TO TSUNAMI WARNING At 1951 PDT, an earthquake of magnitude 7.4 on the Richter scale was reported at a location near Crescent City, CA. This is approximately 85 miles NW of Humboldt Bay and about 300 miles NW of San Francisco, CA. Based on the earthquake, a Tsunami Warning was issued for California coastal sites by NOAA and promulgated by the California State Warning Center. Based on the Tsunami Warning, Humboldt declared an Unusual Event at 2000 PDT. The licensee stated that the earthquake was not felt at Humboldt but that precautionary measures had been taken to move plant staff to higher ground for personnel safety based on the Tsunami Warning. During the initial notification call from the licensee, notification was received from the California State Warning Center that the Tsunami Warring had been canceled. The licensee has been coordinating with local authorities. The NRC remained in the Normal Mode. * * * UPDATE FROM EASLEY TO HUFFMAN AT 1235 EDT ON 06/15/05 * * * Based on the cancellation of the Tsunami Warning the licensee terminated the Unusual Event at 2104 EDT. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-06-15
41774 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-06-14 20:50 | 2005-06-15 00:10 | 2005-06-15 | NOTIFICATION OF UNUSUAL EVENT DUE TO TSUNAMI WARNING Diablo Canyon Units 1 and 2 declared a Notification of Unusual Event at 2050 PDT 06/14/05 due to the receipt of a Tsunami Warning from the California State Warning Center. The licensee notified State and local agencies and will notify the NRC Resident Inspector. The NRC remained in the Normal Mode. * * * UPDATE FROM D. BAHNER TO M. RIPLEY 0045 EDT 06/15/05 * * * The Tsunami Warning was cancelled and Diablo Canyon Units 1 and 2 terminated the Notification of Unusual Event at 2138 PDT 06/14/05. The licensee notified State and local agencies and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-06-15
41773 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2005-06-14 11:24 | 2005-06-14 17:13 | 2005-06-14 | GREATER THAN 25% OF THE LICENSEE NOTIFICATION SIRENS BECAME UNAVAILABLE "On June 14, 2005, at 1124 hours (CDT), greater than 25% of the CPS (Clinton Power Station) notification sirens became unavailable due to a loss of power. The loss of power affected 13 of the 44 emergency sirens. The cause has not yet been determined. At 1307, three sirens were restored. As of 1436 hours, only one siren was inoperable. Restoration of the inoperable sirens is continuing." The NRC Senior Resident Inspector, Illinois Emergency Management Agency, and DeWitt County ESDA have been notified. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-14
41772 | 0 | INTERSTATE CONCRETE AND ASPHALT |  |  |  |  | 2005-06-09 18:30 | 2005-06-14 15:37 | 2005-06-14 | LICENSEE REPORTED DAMAGED TO A CPN MODEL MC-3 NUCLEAR GAUGE The Interstate Concrete and Asphalt Company reported that a dump truck ran over a CPN nuclear gauge at a construction site in Coeur d' Alene, ID. The gauge was tested for source leakage and none was detected. The gauge which contained 10 millicuries Cs 137 and 50 millicuries Am/Be was still intact, however, it was not operational. It will be returned to the manufacturer in CA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | ID | MAT | [5 empty] | 0 | 2005-06-14
41771 | 0 | BURLE INDUSTRIES INC |  |  |  |  | 2005-06-10 | 2005-06-14 13:52 | 2005-06-14 | LOST SEALED TRITIUM SOURCE The licensee reported they discovered one missing gaseous tritium light source from a total of 892 at the site (550 had previously been shipped to their Mexico plant). The missing light source, which measured 27 millicuries, was to be part of a shipment of 700 to be returned to the manufacturer, SRB Technologies, since they are being replaced by LED light sources. These lights, which are mounted in blocks of Lucite, are used in the production of photomultipliers which are used in equipment produced for the medical industry. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-06-14
41770 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2005-04-15 15:15 | 2005-06-14 13:45 | 2005-06-14 | INVALID ACTUATION DURING EXCESS FLOW CHECK VALVE TESTING "At 1515 hours on April 15, 2005, while conducting excess flow check valve testing in conjunction with a reactor vessel pressure test during a scheduled refueling outage, Unit 1 received an invalid Anticipated Transient Without Scram (ATWS) Channel A trip signal and invalid reactor Lo-Lo water level trips on the A and C channels for ECCS. The operating Reactor Recirculation pump (1 A) tripped and both Emergency Diesel Generators (Unit 1 and Unit 0) auto-started and ran unloaded. RCIC received an initiation signal, which resulted in proper valve repositioning for the system but no injection due to the steam supply being isolated to support the reactor vessel pressure test. In addition, all appropriate running equipment tripped due to load shedding. Reactor pressure was 787 psig at the time of the event and no pressure transient or vessel injection occurred. All equipment responded to the actuation as expected for plant conditions. The excess flow check valve testing was stopped and the reactor vessel pressure test was terminated as a result of this invalid actuation. "It was subsequently determined that a leaking drain valve at the instrument rack where the excess flow check valve testing was being performed caused a slow depressurization of the high-pressure side sensing line for the level transmitters associated with ATWS Channel A and the A and C channels for ECCS, resulting in an erroneous level signal and the invalid actuation. The instrument rack drain valve is scheduled for replacement." The NRC Resident Inspector was notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-06-14
41768 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-05-27 | 2005-06-13 17:20 | 2005-06-17 | NC AGREEMENT STATE REPORT ON HDR SOURCE MISSING IN TRANSIT A Varian Medical Systems technician replaced a source from a high dose rate (HDR) brachytherapy unit at the Forsyth Memorial Medical Center on 5/26/05. The technician then shipped the replaced source on 5/27/05 in a type A package via Federal Express to Excel Logistics (Freight Forwarder for Varian) in Sterling, Virginia. The shipped source contains 3.3 Curies of Iridium-192. The source was not received at Excel Logistics Sterling, VA. The Varian Radiation Safety Officer contacted the Federal Express on 6/10/05. The package was reported missing with its last known location at the Federal Express hub in Memphis, Tennessee. The search for the package is ongoing. * * * UPDATE FROM DR. C. HARRIS TO W. GOTT AT 1152 ON 06/17/05 * * * The missing source was located at 1030 on 06/17/05. It had been misrouted to Paris, France, found, and then rerouted to Memphis, TN. It will be forwarded to Excel Logistics in Sterling, VA. Varian Medical Systems is sending a technician to Excel Logistics to inspect the package before it is forwarded to Belgium. Notified R1DO (Krohn), NMSS (R. Correia), and emailed to TAS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-06-16
41767 | -1 | U.S. ARMY |  |  |  |  | 2005-06-10 | 2005-06-13 09:39 | 2005-07-12 | STOLEN M-22 AUTOMATIC CHEMICAL DETECTORS Five M-22 Automatic Chemical Detectors were stolen from the NBC Room (locked secure storage) at Fort Campbell, KY. The theft was discovered on June 10, 2005. Each device contains 20 milliCuries of Nickel - 63. The Army Criminal Investigative Service and the Fort Campbell Military police are conducting an investigation. The Device serial number/source serial numbers are: Y14M0989/Y14C0989, Y14M08283/Y14D08283, Y14M08429/Y14D08429, Y14M08075/Y14D08075, Y14M08548/Y14D08548. The licensee notified R3 (D. Wiedeman) * * * UPDATE AT 10:00 AM ON 7/8/05 FROM T. GIZICKI TO P. SNYDER * * * U. S. Army TACOM Command Rock Island, IL called to update the event. It was discovered that the detectors reported as stolen on 10 June 2005 were not stolen but inappropriately removed from a storage room. The Army found the material in another room on 20 June 2005. Notified R3 (L. Kozak), R1 (G. Bowman), and NMSS EO (J. Hickey) *** RETRACTION AT 09:10 ON 07/12/05 FROM J. HAVENNER TO J. KNOKE *** U. S. Army TACOM Command Rock Island, IL (Havenner) stated that upon further investigation of the incident it was concluded the radioactive material was never lost and no criminal act was involved, therefore the Event Notification is retracted. Notified R1 (Henderson), R3 (Pelke), and NMSS EO (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-06-13
41766 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-06-11 13:10 | 2005-06-11 15:30 | 2005-08-09 | MINIMUM SWITCHYARD VOLTAGE REQUIREMENTS NOT MET "At 1310 on June 11, 2005 Quad Cities Station was notified that the calculated post-LOCA switchyard voltage is below the minimum acceptable value required to ensure offsite power will remain available following a design basis accident. The appropriate Technical Specification Actions have been taken for both Units. The ability of the Emergency Diesel Generators to fulfill their design function is not affected by this condition. This event is being reported in accordance with 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function given the predicted post-LOCA switchyard voltage. "Actual Switchyard voltage at the time of this notification is 356 Kv. The required minimum post-accident switchyard voltage for current conditions is 352.9 Kv for U-1 and 351 Kv for U-2, while the projected post-accident voltage which prompted this notification is 347.4 Kv. "This notification is similar to the condition reported on March 24, 2005 (EN #41524), April 4, 2005 (EN #41562) and April 11, 2005 (EN #41587)." Both Units entered T.S. 3.8.1 which requires verification of EDG operability (completed) and continued monitoring of line voltages with restoration of at least one offsite-line to the required minimum within 24-hours. The licensee informed the NRC Resident Inspector. * * * UPDATE 1610 EDT ON 6/11/05 FROM RON RUSTICK TO S. SANDIN * * * At 1505 CDT both Units exited T.S. 3.8.1 when projected post-accident line voltage reached 353.8 kV. Notified R3DO (Lara). * * * RETRACTION FROM J. COX TO W. GOTT 1906 ET 08/09/05 * * * "The purpose of this report is to retract ENS report #41652 (April 29, 2005), ENS report 41766 (June 11, 2005), and ENS report #41801 (June 27, 2005). The reports were made following notification that the switchyard predicted voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. For each event, both sources of offsite power were declared inoperable, the appropriate Technical Specification required actions were taken for the units, and an ENS notification was made for a condition that could have prevented the fulfillment of a safety function. "Each Quad Cities unit has two sources of off-site power. For a specific unit, one source is from the switchyard through the unit's Reserve Auxiliary Transformer (RAT) and the second source is from the switchyard through the opposite unit's RAT. Following further analysis of the loading on the RATs during an accident, it was determined that only one source of offsite power to each unit should have been considered inoperable. The analysis determined that because the RAT for the non-accident unit (i.e., the offsite source supplied through the opposite unit) would be carrying a much smaller load, it would not be subject to a degraded voltage condition and resultant isolation from the grid. Therefore, an accident on one unit would not affect the operability of the source of offsite power supplied through the opposite unit's RAT. As a result, only the source of offsite power supplied through the unit's RAT was inoperable. With one source of offsite power available at all times, there was no condition present that could have prevented fulfillment of a safety function, and therefore, these events are not reportable." The licensee notified the NRC Resident Inspector. Notified R3 DO (R. Lanksbury) | 85 | 95 | 0 | 85 | 95 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-06-11
41765 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2005-06-10 13:51 | 2005-06-10 20:55 | 2005-06-10 | LOSS OF OFFSITE BUS DUE TO A LIGHTING STRIKE WITH ACTUATION OF EMERGENCY DIESEL GENERATOR "At 1351 hours, a lightning strike resulted in a loss of Offsite Circuit #751. Loss of Circuit #751 resulted in a momentary loss of Bus 16 until its re-energization by Emergency Diesel Generator B. Safeguards Bus 17 remained de-energized as its Supply Breaker from Emergency Diesel Generator B failed to close as expected. "Additionally, while responding per applicable Abnormal Procedures, Service Water Pump A was manually started. Service Water Pump A tripped approximately 2 minutes later with a report of smoke and sparks emanating from the Service Water Pump A motor. Due to the loss of Safeguards Bus 17 and Service Water Pump A, the plant ran on Service Water Pump C only. Emergency Diesel Generator B was transferred to alternate cooling during the event. "The plant remained stable in Mode 1, 100% power, Tavg at 561°F, and RCS pressure at 2235 psig during the entire event. Emergency Buses 16 and 17 are now powered by Offsite Circuit #767. Service Water Pumps B and C are now operating. Offsite Circuit #751 has been restored to operable status. "Emergency Diesel Generator B is secure and remains inoperable per Technical Specifications while work continues on the Emergency Diesel Generator B Supply Breaker to Bus 17. "Service Water Pump A remains inoperable while work continues on it's motor." Licensee stated that they are in a 7 day LCO for restoring the equipment. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-06-10
41764 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-06-10 | 2005-06-10 17:33 | 2005-06-10 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The State of Florida reported that a Troxler gauge, Model # 3411B, Serial # 8280, was found in the trunk of a vehicle in which the occupants were being investigated for attempted robbery. The incident location was at a Wal-Mart store in Lake City, Florida. The gauge, which was impounded and placed in Florida's DOT District Office, was found undamaged. The Soil Moisture Density Gauge will remain in a licensed storage area until picked up by the owner. The isotopes used in the gauge are 10 mCi of Cs-137 and 40 mCi of Am-241/Be. Incident Number FL05-093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2005-06-15
41763 | 0 | EDWARD W. SPARROW REGIONAL CENTER |  |  |  |  | 2005-06-10 | 2005-06-10 14:07 | 2005-06-22 | FRACTIONAL DOSE DELIVERED DIFFERED FROM THE PRESCRIBED DOSE "A hyperthyroid therapy patient received one of the intended two Nal-131 capsules sent by the radio pharmacy for the therapy. The patient received 10.2 mCi in one capsule instead of the intended 20.6 mCi in two capsules. Both capsules were received in one plastic vial inside of a lead shield. The entire vial was assayed and the assay of 20.6 mCi was within 10% of the prescribed dose of 20.0 mCi. The technologist failed to notice that there were two capsules in the vial because a desiccant inside the vial blocked the view of the second capsule and prevented the second capsule from leaving the vial. Normally, hyperthyroid therapy doses are received in one capsule. Therefore, the technologist was not expecting a second capsule. "The radio pharmacy discovered the second capsule when the package was returned to the pharmacy the next day, June 10, 2005. They called the Nuclear Medicine department at 8:30 am on June 10, 2005. The prescribing physician was called and he requested that the patient receive the second capsule. The patient returned to the Nuclear Medicine department at 10:00 am on June 10, 2005 and received the second capsule, which assayed at 9.74 mCi at that time. The total dose the patient received was 19.94 mCi. "Why the event occurred: Hyperthyroid therapy doses are normally received in one capsule. The technologist was not expecting a second capsule. The desiccant placed in the vial by the radio pharmacy obscured the second capsule from the technologist's sight. The desiccant also prevented the second capsule from coming out of the vial when the first capsule came out of the vial. "Effect on the patient: The prescribing physician does not believe this event will have a negative effect on the patient as she received the remainder of the dose within 24 hours. "To prevent recurrence of this action the licensee will assay all applicable capsule vials after the patient has received their dose, but before the patient leaves the department. This will ensure that no capsules remain in the vial. "Certification that the licensee notified the individual: The patient was notified by telephone on June 10, 2005 and the patient returned to the hospital to receive the second capsule of 9.74 mCi Nal-131." * * * RETRACTION ON 06/13/05 AT 1720 BY MARTY JOHNSON TO CHAUNCEY GOULD * * * Based on a re-reading of Part 35 and a conversation with Region 3 Materials Inspection and Materials Licensing Branches it was determined that this is not a medical event and should be retracted. Notified Reg 3 RDO (Patrick Louden) and NMSS (Patricia Holahan) * * * UNRETRACTION ON 06/22/05 AT 0945 EDT BY MARTY JOHNSON TO HOWIE CROUCH * * * Through discussions with Region 3, the licensee was informed that the NRC has determined this event is, in fact, a medical event therefore should not be retracted. Notified R3DO (Burgess) and NMSS (Michelle Burgess). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-06-10
41762 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2005-06-10 09:24 | 2005-06-10 09:55 | 2005-06-10 | MANUAL REACTOR TRIP DUE TO SERVICE WATER LEAK IN EXCITER CABINET At 0924 on 06/10/05, Indian Point 3 was manually tripped due to a service water leak in the main generator exciter. All control rods fully inserted. Plant response was as designed. Unit 3 is stable in Mode 3. Investigation is ongoing. Unit 2 [was not affected and] remains at 100% power." The steam generators are discharging steam to the main condenser to remove decay heat. The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-06-10
41761 | 0 | AMETEK SOLID STATE CONTROLS |  |  |  |  | 2005-06-07 | 2005-06-10 09:07 | 2005-06-10 | PART 21 REPORT INVOLVING A POTENTIAL FOR PREMATURE FAILURE OF CONTROL ROD INSTRUMENTATION POWER SUPPLY Ametek Solid State Controls produces AC-DC power supplies that are used at several nuclear power plants. Ametek states that its Series AC-DC power supplies may have a problem with premature failure. The specific Model Numbers affected are as follows: 85-RP1510-00 85-RP4804-00 85-RP4808-00 85-RP DUAL-4807\1 Ametek states that an intermittent loss of continuity in a magnet wire connector may cause overheating in a lug and transformer which could eventually result in a premature failure of the power supply ( within approximately two years of initial service). The problem was discovered during testing of a power supplies by Ametek. No nuclear power plants have reported any problems with the power supplies. Ametek states that its records indicate that these power supplies were supplied to Braidwood, Byron, and DC Cook. Ametek believes that the power supplies are used for control rod instrumentation. A total of 33 power supplies have been sold but Ametek believes that most of these are not in service. Ametek recommends that these power supplies either be returned to Ametek for rework or that the affected sites request a service by an Ametek representative onsite. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | OTH | PAR | 21.21 |  |  |  | 0 | 2005-06-10
41760 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-04-14 15:40 | 2005-06-09 14:12 | 2005-06-09 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION WHILE PERFORMING RE-TERMINATION. "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73 (a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 1540 on April 14, 2005, with the Duane Arnold Energy Center (DAEC) shutdown for refueling, an invalid Group 3 isolation on the 'A' side of PCIS occurred. Group 3 isolation signals were generated for Primary Containment Isolation Valves for Drywell and Torus Ventilation, and Purge, Containment Nitrogen Compressor Suction and Discharge; Recirculation Pump Seals, and Post Accident Sample System. "This event was caused while landing a lead on a relay terminal. During this activity the lead brushed another terminal, causing a fuse to blow which resulted in the inadvertent Group 3 isolation. "All equipment responded In accordance with the plant design. Specifically, all actuations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-06-09
41759 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-04-14 06:13 | 2005-06-09 14:12 | 2005-06-09 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM (PCIS) ACTUATION DURING POST MAINTENANCE TESTING "This 60-day telephone notification is being made under reporting requirements specified by 10CFR50.73 (a)(2)(iv)(A) to describe an invalid actuation of a containment isolation signal affecting more than one system. "At 0613 on April 14, 2005, with the Duane Arnold Energy Center (DAEC) shutdown for refueling, a PCIS Group 7 (Well Water and RBCCW Drywall Isolation Valves) signal was generated during post-maintenance testing on MO-4841A. This event was caused by an error in work planning which resulted in an incorrect relay being listed in a work order. When a jumper was installed across the terminals of the incorrect relay, an isolation signal was generated. "All equipment responded in accordance with the plant design. Specifically, all isolations were complete and successful. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into DAEC's corrective action program for resolution." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-06-09
41758 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-06-08 17:24 | 2005-06-08 22:15 | 2005-06-08 | UNANALYZED CONDITION - FIRE ORGANIZATIONAL PLAN NO LONGER ALIGNED WITH SAFE SHUTDOWN ANALYSIS "It has been identified that during a revision change between Revision 5 of FOP 1.2 (July 20, 2004), and Revision 6 of FOP 1.2 (November 1, 2004), a number of omissions of safe shutdown equipment occurred. Because of these omissions, FOP 1.2 is no longer aligned with the Safe Shutdown Analysis. As a result, some of the manual actions that would be necessary to accomplish safe shutdown are no longer identified in FOP 1.2. "FOP 1.2, Fire Organizational Plan is used by Operations to provide guidance on plant operation for fires within safe shutdown areas. Included in this guidance is a list of safe shutdown equipment affected by a postulated fire and the manual actions that may be required to compensate for the fire damage. "It has been determined that this condition is reportable because the missing procedural guidance may result in safety significant operator actions not being performed which are credited in the Safe Shutdown Analysis. Corrective actions have been entered into the Corrective Actions program, and a procedure revision to correct FOP 1.2 is currently in progress." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-06-08
41757 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-06-03 | 2005-06-08 12:00 | 2005-06-08 | COLORADO AGREEMENT STATE REPORT - INSTRUMENT SOURCE FAILURE AND SOURCE MATERIAL PLACED IN UNCONTROLLED STORAGE LOCATION The State provided the following information via facsimile: "On Monday, June 6, 2005, the Department received a call from the RSO for Martek Biosciences Boulder. He was reporting an incident that occurred at his facility on Friday, June 3, 2005. "Martek Biosciences is a small research laboratory authorized to used milliCurie quantities of P-32, C-14, and H-3. Martek has a Beckman model 3801 liquid scintillation counter. The counter contains an internal 30 microCurie Cs-137 calibration source. "The licensee's RSO reported that the liquid scintillation counter had been producing unusual results and a request for service was made to Beckman. A Beckman serviceman arrived at the facility on Friday to replace the 30 microCurie Cs-137 source. He came without survey equipment and did not have a lab coat. On disassembly of the device for source removal and replacement, it was determined that the source had disintegrated. The licensee RSO surveyed his facility and found contamination on the floor and the lab coat he had loaned to the Beckman serviceman. He decontaminated the areas where he found contamination. "The Department contacted the Beckman serviceman by phone to discuss the incident. He indicated that the remains of the source and some of the contaminated lead shielding had been packaged and removed from the facility. This package was being stored in a rented storage facility pending return to Beckman. The Beckman serviceman did not know the exact address of the storage facility. At the time of the phone conversation, the Beckman serviceman was on vacation and was heading out of state. He was confident that there was no concern for contamination of the package or himself due to the surveys conducted by the licensee RSO. "The Department contacted Beckman to obtain additional information on the 3801 liquid scintillation counter. He indicated that this device is generally licensed and is equivalent to the model 5801. The Beckman representative provided a copy of his California license and a copy of the request to amend the device registry sheet for the liquid scintillation counter. Apparently, Beckman is aware of other source failures for the liquid scintillation counter and has asked for a limited operational life of the source. The Beckman representative was not able to provide the actual address for the storage facility and he could not provide the names of any other service representatives in Colorado who might have access to the storage shed. He indicated that he would provide that information the next day. "Tuesday, June 7, 2005: In phone messages from the Beckman representative the Department received the address of the storage facility and name of the regional service manager for Beckman. "Wednesday, June 8, 2005: The Department received a call from the Beckman service manager. He indicated that there are two service representatives who have the key to the storage shed. The two Colorado service representatives are the only persons with the keys to the storage shed. One of the Beckman service representatives is out of state and a second is currently in Albuquerque, NM. "The Beckman service manager indicated that the Beckman serviceman should not have removed the source from the Martek facility. He also indicated that the shed did not contain any other sources and that it was only used for the storage of parts. One of the Beckman service representative is expected to return to Denver on Thursday morning. He will open the shed for inspection by the Department. "Additional data to be provided to complete this report pending the inspection at Martek and the storage facility." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-06-13
41756 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-05-25 | 2005-06-08 08:08 | 2005-06-08 | AGREEMENT STATE REPORT The State provided the following information via email: "The patient was to receive 2 GigaBecquerel (GBq) (Yttrium-90) from siraspheres. Backpressure from the liver catheter popped the tubing off the 3-way stopcock; approximately 25% of the material was spilled before the tubing could be re-attached. A lower flow rate was used and no further problems were encountered. The spill was contained in the case around the stopcock. Patient received approximately 75% of the material/intended dose. The licensee will send a letter explaining the event. Determination of whether this qualifies as a medical event is the reason for the late NRC notification. Florida continues to investigate. Florida event number: FL05-086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-06-13
41755 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2005-06-07 20:20 | 2005-06-08 02:48 | 2006-12-21 | TWENTY-EIGHT EARLY WARNING SIRENS TEMPORARILY INOPERABLE "On June 7th 2005 at 20:00 hours our EWSS System performed an automated poll of active Early Warning Sirens. Normally this action is completed in 15 to 20 minutes. This polling indicated not all sirens had responded to the automated signal. Emergency planning department personnel were notified and called to site to determine system status. Their attempts to manually poll the active sirens determined that twenty eight (28) sirens were not responding. Our EWSS system consists of one hundred six (106) sirens. A loss of twenty eight (28) sirens left our system at seventy three percent (73%) of its capacity. South Carolina state and the four (4) local counties were notified of the systems condition within one hour as required by our Nuclear Licensing procedure (NL-122). This same procedure requires an eight (8) hour telephone notification to the Nuclear Regulatory Commission. This requirement is based on 10CFR50.72(b)(3)(xiii). "At 00:15 hours June 8th 2005 our communications department located the faulty siren and disabled its radio transponder, this action restored the other twenty seven (27) sirens to service. This restoration was verified by performing a manual poll of active sirens. The South Carolina state and local counties were notified of system restoration. "During the evening hours of June 7th 2005 a thunder storm passed through the station's ten (10) mile emergency planning zone. One siren, Fairfield fifty two (F-52) had apparently been struck by lightning and caused its radio transponder to go into a continuous transmit mode. This errant radio signal blocked the polling signal from the other twenty seven (27) sirens. Based on communications department report had the EWSS system been actuated those twenty eight (28) sirens would not have sounded as required." The licensee has notified State and local authorities as well as the NRC Resident Inspector. * * * UPDATE FROM SUSAN REESE TO JOE O'HARA ON 12/21/06 AT 1013 * * * "On June 7th 2005 at 20:00 hours our EWSS System performed an automated poll of active Early Warning Sirens. Normally this action is completed in 15 to 20 minutes. This polling indicated not all sirens had responded to the automated signal. Emergency planning department personnel were notified and called to site to determine system status. Their attempts to manually poll the active sirens determined that twenty eight (28) sirens were not responding. Our EWSS system consists of one hundred six (106) sirens. A loss of twenty eight (28) sirens left our system at seventy three percent (73%) of its capacity. South Carolina state and the four (4) local counties were notified of the systems condition within one hour as required by our Nuclear Licensing procedure (NL-122). This same procedure requires an eight (8) hour telephone notification to the Nuclear Regulatory Commission. This requirement is based on 10CFR50.72(b)(3)(xiii). "At 00:15 hours June 8th 2005 our communications department located the faulty siren and disabled its radio transponder, this action restored the other twenty seven (27) sirens to service. This restoration was verified by performing a manual poll of active sirens. The South Carolina state and local counties were notified of system restoration. "During the evening hours of June 7th 2005 a thunder storm passed through the station's ten (10) mile emergency planning zone. One siren, Fairfield fifty two (F-52) had apparently been struck by lightning and caused its radio transponder to go into a continuous transmit mode. This errant radio signal blocked the polling signal from the other twenty seven (27) sirens. Based on the licensee's Communications Department Report, if the EWSS had been actuated, all sirens, except the faulty siren struck by lightning would have activated. However, the siren feedback system may not have been able to determine if all sirens activated." The licensee notified the NRC Resident Inspector. Notified R2DO (Munday) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-06-08
41754 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2005-06-07 18:00 | 2005-06-07 22:33 | 2005-06-07 | APPENDIX R SAFE SHUTDOWN STRATEGY DEFICIENCY "This report is a result of an ongoing evaluation of a previously identified deficiency with the Appendix R Safe Shutdown Strategy with respect to use of charging pumps for a fire in Fire Area A06, 1B-32 480V MCC area. "This issue was originally identified on April 8, 2005 during work on the Fire Probabilistic Risk Assessment Project. This was entered into the Point Beach Corrective Action Program, and compensatory fire rounds were initiated. "A postulated fire in the east side of the MCC 1 B-32 could damage both the power and the control cables for charging pumps 1 P-2A and 1 P-2B, and the control cables for redundant charging pump 1 P-2C. The resultant condition of the 1 P-2C charging pump control circuit could prevent operation of this pump as directed in the Safe Shutdown Analysis and FOP 1.2, Potential Fire Effected Safe Shutdown Components. The condition exists as the result of a lack of physical cable separation for power and control cables for the Unit 1 charging pumps. An Operability recommendation was performed for this issue and determined that the condition was Operable but Non-Conforming. "Based on a continuing review of further information related to this condition, it has been determined that this condition is reportable based on the resultant effect on available charging pump capability. The condition could have resulted in losing the availability of all but a single charging pump operating at slow speed, which would not provide sufficient reactor coolant pump seal cooling, and thereby degrade the level of plant safety. The identified condition requires a revision to the Safe Shutdown Analysis. "Plant fire mitigation procedure changes to ensure adequate charging pump capability, and reactor coolant pump seal cooling have been made. The Safe Shutdown Analysis will be revised." The Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-06-07
41753 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-06-07 14:37 | 2005-06-07 15:30 | 2005-06-08 | UNUSUAL EVENT DECLARED DUE TO UNIDENTIFIED DRYWELL LEAKAGE GREATER THAN 10 GPM "Hope Creek manually scrammed the reactor from 100% power at 1413 and declared an Unusual Event due to unidentified drywell leakage exceeding 10 gpm (EAL 2.1.1.b) at 1437. The drywell unidentified leak rate peaked at approximately 15 gpm and is currently 12 gpm and slowly lowering. All safety systems were operable prior to the transient and responded as expected. Drywell pressure peaked at approximately 0.5 psig and is steady using normal drywell cooling (the normal pressure band is 0.1 to 0.7 psig). Drywell and suppression pools sprays were not required to mitigate the drywell pressure transient. Reactor vessel level lowered to approximately -30 inches following the scram and was returned to the normal level band using the feedwater and condensate systems. The expected vessel level 3 (setpoint +12.5 inches) ESF actuations occurred. The plant is proceeding to cold shutdown to investigate the drywell leak." The licensee notified the NRC Resident Inspector. * * * UPDATE BY NRC (HOLIAN) TO HUFFMAN AT 0330 EDT ON 6/08/05 * * * As of 0330, Region I IRC in consultation with NRC/IRD (McGinty) secured from Monitoring Mode based on the plant being stable at about 55 psig (about 300 degrees F) and preparing to initiate shutdown cooling. The leak rate remains at about 8 gpm, and an initial drywell entry determined the source of the leakage to be from the A-loop of shutdown cooling testable check valve (50A ). The valve was found with the position indication failed/separated and an approximate 20 foot plume of steam/liquid coming out. Plans are to continue to cool down the plant, go onto the B-loop of shutdown cooling , and isolate valve 50A. The licensee has conservatively remained in the UE and plans to exit when leak rate is assured to remain below 10 gpm (EAL entry condition) or cold shutdown is achieved and the EAL is no longer applicable. The licensee's outage center remains manned, and an NRC inspector remains on site around the clock. DHS (Hoisington), FEMA (Sweetser), DOE (Turner) EPA (Crews), USDA (Pimmons), HHS (Williams) were notified. * * * UPDATE BY NRC (MANGAN - RG 1) TO HUFFMAN AT 0500 EDT ON 6/08/05 * * * The licensee has placed RHR loop B into service and reached Mode 4 (cold shutdown) at 0455. Preparations are in progress to isolate the leak by closing manual valve 183. * * * UPDATE FROM LICENSEE (WILSON) TO HUFFMAN AT 0530 EDT ON 6/08/05 * * * The licensee terminated the Unusual Event at 0515 EDT based on reaching cold shutdown with the leak rate less than 10 gpm. The licensee notified the NRC Resident Inspector. DHS (Hoisington) and FEMA (Sweetser), R1D0 (Jackson), NRR EO (Hannon), and IRD (Leach) notified. * * * UPDATE FROM LICENSEE (BAUER) TO HUFFMAN AT 1101 EDT ON 6/08/05 * * * "On the morning; of 06/08/05, investigation into a previously reported increase in unidentified drywell leakage (Event #41753) identified the leak location as the F050A residual heat removal (RHR) check valve. The F050A check valve is on the return line to the 'A' recirculation loop,. The F050A check valve was isolated at approximately 0545 hours. The position indication magnatrol assembly for the F050A check valve appears to be the source of the leakage. Additional investigation is proceeding to identify the exact location of the leak as well as address the structural integrity of the valve. "This updated report is being made in accordance with 10CFR50.72(b)(3)(ii). At the time of this notification Hope Creek Generating station is in OPCON 4 [Cold Shutdown] at 122 degrees reactor coolant temperature." The licensee notified the NRC Resident Inspector. R1DO (Jackson) and NRR EO (Jung) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-06-07
41752 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-06-07 11:25 | 2005-06-07 14:33 | 2005-07-26 | UNANALYZED POTENTIAL IMPACT ON EMERGENCY DIESEL GENERATOR OPERABILITY "At 1125 on 6/7/2005 it was determined that the Emergency Diesel Generators A and B were out of service due to the possibility of Tornado Missiles potentially collapsing the D/G Fuel Oil Tank Vents. The Emergency Diesel Generators are required as a support system for RHR Decay Heat Removal and RHR was also declared inoperable at the same time. Technical Specification requirements for RHR Decay Heat Removal are, if less than the required number of heat sinks are operable, then corrective action shall be taken immediately to restore the minimum number to operable status. Actions are being taken to restore full operability of the Emergency Diesel Generators A and B. "Currently RHR is operating and providing decay heat removal and Emergency Diesel Generators are available as a support system for RHR. Event Report # 41528 had similar issues associated with the Emergency Diesel Generators exhaust ducts and their ability to withstand tornado forces." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM G. RISTE TO P. SNYDER ON 7/26/05 AT 1541 * * * "Event Notice #41752 was initiated on 6/7/2005 to report an unanalyzed condition with the Emergency Diesel Generators A and B. The initial analysis for tornado missile strike probability results for the Emergency Diesel Generator fuel oil tank vent lines indicated they could be damaged by a tornado missile to the point they would potentially adversely affect Diesel operability. "Additional analysis was performed and it was determined that the original fuel tank oil vent line configuration was acceptable." The licensee notified the NRC Resident Inspector. Notified R3DO (Mark Ring). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-06-07
41751 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-06-07 10:34 | 2005-06-07 11:45 | 2005-06-07 | OFFSITE NOTIFICATION - OIL SPILL AT PLANT LIQUID DISCHARGE "An oil spill has been reported at the plant liquid discharge to Lake Wylie. The on-site Hazmat Team has responded to the scene. The spill is contained within the discharge cove and cleanup is on-going. The source of the spill is unknown at this time. South Carolina Dept. of Health and Environmental Control and the National Spill Response Center were notified at approximately 1030. Off-site assistance is being requested for cleanup of the spill. The quantity of oil spilled has not yet been determined. The licensee has notified York, Gaston, and Mecklenburg Counties and the NRC Resident Inspector. | 56 | 100 | 0 | 50 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-06-07
41750 | -1 | PENN STATE UNIVERSITY |  |  |  |  | 2005-06-06 11:00 | 2005-06-07 10:44 | 2006-02-21 | LOST OR STOLEN VIAL OF PHOSPHORUS 32 "In accordance with 10 CFR 20.2201 Reports of theft or loss of licensed material [the Penn State University Radiation Safety Officer called] to report missing radioactive material in excess of 10 times the quantity specified in appendix C to part 20. The missing material is one vial of phosphorus-32. The vial contained a nominal 74 MBq (2 milliCuries) of P-32. The material in question was never in the possession of Penn State University. "On June 4, 2005, a Type-A package containing three vials of radioactive P-32 was shipped from California to Penn State University via FedEx (tracking number 689818990843). When the package arrived at Penn State University on June 6, 2005, it only contained two of the three vials of P-32. When the vendor was contacted by Penn State University personnel, the vendor insisted that the material had been placed inside the package as was indicated on the shipping papers. The Penn State Health Physics Office staff member who opened the package reported that the security seal tape was properly attached and that the package displayed no evidence of tampering. "The frozen liquid radioactive material that was not received was in the chemical form of Adenosine 5-Triphosphate (gamma P-32) End Labeling (P-32). Lot number J5E32. The package also contained dry ice. "All other packages in the shipment were double checked to verify that the vial was not present in a separate package. The activity reported on the package's shipping label indicated the that the vial was within the package, the shipping papers indicated that the vial was within the package. The package was shipped by the vendor via FedEx in accordance with their normal procedures." The licensee does not believe the box was opened or the material misdirected. Vendor: MP Biomedicals, Inc 15 Morgan Irvine, CA * * * UPDATED AT 0730 EDT ON 6/8/05 BY HUFFMAN TO MAKE A CORRECTION IN THE EVENT HEADER * * * * * * UPDATED AT 1430 EST ON 2/21/06 FROM CA RAD PGM OFFICE (DONELLE KRAJEWSKI) TO S. SANDIN * * * Received a call from the State of California Rad Program representative. During a followup investigation by CA, it was determined that only two of the three vials ordered had been shipped. CA would update the original licensee NMED report to show that there was no missing rad material. Notified R4DO(Pick) and NMSS(Morell). * * * UPDATED AT 1445 EST ON 2/21/06 FROM ERIC BOELDT TO S. SANDIN * * * Contacted the licensee to provide information received from the State of CA. The licensee is retracting this report based on this information. Notified R1DO(Henderson) and NMSS(Morell). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-06-07
41749 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-06-06 | 2005-06-07 07:37 | 2005-06-07 | FLORIDA AGREEMENT STATE REPORT - LOST AM-241 SOURCE The following information was obtained from the State of Florida Bureau of Radiation Control via e-mail: "Searle marker containing Am-241 source was reported missing from Children's Hospital Miami. Device was bought in early 1980's. This source is in a 'storage only' mode and was last seen during the May 2005 inventory. Florida is investigating." The device description is a Searle marker, manufacturer and model unknown, serial number ACM-24, containing 14 milliCuries of Am-241. Florida Incident Number FL05-088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-06-10
41747 | 0 | NATIONAL NAVAL MEDICAL CENTER |  |  |  |  | 2005-06-06 10:00 | 2005-06-06 15:50 | 2005-06-07 | IRRADIATOR SOURCE STUCK OUTSIDE OF WATER SHIELD Testing was being performed on the panoramic pool irradiator (wet-source storage, cat IV). Two sources were pulled from the water for scram time testing. One of the sources fell back to its storage position however, the second source failed to return to storage. The source is a Co-60 source of approximately 180,000 Curies. The licensee expects to troubleshoot the problem and return the source to its storage location within the next four days (end of the week). The source is stuck eight feet below the water line and the irradiator room is locked. * * * UPDATE FROM S. MILLER TO HOWIE CROUCH @ 1103 HRS. EDT ON 6/7/05 * * * Through troubleshooting efforts, the licensee was able to return the stuck source to its normal storage location. There were no exposures as a result of this event or the troubleshooting effort. Notified R1DO (Jackson), NMSS EO (Hickey) and IRD (McGinty). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNSHIELD STUCK SOURCE | [9 empty] | NON EMERGENCY | 1 | MD | HOS |  | 36.83(a)(1) |  |  |  | 0 | 2005-06-06
41746 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-06-06 12:33 | 2005-06-06 15:44 | 2005-06-06 | AUTOMATIC REACTOR SCRAM DUE TO APPARENT GENERATOR LOAD REJECTION "At approximately 1233 hours, the Susquehanna Unit Two reactor automatically scrammed due to an apparent generator load reject. All rods inserted, and both reactor recirculation pumps tripped. Reactor water level lowered to -6" causing level 3 (setpoint +13") isolations, and was restored to normal level (+35") by the feedwater system. All isolations at this level occurred as expected. Two steam relief valves opened, then reclosed. Pressure was subsequently controlled via turbine bypass valve operation. All safety systems operated as expected. Some balance of plant loads shutdown apparently due to a voltage perturbation. "A reactor recirculation pump was restarted to re-establish forced core circulation. The reactor is currently stable in condition 3. An investigation into the cause of the shutdown is underway. Unit One continued power operation. "The NRC resident inspectors were notified. A press release will occur." The licensee will be notifying the State of Pennsylvania. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-06-06
41745 | 0 | SAN ONOFRE | 1 | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-06-03 06:33 | 2005-06-03 14:57 | 2005-06-03 | FITNESS FOR DUTY - NON-LICENSED SUPERVISOR FAILED BREATHALYZER A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness for duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2005-06-03
41744 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-06-03 | 2005-06-03 13:10 | 2005-06-03 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The gauge was damaged by a construction vehicle while the moisture density gauge was in use. The probe was not extended at the time of the accident. There was no release from the radioactive source. The state will follow up with the licensee. Troxler Serial 28753 Sources: Am-241 40milliCuries Cs-137 8 milliCuries Texas Incident Number: I-8235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-06-08
41743 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-06-03 00:33 | 2005-06-03 01:00 | 2005-06-15 | DECLARED UNUSUAL EVENT DUE TO RCS LEAKAGE IN EXCESS OF TECHNICAL SPECIFICATION LIMIT "Declared Unusual Event due to RCS leakage greater than 10 gallons per minute. VCT level is lowering with constant plant temperature, pressure and pressurizer level. VCT level lowering at approximately 19 gallons per minute with associated rise in RWST level approximately 20 gallons per minute." The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM MELIN TO W. GOTT AT 0120 ON 06/03/05 * * * The licensee briefed NRC Management (McGinty, P. Hiland, R. Haag, J Munday) that the leakage was verified to be CVCS leakage and not RCS leakage. The leakage was stopped at 0055 and the licensee is evaluating termination/retraction criteria. NRC will not enter Monitoring Mode. * * * UPDATE FROM G MELIN TO W. GOTT AT 0140 ON 06/03/05 * * * "At 0055, leakage stopped. Leakage verified to be CVCS leakage, not RCS. The leakage is stopped. Validating no other anomalies exist then will evaluate termination and retraction of UE notification." * * * UPDATE FROM G MELIN TO P. SNYDER AT 0221 ON 06/03/05 * * * "Notification of termination of Unusual Event at 0221. Plant validation complete. RCS gross leakage is 0.07 gallon per minute and plant parameters are stable. Leakage confirmed to be from CVCS system which has been isolated." The licensee will notify the NRC Resident Inspector. Notified R2DO (R. Haag), NRR EO (P. Hiland), IRD (T. McGinty), R2 (J. Munday), DHS (I. Lee), FEMA (C. Ligget), and DOE (M. Smith) * * * UPDATE ON 6/15/05 @ 1243 FROM JIM SPEICHER TO CHAUNCEY GOULD * * * RETRACTION Event Notice 41743 reported declaration of an Unusual Event at 00:33 on 6/3/05 for RCS leakage in excess of Technical Specification Limits. The source of leakage was subsequently determined to be from the Chemical and Volume Control System (CVCS) and not from the RCS. The Unusual Event was terminated at 02:00 6/3/05 after the leak was isolated. This event is retracted since the source of the leakage was not from the RCS and upon further review the event did not meet reporting requirements. The NRC Resident Inspector was notified. RDO (Tom Decker), EO (M. Mayfield) and IRD (Peter Wilson) were notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-06-03
41742 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-06-02 17:49 | 2005-06-02 21:51 | 2005-06-02 | APPENDIX R ASSESSMENT ON REMOTE SHUTDOWN PANEL The licensee provided the following information via facsimile: "On 6/2/05, while performing an Appendix 'R' assessment, it was determined that the capability to achieve and maintain safe shutdown conditions, as required by Appendix 'R', has not been adequately demonstrated. Specifically, a postulated fire requiring the evacuation of the Control Room could also cause a spurious hot short in the protective relaying circuitry for the credited division of essential electrical power and subsequent loss of that division. It was recently determined that the hot short could occur at anytime during the transient, whereas previous evaluations had assumed any such hot short would be associated with the initiating event. Consequently, existing compensatory measures would only be implemented if the adverse consequences were apparent, and therefore might not be implemented within the timeframe required to assure satisfactory results. The result is that Appendix 'R' requirements are not met, and an unanalyzed condition that significantly degrades plant safety may exist. "A 30 day LCO was entered at 1749 per Tech Spec LCO 3.3.3.2 Function 4.e for the Remote Shutdown Panel 'B' Essential 4160 Instrumentation transfer and control." The licensee notified the NRC Resident Inspector. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-06-02
41741 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2005-06-01 21:09 | 2005-06-01 23:12 | 2005-06-01 | REACTOR SCRAM DUE TO GENERATOR TRIP/TURBINE TRIP FOLLOWING OFFSITE ELECTICAL TRANSIENT The licensee reported that an offsite electrical transient on the 230KV transmission line appears to have caused a generator trip and corresponding turbine trip and reactor scram. The scram was uncomplicated. All rods fully inserted. No safety relief valves lifted during the transient. The reactor is stable at 920 psi with decay heat being discharged to the main condenser and fed via the main feed pumps. There was no loss of offsite power during the transient and the plant is in a normal electrical lineup. The specific cause of the generator lockout is still under investigation but is believed to have been caused by maintenance work at the Manitou 230KV substation about 25 miles from the plant. Lightning arrestors were being placed in service at the substation and are believed to have resulted in an electrical disturbance on the grid. The licensee notes that switchgear for the stack lighting did trip during the transient and so the FAA was notified on the stack lighting outage. The licensee plans to remain in hot shutdown for approximately 24 hours before restart. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) |  |  | 0 | 2005-06-01
41740 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-05-27 14:00 | 2005-06-01 16:13 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * CONCURRENT REPORT UNDER PART 70 APPENDIX "A" FOR OFFSITE NEWS RELEASE "This concurrent report is being made to the NRC as a result of a Letter to the Editor that was submitted by BWX Technologies, Inc. This letter was submitted in response to recent information that was published on May 26, 2005, in the Lynchburg News & Advance. The May 26, 2005, article specifically asked the question 'Is BWXT highly secure?' The attached letter is related to the adequacy of BWXT's security program and was submitted to the News & Advance at approximately 1400 on May 27, 2005. Although BWXT does not feel that the reporting criteria listed under Part 70, Appendix A is applicable, this article is related to licensed activity. Therefore, a concurrent NRC notification is being made." Contact the Headquarters Operations Officer for the text of the attachment. The licensee will notify the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
41739 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-06-01 08:08 | 2005-06-01 14:33 | 2005-06-01 | CONTAMINATED INJURED PERSON TAKEN TO OFFSITE HOSPITAL "During the R-17 refueling outage, a contract worker fell approximately 15 feet in the condenser. The individual was conscious but unable to egress from the main condenser due to injuries sustained from the fall. A response team was used to bring the worker out of the plant. "Health Physics (HP) technicians accompanied the worker to the hospital. The individual has been transported to Kadlec Medical Center by the Hanford Fire Department. The HP technicians surveyed the individual at the hospital and discovered contamination. "The ENS notification is being made because of the transport of a potentially radioactive contaminated person to an offsite medical facility for treatment. FEMA, State of Washington and local representatives have been notified." A press release will be issued. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | OFFSITE MEDICAL |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xii) |  |  | 0 | 2005-06-01
41738 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-06-01 11:45 | 2005-06-01 12:23 | 2005-06-01 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via e-mail: "Licensee reported that employee's truck, containing moisture density gauge, was stolen from employee's apartment complex parking lot in Hamilton, Ohio sometime between 1:30 AM and 7:00 AM on June 1, 2005. The gauge was chained inside the bed of the pick-up. Employee went home after late work assignment at remote location with the gauge still in the vehicle. The employee failed to follow licensee procedures requiring that the gauge remain in secure location at the remote job site or be returned to licensee's offices. The gauge is a CPN Model MC1DR, containing a 10 mCi Cs-137 source and a 50 mCi Am-241 source (maximum activities). The serial number is MD50407830. A police report (# 29319) has been filed with the Hamilton, Ohio police department. There is no indication at this time that the gauge itself was stolen for malicious purposes. This information is current as of 11:45 PM on 6/1/05." Ohio Reference Number: OH 2005-068 * * * UPDATE FROM STATE (JAMES) TO NRC (HUFFMAN) AT 1430 EDT ON 6/1/05 * * * The licensee provided the following information via e-mail: "Licensee called Ohio Department of Health (ODH) at 2:00 PM on 6/1/05 to report that truck and gauge had been recovered and that gauge was fully intact in shipping container. Licensee further stated that gauge was never technically stolen. Licensee's employee parked in the wrong space at the apartment complex and apartment management had the vehicle towed early this morning. The vehicle, with the gauge, had been at the Hamilton, Ohio police department vehicle impound lot until employee was notified that vehicle had been towed. Once notified, licensee recovered the gauge and is taking it to their Dayton office for storage." ODH representative (Owen) noted in a followup e-mail that [albeit the gauge was] not stolen, there remains an issue of adequate control in accordance with licensing requirements. R3DO (Burgess) and NMSS (Correia) notified. TAS (English) informed via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-06-06
41737 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-05-31 10:00 | 2005-05-31 20:26 | 2005-05-31 | LOSS AND SUBSEQUENT RESTORATION OF EMERGENCY RESPONSE DATA SYSTEM (ERDS) "At about 10:00 (PDT) on May 31, 2005, plant personnel discovered that the plant's Emergency Response Data System (ERDS) was not able to transmit data to the NRC. The problem was discovered during a scheduled test to validate changes to the Columbia Generating Station ERDS data point library. This proposed test included initiating the ERDS and synchronizing to the NRC system. "During the initiation of this test, plant personnel discovered that the ERDS was not able to initiate a connection with the NRC system. The ERDS was subsequently returned to service at 17:15 PDT on May 31, 2005." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-31
41736 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-05-31 10:31 | 2005-05-31 17:22 | 2005-05-31 | OPERATION AT GREATER THAN LICENSED POWER LEVER (106% RATED) DUE TO RECIRC PUMP MOTOR GENERATOR SET FAULT "On Tuesday May 31, 2005, Limerick Unit 2 was operating at 100% power at 10:31 hours when the 2A Reactor Recirculation Motor-Generator speed increased to the high-speed stop. Reactor power increased to approximately 106% and three main steam bypass valves opened as designed to control pressure. Operators reduced power to 98% as directed by emergency operating procedures using the 2B Reactor Recirculation Pump. "This event caused thermal power to exceed the 100% rated maximum power level of 3458 megawatts thermal specified in section 2.C.(1.) of the Limerick Unit 2 operating license. Therefore, this event is being reported via ENS within 24 hours with a written followup within 30 days as required by section 2.E of the Limerick Unit 2 operating license." The licensee stated that power level exceeded 100% for approximately 1 minute during the event transient. Both the mechanical and electrical overspeed stops on the MG set were actuated. The licensee reviewed the transient and it does not appear that any other thermal limits were exceeded and there is no indication of any affect on the core or the fuel. Although trouble-shooting of the problem is still in progress, the licensee currently believes that the event was caused by the MG set controller. The licensee plans to remain at approximately 97% power until the problem is resolved. The licensee notified the NRC Resident Inspector. | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2005-05-31
41735 | 0 | GLOBAL X-RAY AND TESTING CORPORATIO |  |  |  |  | 2005-05-29 06:20 | 2005-05-29 12:11 | 2005-06-06 | RADIOGRAPHY EXPOSURE DEVICE AND SOURCE FELL OVERBOARD "While transferring from the [offshore] platform to a boat, the device and source fell overboard. The source is in it's shielded position; front and back covers are in place. The device and source pose no immediate threat." "BP [the owner] is coordinating a dive team and plan to be on location in 4-5 days. Tentatively on June 3, 2005 weather permitting. "Location: Grand Isle 47 AQ Water Depth: 80 to 100 feet Latitude: 28 56 .7 Longitude: 90 01 .9 [Approximately 15 mi. SE of Fort Fourchon, LA] Time of Incident: 06:20 AM Date: 05/29/05 Exposure Device Mfg/Serial # :Spec 150 # 825 Source Mfg/ Serial #: Spec G-60 Ser# MA-1702 Activity: 44 curies IR-192" * * * UPDATE 1035EDT ON 6/6/05 FROM CHRIS MOREAU TO S. SANDIN * * * After an extensive search involving four (4) divers, the licensee was unable to locate the missing device. The licensee considers the device lost and has abandoned their efforts at recovery. Notified R4DO (Chuck Cain) and NMSS (Richard Correia). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-05-29
41734 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-05-28 13:05 | 2005-05-28 18:45 | 2005-05-28 | FAILURE OF THE PLANT INTEGRATED COMPUTER SYSTEM (PICS) "At 1305 hours [EDT] on 5/28/05, the Plant Integrated Computer (PICS) failed. This process computer provides Safety [Parameter] Display System (SPDS) and Emergency Response Data System (ERDS). Troubleshooting efforts and repairs were performed and ERDS/SPDS were returned to service at 15:55 [hrs.] on 5/28/2005. All redundant plant data indicators, annunciators and recorders functioned normally during the PICS outage." The licensee will be notifying the New York State Public Service Commission and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-28
41733 | 0 | WATERFORD | 3 |  |  | [3] CE | 2005-05-27 21:50 | 2005-05-28 06:34 | 2005-05-28 | OFFSITE NOTIFICATION TO OSHA DUE TO ONSITE FATALITY "In accordance with 10CFR50.72(b)(2)(xi), this report is being made to notify the NRC, via ENS, under a four hour report based on a planned notification to OSHA. "Based on 29CFR1904.39(b)(5) and (b)(2) OSHA requirements for notification in case of a fatality at work, the below information will be provided to OSHA. At 04:00 [CDT] on 5/28105, the site decided to report the following information, although the cause of death has not yet been determined. "An employee exited the work area and was found sitting in a chair in the office area slumped over, unconscious, no pulse, no breathing. Ventilation and CPR was initiated. An AED was utilized, and one shock was advised and administered. EMT's arrived [at 21:50 CDT] and transported [the] employee [via ambulance] to the hospital [at 22:07 CDT] without incident, while still performing CPR. The employee was not contaminated." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-05-28
41732 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-05-17 20:00 | 2005-05-27 22:02 | 2005-05-27 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGE A Troxler moisture density gauge was stolen from the back of a pickup truck parked at a licensee employee's residence sometime between 2000 PDT 05/17/05 and 0550 PDT on 05/18/05. The gauge was in its transportation case and the case was strapped down (vice chained) in the back of the truck. The employee delayed notification to the licensee until 5/26/05. The licensee notified the State at 1100 PDT on 05/27/05. The Los Angeles Police Department was notified and the licensee is offering a reward for return of the gauge. The licensee also notified the gauge manufacturer's local representative. The Troxler was a model 3440, Serial Number 29792, with an 8 milliCuries Cs-137 and a 44 milliCuries Am-241/Be source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-06-01
41731 | 0 | FROEHLING AND ROBERTSON, INC. |  |  |  |  | 2005-05-17 15:30 | 2005-05-27 10:27 | 2005-05-27 | DAMAGED TROXLER MOISTURE DENSITY GAUGE "On Tuesday, 5/17/05 at approximately 1530 hours, technician [DELETED] of our Crozet (Charlottesville), VA branch was performing a field density measurement with a Troxler Model 3411 moisture/density gauge (SN 5278) in an area of pipe backfill at the GEI project site in Charlottesville, Virginia. When finished with the test, he exited the trench and placed the Troxler nuclear density gauge at the corner of a fence line opposite the sediment pond behind him and was watching mixed fill being placed as backfill and compacted in the trench. A sheepsfoot roller backed up onto the bank near the fence because a rubber-tired roller was coming down the hill on the access road. [The roller driver] backed over and then pulled away from the gauge when he realized what he had done. "The technician immediately conducted a visual examination and noted that the source rod base (with the Cesium 137 source) had remained inside the gauge, but the source rod itself was bent and the depth gauge rod broken. The site was roped off and the technician called the Crozet office RSO informing him of the incident. A survey meter was sent out to the site to check the gauge and area for radiation levels. Normal readings were noted with the source still in the rod in the gauge. The lock was still on the trigger; but, with the depth rod broken, the source rod could be extracted from the upper side of the gauge. Duct tape was used to wrap the bent source rod to prevent the rod coming out of the gauge during transit. The Corporate RSO was called and informed of the incident. "The gauge was transported back to the Crozet nuclear storage room and marked out of service until repairs are made. "Despite the fact that the technician was in close proximity to the gauge it was not in his direct line of sight or control. " The sources were Cs-137 (8.4 milliCuries on 2/10/78) and Am/Be (40 milliCuries on 2/14/78). The RSO intends to transport the gauge to Troxler for disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2005-05-27
41730 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-03-14 02:47 | 2005-05-26 18:38 | 2005-05-26 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "On March 14, 2005, a fire occurred in a trash receptacle adjacent to a shipping container, in the Cooper Nuclear Station (CNS) Multi-Purpose Facility (MPF). The MPF is a machine shop attached to the Radwaste Building inside the Protected Area of CNS. At 0249 upon receipt of the fire alarm in the MPF and alarms received for the automatic start of station fire pumps, Control Room Operators entered the CNS Fire Procedure and dispatched a Station Operator (SO) to the scene. At 0251 the SO was permitted to fight the fire with a fire hose, and the fire brigade was mobilized. The SO extinguished the fire in the trash receptacle at 0258. The SO reported to the Fire Brigade Leader that he had felt heat from the walls of the adjacent shipping container, but was unable to access it due to being locked. At 0308 the Fire Brigade gained access to the shipping container and reported a small fire inside. At 0313 the fire was extinguished. Subsequently, the embers were overhauled, and the reflash watch was set. No further reflashes occurred. All applicable steps in the Fire Procedure were completed. The apparent cause of the fire was the failure of a large overhead light. "Because these were regarded as two separate fires, CNS did not enter the Emergency Action Level (EAL) for a Notice of Unusual Event (NOUE.) Further review, continued benchmarking with other utilities, and consideration of the lack of a consistent treatment for declaring a fire being out, has prompted CNS to determine that a declaration of NOUE should have been made. Upon making that determination, CNS is required to notify the NRC in accordance with the guidance of NUREG-1022, Revision 2. The event has been concluded and the basis for the emergency no longer exists. "The Licensee will notify both state and local agencies and has informed the NRC Resident Inspector. " The licensee stated that the discovery that a declaration of NOUE should have been made occurred at 1700 CDT 05/26/05. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2005-05-26
41728 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-05-24 13:50 | 2005-05-24 20:00 | 2005-05-24 | UNANALYZED CONDITION INVOLVING EMERGENCY BACKUP POWER GENERATORS "Event: On 5-19-05, Oconee discovered that an electrical contactor had failed at Keowee Hydro Station. This contactor normally can provide auxiliary power from one Keowee Hydro Unit (KHU) to cooling fans on the Keowee Main Transformer, which is part of the Overhead power path (one train of emergency power to the three Oconee units). At the time, power to the cooling fans was being provided by an alternate power source. A problem report (PIP) was written and an Operability Assessment concluded that the Overhead power path was fully operable. On 5-24-05 at 1350 hours, it was recognized that the alternate power source supplying the cooling fans was supplied from the auxiliary power bus associated with the KHU then aligned to the Underground power path (the redundant train of emergency power to the three Oconee units). "It was recognized that this alignment presented a single failure vulnerability in that loss of the auxiliary power bus for the KHU aligned to the Underground path could also result in loss of Main Transformer cooling on the Overhead power path. As a result, Operations declared entry at 1350 hours into Technical Specification (TS) 3.8.1 condition C for the Overhead power path being inoperable (a 72 hour allowed completion time). A review of available information indicates that the electrical contactor actually failed on or before 5-2-05. Therefore the period of vulnerability to this potential single failure was approximately 22 days. This condition is being reported as an unanalyzed condition per guidance in NUREG 1022 section 3.2.4. "Initial Safety Significance: If the postulated single failure occurred during a design basis event, it is expected that, without credit for Operator intervention, both KHUs would fail, but the failure is not expected until a minimum of one hour after the loss of auxiliary power. During this time Operations would have been able to realign the KHU with auxiliary power to the Underground path and/or to have started and aligned a combustion turbine at Lee Steam Station. Therefore, the condition being reported is not expected to result in a loss of safety function. "Corrective Action(s): The immediate corrective action was to realign the Keowee units to the opposite power paths. This aligned the KHU capable of supplying power to the Main Transformer cooling fans to the Overhead path. The KHU associated with the failed contactor was aligned to the Underground path. The TS condition was exited at 1540 hours when this realignment was complete." The licensee notified the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-05-24
41726 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-05-24 09:14 | 2005-05-24 15:33 | 2005-05-24 | FITNESS FOR DUTY A non-licensed employee supervisor had a confirmed positive for alcohol during a random fitness-for-duty test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2005-05-24
41725 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-05-23 17:47 | 2005-05-23 20:07 | 2005-06-08 | MANUAL SCRAM DUE TO CONDENSER HOTWELL CHEMISTRY "Based on increasing conductivity in the reactor vessel and condenser hotwell, a power reduction was initiated from 100 percent power. A manual scram was inserted at 57 percent RTP and 49 percent Core Flow based on Chemistry recommendations due to sulfates and chlorides in the hotwell. Following the scram a reduction in reactor water level to -28 inches resulted in a Primary Containment Group 2 Isolation (ESF) occurring. All isolations and systems responded as expected. "Current plant status is Hot Shutdown with plans to proceed to cold shutdown." All control rods fully inserted and decay heat is being removed with the bypass valves into the condenser. The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM SHIFT SUPERVISOR (TONY SPRING) TO ABRAMOVITZ AT 16:33 ON 6/6/2005 * * * "After further review and evaluation it has been determined that the four hour call made May 23, 2005 per the guidance of 50.72(b)(2)(iv)(B) should be retracted. "A review of the event with respect to NUREG 1022 Revision 2 determined that: "The manual scram was part of a pre-planned sequence to shut the plant down due to an equipment problem. The manual scram was part of a pre-planned sequence. The guidance to scram the reactor was established by the plant's Abnormal Operating Procedure addressing a condenser tube leak and was part of a preplanned sequence to prevent future equipment and component failures. The Manual Scram was not inserted to protect the plant against an event that presented a challenge to an FSAR analyzed event. In other words, this was not an Anticipated Operational Occurrence, an Accident, or a Special Event as defined in section 15.1.3 of the Unit 2 FSAR. Rather it was part of a plan to shutdown the reactor to protect against future potential equipment problems due to out of limits chemistry parameters. Further justification is provided by the fact that the manual scram was not initiated in anticipation of an automatic scram. "Per NUREG 1022 Rev. 2: 'The staff also considers intentional manual actions, in which one or more system components are actuated in response to actual plant conditions resulting from equipment failure or human error, to be reportable because such actions would usually mitigate the consequences of a significant event. This position is consistent with the statement that the commission is interested in events where a system was needed to mitigate the consequences of the event.' "However, the reporting requirement itself indicates that actuations that result from pre-planned sequences are not reportable. An example is provided in the NUREG of an equipment problem involving the loss of recirc pumps. In this example it is stated that: 'Even though the reactor scram was in response to an existing written procedure, this event does not involve a preplanned sequence because the loss of the recirc pumps and the resultant off-normal procedure entry were event driven, not pre-planned.' "This is similar to our event, however, in the NUREG example, the reactor is scrammed to protect against the possibility of a stability event and stability is an FSAR analyzed event. In our case we were shutting down for chemistry reasons, not an FSAR type event. "It is concluded that when the RPS is used to shutdown the reactor as part of a plan for the resolution of equipment problems, and the RPS is not needed to mitigate the consequences of an FSAR analyzed event, i.e., one which threatens a fission product boundary (i.e., fuel cladding, RCPB, primary and secondary containments), the RPS actuation is not reportable under 50.72(b)(2)(iv)(B)." The licensee notified the NRC Resident Inspector. Notified R2DO (Haag). * * * RETRACTION RESCINDED - S. BURTON TO M. RIPLEY 1524 EDT 06/08/05 * * * "On May 23, 2005 a four hour report was made per the guidance of 50.72(b)(2)(iv)(B), 'Any event or condition that results in an actuation of the RPS when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' This was made per event # 41725. The report was made within the four hour time frame of 10 CFR 50.72(b)(2). "The four hour report for event # 41725 was retracted on June 6, 2005. "After further consideration, the retraction made on June 6, 2005 is being cancelled and the original report re-instated." The licensee notified the NRC Resident Inspector. Notified R2 DO (K. Landis) | 0 | 0 | 0 | 0 | 57 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-05-23
41724 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-05-23 15:12 | 2005-05-23 16:25 | 2005-05-23 | OFFSITE NOTIFICATION - SMALL FIRE IN OWNER CONTROLLED AREA OUTSIDE OWNER PROTECTED AREA A small pile of scrap wood, located [near motor pool service area] outside the Owner Protected Area (OPA), was discovered to be on fire. The local fire department was notified at 15:12 EDT and responded onto the Owner Controlled Area . The fire was extinguished by onsite fire brigade and offsite fire agency [personnel] by 15:25 EDT. The licensee will be notifying State and County authorities, and has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-05-23
41723 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2005-05-20 18:40 | 2005-05-21 18:39 | 2005-05-21 | DEVIATION FROM INTEGRATED SAFETY ANALYSIS, AND A 24 HOUR NOTIFICATION - BULLETIN 91-01 CRITICALITY CONTROL "Facility Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia, SC, low enriched PWR fuel fabricator for commercial light water reactors. "Time and Date of Event May 20, 2005, 1840 hours. "Reason for Notification During a routine filter change-out in a HVAC recirculation filter housing, maintenance mechanics detected an excessive amount of material buildup on the filters and contacted the ventilation engineer. Human performance training at the plant has engendered a heightened awareness for process upsets or unusual conditions in all plant personnel. "The ventilation engineer examined the filter housing beneath the filter array and discovered a minor build up of powder in the corners of the housing. This caused him to contact the Nuclear Criticality Safety function. The ventilation engineer and the NCS engineer had samples pulled from the powder and filters to confirm the absence of uranium. The system was believed to serve hoods where entrainment of uranium was not credible, i.e. hoods that contained only sintered pellets, not powder in any form. The samples from the filters returned results in a range from 3.5 to 50 weight percent uranium (average 19 weight percent). "This notification [Deviation from Integrated Safety Analysis] is made in accordance with Appendix A [(b)(5)(i)] to Part 70 - Reportable Safety Events. Events to be reported to the NRC Operations Center, (b) within 24 hours of discovery, (5) An occurrence of an event or process deviation that was considered in the Integrated Safety Analysis and : (i) Was dismissed due to its likelihood. "As Found Condition The samples from the filters returned results in a range from 3.5 to 50 weight percent uranium (average of all samples for filters was 19 weight percent). An approximate mass of material mass held up in the filters is 119 kg. Based on the average weight percent uranium, the mass of uranium held up in the filters was 22.6 kg, which is less than a critical mass for spherical fully reflected UO2 and water system. The system was already shut down for filter replacement. "Summary of Activity The entire functional area that the system serves was shut down immediately. A team of process experts, system experts, NCS specialists, maintenance personnel, and management was immediately formed to determine the source of the uranium in the system. "Conclusions At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | DEV FROM ISA | RESPONSE-BULLETIN | [8 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(5) |  |  |  | 0 | 2005-05-21
41722 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-05-20 15:00 | 2005-05-20 17:55 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * CONCURRENT REPORT UNDER PART 70 APPENDIX "A" FOR OFFSITE NEWS RELEASE "This concurrent report is being made to the NRC as a result of [the below stated] press release that was made by BWX Technologies. Inc in response to recent information that has been published and broadcast by local media. This [local media] information has the potential to mislead the public into thinking that BWXT manufactures nuclear weapons at its owned and operated facilities in Virginia, Ohio, and Indiana. "The [below stated] press release was provided to the Lynchburg News & Advance which is a local newspaper, and the following central Virginia television stations: WSET (Lynchburg), WSLS (Roanoke), and WDBJ (Roanoke). The press release was provided to these agencies at approximately 1500 on May 20, 2005. PRESS RELEASE: "Recent information that has been published and broadcasted by local media regarding BWX Technologies, Inc. (BWXT) has the misfortunate potential to mislead the public in thinking that BWXT manufactures nuclear weapons at its owned and operated facilities in Virginia, Ohio, and. Indiana. At these facilities, BWXT does not manufacture nuclear weapons nor will the nuclear materials processed at these facilities be utilized in nuclear weapons. BWXT does not have any plans, and is not in any discussions with the Government, to conduct nuclear weapons manufacturing at these facilities, nor does BWXT plan to pursue this business area for these sites. "For more than 50 years, facilities at these locations have supported other national defense programs for the Department of Energy. In addition, the Virginia facility produces research and test reactor components for laboratories, colleges and universities nationwide. [It] converts enriched uranium for commercial use in support of the fissile material disposition program, and supplies uranium targets for use in the production of medical isotopes." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
41721 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2005-03-31 | 2005-05-20 11:20 | 2005-05-20 | AGREEMENT STATE REPORT LOST/STOLEN TRITIUM SOURCE EXIT LIGHTS "Kellogg's did an extensive inventory of the exit signs at their facility in the past couple months. They determined that nine exit signs are missing, that were listed on a previous inventory. They believe that the signs are now in the local landfill because a number of remodeling projects have been done at Kellogg's. They have communicated with staff and contractors the importance of maintaining control of these devices. Kellogg's is also looking into alternative methods for providing exit signage". Type of sign - Radioluminescent sign Manufacturer - SRB Technologies Inc Model # BXU20SW Serial Numbers - 217791, 217808, 217845, 217897, 217903, 217949, 217950, 217951, 218307 Each sign measured 17.51 Ci tritium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2005-05-25
41720 | 0 | BRYN MAWR HOSPITAL |  |  |  |  | 2005-05-17 | 2005-05-19 15:57 | 2005-05-19 | PART 21 REPORT - MALFUNCTION OF NOVOSTE INTRAVASCULAR BRACHYTHERAPY BETA-CATH SYSTEM TRANSFER DEVICE During a medical procedure on a patient, two individual coronary artery locations were being irradiated with Sr-90 (2.05 GBq, serial # ZA-494). The device being used, Novoste Intravascular Brachytherapy Beta-Cath System Transfer (S/N# 90556), hereinafter called "Device", failed to work properly. The licensee noticed the source did not retract into the Device. At this point the licensee pulled the entire catheter out of the patient, and within one minute was able to return the sources safely into the Device. It was assumed the problem was with the catheter and it's connection to the Device. The licensee continued to the next location on the patient. Upon attempting to return the source, the licensee noticed the sources were not moving from the patient. Within 5-10 seconds, the licensee pulled the entire catheter from the patient, and then placed the entire system into the "bailout" box for proper shielding from beta radiation. The next day the licensee called Novoste and explained the events. Novoste determined it was a faulty Device and sent the licensee a replacement. On May 19, 2005 the replacement arrived and the faulty device was sent back to the company. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 21.21 |  |  |  | 0 | 2005-05-19
41719 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-03-21 | 2005-05-19 13:42 | 2005-05-20 | AGREEMENT STATE REPORT - LOST 12 UNUSED I-125 THERAPY SEEDS TOTALING 4.8 MILLICURIES The State provided the following information via facsimile: "On March 21, 2005, the licensee, Western Medical Center, shipped 12 unused I-125 therapy seeds of 0.4 mCi/seed (4.8 mCi total) to GE Healthcare via Fed-Ex. On April 19, 2005, Fed-Ex notified the licensee by letter that the shipment had apparently been lost in transit. The shipment has not yet been located. [The State] will update NMED as more information becomes available." The Fed Ex shipment information will be forthcoming from the State as they receive it. The State report number is 051905. * * * UPDATE ON 05/19/05 AT 14:58 EDT FROM HAMRICK TO KNOKE * * * "The number of seeds should be 14 at 0.391 mCi/seed for a total of 5.474 mCi (as of 2/26/05; activity is now about 2.12 mCi). "The shipment left the licensee's facility on 3/21/05 via FedEx to GE Healthcare in Arlington, IL. "On 3/24/05, the licensee was first notified by GE Healthcare that they had received the package, but that it did not contain the seeds, but some type of brackets. The licensee notified FedEx, who initiated a tracking operation. On 4/19/05, the licensee received written notice from FedEx that the package still had not been found. The records internal to FedEx indicated the package had apparently been damaged during the shipment, and FedEx speculates the shipping papers were switched with the other shipment. [The State] will provide additional information at the close of the investigation into this matter." Notifications were given to R4DO (Nease) and NMSS (Moore & Correia) * * * UPDATE ON 05/20/05 AT 15:30 EDT FROM THE STATE ( HAMRICK) VIA E-MAIL * * * "This is a follow up to the reported lost shipment of I-125 seeds, which are now found. The seeds were delivered to the shippee, GE Healthcare, on March 24, 2005. The contact from GE Healthcare to the licensee in California indicated they had received an unexpected package from them (containing some type of brackets), but was not intended to indicate they had not received the package containing the seeds. The California licensee interpreted the information from GE Healthcare to mean that the seeds they had shipped had not arrived, however this apparently was not the case. Receipts of non-radioactive and radioactive shipments are handled separately at GE Healthcare, so the call to the California licensee was only to report the receipt of the unexpected non-radioactive shipment. Thus, GE Healthcare received the seeds on March 24, 2005, and knew they had received them on that date. There was simply a misunderstanding in the communication with the California licensee." Notifications were given to R4DO (Nease) and NMSS (Correia) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-05-24
41718 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-05-18 | 2005-05-19 12:34 | 2005-05-19 | AGREEMENT STATE REPORT - UNPLANNED CONTAMINATION WITH BROKEN PD-103 SEED (1.7 MILLICURIES) The State provided the following information via facsimile: "On May 18, 2005, during a prostate brachytherapy procedure, a pre-loaded cartridge containing Pd-103 seeds jammed in a Mick applicator. The jam occurred during a cartridge change, and when the authorized user attempted to remove the stuck cartridge from the applicator, the end of one seed was sheared off. After the authorized user reattached the applicator to the needle, he determined a seed had broken. Pieces of the broken seed were found in a needle and in the cartridge. This needle was removed from the patient and a new needle was inserted. The cartridge was removed from the Mick applicator and no contamination was detected on the applicator itself. The patient treatment was completed without further incident. Contamination was detected on several pieces of equipment as well as on the floor of the operating room. All personnel were surveyed before they were permitted to leave the operating room. Access to the operating room was restricted until the room was decontaminated by the radiation safety officer and the medical physicist. The seed fragments and cartridge were placed in a lead pig and secured in the radioactive waste storage area, where they will be held for decay-in-storage. The activity of the broken Pd-103 seed was 1.7 mCi. "The licensee notified DHFS on May 18, 2005. The Wisconsin Radiation Protection Section will investigate this event." The State event report number is 26. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-05-24
41717 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2005-05-19 08:49 | 2005-05-19 09:37 | 2005-05-19 | OFFSITE NOTIFICATION OF OIL SPILL "Less that one pint of oil spilled to the ground/soil. Soil has been remediated. Offsite notifications made to CT State Police Message Center and CT Department of Environmental Protection." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-05-19
41715 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2005-05-18 20:59 | 2005-05-19 04:37 | 2005-05-19 | INADVERTENT DE-ENERGIZATION OF 4160 V SAFETY RELATED A.C. BUS WITH EDG AUTO START "On 5/18/05 at 20:59 the 1A3 4160 V safety related A.C. bus inadvertently de-energized and the 1A Emergency Diesel Generator [EDG] automatically started and loaded onto the bus. The inadvertent de-energization of the 1A3, 4160 V bus appears to have resulted from testing of the 4160 V under voltage relays. Currently, normal power has been restored to the 1A3, 4160 V bus and the 1A Emergency Diesel Generator has been secured. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(iv)(A) to be completed within 8 hours as a safety systems actuation of the 1A3, 4160 V under voltage relaying and inadvertent start and load of the 1A Emergency Diesel Generator." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY THE LICENSEE (HURCHALLA) TO NRC (HELD) AT 2207 EDT ON 5/19/05 * * * "On 5/18/05 at 20:59 the 1A3 4,160 KV safety related AC bus inadvertently de-energized and the 1A Emergency Diesel Generator (EDG) automatically started and loaded onto the bus. This event was initiated during the performance of a plant surveillance 1-OSP-100.07, to test the 1A3 4,160 KV Bus Under Voltage Relay. The 1A EDG loaded and carried the 1A3 bus. The 1B3 4,160 KV bus was unaffected and the 'B' side power remained energized. This update is to provide the following additional information identified during the follow up investigation. "This update is to identify that HVS-1B, Containment Fan Cooler, did not start as expected after the 1A EDG automatically loaded on the 1A3 4,160 KV Bus. The HVS-1A and HVS-1B were both load shed from the bus prior to closure of the 1A EDG output breaker. The HVS-1A did start as expected following closure of the EDG output breaker. The HVS-1B is on the three (3) second load block for the 1A EDG to restart, but did not start. "A Root Cause Team has been formed to identify the cause of the initiating event and the auto-start failure of HVS-1B. A Condition Report was generated and a troubleshooting plan has been developed to determine the cause of the initiating event and failure of the HVS-1B to automatically restart. "The 1B3 4,160 KV safety related AC bus and associated EDG were not affected by this event and remained operable during and following the event. Troubleshooting for the subject failed equipment is ongoing." The licensee notified the NRC Resident Inspector. The R2DO (Ogle) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-05-19
41714 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-05-18 18:50 | 2005-05-18 19:27 | 2005-05-18 | IDENTIFICATION OF DESIGN AND OPERATING PROCEDURE DEFICIENCIES RELATED TO APPENDIX R EVENTS "During a review of the dedicated shutdown procedure (20.000.18), several possible design and operating procedure deficiencies were identified affecting Appendix R events. BOP Battery Charger 2C-1 is relied upon to feed post fire emergency shutdown loads. It was determined that although a circuit breaker supplying power to battery charger 2C-1 was re-closed by procedure, an additional action was required to place the battery charger in service. The BOP battery charger 2C-1 contactor circuit logic requires the control switch first be returned to the off-reset position, before the contactor can be re-energized. That control switch and associated control wiring is located in the control room envelope that is evacuated in an Appendix R fire scenario. Furthermore, the dedicated shutdown logic does not isolate this control switch circuitry from cables in the fire affected zone which is a requirement of the Appendix R circuit design. "In addition to the same issues identified for battery charger 2C-1, it was determined that the dedicated shutdown procedure did not provide for closure of the circuit breaker feeding power to battery charger 2C1-2. Battery charger 2C1-2 is required to power 260VDC motor operated valves used by the standby feedwater system to provide reactor cooling water and to control reactor water level after a shutdown due to an Appendix R fire. For both of these problems, power would be initially supplied by the associated batteries, but the batteries are not sized to provide power for the entire duration of the Appendix-R event. Therefore, when the plant must be shutdown from outside of the control room, a safe shutdown cannot be assured using the dedicated shutdown panel. This event is being reported as an unanalyzed condition under 50.72(b)(3)(ii)(B). "The affected Appendix R equipment was declared inoperable, and procedure changes to address this issue are being considered to address these conditions. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-05-18
41713 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2005-05-16 | 2005-05-18 17:31 | 2005-05-18 | CHEMICAL AGENT DETECTORS MISSING FROM DEPARTMENT OF NAVY INVENTORY A representative for the Navy's master materials license reported several chemical agent detectors missing based on the most recent inventory cycle. Specifically, 4 Chemical Agent Monitors (CAMs) are missing, with each CAM utilizing a 10 milliCurie Nickel-63 plated source (SSND# NR-1129-D-103-S) [40 millicuries of Ni-63 total]. In addition, 1 Automatic Chemical Agent Detector Alarm (ACADA) containing two 10 milliCurie Ni-63 plated sources (SSND# NR-1129-D-101-S) is also missing [20 millicuries of Ni-63 total]. These detectors have been reported missing from Marine Corp units deployed in Iraq. Details of the times, locations, and circumstances under which the detectors went missing are still under investigation by the Navy . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-05-18
41712 | 0 | BOONE HOSPITAL |  |  |  |  | 2005-05-18 11:30 | 2005-05-18 16:21 | 2005-05-18 | EIGHT IODINE-125 SEEDS LOST DOWN A SINK Radiation Safety Officer for Boone Hospital located in Columbia, MO., reported the following event: A pre-loaded cartridge containing 15 Iodine-125 seeds, activity of each seed is 0.31 millicuries, was sent to the sterilization room of the hospital. Upon arrival the person handling the pre-loaded cartridge, not familiar with handling the cartridge, unscrewed the cap to the cartridge and the 15 seeds inside the cartridge fell out. Some of the seeds went down the drain of the sink and the rest ended up inside a tray or on the counter around the sink. Seven of the Iodine-125 seeds were recovered. Eight of the seeds that went down the sink were not recovered. Radiation surveys were performed in the sterilization room and no other seeds were found. Total activity of the missing eight Iodine-125 seeds is 2.48 millicures. The person opening the pre-loaded cartridge did not receive any dose according to the Radiation Safety Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-05-18
41711 | 0 | MISTRASS HOLDING GROUP |  |  |  |  | 2005-05-17 16:30 | 2005-05-18 15:15 | 2005-05-18 | LOSS OF CONTROL OF RADIOGRAPHY CAMERA A radiography crew had completed activities at a location at the Sun Refinery in Philadelphia Pennsylvania at approximately 1630 EDT on 5/17/05. The radiography camera used by the crew was an AEA Model 660B, containing a 32 Curie Ir-192 source (serial number B3762). The source was safely retracted and locked in its shielded position in the camera. The radiographer believed that the camera was in the possession of the assistant radiographer. The assistant radiographer believed the camera was in the possession of the radiographer. The camera was actually left unattended on a scaffolding at the Sun Refinery job site. At 2040 EDT on 5/17/05, Sun Refinery personnel discovered the camera while preparing to remove scaffolding at the job site. The licensee was immediately contacted and recovered the camera. The licensee stated that there is no indication that anyone had disturbed or worked in the vicinity of the camera while it was unattended. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | EXCESSIVE RELEASE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2202(b)(2) |  |  |  | 0 | 2005-05-18
41710 | 0 | PHYSICS ASSOCIATES |  |  |  |  | 2005-05-13 | 2005-05-18 14:48 | 2005-05-18 | RECOVERY OF STRONTIUM-90 SOURCE (APPROXIMATELY 4 MILLICURIES) FROM SCRAP YARD Radioactive material was detected in scrap metal waste delivered to a scrap yard (Shredded Products, Montvale VA) on 5/13/05. The scrap yard notified the State of Virginia Department of Health. The State Department of Health, with the assistance of a contractor (Physics Associates) located the radioactive material. The radioactive material was a sealed source of Strontium-90 used in a thickness measuring gauge. Identification marking on the Strontium-90 source indicate that it was a 10 millicurie source in 1967. Based on current radiation measurements, the source strength is estimated at about 4 millicuries. The source has been verified to be intact and not leaking and is safely in possession of Physics Associates (licensed to posses this material). Region 1 (Ragland) provided additional information on the Sr-90 source based on information received from the State of Virginia. The gauge is believed to be a Model 32-19-001, Serial Number 384-41044, manufactured by Avionics Corporation. The origin of the scrap shipment is reported to be from a scrap yard in Salem, Virginia. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-05-18
41709 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-05-18 | 2005-05-18 14:41 | 2005-05-19 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "A Ford F-150 with the CO license plate #225ALO was stolen at approximately 88th and Washington Street in Thornton (at approximately 11:00 am). A Troxler model 3430, gauge serial # 33250 was inside a DOT approved container, which was chained in the back truck bed and the container/box, was also locked. The keys for those locks were with the truck keys, with the individuals who have stole the truck; per Mr. D. "Per Mr. D, he is waiting for the Thronton Police to arrive to document such. Further information will be forwarded to us upon learning." * * * UPDATE FROM STATE (BONZER) VIA FAX RECEIVED AT 1348 EDT ON 5/19/05 * * * The stolen truck was recovered with gauge in the truck bed. The licensee retrieved the truck and gauge at 0115 MDT on 5/19/05 with no evidence that the gauge had been tampered with or disturbed. The licensee intends on leak testing the gauge and will keep the gauge out of service until results are obtained. R4DO (Nease) and NMSS (Correia) have been notified. TAS (Hahn) informed via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-05-23
41708 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2005-05-16 09:45 | 2005-05-18 14:43 | 2005-05-18 | AGREEMENT STATE REPORT - LOST/STOLEN AND RECOVERED MOISTURE DENSITY GAUGE The State provided the following information via facsimile: "Description of Event: Received a report that a Troxler gauge had been found in the middle of Stevens Creek Road. Date of event: 5/16/05. "A delivery truck driver recovered the gauge from the street and notified the Augusta-Richmond County Fire Department. The fire department then notified the Georgia Radioactive Materials Program. The gauge was a model 3430 Troxler Moisture Density Gauge. "Isotope: Cesium 137 and Americium 241, Beryllium. Amount of Activity: 8 mCi [millicuries] Cs 137 and 40 mCi Am/Be. "Describe clean-up actions taken by RCP: None. "List radiation measurements taken by RCP: Took measurements to confirm source was in proper position in gauge and did not exceed transport index." The Augusta Chronicle published a story in this event on May 16, 2005. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2005-05-23
41707 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-05-12 | 2005-05-18 13:55 | 2005-05-18 | AGREEMENT STATE - LOST AND RECOVERED SOURCE The State provided the following information via facsimile: "On the evening of May 12, 2005, Superior Energy Services lost a tool string with a 150 mCi [millicuries] source of Am-241 downhole at about 11,000 feet. Superior's slickline division fished for the tool and recovered the tool string and source on May 14, 2005 with no damage to the source housing. The onsite technician surveyed the tool and did not find any radiation leakage from the housing. The source was returned to the storage location and surveyed again before putting the source in the bunker. No radiation leakage was detected. "Louisiana Event Report ID No.: LA050005" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-05-23
41706 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2005-05-18 01:54 | 2005-05-18 09:27 | 2005-05-18 | LOSS OF BALANCE OF PLANT POWER DUE TO TRANSFORMERS LOCKOUT "At 0154, 5/18/2005, during performance of relay testing, differential lockout 86T3 was manually actuated resulting in lockout of transformers XTF 31 and XTF 32. This resulted in a loss of all balance of plant (BOP) buses, loss of vital bus 1DB, an auto start of 'B' Diesel Generator (DG), and the sequencing of required ESF loads. "At 0154, during relay testing, the 86T3 differential lockout was actuated. This resulted in a total isolation of XTF0031/32 which de-energized all of the BOP power to the plant and the XSW1 DB switchgear. "Plant Engineered Safeguards Features (ESF) systems responded per design as the 'B' DG started and sequenced ESF loads. There were no major problems due to the event; however, the Diesel Fire Pump did not start as expected on a loss of BOP bus 1 C2. "The Control Room entered AOP-304.3, 'Loss of All Balance of Plant Buses' and SOP-306, Section B, 'Operation of Diesel Generator 'B' After An Automatic Start And Load'. "Preliminary review of plant response shows the RHR flow was in the process of coasting down and was restored to full flow within 20 seconds. The inlet temperature of the Residual Heat Removal (RHR) Heat Exchanger increased approximately 0.3 °F due to this event. There was no change in Reactor Coolant System level. V. C. Summer is currently shutdown in Mode 5 during Refueling Outage 15." All plant systems are currently restored to normal configuration for Mode 5 refueling activities and there were no reported reactivity issues associated with this incident. The licensee notified the NRC Resident Inspector and will notify the State, local and other government agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-05-18
41705 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-05-17 09:05 | 2005-05-17 17:08 | 2005-05-18 | FITNESS FOR DUTY A non-licensed contract employee found a can of beer in his lunch box. The licensee's investigation determined that the introduction of alcohol into the Protected Area was not an intentional act. The contract employee's access was restored. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UDATED ON 5/18/05 TO CORRECT UNIT 2 PLANT STATUS INFORMATION * * * | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2005-05-17
41704 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2000-03-23 | 2005-05-17 15:19 | 2005-05-17 | AGREEMENT STATE REPORT - LOSS OF ELECTRON CAPTURE DETECTOR The State provided the following information via email: "During a routine inspection of Chem-Bio Laboratories, Inc. on March 23, 2000, it was determined that a Perkin Elmer Model 330-0119 electron capture detector, previously possessed by the licensee could not be located. The management representative explained that the owner/authorized user had removed that particular source from the device and placed in storage. She stated that she would continue to look for the source. Shortly after the inspector departed the licensee's facility, a call was made to the MSDH-Division of Radiological Health stating that the missing source had been found. During another routine inspection conducted on March 18, 2004, it was discovered that the source was never located. The licensee stated that she called again to inform someone at DRH that she had mistakenly informed the Agency about the source location and the source had never been found. She stated that she has made every effort possible to locate the source, but has not been successful. The licensee also stated that she was aware that a letter should have been sent to our Agency describing the circumstances surrounding the missing source, but failed to do so. "Isotope: Nickel - 63 "Activity: 15 mCi (millicuries) "Date Closed: 4-12-04 "State Event Number: MS-04-002 "Enforcement action taken: Violations cited for failure to secure radioactive material from unauthorized removal or access and failure to properly report lost source and provide a written report to the Agency." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2005-05-20
41703 | 0 | ALLIED INSPECTION |  |  |  |  | 2005-05-17 05:40 | 2005-05-17 11:37 | 2005-05-17 | OVEREXPOSURE DURING RADIOGRAPHY A radiographer and his assistant were conducting a radiography exposure of a pipe weld. As the radiographer was picking up the crank handle to retract the source to the "safe shielded/locked" position, the radiographer was distracted when he heard someone yell "hey." The radiographer and his assistant investigated the sound on either side of the roped boundary. The radiographer left the survey meter back at the crank handle. Thinking the source was stowed, both approached the weld they were radiographing. They removed the source tube and collimator from the weld, and removed the film. The assistant walked back to the crank to place the film with the other exposed films and noticed the survey meter was pegged high. He immediately retracted the source to the "safe shielded/locked" position. Both men checked their pocket dosimeters and found them to be off scale. Dose estimate calculations indicate that the RSO may have received up to 5.5 Rem and the assistant may have received up to 2.5 Rem. The film badges have been shipped via overnight express shipping for immediate processing and report. Exposure Device: Amersham/Sentinel Model 660B S/N B-2790. Source: AEA Technology Iridium-192, model 424-9, S/N 21852, 37.5 Curies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2005-05-17
41702 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2005-03-19 | 2005-05-17 11:24 | 2005-05-17 | PART 21 FOR A FLEX - WEDGE DISC FABRICATED BY CRANE - ALOYCO "On March 19, 2005, during refueling Outage 2R17, it was identified that a Flex-wedge disc intended for installation in a Containment Sump isolation valve, did not have a machined slot around the disc edge, as required by the purchase specifications. A feature of the flex-wedge design is to allow the disc faces to flex, thereby reducing the potential for thermal binding. The discrepancy was identified during pre-installation inspection; therefore, the disc was not installed in the plant. Considering that extensive machining and handling of the disc is necessary during installation, it is extremely unlikely that the discrepancy could have gone undetected. The outboard containment sump isolation valve is normally closed and receives a Recirculation Actuation Signal (RAS) to open when the Refueling Water Tank volume is depleted (post-LOCA) in order to shift the Emergency Core Cooling System (ECCS) suction to the sump. Had the subject disc been installed in this valve, the discrepancy could have resulted in thermal binding of the disc, thereby rendering a complete train of ECCS inoperable upon initiation of a RAS. The subject disc was manufactured by Crane - Aloyco, and was delivered to Arkansas Nuclear One in 1991." "This condition was determined to be reportable pursuant to 10CFR21 on 5/17/2005." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AR | POW |  | 21.21 |  |  |  | 0 | 2005-05-17
41701 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2005-05-16 10:39 | 2005-05-16 14:18 | 2005-05-16 | AFW ACTUATION DURING SURVEILLANCE TESTING "On May 16, 2005, at approximately 1039 hours, both motor driven Auxiliary Boiler Feedwater Pumps automatically started after exceeding their 28 second time delay during performance of the low-low Steam Generator Water Level section of procedure 3PT-M13B1, 'Reactor Protection Logic Channel Functional Test.' The operators secured the pumps and saw no indication of reactivity addition. The operators anticipated the possibility of these results because the test states in its precaution and limitations section, that the pumps would start if the action required by the test is not completed within the 28 second time delay. The cause of the event is under investigation." The licensee notified the NRC Resident Inspector and the NY State Public Service Commission. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-05-16
41700 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2005-05-15 01:18 | 2005-05-15 02:44 | 2005-05-15 | OFFSITE NOTIFICATION OF ONSITE FATALITY "Event Description: Security Officer fatality onsite - apparent heart attack. "Action Taken: Called local ambulance company (Rescue, Inc.). Additional security personnel performed CPR." The licensee stated that the Security Officer was on break at the time of the fatality. The licensee notified the NRC Resident Inspector and will be notifying the State of Vermont. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-05-15
41699 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2005-05-13 10:30 | 2005-05-14 19:55 | 2005-05-14 | AGREEMENT STATE - STOLEN MOISTURE DENSITY GAUGE A CPN moisture density gauge fell off the back of the company pickup truck. The case was not secured to the truck, the case was not locked, and the gauge handle was not locked. The truck drove 40 miles to the next job site and the truck tailgate was found down and the gauge was discovered missing. Upon return to the original job site (Notting Hill development in Edgewood, KY), the case was found but the gauge was missing. The licensee contacted local law enforcement, the fire department and ambulances to help recover the gauge. A reward has been offered. CPN Moisture Density Gauge model MC1DR, Serial #MD50402557 Sources: CS-137 10 milliCuries, Am-241:Be 50 milliCuries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2005-05-18
41698 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2005-05-13 16:00 | 2005-05-13 16:04 | 2005-05-13 | UNANALYZED CONDITION - ELECTRICAL CONTAINMENT PENETRATION "On March 23, 2005, with the plant at 100% power, an issue was discovered questioning the design of an approximately 3-inch diameter module of containment electrical penetration (PBP5D) used to feed a non-safety related lighting panel (L49E1) inside the containment building. Specifically, it was identified that this penetration module was protected from overcurrent by a single 30-amp breaker (BF503). Action was taken at that time to open the supply breakers de-energizing the lighting panel to prevent any potential fault on the subject penetration module while the issue was being evaluated. "Evaluations were initiated to determine the potential for the containment electrical penetration module to be thermally or mechanically damaged by a postulated fault. During this evaluation, no weak link upstream of the penetration module could be found that could be credited for preventing a fault in the penetration module in the event of a random failure of the breaker. The next breaker upstream of this circuit is too large to provide adequate overcurrent protection if the 30-amp breaker fails to open. Furthermore, it could not be shown that the electrical penetration module could withstand the maximum possible fault current while maintaining its containment integrity function. Therefore, it is now assumed that this postulated fault current could have damaged the penetration module to the extent that it would no longer have performed its containment integrity function. "This condition is being reported within 8 hours of discovery in accordance with 10CFR50.72(b)(3)(ii)(B) as the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. Specifically, it was discovered that a system required to meet the single failure criterion does not do so." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-05-13
41697 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-05-13 13:45 | 2005-05-13 13:51 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * MEDIA INQUIRY RESPONSE - CONCURRENT EVENT "This concurrent report is being made to the NRC as a result of a media inquiry response concerning BWXT site security that was provided to [reporter representing] the Lynchburg News & Advance." See Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
41696 | -1 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-05-12 | 2005-05-13 10:29 | 2005-07-18 | AGREEMENT STATE REPORT - NUCLEAR GAUGE FAILS TO FUNCTION AS DESIGNED The State provided the following information via facsimile: "The RSO contacted the DHFS, Radiation Protection Section on May 12, 2005 to report a damaged shutter on a fixed gauge at their facility. The gauge is a Berthold Model LB7400D containing 350 mCi of Cs-137, SN DW954A. "The licensee discovered the problem when they were preparing to do some maintenance work on the gauge. The detector was giving erroneous readings. The licensee observed higher radiation levels (12 Mr/hr on contact with the source holder) with the shutter in the 'closed' position than the 'open' position, (6 Mr/hr on contact with the source holder.) The licensee assumed that the shutter had failed. "Berthold has been contacted and will provide a service visit on May 17 or 18. The gauge is in the same configuration as in operations. Access is restricted by a fence around the area, including a lock with keypad entry. The inspector who recently visited the licensee confirms that access is restricted. The gauge is on Line 5 at the Superior Terminal, Enbridge Pipeline. "The licensee will send the required report following the service visit." * * * RETRACTION FROM M. WELLING TO W. GOTT AT 1515 ON 07/18/05 * * * "Wisconsin Radiation Protection Section would like to retract event number EN41696, Enbridge Pipeline, LLC. After reviewing the in-question housing, Berthold states that there is nothing wrong with the source housing. It appears to be an error on the licensee determining if the shutter was open or closed." Notified NMSS (M. Burgess) and R3DO (P. Louden) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-05-18
41695 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-05-11 | 2005-05-12 17:23 | 2005-06-16 | AGREEMENT STATE - RADIOGRAPHY EQUIPMENT MALFUNCTION The State provided the following information via facsimile: "The Colorado Department of Public Health and Environment received notification on 5/12/05 of a radiography equipment malfunction resulting in a stuck radiography source. "The radiography company, Midwest Inspections, located at 325 Walnut Street, Brighton, Colorado, with the Colorado license number 902-01, reported that a radiography crew was unable to retract a radiography source back into the shielded position while working at a temporary job site near Byers, Colorado on 5/11/05. Per the company's RSO, the crew secured the area and contacted him for assistance when they were unable to fully retract the source. He traveled to the site with shielding equipment and was able to free the source and return it to the shielded position. The cause of the problem is reported to be a dent in the guide tube under the 'bend restrictor' where it was not easily visible to the crew. The RSO reported no excessive exposures to the crew, the public or himself (he estimated an exposure of 50 millirem to himself). Initial corrective action was to remove the defective guide tube from service." * * * UPDATE PROVIDED BY STROUD TO GOULD AT 1738 EDT ON 06/13/05 * * * This update provides information that was originally contained in EN 41769 which has been deleted and provided as an update to the original report. The State provided the following information via facsimile: The exposure device involved was INC Model IR-100 s/n 4035 with a 38 curie Ir-192 source s/n G862. The RSO attempted to retract the source and encountered the same problem as the crew. The source assembly seemed to hang up as it entered the exit port of the camera. The RSO attached a 0-500 millirem pocket dosimeter to his wrist watch on his left hand to measure any exposure to the hands during the following process. He cranked the source into the collimator and placed (2) 25# lead shot bags over the collimator for shielding. Using a pair of 12 inch channel lock pliers, he disconnected the source tube from the collimator. Keeping the source assembly in the collimator and shot bag shielding, he exposed the drive cable and source pigtail connector. After disconnecting the source pigtail connector and drive cable, he disconnected the exit port end of the source tube from the camera and slid the source tube off of the drive cable. The source tube was replaced with a new one and reconnected to the source assembly. The RSO then retracted the source into the camera. The crew x-rayed the remaining welds while RSO remained on site. The RSO's total whole body exposure was 50 millirem and the dosimeter on his wrist indicated an exposure of 220 millirem. Inspection of the source tube showed a kinked area next to the exit port fitting which apparently would not allow the locking ball on the pigtail assembly to pass back through it. Notified R4DO (Whitten) and NMSSEO (Holahan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-05-17
41694 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2005-05-12 07:45 | 2005-05-12 14:54 | 2005-05-12 | AGREEMENT STATE - STOLEN TROXLER GAUGE The State provided the following information via facsimile: "The SC Department of Health and Environmental Control was notified on May 12, 2005, by the Corporate RSO of PSI [Professional Service Industries, Inc.] that a portable gauging device had been stolen from the back of a pick-up truck at the Residence Inn Marriot in Spartanburg, South Carolina. The gauge was located in its transportation case chained to the bed of the truck. The chain had been cut and the gauge and transportation case had been removed. The technician discovered the gauge missing at 7:45 am on May 12, 2005 and notified the police. The gauge is a Troxler Model 3430 containing 9 mCi of Cesium-137 and 44 mCi of Am-241:Be. The local media has also been notified. Updates to this event will be made through the national NMED system." South Carolina State Event Report ID No.: SC050005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2005-05-17
41693 | 0 | SHORE MEMORIAL HOSPITAL |  |  |  |  | 2005-05-11 | 2005-05-12 14:33 | 2005-05-12 | MEDICAL EVENT - ACTUAL DOSE GREATER THAN PRESCRIBED DOSE On 05/11/05, a patient in the hospital was scheduled to receive an I-131 dose of 12 millicuries to the thyroid. Due to an error by the nuclear medical technician, a dose of 14.8 millicuries of I-131 was measured and delivered. There were two doses for different patients being measured in the lab at the time and the prescribing physician typically would write nuclear medicine directives with a range, such as 12-14 millicuries. In this specific instance, the physician wrote the directive for exactly 12 millicuries. The physician stated that there would be no unintended damage to the patient. The hospital RSO stated that the prescribing physician would be notifying the patient. The RSO intends to reinforce following proper lab procedures and exercising caution when working with multiple doses to all physicians and lab personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-05-12
41692 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-05-12 04:11 | 2005-05-12 11:22 | 2005-05-13 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF EMERGENCY BUS E1 "On May 12, 2005, at 0411 hours, electrical power was lost to the 4160 VAC Emergency Bus E1. Emergency Diesel Generator 1 was inoperable for maintenance at the time of the electrical power loss. This power loss to Emergency Bus E1 affected both Units 1 and 2. Unit 1 "The loss of power to E1 resulted in Division 1 Primary Containment Isolation Valve (PCIV) actuations. The actuations included the Primary Containment Isolation System (PCIS) Group 2 (i.e., Drywell Equipment and Floor Drain, Traversing In-core Probe, Residual Heat Removal (RHR) Discharge to Radwaste, and RHR Process Sample), Group 3 (i.e., Reactor Water Cleanup), and Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems) valves, as well as the Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation) and the automatic start of Standby Gas Treatment (SGT) System train B. The actuations of PCIVs and Reactor Building Ventilation System isolation were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). Additionally, SGT System train B started and functioned successfully. "Loss of power to E1 also resulted in entry into LCO 3.0.3 (i.e., be in Mode 2 within 7 hours, Mode 3 within 13 hours, and Mode 4 within 37 hours) due to all required reactor coolant leakage detection instrumentation/systems being inoperable. "At 0440 hours, it was discovered that all three Control Room Air Conditioning (AC) subsystems became inoperable due to failure of the control building air compressors and Technical Specification LCO 3.0.3 was entered. At 0515 hours, it was determined that both Control Room Emergency Ventilation (CREV) subsystems became inoperable when the dampers drifted shut. At 0546 hours, a control building air compressor was started and the control room air conditioning and CREV subsystems were returned to operable status. "Operators initiated a plant shutdown for Unit 1, as required by Technical Specifications at 0948 hours. Unit 2 "Conditions and activities associated with the Control Room AC and CREV systems apply to Unit 2 as well as Unit 1. Reporting Requirements Met by this Notification "10 CFR 50.72(b)(2)(1), the initiation of any nuclear plant shutdown required by the plant's Technical Specifications, applies to Unit 1. "10 CFR 50.72(b)(3)(v)(D), a condition that, at the time of discovery, could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident (i.e., Control Room AC and CREV), applies to both Units 1 and 2. "10 CFR 50.73(a)(i), invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system, applies to Unit 1. INITIAL SAFETY SIGNIFICANCE EVALUATION "Currently Unit 2 is operating at steady state with Unit 1 being shut down. Specified systems actuated as designed. No adverse impact to the control room environment occurred during the period (i.e., one hour and 35 minutes) the affected ventilation system was inoperable. The other redundant emergency busses are operable. Prior to the event reactor coolant leakage level for Unit 1 was well within operating limits. The actions as required by the applicable Technical Specifications have been established. CORRECTIVE ACTIONS "Activities are currently under way to determine the cause of the E1 power loss and restore electrical power to Emergency Bus E1. Causes and actions to preclude recurrence will be addressed in accordance with the corrective action program and provided to the NRC in the associated licensee event report." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/13/05 @ 0952 BY LEONARD BELLER TO CHAUNCEY GOULD * * * "On May 12, 2005, at 0411 hours, electrical power was lost to the 4160 VAC Emergency Bus E1. Emergency Diesel Generator 1 was inoperable for maintenance at the time of the electrical power loss. This power loss to Emergency Bus E1 affected both Units 1 and 2. A non-emergency notification (Event Number 41692) was made to the NRC Operations Center at 112:2 hours. This follow-up notification discusses plant recovery from the Emergency Bus E1 power loss. "Unit 1 "Loss of power to E1 resulted in entry, into LCO 3.0.3 (i.e., be in Mode 2 within 7 hours, Mode 3 within 13 hours, and Mode 4 within 39 hours) due to all required reactor coolant system (RCS) leakage detection instrumentation being inoperable. Operators initiated a plant shutdown for Unit 1, as required by Technical Specifications at 0948 hours. A Notice of Enforcement Discretion (NOED) was requested from the NRC to waive compliance with the shutdown requirements associated with RCS leakage detection instrumentation in order to provide more time for an orderly plant shutdown. In lieu of the RCS leakage detection shutdown requirements (i.e., be in Mode 2 by 1111 hours), Unit 1 would adhere to the shutdown requirements associated with loss of Emergency Bus E1 (i.e.,, be in Mode 3 by May 13, 2005, at 0011 hours). The requested NOED was verbally granted by the NRC on May 12, 2005 at 1050 hours, so shutdown activities for Unit 1 continued versus the insertion of a manual reactor scram, with the unit at approximately 65 percent of rated thermal power. "Power was restored to Emergency Bus E1 and the LCO associated with RCS leakage detection instrumentation was exited on May 12, 2005 at 1740 hours. The LCO associated with loss of power to Emergency Bus E1 was exited at 2015 hours. "Unit 2 "The LCO associated with loss of power to Emergency Bus E1 also applied to Unit 2, and was exited at 2015 hours, "CORRECTIVE ACTIONS Emergency Diesel Generator 1 was made available, but not operable, on May 13, 2005, at 0117 hours." The licensee notified the NRC Resident Inspector. Reg 2 RDO (Moorman) was notified. | 97 | 100 | 0 | 97 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION | INVALID SPECIF SYSTEM ACTUATION |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) | 50.73(a)(1) |  | 0 | 2005-05-12
41691 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-05-10 | 2005-05-11 18:28 | 2005-05-11 | CALIFORNIA AGREEMENT STATE REPORT - LOST TROXLER GAUGE The State provided the following information via email: "[The] licensee called to report [that] one of their Troxler 3430 gauges (serial number 33503- 8 mCi Cs-137 / 40 mCi Am 241/Be) was missing from their temporary storage site at a storage facility in Temecula. The gauge was reported to be locked in the storage facility, in a locked cage, inside a locked storage box at around 1000 on May 10, 2005. A second gauge user noticed the other gauge was not in the storage box when he locked his gauge in the box yesterday. The second gauge user was able to contact the first gauge user this morning at 0630. The first gauge user confirmed the gauge had been locked in the storage box yesterday and it should have been there. There was no evidence of forced entry and the gauge user states he did lock the gauge in the storage area yesterday. A report was filed with the Riverside Sheriff/Temecula Police (TE0513033). The RSO will forward the gauge users statement regarding this incident. For corrective action the RSO plans to have a counseling session with the gauge user immediately and will give additional training regarding gauge security and emergency procedures within the next month." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-05-16
41690 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-05-10 | 2005-05-11 16:02 | 2005-05-11 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE The State provided the following information via email: "Gauge was stolen from back of pick up [truck]. It had been secured by chain and lock through handle of gauge to bed of truck. [The gauge] appears to have been stolen while parked behind field office location in strip shopping center in Pharr, Texas. Discovered missing on arrival at Area office where gauge is stored when not in use. The gauge is a Troxler Model 3430, S/N 26742. It contains 8 mCi Cs-137, s/n 75-9877, and 40 mCi Am-241-Be s/n 23217." Texas Incident I-8230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-05-16
41689 | 0 | ELI LILLY AND COMPANY |  |  |  |  | 2005-04-12 | 2005-05-11 14:40 | 2005-05-11 | LOST Ni-63 SOURCE A 12.1 milliCurie Ni-63 source was missing on 4/12/05 during a regularly scheduled leak test. The source had last been inventoried on 11/23/04. The source was part of an electron capture detector which was inside a gas chromatograph. The gas chromatograph was disposed of in a landfill (date not available). Model: Hewlett Packard (Agilent) type G1223A Serial: F5020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-05-11
41688 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-05-11 01:35 | 2005-05-11 02:22 | 2005-05-11 | NON-WORK RELATED FATALITY AT ONSITE OFFICE AREA " A contract QC welding inspector suffered an apparent heart attack in an office area around 00:09 on 05/11/05. The on-site emergency medical response team was dispatched to provide assistance. The individual was transported to a local hospital for treatment. The site was notified at 01:35 that the individual had not been revived. This is a non-work related fatality. The employee was not contaminated [and] OSHA will be notified." The contract worker, who was employed by "The Atlantic Group", was taken to the Piedmont Medical Center in Rockville, SC for medical treatment. The licensee will be notifying the NRC Resident Inspector, the Emergency Operations Center for the States of NC & SC, and the LLEA for Mecklenburg County. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-05-11
41687 | 0 | WATERFORD | 3 |  |  | [3] CE | 2005-05-10 07:55 | 2005-05-10 15:55 | 2005-05-10 | FITNESS FOR DUTY - ALCOHOL A licensed employee had a confirmed positive for alcohol during a for-cause test. The employee's unescorted access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 26.73 |  |  |  | 0 | 2005-05-10
41686 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-05-10 13:52 | 2005-05-10 15:53 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * PACKAGE ABOVE EXTERNAL RADIATION LIMITS "On Tuesday, May 10, 2005, at approximately 1352, BWXT -- NPD received a Radioactive, Type A Package from: "Baker Hughes, 1999 Ranking Road, Houston, TX 77073 "BWXT performed radiological surveys of the package which indicated that the outer package exceeded the 200 mRem/hr limit for contact reading found in 10 CFR 71.47(a). The external surface reading was 263 mRem/hr. 10 CFR 71.47(b) does not apply since this was not an 'exclusive use shipment.' This event is reportable under 10 CFR 20.1906." The bill of lading shows seven pieces in three crates. Only one container was above the limit. The licensee verified that the shipment vehicle was properly placarded. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(2) |  |  |  | 0 | 2008-05-11
41685 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2005-04-07 | 2005-05-10 14:38 | 2005-05-10 | AGREEMENT STATE REPORT - LOST FLUORESCENCE ANALYZER The State provided the following information via email: "During an inspection at Thomas Wood Preserving on April 7, 2005, it was determined that a generally licensed device, Asoma Model LCA x-ray fluorescence analyzer, Serial No. 466, containing 30 millicuries of Curium-244, was missing. The plant manager of the treatment plant stated that the device had been returned to Spectro Analytical, the device distributor, several years ago. [The Division of Radiation Health] DRH contacted Spectro Analytical on May 2, 2005, and learned that they had never received the device from the company. The plant manager stated that he would continue looking for the device and inform DRH if it was located. It is assumed that the treatment plant purchased a new fluorescence analyzer and the other device was put in storage and/or misplaced. Thomas Wood Preserving, holder of General License No. GL-266 was cited violations for failure to secure radioactive material from authorized removal and failure to report the lost device to the Agency. The licensee is also required to provide a written report to DRH in accordance with State Regulations. It is not known when the device was lost or the event occurred." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2005-05-13
41684 | 0 | MN STATE UNIV AT MANKATO |  |  |  |  | 2005-05-04 | 2005-05-10 09:44 | 2005-05-12 | LOSS OF 100 MG OF PLUTONIUM/BERYLLIUM SEALED SOURCE The Minnesota State University provided notification of a lost sealed source from the radiation facility. The source was a 100mg Pu/Be (6 milliCuries) (Serial # M-1202), and used primarily in the State University laboratory for teaching purposes. In 1962 an inventory was taken and documented that 2 sources (10 gram and 100 mg) were stored in a barrel and shielded in paraffin. Somewhere over the years it was understood that only one 10.1 gram source was in the barrel. When the licensee moved from one facility to another in 1973, no detailed inventory was taken of the contents in the barrel. On 05/04/05 the sealed sources were being reclaimed by Los Alamos and when the paperwork was checked against the actual contents it was noted that the 100mg sealed source was missing. A thorough search by licensee of their facility did not find any evidence of the missing source. The source dimension is 1.75 " long and 1.25 " in diameter. **** UPDATE FROM ANN MARIE STONE, NRC REGION 3 ON 05/12/05 AT 1750 EDT TO PETE SNYDER **** Changed Reporting Organization and Licensee field from the University of Minnesota to Minnesota State University at Mankato. R3DO (A. Marie Stone) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MN | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-05-10
41683 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-05-10 03:23 | 2005-05-10 05:07 | 2005-05-10 | LOSS OF EMERGENCY NOTIFICATION SYSTEM (ENS) COMMUNICATION LINES Licensee discovered that the ENS Communication Lines from both the Control Room and the Technical Support Center were unavailable. This constitutes a loss of emergency preparedness capability. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-10
41682 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2005-04-03 06:04 | 2005-05-09 21:37 | 2005-05-09 | CONTAINMENT ISOLATION VALVE CLOSURE "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1), to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A), 'Any event or condition that resulted in manual or automatic actuation of any system listed in paragraph (a)(2)(iv)(B).' General containment isolation signals affecting containment isolation valves in more than one system are identified in paragraph (a)(2)(iv)(B). "On April 3, 2005, at 0604 hours, with Unit 2 in Mode 1, 'Power Operation,' fuse 2-902-3-RR-F20 in the 902-3 panel failed, which resulted in a partial Group 2 Primary Containment Isolation. The containment isolation signal affected containment isolation valves in more than one system. All affected containment isolation valves operated as designed. "The fuse was successfully replaced and all affected components were restored to operable status." The fuse was replaced at 0630 on 4/3/2005 and isolation valves were restored to the normal at-power lineup at 0637. The licensee notified the NRC Resident Inspector. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-05-09
41681 | 0 | PALISADES | 1 |  |  | [1] CE | 2005-05-09 19:46 | 2005-05-09 20:03 | 2005-05-10 | UNUSUAL EVENT DECLARED "Emergency Category: Primary Coolant System Integrity "Appears leak has been isolated." The plant was performing a SI (Safety Injection) accumulator bottle sampling test. At the conclusion of the test, a valve failed to close which caused excessive pressure in a line. When the pressure source was isolated, thermal expansion occurred which pushed some fluid through the Primary Coolant System check valves into the primary coolant system. When the system was depressurized to relieve the pressure, the primary coolant check valve failed to reseat. As a result, approximately 90 gals of primary coolant back flowed through the primary check valve over a two minute period. The leakage was stopped when the line was isolated remotely from the control room. The plant is still in the unusual event. The exit criteria is a tech spec leak rate calculation to verify that primary coolant leakage is less than the tech spec allowed value which will take approximately three hours to complete. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE P. RHODES TO J. KNOKE ON 05/10/05 AT 00:15 EDT * * * At 00:11 EDT on 05/10/05 the licensee terminated their Unusual Event for Primary Coolant System integrity. The present leak rate is 0.018 gal/min, which is within the allowable Technical Specification limit of <1 gal/min for unidentified primary coolant leakage. There is an LCO (72 hrs) for the primary coolant system check valve that improperly reseated (CK-ES-3131). The licensee notified the NRC Resident Inspector. Notified R3DO (Riemer), NRR EO (Gillespie), IRD Manager (McGinty), DHS (A. Akers) and FEMA (K. Biscoe). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-05-09
41680 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-05-09 18:00 | 2005-05-09 18:35 | 2005-05-10 | FAILURE OF THE SAFETY PARAMETERS DISPLAY SYSTEM (SPDS) "The Unit 1 and Unit 2 SPDS systems are out of service and have been out of service since 05-07-2005 at 22:00 for Unit 1 and 1800 for Unit 2. "The SPDS is a part of the Hatch Emergency Plan as described in Section H of the plan. "Alternate sources for many of the points in SPDS are available in the main control room. Consequently, with much of this information available in the control room, and communications between the emergency facilities also available, emergency assessment capabilities are maintained. However, since the SPDS units have been out of service for approximately 44 hours, this is being reported under the requirements of 10 CFR 50.72(b)(3)(xiii) and under the guidance of NUREG-1022, section 3.2.13, 'Loss of Emergency Preparedness Capabilities.' "Until today the systems could be rebooted to obtain data when needed." The systems were intermittently available throughout the weekend and completely failed on 5/9/2005. Plant maintenance is working "around the clock" to restore SPDS capabilities. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (COLEMAN) TO NRC (HUFFMAN) AT 1113 EDT ON 5/10/05 * * * The licensee reports that both Unit 1 and Unit 2 SPDS systems were returned to service at 2200 EDT on 5/9/05. The licensee notified the NRC Resident Inspector. R2DO (Lesser) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-09
41679 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-05-07 11:50 | 2005-05-07 14:03 | 2005-05-07 | OFFSITE NOTIFICATIONS DUE TO HYDRAZINE RELEASE "An undetermined quantity of water containing 40 [parts per billion] hydrazine was discharged into the Delaware River through a state permitted outfall. The discharge was stopped at 1130 on 5/7/05 and confirmed by chemistry sample at 1150. Clean-up efforts are in progress. This event had no impact on plant safety or operation. No one was injured as a result of this event. No safety systems actuated or were required to activate as a result of this event. All systems operated as required." The cause is under investigation by the licensee. The licensee notified Lower Alloway Creek Township and the state of New Jersey. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-05-07
41678 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-05-07 03:41 | 2005-05-07 05:29 | 2005-05-07 | TONE ALERT NOTIFICATION SYSTEM OUT OF SERVICE Fitzpatrick was informed by Nine Mile Point that the Tone Alert Notification System has been out of service since 0341 EDT. The licensee did not know the nature of the problem with the Tone Alert system nor was there any information on an estimated repair time. The licensee noted that the Siren Notification System was still operable. The licensee planned to contact Oswego County Emergency Management to obtain additional details on the nature of the problem and to discuss pertinent compensatory measures. See related Nine Mile Point event #41677. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (JOHNSON) TO NRC (HUFFMAN) AT 0952 EDT ON 5/7/05 * * * Oswego County informed the licensee that the Tone Alert System was repaired and returned to service at 0734 EDT. The licensee will notify the NRC Resident Inspector. R1DO (McDermott) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-07
41677 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2005-05-07 03:41 | 2005-05-07 05:25 | 2005-05-07 | LOSS OF SERVICE TO TONE ALERT SYSTEM "This is to report a [10CFR] 50.72 Non-Emergency 8 hour notification per 50.72 (b)(3)xiii. Unit 1 was notified at 05:06 [on 05/07/05] that as of 04:41 EST the Tone Alert System has been out of service for greater than 1 hour. [Licensee] will notify NRC when the system has been restored to service." See related Fitzpatrick event #41678 The licensee indicated there was no notifications being made, except for the NRC Resident Inspector. *** UPDATE FROM M. MINNICK TO J. KNOKE AT 07:53 EDT ON 05/07/05 The licensee (Matthew Minnick) reported their Tone Alert System is back in service, and will be notifying the NRC Resident Inspector of that information. | 68 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-07
41676 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2005-05-06 21:36 | 2005-05-07 00:16 | 2005-06-14 | DEGRADED PIPE RESTRAINT ON HPCI DISCHARGE PIPING "This non-emergency 8-hour report is pursuant, to 10CFR50.72(b)(3). On 05/06/05 at 21:36, [High Pressure Coolant Injection] HPCI was declared inoperable based on a degraded pipe restraint and a degraded snubber associated with the Unit 3 HPCI discharge piping. The degraded pipe restraint and snubber were discovered on 05/05/05 at 17:05. "The subsequent engineering evaluation determined that HPCI is inoperable until the supports are repaired. Reactor operation is unaffected and Unit 3 remains at 100% power. The inoperability of the HPCI system places the plant in a 14 day Limiting Condition of Operation, per [Technical Specification] TS 3.5.1. Further investigation of the cause is in progress." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/14/05 AT 1659 EDT FROM D. FOSS TO A. COSTA * * * "The purpose of this notification is to retract a previous report made on 5/7/05 at 0016 hours (EN# 41676). Notification of this issue to the NRC was initially made as a result of declaring the Unit 3 High Pressure Coolant Injection (HPCI) system inoperable on 5/6/05 at 2136 hours. This declaration was based on a preliminary Engineering evaluation concerning degraded pipe supports associated with the Unit 3 HPCI discharge piping. "Since the initial report, it was determined that two HPCI discharge pipe supports required additional Engineering analysis to assess the as-found condition of the pipe supports. One support (S300) had loose base plate bolts while the other support (S46) had cracked welds. Engineering has determined that the S46 HPCI pipe support in the as-found condition was capable of performing its design function. A piping stress analysis was performed to address the as-found condition of the S300 pipe support. This analysis determined that the HPCI system would remain operable with the S300 support out of service. Therefore, during the period of pipe support degradation, the HPCI system was considered as available and capable of performing its safety function. "Maintenance was planned and repairs were performed to HPCI system pipe supports. These repairs were complete and the HPCI system was restored to full compliance on 5/9/05 by approximately 0430 hours. A root cause evaluation is being performed in accordance with the Corrective Action Program (CR 332355). "The NRC resident has been informed of the retraction." Notified R1DO (Krohn). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-05-07
41675 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2005-05-06 | 2005-05-06 16:46 | 2005-06-07 | LOSS OF SAFETY FUNCTION ON REACTOR WATER CLEAN UP INSTRUMENTATION "Report - Loss of Safety Function "On 5/5/06 at 1130 [EDT] it was discovered test equipment was left installed in the Reactor Water System instrumentation that rendered both system delta flow isolation instruments inoperable. "The test equipment was removed and both instruments were declared operable at 1455." The system was in service at the time. The NRC Resident Inspector was notified. * * * RETRACTION FROM K. RUSSELL TO HOWIE CROUCH @ 1115 HRS. EDT ON 6/7/05 * * * "Update to Event Notification (ENF 41675) Retraction: "An 8-hour notification was made on May 6, 2005, in accordance with 10CFR50.72(b)(3)(v), for the loss of the safety function for the control of radiation release. This report was made when it was discovered that test equipment (a pressure gauge) had been left attached to the Reactor Water Cleanup System (RWCU) differential flow isolation piping. The gauge was removed and the system aligned for proper operation. "An engineering evaluation determined the temporary tubing and gauge would have maintained their structural integrity during a seismic event. Therefore, there was no impact on the piping for the leak detection capability of the RWCU differential flow isolation. Since there was no loss of function for the RWCU differential flaw isolation there was no loss of safety function for the control of radiation release. Because there is no loss of safety function, this condition is not reportable. Since the condition is not reportable, ENF 41675 is retracted." The licensee will be notifying the NRC Resident Inspector. Notified R3DO (Lara). | 9 | 0 | 0 | 9 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2005-05-06
41674 | 0 | COUNTY COLLEGE OF MORRIS |  |  |  |  | 2005-05-03 | 2005-05-06 11:10 | 2005-05-06 | 23 TRITIUM EXIT SIGNS UNACCOUNTED FOR AFTER REMODELING OF BUILDING In December, 2003, the County College of Morris started remodeling several campus buildings. In the pre-planning stages of the construction effort, the electrical contractor accepted responsibility to properly dispose of hazardous materials recovered or during the remodeling effort which included the 23 tritium exit signs. On May 3, 2005, the college requested proof of disposal from the contractor. The contractor was not able to produce the required documents. Upon further investigation, the contractor is currently unaware of the location or disposition of the missing signs. The exit signs were Everglo model 700C/10 with average manufacturing date of June, 2002. Maximum tritium content of each sign was 25 Curies. The college has notified New Jersey Department of Environmental Protection of the missing signs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-05-06
41673 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2005-05-06 10:32 | 2005-05-06 13:10 | 2005-05-06 | AUTOMATIC REACTOR TRIP DUE TO STEAM FLOW/ FEED FLOW MISMATCH SIGNAL "On May 6, 2005, at 10:32 hours, an automatic reactor trip occurred due to a Main Steam Flow/Feedwater Flow mismatch on the 32 Steam Generator (SG). All control rods fully inserted and safety equipment operated as expected. Auxiliary Feedwater started as expected. The Emergency Diesel Generators did not start as offsite power remained available. The plant is in Hot Shutdown at Normal Temperature and Pressure and there was no radiation release. The condition is under investigation and a post trip review is being conducted." No primary or secondary relief valves lifted during the reactor trip. Decay heat is being discharged to the main condenser via the high pressure steam dumps. Auxiliary feedwater is being used to maintain SG level. The electrical grid is stable. There was no affect on Unit 2. The licensee notified the NRC Resident Inspector and the State of New York. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-05-06
41672 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-02-04 | 2005-05-06 11:53 | 2005-05-06 | AGREEMENT STATE - POTENTIAL OVEREXPOSURE The State provided the following information via facsimile: "This is a notification of a potential overexposure. [A technician] was repairing a leak on a high pressure line on a cyclotron. While testing the pressure line, the target unload line at the bottom of the target came lose. This resulted in a mist of water containing F-18. This mist contaminated [the technician's] lab coat. The lab coat was removed with the personnel monitoring badge attached and put behind some lead shielding for decay. This occurred on a Friday so the lab coat was [resurveyed on Monday morning] and was not contaminated. [The technician and] the rest of his clothes [were] not contaminated. This is how the facility believes the overexposure of 12 Rem occurred. The facility has put the following in place as corrective action: The technician will share his maintenance work with another qualified operator for the next six months. Chirping personal dosimeters will be worn during high dose maintenance. Instruction will be given concerning the hazards of radioactivity under pressure. All personnel will report any worker contamination to the RSO within 4 hours." LA Event Report ID No.: LA050004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-05-11
41671 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2005-05-06 04:15 | 2005-05-06 11:44 | 2005-05-06 | LOSS OF COMMUNICATION "At approximately 5:45 AM, [EDT], the Harris Nuclear Plant (HNP) Control Room was informed by Chatham County that the county had lost the ability to receive communication due to the loss of a major fiber ring that services the area. The county would not have been able to receive notification from HNP via the Selective Signaling System or the public phone lines from approximately 0415 to 0539 hours. HNP verified that communications are presently available for the State of North Carolina and all four counties within the 10-mile emergency planning zone. Only the Selective Signaling System to Chatham County remains inoperable and under investigation for repair. This requires an 8 hour non-emergency notification per 10CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. The NRC Senior Resident Inspector was informed." Since the phones are now operable, the licensee would notify Chatham County via the public phone system if required. | 52 | 0 | 0 | 52 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-05-06
41670 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-05-05 23:05 | 2005-05-06 00:32 | 2005-05-06 | TECHNICAL SPECIFICATIONS REQUIRED PLANT SHUTDOWN BEGAN AND THEN TERMINATED "Unit shutdown was commenced at 2305 to comply with requirements of technical specification 3.0.3. 14 and 15 Containment Fan Coil Units (CFCU'S), 2 of 5 total CFCU's, had been removed from service to remove silt buildup in their emergency supply piping. While in this configuration, a tubing line supplying service water pressure for control of the 13SW223 (outlet flow control valve) for 13 CFCU developed a leak that rendered that valve and associated CFCU inoperable. With 3 CFCU's inoperable entry into technical specification 3.0.3 was required. A turbine load reduction was commenced at 2305 at 1% per hour. The 15 CFCU was restored to operable status at 2320 and the technical specification 3.0.3 and the load reduction were terminated. 14 CFCU was returned to operable at 2323. Repairs were made on the tubing for 13 CFCU and that was returned to operable status at 0009 on 5/6/05. 11 and 12 CFCU's were operable and in service for the duration of the event. The unit has been returned to 100% rated power. "The only other safety related equipment removed from service at the time of the event was the 13 service water pump for investigation of a reduced flow condition, and had no impact on this event. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-05-06
41669 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2005-05-04 13:35 | 2005-05-05 16:06 | 2005-05-05 | AGREEMENT STATE REPORT - MISSING TROXLER GAUGE The State provided the following information via facsimile: "At approximately 1:35 PM May 4, 2005, the Agency [Arizona Radiation Regulatory] was informed that the Licensee had determined they were missing a Portable Gauge, Troxler Model 3440, SN 19964. The missing gauge was in storage at the company's location at 1335 West Auto Drive, Tempe, Arizona. The gauge was last accounted for when logged into the secured storage room at 6:30 PM on 4/27/2005. The RSO stated that no one had broken into the building. The gauge contains 8 mCi of Cesium-137 and 40 mCi Am:Be-241. "Tempe PD is investigating and has issued report number 05-073866 "The Licensee is offering a $500.00 reward for the recovery of the sources. A press release is to be made. "The Agency continues to look for the source. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2005-05-10
41668 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2005-05-05 07:30 | 2005-05-05 16:06 | 2005-05-05 | FITNESS FOR DUTY- ALCOHOL A licensed employee was determined to be under the influence of alcohol during a for-cause test. The employee's access to the site has been restricted. Contact the Headquarters Operations Officer for additional details. The licensee has notified the State of Connecticut, local officials, and the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0 | 2005-05-05
41667 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-03-06 15:07 | 2005-05-05 15:44 | 2005-05-05 | INVALID SAFETY SYSTEM ACTUATION DURING AN OUTAGE "This 60-day ENS report is being made per 10CFR 50.73(a)(2)(iv)(A) to report an invalid automatic actuation of systems listed in paragraph (a)(2)(iv)(B), namely ECCS, emergency diesel generator (EDG), and emergency service water (ESW). "On March 6, 2005 at 15:07 hours a Unit 2 Division 3 LOCA signal was inadvertently initiated during replacement of a power supply on ECCS. Continuity on the 24 VDC power distribution signal common was lost while lifting leads on the power supply. One terminal on the power supply was part of a daisy chain circuit connection. This resulted in an unplanned actuation of the high drywell pressure relays. "Two 24 VDC power supplies are connected in parallel to supply power to Division 3 ECCS trip units and relays. It was planned to replace one of these power supplies while the power distribution network remained energized by the redundant power supply. However, the continuity of the power distribution network relied on the connection of two leads on one terminal on the out-of-service power supply. When the two leads were separated several relays lost their normal connection to the signal common. Reverse currents caused the false actuation of the Division 3 high drywell pressure relays. "D23 EDG automatically started and ran unloaded. The C ESW pump automatically started due to the EDG start. The 2A Core Spray (CS) loop received a partial actuation in that the Division 3 signal was initiated but the Division 1 signal was not initiated. 2C CS pump started as designed and 2A CS pump did not start which was expected. The 2A CS loop automatic valve alignment is initiated by the Division 1 signal; therefore, no automatic 2A CS loop valve alignment occurred. All systems functioned as designed during the event. "The cause of the event was that the work package planner for the power supply replacement failed to recognize the impact on plant systems and as a result applied less than adequate technical rigor. The maintenance planning procedure will be revised to ensure the appropriate level of technical rigor is applied for work packages that lift or manipulate a signal common lead. "This event Is reportable per 10CFR50.73(a)(2)(iv)(A) since 2C Core Spray pump, D23 EDG and C ESW pump automatically actuated on an invalid signal." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-05-05
41666 | 0 | UNION HOSPITAL |  |  |  |  | 2005-05-02 16:20 | 2005-05-05 14:25 | 2005-05-05 | MEDICAL EVENT: BRACHYTHERAPY UNDER DOSE ADMINISTRATION On May 2, 2005 to May 3, 2005 during a planned 1 day 5 hour 22 minute brachytherapy vaginal dose a calculated 27% under dose of 1825 cGy dose was administered in a 2.5 cm solid vaginal cylinder. Two 19.56 mg Ra equivalent Cs-137 sources were used. This event was discovered on May 4, 2005 at 10 am, during a summary review, when the licensee discovered that the wrong size applicator cylinder was used. A 1.93 cm cylinder was planned to have been used to apply a 2500 cGy total dose. The licensee contacted the patient about the under dose and plans to administer the rest of the dose on May 5, 2005. The licensee is formulating a plan to administer additional training to the hospital staff to prevent future events of this type. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-05-05
41665 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2005-05-04 14:10 | 2005-05-04 15:20 | 2005-05-04 | UNUSUAL EVENT DECLARED DUE TO A FIRE LASTING MORE THAN 15 MINUTES "At 1432 on May 4, 2005, V.C Summer declared a Notification of Unusual Event (NUE) due to a small fire in the reactor building that lasted for more than 15 minutes inside the protected area of the plant. The reactor was defueled at the time. There were no injuries, radiological conditions remained unchanged, and no safety related equipment was affected. Personal were not required to evacuate the building and the fire brigade was not activated. The resident NRC inspector and all appropriate state and local officials were notified. There was no radiological release. Details are as follows: "At 1410, a health physics technician noticed smoke in the refueling cavity. Upon investigation, it was noted that a temporary lighting power cord had electrically shorted. The power source was isolated at 1420. The electrical short had ignited a small patch of strippable coating that was applied to the cavity floor for contamination control. The resulting flames were extinguished with demineralized water at 1430. A NUE was declared at 1432 in accordance with licensee procedure EPP-001, Activation and Implementation of Emergency Plan. The area was monitored to ensure that there were no further issues and the NUE was downgraded at 1517." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-05-04
41663 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2005-05-03 13:10 | 2005-05-03 14:32 | 2005-05-03 | APPENDIX R FIRE SCENARIO INVOLVING MULTIPLE HIGH IMPEDANCE FAULTS "TMI Issue Report # 329440 identifies an issue associated with a previously unidentified/unanalyzed Appendix R fire scenario involving multiple high impedance faults. An engineering evaluation has determined that certain safety related power circuits are not protected against multiple high impedance faults, which in combination with a fire in the 305' elevation of the Control Building, could cause a loss of safe shutdown functions from the control room and the remote shutdown panel. An hourly fire-watch has been established in the affected fire zone in the 305' elevation of the Control Building as an interim compensatory measure." The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-05-03
41662 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-05-02 16:05 | 2005-05-03 11:23 | 2005-05-03 | FITNESS FOR DUTY A non-licensed contract employee was determined to be under the influence of illegal drugs during a random test. The employee's access to the plant has been terminated. Contact the Headquarter Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2005-05-03
41661 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-05-02 15:30 | 2005-05-03 08:53 | 2005-05-06 | AGREEMENT STATE - PERSONNEL OVEREXPOSURE "On 5/2/2005 at 4:00 p.m., Texas Department of State Health Services was notified by [the] Radiation Safety Officer [RSO] with Testmasters, Inc. in Houston. [The RSO] stated that he had just received the Occupational Radiation Exposure Report for Testmasters during the period of 3/20/05 through 4/19/05 with a monthly whole body exposure of 4.665 Rem to one of his radiographers. This puts the radiographer's annual exposure at 6.395 Rem. He stated that this radiographer works the night shift and usually works in the dark room where there is no source. There is however one portable gage that is used on night shift at Testmasters for radiography. It is an Amersham 660B with an Ir-192 source. The source activity is 140 Ci. The radiographer thinks he left his badge in his tool box which is located in the radiography bay area. Testmasters plans to make a badge storage area in the front office where all employees can keep their badges when not in use. An investigation will follow." The employee's badge has been rescinded until this investigation is completed. State report number: I-8228 * * * UPDATE FROM STATE (K. VERSER) TO P. SNYDER 1200 EDT 5/5/05 * * * The State provided the following information via email: The fourth sentence of the original text above should read as follows: "There is however one industrial radiography camera that is used on night shift at Testmasters for radiography." Notified NMSS (Hickey) and R4DO (Pruett). * * * UPDATE FROM STATE (K. VERSER) TO HUFFMAN 0940 EDT 5/6/05 * * * The State provided the following information via email: "On 5/5/05 DSHS was notified by the licensee that the monthly whole body exposure during the period of 4/20/05 through 5/2/05 had been reported for the affected radiographer. He had received 65 mrem during that period. That brings his annual exposure to 6.45 Rem. He has been restricted from radiological work by the licensee." R4DO (Pruett) and NMSS (Cox) have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-05-06
41660 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-05-02 16:20 | 2005-05-02 20:47 | 2005-05-02 | SUSPICIOUS SUBSTANCE FOUND ON FLOOR OF MAINTENANCE BUILDING An employee discovered a substance wrapped in paper lying on the floor of the Maintenance Building. The substance is being submitted to the state laboratory for further analysis. The licensee notified the NRC Resident Inspector. Contact Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 26.73 |  |  |  | 0 | 2005-05-02
41659 | 0 | WATERFORD | 3 |  |  | [3] CE | 2005-05-02 07:55 | 2005-05-02 12:18 | 2005-05-02 | DURING STEAM GENERATOR TUBE INSPECTION - GREATER THAN 1% (106 TUBES) OF THE TUBES WERE FOUND DEFECTIVE "On May 2, 2005, with Waterford 3 in Mode 6, it was determined that Steam Generator 1 In-Service Inspection had identified more than 1 % defective tubes. Per Technical Specification table 4.4.2-C. this percentage of defective tubes is characterized as "C-3" and should be reported to the NRC. Accordingly, this event is being reported pursuant to 10CFR50.72(b)(3)(ii) as an 8-Hr Non-Emergency Degraded Condition. "In addition, per Technical Specification 4.4.4.5, the final results of the Steam Generator tube inspection, which fall into category C-3, shall be reported in a special report within 30 days and prior to resumption of plant operation." Defective tubes will be plugged. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-05-02
41658 | 0 | DEPARTMENT OF VETERAN AFFAIRS |  |  |  |  | 2005-04-29 | 2005-05-02 11:10 | 2005-05-02 | SHIPMENT RECEIVED WITH EXTERNAL REMOVABLE CONTAMINATION "A package [was received] that exceeded the limits for removable radioactive surface contamination. The package was received on Friday, April 29, 2005, by a permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01 VA. The permittee is the VA Medical Center, Durham, North Carolina. The permittee did not notify the NHPP [National Health Physics Program] until today, May 2, 2005 at approximately 1030 EDT. "The basis for reporting is under 10 CFR20.1906(d)(1) in that the package, an ammo box being used to deliver radioactive materials, had approximately 840 DPM per square centimeter removable radioactive contamination on the outside. "The contamination was limited to one small spot on the ammo box exterior. The interior of the box was not contaminated. "The contamination was identified as Tc [-99m]. "The Cardinal Health Nuclear Pharmacy Services delivered the package. "The permittee Radiation Safety Officer notified the vendor about the package." The shipment was by an exclusive use vehicle. The ammo box contained 2 vials with 60.4 mCi Xe-133 and 35 mCi Tc-99m. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | NC | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2005-05-02
41657 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2005-05-02 06:11 | 2005-05-02 09:43 | 2005-06-03 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN - REACTOR VESSEL LEVEL INSTRUMENTATION "On 5/1/05 at 19:16, the plant entered MODE 2 and began a reactor startup. After withdrawing control rods, but prior to criticality, perturbations were noticed on reactor vessel level indications and control rod withdrawal was halted. "At 22:32 control rods were inserted in reverse order to maintain the reactor subcritical. At that time, level instrumentation associated with the 'A' level reference leg was declared inoperable. All control rods were inserted at 23:02 in Mode 2. "At 23:32 on 5/1/05 a 12 hour shutdown statement was entered due to the inoperable level instrumentation. Efforts were underway to troubleshoot and restore the level Instrumentation. "On 5/2/05 at 06:11 the reactor mode switch was placed in shutdown - level instrumentation will not be restored within the time allowed by Technical Specifications. Instrument fill and vent procedures are being implemented at this time. The plant expects to enter Mode 2 later today." Technical specification 3.3.6.1 requires restoration within one hour, shutdown within 12 hours. This reference leg level affects both the wide and narrow range level instruments and feed into the Reactor Protective System, Emergency Core Cooling System Instrumentation, and Isolation Instrumentation systems. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/3/05 AT 12:02 FROM PERRY'S COMPLIANCE SUPERVISOR (KEN MEADE) TO ABRAMOVITZ * * * "Update to Event Notification (EN 41657) Retraction: "A 4-hour notification was made on May 2, 2005, in accordance with 10CFR50.72(b)(2)(i), for a shutdown required by Technical Specifications. The report was made due to inserting all withdrawn control rods during a startup, prior to criticality, for Technical Specification 3.3.6.1 required actions. Technical Specification 3.3.6.1 was entered as a result of level perturbations determined to have been caused by reference leg keep-fill system operation when the reactor pressure vessel (RPV) was under vacuum conditions with minor component compression fitting leaks. Actions were taken to fix the minor leaks in the reference leg keep-fill panel. Additionally, the reference leg keep-fill system was removed from service until the RPV was pressurized. "It was subsequently determined that since the reactor had not yet been taken critical, the reactor was in a shutdown condition. Per NUREG-1022, rev 2, section 3.2.1 'Plant Shutdown Required by Technical Specifications,' the 'initiation of any nuclear plant shutdown' does not include mode changes required by TS if initiated after the plant is already in a shutdown condition. Since the plant remained in a shutdown condition, this issue is not reportable. "Since the condition is not reportable. EN 41657 is retracted." The licensee notified the NRC Resident Inspector. The R3DO (Burgess) has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Startup; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-05-02
41656 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-05-02 | 2005-05-02 09:55 | 2005-05-06 | STOLEN HUMBOLT DENSITY GAUGE "Sometime between Friday afternoon (4/29/05) and 07:00 Monday morning (5/2/05), a Humbolt density gauge was stolen from the HDR job site. The gauge was stored in a shed located at 10 N Atlantic Ave, Daytona Beach, FL 32115. The Florida Bureau of Radiation Control is investigating the case." Humbolt density gauge model: H-5001EZ Serial number: 4360 Source activity: Cs-137 10 mCi, Am:Be-241 40 mCi Police Report Number from Daytona Beach Police: 2005-05-0073 Florida Report: FL05-69 * * * UPDATE PROVIDED BY ADAMS TO GOULD AT 1545 EDT ON 05/03/05 * * * "[State of Florida] investigator inspected the temp work site storage area and interviewed licensee rep's and found no discrepancies. "The gauge was found by Daytona PD mid afternoon on 3 May behind an abandoned house near Lincoln Street in Daytona Beach. The gauge was in its box undamaged, locks were intact and it was working fine. Licensee has taken possession of the gauge The State office will take no further action on this incident." Notified R1DO (McDermott) and NMSS EO (Holahan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-05-05
41655 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-05-01 11:09 | 2005-05-01 12:57 | 2005-05-01 | MANUAL REACTOR TRIP DUE TO MAIN TURBINE HIGH VIBRATION " Seabrook Station initiated a Manual Reactor Trip during initial start of the main turbine following a refueling outage. Turbine vibrations elevated to the automatic trip set point during initial increase to normal operating speed. The reactor was manually tripped to allow breaking main condenser vacuum and reduce main turbine speed. "The plant is currently stable in Mode 3. All control rods [fully] inserted and decay heat removal is via the main condenser steam dumps." Emergency feedwater (EFW) pump actuation occurred because of lowering steam generator level due to the reactor trip. Steam generator level control was maintained using EFW. Condenser vacuum was broken until the turbine vibration alarms cleared and was then restored, allowing the condenser to be used for dumping steam. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-05-01
41654 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2005-05-01 00:21 | 2005-05-01 04:08 | 2005-05-01 | MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSATE PUMP "The plant was in Mode 1 at 100% power. At 0021 [EDT] the reactor was manually tripped following a loss of 1B Condensate pump per AOP-010, Feedwater Malfunctions. The cause of the 1B Condensate pump trip is not known at the present time. The plant is stable in Mode 3 at normal temperature and pressure. All safety systems functioned as expected; AFW automatically actuated due to low level in the steam generators to provide continued decay heat removal." All control rods fully inserted on the manual reactor trip. Secondary PORVs opened on the trip and reclosed. Steam generators are discharging steam to the main condenser using the turbine steam dump valves. AFW has been secured and main feedwater is operating to maintain SG levels. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-05-01
41653 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-04-29 21:55 | 2005-04-30 | 2005-04-30 | MANUAL REACTOR TRIP - LOWERING STEAM GENERATOR LEVEL ON LOOP #1 "At 2155 EDT on 4/29/2005, Vogtle Unit 1 was manually tripped from 100% power due to lowering steam generator level on loop #1. The main feedwater regulating valve was in manual control and a repair plan was in progress to replace a controlling card which failed earlier in the day. The manual reactor trip caused an automatic aux. feedwater actuation of the motor driven and turbine driven feedwater pumps. All other equipment responded as expected on the trip." At approximately 1600, the loop #1 main feed regulating valve had failed shut while in the automatic mode of operation. The operator shifted control to manual and opened the valve, preventing a reactor trip. At 2155 the recovery plan was being implemented using a plant procedure. While performing the procedure, the loop #1 feed regulating valve shut. The reactor was manually tripped on lowering steam generator level. All rods fully inserted after the manual reactor trip. Decay heat removal is to the main condenser with steam generator level being maintained using the motor driven aux. feedwater pumps. The plant is in its normal shutdown electrical lineup. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-04-30
41652 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-04-29 07:32 | 2005-04-29 12:00 | 2005-08-09 | MINIMUM SWITCHYARD VOLTAGE REQUIREMENTS NOT MET "At 0732 [CDT] on April 29, 2005 Quad Cities Station was notified that the calculated post-LOCA switchyard voltage was below the minimum acceptable value required to ensure offsite power would remain available following a design basis accident. As a result, both offsite power sources were declared inoperable and the appropriate Technical Specification Actions were taken for both Units. The ability of the Emergency Diesel Generators to fulfill their design function was not affected by this condition. This event is being reported in accordance with 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function given the predicted post-LOCA switchyard voltage. The condition was exited at 0836 [CDT] on April 29, 2005. "The required minimum post-accident switchyard voltage is 352.9 KV (Unit 1) and 351.0 KV (Unit 2) while the projected post accident voltage, which prompted this notification, was 347.9 KV. During this timeframe, actual switchyard voltage was approximately 358 KV." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM J. COX TO W. GOTT 1906 ET 08/09/05 * * * "The purpose of this report is to retract ENS report #41652 (April 29, 2005), ENS report 41766 (June 11, 2005), and ENS report #41801 (June 27, 2005). The reports were made following notification that the switchyard predicted voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. For each event, both sources of offsite power were declared inoperable, the appropriate Technical Specification required actions were taken for the units, and an ENS notification was made for a condition that could have prevented the fulfillment of a safety function. "Each Quad Cities unit has two sources of off-site power. For a specific unit, one source is from the switchyard through the unit's Reserve Auxiliary Transformer (RAT) and the second source is from the switchyard through the opposite unit's RAT. Following further analysis of the loading on the RATs during an accident, it was determined that only one source of offsite power to each unit should have been considered inoperable. The analysis determined that because the RAT for the non-accident unit (i.e., the offsite source supplied through the opposite unit) would be carrying a much smaller load, it would not be subject to a degraded voltage condition and resultant isolation from the grid. Therefore, an accident on one unit would not affect the operability of the source of offsite power supplied through the opposite unit's RAT. As a result, only the source of offsite power supplied through the unit's RAT was inoperable. With one source of offsite power available at all times, there was no condition present that could have prevented fulfillment of a safety function, and therefore, these events are not reportable." The licensee notified the NRC Resident Inspector. Notified R3 DO (R. Lanksbury) | 85 | 85 | 0 | 85 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-04-29
41651 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-04-28 17:30 | 2005-04-29 10:37 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * INADEQUATELY CONTROLLED OR ANALYZED PATHWAY FOR MATERIAL ACCUMULATION This event occurred at Building [DELETED] in the Uranium-Aluminum Hydrogen dilution system area. The licensee observed a solution accumulated in a HEPA filter housing on the Building [DELETED] roof. Analysis of the solution determined the liquid to be a caustic byproduct of the process. Further analysis indicated that approximately 3 grams of U-235 were in the HEPA housing and filter. Further reviews of the system design identified potential pathways from the Uranium-Aluminum dissolution system that did not appear to be adequately controlled or analyzed. The nuclear criticality safety of the system relied on the physical design to prevent uranium [DELETED] materials from entering the hydrogen dilution system and the filter housing. The system also relied on a drain in the dilution system ductwork to prevent material from entering the filter housing. The licensee considers the Nuclear Criticality Safety significance low given the very low likelihood of accumulating a sufficient mass or concentration of uranium [DELETED] material into the HEPA filter housing The process was not in operation when the solution in the filter housing was found. The operation will remain shut down until additional reviews and/or design modifications are completed. The licensee will notify the NRC Resident Inspector, the Region 2 Inspector (Ayres), and HQ contact (Berg). * * * UPDATE ON 05/11/08 BY J. KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNANALYZED CONDITION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(1) |  |  |  | 0 | 2008-05-11
41650 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-04-29 01:27 | 2005-04-29 09:55 | 2005-04-29 | REACTOR CORE ISOLATION COOLING FULL FLOW TEST LINE MAY NOT ISOLATE "On 4/28/05 Grand Gulf provided a call in on an issue with [two] secondary containment isolation valves on the Main Steam Line drain system. [See EN-41645] "A preliminary detailed review of similar valves has been completed. An additional concern with the Reactor Core Isolation Cooling (RCIC) full flow test line was noted. Specifically preliminary engineering evaluation indicates that during full flow test with flow to the Condensate Storage Tank concurrent with a high drywell pressure secondary containment isolation signal the differential pressure across the valves may prevent adequate design bases closure. Pending further evaluation this issue is conservatively considered reportable under 10CFR50.72(B)(3)(v)(d). Testing of Reactor Core Isolation Cooling with return to the Condensate Storage Tank has been suspended until resolution of this issue." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-04-29
41649 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-04-29 01:05 | 2005-04-29 05:22 | 2005-06-16 | EMERGENCY HYDRO GENERATORS AUTO START - UNKNOWN CAUSE "Event: At 01:05 on 4-29-05, Oconee Nuclear Station received an Emergency Start of both Keowee Hydro Unit emergency power sources. An investigation is in progress to determine the cause of the system actuation. Plant conditions currently do not indicate the need for actuation of the Keowee Hydro Unit emergency power sources. However, this system actuation is being conservatively reported until it can be positively determined whether a valid actuation occurred. "Initial Safety Significance: Units 2 and 3 remain at 100% power with no issues following the Keowee Hydro Unit emergency start. Unit 1 remains in Mode 5 (refueling outage). No units were affected by the safety system actuation. Plant conditions currently do not indicate the need for actuation of the Keowee Hydro Unit emergency power sources. No other safety systems actuated or exhibited abnormal behavior. Therefore, the safety significance of this condition is LOW." At the time of this notification, the Keowee units were still running unloaded. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM L. GENTRY TO M. RIPLEY 0958 EDT 06/16/05 * * * "This report is being made under § 50.73(a)(2)(iv)(A) INVALID SPECIFIC SYSTEM ACTUATION "At 1:05 AM on 4/29/05 an unplanned emergency start of both Keowee Hydro Units occurred. These units are specifically called out in § 50.73(a)(2)(iv) (B) (8) as " hydroelectric facilities used in lieu of EDGs at the Oconee Station." Each Keowee Hydro Unit can supply emergency power to the three Oconee Units via either of two emergency power paths (Overhead path or Underground path). "This event was initially reported as: - 50.72(b)(3)(iv)(A) - VALID SPECIFIC SYSTEM ACTUATION - Event Number: 41649 - Notification Date: 04/29/2005 - Notification Time: 05:22 [ET] - Event Date: 04/29/2005 - Event Time: 01:05 [EDT] "Unit status as stated in that notification: - Unit 1: 0% RP, Mode 5 for a refueling outage - Unit 2: 100% RP, Mode 1 - Unit 3: 100% RP, Mode 1 "Keowee Emergency Start Channel A actuated. By design, each Emergency Start Channel starts both Keowee Hydro Unit 1 and 2. Both Keowee units did respond and came to rated speed and voltage. "It was determined from the alarms received and from direct visual inspection that the signal for the Keowee Units to emergency start came from the actuation of the KA relay located in Emergency Start Channel A cabinet. Investigation and troubleshooting of this event was unable to identify the actual cause of the actuation of relay KA. The investigation confirmed that no valid condition existed which would or should have resulted in an automatic signal and there is no evidence of intentional or unintentional actuation using manual actuation switches. Therefore the actuation is determined to be 'invalid'. "At the time of the event, Oconee Unit 1 was in an outage and a routine Engineered Safeguard Actuation System (ES) Channel 2 surveillance test was in progress. By design ES Channel 2 initiates Keowee Emergency Start Channel B, so DC control power was removed from Keowee Emergency Start Channel B during that test to prevent an unnecessary Keowee Emergency Start signal. Troubleshooting confirmed that the start which occurred was not due to this test in progress. However, the test affected the event slightly in that ES channel 2 also provides a permissive signal which allows Breaker SK-2 to close to connect the underground path to Standby Bus 2. Following the unintentional start, breaker SK-2 closed as designed, which energized Standby Bus 2, as soon as the Keowee Unit connected to the Underground Path achieved adequate voltage. Because there was no actual loss of power on any of the Oconee Units, there was no demand signal to connect Standby Bus 2 to any unit's Main Feeder Bus. "50.73(a)(2)(iv)(A) requires the following information: (a) The specific train(s) and system(s) that were actuated - Keowee Emergency Start Channel A actuated. By design, each Emergency Start Channel starts both Keowee Hydro Unit 1 and 2. Both Keowee units responded and came to rated speed and voltage. Each Keowee Hydro Unit can supply emergency power to the three Oconee Units via either of two emergency power paths (Overhead path or Underground path). They are aligned so that one unit will supply the overhead path and the other unit will supply the underground path. (b) Whether each train actuation was complete or partial - Other systems, such as the Emergency Power Switching Logic system, must also actuate to automatically connect an emergency power path to a Main Feeder Bus and power Oconee loads. Since this was not a valid event, conditions did not require connection of emergency power to any loads. No complete power train/path alignment was established, therefore the actuation was considered partial. (c) Whether or not the system started and functioned successfully - The Keowee Hydro Units both started and functioned successfully. As stated above, due to the existence of a signal during an unrelated test, one additional component, breaker SK2, was challenged and operated as designed. Therefore, all challenged components functioned successfully. The licensee notified the NRC Resident Inspector. Revised the 10 CFR Section designation in the report header according to the update, and notified R2 DO (T. Decker) | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-04-29
41648 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-04-28 08:46 | 2005-04-28 14:43 | 2005-04-28 | AGREEMENT STATE REPORT - TWO LOST NUCLEAR GAUGES The State provided the following information via facsimile: "On 4/28/05 at about 8:46 am, Pacific Soils Engineering, Inc. notified (Radiologic Health Branch) RHB that two nuclear gauges were stolen from a construction site at Oak Valley Parkway, Beaumont, CA. The stolen nuclear gauges were CPN Model M3 with a S/N M330506989 and M38058248 (each gauge contains Am-241/Be, 50 mCi, and Cs-137, 10 mCi). "According to [licensee] RSO, the nuclear gauges were stored securely, at about 5:00 pm on 4/27/05, in the steel office trailer located at the construction site. The next day, at about 6:15 am, the technicians found that a break-in occurred and the two nuclear gauges were missing. The chain that secured the nuclear gauges was cut off. The local police and Riverside county environmental health were also notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-05-03
41647 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-04-27 17:00 | 2005-04-28 09:20 | 2005-12-16 | AGREEMENT STATE REPORT OF STOLEN TROXLER GAUGE A Troxler gauge was stolen from the back of a truck parked at the licensee's address sometime between 1700 EDT on 4/27/05 and 0800 EDT on 4/28/05. Bolt cutters were used to remove the Troxler which was locked. The State noted that the Troxler should not have been left in the truck overnight. The licensee will be contacting the Police. The Troxler was a model 3440, Serial Number 15579, with an 8 millicurie Cs-137 and a 44 millicurie Am-241/Be source. State Report number is 05-17 * * * UPDATE ON 12/16/2005 AT 10:30 FROM JEFFRIES TO ABRAMOVITZ * * * The Troxler Moisture Density Gauge has been recovered. The thief was apprehended and as part of a plea agreement, on 12/14/2005, notified the Durham Public Defender of the location of the density gauge. The Troxler was found partially buried in the woods. It was not in its case but was protected from the elements by a vinyl container. The gauge was transported a few miles to the Troxler plant. Notified the R1DO (Dimitridis), NMSS EO (Karas) and TAS (via E-mail). Sources that are "Less than IAEA Category 3 sources," are either sources that are very unlikely to cause permanent injury to individuals or contain a very small amount of radioactive material that would not cause any permanent injury. Some of these sources, such as moisture density gauges or thickness gauges that are Category 4, the amount of unshielded radioactive material, if not safely managed or securely protected, could possibly - although it is unlikely - temporarily injure someone who handled it or were otherwise in contact with it, or who were close to it for a period of many weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2005-05-03
41646 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-04-28 07:19 | 2005-04-28 09:18 | 2005-04-28 | UNIT 2 MANUAL REACTOR SCRAM DUE TO LOSS OF MAIN TRANSFORMER COOLING "At approximately 0700 U2 B Main Transformer cooling was lost. Unit 2 reactor power was reduced from 100% to 75%. Attempts to restore the 2B Main Transformer cooling were unsuccessful, and Unit 2 was manually scrammed from 75% reactor power. RPV water level decreased to -30" due to the SCRAM and was restored by normal Feedwater and RCIC injection. The Main Condenser remained available as a heat sink and there were no SRV lifts. The low water level did result in receiving the Level 2 Division 2 containment isolation signal (-38"), and all expected isolations and initiations did occur. "This event requires a 4 hour ENS notification in accordance with 10CFR50.72(b)(2)(iv)(B) for an RPS actuation when critical, and an 8 hour ENS notification per 10CFR50.72(b)(3)(iv)(A) for the injection from RCIC and receipt of the level 2 Containment Isolation signal. Additionally, a press release to the public will be issued, and requires a 4 hour ENS notification in accordance with 10CFR50.72(b)(2)(xi)." All rods fully inserted during the manual scram. The electrical system is in a normal shutdown lineup. Secondary containment ventilation was momentarily disrupted in unit-1 and successfully restored. The licensee notified the NRC Resident Inspector and will be notifying the state and media concerning this event. | 0 | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-04-28
41645 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-04-27 18:07 | 2005-04-28 00:28 | 2005-04-28 | MAIN STEAM LINE DRAIN CONTAINMENT ISOLATION VALVES MAY NOT ISOLATE "Based on an engineering evaluation it appears that the inboard and outboard secondary containment isolation valves (total of 2 air operated valves) on the Main Steam Line drain system may not adequately close under all postulated conditions. This evaluation is based on 'worst case' assumptions for parameters such as air pressure to the valve actuator and maximum expected differential pressure across the valve. Both valves were declared inoperable and closed per the Tech Spec action statement at normal 100% power conditions." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-04-28
41644 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-04-22 | 2005-04-27 19:15 | 2005-04-27 | CALIFORNIA AGREEMENT STATE REPORT - NUCLEAR GAUGE MISSING OR STOLEN AND THEN RECOVERED The State provided the following information via facsimile: "On 4/22/05 at about 3:00 pm, [the representative] from Maurer Service Center, notified RHB-Brea that someone called their office reporting a nuclear gauge that was found in Acton Canyon (City of Acton). The person wanted to send the nuclear gauge to a police officer. A police officer and a hazmat person were called to recover the gauge. [The representative from Maurer Service Center] also went to check the nuclear gauge (Troxler Model 3440, S/N 15046) and verify the serial number to determine the owner of the gauge. According to the database, the nuclear gauge is owned by Leighton & Associates (RML 3109-30). [The representative from Maurer Service Center] contacted the RSO of Leighton & Associates. The RSO was not aware that above nuclear gauge was stolen/missing. "This incident will be further investigated. "[As of 4/27/05,] gauge is still with the service rep. being checked out, but no damage is suspected. Gauge was apparently stolen on 3-17-05 from job site storage on Santa Clarita, CA, but not discovered missing until 4-22-05." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-05-02
41643 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-04-27 09:38 | 2005-04-27 11:46 | 2005-04-27 | OFFSITE NOTIFICATION OF ONSITE FATALITY "A vendor maintenance person died onsite from an apparent heart failure. The [death] did not appear to be directly job related. South Carolina OSHA will be notified. North Carolina, South Carolina, York County, Mecklenburg County, and Gaston County will be notified as a courtesy. The person was not contaminated and was transported offsite by ambulance." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-04-27
41642 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2005-04-26 | 2005-04-26 13:21 | 2005-04-26 | OIL SPILL OUTSIDE OF THE TURBINE BUILDING There was an oil spill of between 10 - 25 gallons of 90 weight oil outside of the turbine building. Cleanup has begun and the State of Connecticut and Department of environmental protection were notified. The NRC Resident Inspector, State and local agencies were notified. * * * UPDATE on 04/26/05 by Mike Baldarelli to C Gould * * * The source of the Hydraulic oil leak was a crane that had undergone maintenance the night before. The oil and soil have been removed. Reg 1 RDO(Barkley) informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-04-26
41641 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2005-04-26 12:45 | 2005-04-26 13:21 | 2005-04-26 | THE LICENSEE MADE AN OFFSITE NOTIFICATION DUE TO A FIRE The licensee reported that there was a small fire lasting for 15-20 minutes in the wiring of a manlift on the charging floor of the Containment Building. It was a smoldering fire with lots of smoke. Offsite fire department was called for assistance. There were two minor injuries to licensee personnel due to smoke inhalation requiring them to be taken to a clinic. Damage was restricted to the manlift. The NRC Resident Inspector along with State and Local Agencies were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-04-26
41640 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-04-26 07:31 | 2005-04-26 07:41 | 2005-04-28 | SPDS (SAFETY PARAMETER DISPLAY SYSTEM) IS DOWN FOR PLANNED MAINTENANCE "At 0731 hours [EDT] on 04/26/2005 the Unit 2 SPDS system was removed from service for planned maintenance. The duration of work is expected to be 48 hours (scheduled for completion at 0700 hours [EDT] on 04/28/2005). "ERDS will remain operable during the work window but several points will not be available. For example 23 of 58 ERDS points will be unavailable while SPDS is out of service. However, the ERDS system will still be operable and transmit the remaining points. "Loss of Emergency Assessment Capability - A review of the ability of the emergency organization to function without SPDS was performed. Alternate sources for many of the points in SPDS were identified and are contained on an Emergency Plan format in PICSY (plant integrated computer system). Those points not available from PICSY can be obtained from the control room. With these compensatory actions and the communications in place between the facilities, there will not be a major loss of emergency assessment capability. "Since the Unit 2 SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The NRC Resident Inspector has been notified. * * * UPDATE ON 4/28/05 AT 1412 EDT FROM RON FRY TO A. COSTA * * * "This is a followup courtesy notification to EN#4160. The Unit 2 SPDS system as noted below [above] has been restored to normal at 13:52 [EDT] on 4/28/05" The licensee notified the NRC Resident Inspector. Notified R1DO (Barkley). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-04-26
41639 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-04-26 00:02 | 2005-04-26 02:12 | 2005-04-26 | AUTOMATIC REACTOR TRIP WITH AFW ACTUATION "The DC Cook Unit 1 Reactor automatically tripped during normal plant startup preparations to synchronize the Main Generator with the offsite electrical GRID. Indicated Reactor power at the time of trip was 8 % power and stable. Preliminary review indicates the trip was caused by an Intermediate Range high flux reactor trip signal. The Intermediate Range High Flux Reactor trip occurred below the Reactor Protection System actuation setpoint. This is a one-out-of-two logic and the trip is active below interlock Permissive P-10 (10% reactor power). The cause of the Reactor Trip is under investigation. This event is reportable under 10CFR50.72(b)(2)(iv)(B), RPS actuation, as a four (4) hour report and under 10CFR50,72(b)(3)(iv)(A), Specified system actuation of the Auxiliary Feedwater System, as an eight (8) hour report. Preliminary evaluation indicates all plant systems functioned normally following the Reactor Trip. DC Cook Unit 1 remains stable in Mode 3 while conducting the Post Trip Review. No radioactive release is in progress as a result of this event. The DC Cook Senior Resident NRC Inspector was notified 04/26/05 at approximately 00:30 [hrs. EDT]." The electrical grid is stable and Unit 1 is being supplied by offsite power. Unit 2 is not affected. All control rods fully inserted. Decay heat is being removed via steam dumps to the main condenser. | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-04-26
41638 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2005-04-25 16:55 | 2005-04-25 20:41 | 2005-06-14 | HPCI DECLARED INOPERABLE "On 4/25/05 @1655, Engineering completed an evaluation and notified Operations that leakage at the packing leak off plug on the bonnet of MO-2-23-014, the Unit 2 HPCI Turbine Steam Supply Valve, is part of the ASME Class 2 piping boundary. Per station procedures, upon discovery of leakage from a Class 2 component pressure boundary, the component is declared inoperable. Therefore MO-2-23-014 and the Unit 2 HPCI system was inoperable. Reactor operation is unaffected and Unit 2 remains at 100% power. The inoperability of the HPCI system places the Unit in a 14-day shutdown Tech Spec action statement. Further investigation of the cause and the ASME Code requirements is in progress." The NRC Resident Inspector was notified * * * RETRACTION ON 6/14/05 AT 1659 EDT BY D. FOSS TO A. COSTA * * * "The purpose of this notification is to retract a previous report made on 4/25/05 at 2041 hours (EN# 41638). Notification of this issue to the NRC on 4/25/05 was initially made it's a result of declaring the Unit 2 High Pressure Coolant Injection (HPCI) system inoperable as a result of leakage at the packing leak off line plug on the valve bonnet of the HPCI Turbine Steam Supply valve (MO-2-23-014). It was determined that this condition constituted ASME Section XI Class 2 pressure boundary leakage. Therefore, the associated equipment was declared inoperable in accordance with station procedures. "Since the initial report, Engineering has determined that the HPCI system was capable of performing its safety function. Although station procedures require ASME Section XI Class 2 components to be declared inoperable when pressure boundary leakage is determined to exist, the safety function of the MO-2-23-014 was maintained. Leakage through the seal weld on the packing leak off line plug did not affect the capability of the MO-2-23-014 valve to perform its safety function. Therefore, HPCI was capable of performing its safety function. "Maintenance was planned and HPCI was removed from service on 4/26/05 to repair the HPCI MO-2-23-014 valve bonnet. The valve was repaired and the system was returned to service by 1730 hours on 4/26/05 (CR 328735). "The NRC resident has been informed of the retraction." Notified R1DO (Krohn). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-04-25
41637 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2005-04-25 16:00 | 2005-04-25 20:18 | 2005-04-27 | MOISTURE DENSITY GAUGE LOST AT JOB SITE A Troxler Model 3440 moisture density gauge (S/N 33256, activity 8.8 milliCurie of Cs-137 and 44 milliCurie Am/Be) was lost at a job site after 4:00 pm on April 25, 2005. The gauge user did not check that the gauge was present in the transport vehicle before proceeding to the next job site. The fence around the jobsite was locked, and no other workers were present to determine whether the gauge was found and placed in the licensee's work trailer. Officials (local police, etc) will be notified if the gauge is not found at the job site on 4/26/05. Nevada Report NV-05-005. * * * UPDATE PROVIDED BY THE STATE (MARSHALL) TO NRC (HELD) ON 4/27/05 AT 11:23 * * * The following update was provided by the State via facsimile: "The gauge was found the same day the device was lost. The masonry contractor who found the gauge at the job site contacted a contractor who is also a gauge licensee and was working at the same job site. The gauge licensee/contractor then took possession of the gauge and notified Owens Geotechnical who took possession of the gauge on 4/26/05. This incident is considered to by closed." R4DO (Johnson) and NMSS EO (Essig) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2005-04-28
41636 | 0 | CRAIG TESTING LABORATORY |  |  |  |  | 2005-04-25 13:30 | 2005-04-25 15:57 | 2005-04-25 | LICENSEE REPORTED A LOST TROXLER GAUGE MODEL 3430 A technician for the Craig Testing Laboratory placed a Troxler gauge model 3430 and its transportation box into the back of his pickup securing it with a chain, however he did not latch the top of the box or close his truck's tailgate. When he drove from the job site in Pocoson, PA., he heard a noise but he did not stop until he reached a stop light (approx 2 miles away). He got out of the truck and noticed the transport box was dangling from the back of the truck still attached to the chain, but without the Troxler gauge inside. He retraced his route, but there was no Troxler gauge. The Troxler gauge (SN # 25540) contained 8 millicuries of Cs-137 and 40 millicuries of Am/Be-241. The local police Department was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-04-25
41635 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-04-09 10:39 | 2005-04-25 15:57 | 2005-04-25 | INVALID SPECIFIED SYSTEM ACTUATION "This report is being made under 10CFR50.73(a)(2)(iv)(A) - Invalid Safety System Actuation. "At 10:39:06 on April 9, 2005, the steam supply valve to Unit 2 turbine-driven auxiliary feedwater pump, 25A-48ABC, was manually failed open during a maintenance activity causing the pump to start. There was no valid actuation signal. The train of auxiliary feedwater started and functioned successfully. The actuation was complete and lasted for 1 minute and 25 seconds." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION | [9 empty] | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-04-25
41633 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-04-21 | 2005-04-25 14:23 | 2005-04-25 | TWO TRITIUM SOURCES LOST IN TRANSIT Two 1.6 Curie tritium neutron generator tubes licensed for well logging were picked up by FedEx at the licensee's facility in Houma, LA on 04/11/05. The destination was Princeton Junction, New Jersey. On 04/21/05 it was confirmed that the package was lost. The shipment was tracked to different locations within FedEx. No other information is currently available. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-04-28
41632 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-04-25 12:00 | 2005-04-25 12:30 | 2005-05-04 | THE PLANT'S TSC (TECHNICAL SUPPORT CENTER) HAS BEEN TAKEN OUT OF SERVICE DUE TO PLANNED MAINTENANCE WORK "On 4/2512005 at 12:00 p.m., EDT the Hatch Nuclear Plant's Technical Support Center (TSC) was removed from service for planned maintenance and equipment modifications. The maintenance activities require relocation of the control panel (1X75-C001) which contains the HVAC controls and annunciators as well as the radiation monitoring meter and annunciator. The loss of this equipment requires taking the TSC out of service. The maintenance activities are scheduled to take five weeks. The alternate TSC will remain operable and available, so no loss of TSC function will occur due to the maintenance activity. "This event is reportable per 10CFR50.72 (b)(3)(xiii) as described in NUREG-1022, Rev. 2 since this work activity results in a loss of an emergency response facility for the duration of the evolution." The NRC Resident Inspector was notified and state and local notifications will be made. * * * UPDATE ON 05/04/05 @ 1510 BY GREG JOHNSON TO GOULD * * * The TSC was returned to service at 1100 EDT on 05/04/05. The NRC Resident Inspector was notified. The Reg 2 RDO (Lesser) was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-04-25
41631 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2005-04-24 21:30 | 2005-04-24 21:39 | 2005-04-24 | SPDS (SAFETY PARAMETER DISPLAY SYSTEM) IS DOWN FOR PLANNED MAINTENANCE "At 2130 hours on 04/24/2005 the Unit 1 SPDS system will be removed from service for planned maintenance (cable rework). The duration of work is expected to be 32 hours (scheduled for completion at 0530 hours on 04/26/2005). "ERDS will remain operable during the work window but several points will not be available. For example 23 of 58 ERDS points will be unavailable while SPDS is out of service. However, the ERDS system will still be operable and transmit the remaining points. "Loss of Emergency Assessment Capability - A review of the ability of the Emergency organization to function without SPDS was performed. Alternate sources for many of the points in SPDS were identified and are contained on an Emergency Plan format in PICSY (plant integrated computer system). Those points not available from PICSY can be obtained from the control room. With these compensatory actions and the communications in place between the facilities, there will not be a major loss of emergency assessment capability. "Since the Unit 1-SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii)." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-04-24
41630 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-04-23 23:00 | 2005-04-24 12:25 | 2005-04-24 | FLORIDA AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE State of Florida Bureau of Radiation Control received the following information from the Radiation Safety Officer for Qore Inc., located in West Palm Beach, FL. On 04/23/05 at 2300 EDT a Qore Inc. employee discovered that the Troxler Moisture Density gauge that had been cabled and locked to the bed of his truck was missing, cable had been cut Model number of the Troxler gauge is unknown at this time but usually a Troxler Moisture Density gauge contains 10 milliCuries of cesium-137 and 40 milliCuries of Am-241/Be. The gauge serial number is 22430, cesium-137 source serial number is 75-4160 and the americium-241 source serial number is 47-18251. The gauge was in its locked position and locked inside its case at the time it was stolen. The employee's truck was parked in front of a private residence at the time of the incident. West Palm Beach police were notified by the licensee of the stolen Troxler Moisture Density gauge and the report case number is 0S-9770. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-04-27
41629 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2005-04-23 | 2005-04-23 18:43 | 2005-04-23 | DISCOVERED TWO AXIAL INDICATIONS ON INSIDE DIAMETER OF REACTOR VESSEL HEAD PENETRATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up will be made via the ENS or under the reporting requirements of 10CFR50.73. "On April 23, 2005, at approximately 11:35 Mountain Standard Time (MST) engineering personnel performing preplanned in-service examinations of reactor vessel head vent penetration in accordance with procedure requirements discovered two axial indications in the Palo Verde Nuclear Generating Station Unit 2 reactor vessel head vent penetration. The indications are located on the inner diameter surface of the pipe adjacent to the J-weld to the head and are part of the RCS pressure boundary. The indications are characterized as axial, estimated less than 0.080 inch deep, approximately 0.1 inch long, and oriented at approximately 90 degrees from each other. The indications are not through-wall. There is no evidence of RCS pressure boundary leakage. "Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.14 permits no reactor coolant system (RCS) pressure boundary leakage and there is no evidence of pressure boundary leakage. Nevertheless, the indications are being conservatively identified as abnormal degradation of the reactor coolant system pressure boundary and will necessitate taking corrective action to restore the barrier's capability. Therefore, the ENS notification of this event is in accordance with 10CFR50.72(b)(3)(ii)(A). The Unit had been shutdown for its 12th refueling outage and was being maintained de-fueled for maintenance. "No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. " An investigation of this event will be conducted in accordance with PVNGS corrective action program." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-04-23
41628 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2005-04-23 10:45 | 2005-04-23 14:58 | 2005-04-23 | PLANT LOST ERDADS (EMERGENCY RESPONSE DATA ACQUISITION DISPLAY SYSTEM) DATA LINK CAPABILITY "On April 23, 2005, at 10:45 hours St. Lucie Plant last the ERDADS NRC Data Link capability. The System Engineer reports that the ERDADS periphery switch failed to swap to the "A" CPU from the "B" CPU on a auto failover that occurred at 10:45. The switch has been manually swapped and the Data Link has been restored. A work order has been prepared to investigate and repair the cause for this failure." The NRC resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-04-23
41627 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-04-23 07:30 | 2005-04-23 10:26 | 2005-04-23 | FITNESS FOR DUTY: ALCOHOL A non-licensed contract employee was determined to be under the influence of alcohol during a for cause test. The employee's access to the plant has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee will notify the Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2005-04-23
41626 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2005-04-21 14:50 | 2005-04-22 18:56 | 2005-04-22 | EQUIPMENT FAILURE TO FUNCTION AS DESIGNED "A licensee employee, trained by the device manufacturer, was performing a device inspection (inventory/shutter check/leak test) for one of the licensee's non-portable gauging devices (Ohmart Corporation Model SH-F2, serial number 2296CG) containing 7.4 gigabecquerels (200 millicuries) of cesium-137 (sealed source model number A-2102). A screw broke off while the employee was closing the device shutter. Because the screw broke off, the shutter could not be closed. The licensee plans to follow the manufacturer's procedures for this particular incident as per the manufacturer's training and instruction. This device will either be repaired by an individual specifically licensed by the Executive Secretary, the U.S. Nuclear Regulatory Commission, or an Agreement state to perform such service, or the licensee will return this device to the manufacturer." Event date was March 2005 and reporting date was April 21,2005. Utah event report # UT-05-0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2005-04-27
41625 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-04-22 14:13 | 2005-04-22 15:24 | 2005-04-22 | POTENTIALLY CONTAMINATED PERSON TAKEN OFFSITE VIA AMBULANCE "Individual received laceration to right leg while working in Unit 1 RB (Reactor Building). Individual transported to Oconee Memorial hospital with potential contamination." Ambulance came from Oconee Memorial Hospital. It is site practice to send a Rad Tech along with any potentially contaminated person. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2005-04-22
41624 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2005-04-22 06:00 | 2005-04-22 14:01 | 2005-04-22 | CONTRACT EMPLOYEE TESTED POSITIVE DURING A FOR-CAUSE FITNESS FOR DUTY TEST A contract foreman tested positive for alcohol during a for-cause alcohol test. The employee had not performed any work and was not allowed access to the site. The employee's access to the site was terminated. The NRC Resident Inspector was informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 26.73 |  |  |  | 0 | 2005-04-22
41623 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-04-21 20:13 | 2005-04-22 10:55 | 2005-04-22 | AUTOCLAVE SHUTDOWN DUE TO HIGH CONDENSATE "On 04/21/05 at 2013 hours, Autoclave #2 in the X-343 Facility experienced a Steam Shutdown due to high condensate level alarms (A) and (B) actuating. The autoclave was in an applicable TSR mode (Mode II, Heating) at the time of the alarm actuations. The autoclave was placed in Mode VII (Shutdown) and declared INOPERABLE by the Plant Shift Superintendent (PSS). An investigation is underway to determine the cause of the actuations. No release of radioactive material occurred as a result of this incident. This event is being reported in accordance with UE2-RA RE1030, Appendix D. J. 2. Safety System Actuations. NRC, Region II has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2005-04-22
41621 | 0 | FRAMATOME ANP |  |  |  | URANIUM FUEL FABRICATION | 2005-04-21 10:00 | 2005-04-21 18:12 | 2005-04-21 | RECEIVED TWO PACKAGES EXCEEDING EXTERNAL RADIATION LIMITS. "Framatome ANP, Mt. Athos Road, Lynchburg, VA, received seven packages of nuclear services equipment from Browns Ferry Nuclear Plant. Two of the packages exceeded the surface external radiation limit of 10 CFR 71.47 (200 millirems/hr). The first package , ID # 9070108, had one hot spot on the bottom of the container that read 301 mRem/hr. The second package, ID # 9011352, had one hot spot on the bottom of the container that read 280 mRem/hr. The packages have been received and are in the Framatome secure area. "Framatome ANP is reporting per the requirement of 10 CFR 20.1906." The hot spots on both packages were small, less than one square inch in size. Radiation surveys taken inside the cab of the truck that delivered the packages found no elevated radiation levels. Neither package had surface contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(1) |  |  |  | 0 | 2005-04-21
41620 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-04-19 | 2005-04-21 15:05 | 2005-04-21 | EQUIPMENT FAILED TO FUNCTION AS DESIGNED The following information was provided by the State via facsimile: "On Wednesday, April 19, 2005 while loading a Pd-103 seed into the Mick applicator, the applicator jammed. When the operating room technician attempted to get the seed loose, the seed broke. This spread a small amount of radioactive contamination onto the table, which was cleaned up by the RSO and dosimetrist. The applicator was found to be contaminated. It was put in a plastic bag, placed behind lead shielding and locked in the Nuclear Medicine hot lab. The activity of the Pd-103 seed was 1.578 mCi (millicuries). According to the licensee, there was no overexposure, contamination, or intake of radiation by anyone present in the operating room. The patient was treated, as per the prescription after borrowing a Mick applicator from another hospital. "The licensee notified DHFS on April 20, 2005. The licensee also contacted their consultant and their MIC applicator distributor regarding the event. A replacement applicator is being sent and the contaminated applicator will be allowed to decay before servicing. "The licensee has developed, an action plan for this event based on possible causes: 1. Look into the possibility of having the MIC applicator on a preventative maintenance schedule. 2. Change the sterilization procedure such that central supply does the cleaning of the applicator, not the OR technician. 3. Set up a 'core' group of OR technicians who are involved in their procedure, and document their education. "A voluntary MedWatch form was sent in to the FDA. "Wisconsin Radiation Protection Section plans on investigating this event." State Event Report ID # 24. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-04-26
41619 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-05-26 | 2005-04-21 11:22 | 2005-04-21 | AGREEMENT STATE - LOST KAY-RAY/SENSALL MOISTURE ANALYZER The following information was received from the Washington State via E-mail: "Location of Event: The former Pendleton Flour Mills / Fisher Flour Mills site (located on Harbor Island, at 13th Avenue Southwest and Klickitat Avenue Southwest, Seattle, Washington). "This is to report a missing [Generally Licensed] GL radioactive material device and its radioactive source (one Kay-Ray/Sensall moisture analyzer, device model 7062P, housing serial number 9954, source serial number 9310V, containing 50 millicuries cesium-137 (as of May 31, 1979). The last known location of the device / radioactive source is the former Pendleton Flour Mills / Fisher Flour Mills site (located on Harbor Island, at 13th Avenue Southwest and Klickitat Avenue Southwest, Seattle, Washington). Presumed missing after May 26, 2000 (date of last apparently reliable inventory confirmation from Fisher). "The apparent cause is loss of physical control of general license material during sale of mill site; or possibly inadequate documentation of proper disposal / transfer of the device / radioactive source. Since 1979 the device / radioactive source was reportedly located at that site. Washington State sales records indicate that Pendleton bought the mill site from Fisher on April 24, 2001, and that King County bought the mill site from Pendleton on July 28, 2003. [Office of Radiation Protection] ORP discovered the discrepancy during GL registration for material indicated to be on site. After an extensive investigation, ORP can not determine the status of the material. "Corrective Actions: Pendleton and Fisher replied to ORP March 18, 2005, notice of noncompliance letter for potential loss of control of the device. The replies were unacceptable since they are inconsistent and do not confirm the location of the material. Fisher reported they transferred said device / source to Pendleton; and Pendleton reported that Fisher removed said device / source). The ORP April 18, 2005, noncompliance letter directs Pendleton and Fisher to jointly conduct a thorough and exhaustive physical search of the entire mill site, since both still have spaces there, and for Pendleton and Fisher to perform additional interviews of current and former company employees who may know more about the status of the device. Pendleton and Fisher must cooperate with ORP to provide ORP with a written and acceptable reply identifying the disposition of the missing device. "Event Number WA-05-014, missing Generally Licensed (GL) device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-04-26
41618 | -1 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-04-20 16:10 | 2005-04-20 22:40 | 2005-04-21 | BOTH PENETRATION ROOM VENTILATION SYSTEM TRAINS TEMPORARILY INOPERABLE "At 16:10 on 4-20-05, Oconee Unit 3 entered Technical Specification 3.0.3 due to [valve] 3PR-20 being failed closed for testing on the Penetration Room Ventilation System. 3PR-20 is the suction cross connect valve for the two trains of the Penetration Room Ventilation System. Technical Specification Surveillance requirement 3.7.10.5 requires that 3PR-20 be verified capable of being opened every 18 months. This surveillance cannot be met if 3PR-20 is failed closed. Therefore, both Penetration Room Ventilation System trains had to be declared inoperable since the LCO was declared not met. Entry into Technical Specification 3.0.3 conservatively indicates that a loss of safety function could have occurred. Therefore, this condition warrants reporting via an eight-hour non-emergency report as a condition which could result in a loss of safety function. The Technical Specification 3.0.3 entry condition was recognized 'after the fact' by the Shift Technical Advisor. Following recognition of this condition, operating air was restored to 3PR-20 and it was returned to operable at 18:24 on 4-20-05. "The Penetration Room Ventilation System functions to channel Reactor Building penetration leakage to a high-efficiency carbon/HEPA filtration system prior to release via a ventilation stack. The Penetration Room Ventilation System consists of two trains. Each Penetration Room Ventilation System train has a fan, ducting, suction and discharge valves, and in-line carbon and HEPA filters. The Penetration Room Ventilation System discharges to a larger high-efficiency carbon/HEPA filtration system before being released via a ventilation stack. 3PR-20 is the suction cross connect valve for the two trains of the Penetration Room Ventilation System. 3PR-20 was originally installed to provide cooling of an idle filter train if one trains of the Penetration Room Ventilation System failed. However, subsequent analyses have concluded that 3PR-20 is no longer required to provide this cooling since natural circulation around the idle train filter assembly is adequate to remove decay heat to prevent carbon bed ignition. Appropriate changes to the Technical Specification for this issue have not yet been completed. Therefore, the safety significance of this condition is LOW. "Corrective Action(s): 1) 3PR 20 was returned to operable. 2) A Technical Specification change will be developed to address the discrepancies between design basis and Technical Specifications requirements (licensing basis)." The licensee has notified the NRC Resident Inspector. **** RETRACTION from David Nix to MacKinnon at 1940 EDT on 04/21/05 ***** "Withdrawal of Event Number 41618 "On 04/20/2005 at 22:40 [ET] Oconee reported Unit 3 entry into Technical Specification (TS) 3.0.3 due to valve 3PR-20 being failed closed. 3PR-20 is the suction cross connect valve for the two trains of the Penetration Room Ventilation System. TS Surveillance Requirement 3.7.10.5 can not be met if 3PR-20 is failed closed. Further review concluded that it was inappropriate to enter TS 3.0.3. The appropriate TS condition was TS 3.7.10 Conditon A for one train inoperable. Therefore this event does not meet reportability requirements and is hereby retracted. "Initial Safety Significance: "UFSAR sections 6.5.1.3 and 9.4.7.2 clarify that 3PR-20 was originally installed to open in the event of failure of one fan to allow air flow to be maintained through that fan's filters by connecting to the other train which is assumed to be operating. This would prevent carbon bed ignition by removing decay heat of radioactive materials trapped on the filters. Analysis performed in 1990 concluded that natural circulation around the idle train filter assembly provides adequate heat transfer. Therefore there is no physical or analytical need for 3PR-20 to perform its TS function. A TS amendment was approved 6-1-2004 which will delete TS 3.7.10, and the requirement for 3PR-20, but the implementation of that TS change is awaiting completion of certain modifications. "However, since the existing TS credits 3PR-20 with mitigating a single failure, the result of the inoperability of 3PR-20 is that it cannot mitigate that single failure. It is noted that Oconee Unit 3 is currently in TS 3.7.10 Condition A due to indicated low flow in the 3A PRVS train. While in that TS condition, it is not required to assume a single failure which would make the remaining train inoperable. Therefore 3PR-20 is not required while in Condition A." NRC R2DO (C. Julian) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2005-04-20
41617 | 0 | WATERFORD | 3 |  |  | [3] CE | 2005-04-19 16:51 | 2005-04-19 22:15 | 2005-04-19 | DEGRADED CONDITION FOUND AT WATERFORD UNIT 3 "Waterford Unit 3 shutdown on 4/17/2005 at approximately 0047 hrs to begin refueling outage 13. During performance of the Alloy 600 Program pressurizer "bare metal" inspection, a small amount of boric acid was discovered in the annulus around Pressurizer heater sleeves C4 and D2. Entergy had already planned to weld repair/replace the Alloy 600 pressurizer sleeves and remaining Alloy 600 small bore instrument penetrations using Alloy 690 materials during this refueling outage. "This condition constitutes a degradation of the RCS Pressure Boundary and is reportable in accordance with 10 CFR 50.72(b)(3)(ii)(A) with a required followup written Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(ii)(A)." The NRC Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-04-19
41616 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-04-19 20:52 | 2005-04-19 21:59 | 2005-04-19 | TECHNICAL SPECIFICIATION REQUIRED SHUTDOWN RELATED TO PRESSURE BOUNDARY LEAKAGE The licensee "entered technical specification limiting condition for operation 3.0.3 due to pressure boundary leakage on a 3/4 inch pipe on the piping for the boron injection tank. As a result of this, both trains of high head injection [have been declared] inoperable. Unit shutdown began at 2105 [EDT]. All other safety systems are operable. Current plans are to take the plant to mode 4 and isolate and replace the affected piping. The current leakage is 780 cc/hr." The licensee discovered the leakage during operator rounds at approximately 0500 EDT. Technical Specification 3.0.3 was entered at 2052 EDT. Power reduction is currently in progress. The licensee will be notifying the NRC Resident Inspector and Lower Alloways Creek Township. | 78 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-04-19
41615 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-04-19 19:45 | 2005-04-19 20:06 | 2005-04-19 | FLORIDA AGREEMENT STATE REPORT OF MISSING TROXLER GAUGE The Florida Bureau of Radiation Control reported a missing Troxler moisture density gauge. The agreement state licensee, Burcaw Geotechnical Group, was using the gauge at a site located in Ruskin, Florida. The gauge overpack, which was thought to contain the gauge, was picked up at the end of the work day and placed into a truck. While in transit, the driver realized that he had not been verified the gauge was actually in the overpack. He checked the overpack and found it to be empty. He returned to the job site and conducted a search but could not locate the gauge. The licensee informed the Florida Bureau of Radiation Control. The Bureau of Radiation Control requested the licensee to contact the police and report the gauge missing. The Troxler gauge (serial #34752) contained a 40 milliCurie Am-241/Be source and a 10 milliCurie Cs-137 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-04-22
41613 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-01-04 | 2005-04-19 16:11 | 2005-04-19 | CALIFORNIA AGREEMENT STATE REPORT - MISSING TRITIUM EXIT SIGNS The following information was provided by the State via facsimile: "[The University] reported the loss of six generally licensed tritium exit signs. They do a quarterly inventory and noticed six were missing when they did their inventory on 01-04-05. The previous inventory had been on 06-20-04. They suspect students may have stolen the signs. The current activity estimate for all six signs is 27.6 Curies, with the highest sign having an estimated current activity of 7.5 Curies." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-04-22
41612 | 0 | DIANON SYSTEMS |  |  |  |  | 2005-04-13 | 2005-04-19 13:45 | 2005-04-19 | RECEIPT OF TWO UNIDENTIFIED RADIOACTIVE SOURCES WITHOUT DOCUMENTATION Dianon Systems is a diagnostic laboratory licensed by the NRC to handle P-32 and I-125. On April 13, 2005, Dianon received a shipment of two radioactive sources without any information as to what the sources were, their strength (i.e., radioactivity), or what diagnostics where to be performed. Dianon immediately contacted the originator of the shipment, a doctor out of Brooklyn, NY. The doctor was not willing to provide any information on the sources other than to say that the sources were "6 months old, safe, and no threat." Dianon surveyed the sources and found that they were still radioactive, however, the caller was unable to provide a meaningful millirem/distance reading. Dianon has safely secured the sources in lead shielding and is uncertain on how to proceed in resolving disposition of the sources. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | CT | MAT | [5 empty] | 0 | 2005-04-19
41611 | 0 | NUCLEAR CARDIOLOGY DIAGNOSTICS |  |  |  |  | 2005-04-13 | 2005-04-19 12:52 | 2005-04-19 | RADIOACTIVE MATERIAL INADVERTANTLY PUT INTO NORMAL TRASH On 4/15/05, the licensee discovered that two vial sources were missing. Upon investigation, it was determined that the vials were inadvertently put into the normal trash dumpster on 04/13/05. One vial contains 134 microCuries Cs-137 and the other contains 74 microCuries Ba-133 (both activities as of 04/15/05). The vials were described as approximately 2-inches in height and 1-inch in diameter. The licensee believes that the vials were not labeled. The licensee notified the trash pickup company (Midco) and is currently waiting for a return call. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-04-19
41610 | 0 | SPECTRUM TECHNOLOGIES |  |  |  |  | 2005-04-18 | 2005-04-18 17:30 | 2005-04-18 | PART 21 NOTIFICATION CONCERNING CUTLER-HAMMER A200 NEMA SIZE 1 STARTERS "In March 2002, Spectrum Technologies provided 20 Class 1 E safety related Cutler-Hammer A200 NEMA Size 1 starters to Rochester Gas & Electric Company - Ginna Station. Spectrum Technologies had purchased the starters as commercial grade items from Cutler-Hammer, and dedicated them per EPRI NP5652, method 1, Special Tests and Inspections. "Ginna Station advised Spectrum Technologies that they had installed one of these starters in the circuit for their Boric Acid Storage Tank (BAST) Heaters. Approximately eight (8) weeks later they received an alarm for low BAST temperature. Investigation found an open coil on the starter and replaced the starter. The failed starter was sent to the Ginna Materials Laboratory for analysis. This analysis indicates that a manufacturing defect caused the failure. "The Ginna Materials Laboratory examined the starter using a low power binocular microscope for signs of defects, overheating, or cracks. Resistance measurements between the two coils in the starter were taken and they were then subjected to X-ray radiography. Subsequent to this, the coils were disassembled and sectioned to reveal the defect. The failed coil wire was also examined using scanning electron microscopy for signs of overheating or melting. "It was determined that the failure is the result of a manufacturing defect in the epoxy surrounding the coil. The open circuit was caused when the epoxy cracked at the defect and broke a wire running through the epoxy. This wire connected the two coils and this failure caused the open circuit. "Spectrum Technologies has provided the above information, including all figures, to Cutler-Hammer for them to investigate/evaluate the situation. Spectrum Technologies has requested that they provide a formal report addressing what caused the condition and whether it is unique or a common problem, what other components may be affected, and what will be done to prevent recurrence." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2005-04-18
41609 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-04-18 16:45 | 2005-04-18 16:54 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * CONCURRENT REPORT UNDER PART 70 APPENDIX A FOR OFFSITE NEWS RELEASE "This concurrent report is being made to the NRC as a result of a media inquiry that was made to BWX Technologies as a result of Event #41594, that was originally reported to the NRC by Ledoux & Company on April 13, 2005. The attached BWX Technologies Press Release was provided to Alex Nussbaum of the Bergen Record, Hackensack, NJ at approximately 4:45 pm on April 18, 2005." Contact HOO for information on the press release. The NRC Resident Inspector will be notified. The NMSS EO (Flanders) and R2DO (Fredrickson) have been notified. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 0 | 2008-05-11
41608 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2003-09-30 12:00 | 2005-04-18 10:48 | 2005-04-18 | CHEMICAL AGENT DETECTORS MISSING FROM DEPARTMENT OF NAVY INVENTORY A representative for the Navy's master material license reported two chemical agent detectors were missing since their last audit on 9/30/2003. One detector was a Automatic Chemical Agent Detector Alarms (ACADA) which has 230 microcuries of Am241 with a surface exposure of 0.4 millirem/hr. The identification number is SSND -NR-1065-D-101-E. The other detector was a hand held vapor detector containing a 10 microCurie Ni63 source with identification number SSND-NR-0399-D-101-E. The licensee was informed by a supply room person that the detectors were assigned to the USS Fletcher on 9/30/03, and have not been accounted for since. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-04-18
41607 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2005-04-17 08:42 | 2005-04-17 09:23 | 2005-04-17 | ALERT DECLARED DUE TO UNIT 3 MAIN STEAM RELIEF VALVES NOT RESEATING AFTER ACTUATION At 09:23 the licensee indicated that several Main Steam Relief Valves lifted and stayed open. A high pressure flow signal from the secondary Steam Generator caused initiation of Unit 3 Safety Injection, which in turn caused the Reactor to trip. All rods fully inserted as required. Activation of the Safety Injection subsequently caused the Pressurizer level to go solid. About 30 minutes into the event the primary Reactor Coolant and Main Steam Systems stabilized, including the Pressurizer level and pressure. During the initial briefing, about 09:35, the licensee reported that all secondary Safety Relief Valves have reseated. Decay heat is being directed to the Atmospheric Dumps due to the Main Condenser not being available. The licensee is attempting to establish ERDS. Initial assessment of this incident is believed not to be security related, however, follow-up is being conducted to verify same. At 09:48, NRC management made a decision to enter into Monitoring Mode. At about 11:15 the licensee indicated that a valve in the Charging System indicated some leakage, therefore it was isolated. Licensee stated that no radiological releases and no S/G tube leakage was indicated. Licensee notified State and local emergency response agencies. They will notify the NRC Resident Inspector. Notified DHS (Doyle), FEMA (Biscue), DOE (Smith), USDA (Magners), and HHS (Hogan). * * * UPDATE FROM D. DODSON TO W. GOTT 1328 EDT 04/17/05 * * * "At approximately 0830 on April 17, 2005 Millstone Unit 3 experienced an automatic reactor trip from full power. The Reactor is in a stable shutdown condition and is proceeding to Mode 5 cold shutdown. No release of radioactivity other than those minor releases associated with normal plant operation has occurred. There were no personnel injuries associated with the event. "In addition to the Reactor Trip, half-train Safety Injection (SI) and half-train Main Steam Isolation (MSI) actuations occurred. Control room personnel were successful at manually initiating full SI and MSI. SI has since been terminated and RCS pressure control has been restored. Multiple steam line safety valves (MSSV) lifted with at least one MSSV indicating a failure to reclose. As a result, an ALERT was declared at approximately 0853 due to the failure of at least one MSSV failing to reclose. All MSSVs are currently closed. Auxiliary Feedwater (AFW) actuated automatically as expected, however, the turbine driven auxiliary feedwater pump (TDAFWP) tripped on start-up and was subsequently reset locally. Both motor driven auxiliary feedwater pumps (MDAFWPs) operated as expected to maintain steam generator water levels. Due to the additional inventory injected to the Reactor Coolant System (RCS) as a result of the SI actuation, the pressurizer filled and a primary system safety valve (PSSV) actuated at a lower than expected pressure. All PSSVs are currently closed, however, there is indication of leakage past either a PSSV or Pilot Operated Relief Valve (PORV). Upon alignment of the Charging system to Refueling Water Storage Tank recirculation flow path, 2 valves had indication of packing leakage. Those packing leaks have been terminated. "The cause of the event is under investigation." The licensee has issued a press release. The licensee will notify the NRC Resident Inspector. Notified R1 DO (J. White) and IRD Manager (T. McGinty) * * * UPDATE FROM D. DODSON TO W. GOTT AT 1915 ON 04/17/05 * * * "The previously reported time of the Alert declaration should be corrected to read 08:42. Millstone Unit 3 entered Mode 4 [Hot Shutdown] at approximately 19:03 on April 17, 2005. The event at Millstone Unit 3 was terminated at 19:05. The cause of the event is under investigation. A recovery plan is being formulated." Internal NRC notifications, DHS (Frost), NRC/EPA (Threatt), FEMA (Erwin), DOE (Morone), USDA (Smeltzer), HHS (Desi) The licensee will notify the NRC Resident Inspector. At 23:45 the Agency exited Monitoring Mode and entered into Normal Mode. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | EMERGENCY DECLARED | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | IMode3: Power Operation; FMode3: Hot Standby | ALERT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 0 | 2005-04-17
41606 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-04-15 21:30 | 2005-04-15 22:33 | 2005-04-15 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS - INOPERABLE EMERGENCY DIESEL GENERATOR "Unit 2 Train A emergency diesel generator D5 was removed from service at 0838 CDT on 4/11/05 for surveillance testing and Technical Specification (TS) 3.8.1, 'AC Source - Operating,' Condition B, 'One DG inoperable,' was entered. TS Required Action 3.8.1.B.4 requires D5 be restored to operable status with a Completion Time of 7 days. At 1026 CDT, the test was halted due to high-indicated crankcase pressure on Engine 2 (D5 is a tandem engine generator). The test procedure specifies shutting down the DG if crankcase pressure exceeds 30 mm for more than a few minutes (the setpoint for the crankcase pressure trip is 52 mm). "Investigation of the cause of the high-indicated crankcase pressure on Engine 2 (and whether Engine 1 was effected) started immediately. Unit 2 Train B emergency diesel generator was demonstrated operable by completing a surveillance test at 0423 CDT on 4/12/05. Evaluation of the scope of work to return D5 to operable status and the schedule for completing the work indicated that repairs could not be completed within the 7 days allowed outage time. Based on this assessment an orderly shutdown of Unit 2 is being performed. "Shutdown of Unit 2 commenced at 21:30 CDT on 4/15/05. Unit 2 shutdown will continue until D5 is restored to operable status." The licensee intends to issue a press release. The licensee notified the NRC Resident Inspector. | 0 | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-04-15
41605 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-04-15 07:35 | 2005-04-15 16:32 | 2005-04-15 | FITNESS FOR DUTY A non-licensed employee supervisor tested positive for alcohol during a for-cause fitness for duty test. The employee's access to the plant has been terminated. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2005-04-15
41604 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2005-04-15 08:30 | 2005-04-15 14:09 | 2005-04-15 | FITNESS FOR DUTY A contract supervisor tested positive for alcohol during a for-cause fitness for duty test. The individual's access to the plant was terminated. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IA | POW |  | 26.73 |  |  |  | 0 | 2005-04-15
41603 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-04-12 08:30 | 2005-04-15 12:11 | 2005-04-15 | CALIFORNIA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was provided by the State via facsimile: "On 4/12/05 at about 8:30 am, the RSO [Name Deleted] of Albus-Keefe & Associates, Inc., reported that a Campbell nuclear gauge (Model MC3, S/N M340907583) was stolen from a pickup truck parked at Circle K Store in Lake Elsinore, CA at about 7:00 am. The gauge was in its transportation case, which was chained to the floor of the truck. The chain was cut and the gauge and its transportation case were stolen. According to [the RSO], the local Sheriffs Department was notified. A newspaper ad will be placed as soon as possible offering a reward for the return of the gauge." * * * UPDATE FROM STATE (D. AQUINO) TO M. RIPLEY 1840 EDT 04/15/05 * * * The State received a call from the gauge manufacturer (Campbell-Pacific Nuclear of California) that a citizen brought in the gauge to them and was claiming the reward for its return. The manufacturer stated that the gauge appeared intact and will be performing leak testing and other tests prior to returning the gauge to the licensee. The licensee RSO also contacted the State, confirming that the gauge was in fact the one stolen. Notified R4 DO (R. Nease), NMSS EO (S. Flanders), TAS and Mexico CNSNS (via fax) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-04-20
41602 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-04-15 05:17 | 2005-04-15 10:02 | 2005-04-20 | STEAM GENERATOR BOWL DRAIN LINE WELD LEAK DISCOVERED DURING VISUAL EXAM "During the performance of Alloy 600 bare metal visual examinations, the presence of boric acid deposits indicated a leak in a weld in the steam generator D (EBB01D) bowl drain line. "This condition is being reported as a degraded condition on the primary coolant system under 10 CFR 50.72 (B)(3)(ii)(A). "During investigation the defect was characterized as a 1/16" rounded indication in the drain line to boss weld. "This condition cannot be found acceptable under ASME Section XI, IWB-3600, 'Analytical Evaluation of Flaws' or ASME Section XI, Table IWB-3410-1, 'Acceptable Standards.' "The [NRC] Resident Inspector has been notified." * * * UPDATE FROM S. GIFFORD TO J. KNOKE AT 15:10 EDT ON 04/20/05 * * "On 04/20/05 at 12:10 CDT, during the performance of Alloy 600 Bare Metal Visual Examinations, the presence of boric acid deposits indicated a leak in a weld in the Steam Generator C (EBB01C) bowl drain line." The inspection of Steam Generators A & B showed no presence of boric acid deposits. The licensee notified NRC Resident Inspector. Notified the R4DO (Shannon). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-04-15
41601 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-04-15 04:36 | 2005-04-15 09:26 | 2005-04-15 | REACTOR SCRAM AND SPECIFIED SYSTEM ACTUATIONS "This is both a four hour and eight hour report for the following event: "4 hour Non-Emergency for ECCS Discharge to the RCS and RPS Actuation; "8 hour Non-Emergency for Groups 2 & 6. Also, HPCI [High Pressure Coolant Injection] was placed in pull-to-lock, thereby making HPCI unavailable. "At 0436 [hrs.] CDT 04/15/2005, Cooper Nuclear Station experienced a reactor feed water level transient followed by reactor vessel water level low level alarm and an automatic scram. HPCI and RCIC [Reactor Core Isolation Cooling] automatically initiated and injected into the reactor vessel. Groups 2, 3, and 6 actuated on low reactor water level. Both reactor recirculation pumps tripped and RWCU [Reactor Water Clean-Up system] isolated. Reactor vessel water level reached approximately [minus] 70 inches (instrument zero, approximately 90 inches of water remained above the fuel) and recovered after HPCI and RCIC had begun to inject. All post-scram automatic actions were as expected. HPCI was placed in pull-to-lock to prevent over feeding. The plant is being cooled down to establish natural circulation flow and permit recovery of recirculation pumps. "Investigation into the cause of the reactor feed water level transient is ongoing." All rods inserted during the scram. No safety relief valves lifted during the transient. All group isolation signals have been reset. The electrical grid is stable. Decay heat is being removed via steam dumps to the main condenser. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(D) | 0 | 2005-04-15
41600 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2005-04-14 10:30 | 2005-04-14 17:49 | 2005-04-14 | FITNESS FOR DUTY A contract employee had a positive test result for alcohol during a for-cause test. The employee's access to the plant was terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 87 | 0 | 0 | 87 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 26.73 |  |  |  | 0 | 2005-04-14
41599 | 0 | THERMO ELECTRON CORPORATION |  |  |  |  | 2005-04-07 | 2005-04-14 17:24 | 2005-04-14 | PART 21 NOTIFICATION - THERMO ELECTRON DATA ACQUISITION RECORDERS The following information was provided by the manufacturer via facsimile: On April 7, 2005, Thermo Electron engineers determined that the potential exists that the nuclear safety-related series of paperless data acquisition recorders (SV10C, SV18C and SV28C series recorders) may exhibit failure to start up due to a deficiency in a power supply module. Cycling of power to the recorder may be required to ensure the boot up sequence of the recorder. The power supply module is a commercial grade dedicated item. Thermo Electron has determined that the cause of the anomaly is the rise time variation of the installed commercial power supply module. The module is a generic switching power supply used in a multitude of commercial applications. This module is mounted on a power supply carrier printed circuit assembly (PCA). This anomaly only occurs when a recorder has been turned off and then restarted. Should the recorder fail to boot up, the anomaly can be corrected by cycling power to the recorder until the recorder re-boots. This startup failure may occur on recorder units where the power supply carrier PCA contains a power supply module that does not have a Made in the USA mark. Recorder units that utilize a power supply carrier PCA containing a power supply module labeled with Made in USA do not exhibit the anomaly and are not the subject of this notification. There have been no failures reported in any nuclear safety-related applications of SV10C, SV18C or SV28C recorders. Should the failure occur, it is detectable and will not cause the recorder to present or record any erroneous data. Thermo Electron engineers have redesigned the power supply carrier PCA to accommodate a wider variation in rise times associated with the power supply modules manufactured in the US, China or India as described above. Affected PCA part numbers are CB100492, CB100505, CB100511 and CB100531 which have a power supply module that does not have a Made in USA mark. While there have been no failures reported of recorders in nuclear safety-related applications, as a precaution, Thermo Electron is recommending the replacement of any affected PCA as previously noted with a redesigned PCA for recorders which are used as the primary instrument for recording or reporting critical data and/or functions; are not backed up by a UPS system; and contain the affected PCA. Nuclear utilities that have purchased nuclear safety-related SV10C, SV18C or SV28C recorders potentially affected by this notification (listed individually by Part/Serial Number in the notification): Tennessee Valley Authority - Watts Bar Nuclear Plant First Energy Corporation - Beaver Valley Power Station Duke Energy Corporation - McGuire Site Tennessee Valley Authority - Browns Ferry Nuclear Plant Entergy Operations - River Bend Progress Energy CP&L - Brunswick Nuclear Plant | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2005-04-14
41598 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-04-13 10:45 | 2005-04-14 15:16 | 2005-04-14 | WASHINGTON AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was provided by the State via email: "As reported by the licensee's RSO, the event occurred on 4/13/05, between 9:00am and 10:45am. A CPN Model MC-3, portable moisture/density gauge, serial number M36127293, was stolen from an employee's personal vehicle, parked in the lot of the licensee's office. The car was locked and the gauge was hidden from view beneath the interior hatch cover. However, the gauge was not secured within the car by use of a second, independent security method. The passenger side window was broken; the gauge and a tool box were the only items stolen. The car was apparently parked beside bushes in the parking lot, screening the passenger side of the car from view. The Police (Case Number 051030408), a CPN Representative, and our office were notified soon after the break-in was noticed. "No on-site investigation is planned. No media attention was noted. Isotope and Activity involved: 370 MBq (10 mCi) Cs-137 & 1850 MBq (50 mCi) Am-241/Be" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-04-19
41597 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-04-12 | 2005-04-14 13:48 | 2005-04-14 | WISCONSIN AGREEMENT STATE REPORT - LOSS OF CONTROL OF RADIOACTIVE MATERIAL The following information was provided by the State via facsimile: "Event description: On April 12, 2005, an employee of the St. Vincent de Paul Store in Monroe, Wisconsin dismantled a tritium exit sign thinking it was electrical and requiring repair. Unknown persons had dropped off the exit sign at the store. After dismantling the sign, the individual noticed the 'Caution Radioactive Material' label on the device. The individual wrapped the tubes containing the tritium in aluminum foil, and placed them in a cardboard box inside the facility. The device housing was placed in a scrap recycling bin. The individual initially contacted the NRC Operations Center for assistance. The information was subsequently relayed to the Wisconsin Radiation Protection Section by NRC Region III on April 13, 2005. "The device was identified as an Everglow Safety Sign, Model. 713A, Serial No. 53886 containing 25 curies of tritium in 1987. The device may have been manufactured in New York. "The state investigated on April. 13, 2005. The exit sign tubes were found to be intact. The manufacturer name on the tubes was Self-Powered Lighting, Inc. A local scrap dealer had picked up the device housing with other scrap from St. Vincent de Paul. Staff was unable to locate the device housing but discovered an additional, intact exit sign at a local scrap yard that receives scrap from the dealer. The second exit sign was manufactured by Self-Powered Lighting, Model # 710-A containing 25 curies of tritium. The WI Radiation Protection Section is attempting to locate the owner(s) of these exit signs. The exit sign and tubes have been removed from the public domain. Media attention: None" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-04-19
41596 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2005-04-13 11:00 | 2005-04-13 18:25 | 2005-04-18 | AGREEMENT STATE - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was provided via email from the State of Arizona (State text in quotes): "At approximately 11:00 AM April 13, 2005, the Agency was informed that the Licensee had a pickup truck stolen with a Troxler Model 3401B gauge, SN 10444. The theft occurred between 7:00 PM, 4/12/2005 and 4:00 AM, 4/13/2005. The truck is a green 1995 Nissan. The Troxler gauge was locked in a 16 gauge steel box with a hardened and anti-theft designed lock and hasp. The steel box is bolted to the frame of the truck. The truck license number is Arizona [DELETED]. The gauge contains 8 mCi of Cesium-137 and 40 mCi Am:Be-241. "Phoenix PD is investigating and has issued report number 2005-50689301. "The Licensee is offering a $500.00 reward for the recovery of the truck and sources. A press release is to be made. "The Agency continues to look for the source. "The states of CA, NV, CO, UT, and NM and Mexico and U.S. NRC and FBI are being notified of this event." Arizona State Report ID: 05-03 * * * UPDATE TO NRC (VIA E-MAIL) FROM STATE OF ARIZONA (GODWIN) AT 18:00 EDT ON 4/18/05 * * * "The Phoenix Police Department recovered the truck on April 18, 2005. The gauge does not appear to have been opened. The truck suffered minimal damage." R4DO (Shannon) and NMSS (Flanders) notified. TAS notified via e-mail. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2005-04-18
41595 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-04-13 09:53 | 2005-04-13 18:19 | 2005-04-13 | VALID RPS ACTUATION DUE TO AN INVALID ATWS LOGIC ACTUATION "At 0953 [CDT] on 04/13/2005 with Unit 2 in MODE 4 [and] all Control Rods inserted, a valid RPS Actuation (Reactor SCRAM Signal resulting from the filling of the SCRAM DISCHARGE VOLUME) was received as a result of an invalid ATWS initiation. This occurred during the performance of 2-SR-3.3.5.2.4(FT) RCIC SYSTEM LOGIC FUNCTIONAL TEST. Further review of the test revealed that a Volt/Ohm Meter was attached across contacts in the ATWS LOGIC that conflicted with the RCIC Surveillance and apparently resulted in the ATWS initiation and the filling of the SCRAM DISCHARGE VOLUME. "This event is reportable as an 8-hour Non-Emergency Notification along with a 60-day written report in accordance with 10CFR50.72 (b)(3)(iv)(A) & 10CFR50.73(a)(2)(iv)(A) as 'Any event or condition that results in valid actuation of RPS & PCIS as described in (1) & (2) below.' " The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-04-13
41593 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-04-13 03:50 | 2005-04-13 10:19 | 2005-04-13 | DURING CORE RELOAD REACTOR TRIP BREAKERS OPENED "The plant is in Mode 6 (Refueling) and core reload is in progress with the reactor trip breakers open; both trains of solid state protection system are in the operate mode. "While restoring a line up to place the 'D' steam generator on recirculation, a path was opened that allowed the 'B' steam generator to transfer water to the 'D' steam generator. This alignment lowered the 'B' steam generator to its low-low set point level. This initiated a reactor trip signal (RPS). With the reactor trip breakers open and the reactor core reload in progress, no components actuated as a result of the signal. If the emergency feedwater system had been in service, this would have resulted in equipment actuation. This is an 8-hour report per 10 CFR 50.72 (b)(3)(iv)(A). The resident inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-04-13
41592 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2005-04-09 | 2005-04-12 16:18 | 2005-04-12 | POSSIBLE MEDICAL EVENT The VA National Health Physics Program (master materials licensee) reported a possible medical event at one of its permittees involving a Co-60 teletherapy device. The possible event occurred at the VA North Texas Health Care System, Dallas, Texas, on the dates of April 9 and 10, 2005. "A patient was treated on Saturday and Sunday, April 9 and 10, 2005, for spinal cord compression. The written directive prescribed a dose of 500 cGy in two equal daily fractions. The intent was to give a total dose of about 2900 cGy, with another directive for the remainder of the fractions to be written on April 11, 2005. The treatment time for the fractions on April 9 and 10, 2005, was miscalculated. 330 cGy were administered instead of the prescribed 500 cGy. To avoid too low a dose, an additional fraction of 200 cGy will be given to the patient. This would not have met the definition of a medical event had a single directive, instead of two, been written for the entire treatment series. "No adverse effect to the patient from the event is expected. The permittee has notified the referring physician and patient." The licensee will notify the NRC Region III Project Manager (Kevin Null). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | TX | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-04-12
41591 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-04-08 17:30 | 2005-04-12 09:35 | 2005-04-12 | TWO AMERICIUM-241 SOURCES BEING SHIPPED TO AUSTRALIA WERE REPORTED POTENTIALLY LOST Report # MA050006 "AEA Technology QSA Inc is reporting a potentially lost radioactive material shipment. The shipment contains two Type A packages each containing a 1 Ci AmBe source US model number AMN. PE2. The source serial numbers are 1865NN and 1858NN. "The sources were shipped from AEA Technology on 30 Mar 05 and were designated to leave on a flight to Australia on 2 Apr 05 with arrival scheduled on 5 Apr 2005. AEA was notified on 7 Apr 05 that the shipment had not arrived. The shipment was sent to Surtech Systems Pty Ltd, in Wangara Perth, WA 6055 Australia. "Indication from the airline (Qantas) in New York (JFK) that the packages were on the plane, however the airline in Perth cannot confirm that [they] have the packages. "Discussions with the carrier and freight forwarders indicate that they have so far been unsuccessful in locating the packages. A conference call is currently being arranged between all parties to try and locate the packages." The sources were finally found today (04/12/04) at a Qantas airlines facility in Melbourne, Australia. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-04-15
41590 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-02-19 05:50 | 2005-04-12 08:47 | 2005-04-12 | 60 DAY INVALID ACTUATION OF SYSTEM REPORT. "(A): The specific train(s) and system(s) that were actuated. "This report is being made under 10 CFR 50.73(a)(2)(iv)(A). On February 19, 2005 at 05:50 ET the implementation of a clearance to de-energize the Division 1 24/48 VDC battery chargers were being performed using the system operating procedure. The clearance instructions were misinterpreted and the section of the procedure for de-energizing Division 1 24/48 VDC bus was used. Upon de-energizing the bus, a half scram was received, all 4 Standby Gas Treatment (SBGT) fans auto started and both unit ONE and unit TWO reactor building and refueling floor normal ventilation systems automatically shutdown/isolated. "(b) Whether each train actuation was complete or partial. "The 1/2 scram was a partial initiation of the RPS system logic. No control rods inserted as a result of this event, nor were they required to insert. The RPS logic functioned as expected during the 1/2 RPS trip. "The 4 Standby Gas Treatment (SBGT) fans auto started and both unit ONE and unit TWO reactor building and refueling floor normal ventilation systems automatically shutdown/isolated. THE SBGT initiation and the ventilation system shutdown were both complete actuations. "(C) Whether or not the system started and functioned successfully. "The above systems functioned successfully." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-04-12
41589 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-04-11 16:38 | 2005-04-11 19:59 | 2005-04-11 | OFFSITE NOTIFICATION DUE TO INADVERTENT SINGLE EMERGENCY SIREN ACTIVATION "A single Alert Notification System siren inadvertently sounded. The Clairborne Count Civil Defense Department is issuing a notification to local media advising the public of the inadvertent sounding and that no emergency exists. The siren has been secured. There were no effects on plant operations." The inadvertent siren actuation may have been due to bad weather in the area. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-04-11
41588 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-04-11 16:04 | 2005-04-11 19:11 | 2005-04-12 | LOSS OF PUBLIC PROMPT NOTIFICATION CAPABILITY "At approximately 1604 CDT on 4/11/05, Cooper Nuclear Station (CNS) was informed by Emergency Preparedness officials of Atchison County that the radio transmission tower that provides signals to activate tone alert radios within the 10-mile Emergency Planning Zone (EPZ) was not functioning. Tone alert radio is relied on by approximately 650 households in the EPZ who are not in audible range of sirens for notification of an emergency at CNS. Based on a total EPZ population currently estimated at 4600 persons (who are alerted principally by sirens and the tone alert radio), this is considered to be a major loss of the Public Prompt Notification system capability, and is reportable under 10CFR50.72(b)(3)(xiii). "Investigations are ongoing, a repair technician has been dispatched to the tower. During the interim, compensatory measures have been verified to be in place via state and local emergency planning officials for backup route alerting for personnel within the 10-mile EPZ." NRC Resident Inspector was notified. * * * UPDATED PROVIDED BY LICENSEE (JOBE) TO NRC (HELD) AT 1632 ON 4/12/05 * * * "22:53 on 4/11/05- CNS was notified by the NWS [National Weather Service] that the transmitter had been returned to high power service at 19:35. The cause of the high power transmitter loss was a lightning strike to the transmitter. The strike did not result in any equipment damage, however the transmitter had to be manually reset. "22:55 on 4/11/05- CNS contacted Nemaha and Richardson County Sheriff's Departments and the Atchison County 911 center to notify them that the transmitter/tower had been returned to service. "Operation of equipment was verified. Transmitter tower and tone alert radios have been returned to service." NRC Resident Inspector was notified by the licensee. R4DO (Nease) was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-04-11
41587 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-04-11 12:40 | 2005-04-11 15:39 | 2005-04-13 | MINIMUM SWITCHYARD VOLTAGE REQUIREMENTS NOT MET "At 1240 on April 11, 2005 Quad Cities Station was notified calculated post-LOCA switchyard voltage is below the minimum acceptable value required to ensure offsite power will remain available following a design basis accident. The appropriate Technical Specification Actions have been taken for both Units. The ability of the Emergency Diesel Generators to fulfill their design function is not affected by this condition. This event is being reported in accordance with 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function given the predicted post-LOCA switchyard voltage. "Actual Switchyard voltage at the time of this notification is 361 Kv. The required minimum post-accident switchyard voltage is 348.4 Kv, while the projected post-accident voltage which prompted this notification is 346.3 Kv. "This notification is similar to the condition reported on March 24, 2005 (EN #41524) and April 4, 2005 (EN #41562)." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM C. STEFFES TO M. RIPLEY 1556 EDT 04/13/05 * * * "The purpose of this report is to retract the following ENS reports: 1) ENS # 41524 on March 24, 2005; 2) ENS # 41562 on April 4, 2005; and 3) ENS # 41587 on April 11, 2005. "These reports were made following notification to Quad Cities that the switchyard voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. For each event, both sources of offsite power were declared inoperable, the appropriate Technical Specification required actions were taken for both units, and an ENS notification was made for a condition that could have prevented fulfillment of a safety function. "The events occurred when Unit 1 was in a refueling outage and Unit 2 was operating at 85% power. Subsequent Engineering analysis has determined that with a unit shutdown, and the large 4 Kv loads on that unit not running, the required minimum post-accident switchyard voltage is reduced to 339.3 kV (for the shutdown unit). Given the new minimum post-accident switchyard voltage, it was confirmed that there was a source of off-site power available to the Station. Specifically for all three events, the projected post-accident switchyard voltage (which ranged between 343 kV to 347.5 kV) was higher than the required minimum post-accident switchyard voltage (339.3 kV) for the shutdown unit. As a result, there was no condition present that could have prevented fulfillment of a safety function, and thus these events are not reportable." The licensee notified the NRC Resident Inspector. Notified R3 DO (J. Madera) | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-04-11
41586 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-04-11 09:49 | 2005-04-11 11:03 | 2005-04-11 | POSSIBLE CONTAMINATED INJURED PERSONNEL TRANSPORTED TO HOSPITAL "Individual received laceration to right leg while working in Unit 1 Reactor Building. Individual transported to Oconee Hospital at 0949 with potential contamination. Radiation Protection conducted survey at 1046 in hospital and found no indication of contamination in wounded of individual." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2005-04-11
41585 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-04-10 11:50 | 2005-04-10 12:08 | 2005-04-12 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO FAILED 125V DC BATTERY CHARGER "At 0352 the 2C 125VDC battery charger failed. Fuses internal to the charger were found blown. Technical Specifications require restoration of the charger within 2 hrs or enter Mode 3 within the next 12 hrs and Mode 4 within the next 36 hrs. Investigation has not been able to restore the charger, and therefore the shutdown of the unit has commenced. Loads are currently being carried by the batteries, and personnel are monitoring battery voltage. Initial investigation has not identified any generic issues or any indication of tampering. "This event is a Technical Specification required shutdown, and is reportable as a four hour ENS Notification under 10 CFR 50.72(b)(2)(i). Additionally, this is a voluntary notification due to an anticipated press release associated with the downpower towards unit shutdown." There is evidence of degraded insulation on wires inside the affected battery charger. Battery loads are very small with an initial estimate of battery life at 80 hours. All safety systems are operable. There is no impact on Unit 1. Unit 2 is expected to reach Mode 3 at 1720 on 4/10/05. The NRC Resident Inspector has been notified. State (FEMA) will be notified. * * * UPDATE PROVIDED BY LICENSEE (HUFFORD) TO NRC (HELD) AT 2030 ON 4/10/05 * * * "At 17:28 the plant completed a normal reactor shutdown and entered Mode 3 in accordance with plant procedures to fulfill the requirements of Technical Specification 3.8.4. There were no ECCS initiations and lowest water level was approximately -4 inches." The licensee reported that the 2C battery charger was back in service but remained in the LCO due to battery requirements. They are also completing engineering evaluations for extent of condition. The NRC Resident Inspector was notified. R1DO (Noggle) notified. * * * UPDATE PROVIDED BY LICENSEE (KLINEFELTER) TO NRC (HELD) AT 1710 ON 4/12/05 * * * "At 16:28 on April 12th, 2005 Susquehanna Unit 2 entered Mode 2 (Start-up) following the completion of repairs to the failed 125VDC battery charger and inspection to the remaining 3 Unit 2 125VDC battery chargers. A courtesy call was made [to] the Pennsylvania Emergency Management Agency. An informational press release will be made." The NRC Resident Inspector was notified by the licensee. R1DO (White) was notified. | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-04-10
41584 | -1 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2005-04-10 05:00 | 2005-04-10 11:46 | 2005-05-19 | SCRAM SIGNAL RESULTING FROM FAILURE OF A SUPPLY VALVE TO THE SCRAM AIR HEADER "Nine Mile Point Unit 1 received a valid RPS SCRAM signal from high water level in the SCRAM Dump Volume (SDV). While restoring the Hydraulic Control Rod Unit (HCU) for control rod 02-35 to service, the internals to the plug valve for the Instrument Air Supply (116 Valve) to the SCRAM Inlet and Outlet valves failed. This failure caused an approximate 1/2" hole in the SCRAM Air Header, which resulted in the SCRAM Air Header pressure lowering rapidly due to the leak. "Operators at the HCU recommended isolating the SCRAM Air Header. The Shift Manager was contacted by the job supervisor and received permission to isolate the SCRAM Air Header. SCRAM inlet and outlet valves opened, SDV vents and drains closed due to the loss of SCRAM Air Header pressure. Approximately 3 minutes after SCRAM Air Header depressurization, a full SCRAM signal occurred as expected due to the water level in the SDV. There was no fuel in the Reactor Vessel (RPV). No Control Rod motion occurred due to all Control Rods being inserted or isolated for maintenance. "Immediate (8 Hour Non-Emergency) notification of this event being made as a result of the requirements of 10CRF50.72(b)3(iv)(A)." The licensee stated that more information on the event can be found in Nine Mile Point Internal document DER - NM-2005-1565. The license will be notifying the NRC Resident Inspector. * * * RETRACTION PROVIDED BY LICENSEE (SHEEHAN) TO NRC (HELD) AT 1739 EDT ON 5/19/05 * * * "The scram event that occurred on April 10, 2005 was not initiated from a 'valid' scram initiation signal (i.e., none of the instrumentation signals identified in Technical Specification Table 3.6.2a triggered the scram). To the contrary, a valve on a CRD hydraulic control unit (HCU) failed and Operations took action to isolate instrument air from the scram air header. This operator action had the identical effect that a scram signal would have had - the scram air header completely vented through the broken valve and caused the scram inlet and outlet valves on the HCUs to open and the scram discharge volume vents and drains to close. At the time, the reactor was defueled and all control rods were either already inserted or properly removed from service for maintenance, thus, the event did not result in any control rod movement (i.e., the system had been properly removed from service and the safety function had already been performed). Subsequent to the initiating event, as per the design of the CRD and RPS systems, the scram discharge volume filled and a full RPS scram signal was generated. "Conclusion: The scram event that occurred on April 10, 2005, resulted from an invalid scram initiation signal. At the time, the reactor was defueled, the CRD system had been properly removed from service and the safety function had been properly performed (no control rods moved). Thus, pursuant to the guidance in NUREG-1022, it is appropriate to conclude that the event is not reportable under 10CFR50.72(b)(2)(iv) or 10CFR50.73(a)(2)(iv). As such, the 8-hour ENS notification that was made at 11:46 on 4/10/05 (reference Event Number #41584) is being retracted." The licensee notified the NRC Resident Inspector. R1DO (Bellamy) was contacted. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-04-10
41583 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-04-09 11:11 | 2005-04-09 13:20 | 2005-04-09 | AUTOMATIC REACTOR TRIP ON TURBINE TRIP DUE TO LOW AUTO STOP OIL PRESSURE ON PRESSURE SWITCHES "At 11:11 Unit 1 Turbine Tripped initiating Reactor Trip. Initial Indications are Turbine Trip due to Lo Auto Stop Oil Pressure on 2 pressure switches. Investigating Switch Actuations. "#2 and #4 S/G [Steam Generator] Atmospheric Relief Valves did not control properly and RxOp [Reactor Operator] closed valves with Control Switch. "Current Conditions: U1 [Unit 1] Mode 3, Stm Dumps In Service Normal, RCS temp at 547.4F, Pressure 2238 psig. 2 AFW [Auxiliary Feedwater] trains In Service at Normal Operation. "All Rods Fully Inserted. Yes." The licensee indicated there was not excessive cooldown or depressurization in the steam generators whose atmospheric relief valves had to be manually closed. The NRC Resident Inspector has been notified. * * * UPDATE PROVIDED BY LICENSEE (FIELDS) TO NRC (HELD) ON 4/9/05 ON 1901 * * * "AFW Actuation - due to FW [Feedwater] Isol[ation] tripping both MFPs [Main Feed Pumps] (trips start AFW)" AFW includes 2 motor-driven and 1 turbine-driven pump. R2DO (Rogers) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-04-09
41582 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-04-09 00:50 | 2005-04-09 04:53 | 2005-04-09 | REACTOR SCRAMMED FROM 61% POWER DUE TO LOW REACTOR WATER LEVEL "On 04/09/05 at approximately 00:50 an automatic reactor scram occurred on Brunswick Unit 2. The Reactor Protection System (RPS) actuated on low reactor water level (LL1). All control rods inserted from the RPS signal. The LL1 signal also provided a Group 2 (floor and equipment drain isolation valves), 6 (monitoring and sampling isolation valves) and 8 (shutdown cooling isolation valves) isolation signal for the respective containment Isolation valves. Reactor low level 2 (LL2) resulted in a Reactor Core Isolation Cooling (RCIC) system actuation and injection into the reactor. The High Pressure Coolant Injection (HPCI) system actuated but did not inject because reactor water level recovered. The Reactor Water Cleanup system (RWCU) isolated (Group 3 isolation). Secondary Containment isolated and the Standby Gas Treatment (SBGT) system initiated. An Alternate Rod Insertion signal was received and the Reactor Recirculation Pumps tripped as designed. An investigation is in progress to determine the cause of the reactor level transient. Safety systems and isolations functioned as designed." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 61 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-04-09
41581 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-04-08 19:09 | 2005-04-08 21:13 | 2005-04-08 | OFFSITE NOTIFICATION OF WATER DISCHARGE CONTAINING HYDRAZINE The following information was provided by facsimile (licensee quotes in text): "The licensee made notification to the New Jersey Department of Environmental Protection of a discharge of approximately 5000 gallons of water containing 7 parts per million of hydrazine. [The discharge went] to the Delaware river, via the storm drain system. The water originated from a feedwater system clearance that had an isolation valve leak by. The discharge was terminated at the time of discovery. "There were no personnel injuries as a result of this event." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-04-08
41580 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-04-08 12:35 | 2005-04-08 17:42 | 2005-04-08 | AGREEMENT STATE REPORT OF POTENTIAL MEDICAL MISADMINISTRATION The following information was provided by the State of CA via e-mail (text in quotes): "At 12:35 pm [the] manager of the [Saddleback Memorial Hospital] Imaging Department contacted [the CA Radiological Health Branch] to report a therapy misadministration involving HDR and Ir-192. [The hospital manager] knew few details, other than to report that the source was apparently implanted 8 cm short of its desired location. At this time it is not known how much under treatment there was to the tumor site, nor how much exposure there was to healthy tissue. [It has] not been determined if this is a CA SS&D [Sealed Source and Device]. [The hospital manager] is obtaining this information and will be reporting it back, via fax, as soon as possible. [The CA Radiological Health Branch] has requested narrative as to flow of events. "This form will be updated and forwarded to NRC Ops Center as information comes in." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-04-13
41579 | 0 | LANKENAU HOSPITAL |  |  |  |  | 2005-04-06 | 2005-04-08 17:18 | 2005-04-08 | 10 CFR PART 21 REPORT INVOLVING POTENTIAL DEFECT IN AN HIGH DOSE RATE AFTERLOADING DEVICE Lankenau Hospital reported an incident involving a Nucletron V2 microselectron High Dose Rate Afterloading device. The Hospital reports that a source stuck in a GYN transfer tube during quality operational checks. The source had to be manually retracted with a hand crank back into a safe position. Inspection of the GYN tube revealed a restriction (described as an edge) that developed on the end that connects to the treatment unit. The Hospital report states that the tube had been in use for two years and may have developed the restriction from normal wear and tear. The tube was replaced and the defective tube transferred to Nucletron. The Hospital report notes that normal wire transfer checks (without the source present) did not identify the problem - but probably should have. The Hospital report also stated that the restriction should not have prevent the source from being automatically retracted to its safe location once the emergency stop was actuated. The cause of the GYN tube restriction is unknown. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 21.21 |  |  |  | 0 | 2005-04-08
41578 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-04-08 15:43 | 2005-04-08 16:32 | 2005-04-08 | MAIN STEAMLINE ISOLATION VALVES CLOSED ON VALID SIGNAL The following information was provided by facsimile (licensee quotes in text): "Valid actuation of main steam isolation valves that was not a part of pre-planned testing. Actuation was caused by going above pressurizer high pressure block (1955 psig) with steamline pressure less than 775 psig. Main steam isolation signal was reset. Main steam isolation valves reopened. No plant transient." The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-04-08
41577 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-03-12 10:00 | 2005-04-08 14:30 | 2005-04-08 | OFFSITE NOTIFICATION OF INAPPROPRIATELY MARKED RADIOACTIVE MATERIAL PACKAGES The licensee provided the following information via facsimile (licensee text in quotes): "On March 12, 2005, Turkey Point received two packages from, Nucon International that were inappropriately marked. 49CFR173.422(a) requires that packages containing radioactive material be marked on the outside with the UN number proceeded by the letters 'UN.' The packages had the Radioactive Material marking an the outside of the inner packing. The shipment of the unmarked packages constitute an "Undeclared Hazardous Material" as defined in 49CFR171.8. In accordance with 49CFR171.16(a)4, a 30-day report documenting the event was submitted to DOT on April 8, 2005. "The survey of the two packages confirmed there was no spread of contamination. "This report is being submitted in. accordance with 10CFR50.72(b)(2)(xi) due to offsite notification to DOT of the above incident." The licensee will notify the NRC Resident Inspector. | 100 | 63 | 0 | 100 | 63 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-04-08
41576 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-04-08 08:30 | 2005-04-08 14:07 | 2005-04-08 | POTENTIAL MEDICAL EVENT INVOLVING A THERAPEUTIC ADMINISTRATION OF YTTRIUM-90 The licensee provided the following information via facsimile (licensee text in quotes): "On Friday, April 8, 2005 at approximately 8:30 a.m., the Wisconsin Radiation Protection Section (RPS) received notification from the University of Wisconsin, Madison, WI (license number 25-1323-01) of a potential medical event involving a therapeutic radiation dose from a Yittrium-90 Zevelin treatment in which the delivered dose may have differed from the prescribed dose by more than 0.5 Sv (50 rem) and by 20% or more of the prescribed dose. [HFS 157.72 (1) (a) 1.] "On Tuesday, April 5, 2005, a physician at the University of Wisconsin Hospital and Clinics, Madison, WI administered a 48 mCi dose of Y-90 Zevalin to a patient. Based upon patient weight and platelet count, the intended dose should have been 28 mCi. The dose was dispensed as a unit dose by a nuclear pharmacy and administered as received. There is no indication of a written directive. The error was not discovered until Thursday, April 7 during a licensee review of records. "The licensee is investigating the incident. The ordering physician has been notified "HFS 157.72 (1) (a) 1. requires a licensee to report an event in which the administration of radioactive material or resulting radiation results in 'A dose that differs from the prescribed dose by more than 0.05 Sv (5 rem), 0.5 Sv (50 Rem) to an organ or tissue or 0.5 Sv (50 rem) shallow dose equivalent to the skin and the total dose delivered differs from the prescribed dose by 20% or more'. "DHFS, RPS staff plan to investigate. " | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-04-13
41575 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2005-04-07 20:28 | 2005-04-08 05:32 | 2005-04-24 | POTENTIAL INABILITY TO SAFE SHUTDOWN DUE TO INOPERABLE EMERGENCY DIESEL GENERATORS The following information was provided by the licensee (licensee text in quotes): "All three divisions of Emergency Diesel Generators were declared inoperable due to performing at risk design changes on the operable diesel. The design change was removed from the division one diesel and it was declared available at 2045 on 4/7/05. All three diesels remain inoperable." Perry 1 is currently shutdown in refueling mode 5 and no core alterations are in progress. The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM KEN MEADE TO PETE SNYDER AT 0852 EDT ON 4/24/05 * * * "Update to Event Notification (ENF 41575) Retraction: "An 8-hour notification was made on April 7, 2005 under 10CFR50.72(b)(3)(v) for the loss of the safety function. The report was made due to declaring division 1 diesel generator inoperable at 2028 hours on April 7, 2005 with Division 2 and 3 inoperable for unrelated refuel outage activities. Division 1 diesel generator was declared inoperable as a result of performing an at-risk design change on the exhaust system, i.e., installing insulation blankets on the exhaust piping. The at-risk design change was removed from the division one diesel generator by 2045 hours on April 7, 2005. No other actions were taken during the course of events that would have otherwise rendered the Division 1 diesel generator inoperable. "An evaluation was completed on April 8, 2005 confirming that the additional weight of the insulation on the exhaust piping had no impact on diesel generator operability. Division 1 diesel generator was subsequently declared operable at 0534 hours on April 9, 2005. "Since there was no loss of safety function, there is no reportable condition. Since there was no reportable condition. ENF 41575 is retracted." The licensee has notified the NRC Resident Inspector. Headquarters Operations Officer notified R3DO (Hills). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2005-04-08
41573 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-04-06 16:55 | 2005-04-06 22:56 | 2005-04-06 | PARTIAL LOSS OF OFFSITE POWER RESULTING IN AUTOSTART OF EMERGENCY DIESEL GENERATORS "At 1655 on April 6, 2005, a trip of the 4A/4B Transformer occurred at Limerick Generating Station in the 500 KV Substation. This de-energized one of the required off site sources and the associated 20 Start-up Bus and 201 Safeguard Bus, causing a valid actuation signal for the D12, D14, D21, and D23 Diesel Generators. All Diesels started and their associated 4 KV buses swapped to the 101 Safeguard Bus as required. Cause of the 4A/4B Transformer trip is under investigation. Power reduction on Unit 2 was performed in response to lowering Main Condenser vacuum during power supply transfers. Condition was stabilized and Unit 2 Reactor power restored to 100 %." The cause of the lowering main condenser vacuum was that when the bus transfer occurred, several air valves on Unit 2 cycled which caused the lowering vacuum. Once power transferred, Unit 2 stabilized and was restored to 100% power. Unit 1 main condenser vacuum was not affected since power was not transferred on Unit 1. Additionally, a Group 6A valve isolation signal was generated. This caused the purge valves to receive an isolation signal but the purge valves were not in operation nor were they required to be in operation at the time of the isolation signal. Both unit's Reactor Water Clean-up (RWCU) pumps tripped due to the isolation signal. At the time of this report, the isolation signal was reset, Unit 1 RWCU pump has been reset, and preparations are being made to restart Unit 2 RWCU pump. The only other anomaly is that Unit 2 D22 diesel is in a maintenance outage and is scheduled to be returned to service tomorrow. Currently, both units are in a 72-hour LCO action statement due to loss of one offsite power supply. The licensee will inform the NRC resident inspector. | 100 | 95 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-04-06
41572 | 0 | UNIVERSITY OF VIRGINIA |  |  |  |  | 2005-04-06 | 2005-04-06 16:59 | 2005-04-07 | MEDICAL EVENT INVOLVING ADMINISTRATION OF WRONG DIAGNOSTIC TEST On the morning of 4/6, the Resident Physician reviewed the prescribing Physician's order for administration of a brain scan diagnostic test to image a tumor and instructed the technician to perform a "standard" brain scan which images blood flow. The Technician administered 30 mCi Tc-99m as instructed rather than the 3 mCi Thallium prescribed. The RSO noted that the test performed would result in a total dose of 3.22 mGy and a urinary bladder wall dose of 81 mGy (information from package insert). The RSO does not believe there will be any adverse consequences to the patient in that this was a diagnostic test. The error was identified by the Director of Nuclear Medicine during review. The patient had not been informed as of the time of this report. The patient will be rescheduled for the appropriate diagnostic test after elimination and decay of the Tc-99m. * * * UPDATE FROM LICENSEE (STEVA) TO NRC (HUFFMAN) AT 1251 EDT ON 4/07/05 * * * The license stated that the patient involved was a 66 year old female. The licensee does not consider that this event meets the criteria of a medical event. R1DO (Noggle) and NMSS (Essig) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2005-04-06
41571 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-04-06 07:00 | 2005-04-06 16:50 | 2007-07-09 | AGREEMENT STATE REPORT INVOLVING THEFT OF A TROXLER PORTABLE GAUGE The following information was received via fax: "On 4/6/2005, Linda McLean (NRC) notified Texas DSHS at 10:30 am that their regional office had just received a phone call from the White Settlement, TX Police Department. The police department had been notified of a burglary between 5:00 am and 7:00 am on the morning of April 6, 2005 involving a stolen Troxler (model 3411B) portable gauge containing 10 mCi of Cs-137, serial number 40-9599, and 40 mCi of Am-241, serial number 47-7075. Serial Number for the gauge is 11979. [The authorized user] contacted the police department that he had stopped by his girlfriend's apartment at 5:00 am. When he went outside at 7:00 am, the passenger window had been broken out of his pickup truck and the portable gauge he was planning on using for work had been removed. He stated his radio had been stolen two weeks earlier at the same address. Police report number is 0506384." Texas Incident No.: I-8227 *** UPDATE FROM RATLIFF TO KNOKE AT 1347 EDT ON 07/09/07 *** The licensee provided the following information via email: "On April 6, 2005, the Agency received a phone call from the Nuclear Regulator Commission (NRC) informing them of a reported theft of a moisture density gauge containing one 7.8 millicurie Cesium-137 source and a 40 millicurie Americium source. The NRC had received a notification of the theft from the White Settlement Police Department. The technician had taken the gauge home with him so he could get an early start the next morning. The passenger's window was broke out of the pickup and the gauge was stolen. The gauge was removed from the transport case in the bed of the pickup and had been placed in the cab of the vehicle to protect it from theft. The local police were contacted and a police report was filed. The gauge was not recovered. The technician was placed on ninety day probation and a letter stating the company's policy on returning the gauges to the laboratory prior to going home each night. The licensee was issued two violations for failure to adequately secure the sources from unauthorized removal and failure of the Radiation Safety Office to insure compliance with company procedures. File closed." Notified R4DO (Nease), CNSNS (Email), ILTAB (Whitney), FSME (Joe Giitter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-04-11
41570 | 0 | NATIONAL INSTITUTES OF HEALTH |  |  |  |  | 2005-03-10 | 2005-04-06 16:04 | 2005-04-06 | SOURCE VIAL OF GADOLINIUM-153 REPORTED MISSING The following information was obtained from the licensee via facsimile (licensee text in quotes): "This notification to the NRC Operations Center is in accordance with 10 CFR 20.2201(a)(ii) regarding the incident described below: "On 3/10/05, we determined that 245 [microCurie] (9.1 MBq) of [Gd-153] (0.5N HCI) in a source vial was missing. The original activity was 1 [milliCurie] (37 MBq) on 4/12/2004, and the missing quantity, corrected for radioactive decay, represented the remaining activity after several labeling experiments. "Following this discovery, the Authorized User interviewed all researchers who had access to her laboratory. None recalled disposing of the vial. In addition, a health physicist contacted a number of the researchers and performed an independent survey of this and adjacent laboratories with a photon-sensitive survey meter. The original lead pig was found in a box where other lead pigs were stored awaiting disposal. However, the source vial was not in the lead pig. In addition to searching the laboratory areas, we checked the records of both radioactive waste pick ups and other monitored waste from the building in which this laboratory is located. There was no indication of [Gd-153] in any of the records or surveys. "At this time, the disposition of the material is unknown. Considering that the exposure rate for an unshielded point source of 245 [microCuries] of [Gd-153] is only 0.04 mR/hr, the missing material would not represent a significant external exposure risk. The approximately 69 nanograms of material missing would not represent a significant toxic hazard either. "Corrective actions have been implemented by suspending the Authorized User's ability to order more radioactive material. With her pending departure from NIH, we do not feel any further actions will be warranted in this situation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-04-06
41568 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2005-04-06 10:06 | 2005-04-06 13:54 | 2005-04-08 | MAJOR LOSS OF COMMUNICATIONS CAPABILITY DUE TO OFFSITE FIBER OPTIC CABLE CUT "On 4/6 at approximately 0900 Emergency Planning (EP) was notified by Arkansas Department of Health that they had lost communications with their Communications Center in Little Rock and asked ANO to perform tests to validate. "Pope County 911 advised EP that there had been a major fiber optics cut east of Russellville. The NRC Resident also notified EP that their contact with Arlington and headquarters was out including commercial lines. Subsequent investigations revealed that ERDS, ENS, and Health Physics Network (HPN) lines are not functioning at ANO. Backup methods of communications are defined in the Emergency Plan procedures and are available. "Establishment of communications are ongoing." The licensee informed the State and NRC Resident Inspector. * * * UPDATE FROM LICENSEE (HARRIS) TO NRC (HUFFMAN) AT 1507 EDT ON 4/8/05 * * * The licensee reports that the fiber optic cut had been repaired and all phone circuits returned to operable status by 1618 CST on 4/6/05. The licensee has notified the NRC Resident Inspector. R4DO (Howell) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-04-06
41567 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-04-05 16:00 | 2005-04-05 22:26 | 2005-04-05 | POTENTIAL VULNERABILITY WITH ALTERNATE SHUTDOWN SYSTEM (ASDS) ISOLATION DESIGN The following information was obtained from the licensee via facsimile (licensee text in quotes): "On April 5, 2005 at 1600 [hrs. CDT], Monticello Nuclear Generating Plant during a review of the Alternate Shutdown System (ASDS) as part of the corrective actions for LER 2005-01, submitted on April 4, 2005 (Event Notification #41436) discovered a second breaker affected by a similar cause as identified in the LER. The Bus 16 source (Breaker 152-609) to Load Center #104 has a similar potential vulnerability with the ASDS isolation design that could result in Load Center #104 being locked out in the event of a Control Room or Cable Spreading Room fire. The Monticello Appendix R Safe Shutdown Analysis for Control Room/Cable Spreading [Room] fire assumes a loss of control of Division I and II equipment from the Control room, however safe shutdown is achieved remotely from the ASDS panel. ASDS design is such that a Control Room/Cable Spreading Room fire would not impede the ability to safely shutdown and maintain the plant in a shutdown condition. "Contrary to the ASDS design, it was discovered that an unisolated metering circuit could result in Load Center #104 being locked out in the event of a Control Room/Cable Spreading Room fire. The bus lockout is not isolated by the ASDS transfer switches, therefore, this condition could result in failure of Load Center #104 to re-energize during the implementation of the Shutdown Outside Control Room procedure. ASDS is not required to be operable at this time. "As a result of this determination, MNGP will issue a revision to LER 2005-01 to the NRC to reflect the new information. "This event is being reported as a potential loss of safety function (10CFR50.72(b)(3)(v)(A,B, and D) and as a degraded or unanalyzed condition (10CFR50.72(b)(3)(ii)(B). The NRC [Resident Inspector] has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2005-04-05
41565 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-04-05 16:12 | 2005-04-05 19:59 | 2005-04-05 | UNUSUAL EVENT DECLARED UNDER E.A.L. 9-3.U.1 The following information was obtained from the licensee via facsimile (licensee text in quotes): "Columbia Generating Station has declared an unusual event ([EAL] 9-3.U.1) due to an unintentional vehicle crash into the Radwaste Building (Safe-Shutdown Bldg) roll-up door during the normal course of plant activities. Damage to the door has prevented normal closure of the door. Efforts to close the door are on-going. "Terminated the event @ 1655 [PDT] due to determination that an unusual event did not exist." A plant employee was using a plant-owned vehicle to move a sea-land container into the Radwaste Building when he struck the bottom of the roll-up door. There were no injuries to plant personnel and no other damage to plant equipment. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM PAM ANKRUM TO HOWIE CROUCH @ 2133 EDT ON 4/5/05 * * * The following retraction was obtained from the licensee via facsimile (licensee text in quotes): "At 1912 EDT on April 5, 2005, NRC was notified of an Unusual Event at Columbia Generating Station (EN #41565). This notification also informed the NRC that the event was terminated at 1955 EDT (1655 PDT) on April 5, 2005. "This is a follow-up to inform the NRC that Columbia Generating Station is retracting its Unusual Event Declaration due to the following reason. Columbia Generating Station Procedure 13.1.1A requires entry into Unusual Event EAL 9.3.U.1 if 'the impact is of such force that damage to structures or equipment inside a Safe Shutdown Building may have occurred.' Upon further evaluation, the impact was not of sufficient force to have caused damage to structures or equipment inside a Safe Shutdown Building. Based on this information, the Unusual Event criteria was not met. "The licensee notified the NRC Resident Inspector and local, State, and other Government Agencies of this update." Notified IRD (Kennedy), R4DO (Howell), NRR EO (Lyons), FEMA (Liggett) and DHS (Frost) and HQPAO (Brenner). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | WA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-04-05
41564 | 0 | DAVID BLACKMORE AND ASSOCIATES |  |  |  |  | 2005-04-05 11:00 | 2005-04-05 15:25 | 2005-04-05 | DAMAGED MOISTURE DENSITY GAGE DURING CONSTRUCTION During construction at the Providence Regency residential construction site in Lower Providence Township, a CPN MCMDR moisture density gage was damaged when run over by a bulldozer. The gage was a model MC3, Serial number 300405564, containing 10 millicuries of Cs-137 and 50 millicuries of Am-241: Be. The external case of the gage was damaged and the rod snapped off. The radioactive sources were intact and stored in the locked position of the gage and not damaged. No leakage was detected. The gage will be shipped to the manufacturer for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN | 30.50(b)(2) |  |  |  | 0 | 2005-04-05
41563 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-04-04 20:36 | 2005-04-05 14:00 | 2005-04-05 | FITNESS FOR DUTY REPORT A non-licensed contract supervisor was determined to be under the influence of alcohol during for-cause testing. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NH | POW |  | 26.73 |  |  |  | 0 | 2005-04-05
41562 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-04-04 16:07 | 2005-04-04 19:51 | 2005-04-13 | MINIMUM SWITCHYARD VOLTAGE REQUIREMENTS NOT MET The following information was obtained from the licensee via facsimile (licensee text in quotes): "On April 4, 2005, at 1607 hours [CDT], Quad Cities was notified that the switchyard voltage was below that required to ensure that offsite power would remain available following a design basis accident. Both sources of off site power were declared inoperable. The appropriate Technical Specification required actions were taken for both units. The ability of the Emergency Diesel Generators to perform their design function is not affected by this condition. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function given the predicted post-LOCA switchyard voltage. "This notification report is similar to the condition reported on March 24, 2005 (reference EN#41524 for additional information)." Technical Specification minimum switchyard voltage is 348.4 KV. Switchyard voltage at 1607 hrs. was approximately 343.7 KV. Switchyard voltage at the time of NRC notification was 358 KV which is above the Technical Specification minimum. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM C. STEFFES TO M. RIPLEY 1556 EDT 04/13/05 * * * "The purpose of this report is to retract the following ENS reports: 1) ENS # 41524 on March 24, 2005; 2) ENS # 41562 on April 4, 2005; and 3) ENS # 41587 on April 11, 2005. "These reports were made following notification to Quad Cities that the switchyard voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. For each event, both sources of offsite power were declared inoperable, the appropriate Technical Specification required actions were taken for both units, and an ENS notification was made for a condition that could have prevented fulfillment of a safety function. "The events occurred when Unit 1 was in a refueling outage and Unit 2 was operating at 85% power. Subsequent Engineering analysis has determined that with a unit shutdown, and the large 4 Kv loads on that unit not running, the required minimum post-accident switchyard voltage is reduced to 339.3 kV (for the shutdown unit). Given the new minimum post-accident switchyard voltage, it was confirmed that there was a source of off-site power available to the Station. Specifically for all three events, the projected post-accident switchyard voltage (which ranged between 343 kV to 347.5 kV) was higher than the required minimum post-accident switchyard voltage (339.3 kV) for the shutdown unit. As a result, there was no condition present that could have prevented fulfillment of a safety function, and thus these events are not reportable." The licensee notified the NRC Resident Inspector. Notified R3 DO (J. Madera) | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-04-04
41561 | 0 | LANCASTER GENERAL HOSPITAL |  |  |  |  | 2003-09-30 | 2005-04-04 15:01 | 2005-04-07 | MEDICAL EVENT NOTIFICATION In September, 2003, a patient at Lancaster General Hospital's Health Campus was undergoing Co-60 gamma knife treatment. In preparation for the treatment, the patient was immobilized to ensure that the gamma knife was accurately aimed at the treatment site. During the treatment, the patient became uncomfortable and asked to move. He was told to move only his legs, but he shifted his body. As a result, the patient shifted 7cm away from the gamma knife. Licensee was unable to calculate dose to unintended site. There were no adverse effects to the patient. * * * UPDATE FROM LICENSEE (MONTAGNES) TO NRC (HUFFMAN) AT 1048 EDT ON 4/07/05 * * * The following additional details were provided on the event. The licensee also is reporting this as a 10 CRF Part 21 report. The Licensee reported an incident involving component of a Leksell Model 23004 Type B Gamma Knife unit (Elekta AB, Stockholm, Sweden). The specific components involved are the "z-bars". During the treatment with this device, a patient's head is secured into a head frame in preparation for irradiation treatment of deep head disease. This head frame is then also secured to a helmet and couch assembly to ensure immobilization during treatment. In, order to localize the therapeutic radiation beam to a precise location, the frame is able to be adjusted in the X, Y, or Z directions. In the "Z" direction, there are metal bars that are adjusted to a desired position, then locked into place by the treatment staff with a number of screens. During the case which lead to the incident, a large patient is believed to have made an exaggerated movement during treatment, against staff instructions, as a means of alleviating some discomfort. At the conclusion of the treatment, the staff noted that the patient's position - as indicated by the z-bars - had slipped caudally by approximately 7 cm. The incident occurred on September 30, 2003 in the Lancaster General Gamma Knife Center, 2102 Harrisburg Pike, Lancaster, Pennsylvania, 17603. Although this original incident occurred on September 30, 2003, this report is only being filed now as a result of an investigation by the NRC that concluded on April 5, 2005. R1DO (Noggle) and NMSS (Essig) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PATIENT INTERVENTION DAMAGE | UNSPECIFIED PARAGRAPH | [8 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(b) | 21.21 |  |  | 0 | 2005-04-04
41560 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2005-02-07 07:56 | 2005-04-04 13:19 | 2005-04-04 | INVALID SPECIFIED SYSTEM ACTUATION The following information was obtained from the licensee via facsimile (licensee text in quotes): "This telephone notification is provided in accordance with 10 CFR 50.73(a)(1), to report an invalid actuation reportable under 10 CFR 50.73(a)(2)(iv)(A). "On February 7, 2005, at 0756 [CST], with Unit 2 in Mode 3 'Hot Shutdown' in preparation for the 2005 refueling outage, the 2A Reactor Protection System (RPS) bus unexpectedly de-energized during performance of LOS-RP-W1, 'Manual Scram Instrumentation.' As a result, an RPS Bus A half scram and Division 1 Primary Containment Isolation System (PCIS) isolations were received, including the isolation of shutdown cooling. All affected containment isolation valves closed as designed. "An inspection found that the 2A RPS MG set output breaker had opened. RPS Bus A was transferred to its alternate feed, and the associated containment isolations were reset. Shutdown cooling was restored at 0845 hours on February 7, 2005. "Troubleshooting found that the 2A RPS MG set voltage regulator had failed. The voltage regulator was replaced and successfully tested, and the 2A RPS MG set was returned to service. Laboratory testing of the failed voltage regulator circuit board found that a solder joint had failed on load-dropping resistor R8, which caused the excitation output voltage to decrease sharply. This resulted in a trip of the 2A RPS MG set output breaker on low voltage. "The apparent cause of the failed solder joint was a manufacturing defect. Corrective actions include visual inspections of RPS MG set voltage regulatory circuit boards in the field and in the storeroom, and the development of enhanced receipt inspection requirements. "This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an invalid actuation of containment isolation valves in more than one system." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-04-04
41558 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2005-04-01 14:02 | 2005-04-01 16:30 | 2005-04-01 | EMERGENCY DIESEL GENERATOR START DUE TO A PARTIAL LOSS OF OFFSITE POWER The following information was provided by the licensee via fax (licensee text in quotes): "With the plant in mode 6 and refueling operations in progress, a loss of offsite power circuit 751 occurred. This loss of power caused an undervoltage condition on safeguards busses 16 and 17 and an automatic start of Emergency Diesel Generator 1B. Both of these busses were subsequently energized by the diesel. Refueling operations in progress were immediately halted. Core cooling was momentarily interrupted and restored upon safeguards bus reenergization. The spent fuel pool cooling loop in operation was powered from the opposite train and hence was not interrupted. RCS temperature was maintained at 74 degrees Fahrenheit and spent fuel pool temperature was also at 74 degrees Fahrenheit throughout the event." This partial loss of power was due to a substation transformer fault (one of two offsite power sources were lost). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-04-01
41557 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2005-03-30 | 2005-04-01 13:56 | 2005-04-08 | AGREEMENT STATE - LOST Am-241 SOURCE An Am-241 sealed source (Serial #: NM-129 received in January 1978) was last inventoried in February 2005. On the afternoon of March 30, 2005, it was concluded that a wand marker containing 2 mCi of Am-241 was missing. The marker had not been in use and was secured "in storage" in the Nuclear Medicine Hot Lab at the Miriam Hospital. Initially the source was considered to be misplaced. However, on March 30, 2005, the hospital's preliminary investigations had not recovered the source and it was reported as lost. The source is identified as an Am-241 (2mCi) wand formerly used as a marker for an ELCINT camera. The source is in a steel wand and is shielded until a window is opened when used as a marker. It was described as a steel rod with wires out the back end approximately 8 inches long and approximately 0.75 inches in diameter. The Rhode Island RCA was notified of the incident on March 30, 2005 via a voice message and retrieved by RCA personnel on April 1, 2005 after returning from training out of state. The licensee is continuing a search of each campus in an attempt to retrieve or account for the source. Event Report ID: RI-05-002 * * * UPDATE 1358 EDT ON 4/8/05 FROM JACK FERRUOLO TO PETE SNYDER VIA FAX * * * "Investigation conducted on 1 April 05 at RI Hospital Campus of licensee with follow-up at Miriam Campus on 5 April 2006. Findings: Inventory records supported inventory and accountability of source on 11/29/04. Inventory record for 2/16/05 identified the Am-241 source as missing. Notification of RI RCA was not effected until 30 March 05. The source is as described above with the following clarifications: It has a wooden handle at one end-total length of wand increased to approx. 12 inches. A radiation symbol was embossed on the metal portion of the wand, however, the wand was typically placed in a scabbard thus concealing the radiation warning. The Hot tab was confirmed to be locked - key code locking mechanism. The source was stored in a separate waste storage location accessible only from the Hot Lab. All areas in the storage location were checked and the source was not recovered, it is presumed lost and not retrievable. Licensee has scheduled in service with all Nuclear medicine and physics staff to review protocols and to investigate further." Notified R1DO (Noggle) and NMSS (Leach) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2005-04-06
41556 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-02-21 18:55 | 2005-03-31 16:33 | 2005-03-31 | AGREEMENT STATE - RADIOGRAPHIC SOURCE PARTIALLY DISCONNECTED FROM CAMERA The following information was provided via E-mail by the Texas Department of State Health Services (DSHS) (state text in quotes): "On February 21,2005 at the Motiva Enterprise facility located in Port Arthur, Texas an event took place that prevented the return of a radiography source to the shielded position via normal operations. The unauthorized retrieval of the source was done without proper license condition authorization. All dosimeters have been processed and no overexposures have occurred as a result of the retrieval. Additionally, a verbal notification was made to DSHS, and followed by written report received 03/21/05. "The Operating and Emergency procedures to be employed in an incident of this type were reviewed for full understanding by all staff involved in Radiographic operations." The source was Ir-192 (150 Ci) from a SPEC Model G-60; AEA Model 969. Texas Incident # I-8224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-04-05
41555 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-02-14 07:18 | 2005-03-31 14:29 | 2005-03-31 | INADVERTANT SAFETY SYSTEM ACTUATION DURING MAINTENANCE The following information was provided by the licensee via fax (licensee text in quotes): "At 0718 on February 14, 2005, with the James A. FitzPatrick Nuclear Power Plant operating at 100% reactor power, the High Voltage Power Supply (HVPS) for Reactor Building (RB) Radiation Monitor 17RM-452A was inadvertently de-energized. "At 0724 the HVPS was re-energized and the technician began to adjust the output of the high voltage power supply. This adjustment resulted in an unanticipated voltage spike in the radiation monitor circuit. The voltage spike caused the radiation monitor to see a false Hi-Hi signal resulting in an actuation of the RB ventilation system isolation logic, start-up of the 'A' Standby Gas Treatment (SBGT) System, and a Half PCIS Group II Isolation. AOP-15, Isolation Verification and Recovery, was entered and at 0728 an 'A' train Group II PCIS Isolation was verified for that Channel. "At 0750 AOP-15 was exited and plant systems were restored from the Half Group II PCIS Isolation. "The reactor remained at 100% power throughout the event, and short-term LCOs were entered for equipment isolated as a result of the isolation, as applicable. While the Hi-Hi signal was falsely generated by the voltage spike encountered when re-energizing the HVPS the actuation logic functioned properly and the plant equipment responded as designed. There were no equipment failures associated with this event and neither plant operation nor the health and safety of the public were affected by this event. "The condition meets the reporting criteria of 10 CFR 50.73 (a)(2)(iv)(a) because the invalid RB Radiation Monitor Hi - Hi signal resulted in a general containment isolation signal affecting containment isolation valves in more than one system ('A' SBGT, 'A' H2/02 Exosensors, 'A' Drywell Cam, 'A' Containment Atmosphere Dilution (CAD), 'A' PCP Vent and Purge). Since the signal was invalid this event meets the criteria in 10 CFR 50.73 (a)(1) for being reported as a 60-day phone call rather than as an LER. "The event has been entered into the corrective action program and the resident inspector has been briefed. "The apparent cause evaluation identified 1) a failure on the part of the technicians to plan for or provide a barrier to prevent the inadvertent actuation of the HVPS switch resulting in the initial deenergization of the radiation monitor circuit and then 2) failure to recognize that the restoration of the HVPS switch after inadvertent actuation should have been accomplished by entering the site work process and obtaining a work order which would have allowed for proper review and incorporation of barriers to minimize the probability of inadvertent isolations." The licensee notified the NRC Resident Inspector and the State. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-03-31
41554 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-01-18 | 2005-03-31 16:21 | 2005-03-31 | AGREEMENT STATE - OVEREXPOSURE The following information was provided by the Texas Department of State Health Services via E-mail (state text in quotes): "Radiography was conducted at both field and fixed locations during the December [2004] monitoring period. The badge of [the radiographer trainee] was the only high badge for the Licensee during the monitoring period. The Radiography Trainer claims that his pocket dosimeter and alarming rate meter showed no unusual activity during the monitoring period. All exposure devices were leak tested December 30, 2004, with no leakage in excess of applicable limits being exceeded - no leakage. The Radiographer Trainer was on two crews during the monitoring period. Both other crew members had normal exposures for the monitoring period. No explanation for a possible source of exposure to the badge was offered by the Licensee or the wearer of the badge. The Licensee was cited for violating the Deep dose annual exposure limits for calendar year 2004." The trainee was seen by a physician however, the blood work results are not yet available. As corrective action, the licensee has notified all radiographers to carefully monitor their pocket dosimeters and alarming rate meters, and to keep their personal monitoring badges away from sources of radiation. The four cameras used contained Ir-192 (72.4 Ci, 81.5 Ci, 34.1 Ci, and 39.4 Ci). Total dose received by the radiographer trainee was 11.885 REM DDE for December 2004 and 12.771 REM DDE for the annual monitoring period. Texas Incident # I-8199. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-04-05
41552 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-03-30 15:30 | 2005-03-31 13:00 | 2005-03-31 | TWO CONTRACT SUPERVISORS TESTED POSITIVE DURING A RANDOM DRUG TEST Two contract supervisors had a positive test during a random drug sampling. Both supervisors have had their plant access terminated and were escorted offsite. A review of the work performed by both individuals is in progress. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 60 | 0 | 100 | 60 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2005-03-31
41551 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-03-30 16:00 | 2005-03-30 18:13 | 2005-03-30 | IDENTIFICATION OF DESIGN AND OPERATING PROCEDURE DEFICIENCIES The following information was provided by the licensee (licensee text in quotes): "On March 7, 2005, a condition assessment and resolution document was initiated to document several possible design and operating procedure deficiencies affecting Appendix R and Station Blackout (SBO) events. The deficiencies were identified during development of a proposed modification affecting existing Appendix R and SBO power supplies. On March 30, 2005, it was determined that the applicable Appendix R success criteria could not be assured under all of the postulated scenarios described in the Updated Final Safety Analysis Report (UFSAR). Specifically, during the scenarios where Combustion Turbine Generator (CTG) 11-1 (the dedicated Appendix R alternate power source) or other station CTGs are operating in parallel with the grid, availability of the alternate power source under Appendix R and SBO scenarios cannot be assured. Therefore, this event is being reported under 50.72(b)(3)(ii)(B). Actions to address the potentially affected Appendix R and SBO scenarios were put in place on March 7, 2005, when the deficiencies were identified. The NRC Resident Inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-03-30
41550 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2005-03-30 16:35 | 2005-03-30 17:57 | 2005-03-30 | OFFSITE NOTIFICATION DUE TO DISCOVERY OF LEGACY OIL SPILL During demolition of the auxiliary building, a 3 cubic yard front end loader picked up a load of dirt which was discolored and had a strong smell of diesel fuel oil. Excavation was suspended for investigation. At this time the extent of the contaminated area is unknown as well as the potential for ground water contamination. The licensee notified the National Response Center (Report # 754298) as well as the Connecticut Department of Environmental Protection. The licensee will notify NRC Region I. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-30
41549 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-30 09:00 | 2005-03-30 14:43 | 2005-03-30 | FITNESS FOR DUTY REPORT - UNDER INFLUENCE OF ALCOHOL A non-licensed employee was determined to be under the influence of alcohol during a new employee pre-screening evaluation. The employee never had access to the plant. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2005-03-30
41548 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-03-30 07:35 | 2005-03-30 09:35 | 2005-03-30 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO CONTAINMENT FAN COIL UNITS DECLARED INOPERABLE The following information was obtained from the licensee via facsimile (licensee text in quotes): "The site determined that previous repairs to 21, 22, and 23 Containment Fan Coil Unit (CFCU) Heat Exchangers were not in compliance with applicable ASME codes. The three CFCUs were declared inoperable per Generic Letter 90-05 for ASME Class II Piping. Shutdown of Unit 2 to Mode 3 commenced at 0735. Code repairs are being performed and the technical specification required shutdown (LCO 3.0.3/3.6.1.B) is expected to be stopped once one CFCU train is returned to operability and the other is isolated to meet technical specification LCO 3.6.1. 'Containment.'" The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-03-30
41547 | 0 | GENERAL ELECTRIC NUCLEAR ENERGY |  |  |  |  | 2005-01-28 | 2005-03-29 19:17 | 2005-03-29 | PART 21 REPORT INVOLVING POTENTIAL TO EXCEED LOW PRESSURE TECHNICAL SPECIFICATION SAFETY LIMIT The following is a portion of a facsimile submitted by GE Energy-Nuclear: "The defect is a calculation of an anticipated operational occurrence (AOO), which predicts that the Pressure Regulator Failure Maximum Demand (Open) (PRFO) transient will be terminated by a high water level trip as a result of level swell in the reactor. An improved (and approved) model predicts that MSIV closure will occur when steam line pressure reaches the low-pressure isolation setpoint (LPIS), rather than terminate due to a high water level trip. Depending upon the plant-specific response to a PRFO, including the value of the LPIS, reactor steam dome pressure could decrease to below 785 psig while thermal power exceeds 25% of rated, which would be a violation of SL 2.1.1.1. This constitutes a Defect as defined in 10 CFR 21.3, even though there is no safety hazard created. SL 2.1.1.1 was intended to protect fuel cladding integrity during startup conditions without the need to perform a Critical Power Ratio (CPR) calculation. The AOO of concern is a transient from normal operating conditions that causes CPR to increase, so the event produces additional margin to the Minimum Critical Power Ratio Safety Limit (SLMCPR) and does not threaten fuel cladding integrity. The LPIS should not be considered as a Limiting Safety System Setting (LSSS) for SL 2.1.1.1 since it does not provide a 'significant safety function' with regard to protecting fuel cladding integrity. This indicates that SL 2.1.1.1 is overly conservative because an event that causes CPR to increase and does not threaten fuel cladding integrity, may result in exceeding a reactor core SL." Notified Plants: AFFECTED: Nine Mile Point 2, Fermi 2, Pilgrim, Vermont Yankee, Limerick 1 & 2, Peach Bottom 2 & 3, Perry 1, and Hope Creek. POTENTIALLY AFFECTED: Clinton, Oyster Creek, Brunswick 1 & 2, Nine Mile Point 1, FitzPatrick, Grand Gulf, River Bend, Dresden 2 & 3, LaSalle 1 & 2, Quad Cities 1 & 2, Cooper, Duane Arnold, Monticello, Hatch 1 & 2, Browns Ferry 1, 2 & 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2005-03-29
41546 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-03-29 10:57 | 2005-03-29 19:07 | 2005-03-29 | ACTUATION OF THE REACTOR PROTECTION SYSTEM AND AUXILIARY FEEDWATER SYSTEM WHILE ESTABLISHING INITIAL CONDITIONS FOR LEAK TEST IN MODE 3. The licensee faxed the following information: "On 3/29/05, with the Callaway plant at 0 % power in Mode 3, Steam Generator (S/G) levels were being maintained using 'B' Condensate Pump. Reactor Coolant System (RCS) temperature was being controlled using Condenser Steam Dumps. Preparation was in progress for performance of a leak test on Main Feedwater Isolation Valve AEFV0041. As part of the leak test, condensate flow was temporarily isolated to 'C' S/G and the Auxiliary Feedwater System was aligned to provide water to the 'C' S/G. When low was initiated to 'C' S/G using auxiliary Feedwater, level initially increased due to the injection of a small volume of warm water contained within the Feedwater piping at the S/G, then proceeded to rapidly decrease due to S/G shrink caused by the injection of Auxiliary Feedwater with a temperature of approximately 70 degree F. Level in 'C' S/G decreased until S/G Lo Lo Level reactor trip and Auxiliary Feedwater Actuation signals were generated. Performance of the leak test was terminated and RCS temperature and S/G levels were stabilized at normal parameters for Mode 3." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-03-29
41543 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-03-29 14:00 | 2005-03-29 15:24 | 2005-03-29 | 24 - HR CONDITION OF LICENSE REPORT DUE TO T.S. NOT MET The licensee provided the following information: "On March 29, 2005, Seabrook determined that the requirements of T.S. 3.8.1.1 were not met when the Reserve Auxiliary Transformer (RAT), AC supply to the Bus E5, was removed from service on February 14, 2005. T.S. 3.8..1.1, Action a. requires that the operability of the remaining AC power source be verified within 1 hour, and at least once every 8 hours thereafter. This action requirement was not completed on February 14, 2005 when the RAT AC power supply to Bus E5 was removed from service. At the time of this event the unit Auxiliary Transformer AC power supply to Bus E5 and E6, and the RAT AC power supply to bus E6, were in service. This event is reportable pursuant to Seabrook Station license, Condition 2.G., as a violation of the Technical Specifications. The licensee notified the NRC Resident Inspector. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2005-03-29
41542 | -1 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-01-17 12:00 | 2005-03-29 12:46 | 2005-04-04 | MEDICAL MISADMINISTRATION - WRONG TREATMENT SITE The State provided the following NMED information: "On 1/18/05, the licensee reported to the Agency a teletherapy misadministration that occurred on 1/17/05. The situation was described as 'the treatment field was displaced by six cm when the therapist set the central axis of the field at the tattoo marking the bottom of the field'. An area of 15 cm x 6 cm (treatment site) received dose when the plan called for that tissue to receive no dose. The dose was one day's treatment of 180 cGy. The treatment monitor units and energy were correct, the error was entirely an issue of field placement." The Regulation Code cited is 105 CFR 120.502 (4) (a). The intended dose to the patient was 180 cGy, however, only 90 cGy was given to the wrong treatment site (15 cm x 6 cm area). Per the treating physician, no corrective action is needed. The hospital retrained staff to ensure confirming proper positioning of therapy prior to treatment. "Event type Description: MD2 - Wrong Treatment Site. "Cause description: The therapist did not correctly align the treatment field with the patient's treatment alignment tattoo." "The Agency considers this event closed." * * * UPDATE FROM STATE (TONY CARPENITO) TO M. RIPLEY AT 0953 EST 04/04/05 * * * The following information was provided by the State via facsimile (State text in quotes): "The device used to deliver the radiation treatment was a LINEAR ACCELERATOR." Notified R1 DO (Noggle) and NMSS EO (T. Essig) * * * RETRACTION FROM STATE (TONY CARPENITO) TO M. RIPLEY AT 1130 EST 04/04/05 * * * Based on a discussion with the NMSS EO (T. Essig) and the State (T. Carpenito), this notification is retracted because the device used to deliver the radiation treatment is not regulated by NRC. Notified R1 DO (Noggle) and NMSS EO (T. Essig) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-04-01
41541 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2005-03-23 12:00 | 2005-03-29 09:54 | 2005-03-29 | CHEMICAL AGENT DETECTORS MISSING FROM DEPARTMENT OF NAVY INVENTORY A representative for the Navy's master materials license reported a number of chemical agent detectors missing based on the two most recent inventory cycles. Specifically, 27 Chemical Agent Monitors (CAMs) that utilize a 10 milliCurie Nickel-63 plated source (SSND# NR-1129-D-103-S) are missing [270 millicuries of Ni-63 total]. In addition, 11 Automatic Chemical Agent Detector Alarms (ACADAs) with two 10 milliCurie Ni-63 plated sources in each detector (SSND# NR-1129-D-101-S) are missing [220 millicuries of Ni-63 total]. The majority of these detectors have been reported missing from Marine Core Logistics Base in Albany, GA. However, a number of these detectors have been distributed to Marine Expeditionary Units in the field. Details of the times, locations, and circumstances under which the detectors went missing are still under investigation by the Navy and will be reported in a followup 30-day written report. The licensee has contacted the NRC Regional Inspector (Masnyk-Bailey) and HQ contact (Bhachu). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-03-29
41540 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-03-28 17:38 | 2005-03-28 23:56 | 2005-03-29 | HIGH PRESSURE COOLANT INJECTION TEMPORARILY INOPERABLE The following information was obtained from the licensee via facsimile (licensee text in quotes): "Unit 2 High Pressure Coolant Injection (HPCI) [was] declared inoperable due to a loose control power fuse clip associated with the HPCI Pump Suction from Suppression Pool Valve HV-055-212041. The loose clip resulted in loss of control power to this DC motor operated valve and therefore rendered the HPCI system inoperable. The fuse clip has been replaced and the HPCI system returned to an operable status. This report is being made pursuant to 10CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident." The licensee will notify the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-29
41539 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-03-28 15:30 | 2005-03-28 22:53 | 2005-03-28 | HISTORICAL REPORT - AFTER-THE-FACT OPERABILITY ASSESSMENT The licensee provided the following information: "This event notification reports a previously unrecognized reportable event that occurred in 2002. This past event is being reported under the criterion of 10CFR50.72(b)(3)(ii)(B), an event or condition that results in the plant being in an unanalyzed condition. "On 1/23/2002, at 1815 hours, while the plant was operating at full power, the plant entered a 72 hour Technical Specifications (TS) limiting conditions for operation (LCO) for one train of the Residual Heat Removal (RHR) system. The RHR system LCO was entered when the plant discovered a potential for reaching pump runout under specific post-accident operating conditions for single pump operation of the Component Cooling Water (CCW) system. The CCW system provides cooling support to the RHR system for post-accident long term recirculation core and containment cooling operation. The RHR train was returned to service at 2002 hours on 01/25/2002, within the TS allowed 72 hours, after a flow limiting device was installed on a non-critical CCW system flaw control air operated valve. "An after-the-fact past operability assessment of the condition found that, compared to corrective actions taken to remove the potential for runout, the condition potentially existed since original plant design. As a minimum, it existed for a period longer than the TS allowed LCO for the RHR system. Therefore, an unanalyzed condition did exist and as such this is a late report." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-03-28
41538 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-03-28 13:43 | 2005-03-28 17:19 | 2005-03-28 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO POWER OUTAGE "The purpose of this 8 Hour notification is to inform the Nuclear Regulatory Commission of a Loss of Emergency Preparedness Capabilities per NUREG 1022 and 10CFR50.72(b)(3)(xiii). Specifically, at 1455 central standard time on 3/28/05, Point Beach Nuclear Plant was notified that Emergency Plan Sirens, P012, P013, and P014 were out of service. These three sirens constitute 59.32% loss of population coverage. "The time that the emergency sirens went out of service was 1343 CST, 3/28/05. These sirens are fed from Two Rivers Water/Light (WIPPI). Point Beach Nuclear Plant has contacted Manitowoc County Dispatch at 1517 of the loss of population coverage, and subsequent power restoration. Two Rivers Municipal Utilities has restored power to the Emergency Plan Sirens at 1533 on 3/28/05." The licensee informed the NRC Resident Inspector. *** UPDATE FROM J.FOUSE TO J. KNOKE AT 19:02 EST ON 03/28/05 *** The licensee faxed the following update: "The purpose of this update is to provide additional clarification to EN#41538. At 1343 CST, Emergency Plan Siren P012 went out of service due to a power outage. The loss of P012 represents a 3.38% loss in population coverage in and of itself. At 1502 CST, Emergency Plan Sirens P013, and P014 went out of service due to a power outage. When all three sirens are out, as they were from 1502 to 1533 CST, the loss of coverage to the population is 59.32%. "Power was restored to Emergency Plan Sirens P012, P013, and P014, and they were returned to service at 1533 CST. The remainder of EN#41538 remains accurate as written." The licensee informed the NRC Resident Inspector. Notified the R3DO( Riemer). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-28
41537 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-03-28 12:48 | 2005-03-28 17:15 | 2005-03-28 | NOTIFICATION OF A FORCED OUTAGE EXPECTED TO LAST LONGER THAN THREE DAYS. The licensee faxed the following information: "At 1248, 03/28/05, Callaway Plant notified the Missouri Public Service Commission (MPSC) of a forced outage expecting to last longer than three days. This notification was performed in accordance with 4CSR2403.190(3)(B). "The information was supplied to the MPSC: * the plant shutdown occurred at 0520, 03/26/05 due to a minor leak in the Essential Service Water system, and that additional repairs were going, to be performed while shutdown. * the scope of the work addition had not been finalized and a formal restart date had not been established. "This ENS notification is being made in accordance with 10CFR50.72(b)(2)(xi) for notification of another government agency." The licensee notified other governmental agencies and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-28
41536 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-03-28 10:35 | 2005-03-28 15:52 | 2005-03-28 | RCS THROUGH WALL LEAKAGE IDENTIFIED AT WELDED PIPING JUNCTION "At 1035 hours on the morning of 3/28/05, investigation into a previously reported leak (Event #41530) identified an approximate 3 inch through wall flaw at the welded junction of the 4 inch diameter decon port and the 28 inch diameter 'B' Reactor Recirculation Systems pump suction piping. The identification of the indication required the removal of insulation in order to complete the inspection. The unidentified leakage rate is below Tech Spec limits and the leak location is within the isolable boundary of the 'B' Reactor Recirculation Pump. This failure constitutes a welding or material defect in the primary coolant system that is not acceptable under ASME Section XI for ASME Code Class 1 piping. "This report is being made under Hope Creek Event Classification Guide RAL# 11.2.1 in accordance with 10CFR50.72(b)(3)(ii). At the time of this notification, the Hope Creek Generating Station is in OPCON 4 at 150 degrees reactor coolant temperature to support piping repairs." The licensee informed the Lower Alloways Creek Township and NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-03-28
41535 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-28 12:46 | 2005-03-28 15:27 | 2005-03-28 | REACTOR TRIP DUE TO GENERATOR PROTECTION CIRCUITRY The licensee faxed the following: "Unit 2 reactor trip due to generator protection circuitry. Auxiliary feedwater actuated as expected. There were no additional malfunctions or unexpected plant response. The cause of the generator protection circuitry induced trip is still under investigation. "This is a 4 hour notification of an RPS actuation per 10CFR 50.72(b)(2)(iv)(B). The 8 hour notification of an auxiliary feedwater system actuation per 10CFR 50.72(b)(3)(iv)(A) is being made under the same telephone call." See Event 41534. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-03-28
41534 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-28 13:59 | 2005-03-28 15:27 | 2005-03-29 | UNUSUAL EVENT DECLARED DUE TO HYDROGEN LEAK The licensee faxed the following information: "Following the Unit 2 trip, (due to a malfunction of the generator protection circuitry), a hydrogen leak was identified on the Unit 2 main generator. The leakage was sufficient enough to cause a flammable gas release affecting normal plant operation. The Unusual Event was declared under HU6 - Hazards and Other Conditions. The State and local authorities were notified at 14:09 CST. There is NO fire, it is a hydrogen release only." The licensee said the hydrogen totalizer, which indicated a flow rate of 100 cfm, may be a probable area of leakage. The hydrogen leaked directly into the turbine building. Air samples indicated personnel breathing apparatus was not required. The licensee expects to exit from the UE once the hydrogen system was purged with CO2. Estimated timeframe is 3-6 hours. The licensee notified the NRC Resident Inspector. *** UPDATE FROM D. BRAGLIA TO J. KNOKE AT 17:40 EST ON 3/28/05 *** The licensee terminated their Unusual Event at 16:40 CST, and the plant status is 0% power / Mode 3. The hydrogen leak was determined to be from a bushing on the main generator. The hydrogen leakage is believed to have lasted only 5 minutes. The licensee notified the State and NRC Resident Inspector. Notified R3DO (Riemer), IRD Manager (Crlenjak), NRR EO (Berkow), FEMA and DHS. *** UPDATE FROM J. GERRITY TO J. KNOKE AT 14:30 EST ON 3/29/05 *** Received Event Summary Report from Braidwood station. Corrected Unusual Event termination time from 16:40 to 16:23 CST. Notified R3DO (Riemer) and NRR EO (Brenner) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-03-28
41533 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-03-28 14:21 | 2005-03-28 14:21 | 2005-04-07 | PLANNED OUTAGE OF SPDS DUE TO SYSTEM UPGRADE The licensee faxed the following information: "On Tuesday, March 29, 2005, Surry Power Station will remove a portion of the Emergency Response Facilities Computer System (ERFCS) in the Main Control Room (MCR) for planned upgrades to a new system for increased reliability and improved human interface design. For approximately 1 week, there will not be a qualified Safety Parameter Display System (SPDS) available in the MCR. "During the time period that SPDS is unavailable in the MCR while the upgrade is occurring, the replacement SPDS system is available in the MCR on the Plant Computer System (PCS), but final testing will not qualify the software until completion of this work. There will also remain one ERFCS terminal operable in both the Technical Support Center (TSC) and Local Emergency Operations Facility (LEOF) with operable SPDS throughout the duration of this work. The Emergency Response Data System (ERDS) will remain available from those terminals for the duration of this planned work and normal data transmission capability will remain in the event of an emergency. "Since SPDS will be out of service for greater than 1 hour, this report is being submitted in accordance with the guidance in 10CFR50.72(b)(3)(xiii) and NUREG-1022." The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED TO NRC (HUFFMAN) BY DEANE ON 1827 EDT ON 4/7/05 * * * The following information was provided by the licensee via facsimile: "This report is an update to previous report EN #41533, dated 03/28/05, regarding the availability of the Emergency Response Facilities Computer System (ERFCS) and Safety Parameter Display System (SPDS) in the main control room for Surry Power Station. "The ERFCS and SPDS modifications and testing were completed at 1630 hours on 04/07/05. These functions have been transferred to the Surry Plant Computer System. "Senior NRC resident, Norm Garrett was notified via alphanumeric page. Notification was made to NRC duty officer Bill Huffman." R2DO (Rogers) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-28
41532 | 0 | ST JOSEPH REGIONAL MEDICAL CENTER |  |  |  |  | 2004-02-23 | 2005-03-28 11:13 | 2005-04-05 | MEDICAL EVENT The following information was supplied by the licensee: "Two patients involved in what we now think to be reportable events. 1. A.M. 2-23-04 to 2-24-04 2. R.M. 3-01-04 to 3-02-04 "In both cases the patients were being treated for endometrial cancer with brachytherapy. A new Wang vaginal applicator was used. The tandem was loaded with incorrect size sources (of Cs-137) which then had the ability to slide out of the intended treatment position through the placement spring when the patient would sit in a more up-right position. With the sources out of position they would irradiate the patients inner thigh. The dose to the thigh had to be estimated based on estimated time the patient was in an up-right position and the effect seen on the skin. "At the time these incidents took place it was not felt that reportable events had taken place because of the calculated exposure to the thigh, patient symptoms, and the interpretation of 35.3045 (a) (1)(2), (3). "One of the patients (A.M.) returned recently (1/05) with an ulcer at the area of thigh exposure. This has caused the radiation therapy staff to reevaluate their dose estimation to the patients. After review, it is believed that reportable events my have occurred based on 35.3045 (A) (3). "This conclusion was formulated on 3-25-05 after a staff meeting and 1 received the final letter from the physician today 3-28-05." The tandem manufacturer recommends 3M seeds and the facility used Amersham seeds which resulted in the seeds shifting. A total of 5 patients were treated. The initial estimates determined that the exposure was less than the reportable limit. All the patients were notified of the exposure. One of the two overexposed patients is responding well to treatment. The other patient may have received the higher dose. The remaining three patients appear to have received less than the reportable dose. * * * UPDATE FROM JOHN SCHEU TO JEFF ROTTON ON 4/1/2005 AT 1608 * * * Discussion between the licensee and NRC Region 3 inspectors determined that a third patient should be added to this event: 3. K.B. 3-19-04 to 3-22-04 Notified R3DO (Riemer) and NMSSEO (Collins). * * * UPDATE FROM JOHN SCHEU TO HOWIE CROUCH ON 4/5/05 AT 1833 EDT * * * Discussion between the licensee and NRC Region 3 inspectors determined that a fourth and fifth patient should be added to this event: 4. D. T. 1/26/04 to 1/27/04 5. M. S. 2/18/04 to 4/21/04 Notified R3DO (O'Brien) and NMSS EO (Leach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2005-03-28
41531 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-03-27 19:30 | 2005-03-28 01:12 | 2005-03-28 | ELECTRICAL SAFETY BUS TRIP DURING QUAD CITIES UNIT 1 REFUELING OUTAGE The following information was obtained from the licensee via facsimile (licensee text in quotes): "At 1930, Unit 1 experienced a loss of 480 VAC busses 18 and 19. This caused a loss of power to the Control Room Emergency Ventilation System (CREVS) and the CREVS Air Conditioning System (CREVS AC). This event also caused a loss of power to the U1 equipment that was supporting the Alternate Decay Heat Removal (ADHR) mode of operation. "Power was restored to Bus 19 at 2001 and Bus 18 at 2013. The restoration of Bus 18 also restored power to CREVS and CREVS AC. All systems supporting ADHR were restored by 2015. At the time of the occurrence, the estimated time to boil without decay heat removal capability was 571 minutes. All isolations and actuations occurred as expected. The cause of the bus trips is being investigated. "This Event is being reported under 50.72 (b)(3)(v)(B) and 50.72 (b)(3)(v)(D)." The licensee stated at the time of the event, Busses 18 and 19 were cross-tied and the feeder breaker to Bus 18 tripped open. The breaker was changed out and power to Busses 18 and 19 restored. The cause of the Bus 18 feeder breaker trip has not yet been determined. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM THE LICENSEE (OSELAND) TO NRC (HUFFMAN) AT 0312 EST ON 3/28/05 * * * The licensee stated that the Alternate Decay Heat Removal pumps from Unit 2 remained in service so that all decay heat removal was not lost. The Unit 1 primary coolant system temperature increase during the 45 minute duration of this event was approximately 1 degree. R3DO (Kozak) has been notified. | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2005-03-28
41530 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2005-03-27 22:00 | 2005-03-28 00:35 | 2005-03-28 | PLANT SHUTDOWN TO REPAIR SMALL REACTOR COOLANT SYSTEM LEAK The following information was obtained from the licensee via facsimile (licensee text in quotes): "While in OPCON 2 with the Main Turbine secured, Hope Creek personnel performed a Primary Containment entry to determine the source of slightly elevated unidentified leakage. This leakage has slowly trended up since plant start-up in February to approximately 0.73 gpm. With the current unidentified leak rate at 0.436 gpm, personnel identified a steam leak from an insulated decontamination port, sealed via a bolted flange, within the isolable boundary of the 'B' Reactor Recirculation pump. This was the only source of reactor coolant system leakage identified although some minor leakage (totaling approximately 250ml/min) from two drywell recirculation fans was also identified. This is a voluntary/courtesy Emergency Notification System (ENS) notification that Hope Creek is proceeding to Cold Shutdown to precisely identify and repair the leakage source. At the time of this notification, Hope Creek Generating Station is in OPCON 3 with plant cooldown in process." The licensee reported this event under 10 CFR 50.72(b)(2) as a 4-Hour Non-Emergency Voluntary notification. The NRC Resident Inspector has been notified and the licensee plans to notify LAC Township. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2005-03-28
41529 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-03-26 04:14 | 2005-03-27 08:16 | 2005-03-27 | AGREEMENT STATE REPORT - FIRE INVOLVING RADIOACTIVE MATERIAL At 0414 on 03/26/05, a fire broke out in a laboratory of the Perkin Elmer Life Sciences in Boston, MA, that contained 8 Curies Carbon 14. The C-14 was stored in multiple locations. Local fire fighters and hazmat team responded. The fire was extinguished at approximately 0800. There was evidence of contamination inside the building and on the firefighters protective clothing. The levels were 3 - 4 times background. Two firefighters were treated at the hospital for smoke inhalation. The licensee has taken bioassay samples from the two individuals. Wipes outside the facility had no contamination. The cause of the fire is unknown. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-03-30
41528 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-03-24 15:08 | 2005-03-26 02:43 | 2005-03-26 | UNANALYZED CONDITION RELATING TO THE INTEGRITY OF THE DIESEL GENERATOR EXHAUST STACKS DURING A TORNADO The following information was obtained from the licensee via facsimile (licensee text in quotes): "While evaluating the capability of the plant to withstand a tornado it was identified that the Diesel Generator Exhaust Stacks may not maintain their design structural integrity. This would place the plant in an unanalyzed condition, however expert engineering judgment is that the damage to the Emergency Diesel Generator Exhausts would not reduce the capacity below that required to ensure decay heat removal. Currently the plant is in refueling shutdown and the Emergency Diesel Generators are not required to be operable per Technical Specifications. This condition will be corrected prior to plant startup. Power is still being supplied to the plant from the Reserve and Tertiary Auxiliary Transformers. This event was determined to be reportable per 10CFR50.73(a)(2)(ii)(B) and further review of the reporting criteria identified that if there is any doubt, this condition should be reported under 10CFR50.72(b)(3)(ii)(B). "At the request of the Plant Manager at approximately 2100 on 3/25/05, the Shift Manger and Shift Technical Advisor independently reviewed the reporting criteria. Based on the statement in NUREG 1022, Rev 2, when applying engineering judgment and there is doubt regarding whether to report or not, the commission's policy is that the licensees should make the report, it was decided to report per 10CFR50.72." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-03-26
41527 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-03-26 03:00 | 2005-03-25 22:45 | 2005-03-27 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE ESW TRAIN. The following information was faxed by the licensee: "At 0300, 3/23/05, 72-hour Technical Specification Action 3.7.8.A was entered when a pinhole leak was discovered in 'B' Essential Service Water (ESW). Subsequent ultrasonic testing (UT) determined that approximately seven linear feet of piping in the 'B' ESW train was affected and required replacement. UT testing was satisfactorily performed on the 'A' ESW train to ensure a similar problem did not exist. "'B' ESW train piping replacement was performed in accordance with planned work documents, however at 2100, 3/25/05 all necessary repairs and retests had not been completed. Although only 66 hours had expired since entering 72-hour Technical Specification Action 3.7.8.A, Callaway Plant proactively decided to commence a reactor plant shutdown in accordance with Technical Specification Action 3.7.8.B for an inoperable 'B' Essential Service Water train. Once entered, Technical Specification Action 3.7.8.B requires the reactor plant to be in Mode 3 within 6 hours and Mode 5 within 36 hours. "The Licensee notified the NRC resident inspector." The licensee will perform other maintenance activities during this outage. All systems functioned as required. * * * UPDATE FROM F. BIERMANN TO W. GOTT AT 0411 ON 03/27/05 * * * The licensee completed repairs on the B ESW system and exited the LCO at 0249 on 03/27/05. Notified R4DO (Pick). | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-03-25
41526 | 0 | GEO-TECHNOLOGY ASSOCIATES, INC |  |  |  |  | 2005-03-25 07:00 | 2005-03-25 16:18 | 2005-03-28 | TROXLER GAUGE REPORTED STOLEN Geo-Technology Associates, Inc. (GTA) reported the theft of a Troxler gauge, Model 3411, Serial # 15742. The source strength of this gauge is 8 milliCi of Cs-137 and 40 milliCi of Am-241. A contract employee was last seen with the gauge when he signed out for the device at GTA's office on the morning of 3/24/05. He was supposed to have gone to a construction job site in Gainesville, VA, and then return to GTA's office that evening with the Troxler gauge. It is unknown at this time if he reported to the jobsite or returned to the office. An employee of GTA came into the office about 07:00 on 03/25/05 and discovered the Troxler gauge missing. Normally a worker returns equipment (Troxler gauge) to the office at the end of each workday. The GTA employee reported the possible theft to the Loudoun County Sheriff in VA. *** UPDATE FROM T. UPSON TO J. KNOKE AT 19:30 ON 03/25/05 *** An employee of GTA called to report the Troxler gauge was returned to GTA's office sometime between 17:00 and 18:00 on 03/25/05. It was assumed to be the contract employee who originally signed out for the gauge had returned it since it was found inside the locked office of GTA. No visible damage to the device was detected. GTA indicated that early next week a decision would be made on whether or not they will rescind the sheriff's report of a stolen Troxler gauge. * * * UPDATE FROM T. UPSON TO W. GOTT AT 0950 ON 03/28/05 * * * The licensee reported that, since the gauge was returned intact and undamaged, they did not plan on pursuing charges against the individual that allegedly used the gauge. Notified R1DO (J Trapp) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-03-25
41525 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-24 20:15 | 2005-03-25 01:53 | 2005-03-25 | REACTOR COOLANT LEAKAGE OUTSIDE CONTAINMENT EXCEEDING DESIGN BASIS The following information was obtained from the licensee via facsimile (licensee text in quotes): "This is an 8-hour notification being made to report exceeding the design basis for the reactor coolant leakage outside of containment. The event is being reported under paragraph (b)(3)(v) of 10CFR50.72. An event or condition that could have prevented mitigating the consequences of an accident. "On 03/24/05 at 2015 operators discovered that a closed manual discharge valve for the positive displacement charging pump was leaking through allowing Reactor Coolant System to leak back to the refueling water storage tank. The leakage was 0.34 gallons per minute. This leakage is greater than the UFSAR limit for ECCS leakage outside containment. "With leakage greater than the UFSAR allowed limits (greater than 3800 cc/hr), GDC-19 limits for control room habitability cannot be assured. "Actions were taken and the leakage was stopped at 2040. The affected positive displacement charging pump is not a safety related pump and is not required for accident mitigation; however it is in the ECCS recirculation flow path during the cold leg injection phase of the accident mitigation. "The licensee will notify the NRC Resident Inspector of this event." The licensee will be notifying local authorities. The licensee reported that the event had no impact on Unit 1. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-25
41524 | -1 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-03-24 09:30 | 2005-03-24 17:50 | 2005-04-13 | MINIMUM SWITCHYARD VOLTAGE REQUIREMENTS NOT MET The following information was obtained from the licensee via facsimile (licensee text in quotes): "Minimum Switchyard Voltage Requirements Not Met "On March 24, 2005, at 0930 hours, Quad Cities was notified that the switchyard voltage was below that required to ensure that offsite power would remain available following a design basis accident. Both sources of off-site power were declared inoperable. The appropriate Technical Specification required actions were taken for both units. The ability of the Emergency Diesel Generators to perform their design function is not affected by this condition. This event is being reported in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function given the predicted post-LOCA switchyard voltage. "A preliminary engineering assessment indicates that one source of offsite power was available. Additional confirmatory reviews are being performed to determine if the safety function was preserved. "At this time, grid/switchyard voltage has been restored." Minimum switchyard voltage required is 348.4 KV. The analyzed minimum voltage which prompted notification to the NRC was 347.5 KV. Switchyard voltage at the time of this report was ~359 KV. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM C. STEFFES TO M. RIPLEY 1556 EDT 04/13/05 * * * "The purpose of this report is to retract the following ENS reports: 1) ENS # 41524 on March 24, 2005; 2) ENS # 41562 on April 4, 2005; and 3) ENS # 41587 on April 11, 2005. "These reports were made following notification to Quad Cities that the switchyard voltage was below the required value necessary to ensure that offsite power would remain available following a design basis accident. For each event, both sources of offsite power were declared inoperable, the appropriate Technical Specification required actions were taken for both units, and an ENS notification was made for a condition that could have prevented fulfillment of a safety function. "The events occurred when Unit 1 was in a refueling outage and Unit 2 was operating at 85% power. Subsequent Engineering analysis has determined that with a unit shutdown, and the large 4 Kv loads on that unit not running, the required minimum post-accident switchyard voltage is reduced to 339.3 kV (for the shutdown unit). Given the new minimum post-accident switchyard voltage, it was confirmed that there was a source of off-site power available to the Station. Specifically for all three events, the projected post-accident switchyard voltage (which ranged between 343 kV to 347.5 kV) was higher than the required minimum post-accident switchyard voltage (339.3 kV) for the shutdown unit. As a result, there was no condition present that could have prevented fulfillment of a safety function, and thus these events are not reportable." The licensee notified the NRC Resident Inspector. Notified R3 DO (J. Madera) | 0 | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-24
41523 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-03-24 14:00 | 2005-03-24 17:49 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * EQUIPMENT PIECE FOR STORAGE RACK NOT IN PLACE FOR SAFE STORAGE OF SNM The following information was faxed by Nuclear Fuels Services: "ACTUAL OR POTENTIAL HEALTH AND SAFETY CONSEQUENCES TO THE WORKERS, THE PUBLIC, AND THE ENVIRONMENT, INCLUDING RELEVANT CHEMICAL AND RADIATION DATA FOR ACTUAL PERSONNEL EXPOSURES TO RADIATION OR RADIOACTIVE MATERIALS OR HAZARDOUS CHEMICALS REPRODUCED FROM LICENSED MATERIALS "There were no actual health and safety consequences to workers, the public, or the environment. There were also no personnel exposures to radiation, radioactive materials, or hazardous chemicals produced from licensed materials. The potential Nuclear Criticality Safety (NCS) consequences for workers were very low given the actual material storage conditions. No additional containers of SNM above the approved limit were stored in the storage racks and additional containers were specifically evaluated and determined to be subcritical. "THE SEQUENCE OF OCCURRENCES LEADING TO THE EVENT, INCLUDING DEGRADATION OR FAILURE OF STRUCTURES, SYSTEMS, EQUIPMENT, COMPONENTS, AND ACTIVITIES OF PERSONNEL RELIED ON TO PREVENT POTENTIAL ACCIDENTS OR MITIGATE THEIR CONSEQUENCES: "On March 24, 2005, a Nuclear Criticality Safety Engineer (NCSE) inspected a storage rack and observed that a piece of Configuration Controlled Equipment (CCE) was not in place. The piece of equipment is credited for preventing containers of SNM from being stored between approved storage positions. A posted Station Limit Card (SLC) instructs the operations personnel on the number and location where containers of SNM may be stored in the racks. "DISCUSS WHETHER REMAINING STRUCTURES, SYSTEMS, EQUIPMENT COMPONENTS, AND ACTIVITIES RELIED ON TO PREVENT POTENTIAL ACCIDENTS OR MITIGATE THEIR CONSEQUENCES ARE AVAILABLE AND RELIABLE TO PERFORM THEIR FUNCTION: "The remaining activities relied on to prevent potential accidents are available and reliable to perform their function. The storage requirements are posted via a Station Limit Card on the storage rack and no containers were observed to be stored in unapproved locations. "ACTIONS TAKEN IN RESPONSE TO THE EVENT: "The bottom two storage positions that could be involved were covered by signs instructing the operations personnel to not use them. The process engineer for the area was instructed to install the needed equipment to bring the storage rack into compliance. The event was entered into the PIRCS system (PIRCS ID 4704). "SAFETY SIGNIFICANCE OF THE EVENT: "The safety significance was very low for the event given that no violation of container storage was found. Containers of SNM were not stored in unapproved locations in the storage rack. More than one failure would have been necessary to be outside of the normal case configuration modeled in the Nuclear Criticality Safety Evaluation. The risk index could very easily have been written to credit additional limits and requirements that would have made this report unnecessary. "BRIEF SCENARIO OF HOW A CRITICALITY COULD OCCUR: "For a criticality to occur, multiple containers (more than two) would have had to have been stored incorrectly. "WHAT ARE THE CONTROLS OR CONTROL SYSTEMS AND THE FAILURES OR DEFICIENCIES? "The controls were equipment design to prevent containers of SNM from being stored between approved storage locations in a storage rack. The bottom of the storage rack had not been modified to prevent a container from being stored between approved storage locations. "WHAT ARE THE CORRECTIVE ACTIONS TAKEN AN WHEN WAS EACH IMPLEMENTED? "The storage positions involved at the bottom of the storage rack were taken out of service immediately on 3/24/2005. The process engineer for the area was immediately notified of the necessary modification to the equipment. The event was entered into the PII2CS system." There was no exposure to personnel with this event. The licensee notified the NRC Resident Inspector. No other notifications were issued. * * * UPDATE 1030 EDT ON 4/6/05 FROM RANDY SHACKELFORD TO JEFF ROTTON * * * NFS Erwin is retracting this report based on the following: "On 3/24/2005, NFS made a 24-hour report to the operations center based on l OCFR70, Appendix A, Paragraph (a)(2). L OCFR70, Appendix A, Paragraph (a)(2) requires a 24hour report for loss or degradation of items relied on for safety (IROFS) that results in failure to meet the performance requirement of Sec. 70.61. The report was made because it was observed that a piece of configuration controlled equipment for a storage rack was not in place that would prevent containers from being stored between approved storage positions. "The storage of containers between approved storage positions was bounded by the normal case Nuclear Criticality Safety (NCS) model; and, it was later determined that other IROFS listed in the ISA Summary were in place such that the performance requirements were met. This information was discussed and reviewed with an NRC Nuclear Criticality Safety (NCS) Inspector during the week of March 28, 2005. Based on this information and discussion with the NRC Inspector, it is requested that this event report be retracted." Notified R2DO (Rodgers) and NMSS (Burgess). * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
41522 | 0 | ST. BARNABAS HEALTH CARE SYSTEM |  |  |  |  | 2004-07-06 12:00 | 2005-03-23 23:05 | 2005-03-24 | PART 21 REPORT ON BRACHYTHERAPY DEVICE (MICROSELETRON-HDR) On July 6, 2004, while performing routine QC tests prior to patient treatment, the High Dose Rate afterloading brachytherapy device (microSeletron-HDR) failed to retract. With Nucletron service personnel on the phone giving technical support, the RSO entered the room and manually retracted the 6.7 Ci of Ir- 192 source. His whole body exposure was subsequently found to be 7 mRem and ring badge <10 mRem. The device, which is manufactured by Nucletron, Inc, was found to have a defective "TU MPU PCB" board. After replacement and testing, the device was returned to operating status for future patient treatment. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | PAR | 21.21 |  |  |  | 0 | 2005-03-24
41521 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2005-03-24 | 2005-03-24 11:48 | 2005-03-25 | MISSING SHIPMENT OF 105 BRACHYTHERAPY (I-125) SEEDS TOTALING 66 MILLICURIES GE Healthcare, also known as Medi Physics, reported that a package of radioactive material had not been received as expected by Northwest Arkansas Medical Center in Springdale, Arkansas. The package, which contains 105 brachytherapy seeds, was to be delivered on Monday March 21, 2005. The seeds contain approximately 0.63 milliCi of activity each, with a total package activity of 66 milliCi. The maximum radiation level on the surface of the package is less than 0.5 milliR/hr. The material was sent via FedEx on Friday March 18 and received at the FedEx facility in Tulsa, Oklahoma on March 19. No further information has been logged since. Medi Physics' customer service group has begun their investigation. The Arkansas Division of Radiation Control has been advised of the situation. IL report number: IL050022 *** UPDATE FROM STATE OF IL (G. VINSON) TO (J. KNOKE) AT 15:14 EST ON 3/25/05 *** The State of IL, Division of Nuclear Safety, called to indicate the missing package containing 105 brachytherapy seeds was located in the Fed Express facility in Arkansas. The package, which was estimated to be found about 11:30 EST on 3/25/05, was intact and in its original condition. The licensee believes the missing package was in the possession of Fed Ex at all times, with no third party intervention. The brachytherapy seeds are being returned to G.E. Healthcare to determine that all seeds are accounted for and to further investigate how the package was lost within the Fed Ex system. Notifications were given to R3 (Kozak), NMSS (Moore), and TAS (Sandler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2005-03-29
41520 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2005-03-23 10:45 | 2005-03-24 09:49 | 2005-03-24 | FAILURE OF SAFETY EQUIPMENT ON RADIOGRAPHY CAMERA A representative for the Navy's master material license reported a safety equipment failure of a Gamma Radiography Camera with a 16 curie Iridium-192 source (Model 660) that was being used at the Norfolk Naval Shipyard. After an exposure with the camera had been completed, the radiographer was retracting the source and could not lock it into its safe position. After a second attempt, the radiographer was able to lock the source in place manually - the locking ring did not lock automatically as designed. The radiographer noted that the retraction cable on the camera had also become disconnected from the camera. The camera is being returned to the vendor (AEA) for inspection and repair. A 30 day written followup report will be provided. The licensee has notified the NRC regional inspector (Masnyk-Bailey) and NRC HQ (Bhachu). The licensee stated that this report was being provided to the NRC under 10 CFR 34.101(a))(3). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2005-03-24
41519 | 0 | DEPT OF NAVY RADIATION SAFETY CMTE |  |  |  |  | 2005-03-02 | 2005-03-24 09:49 | 2005-03-24 | RECEIPT OF RADIOACTIVE MATERIAL WITHOUT PROPER CONTROL An 89 curie Iridium-192 Gamma Radiography Camera (Model 660) was received at a Naval warehouse in Guam without proper controls or receipt inspection. The Navy Master Materials licensee representative states that the radiography camera was sent by AEA (the camera vendor) to a submarine tender stationed in Guam without preshipment notification or any request for the camera by Naval personnel stationed on the tender. The camera was received by the warehouse on March 2, 2005, and placed in warehouse storage without procedural control related to the receipt of radioactive materials. On March 14, 2005, during unrelated survey of materials in the warehouse, the camera was discovered. The submarine tender radiographer was contacted and performed receipt inspection and survey and determined that there is not radiological problems and the camera source is in its proper safe storage position. This event is still under investigation and a 30 day written followup report will be prepared. The licensee is reporting this event under 10 CFR 20.2201(a)(1) because the material was not under proper control from March 2 through March 14, 2005. The licensee has notified the NRC regional inspector (Masnyk-Bailey) and NRC HQ (Bhachu). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-03-24
41518 | -1 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-24 07:42 | 2005-03-24 08:04 | 2005-03-24 | UNUSUAL EVENT DECLARED DUE TO LOSS OF CONTROL ROOM ANNUNCIATORS The licensee reported an Unusual Event following a loss of all control room overhead annunciators (per EAL 8.2.1). The cause of the loss of the overhead annunciators is still being investigated. The licensee states that the plant is stable with no other problems. This licensee plans to remain at 100% power while troubleshooting the condition. The licensee has notified the NRC Resident Inspector, State , and local government agencies. The NRC Resident Inspector in the control room provided some additional information related to this event (0820 EST). The condition was discovered during a routine lamp check of the annunciators. When the lamps failed to clear after the check, the licensee entered its abnormal operating procedure and discovered the problem. The licensee does have compensatory means of monitoring the alarms through a control room CRT display as well as a printer that registers alarms. The resident stated that the extent of the annunciator loss is unclear. * * * UPDATE FROM LICENSEE (PRZEKOP) TO NRC (HUFFMAN) AT 10:55 EST ON 3/24/05 * * * The licensee terminated from the Unusual Event at 10:50 EST. The licensee stated that the annunciator system has been repaired and reset and verified to be operable. No information on the specific nature of the problem or repairs affected to restore the system to operable was provided. The NRC Resident Inspector, State, and local authorities have been notified by the licensee. R1DO (Rogge), NRR (Benner), IRD (Crlenjak), FEMA (DUNKET), and DHS (EVANS) were notified. * * * UPDATE FROM LICENSEE (S. SAUER) TO NRC (J. KNOKE) AT 15:21 EST ON 3/24/05 * * * UNUSUAL EVENT RETRACTED The licensee faxed the following update: "Upon further investigation and testing it was determined that the annunciator system was always functional; redundant capability of the annunciators was unavailable. Plant equipment information was always available to Operators during this time period (07:42 to present), and as such the emergency condition did not exist and the Unusual Event is retracted." The NRC Resident Inspector, State, and local authorities will be notified by the licensee. Notified R1 (Rogge), IRD (Crlenjak), NRR (Berkow), FEMA (Dunket), and DHS (Evans). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-03-24
41517 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2005-03-24 05:29 | 2005-03-24 07:59 | 2005-03-24 | REACTOR AUTOMATIC SCRAM DUE TO MAIN STEAM HIGH FLOW ISOLATION SIGNAL The licensee provided the following information via email (licensee text in quotes): "On 3/24/05 at approximately 0529 Unit 2 received a Group 1 isolation on main steam line high flow. All Group 1 valves closed as required and the reactor scrammed. The Isolation Condenser was manually initiated to control reactor pressure. Group 2 and 3 Containment Isolations occurred as expected. Investigation as to the cause of the Group 1 isolation is in progress. "All systems responded as required with no abnormalities noted." The licensee also indicated that a Main Turbine Generator EHC transient occurred at the time of the isolation. All control rods fully inserted, the electrical grid is stable, and decay heat is being removed via the Isolation Condenser System. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-03-24
41516 | -1 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-03-23 19:56 | 2005-03-23 22:29 | 2005-03-24 | REACTOR MANUALLY TRIPPED FROM 20% POWER DURING LOAD REDUCTION. Unit 4 reactor was manually tripped from 20 percent power per 4 - GOP - 103 "Power Operation to Hot Standby" (normal shutdown procedure), during a load reduction to take the unit off line. The reason for the load reduction was an oil leak of approximately 100 drops per minute on the "4B" steam generator feed pump. The reactor was tripped when directed by 4 - GOP - 103. All rods fully inserted, no relief valves lifted, and all other systems functioned normally. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM V. BARRY TO M. RIPLEY 1125 EST 03/24/05 * * * The licensee provided the following information via facsimile (licensee text in quotes): "Upon review, the manual reactor trip from 20 percent power is not reportable in accordance with 10 CFR 50.72(b)(2)(iv)(13) since it was part of the pre-planned sequence of reactor shutdown steps contained in procedure 4-GOP-103, "Power Operation to Hot Standby." In addition, the reactor shutdown was not required by Technical Specifications. "The NRC Resident Inspector will be notified of this retraction." | 0 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-03-23
41515 | 0 | HARPER UNIVERSITY HOSPITAL |  |  |  |  | 2005-03-21 10:00 | 2005-03-22 12:28 | 2005-03-22 | MEDICAL EVENT - TOTAL DOSAGE DELIVERED IS LESS THAN THE PRESCRIBED DOSAGE During a quarterly review of written directives by hospital personnel, it was noted that a patient was administered a dosage of 12.51 millicuries of the isotope NaI-131 for hyperthyroidism instead of the prescribed dosage of 21 millicuries. Radiopharmaceutical unit dose dispensing records as well as internal scheduling paperwork confirm that the 12 millicuries dosage was in fact ordered and subsequently administered to the correct patient. The root cause of this event has been determined by the licensee to be lack of strict attention to detail and they have evaluated their policy and procedures to prevent reoccurrence. The attending physician has reviewed the patient's records and felt that there would be no adverse affect due to this misadministration. He will notify the patient regarding this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-03-22
41514 | 0 | U.S. ARMY ROCK ISLAND IL |  |  |  |  | 2005-03-10 11:00 | 2005-03-22 13:50 | 2005-03-22 | TRITIUM CONTAMINATION FROM A BROKEN M1A1 COLLIMATOR The following information was provided by the licensee by fax. "On 17 March 2005, the TACOM-RI RSO received a call from the Ft. Sill RSO informing the licensee that he discovered 3 ea broken M1A1 collimators (nsn 1240-00-332-1780 sealed source registration no. NR-155-S-102-S). Each M1A1 collimator contains a 10 curie sealed source lamp. One collimator (s/n 933) was discovered in a training area. After this collimator was discovered, the Ft Sill RSO immediately proceeded to inspect all M1A1 collimators found in the 3/30th Field Artillery, sections 2nd, 3rd, and 6th. As a result of this inspection, the RSO discovered two additional broken M1A1 collimators, (s/n's 8644, 4116). The RSO immediately took survey wipes of the collimators and areas where they were located. There was no physical damage on the exterior of the devices or cases containing the devices. Physical damage was observed of the tritium sealed source cell itself, however exterior lenses were intact on all three collimators. It could not be determined how the damage occurred. Leak tests were performed on the three collimators with the following results s/n 933 (837,000 dpm or 3.7E-4 millicuries), s/n 8644 (6,950 dpms or 3.1E-7 millicuries), and s/n 4116 (26,300 dpms or 1.2E-5 millicuries). Only Collimator s/n 933 exceeded reportable limits [110,000 DPM]. The RSO secured the purging and training areas upon discovery of the broken devices and conducted area survey in the purging area, conex trailers (where collimators are stored) and training area. None of the areas surveyed had removable tritium contamination in excess of 5,000 dpms. Tritium bioassay samples were taken on individuals (approx 10) who may have actually handled the broken M1A1 collimators. Bioassay samples will be analyzed at the US Army lab, CHPPM Aberdeen, MD. At the time of this report, the bioassay results were not available, The Ft Sill RSO has secured the three collimators in a low-level rad waste storage site for future disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2005-03-22
41513 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-03-22 11:02 | 2005-03-22 12:25 | 2005-03-22 | PLANT SHUTTING DOWN TO MODE 3 FROM 100% POWER DUE TO A REACTOR TRIP BREAKER BEING INOPERABLE. A plant shutdown to mode 3( 0% power) was started at 1102 on 3/22/05. The shutdown was required per T.S. 3.3-1 Table 3.3-1, item 19, action 9. Reactor trip breaker "A" is inoperable. T.S.3.3.1, Table 3.3-1 item 19, action requires a shutdown to mode 3 within 6 hours. Plant must be in mode 3 by 1622 EST on 3-22-05. They are currently troubleshooting on the reactor trip breaker. The NRC Resident Inspector was notified. | 61 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-03-22
41512 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2005-03-22 | 2005-03-22 08:10 | 2005-03-22 | FOR CAUSE FITNESS FOR DUTY TEST FAILURE A contract supervisor had a confirmed positive for alcohol during a "for-cause" fitness for duty test. The contractor's site access was denied, the contractor was escorted off site and provided a ride home. Contact the Headquarters Operations Officer for additional details. The NRC Resident will be notified by the site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2005-03-22
41511 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-03-22 03:47 | 2005-03-22 04:21 | 2005-03-22 | REACTOR MANUALLY TRIPPED FOLLOWING LOSS OF MAIN FEED PUMP The licensee provided the following information via fax (licensee text in quotes) "The 4A SGFP [Steam Generator Feed Pump] tripped, initiating a Turbine Runback. Operators manually inserted a Reactor Trip at 15% Steam Generator level. The reactor tripped and all control rods inserted. Auxiliary Feedwater automatically initiated as expected. All systems operated as expected except the 4A SGFP discharge MOV which has no [position] indication [in the main control room and is being] investigated." Decay heat is being removed by atmospheric steam dumps. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-03-22
41510 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2005-03-21 17:00 | 2005-03-21 22:34 | 2005-03-21 | HPCI DECLARED INOPERABLE - ENTERING 14 DAY LCO ACTION STATEMENT The following information was provided by the licensee by fax. "At approximately 17:00 on March 21, 2005, while performing required surveillance testing on the Unit 3 HPCI system, the HPCI Condensate Storage Tank (CST) suction valve (MO-3-23-17) failed to close after the HPCI Torus suction valves (MO-3-23-57 & MO-3-23-58) were full open. Failure of the CST suction valve MO-3-23-17 to close when a Torus suction path was established, required entry into Technical Specification 3.3.5.1 for loss of initiation function for CST level low and Torus level high (Functions 3d, 3e). The loss of initiation function under Technical Specification 3.3.5.1 required that the HPCI system be declared inoperable in one (1) hour after discovery. HPCI was initially declared inoperable at 16:41 for surveillance testing. HPCI inoperability has been maintained as of that time. Pursuant to 10CFR 50.72(b)(3), this notification is being made due to Unit 3 HPCI inoperability, which prevents fulfillment of a Safety Function." Initial troubleshooting hints that the cause of the failure may be due to a limit switch malfunction. The NRC Resident Inspector was notified. | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-21
41509 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-03-21 15:53 | 2005-03-21 18:25 | 2005-03-21 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM (SPDS) FUNCTION FOR GREATER THAN 8 HOURS. The following information was provided by the licensee "On 3-21-05 the Plant Computer system was removed from service at 0753 for scheduled maintenance. The system was not verified restored until 1558. This is in excess of the eight hours allowed by 10CFR50.72(b)(3)(xiii). The Plant Computer system supplies the Safety Parameter Display System (SPDS) function, which is required for Emergency Assessment Capability. The Plant Computer is currently operable." "This event did not effect the plant operations. The unit is stable in Mode 1 at 100% power." "The NRC Resident inspector has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-21
41508 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-03-21 10:45 | 2005-03-21 12:20 | 2005-03-21 | OFFSITE NOTIFICATION TO DERM ABOUT FUEL OIL SPILL On 3/21/05 at 1045, the Control Room was notified of a fuel oil spill. The event was believed to have occurred on Saturday, 3/19/05 between 1900 and 0300. The amount of fuel oil ( Grade 2 Diesel) that was spilled was approximately 219 gallons and dispersed over a distance of about 1 mile. The cause of the spill was possibly due to a valve left open on the tanker after making a fuel delivery. The long trail of oil was made as the tanker left the site. The spill is contained and being cleaned up at this time. The area will be excavated and transported to Redland Construction. The location of the fuel oil spill occurred outside of the Nuclear Plant protected area at the new fossil plant. Construction site. DERM (Department of Environmental Resources Management) will be notified by Turkey Point Land Utilization representative. The NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-21
41507 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-03-11 13:00 | 2005-03-21 08:50 | 2005-03-21 | POSSIBLE MEDICAL MISADMINISTRATION A prostate implant patient at Marietta Memorial Hospital was to have received 98 Iodine-125 seeds, 0.310 millicuries per seed, but instead received 83 iodine-125 seeds and 15 palladium-103 seeds, 1.2 millicuries each (palladium-103 is accelerator produced). The patient received 98% of the planned dose. The holders for the iodine-125 seeds and the palladium-103 seeds are similar in shape and size. The State of Ohio Bureau of Radiation Protection received the above information on 03/16/05 around 1300 hours. The Ohio Bureau of Radiation Protection is investigating this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-03-24
41506 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-03-20 22:30 | 2005-03-21 03:35 | 2005-03-21 | PRESSURE BOUNDARY LEAKAGE DISCOVERED DURING HYDRO TEST The following information was obtained from the licensee via fax (licensee text in quotes): "At 22:30 on 3/20/2005, the Control Room was notified by the test director that ASME CLASS I Boundary System Leakage Hydrostatic Pressure Test (SE-200-002) had failed. The reason was a leak identified on Reactor Recirc Pump B Discharge Valve, HV243F031B. The leak is coming from the Stub Tube Weld Leakoff Connection for the valve. It is leaking approx. 10 drops per minute. Technical Requirement 3.4.2 was entered. It was determined to be unacceptable under the ASME Section XI Code. Based on guidance provided in NUREG-1022, Rev. 2, this material defect in the primary coolant boundary constitutes a seriously degraded condition and is reportable under 10CFR50.72(b)(3)(ii)(A). A final evaluation of the flaw and a repair plan is being developed." The NRC Resident was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-03-21
41505 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-03-19 08:27 | 2005-03-19 12:27 | 2005-03-19 | OFFSITE NOTIFICATION DUE TO INJURED CONTRACT EMPLOYEE The following information was obtained from the licensee via facsimile (licensee text in quotes): "South Texas Project Nuclear Operating Company has been in contact with various news agencies following an industrial accident that occurred at 0827 this morning. A contract employee fell approximately eight to ten feet while descending a permanent plant ladder on a structure in the secondary plant. The individual sustained injuries to his head and back, and has been transported to Herman Hospital in Houston, TX by a Life Flight Helicopter. "The NRC Regional Office has been informed." The individual was conscious and in stable condition when he left the facility. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-19
41504 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2005-03-19 01:30 | 2005-03-19 02:12 | 2005-03-19 | ADVANCED NOTIFICATION PRIOR TO TAKING SPDS OUT OF SERVICE At 01:30 CST the Safety Parameter Display System (SPDS) will be taken out of service for planned maintenance. This planned maintenance is scheduled for approximately four hours. ANO Unit-2 is currently in a refueling outage with the reactor defueled. The licensee notified the NRC Resident Inspector and the Arkansas Department of Health. * * * UPDATE PROVIDED BY OLSON TO ABRAMOVITZ @ 1102 3/19/2005 * * * SPDS restored at 09:40 CST. Resident Inspector will be notified by the licensee. Notified R4DO (FARNHOLTZ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-19
41503 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2005-03-18 14:00 | 2005-03-18 19:37 | 2005-03-18 | OTHER UNSPECIFIED REQUIREMENT - LICENSE CONDITION 2.C The following information was obtained from the licensee via facsimile (licensee text in quotes): "Report of a violation of the Technical Requirements contained in section 2C of the operating license, which requires initial notification within 24 hours to the NRC via the ENS with written follow-up within 30 days. "A recent failure of the 'A' CRD pump to start required maintenance on an associated local shutdown panel. Troubleshooting indicated that a relay associated with the panel was the cause of the breaker for the pump to not be set up for a remote start from the control room. The relay in question malfunctioned on Feb. 17th so the 'A' CRD pump was not available since that time. The failure of this pump requires entry into a 7-day shutdown LCO. Troubleshooting, indicated there is firm evidence that this condition, which is prohibited by technical specifications, existed before the discovery on 3/16/5. A 7-day LCO was entered upon discovery and repairs have been completed and the LCO exited." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2005-03-18
41502 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2005-03-18 15:00 | 2005-03-18 17:51 | 2005-03-18 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE DIESEL GENERATOR The following information was obtained from the licensee via facsimile (licensee text in quotes): "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 18, 2005, at approximately 15:00 hours Mountain Standard Time (MST), Palo Verde Nuclear Generating Station (PVNGS) Unit 1 commenced a reactor shutdown required by Technical Specification 3.8.1. "Limiting Condition for Operability (LCO) 3.8.1 requires two diesel generators (DGs) each capable of supplying one train of the onsite Class 1E AC Electrical Power Distribution System be available. On March 17, 2005, at approximately 04:11 MST, Unit 1 Diesel Generator "A" failed to start during its post maintenance retest. The diesel generator (DG) tripped on incomplete sequence. Prior to tripping, the DG reached approximately 100 rpm for fifteen seconds. "It has been determined that the cause of the DG failure was due to a governor failure. The failed governor has been replaced. At 17:50 on March 17, 2005, DG "B" was tested satisfactorily to confirm there is not a common cause failure. Unit 1 is being shutdown because the retest of DG "A" requires the Unit to be in Mode 5. The LCO 3.8.1 would expire at 04:00 MST, March 19, 2005 requiring initiation of Shut Down required by Technical Specifications if no action was taken. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified." At the time of the notification, power was 70% and was being reduced in preparation for reactor shutdown to Mode 3. | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-03-18
41501 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2005-03-17 12:00 | 2005-03-18 11:30 | 2005-03-18 | ARGEEMENT STATE MEDICAL EVENT The following information was provided by the State via e-mail (State text in quotes): "At 2 PM on March 17, 2005, the Swedish Medical Center, Radiation Safety Officer reported that an incident occurred at 12 PM, March 17, due to a clogged filter in the i.v. tubing used to administer an Iodine 131 radioisotope. The clog occurred during the procedure and prevented the administration of the total prescribed dose. "The dosimetric protocol of the I-131 administration requires a 'cold' infusion of AntiB Antibody prior to radioisotope administration. This cold administration needs to pass through a 0.22 micron filter. The manufacturer's protocol states that the radioisotope should also be administered through the filter. The protocol further indicates that if the filter clogs, that the remainder of the radioisotope is administered without the presence of the filter. "When the filter clogged, the nuclear medicine technologist first attempted to flush the clog with saline and then bypass the filter to complete the administration. After the administration it was determined by dose calibrator that 43.7 MBq (1.18 mCi) of I-131 was trapped in the tubing behind the filter. The actual administered activity was about 146.2 MBq (3.95 mCi) of the prescribed 185 MBq (5 mCi) dose. "Corrective Actions: Since the preliminary investigation indicates the cause of the misadministration was due to clogging of the filter, the Radiation Safety Officer has recommended immediately bypassing the filter during administration instead of attempting to unclog it. The RSO plans to contact the vendor to get a protocol clarification and will include that information in the formal written report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2005-03-23
41500 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2005-03-17 17:55 | 2005-03-17 21:45 | 2005-03-17 | OTHER UNSPECIFIED REQUIREMENT - LICENSE CONDITION 2.F The following information was obtained from the licensee via facsimile (licensee text in quotes): "This notification is being made in accordance with License Condition 2.F for Nine Mile Point Unit 2 which states in part 'report any violations of the requirements contained in Section 2.C of this license in the following manner: initial notification shall be made within 24 hours to the NRC Operations Center via the Emergency Notification System, with written follow-up within 30 days in accordance with the procedures described in 10 CFR 50.73(b), (c), and (e).' License condition 2.C (2) states in part 'Nine Mile Point Nuclear Station, LLC shall operate the facility in accordance with the Technical Specifications.' "Earlier this year Operations was notified by Engineering that a portion of the procedural guidance contained in the Operating Procedure for Standby Gas Treatment System (SGTS) would render an operating SGTS sub-system inoperable during certain evolutions (e.g. Primary Containment Purge). Specifically when the filter train's recirculation valves are taken out of the automatic mode of operation, the subsystem's ability to drawdown the Secondary Containment within the required time and maintain less than 1/4" W.C. vacuum cannot be assured. "In accordance with the guidance provided in NUREG-1022, an extensive review of the operation of the SGTS system over the past 3 years was performed. This review identified two (2) instances where, if a SGTS subsystem(s) had been declared inoperable as required, one or more Technical Specifications would have been violated. For example: on 3/15/2002 one SGTS subsystem was being utilized for Primary Containment Purge evolutions (and as such inoperable) and the opposite Division's EDG was simultaneously inoperable for pre-planned maintenance for greater than 4 hours. Technical Specification 3.8.1 Condition B.2 requires declaring required feature(s), supported by the inoperable DG, inoperable when the redundant required feature(s) are inoperable (i.e. the non-running SGTS subsystem). This was not recognized and the requirement to initiate a plant shutdown per LCO 3.0.3 was not performed. The second instance occurred in November of 2002 and was similar to the first occurrence. Following the identification of these occurrences Engineering performed an analysis of actual plant data to confirm inoperability of SGTS. "The example noted above and the others identified will be explained in detail in the follow-up LER that will be submitted as required by 10CFR 50.73(a)(2)(i)(B) - 'Any operation or condition which was prohibited by the plant's Technical Specifications.'" The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2005-03-17
41499 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-03-16 09:43 | 2005-03-16 19:55 | 2005-03-16 | HIGH PRESSURE CORE SPRAY SYSTEM INOPERABLE DUE TO DEGRADED PUMP MOTOR AIR DEFLECTOR The following information was provided by the licensee via facsimile (licensee text in quotes): "At 0943 with Columbia Generating Station operating at 100% power the High Pressure Core Spray (HPCS) system was taken out of service for maintenance. During the maintenance activity, severe cracking and degradation was discovered on the upper air deflector of the HPCS pump motor. This component functions to direct air into the motor housing to provide cooling while the system is operating. A preliminary evaluation determined this represents a condition that at the time of discovery could have prevented fulfillment of the safety function of the HPCS system to mitigate the consequence of an accident and is reportable pursuant to 10 CFR 50.72(b)(3)(v)(D). Upon discovery of this condition plant operators fulfilled the action required by Technical Specifications LCO 3.5.1 condition B to verify by administrative means that the Reactor Core Isolation Cooling (RCIC) system is operable and took action to restore the HPCS system to operable status within 14 days. No other systems were required to function in response to this event." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-16
41498 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-03-16 05:40 | 2005-03-16 10:22 | 2005-03-16 | DISCOVERY OF AFTER-THE FACT EMERGENCY CONDITION UNUSUAL EVENT The licensee provided the following information about the event via facsimile (licensee test in quotes): "On 3/16/2005 at approximately 0540 preparations were being made to drain down the RCS. A tagout needed to be released to support aligning the RCS for drain down. The tagout was not completely released prior to opening the intermediate leg loop drain valves. When the intermediate leg loop drain valves were opened, a flow path was created which resulted in draining the RCS. The Control Room noted approximately 70 gpm mismatch between letdown flow and charging. Personnel in containment manipulating the valves discovered that water was flowing unexpectedly to a trough in containment when they went to position the last set of intermediate leg loop drain valves and they quickly isolated the flow path. The time frame that the flow path existed was approximately 10 minutes. When the Shift Manager evaluated the event for Emergency classification the flow path had been isolated. The Shift Manager was not clear on if this event met the guidance for an NOUE declaration and asked for assistance from the Outage Control Center. Corporate licensing and Emergency preparedness were contacted for additional assistance. "At 0930 it was decided to report the event per 50.72 (a) General Requirements even though it is not clear that the threshold for an EAL was met. Per NUREG-1022 the NRC staff does not consider actual declaration of the Emergency Class to be necessary when the event has rapidly terminated and the basis for the emergency class no longer exists." The licensee stated that the threshold for an Unusual Event declaration per the Vogtle EALs is 25 gpm identified RCS leakage. The NRC Resident Inspector has been notified as well as courtesy notifications to state and local authorities. * * * UPDATE TO NRC (HUFFMAN) FROM LICENSEE (DORMAN) AT 10:58 ON 3/16/05 * * * After further consideration, the licensee decided that this event should have been classified as an Unusual Event at the time of the occurrence. The licensee will notify the NRC Resident Inspector of this classification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW | [5 empty] | 0 | 2005-03-16
41497 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2005-03-15 18:51 | 2005-03-15 23:07 | 2005-03-15 | OFFSITE NOTIFICATIONS DUE TO CAUSTIC SPILL The following information was provided by the licensee via facsimile (licensee text in quotes): "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 15, 2005 at approximately 18:51 Mountain Standard Time (MST), the Palo Verde Nuclear Generating Station informed another government agency, the EPA/DOT National Response Center, of a caustic spill, related to the protection of the environment. Notification was also made to the Arizona Department of Environmental Quality and the Arizona Department of Public Safety (State Police). No news release is planned or expected. "A commercial tanker truck was transferring caustic sodium hydroxide at Unit 1 when a drip was observed from the transfer hose at approximately 16:54 MST. The spill was limited to approximately one quart outside of the spill containment berm. The evolution was terminated and the tanker truck was driven out of the Protected Area. "A drip trail was later discovered at approximately 18:00 along the path of the truck out of the Protected Area, including a puddle of approximately 3 gallons in the sally port (access point). The truck was returning to Phoenix, AZ. The spill quantity on-site is not estimated to have approached a reportable quantity (1,000 pounds), but due to the evidence that the truck was leaking while in transit to Phoenix, the Palo Verde Hazardous Materials Emergency Coordinator conservatively elected to make the government notifications. Additionally, Palo Verde notified the trucking company which ultimately located the truck upon its return to the company yard. No leak existed at that time, suggesting the leakage was limited to the caustic that remained in the truck's discharge pipe after the transfer was stopped. "There was no impact to control room habitability and no safety systems, including essential ventilation, were actuated or required. The spill did not hamper site personnel in the performance of duties necessary for the safe operation of the nuclear power plant. "The NRC Resident inspector was notified of the chemical spill and this ENS notification." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-15
41496 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-03-15 16:30 | 2005-03-15 22:48 | 2005-03-15 | KEWAUNEE PLANT DESIGN FOR FLOODING EVENTS MAY NOT MITIGATE THE CONSEQUENCES OF PIPING SYSTEM FAILURES The following was provided by the licensee: "While reviewing Nuclear Regulatory Commission's (NRC) memorandum regarding Task Interface Agreement (TIA), TIA 2001-02,'Design Basis Assumptions For Non-Seismic Piping Failures at Prairie Island Plant,' Kewaunee staff determined that the Kewaunee plant design for flooding events may not mitigate the consequences of piping system failures. As a minimum, and as a consequence of assuming failure of non-seismically qualified piping systems as prescribed in the TIA, water has been assumed to collect in the turbine building from a circulating water system piping failure that would result in substantial damage to Engineered Safeguards (ESF) and Safe Shutdown (SS) plant equipment, most notably electrical equipment. As a consequence of high water level in the turbine building, water could flow into the ESF equipment rooms that contain the Auxiliary Feedwater pumps, Emergency Diesel Generators and both the 480 volt and 4160 volt electrical switchgear. Water is assumed to flow into the equipment rooms by way of leakage past non-water-tight doors and the plant's unchecked floor-drain system. The expected water levels In the safeguards and electrical equipment rooms are assumed to increase to the point of causing multiple trains of both ESF and SS equipment to be unavailable to safely shutdown the plant." "Kewaunee's primary mitigation strategy to combat flooding events is to recognize the event and initiate manual actions to open doors/ barriers. Opening the barriers to flooding directs the water out of the turbine building through the safeguards equipment rooms and returns it to the lake. Normally the manual actions would be expected to be performed before water level accumulates to a point of causing equipment damage. However, under the seismic failure assumptions, water levels are assumed to accumulate faster than the plant's ability to identify and react in order to assure protection of equipment required to initiate and complete a safe plant shutdown. "Coincidental to the condition being reported, the plant had recently implemented additional precautionary measures to combat internal flooding events that lesson the significance of the condition being reported. Temporary pumping equipment, temporary sandbag barriers and additional personnel have been staged to minimize the consequences of previously questioned flooding events. Furthermore, a number of plant equipment design changes are being processed to further improve Kewaunee's defenses against internal flooding events. However, given the event being reported, the full scope of any additional actions is still to be determined." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2005-03-15
41495 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-03-14 09:30 | 2005-03-15 17:03 | 2005-03-15 | AGREEMENT STATE REPORT - CONTAMINATED DIAPER PLACED IN REGULAR TRASH The following information was provided by the State via email (State text in quotes): "On March 14, 2005 BFI returned a compactor/dumpster to Renaissance Hospital because of radiation detector alarms. After surveying the entire container, one area was reading 9 mR/hr on contact. The trash from this area was again surveyed. A diaper from a patient that had received an I-131 iodine therapy treatment was accidentally put in the regular hospital trash for immediate disposal. The diaper has been removed from the dumpster and sent to the hospital's Nuclear Medicine department for decay. The dumpster was again surveyed after removing the diaper and there were no dose rates above background found. The diaper was reading 10 mR/hr on contact. The diaper was again surveyed on 3/15/05. It was reading 5 mR/hr on contact with a 1 foot reading of 2 mR/hr." Texas Incident No. I-8220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-03-18
41493 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2004-09-30 | 2005-03-15 17:02 | 2005-03-15 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The following information was provided by the State via facsimile (State text in quotes): "Isolite/Safety Light shipped two exit signs [Serial Nos. 281266 and 2181268], model SLX60 with 9.5 curies [each] of H-3 on September 1, 2004 to Wave Form Specialists via General Electric Supply. The signs were to be installed in a new facility for the City of Omaha at 4001 South 120th St, as the end user. Wave Form Specialist never installed the signs. Wave Form Specialists declared bankruptcy in September. Wave Form was bonded and another company finished the electrical contract work. The bonding company and the electrical contactor never found the signs when they took over the job. The signs were not returned to Isolite. Have not been able to contact owner of Wave Form Specialists." Nebraska Incident No: NE050004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2005-03-18
41492 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-03-14 11:25 | 2005-03-14 19:37 | 2005-03-14 | FITNESS FOR DUTY REPORT A non-licensed employee was determined to be under the influence of illegal drugs during a random test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2005-03-14
41491 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-12-20 | 2005-03-14 12:41 | 2005-03-14 | TEXAS AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURES The following is a summary of a report submitted by the State of Texas to the NRC via email: On January 11, 2005 the licensee [Testmasters, Inc.] was notified by their Atomic Energy Industrial Laboratory that two Testmaster employees had received high doses on their 11/20/04 through 12/19/04 film badges, i.e., 7,035 mRem and 950 mRem. The licensee initiated an investigation and determined that both individuals had performed an adjustment of the collimator on the 117.8 curie AEA Model 424-9 Ir-192 camera, S/N B1831, after cranking in the source following a shot. Neither individual had a survey meter when they approached the camera for the collimator adjustment. A subsequent review of their pocket dosimeters showed a "high off-scale" reading which was not reported to the company RSO. The State cited the licensee for six violations of their TX license. Texas Incident No. I-8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-03-17
41490 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-10-31 | 2005-03-14 16:44 | 2005-03-14 | AGREEMENT STATE REPORT - UNEXPLAINED EXPOSURE DOSE The following is a summary of a report submitted by the State of Texas to the NRC via email: A radiographer employed by Texas Gamma Ray, LLC received an unexplained dose of 6730 mrem during the month of October 2004. Additional dose reported for the month of November 2004 increased the annual accrued dose for the year 2004 to 7780 mrem which exceeds the yearly occupational dose limit [5 Rem]. The licensee [Texas Gamma Ray, LLC] immediately informed the State of the overexposure via telephone and initiated an investigation. The investigation determined through interviews with the radiographer and a review of his October work assignments that he had dropped his film badge near a radioactive source (approximately 1 meter distance from a camera containing 30-40 Curies Ir-192) for about thirty minutes to an hour. The radiographer did not report the incident at that time or in his written statement describing his work activities. The licensee noted during their review of the monthly dosimetry monitoring reports provided by Atomic Energy Industrial Laboratory that two of the three individuals assigned to work with this radiographer wore spare film badges. The State cited the licensee for eleven violations of their TX license. Texas Incident No. I-8190. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-03-17
41489 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-03-14 10:17 | 2005-03-14 13:38 | 2005-03-18 | OFFSITE NOTIFICATION OF SODIUM HYPOCHLORITE SPILL The following information was obtained from the licensee via facsimile (licensee text in quotes): "This is a 4-hour notification to report a sodium hypochlorite spill from a pipe flange elbow on the permanent sodium hypochlorite tank to the ground at Salem generating station. The spill was over an excavation trench that was filled with rain water. The trench was being pumped to the nearest manhole. Maintenance personnel noticed a 2 drops per second sodium hypochlorite leak from the elbow. The operations shift manager made a 15-minute report to the State of New Jersey to report the spill. The sodium hypochlorite tank was out of service at the time undergoing corrective maintenance. The spill has been contained. Chemistry samples are being taken to determine if any reportable quantities were pumped to the nearest manhole. There was no effect on plant operation since the tank was out of service. Actions include follow up samples and if necessary remediation of the ground soil. There was no one injured during the event." The licensee notified State and local authorities and the NRC Resident Inspector. * * * RETRACTION FROM S. SAUER TO W. GOTT AT 2037 ON 3/18/05 * * * The following information was obtained from the licensee via facsimile (licensee text in quotes): "On March 14, PSEG reported to the NRC that Report had been made to the New Jersey Department of Environmental Protection regarding a spill of sodium hypochlorite (Event No. 41489). As the spill was cleaned up within 24 hours and there was no direct discharge to the Delaware River, this report has been retracted from the State of New Jersey. Chemistry samples taken indicated no reportable quantities pumped to the river. Ground water was pumped from the excavation to a concrete diked area and the excavation flushed with fresh water until chemistry samples indicated no residual sodium hypochlorite. This EVENT is retracted." The licensee will notify the NRC Resident Inspector. Notified R1DO (L. Doerflein) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-14
41488 | 0 | DC DEPT OF TRANSPORTATION |  |  |  |  | 2005-03-01 | 2005-03-14 13:13 | 2005-03-14 | DISTRICT OF COLUMBIA DEPARTMENT OF TRANSPORTATION REPORTED A TROXLER MOISTURE DENSITY GAUGE WAS FOUND MISSING DURING INVENTORY The licensee reported that during inventory an old (20 years old) Troxler gauge model 3411-B serial # 7520 was found missing from its case which was stored in the storage area at their office. This gauge had not been used for a number of years since it was broken. It contains 8 millicuries Cs-137 and 40 millicuries Am-241-Be. The last inventory was 12/06/04 and at that time it is believed the device was in the case, but they are not sure the case was opened to verify. They are continuing the search and have reported it to the DC Police Dept (report # 029650). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-03-14
41487 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2005-03-12 18:30 | 2005-03-13 00:18 | 2005-03-13 | PINHOLE LEAK IN INSTRUMENT DRAIN LINE OFF MAIN STEAM SYSTEM The following was provided by the licensee: "This report is being made pursuant to 10CFR50.72(b)(3)(ii)(A). At 1830 on March 12, 2005, during the U-2 vessel pressure test, a leak was identified on the 2B21-F028D. The drain piping weld had pinhole leaks at the weld with a leak rate of 60 drops per minute. Due to welding or material defects in ASME Class 1 components, Technical Requirement Manual 3.4.a., condition A was entered. The component was isolated and corrective actions are in progress to repair the leakage. Repairs will be completed and tested prior to startup." The valve 2B21-F028D is located in the Main Steam system downstream of the outboard main steam isolation valve. The leaking weld is the connecting weld of the valve body to the drain line. There was no prior history of repair on the valve or weld from the last outage. The licensee stated no indication was present to indicate the valve was leaking steam during normal operation. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-03-13
41486 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-03-12 18:45 | 2005-03-13 00:10 | 2005-03-13 | LOSS OF OPERABILITY OF ONE EMERGENCY EVACUATION SIREN The following was provided by the licensee: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 12, 2005 at approximately 18:45 Mountain Standard Time, the Palo Verde Emergency Preparedness Program Manager was notified of an inoperable single siren #36. Palo Verde has had 4 other sirens vandalized by breaking locks and stealing the internal battery since approximately February 25, 2005. The specific cause of this siren being inoperable has not been determined. Based on evidence from previous testing, this loss of siren #36 has been established to have occurred sometime between 22:00, Friday, 03/11/2005 and 03:00, Saturday, 03/12/2005. The affected siren is estimated to impact approximately 82 members of population (5.1 %) in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles (or 10% within 5 to 10 miles) for greater than 1 hour. This call is being placed due to the relatively large segment of the population affected and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "Palo Verde has also been informed that Siren #42, previously inoperable due to the same vandalism and reported in EN #41451 on February 28, 2005, has been returned to service. There are no events in progress that require siren operation. There was not anything unusual or not understood concerning this event and all systems functioned as required. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." The licensee will inspect the siren on Sunday or Monday to determine if vandalism is involved. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-13
41485 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-03-10 12:00 | 2005-03-12 01:14 | 2005-03-14 | AGREEMENT STATE REPORT - POTENTIAL OVEREXPOSURE DURING RADIOGRAPHY Initial report made by licensee to the State of California at 1330 PST on 03/11/05 via voicemail: While performing radiography at the BP Refinery located in Carson, CA, a radiography camera source was not fully retracted while disconnecting the guide tube. The camera was an INC Model IR100 Serial #4043, which contains a 90 Curie Iridium-192 source. After performing several operations of the radiography camera (approximately 10 shots) the radiographer approached the camera without his survey instruments. After disconnecting the guide tube, it became apparent to the radiographer and his assistant that there was a problem since their survey instruments were off scale, and when the radiography crew checked their pocket reading dosimeters, they were off scale also. The radiographer used pliers to force the source into the shielded position and secure the camera. The licensee estimates that the radiographer received 1800 millirem whole body, 212 Rem to the hands, and the assistant received 2766 millirem whole body. There are no reported physical manifestations from the exposure at this time. The corporate RSO is flying to the scene of the incident to reenact the events for their investigation. The personal dosimetry for both operators has been sent for processing. The camera will be sent to the manufacturer for evaluation and repair. The State of California will be conducting their own investigation into the event. * * * UPDATE FROM CALIFORNIA (SALGADO) TO M. RIPLEY AT 1510 EST ON 03/14/05 * * * The following information was obtained from the State via facsimile (State text in quotes): "3/14/05, 1030 [PST]: Update, licensee is reporting that dosimetry for involved individuals has been processed with results as follow: radiographer shows 1.6 rem, whole body. Assistant shows 2.7 rem, whole body. No physical manifestations displayed at this time. Preliminary written report from licensee pending." No further information available at this time on refinements to the extremity dose estimates. Notified R4 DO (T. Farnholtz) and NMSS EO (T. Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-03-16
41483 | 0 | ST. JOHNS MERCY MEDICAL CENTER |  |  |  |  | 2005-03-09 08:35 | 2005-03-11 17:24 | 2005-03-11 | INCORRECT DOSE GIVEN TO AN INFANT A 5 month old infant was to have received 0.5 millicuries of technetium-99 myoview sulfur colloid but instead received 11.6 millicuries of technetium-99 myoview sulfur colloid. Person did not look at the label when measuring the dose to be given to the 5 month old infant. Calculated whole body dose to the infant ranges from 1.0 to 10 rem (most likely between 5.2 and 10 rem whole body dose to the infant) . No adverse reaction to the infant due to receiving 11.6 millicuries of technetium-99 myoview sulfur colloid. Physician has talked to the parents of the infant. Licensee looking into what corrective actions to take in order to prevent this same incident from happening in the future. A written report will be issued. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-03-11
41482 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-03-11 14:29 | 2005-03-11 17:06 | 2005-03-11 | IT WAS DETERMINEDED THAT GREATER THAN 1% OF INSPECTED S/G TUBES MUST BE REPAIRED. "As part of the Cycle 6 refueling outage, inspections are being performed in accordance with Technical Specification (TS) 5.7.2.12, 'Steam Generator (SG) Tube Surveillance Program.' Based on a review of the inspection results to date, it was established at approximately 14:29 EST on March 11, 2005, that greater than 1 percent of the inspected SG tubes must be repaired. In accordance with the criteria stated in TS 5.7.2.12 and the inspection findings, the four SGs must be classified as C-3. The current inspection results do not meet the criteria specified for steam generator tube degradation in Revision 2 of NUREG 1022, 'Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73.' However, for the C-3 classification, WBN TS Table 5.7.2,12-1, 'SG Tube Inspection Supplemental Sampling Requirements,' requires that the results of the inspection be reported under 10 CFR 50.72. At this time, the submittal of a Licensee Event Report in accordance with 10 CFR 50.73 is not planned." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2005-03-11
41481 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-03-10 16:45 | 2005-03-10 19:06 | 2005-03-10 | STOLEN TROXLER GUAGE The licensee had a Troxler gauge model 3400 serial # 31101 with 8 millicuries Cs - 137 and 40 millicuries Am - 241:Be stolen from their storage building on their parking lot in Miami. The theft was considered a general burglary and was given a Miami Dade police report number of 7088G-D. No reward notice has yet been made. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-03-15
41480 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-03-10 15:45 | 2005-03-10 18:15 | 2005-03-10 | OFFSITE NOTIFICATION TO GOVERNMENT AGENCIES DUE TO OIL SPILL "At approximately 15:45 a hydraulic line ruptured on a 90-ton mobile crane located outside of the Unit 2 Turbine Building. Approximately 50 gallons of hydraulic oil leaked onto the surrounding pavement. Barriers and absorption materials were positioned around the spill area and no oil was released to soil or the river. "Required offsite notifications included the NYS Department of Environmental Conservation and the Westchester County (NY) Department of Health." The licensee notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-10
41479 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-03-10 11:00 | 2005-03-10 16:09 | 2005-03-10 | CONTRACTOR SUPERVISOR FOUND POSITIVE FOR ILLEGAL DRUGS DURING A PRE-ACCESS DRUG TEST A contractor supervisor was determined to have been under the influence of an illegal drug during a pre-access drug test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2005-03-10
41478 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-01-26 | 2005-03-10 10:18 | 2005-03-10 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was provided by the licensee to the State of Louisiana (licensee text in quotes): "The following incident took place on 1/26/05 in the Tulane Hospital/Clinic Nuclear Medicine area. " A patient was to be administered 5[milliCuries] of I-131 for a total body scan in order to look for thyroid metastases. Due to an error in transcription of the order, a student technologist injected a 27 [millicuries] Tc-99m MDP bone scan. The resulting Effective Dose Equivalents were 0.675 rad to the bone and 0.189 rad to the total body. "The patient was notified of the error and the correct radiopharmaceutical later administered. The senior technologist was reprimanded by the Radiology Department Head for not properly supervising the procedure." The physician was notified. The State of Louisiana Department of Environmental Quality will be conducting their own investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-03-15
41477 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2005-03-09 | 2005-03-09 20:36 | 2005-03-18 | PLANNED LOSS OF THE EMERGENCY RESPONSE DATA SYSTEM The following information was obtained from the licensee via e-mail (licensee text in quotes): "On Thursday, March 10, 2005 San Onofre Nuclear Generating Station, Unit 2, will remove a portion of the Safety Parameter Display System (SPDS) and the Emergency Response Data System (ERDS) from service for a planned upgrade to ensure long-term reliability and improve the human-machine interface. This work is expected to complete within seven days. "The SPDS emergency assessment function at San Onofre is implemented by a combination of the Qualified Safety Parameter Display System (QSPDS) and the Critical Function Monitoring System (CFMS). The QSPDS portion, which provides emergency assessment capability to plant operators in the control room, will remain functional. The CFMS portion, which receives input from the QSPDS, implements the ERDS and communicates data to the Technical Support Center and Emergency Offsite Facility. Only the CFMS and ERDS are impacted by this upgrade. "This planned CFMS outage is being reported in accordance with 10CFR50.72(b)(3)(xiii) as a courtesy notification even though only a portion of the SPDS will be removed from service and preplanned compensatory measures will be in place for the duration of the work. "At the time of this report, Unit 2 and Unit 3 were operating at about 79 percent and 99 percent power, respectively. "The NRC Resident Inspectors will be notified of this occurrence and will be provided with a copy of this report." Should an emergency event occur, the licensee intends to transmit emergency response data to the NRC via facsimile and voice via the emergency notification system. No electronic data will be sent to the NRC Operations Center for the outage duration. * * * UPDATE FROM CLAY WILLIAMS TO HOWIE CROUCH ON MARCH 18, 2005 @ 1551 EST * * * "The CFMS upgrade work was completed on March 17, 2005 at 2310 PST. The SPDS and ERDS have been returned to service." The licensee has notified the NRC Resident Inspector. Notified R4DO (Farnholtz). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-09
41475 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2005-03-09 13:04 | 2005-03-09 16:40 | 2005-03-09 | OFFSITE NOTIFICATION DUE TO INVESTIGATION OF INADVERTENT SIREN ACTIVATION The following information was obtained from the licensee via facsimile (licensee text in quotes): "On Tuesday 3/8, a local radio station carried a message about inadvertent siren soundings on the previous weekend. Neither the Arkansas Department of Health (ADH) staff nor ANO EP staff received any notifications relative to the inadvertent sounding or the number or location of the sirens. The ADH considers the sirens to be operable. A possible cause was reported as loss of electric service in some areas. ANO has some history that indicates power surges may cause inadvertent actuation of the sirens." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-09
41474 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-11-30 10:00 | 2005-03-09 11:18 | 2005-03-09 | TEXAS AGREEMENT STATE - RECOVERED RADIOACTIVE MATERIAL The following information was provided by the Texas Department of State Health Services [DSHS]: At approximately 10:00 am, November 30, 2004 a tractor-trailer alarmed radiation monitors with a load of scrap steel at Commercial Metals Austin [CMC - Austin] scrap yard. Earth Tech, Inc. in San Antonio was notified by ThermoMeasuretech for help with a possible source. Commercial Metals confirmed the load triggered a scale-mounted radiation detector at SMI- Texas, Sequin, TX and the [CMC - Austin] driver had returned the load to Commercial Metals-Austin. Earth Tech contacted [CMC - Austin] warehouse manager and noted that he had indeed isolated the source from the load and that he had roped off a 2 mR/hr barrier around the affected area. He stated that he needed additional instrumentation as his Ludlum model 19 was reading off-scale. Personnel from the Earth Tech office in San Antonio were deployed with a SAMS unit and a Ludlum model 9. They arrived at [CMC - Austin] at 1:30 pm. Searching through a small amount of soil, an actual source was revealed. The source was found to be a metallic foil disk approximately 1.5 cm. in diameter. The source emissions were found to be nonisotropic, reading high levels on one side and low levels on the other. Once the source was identified and separated from the soil, the SAMS was utilized to identify the radioisotope. The SAMS identified two low-energy photo peaks and identified the source as cadmium-109. However, the spectrum showed an unusually large amount of high-end tailing with a continuum shape similar to that found from sources of high-energy x-rays. The source was shielded and transported to ThermoMeasuretech for further investigation. It was initially presumed the source was possibly an activated foil. DSHS records for this incident showed the source was 120 microCuries of Cd-109. When CMC was called on 3/8/05 to follow up on the incident, they stated that the source had been later identified as 1 milliCurie of Sr-90. This amount of Sr-90 required immediate notification. Texas Incident No. I-8187 Due to personnel changes at the Texas Department of State Health Services and Commercial Metals in late 2004, the initial report to the NRC was delayed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-03-14
41473 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2005-03-09 05:37 | 2005-03-09 09:36 | 2005-03-15 | PRESSURIZER HEATER SLEEVE LEAKAGE The following information was obtained from the licensee via facsimile (licensee text in quotes): "ANO (Arkansas Nuclear One) Unit 2 shutdown on 3/9/05 at approximately 0038 [CST] to begin the 2R17 refueling outage. While performing the Mode 3 Hot Shutdown Walk down on ANO Unit 2, evidence of leakage was discovered around three (3) pressurizer heater sleeves. The amount of leakage was minor since no indication of moisture was present and the build up of boric acid was minimal. Investigations are underway as to the repair of the affected nozzles." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 03/12/05 @ 2255 BY JAMES CRABILL TO CHAUNCEY GOULD * * * The following information was obtained from the licensee via facsimile (licensee text in quotes): " ANO Unit 2 shutdown on 3-9-05 at approximately 0038 to begin the 2R17 refueling outage. While performing the Mode 3 Hot Shutdown Walk down on ANO Unit 2, evidence of leakage was discovered around three (3) pressurizer Heater Sleeves. The amount of leakage was minor since no indication of moisture was present and the build up of boric acid was minimal. Investigations are underway as to the repair of the affected nozzles. "Update on 3/12/2005 @ 2140: During the followup inspection performed on 3-12-2005, eight pressurizer heater nozzles had evidence of boric acid leakage at the annulus between the nozzle and pressurizer. One plug was also discovered with evidence of boric acid leakage. The nozzle at this location was plugged during the late 1980's." The reactor is presently in cold shutdown. The NRC Resident Inspector was notified. * * * UPDATE FROM J. CRABILL TO M. RIPLEY 2220 EST 03/15/05 * * * The following information was obtained from the licensee via facsimile (licensee text in quotes): "Following decontamination activities performed on 3-15-2005, 1 [one] additional pressurizer heater nozzle had evidence of leakage at the annulus between the nozzle and pressurizer." The licensee notified the NRC Resident Inspector. Notified R4 DO (T. Farnholtz) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-03-09
41472 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-03-08 | 2005-03-08 13:55 | 2005-03-08 | TEXAS AGREEMENT STATE REPORT The following information was obtained via e-mail from the Texas Department of Health Services, Inspection Unit, Radiation Branch (e-mailed text in quotes): "The following is a description of the incident: Unit 10560498/10540094 went out on 02/02/05 at 19:30 hours to a temporary job site. Unit returned to the Laredo, TX facility at 16:53 hours 02/03/05. The Unit was serviced by HES [Halliburton Energy Services] employee checking out at 19:30 hours 02/03/05. The Unit was detained by Border Patrol at Freer check point with ex-employee driving Unit at 23:22 hours 02/03/05. The densometers were inventoried at the time HES recovered the Unit from the Border Patrol. "The densometers that were on the unit were: Densometer V3C- 131, Isotope Cs- 137, Activity 11.7 [milliCuries] and Densometer W2C-086, Isotope Cs-137, Activity 11.7 [milliCuries]. "After a phone call with the licensee, it turns out that the driver was an ex-employee that went into Halliburton's yard and stole a truck that was later used in an attempt to smuggle contraband thru a Border Patrol check point. The truck never crossed the Texas border. The driver was arrested after Border Patrol agents were alerted to the truck and Halliburton was immediately notified of the theft of the truck. They [HES] then sent someone to claim the vehicle and the sources. [State of Texas Department of Health] has requested a copy of the police report." Texas Incident Number I-8215. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-03-11
41471 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-08 12:30 | 2005-03-08 15:14 | 2005-03-08 | OFFSITE NOTIFICATION TO SOUTH CAROLINA DEPARTMENT OF HEALTH AND ENVIRONMENTAL CONTROL The following information was obtained from the licensee via facsimile (licensee text in quotes): "During routine test shots, a 24 Curie Iridium-192 source was stuck partially inserted in a radiography camera inside of radiography vault. The source was returned to the fully locked and shielded position in the camera at 1345 [EST]. There was no unplanned exposure to plant personnel. South Carolina DHEC [Department of Health and Environmental Control] notified at 1230 on 03/08/05." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-03-08
41470 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-03-07 22:00 | 2005-03-08 15:02 | 2005-03-08 | CALIFORNIA AGREEMENT STATE REPORT The following information was obtained from the California Department of Health Services, Radiologic Health Branch, Granada Hills (transmitted text in quotes): "Licensee reported to Radiologic Health Branch-Granada Hills (RHB-GH) that on 3/7/05 two well-logging sealed sources became stuck in a well bore at a depth of 9137 feet (top of tool string). Sources are ~35-45 feet below that. The sources involved are a 1.5 Ci Cs-137, GSR-J 1958, source and a 16 Ci AmBe-241, NSR-F 1441, source, nominal activities. For the last day the 'fishing' company, Baker Hughes, has been attempting to retrieve the sources which became detached [on] 3/7/05, [at] ~2200 [hrs. PST]. They will continue to do so but, if that's not successful, it's appearing as if the sources will be deemed irretrievable. This occurred on the 'Aera Ventura Avenue' well site, Ventura County, CA. The well is designated 'McGonigle 39.' If deemed irretrievable, the well will likely be sealed in place with a cement plug. Licensee will provide further details shortly and follow with written report." California Incident Number 0510# 030805. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-03-11
41469 | 0 | RI DEPT OF RADIOLOGICAL HEALTH |  |  |  |  | 2005-03-08 08:40 | 2005-03-08 15:03 | 2005-03-10 | AGREEMENT STATE REPORT - TRUCK CONTAINING RADIOPHARMACEUTICALS STOLEN IN MASSACHUSETTS At approximately 0840 EST on 03/08/05 a truck operated by Cardinal Health (a Rhode Island licensee) was stolen while parked and unattended at a store in Seekonk, MA. The truck contained four unit doses of Tc-99m (total of 1.2 Curies) being delivered to a client of the licensee. The Seekonk, MA Police Department was notified and an investigation is in progress. No information is available on any planned reward or press release. * * * UPDATE 0730 EST ON 3/10/05 FROM NRC REGION 1 (SHERI MINNICK) TO S. SANDIN * * * The truck was recovered in MA at approximately 2200 hours on 3/8/05. The rad material was found intact with the seals not disturbed or broken. RI Rad Health will inspect their licensee this week. Notified R1(Shanbaky), NMSS(Hickey) and TAS via email. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | RI | OTH | AGR |  |  |  |  | 0 | 2005-03-11
41468 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-03-08 04:54 | 2005-03-08 11:41 | 2005-03-08 | RHR PUMP TRIPPED DUE TO LOSS OF VALVE POSITION INDICATION The following information was provided by the licensee (licensee text in quotes) "During isolation of the 'A' Safety Relief Valve, the 12 Residual Heat Removal (RHR) Pump tripped while in service for shutdown cooling. The isolation and shutdown cooling were subsequently restored such that shutdown cooling was lost for approximately 13 minutes. "Several Control Room alarms were received at approximately 0454 [CST] while the isolation was being hung. The Control Room Supervisor investigated the alarms and the Reactor Operator identified that the 12 RHR Pump had tripped. The isolation was lifted and shutdown cooling was restored at approximately 0507 [CST]. Operators observed that reactor water temperature and level remained stable at 99 degrees F and 651 inches (above the bottom of the vessel), respectively, during the event. "The isolation being hung apparently caused a loss of position indication for the RHR pump inlet valve. With no position indication, the pump logic sensed a loss of suction flow path, which caused the RHR pump to trip. The event is under investigation. "The NRC resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2005-03-08
41467 | 0 | UNITED STATES NAVY |  |  |  |  | 2005-01-25 | 2005-03-07 13:34 | 2005-03-07 | UNRECOVERED RADIOACTIVE MATERIAL On January 25, 2005, a U.S. Navy CH-53E Super Stallion helicopter executed a forced water landing and subsequently sank off of the Virginia Cape Operations area. An in-flight safety feature onboard the aircraft, containing approximately 3500 microCuries of Strontium-90, sank with the helicopter. The U.S. Navy is planning on recovering the aircraft (and sources) when the weather becomes more amenable to recovery operations. The licensee has notified the Region 1 Division of Nuclear Materials Safety. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-03-07
41466 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-03-07 08:10 | 2005-03-07 11:49 | 2005-03-07 | TWO EMERGENCY SIRENS INOPERABLE The following information was received from the licensee via facsimile (licensee text in quotes): "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On March 7, 2005 at approximately 08:10 Mountain Standard Time, the Palo Verde Emergency Preparedness Program Manager was notified of vandalism to two sirens, #18 and #23, that resulted in the sirens being inoperable. The affected sirens are estimated to impact approximately 465 (total) members of population (approximately 29%) in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles (or 10% within 5 to 10 miles) for greater than 1 hour. This call is being placed due to the relatively large segment of the population affected, and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." The vandals cut the battery cables and removed the batteries. The theft has been reported to the MCSO. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-07
41465 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-03-06 11:40 | 2005-03-07 08:50 | 2005-03-24 | SMALL HYDROGEN FLUORIDE LEAK The following information was obtained from the Paducah Gaseous Diffusion Plant via facsimile (text in quotes); "At 1140, on 03-6-05, the Plant Shift Superintendent was notified that the C-360 Toll and Transfer Facility Zone 1 PGLD (Process Gas Leak Detection) system (Q Safety System) on # 4 Sample Cabinet actuated. The operators evacuated to the proper assembly point. The emergency Squad entered the building and sampled for Hydrogen Fluoride and sample results were positive. The autoclave and sample cabinet UF6 lines were evacuated and purged. Operators gave bioassay sample and the results indicated an uptake of Uranium. Event investigation is ongoing. "This event is reportable as a 24 hour event in accordance with the plant procedure UE2-RA-RE1030, Nuclear Regulatory Event Reporting (no 10 CFR section is referenced). An automatic or manual actuation of a Q safety system that results from an event or condition that has the potential for significant impact on the health or safety of personnel. Event having the potential for significant impact are those events where actual plant conditions existed that the system was designed to protect against. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Problem Report No. ATRC-05-0892; PGDP Event Report No. PAD-2005-07; Worksheet Responsible Division: Operations" Atmospheric leak was on line between the autoclave and the sample cabinet. C-360 Toll and Transfer Facility is a stand alone facility. Operations were secured and two individuals had uptakes (Minimal risk): One had an uptake of 7.3 mg/ liter uranium and the other individual had an uptake level of 5.2 mg/ liter uranium. The limit is 5.0 mg/ liter uranium. There was no smoke (very small leak) and a slight smell of Hydrogen Fluoride caused by the leak. * * * UPDATE 1230 EST ON 3/24/05 FROM THOMAS WHITE TO S. SANDIN * * * This report is being retracted based on the following information received from the regulatee via fax: "This report is being retracted. Subsequent analysis of the actuation determined that the PGLD head actuation occurred from a minor incidental release of UF6 from a valve packing that is not considered a breach of the pressure boundary. Reporting is required if the safety system actuates in response to a condition that the system is designed against and that could result in significant impact on the safety and health of personnel. The PGLD systems safety function, described in the PGDP accident analysis, is to mitigate pigtail/line failures outside of the autoclave that could cause offsite consequences. This incidental UF6 leak did not have the potential for significant impact on personnel or offsite consequences and is not what the safety system is designed to protect against. Thus, the reporting criteria were not met in this case. [The] resident inspector has been notified of this retraction." Notified R2DO (Ayres) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2005-03-07
41464 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2005-03-07 04:37 | 2005-03-07 06:00 | 2005-03-07 | AUTOMATIC TURBINE TRIP/ REACTOR SCRAM The following information was provided by the licensee (text in quotes): "At 0437 Unit 1 scrammed. The initiating event appears to be a turbine tripped initiated by a High level in 122 moisture separator drain tank. Investigating [the cause] of the scram will determine the actual cause." All control rods fully inserted into the core. HPCI initiated. Three relief valves lifted and reseated normally. The Reactor water clean up system is removing decay heat. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) |  |  | 0 | 2005-03-07
41463 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2005-03-06 15:00 | 2005-03-06 15:25 | 2005-03-30 | POST-ACCIDENT MONITORING INSTRUMENTATION INOPERABLE The following information was provided by the licensee via facsimile (licensee text in quotes): "At 1500, on March 6, 2005, the Control Room declared both required divisions for three functions (Primary Containment Pressure, Primary Containment Hydrogen and Oxygen Analyzer, and Drywell Atmosphere Temperature) of Post Accident Monitoring Instrumentation (a Safety System) inoperable. The control room was notified of 'Non Quality' (non-Q) parts installed in both required divisions of a Post Accident Monitoring Instrumentation Recorder. The appropriate LCO Conditions were entered for one or more functions with two required channels inoperable. This equipment has passed all surveillance requirements and has been functional since installation. "Plans are being developed to replace the non-qualified parts. "This is being reported as an event or condition that could have prevented fulfillment of a safety function required to mitigate the consequences of an accident in accordance with 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 03/30/05 @ 1128 BY JIM HUFFORD TO CHAUNCEY GOULD * * * RETRACTION The following information was provided by the licensee via facsimile (licensee text in quotes): "On March 6, 2005, PPL Susquehanna, LLC reported a perceived loss of safety function for three functions of Post Accident Monitoring Instrumentation on Unit 1. The notification was made pursuant to the reporting requirements of 10CFR50,72(b)(3)(v)(d). Engineering analysis has subsequently determined that the use of non-Q fuse holders in the Quality application did not adversely affect the safety-related functions which they supported. The fuse holders were removed, subjected to testing, and determined to be electrically and functionally equivalent 'to Quality fuse holders maintained at the station. This analysis conclusion provides the basis for retraction of the ENS report of March 6." The NRC Resident Inspector was notified. The Reg 1 RDO (Jim Trapp) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-06
41462 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-03-04 15:10 | 2005-03-04 15:44 | 2005-03-04 | UNUSUAL EVENT DECLARED The following information was obtained from the licensee via facsimile (licensee text in quotes): "At 3:10 PM EST PPL Susquehanna, LLC, declared a Notification of Unusual Event (classification OU4) for a Fire within Protected Area Boundary not Extinguished within 15 Minutes of Detection. The fire occurred in the turbine building of unit 2 which is currently in a refueling outage. Activation of the Emergency plan is reportable under 10CFR50.72(a)(3)." There were no open flames observed, only smoke. The source of the smoke was weld slag that fell into a bucket of material. Due to the temporary ventilation system installed, the smoke spread throughout the turbine building prompting the licensee to call away a fire. The licensee is investigating the area at this time. There are no personnel injuries or equipment damage at this time. The licensee will inform the NRC Operations Center when the NOUE is terminated. * * * UPDATE FROM PRESTON PRATT TO MIKE RIPLEY @ 1614 EST ON 3/4/05 * * * The licensee has terminated the Unusual Event. The source of the smoldering material was discovered and extinguished. The licensee has notified the NRC Resident Inspector. The Headquarters Operations Officer notified DHS (Frost), IRD (Wilson), NRR (Reis), FEMA (Sweitzer), and R1DO (Holody). * * * UPDATE FROM R. FRY TO M. RIPLEY 2015 EST 03/04/05 * * * "At 16:30 PM EST PPL Susquehanna, LLC, authorized a press release as a result of a Notification of Unusual Event (classification OU4) for a Fire within Protected Area Boundary not Extinguished within 15 Minutes of Detection. The fire occurred in the Turbine Building of Unit 2 which is currently in a refueling outage. The press release was issued at 17:15 EST. Any event or situation related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made is reportable under 10 CFR 50.72(b)(2)(xi)." The licensee notified the NRC Resident Inspector. Notified R1 DO (D. Holody) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Refueling; FMode2: Refueling | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2005-03-04
41461 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2005-03-04 08:00 | 2005-03-04 12:49 | 2005-03-17 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Troxler Model 3440 Moisture Density Gauge (Serial Number 35472) was stolen from a licensee's pickup truck sometime during the night or early morning of 03/03/05 - 03/04/05 while parked at a Holiday Inn Express Motel in Bend, OR. The gauge contains an 8 milliCurie Cs-137 source (Serial Number 772585) and a 40 milliCurie Am-241/Be source (Serial Number 78-408). The licensee notified the Oregon State Police and the Bend, OR Police Department. The State of Oregon has dispatched an investigator to the area and plans on issuing a press release. Oregon Incident No. RPS 05-0013. * * * UPDATE FROM STATE OF OREGON (WRIGHT) TO NRC (HUFFMAN) AT 1017 EST ON 3/17/05 * * * The Department of Radiation Protection for the State of Oregon reported that the gauge was recovered in Bend, Oregon during the evening of 3/16/05. The local Fire Department responded to a report of a yellow box along the side of a road and found the gauge and container intact and apparently undamaged. The HAZMAT team performed a survey which showed no indication of contamination. The owner has been notified and is en route to pick up the gauge. R4DO (Farnholtz), NMSS (Essig), and TAS (Foster via e-mail) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2005-03-09
41458 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2005-03-03 18:25 | 2005-03-03 19:48 | 2005-03-03 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE The following information was provided by the licensee via facsimile (licensee text in quotes): "The non-emergency 8-hour report is pursuant to 10CFR50.72(b)(3). On 03/03/05 at 1825 [EST], the Unit Reactor Operator identified the High Pressure Coolant Injection (HPCI) Flow Controller had no indication, indicating it was deenergized. With the flow controller de-energized, the HPCI system is unable to perform its design function of providing core cooling upon receipt of an initiation signal. Reactor operation is unaffected and Unit 3 remains at 100% power. The inoperability of the HPCI system places the plant in a 14 day shutdown Tech Spec action statement. Initial investigation has discovered the output of the inverter which supplies power to the flow controller (and other HPCI instrumentation) is lower than expected. Further investigation is in progress." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-03-03
41457 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-02 16:29 | 2005-03-02 20:15 | 2005-03-02 | AUTOMATIC ACTUATION OF MOTOR DRIVEN AFW PUMPS DURING OUTAGE The following information was provided by the licensee via facsimile (licensee text in quotes): "At 1629 [EST] on March 2, 2005, McGuire Nuclear Station Unit 2 experienced an automatic actuation of the 2A and 2B Motor Driven Auxiliary Feedwater (MDCA) Pumps. At the time of these actuations, Unit 2 was in MODE 3 in a refueling outage, the 2A Main Feedwater (CF) Pump was in service and, as per procedure, the 2B CF Pump was in a tripped condition and out of service. "While performing system evolutions, Unit 2 CF system pressure unexpectedly dropped to a level that caused initiation of a low CF pump suction pressure signal which tripped the 2A CF Pump. Since the 2B CF Pump had previously been placed in a tripped condition, the logic for automatic start of the 2A and 2B MDCA Pumps was satisfied and these pumps started as designed. Since the 2A and 2B MDCA Pumps started in response to actual plant conditions or parameters satisfying the requirements for initiation of the Auxiliary Feedwater (CA) System safety function, this represented a valid actuation of the CA system reportable under the requirements of 10 CFR 50.72(b)(3)(iv)(A) . "Note that the 2A and 2B MDCA Pumps started and operated normally and Unit 2 remained in a stable condition during this event. Unit 2 CF system parameters and alignments have been returned to normal for the current plant MODE and conditions. The 2A and 2B CA Pumps are now off." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-03-02
41456 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-03-02 12:39 | 2005-03-02 17:49 | 2005-03-02 | LOSS OF EMERGENCY SIRENS The following information was provided by the licensee via facsimile (licensee text in quotes): "On March 2, 2005, at approximately 1239 hours [EST], the transmitter antenna that provides the signal that activates the emergency sirens was determined to be inoperable during testing activities. This affected the system's ability to automatically activate the emergency sirens. The antenna system was restored to service at 1249 hours on March 2, 2005. All sirens re-tested satisfactorily. This event is a loss of the Emergency Notification System and is reportable under 10 CFR 50.72(b)(3)(xiii)." The equipment was repaired by replacing faulty components. Troubleshooting the failure is in progress. Sirens were last tested satisfactorily on 02/23/05. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-03-02
41455 | 0 | FRAMATOME ANP RICHLAND |  |  |  | URANIUM FUEL FABRICATION | 2005-01-27 | 2005-03-02 12:27 | 2005-03-02 | PART 21 REPORT CONCERNING MCPR LIMITS AND MCPR MONITORING On 01/27/05, Framatome ANP determined that a deviation exists in the interpolation scheme for the minimum critical power ratio (MCPR) within a range of fuel bundle flows for several operating plants. The condition could be experienced during startup, shutdown, or for other generally very infrequent reasons with core flows in the 30-45% range. The error has no impact on reactor operation above 45% flow. The defect involves the MCPR operating limit and the monitoring of that limit. The plants where the MCPR operating limit was affected are Browns Ferry Unit 3 and Grand Gulf. The plants where the steady state MCPR predicted by the monitoring system was affected are Browns Ferry Unit 3, Columbia Generating Station, Grand Gulf, LaSalle Unit 2, and River Bend. All affected plants have been notified. Recommendations for compensatory actions have been provided to those plants (Grand Gulf and River Bend) where the impact of the error is evident for current and future cycle exposures. Compensatory measures have been provided to the affected plants for use until the incore monitoring code can be updated at each plant. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | WA | FUE |  | 21.21 |  |  |  | 0 | 2005-03-02
41454 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-02-07 | 2005-03-02 11:34 | 2005-03-02 | AGREEMENT STATE STOLEN SOURCE The following information was provided by the State of Louisiana Radiation Protection Division (text in quotes): "On February 7, 2005, Dr. Khalil's Cardiology practice was broke(n) into. A 118 microcuries sealed source of Cs-137 was stolen from the lead pig at the facility. The serial number for the source is 3560380A-16. The model number and manufacturer was not reported at this time. The individual that stole the source was caught at the facility, but apparently he made [a] few trips in and out of the facility. He does not remember what he did with the source. The individual was passed out [intoxicated] at the facility when he was caught. Kilgores, Inc provides Health Physics support for the facility. He [Kilgores, Inc] did a survey of the facility and could not locate the source. This event occurred on February 7, 2005 and was reported to the Louisiana Department of Environmental Quality on March 2, 2005." LA Report Number: LA050002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-03-07
41453 | -1 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-03-01 15:45 | 2005-03-01 16:19 | 2005-03-17 | MANUAL REACTOR TRIP DURING A RAPID SHUTDOWN FOR STEAM LEAK REPAIR The following information was provided by the licensee via facsimile (licensee text in quotes): "[The licensee] reduced power on Unit 2 due to a steam leak on a moisture separator reheater vent line. The reactor was manually tripped at 20% reactor power per normal shutdown sequence. All systems and components operated correctly. Unit restart will commence following completion of a planned refueling outage." All rods fully inserted. One steam line secondary PORV lifted and reseated. Decay heat removal is via AFW and steam bypass valves to the main condenser. The steam leak was reported to be on a 2-inch MSR vent line elbow. The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM GRADY PICKLER TO HOWIE CROUCH @ 1501 EST ON 3/17/05 * * * The following information was obtained from the licensee via facsimile (licensee text in quotes): "On March 1, 2005, McGuire Unit 2 experienced a steam leak on a two-inch pipe in the heater bleed steam system. In consideration of that leak, Unit 2 was shutdown by manually tripping the reactor. This was reported as an unplanned valid actuation of the reactor protection system [10CFR 50.72 (b) (2)(iv)(B)]. Reference Event Report 41453. "The manual reactor trip of Unit 2 was not required to mitigate the steam leak. However, in consideration of the steam leak, a decision was made to perform a shutdown of Unit 2 using the normal reactor shutdown procedure. This procedure requires that the control rods be inserted by manually tripping the reactor. As per guidance provided in NUREG-1022, the above actions do not satisfy the criteria for reporting under the requirements of 10CFR 50.72 (b) (2)(iv)(B) or any other reporting criteria. Therefore, McGuire is retracting Event Report 41453." The licensee has notified the NRC Resident Inspector. Notified R2DO (Cahill). | 0 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-03-01
41452 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2005-03-01 00:43 | 2005-03-01 02:51 | 2005-03-01 | MANUAL REACTOR SCRAM FROM 15% POWER DUE TO HIGH TURBINE VIBRATION The following details were provided by the licensee via fax as part of their telephonic notification: "Manual reactor scram due to high turbine generator vibration during a planned Unit 1 power reduction to Mode 2 to perform maintenance to replace the vent line piping on 11 MSR drain tank. The manual reactor scram was initiated per AOP-7E, section V, 'High Turbine Vibration' trip criteria when bearing #5 exceeded 12 mils vibration. This event meets NUREG-1022 Rev. 2, Section 3.2.6 'System Actuation' Part 50.72(b)(2)(iv)(B) 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.'" All rods fully inserted and no ECCS or relief valve actuations occurred. Heat sink is the condenser and turbine bypass valves. The NRC resident inspector was notified. | 0 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-03-01
41451 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2005-02-28 14:57 | 2005-02-28 19:52 | 2005-02-28 | MAJOR LOSS OF SIREN COVERAGE WITHIN THE EMERGENCY PLANNING ZONE The following information was provided by the licensee via facsimile (licensee text in quotes): "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 28, 2005 at approximately 14:57 Mountain Standard Time, the Palo Verde Emergency Preparedness Program Manager was notified of vandalism to a single siren (#42) that resulted in the siren being inoperable. Based on evidence from previous testing, the vandalism has been established to have occurred sometime between 15:00, Friday, 02/25/2005 and 03:00, Saturday, 02/26/2005. The affected siren is estimated to impact approximately 116 members of the population (7.3%) in the emergency planning zone (EPZ) within 5 miles. Palo Verde's reporting criterion is a loss of capability to inform greater than 5% of the population within 5 miles (or 10% within 5 to 10 miles) for greater than 1 hour. This call is being placed due to the relatively large segment of the population affected, and the uncertainty of the length of time that will be needed to restore the siren to operable condition. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area(s) when sirens are inoperable. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-02-28
41450 | 0 | BYRON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-02-28 02:06 | 2005-02-28 17:27 | 2005-02-28 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION - UNUSUAL EVENT The following information was provided by the licensee via fax (licensee text in quotes): "At 1535 [CST] hours on 2/28/05, Byron Station determined that an emergency classification for an Unusual Event was not declared previously at 0206 [CST] on 2/28/05. The missed Unusual Event classification was due to a RCS dose equivalent I-131 value for Byron Unit 1 exceeding the EAL threshold value of >1.0 microCuries/gm [Iodine] for EAL MU7. An RCS iodine sample was taken at 0106 hours on 2/28/05 during shutdown activities for the B1R13 refueling outage. The sample was analyzed and reported back to the Operations shift at 0206 hours with a value of 1.07 microCuries/gm[Iodine]. This sample has been reconfirmed. At 0206 on 2/28/05, Byron Unit 1 was not in the mode of applicability for the RCS coolant activity Technical Specification 3.4.16. It was not recognized at that time that the EAL threshold value was exceeded until 1535 hours on 2/28/05. Note that a subsequent RCS sample taken at 0930 on 2/28/05 determined that the EAL threshold value is no longer exceeded and the current value remains less than the threshold. Byron Unit 1 has been operating the current cycle with an estimated 1-3 leaking fuel rods and special limitations were implemented by the site during shutdown. "This notification is being made in accordance with the requirements of 10 CFR 50.72(a) for a missed declaration of an Unusual Event for RCS dose EQ I-131 exceeding the EAL threshold value of 1.0 microCuries/gm[Iodine] during shutdown activities for the Byron Unit 1 refueling outage. This issue has been placed in the Byron Corrective Action Program." The licensee will notify the NRC Resident Inspector, State and Local agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2005-02-28
41449 | 0 | FOX CHASE CANCER CENTER |  |  |  |  | 2005-02-25 11:11 | 2005-02-28 15:35 | 2005-02-28 | DELIVERY OF RADIOACTIVE PHOSPHORUS (P-32) TO UNAUTHORIZED INDIVIDUAL BY FED-EX The Radiation Safety Officer (RSO) for the Fox Chase Cancer Center reported that a shipment of P-32 (3.2 millicuries based on a 2/24/05 calculated decay) was received by her that had been opened by an unknown and unauthorized individual. She stated that she had been expecting the shipment of P-32 from M.P Biomedical of Irvine CA to arrive at the Fox Chase facility on Friday 2/25/05. The RSO stated that when she received the package on 2/28/05, there was clear evidence that the package had been opened and resealed. She stated that the P-32 contents were undamaged and nothing was missing. In addition, a survey of the package showed no contamination. The RSO tracked the history of the package through Fed-Ex and determined that the package had been delivered to someone else (Contact the Headquarters Operations Officer for the name of the person) on 2/25/05 at 11:11a.m. The delivery location was listed as the address previously used by Fox Chase (although a different address it is still at the same building location). The RSO was unable to find anyone in the Fox Chase building by the name documented in the Fed-Ex tracking system. The licensee believes that this is reportable since the P-32 was unaccounted for and apparently possessed by an unauthorized individual for some period of time after 11:11a.m. on 2/25/05 such that an exposure could have resulted to persons in an unrestricted area. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-02-28
41448 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2005-02-27 15:00 | 2005-02-27 20:23 | 2005-02-27 | DEGRADED CONDITION OF REACTOR COOLANT BOUNDARY WELD The licensee provided the following information, via facsimile, about its ongoing Alloy 600 inspection: "IRE-003-574 has identified an axial flaw on line 2-LD-2004-1, 22A cold leg letdown nozzle. Engineering has evaluated the flaws using the procedures of ASME Code Section XI, IWB-3600. The calculated growth rates of the postulated axial flaws are large and do not meet the ASME Section XI Code requirements. This is reportable per NUREG-1022, Rev. 2, Sect. 3.2.4 (degraded or unanalyzed condition). 'Any event or condition resulting in the condition of the nuclear power plant, including its principal safety barriers, being serious degraded.' Unit two is in Mode 6 for refueling and a repair plan is currently being developed." The discovery of this flaw will likely result in the expansion of the inspection scope. Generic concerns for both units have not yet been fully developed by the licensee. The licensee has notified the NRC Resident Inspector. See similar event #41445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-02-27
41447 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2005-02-27 11:58 | 2005-02-27 16:29 | 2005-02-27 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF DC BATTERY CHARGERS The following information was provided by the licensee via facsimile: "A Technical Specification (TS)-required plant shutdown was initiated on Point Beach Unit 2 at 11:58 a.m. CST on February 27, 2005. The initiation of the unit shutdown was required by TS 3.8.4, Condition 13, due to the Completion Time of TS 3.8.4 Condition A not being met. Both units were operating at 100% power prior to the event. "At 09:48 CST, offsite transmission network line 151 was lost. The associated electrical transient resulted in the loss of all four required battery chargers. This condition resulted in TS 3.8.4 not being met; however, no associated Actions are provided in TS 3.8.4 for the Condition of four inoperable DC power subsystems, requiring entry of both operating units into TS LCO 3.0.3. LCO 3.0.3 specifies that action be initiated within 1 hour to shut down both units. Three of the four required battery chargers were subsequently restored to operable status by 10:00 a.m. CST. As a result, LCO 3.0.3 was exited prior to initiation of power reduction on either unit. During the 12 minutes while less than 3 battery chargers were available, the associated station DC loads were being provided by the station batteries. The DC battery drain during this time was minimal and the DC electrical subsystems remained within their analyzed condition. "At 10:00 a.m. CST, the only remaining inoperable battery charger was swing battery charger D09. D09 had been powering the D02 electrical subsystem at the time due to previously ongoing maintenance on normal battery charger D08. "The continued unavailability of D09 resulted in TS 3.8.4 not being met for both Unit 1 and Unit 2 due to D02 electrical power subsystem becoming inoperable, Required Action 3.8.4 A.1 directs restoring the electrical power subsystem to operable status with a Completion Time of 2 hours. At 11:48 a.m. CST, Required Actions 3.8.4 B.1 and B.2 were entered for both units due to the Completion Time of TS 3.8.4 Condition A not being met. This Required Action directs that the units be in Mode 3 in 6 hours and Mode 5 in 36 hours. Plant operators planned an orderly sequential shutdown of both units and initiated the process by beginning a shutdown of Unit 2 at 11:58 a.m. CST. This condition is reportable per 10 CFR 50.72(b)(2)(i). "At 12:02 p.m. CST, battery charger D09 and electrical subsystem D02 were restored to operable status. This resulted in TS 3.8.4 being met and Conditions 3.8.4 A and B were exited. Reactor power on Unit 2 had only been reduced to approximately 99% power at that time. No shutdown was initiated on Unit 1, which remained at 100% power. "The power reduction on Unit 2 continued in accordance with normal plant procedures governing loss of offsite transmission network line 151. Plant procedures specify a reduction to less than 50% power as a precautionary measure associated with a potential for grid instability under certain postulated conditions. "Both reactors continue to operate in a safe and stable manner." The licensee stated that the loss of offsite power line 151 (345KV) was due to an insulator problem on a high voltage tower about 7 miles from the plant. The estimated repair and restoration time for line 151 is approximately 2100 CST tonight. The licensee has notified the NRC Resident Inspector. | 0 | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-02-27
41446 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2005-02-26 21:34 | 2005-02-27 01:26 | 2005-02-27 | PLANT HAD A REACTOR TRIP FROM 16.1% POWER DUE TO A LOSS OF TURBINE LOAD SIGNAL The following information, in addition to the phone report, was obtained from the licensee via facsimile: "Fort Calhoun Station Unit 1 experienced a reactor trip from 16.1% Reactor Power on a Loss of Turbine Load during a scheduled plant shutdown for a refueling outage. "The turbine generator was tripped offline at 2101 per refueling outage schedule. A feedwater transient occurred [cause being investigated] during turbine testing, resulting in power rising rapidly from 12.6% to 16.1% . At which point the reactor tripped on loss of load due to being greater than 15% power with all turbine stop valves closed. "All plant equipment functioned as designed. A Reactor Coolant System (RCS) cooldown resulted due to a feedwater transient. Main Feedwater was isolated, which terminated the cooldown. Auxiliary Feedwater (AFW) was established with the diesel driven auxiliary feed pump. Emergency Boration was manually initiated due to the RCS cooldown and secured after shutdown margin verification. Plant is currently stable in mode 3. "This report is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for an event that resulted in an event that resulted in an unplanned RPS actuation while the reactor was critical." All rods fully inserted, no ECCS actuation and no relief valves lifted. Steam generators are being used for heat sink. The NRC resident Inspector was notified | 0 | 0 | 0 | 12 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-02-27
41445 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2005-02-26 15:30 | 2005-02-26 20:08 | 2005-02-26 | DEGRADED CONDITION OF REACTOR COOLANT BOUNDARY WELD "IRE-003-469 identified flaws (one circumferential and two axial indications) on 2-DR-2007 weld of hot leg drain line. Engineering has evaluated the flaws using the procedures of ASME Code Section XI, IWB-3600. Although the circumferential flaw was found to be acceptable in accordance with ASME section XI, IWB-3600, the calculated growth rates of the postulated axial flaws are large and do not meet the ASME Section XI Code requirements per NUREG 1022, Rev. 2 sect. 3.2.4 (degraded or unanalyzed condition). 'Any event or condition resulting in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.' Currently a repair plan is being developed. " The licensee indicated that they will not be able to enter mode (4) until the repair is completed (using weld overlay as the repair method) and an inspection of the repair is conducted. The licensee will perform a design engineering evaluation of extent of condition to determine the impact of this on the operating unit (Unit 1). The NRC Resident Inspector will be notified. See similar event #41448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Cold Shutdown; FMode2: Refueling | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-02-26
41444 | -1 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2005-02-15 20:55 | 2005-02-26 00:59 | 2005-03-30 | POSSIBLE FAILURE TO MEET DESIGN BASIS REQUIREMENTS OF POSITIVE PRESSURE IN THE CONTROL TOWER ENVELOPE FOLLOWING A DESIGN BASIS ACCIDENT. The licensee provided the following information: "During operator rounds it was discovered that a double door for the control tower habitability envelope was propped open [from painting earlier in the day]. This condition would have resulted in not meeting the design basis requirements of maintaining a positive pressure inside the control tower envelope following a design basis accident. The doors were immediately closed." "An issue report was generated and a prompt investigation was commenced in accordance with station policies." The NRC resident Inspector was notified. *** RETRACTION FROM A. MILLER TO J. KNOKE AT 13:15 EST ON 03/30/05 *** The licensee provided the following information: "An ENS notification (EN# 41444) was made at approximately 00:59 on 2/20/2005 regarding a potentially unanalyzed condition associated with a double door for the Control Tower Habitability Envelope, which was propped open. It was initially thought that this condition could have resulted in not meeting the design basis requirements for the Control Tower Envelope. However, an analysis of an air flow measurement across the open door has shown that the unfiltered air in-leakage into the Control Tower Habitability Envelop would not exceed the value assumed in the design basis accident analysis for Control Room Habitability. Since this event did not result in an unanalyzed condition, this event is being retracted." The licensee notified NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2005-02-26
41443 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2005-02-24 | 2005-02-25 12:18 | 2005-02-25 | MEDICAL EVENT The following information was provide by the licensee via facsimile: "[The Department of Veteran Affairs National Health Physics Program called] per 10 CFR 35.3045 to notify [the NRC] of a possible medical event at the VA Medical Center, Durham, North Carolina, a permittee under the VA license. This event was discovered on February 25, 2005. On February 24, 2005, a permanent-implant prostate brachytherapy procedure was performed at the medical center. 84 Iodine-125 seeds were implanted in the patient. These seeds had around 400 microcuries per seed. A number of seeds were mistakenly placed in fatty tissue, outside of the intended area of treatment. Based on a preliminary evaluation, a possible medical event occurred since the dose to the prostate was possibly more than 20 percent less than that prescribed and a dose to tissue other than the treatment site is possibly more than 50 rem and greater than 50% of the prescribed dose. The authorized user notified the patient and will notify the referring physician within 24-hours of discovery. The National Health Physics Program intends to conduct a reactive inspection next week. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NC | MAT |  | 35.3045(a)(1) |  |  |  | 0 | 2005-02-25
41442 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2005-02-24 18:00 | 2005-02-25 04:42 | 2005-04-05 | POTENTIAL BREACH OF SECONDARY CONTAINMENT DURING SEISMIC EVENT. The licensee provided the following information: "This event notification is being made to report an event that could have prevented fulfillment of the safety function to mitigate the consequences of an accident IAW 10CFR50.72(b)(3)(v)(D). "The potential for creation of an actual hole through Secondary Containment (SC) via the Plant Service Water (TSW) system high point reactor building auto vents (TSW-AV-1A and TSW-AV-1 B) exists if a seismic event occurs and the Seismic Category 2 TSW loop-seal piping outside of Secondary Containment is breached (e.g., because of a pipe break) and has drained. "Neither of the above conditions presently exists. However, a Secondary Containment breach could occur as a result of a single passive failure (i.e., pipe break in the TSW loop-seal piping described above). TSW-AV-1A and TSW-AV-1B are designed to open automatically when neither TSW system pump is operating to break the vacuum condition that would otherwise exist in the piping. When TSW-AV-1A and TSW-AV-1B are open in vacuum breaker mode, the resultant hole size into the TSW system piping would exceed the allowable Secondary Containment cumulative hole size [ of 32 square inches total], if the loop seal were also breached as described above. Due to this condition Secondary Containment was declared INOPERABLE at 1800 PST 2/24/05. As a compensatory measure to prevent exceeding the allowable Secondary Containment cumulative hole size, one of the two TSW reactor building auto vents (TSW-AV-1B) was isolated by closure of a manual valve (TSW-V-55B). This action was completed at 1828 PST 2/24/05 and the Secondary Containment was declared OPERABLE. One TSW auto vent is sufficient to perform the vacuum breaker function." This condition was found by the licensee's System Engineer. The extent of condition and long term corrective action is under review by licensee. Licensee will inform the NRC Resident Inspector. * * * RETRACTION FROM FRED SCHILL TO HOWIE CROUCH @ 1535 EDT ON 04/05/05 * * * The following information was obtained from the licensee via facsimile (licensee text in quotes): "On 2/25/05, Columbia Generating Station reported (ref: EN 41442) a condition that was discovered while reviewing service water (TSW) system design documents. During the review, it was determined that Seismic Category II TSW piping in the turbine (TG) and radwaste (RW) buildings could rupture and drain during a seismic event. This event would result in an inoperable secondary containment (SC) because TSW system high point vent valves located within the SC would automatically open when the piping drained after rupturing. Such an event would allow direct communication between the SC atmosphere and the TG/RW atmospheres and exceed the leakage rate assumed in Columbia's accident analysis. There are two principal accidents in Columbia's safety analysis for which SC is credited as a mitigating system. These are the Loss Of Coolant Accident (LOCA) and the Fuel Handling Accident (FHA). The SC performs no active function in response to either of these limiting events, however, its leak tightness is required to ensure that the release of radioactive materials from the primary containment is restricted to those leakage paths and associated leakage rates assumed in the accident analysis, and that fission products entrapped within the SC structure will be treated prior to discharge to the environment. "Assuming a seismic event of the magnitude (0.25g) of the Safe Shutdown Earthquake (SSE) occurred and ruptured the TSW piping causing SC to become inoperable, it is beyond Columbia's safety analysis to postulate a release of radioactive material beyond Part 100 limits for that event. This is because analysis shows that the SSE will not in itself cause a LOCA or an FHA and Columbia's design and licensing bases do not assume a LOCA or FHA coincident with a seismic event. In the event that the SSE made SC inoperable, the Technical Specifications (LCO 3.6.4.1.B) require that the plant be in mode 3 in 12 hours and in mode 4 in 36 hours. Since this is achievable, it is reasonable to conclude that, in the event previously reported, plant shutdown can be accomplished without radiological release and within the completion time of the action required by the Technical Specifications. "The discussion in the guidance document (NUREG 1022) for reporting under Part 50.72(b)(3)(v) states the level of judgment for reporting under these criteria is a reasonable expectation of preventing fulfillment of a safety function. It also states that the intent of the criteria is to capture those events where there would have been a failure of a safety system to properly complete a safety function regardless of whether there was an actual demand. This discussion however, as the Part 50.72(b)(3)(v) and Part 50.73(a)(2)(v) criteria state, apply to safety functions of systems or structures that are needed to control the release of radioactive material, because safe shutdown of the plant without radiological release is assured post SSE (sans SC), as described in Columbia's design and licensing bases, SC would not be needed to control the release of radioactive material and therefore the reporting criteria is not met." The licensee will be voluntarily submitting a Licensee Event Report as a method of information sharing with the rest of the industry. The licensee has notified the NRC Resident Inspector. Headquarters Operations Officer notified R4DO (Howell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-02-25
41441 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-02-24 21:11 | 2005-02-24 22:39 | 2005-02-24 | ESF ACTUATION FOLLOWING TRIP OF REACTOR PROTECTION MOTOR-GENERATOR SET A trip of the "A" RPS M-G set resulted in an "A" Group 2 isolation and startup of the standby gas treatment system. There was a preliminary report of a possible fire/smoke smell in the vicinity of the M-G set. However, when an operator reported to the location there was no observed fire. The fire brigade was also dispatched but found no fire or smoke in the M-G set area. The licensee is preparing to place the RPS on its alternate power supply. This will allow the Group 2 isolations and standby gas treatment system actions to be reset. The cause of the M-G set trip is still under investigation. The licensee will be notifying the NRC Resident Inspector as well as state and local authorities. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-02-24
41440 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2005-02-24 15:30 | 2005-02-24 17:56 | 2005-02-24 | OFFSITE NOTIFICATION RELATED TO HEART ATTACK FATALITY "At 1423 the control room received an emergency phone call of an employee who was experiencing intermittent unconsciousness and in cardiac arrest. The individual was transported to a local hospital where he was declared deceased at 1530. 29CFR1904.39(b)(5) requires to report a fatality to OSHA caused by a heart attack at work. This ENS report is being made in accordance with 50.72(b)(2)(xi) contact of off site agency." There was no radioactive contamination involved in this event. The licensee does not plan any media or press release and has not notified any other government agencies besides OSHA. The NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-02-24
41439 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2005-02-24 10:35 | 2005-02-24 15:10 | 2005-02-24 | REMOVABLE RADIOACTIVE SURFACE CONTAMINATION ON A PACKAGE The Department of Veterans Affairs, National Health Physics Program reported that a package received at one of its facilities had removable radioactive surface contamination that exceeded limits. The package was received on 2/24/05 at the VA Southern Nevada Health Care System in Las Vegas, NV. The package had a contamination level of 85,000 DPM over a 300 square cm wipe. The contamination was identified as Technetium-99M via spectral analysis. The package was received from Bio Tech, a commercial pharmacy in Las Vegas. Southern Nevada Health Care notified Bio Tech and the pharmacy has sent a representative to the facility to assist in the investigation. The package was delivered by a pharmacy delivery vehicle and the status of any contamination in the vehicle is unknown. There was no apparent damage to the package. Appropriate steps have been taken to prevent the spread of contamination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | NV | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2005-02-24
41438 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2005-01-07 10:35 | 2005-02-24 12:41 | 2005-02-24 | AGREEMENT STATE MEDICAL EVENT The following report was received from the Massachusetts Department of Public Health and Radiation Control via facsimile: "Endocrinologist ordered thyroid uptake study on a patient - dose to be 17 uCi of I-131. The Central Booking Department scheduled the patient to arrive in the Nuclear Medicine Department for an I-131 'total body scan.' On 1/4/05, CNMT 1 received the appointment roster form for 1/7/05, posted it on exam scheduling bulletin board, and placed the order for a total body scan - which is generally 3.7 mCi of I-131 - without looking at the diagnosis. Total body scan ordered on roster was reviewed by Nuclear Medicine Physician and checked off for that day's activity. On the day of the exam, CNMT 2 retrieved the paper work and administered the 3.7 mCi, I-131 whole body scan. Patient sent home and came back 2 days later for thyroid scan. The imaging CNMT 3 noted that the thyroid scan did not look as expected, thus, reviewed all the paperwork and discovered that the wrong procedure (and dose) was administered. The Nuclear Medicine Physician and the RSO were then immediately notified by the CNMT 3, who in turn, notified the prescribing Endocrinologist. The Nuclear Medicine Physician then notified the patient (on 1/7/05) and the Department Administration. A summary report will be sent to the patient which will include notification that a formal report has been submitted to the Massachusetts Radiation Control Program. "The patient ultimately received 3.6 mCi of I-131, had a thyroid uptake of 70% which resulted in a thyroid dose of 13,111 rads and a TEDE of 2.6 rads. This dose will be taken into consideration when the patient is treated next for hyperthyroidism." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-03-01
41437 | 0 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-02-23 21:06 | 2005-02-24 00:35 | 2005-02-24 | AUTOMATIC REACTOR TRIP ON LOW-LOW STEAM GENERATOR LEVEL The following information, in addition to the phone report, was obtained from the licensee via facsimile: "While performing maintenance, [Maintenance] inadvertently opened a 125 VDC battery board [four] breaker which resulted in a reactor trip from steam generator low-low level. "The plant is being maintained in Mode 3 at NOP/NOT [Normal Operating Pressure/Normal Operating Temperature], 547 [degrees] and 2235 psig, with auxiliary feedwater supplying the steam generators and steam dumps removing the decay heat." All rods inserted on the trip. No relief valves lifted during the transient. The electric plant is stable with 125 VDC restored to a normal configuration. Steam generator level has been restored to normal levels. Unit 1 was not affected by the transient. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-02-24
41436 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-02-23 12:00 | 2005-02-23 19:20 | 2005-02-23 | POTENTIAL VULNERABILITY WITH ALTERNATE SHUTDOWN SYSTEM (ASDS) ISOLATION DESIGN. The licensee provided via facsimile the following report: " During an extent of condition review of the corrective actions associated (with) Event Notification #41374, the Monticello Nuclear Generating Plant (MNGP) engineering staff made the following discovery. On February 22, 2005 at 12:00 hours, MNGP discovered a potential vulnerability with Alternate Shutdown System (ASDS) isolation design which could result in Bus 16 being locked out in the event of a Control Room or Cable Spreading Room fire. The Monticello Appendix R Safe Shutdown Analysis for Control Room/Cable Spreading Room fire assumes a loss of control of Division I and II equipment from the Control Room, however, safe shutdown is achieved remotely from the ASDS panel. ASDS design is such that a Control Room/Cable Spreading Room fire would not impede the ability to safely shutdown and maintain the plant in a shutdown condition. "Contrary to the ASDS design, it was discovered that an un-isolated metering circuit from the 1AR transformer could result in Bus 16 being locked out in the event of a Control Room or Cable Spreading Room fire. The bus lockout relay from the 1AR transformer is not isolated by the ASDS transfer switches, therefore, this condition could result in failure of Bus 16 to re-energize during the implementation of the Shutdown Outside Control Room procedure. Since the Bus 16 feeder breaker from the 1AR transformer is not required at this time, it has been isolated from the safeguards bus to preclude occurrences of this event. "The event is being reported as a potential loss of safety function (10CFR50.72(b)(v)(A,B and D) and as a degraded or unanalyzed condition (10CFR50.72(b)(3)(ii)(B))." The licensee informed NRC Resident Inspector. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | UNANALYZED CONDITION | VALID SPECIF SYS ACTUATION | POT UNABLE TO SAFE SD | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(3)(v)(A) | 0 | 2005-02-23
41435 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2005-02-22 | 2005-02-23 16:53 | 2005-02-23 | PART 21 INVOLVING A DEFECT OF A DESCOTE BRAND VALVE USED ON UF6 14 TON CYLINDERS The licensee faxed over the following information for their Part 21 report: "Metropolis Works, Metropolis, Illinois (Uranium Conversion Facility) is reporting a potential deviation and defect of a Descote brand valve used in UF6 14 Ton Cylinders. "While preparing to fill a new UF6 14 Ton Cylinder from Urenco (Supplier/Customer), a potential deviation was recognized during the plant procedural pre-fill 60 lb. pressure check that identified improper torque of the Descote brand valve's packing nut. Torque inspections of all new Urenco cylinders on site were initiated when the deviation became apparent in four cylinders. A total of 57 cylinders at the plant were found to be outside the required torque specifications for these new 14 Ton UF6 cylinders. All of these valves on-site have been properly torqued as of 2/23/05. "Secondly, one of the valves noted above was re-torqued and passed the procedural pressure check after which the filling process proceeded. Upon filling the cylinder, a small, localized seepage occurred that was controlled immediately per procedure. The cylinder was isolated and allowed to cool (liquid to solid phase) to facilitate valve replacement and further investigation of the valve. During the investigation on 2/22/05, two issues were apparent including improper seating of the valve (though no obvious signs were recognized) and a potential minor crack/imperfection was recognized on this 613 packing nut under magnification. This valve is being prepared to send off site for detailed metallurgical analysis. MTW personnel have communicated this inconsistency with the certifying organization (Urenco) and determined this is a reportable event as a defect per 10 CFR 21.21 requirements and plant procedures. "No workers have received a chemical exposure from this issue and no material release from the facility occurred. "Marking on the valve are as follows (comments): "Descote Valve Type 51.1 valve (revision # /size) N-1000 (in casting) 11 246 (valve #/type:) "Opposite side of valve (manufacture information) 0011068173 557 R05 204250 636 made in France "Packing Nut Information 613 579 R08 51.1 Type" Licensee notified NRC personnel Dave Hartland, Region 2 and Michael Raddatz NRC HQ. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 21.21 |  |  |  | 0 | 2005-02-23
41434 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2005-02-23 09:00 | 2005-02-23 12:18 | 2005-02-23 | POWER LOSS AND RESTORED TO TONE ALERT RADIO NOTIFICATION SYSTEM On February 23, 2005, the state and local officials notified Nine Mile Point that there was a loss of power to the tone alert radio notification system. At 1152 EST, on February 23, 2005, power was restored to the tone alert radio notification system. (See EN #41433). The NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-02-23
41433 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2005-02-23 09:00 | 2005-02-23 11:36 | 2005-02-23 | TONE ALERT RADIO NOTIFICATION SYSTEM OUT OF SERVICE "At 1030 on February 23, 2005, with the James A. Fitzpatrick (JAF) Nuclear Power Plant operating at 100% reactor power, Oswego County Emergency Management notified JAF that the National Weather Service had notified them that the Tone Alert Radios had been out of service since 0900. "This impacts the ability to readily notify a portion of the Emergency Planning Zone (EPZ) Population for the Nine Mile Point and JAF Nuclear Power Plants. This failure meets NRC 8 hour reporting criterion 10 CFR 50.72(b)(3)(xiii). "The failure was caused by a computer upset that required reloading of the software that initializes the Tone Alert Radio notification. The National Weather service is currently working on the software reload and estimates the Tone Alert Radios will return to Service by 1130. "The loss of the Tone Alert Radios constitutes a significant loss of emergency off-site communications ability. Compensatory measures have been verified to be available should the Prompt Notification System be needed. This consists of utilizing Local Law Enforcement Personnel for 'Route Alerting' of the affected areas of the EPZ. "The event has been entered into the corrective action program and the resident inspector has been briefed and the state PSC will also be notified." * * * UPDATE FROM D. SQUIRES TO W. GOTT AT 1205 EST ON 2/23/05 * * * The Tone Alert System was restored at 1152 EST. The licensee will notify the NRC Resident Inspector. Notified R1DO (P. Henderson) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-02-23
41432 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-02-23 01:53 | 2005-02-23 07:11 | 2005-02-23 | AUXILIARY FEEDWATER ACTION FOLLOWING MOMENTARY POWER INTERRUPTION "A momentary interruption in the preferred offsite power source to Unit 2 safeguards 6.9 KV busses occurred due to adverse weather. A blackout signal was generated as a result which in turn initiated an auxiliary feedwater signal. Operators took action to reduce turbine load to 1100 MWe to ensure reactor power would remain below 100% following the reactivity effects associated with the addition of cold auxiliary feedwater. "The event was caused by both feeder breakers to the 138 KV switchyard opening. Breaker 7050 auto-reclosed but breaker 7020 needed to be manually reclosed. The cause of the breaker operation is not fully understood and is still under investigation. "Auxiliary feedwater has been returned to standby condition and reactor power is being restored to 100%." The NRC Resident Inspector has been notified. | 0 | 94 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-02-23
41431 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2005-02-21 08:50 | 2005-02-22 16:22 | 2005-02-22 | AGREEMENT STATE - GENERAL LICENSE - LOST AND DAMAGED TRITIUM SIGNS The following information was provided by the State of Arizona via facsimile: "At approximately 8:50 AM, February 21, 2005, the Agency received notice from AZ DPS advising that 9 Tritium Exit signs were missing. In addition, three signs were located in the store (under construction). A forth sign was damaged in the store. The [damaged] sign was not glowing as the other three. This information was supplied by the Tucson Police Department to AZ DPS who advised the Agency. The Tucson Fire Department was also at the site and they indicated they thought the sources were removed between Friday night and Monday morning. The building does not have doors or windows, but is otherwise closed. "Since the facility is under construction, who is the responsible party is a portion of the investigation. The signs have not been reported as transferred into the State. The devices were made by Isolite and contain 11.5 Curies of Tritium each. As much as 103.5 Curies of tritium may be missing in addition to the 11.5 [Curies] in the broken exit sign. Tucson Police report # 0502210205 applies to this event. "Due to the potential contamination of persons a press release may be made. "The Agency continues to investigate this event. The US FBI will be notified of this event." Arizona Report #: 05-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2005-02-25
41430 | 0 | HUMBOLDT BAY | 3 |  |  | [3] GE-1 | 2005-02-22 14:25 | 2005-02-22 17:25 | 2005-02-22 | REPORT OF MISSING SPECIAL NUCLEAR MATERIAL The following details were provided by the licensee via email after the telephonic notification: "This is a non-emergency Event Notification in accordance with 10 CFR 20.2201(a)(1)(ii) to inform the NRC of missing special nuclear material (SNM) (up to approximately 0.15 grams of U235). The missing SNM consists of one complete and three partial in-core detectors. "Since June 2004, Pacific Gas and Electric (PG&E) has been performing an investigation and search for three missing 18-inch rod segments at the Humboldt Bay Power Plant (HBPP) (reference NRC Event Notifications 40877 and 40963). The investigation also included a verification of the inventory of all SNM, including fuel and non-fuel SNM. As a result of the investigation, plant personnel identified HBPP records that indicate 54 in-core detectors should be in the spent fuel pool (SFP). "In-core detectors were used inside in-core assemblies during plant operations to measure reactor power level. There were three in-core detectors contained inside each in-core assembly. The in-core assemblies were segmented for storage, and the in-core detectors from a total of 18 in-core assemblies (containing 54 in-core detectors) should be onsite. Each in-core detector is approximately 2-1/2 inches long. Depending on design, an in-core detector contains as much as 0.04 grams of U235, to slightly less than 0.002 grams of U235. "PG&E personnel performed a search in the SFP for the in-core detectors from December 2004 through February 2005. On February 4, 2005, PG&E determined that not all 54 in-core detectors could be located and informed the NRC. PG&E is submitting this Event Notification in accordance with 10 CFR 20.2201(a)(1)(ii) that requires a telephonic report and an Event Notification to be made within 30 days from February 4, 2005. "PG&E will be issuing a press release tomorrow that includes this issue. "PG&E's search for in-core detectors is complete. PG&E has determined that 50 complete and three partial in-core detectors are in the SFP. Therefore, one complete and three partial in-core detectors are missing. The partial in-core detectors appear to have been cut when the in-core assemblies were cut to be shortened for SFP storage in the mid-1970s or mid-1980s. "Most probable locations for the missing in-core detectors are licensed, monitored and restricted radiological control areas, therefore the public health and safety has not been adversely affected. "PG&E will issue licensee event report (LER) 2005-001-00, 'Missing In-core Detectors,' dated February 22, 2005, to be submitted in accordance with 10 CFR 20.2201(b)(2)(ii) (Reference PG&E Letter HBL-05-002). Information pertaining to the missing in-core detectors is also included in the HBPP SNM Control and Accountability Project Interim Reports, to be submitted February 22, 2005 (Reference PG&E Letter HBL-05-001). "NRC personnel at headquarters and in Region IV have been notified of the status of this issue." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-02-22
41429 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-02-19 17:35 | 2005-02-22 16:00 | 2005-02-23 | AGREEMENT STATE - LOST TROXLER THIN LAYER DENSITY GAGE The following was received from the state via e-mail: "On Saturday, 02/19/2005, 1430 CST, the licensee's representative received notification that a technician had lost a Troxler Model 4640-B, Thin layer Density Gauge, S/N 1880. The device contains a double encapsulated source of 10mCi of Cs-137 that was last leak tested on 12/09/04. The source rod handle was padlocked and key was removed according to the technician. The shipping/transport case was lost in the Brownsville, TX area where it was being used at a temporary jobsite. "Per company protocol and as discussed during loss notification to TX DSHS, a $500.00 'no-questions-asked' reward for the recovery of the device to be issued to area media outlets." Texas Incident No: I-8213 * * * UPDATE FROM R. JISHA TO J. KNOKE AT 12:41 EST ON 2/23/05 * * * "The gauge was apparently lost off the back of a pick-up truck at a job site in the vicinity of FR511 and EXPWY. 77 an incorporated area northwest of Brownsville proper. Since the gauge was not secured in the case which was secured to the vehicle, it was not lost but presumably the device had bounced off the truck on a rough section of road. Multiple attempts were made to retrace the route but none were successful in recovering the device. The manufacture (Troxler) has been notified." Notified R4DO (D. Powers) and NMSS (S. Moore) and CNSNS Mexico via fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-02-25
41428 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-02-22 03:08 | 2005-02-22 06:20 | 2005-02-22 | EMERGENCY DIESEL GENERATOR AND EMERGENCY FEEDWATER AUTO START ON VITAL BUS FAILURE TO TRANSFER "To support routine preventative maintenance on the 4160V Unit Auxiliary Transformer breaker, 4160V Vital Bus 5 did not successfully transfer to the Reserve Auxiliary Transformer. Bus 5 momentarily de-energized and the Emergency Diesel Generator started and loaded as expected supplying Bus 5. The Emergency Feedwater System actuated as expected on momentary undervoltage to Bus 5. The plant remains stable at 100% power. A station troubleshooting team has been established. "The reason that Bus 5 did not transfer to the Reserve Auxiliary Transformer is not known at this time." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-02-22
41427 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-02-21 13:45 | 2005-02-21 16:35 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * EXTERNAL RADIATION LEVELS EXCEEDED THE TRANSPORTATION INDEX (TI) LIMIT OF 10. On 2/16/05 a radioactive Yellow - III shipment containing eight well logging sources was shipped from Baker Hughes Inteq in Houston, TX. The shipment of sources, Am-241/Be (1480 GBq), arrived at BWXT in Lynchburg, VA. On 02/21/05. Emery Worldwide indicated the shipment mode had a Transportation Index (TI) reading of 9, however, BWXT's reading was 12.6. BWXT placed the package in a restricted area to minimize exposure to personnel, which has a surface contact reading of 83.3 millirem/hr, and at one meter away it read 12.6 millirem/hr. Since this shipment had a TI >10 it was reportable under 10CFR 20.1906. (Note: Transportation Index is the radiation reading in millirem/hr at a distance of one meter.) Licensee notified NRC Resident Inspector and final carrier. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(2) |  |  |  | 0 | 2008-05-11
41426 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2005-02-21 02:50 | 2005-02-21 09:37 | 2005-02-21 | SAFETY PARAMETER DISPLAY SYSTEM INOPERABLE FOR GREATER THAN ONE HOUR "On February 21, 2005, at 0250 hours [EST], the Unit 1 Plant Computer System (PCS) failed rendering the Safety Parameter Display System (SPDS) inoperable. The PCS and SPDS were restored at 0650 hours. This event is a major loss of emergency assessment capability for greater than one hour and is reportable under 10 CFR 50.72(b)(3)(xiii)." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-02-21
41425 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-02-20 11:58 | 2005-02-20 16:37 | 2005-02-20 | RPS ACTUATION ON STEAM GENERATOR LOW LEVEL The following information was reported by fax: "During a plant shutdown from 100% power due to the condition as discussed in previous event notice EN #41423, a valid actuation of the reactor protection system occurred. The plant was in the intermediate shutdown mode at approximately 510°F, using the S/G's to cool the Reactor Coolant System, S/G water level was being controlled with one Auxiliary Feedwater Pump and manual control of its outlet valve. "Following the initiation of RCS cooldown, Steam Generator levels began to decrease. The operator began to throttle the operating AFW pump's outlet valve open, however at 1158 on 2/20/05, the Control Room received the Annunciator for S/G B Low-Low Water Reactor Trip, which has a setpoint of 2/3 S/G level channels <17% narrow range level. This caused a Reactor Trip signal to be initiated by the Reactor Protection System. The trip signal was generated, however the plant was already in a shutdown condition with the reactor trip breakers open." "All systems were functioning normally. The operator started an additional AFW pump and, at 1206, normal level was restored to S/G B and the automatic Reactor Trip signal cleared." The lowest level during this transient in Steam Generator B was 14.5% narrow range level. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-02-20
41424 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2005-02-19 16:04 | 2005-02-20 11:17 | 2005-02-20 | 24-HOUR CRITICALITY CONTROL REPORT - FAILURE TO OBTAIN REQUIRED POWDER SAMPLES The licensee provided the following information via email: "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia, SC, low enriched (less than or equal to 5.0 wt% U 235) PWR fuel fabricator for commercial light water reactors. "Time and Date of Event: February 19, 2005, 1604 hours. "Reason for Notification: Double contingency protection for non-favorable geometry (NFG) bulk containers is based on preventing moderation from entering the bulk powder blending room and then by preventing the moderator from entering the bulk containers. "Prevention of moderation from entering the bulk powder container is assured through application of tiered layers of controls, such as limiting materials allowed to be utilized in the bulk powder blending room, requiring a double roof on the bulk powder room, and by rigorous controls on the handling of polypaks to be transferred into the bulk powder container. "Rigorous controls are instituted on the moisture content of each polypak to ensure that the contents are less than 0.3 wt% moisture. Each filled polypak coming off of the Fitzmill is transferred to a polypak cart for handling and storage prior to transfer into a bulk powder container. Each polypak cart is capable of handling up to 56 polypaks. Prior to storage on the cart, each polypak is required to be sampled, with the sample material obtained being combined into a single composite sample for the entire cart. In addition, three additional polpaks on the cart are randomly chosen and sampled. These three additional samples are completely independent of the composite sample. Thus the composite sample and the three random samples comprise the double contingency protection for the moisture content of the polpaks to be transferred to a bulk powder container. "During an audit of the operation, it was observed that the composite sample was not being taken in several instances. Thus the sample being analyzed may not have been representative of polypaks on the cart. This compromised a loss of one leg of double contingency for polpaks to be transferred into the bulk powder NFG. All of the random individual samples have been taken and analyzed properly, and thus no material has been observed that exceed the allowed moisture content. "In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criteria for a 24-hour notification, specifically, 'Any nuclear criticality safety incident, in an analyzed system, for which less than previously documented double contingency protection remains (multi-parameter control or single-parameter control) and less than a safe mass is involved.' and 10CFR70, specifically Appendix A.b.2 'Loss or degradation of items relied on for safety that results in failure to meet performance requirements of 10CFR70.61.'" "As Found Condition: During an audit of the Fitzmill operation it was observed that the required samples for generation of the composite sample were not being taken consistently. "Summary of Activity: - All impacted operations/equipment affected has been shut down pending confirmation of the moisture content. - Revised operational methods are being developed and implemented. "Conclusions: - At no time was material observed to have a moisture content above the allowed limits. - At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. - The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. - A causal analysis will be performed." The licensee is notifying NRC Region 2 and HQ NMSS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | SC | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2005-02-20
41423 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-02-19 19:10 | 2005-02-20 00:47 | 2005-02-20 | TECHNICAL SPECIFICATIONS REQUIRED SHUTDOWN DUE TO INOPERABLE AUXILIARY FEEDWATER PUMPS "During continuing evaluation of the operability of the Auxiliary Feedwater (AFW) Pump discharge pressure switches, engineering determined that a high energy line break had the potential to affect the AFW Pump Suction line from the Condensate Storage Tank (CST) due to the inability of the discharge pressure switches to protect the AFW pumps from a loss of suction from the CST. At 1910 CST on 02/19/2005 it was determined that all three AFW Pumps were inoperable as a result of the condition discovered by engineering. Due to the high energy line break, there is the potential for damage to the CST supply line to the AFW Pumps (due to pipe whip resulting from a feedwater line circumferential break). Damage to the CST supply line may result in air entrainment in the AFW Pump supply and potential AFW pump damage following an automatic AFW Pump Start. "Technical Specification 3.4.b.7 allows AFW Pumps to be placed in "pull-out" at less than 15% power because analysis shows that there is at least 10 minutes available for an operator to manually initiate AFW flow if needed. At 2003 CST a power reduction to <15% power was initiated to restore the operability of an AFW Pump. When power is less than 15%, the Turbine Driven AFW Pump will be placed in "pull-out" and Service Water will be aligned to the suction of the Turbine Driven AFW Pump to restore Operability of the Turbine Driven AFW Pump. When operability is restored to one AFW pump, the plant will enter a 4 hour LCO as a result of two AFW Pumps remaining out of service. Since operability of the two motor driven pumps will not be restored within the 4 hour LCO time, plant cooldown to less than 350 deg F will continue in accordance with Technical Specification 3.4.b.6." The licensee notified the NRC Resident Inspector. | 10 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  | 0 | 2005-02-20
41420 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2005-02-16 | 2005-02-18 17:04 | 2005-02-18 | AGREEMENT STATE MEDICAL EVENT The following information was provided by the State of Wisconsin via facsimile: "On Thursday, February 17, 2005 at approximately 3:45p.m. [CST], the Wisconsin Radiation Protection Section (RPS) received a telephone call from the Marshfield Clinic, Marshfield, WI (license number 141-01162-001) informing the section of a medical event involving a therapeutic radiation dose from a gamma knife exposing a site outside the intended treatment volume to a level greater than 50% of the expected dose. (HFS 157.72 (1) (a) 3.) "Preliminary Information From the Licensee: "On Wednesday, February 16, 2005, the Marshfield Clinic had scheduled a therapeutic radiation treatment of 18 Gray (1800 Rads) using a gamma knife. During the process of manually programming the positioning system, the y and z coordinates were transposed. The error was not noticed during a double check of the treatment coordinates. As a result, a site outside the intended treatment volume received an estimated dose of 5.06 Gray (506 Rads) instead of the originally estimated 0.4 Gray (40 Rads). The volume of the unintended treatment site was 0.7 cubic centimeters. The treatment duration was 2.42 minutes. The prescribed dose of 18 Gray was delivered and the patient treatment was completed. "The attending neurosurgeon and radiation oncologist believe there will be no medical consequences to the patient from the unintended exposure. The referring physician has been notified. "[State of Wisconsin] is reporting this event under: "HFS 157.72 (1) (a) 3. requires a licensee to report an event where there is 'A dose to an organ outside the intended treatment volume that exceeds the expected dose to that organ by 0.5 Sv (50 Rem) where the excess dose is greater than 50% of the expected dose to that organ. . . ' "DHFS, RPS staff have been dispatched on Friday, February 18, 2005 to investigate. "Wisconsin Incident No: 20" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2005-02-23
41419 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2005-02-18 14:20 | 2005-02-18 15:34 | 2005-02-18 | AGREEMENT STATE REPORT - STUCK WELL LOGGING SOURCE Today at 1520 EST Schlumberger out of Houston office notified Kentucky Dept. of Radiation Control of the following event. Equitable Production Co. (main office located somewhere in Kentucky) has a stuck well logging source tool. Sometime in the last week the well logging source became stuck at which time the State of Kentucky should have been notified. When trying to retrieve the well logging source the well logging source was broken in half (located in Knott County, Eastern Kentucky). The upper portion of the well logging source containing the americium-241 portion of the well logging was retrieved, no contamination. The top of the stuck well logging tool is at an estimated depth of 3454 feet and the top the cesium-137, 1.7 curies, is at a depth of 3460 feet. According to the State of Kentucky Radiation Control Officer, the 3454 foot depth is vertical depth and there is no contamination or ruptured sources. Plugging well: Will do a 500 foot pour on top the of the stuck well logging source and then place a wipstock on top of the plug. A State of Kentucky Dept. of Radiation Control person will be present when the well is plugged. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2005-02-23
41418 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2005-02-17 12:00 | 2005-02-18 11:24 | 2005-02-18 | 24 HOUR 91-01 RESPONSE BULLETIN AND PART 70 APP A UNANALYZED CONDITION The following information was provided by licensee via email: "The sponge jet blast system is a non-favorable geometry (NFG) decontamination unit that scours contaminated items with pressurized hydrogenous sponge media imbedded with aluminum oxide to decontaminate the items. The safety basis of the system is based upon extremely conservative calculations modeling 1-3g/cc Uranium dioxide in a specified, controlled sponge jet media. Based upon these calculations, criticality is not credible in the sponge jet system when using the specified media, which is the only media allowed in the unit. This critical item, for which an IROF (discussed below) was put in place, was that the physical characteristics of the sponge jet media could never be changed without criticality analysis. "During a routine procedure review, a criticality safety engineer noticed that specific manufacturer and product information he had previously required was not present in the procedure for the sponge jet blaster. "An IROF had been specified for the equipment with an action expected stating, 'Operator/Area Engineer utilize only approved aluminum oxide sponge media.' The configuration control process was bypassed and the approved sponge jet blast media was replaced with a media with double the specific gravity of the approved media and four times the content of hydrogenous material. "In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criteria for a 24-hour notification, specifically, 'Any nuclear criticality safety incident, in an analyzed system, for which less than previously documented double contingency protection remains (multi-parameter control or single parameter control) and less than a safe mass is involved.' "Also, in accordance with Appendix A to Part 70--Reportable Safety Events (b) Twenty-four hour reports. Events to be reported to the NRC Operations Center within 24 hours of discovery:(1) Any event or condition that results in the facility being in a state that was not analyzed, was improperly analyzed, or is different from that analyzed in the Integrated Safety Analysis, and which results in failure to meet the performance requirements of § 70.61. " Sponge jet blaster contained the unauthorized material with contamination levels (2700 ppm U preliminary results) of Uranium. This is two orders of magnitude less than a critical concentration for an optimally moderated mixture. A very conservative mass estimate was made assuming the entire unit was filled with the 2700 ppm material, when less than 1/4 of the unit would contain material at any given time. This mass calculation estimates the mass total at 3.149 kg U which is an order of magnitude less than a critical mass. A more realistic estimate is 0.25 kg U [based on the amount of sponge media actually in the jet blaster (5 bags)]. "Summary of Activity: The Sponge jet blaster has been shut down. "Conclusions: There was much less than a critical mass of SNM involved. There was much less than a critical concentration. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | UNANALYZED CONDITION | [8 empty] | NON EMERGENCY | 2 | SC | FUE |  |  | PART 70 APP A (b)(1) |  |  | 0 | 2005-02-18
41417 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2005-02-17 17:30 | 2005-02-17 22:05 | 2005-02-17 | EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE DUE TO UNANALYZED CONDITION The following information was provided by the licensee via facsimile: "During testing of the Division 2 Diesel Generator Testable Rupture Disc (TRD), it was discovered that excessive force was needed to open its damper. The function of the TRD is to open to relieve exhaust pressure should the diesel generator's non-safety exhaust silencer become blocked. Upon inspection of the TRD, some deformation was noted on the TRD damper. Since the possibility that the condition might exist on the other two divisional diesel generators could not be ruled out, they were also declared inoperable and LCO 3.0.3 entered. An unanalyzed condition potentially exists because a change in engineering design potentially affected multiple trains. Since all three diesel generators are inoperable, a loss of off-site power would challenge safe shutdown capability, the ability to remove decay heat and accident mitigation. "A plant shutdown required by Technical Specifications (LCO 3.0.3) was required due to declaring all 3 divisional diesel generators inoperable. LCO 3.0.3 was entered at 1730 hrs on 2/17/05. No power reduction was required as the Division 2 Diesel Generator was declared operable at 2011 after unlatching its Testable Rupture Disc (TRD) [and LCO 3.0.3 was exited]. "The resident NRC inspector was informed of the LCO 3.0.3 entry and exit [and this event notification]. No other notifications of governmental agencies or the press are planned." At the time of the notification to NRC Headquarters, the Division 1 EDG TRD had been unlatched and declared operable. The Division 3 EDG TRD was expected to be unlatched within the next hour. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2005-02-17
41416 | 0 | PORTER MEMORIAL HOSPITAL |  |  |  |  | 2005-02-17 13:40 | 2005-02-17 14:48 | 2005-02-17 | MEDICAL EVENT - TOTAL DOSE DELIVERED DIFFERS FROM PRESCRIBED DOSE Licensee called to report that on 02/16/05, the hospital performed a prostate seed implant. It was discovered after the implants were performed that the activity content for the first set of seeds (63 seeds) was incorrect. The hospital had ordered 0.27 millicuries per seed of I-125 and received 0.37 millicuries per seed. The order had been placed and confirmed with the seed manufacturing company, but the incorrect activity per seed was sent for the first of three implants for this patient. The documentation that was supplied with the order did identify the first set of seeds containing 0.37 millicuries per seed. Both the patient and the referring physician have been notified of the error. A post implant CT was performed to attempt to accurately calculate the dose overage, but the licensee determined that process would be difficult to verify. Licensee is evaluating methods to prevent reoccurrence (such as - perform own source calibration, verify documentation prior to implantation). Licensee did state that there was no unintended permanent functional damage to an organ or physiological system. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-02-17
41415 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-02-17 | 2005-02-17 10:28 | 2005-02-17 | MISSING CALIBRATION SOURCE "On January 22, 2005 a radiation protection technician discovered that a radiation detector calibration source was missing from its locked storage cabinet. An investigation was initiated and efforts to locate the source continue but the source has not been located. The source is approximately 2 inches in diameter in the form of a metal disc containing 0.0154 micro-curies of Thorium-230 that is used to calibrate SAC-4 alpha counters. The source is labeled and poses no radiological hazard to individuals that could unknowingly be in close proximity to it. The source was last used to calibrate a SAC-4 alpha counter on 1/20/2005. "10CFR20.2201(a)(1)(ii) requires a telephone report to the Operations Center in accordance with 10CFR50.72 within 30 days of the loss of licensed material in a quantity greater than 10 times the quantity specified in Appendix C to Part 20. The quantity specified in Appendix C for Thorium-230 is 0.001 micro-curies; therefore, this report is required." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2005-02-17
41414 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2005-02-16 21:12 | 2005-02-17 00:18 | 2005-02-17 | REACTOR TRIP DUE TO TURBINE TRIP AS A RESULT OF FAILED POWER SUPPLY "Ginna Station received a reactor trip from Turbine Trip at 2112 hrs on 02/16/05. The Turbine Trip signal was generated from the ATWS Mitigation System Actuation Circuitry (AMSAC) related to a failed power supply in the Advanced Digital Feedwater Control System. All control rods inserted on the reactor trip. The plant is currently stable in Mode 3, RCS Pressure 2235 psig, Temperature 540 deg F. AFW [Auxiliary Feed Water] did actuate as designed after the trip. "For the transient, min & max Temperatures, Pressures & Levels are: RCS Temperature: Max - 561 deg F Min - 538 deg F RCS Pressure: Max - 2250 psig Min - 2218 psig Pressurizer Level: Max - 50% Min - 28%" The electrical grid is stable. Decay heat is being rejected to the Main Condenser. The licensee notified the NRC Resident Inspector and the State Public Service Commission. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-02-17
41413 | -1 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-02-16 13:31 | 2005-02-16 21:20 | 2005-02-17 | DEGRADED CONDITION - REACTOR BUILDING NORMAL SUMP LEVEL INCREASING The licensee provided the following information via facsimile: "Event: "On February 16, 2005 at 1331 hours EST, Operations discovered that the Oconee Unit 3 Reactor Building Normal Sump (RBNS) level was increasing. Chemistry sampled the containment normal sump to determine the water source and could not conclusively rule out Low Pressure Service Water (LPSW). The leak rate into the sump is approximately 1.9 gpm. LPSW is the cooling medium used for the Reactor Cooling Pump (RCP) motor coolers, the Reactor Building Cooling Units (RBCU), and the Reactor Building Auxiliary Cooling Units (RBACU). "Unit 3 entered Technical Specification 3.6.1.A at 1331. This requires restoring containment to Operable status within 1 hour. The approximately 1.9 gpm leakage is above the leakage allowed in calculation OSC-7005 "LPSW Allowable Leakage Inside Containment". At 1431 Unit 3 entered Technical Specification 3.6.1 B which requires being in mode 3 in 12 hours. "Initial Safety Significance: "By limiting the amount of LPSW leakage inside containment then containment operability is ensured. Above the calculated LPSW leakage as stated in OSC-7005, containment operability is in question. The LPSW system pressure could be less than containment LOCA peak pressure. Therefore containment atmosphere has the potential to leak through the LPSW system, during a LOCA, and out the return line resulting in a containment leak path. "Collective Action(s): "Additional sampling and process indications suggest that the cause of the Reactor Building Normal Sump rate increase is feedwater or main steam. A power reduction to 18% has been completed and a reactor building entry is in progress to confirm the source of the leakage. If the source is confirmed to be feedwater or main steam, Technical Specification 3.6.1 will be exited." The turbine is still loaded and the electrical grid was not affected by the power decrease to 18%. All systems functioned as required and other units at Oconee were not affected by this event. NRC Resident Inspector was notified. * * * UPDATE ON 2/17/05 @ 0018 BY JOHN COLLINS TO CHAUNCEY GOULD * * * UPDATE They entered the containment and verified a steam leak off the impulse line for the "3B" steam generator main steam pressure transmitters. They are currently at 18% power and making a decisions on repair options. The NRC Resident Inspector will be informed. The Reg 2 RDO(Bernhard) was notified. * * * UPDATE ON 2/17/05 @ 0139 BY JOHN COLLINS TO CHAUNCEY GOULD * * * RETRACTION At 0012 on February 17, 2005 entry into the Unit 3 reactor building confirmed that the source of leakage into the reactor building normal sump was the Main Steam system. Specifically, the location of the leak appears to be a fitting downstream of an instrument root valve off the 3B Main Steam line. Based on this information, Technical Specification 3.6.1 was exited and this event is not reportable per 10CFR50.72. and therefore being retracted. A shutdown to MODE 3 will be conducted to facilitate repairing the leak. The NRC Resident Inspector will be informed. Reg 2 RDO(Bernhard) was notified. | 0 | 0 | 18 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-02-16
41412 | 0 | ALCO CORPORATION |  |  |  |  | 2005-02-16 14:55 | 2005-02-16 14:59 | 2005-02-17 | CPN NUCLEAR GAUGE STOLEN FROM THE JOBSITE An employee of the ALCO Corporation was working at a jobsite on Highway PR837 in Guaynabo, Puerto Rico with a CPN nuclear gauge. About 14:55 on 2/16/05 he had walked 40 feet away from the nuclear gauge and when he returned to the area he noticed the gauge missing. The gauge contain two sources, 50 millicuries Am-241and 10 millicuries of Cs-137. A police report was being taken and that information will be provided as a later update. No reward for the return of the gauge is being offered at this time. * * * UPDATE ON 02/17/05 AT 0742 FROM DAVID RHOE TO GERRY WAIG * * * The following information was received via facsimile from Mr. Rhoe: "RE: Stolen CPN Nuclear Gauge [Serial number] MD20801021 "On February 16, 2005 the above nuclear gauge was stolen from a [deleted] vehicle. The nuclear gauge was located inside the carrying case and the case was secured by chains/padlock to the vehicle. The chain was cut and the nuclear gauge/case/chains were removed. Mr. [deleted] was inspecting the asphalt and the vehicle was temporarily out of sight due to the blind spots around the corner of the road. The handle of the nuclear gauge inside the case was not locked. The incident occurred between 3:30 to 4:00 pm on RP 837 in Guaynabo at the Barrio Camarones site. The police and NRC were immediately notified. The police report number is 05-7-132-02011. "The following media stations were notified: Channel 2 WKAQ TV Channel 4 WAPA TV University of Puerto Rico TV "Today the radio stations and newspaper will be notified. There will be a reward offered for the return of the gauge." Notified TAS DO, R1DO (Eugene Cobey), NMSS (Sandra Wastler) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-02-16
41411 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2005-02-04 | 2005-02-15 18:00 | 2005-02-15 | FAILURE OF SAFETY EQUIPMENT - FIXED GAUGE The following information (Report # NE050003) was provided by the State of Nebraska (Julia Schmitt) via facsimile: "Operators noticed that strand line #2 was showing erratic readings that were not consistent with the other three operating molds. Operations were suspended to investigate the cause. The assistant RSOs responded and observed that the gauge had separated between the top actuator flange and the shield housing. It was determined that the gauge's lead housing had separated from the flange, leaving approximately seven inches of the source rod unshielded. There was no visible exterior damage to the flange or housing. Leak tests and surveys were performed that verified that the gauge's actuator was locked-out. The device was removed from service and placed in an onsite storage vault awaiting analysis as to the cause of the failure." The licensee reporting this malfunction is Nucor Corporation, located in Norfolk, NE 68702. The source of radiation is a fixed gauge, model number P2608-100, manufactured by Berthold, and contained 0.003 curies of Co-60. The malfunctioned equipment is a fixed gauge, model number LB300 ML, also manufactured by Berthold. Ms. Schmitt believed the radiation exposure to personnel was < 2mrem/hr, however, this has not been determined as fact. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2005-02-18
41410 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2005-02-14 21:55 | 2005-02-15 01:13 | 2005-02-15 | TECH SPEC REQUIRED SHUTDOWN The following information was provided by the licensee via e-mail: "On February 10, 2005, plant operators observed an abnormal flow condition on Unit 2 Train 'B' Component Cooling Water (CCW) from the Shutdown Cooling Heat (SDC) exchanger and, at about 2315 PST, declared Train 'B' of Containment Spray inoperable. This caused Unit 2 to enter a seven-day action statement (TS 3.6.6.1). "Although it may have been possible to correct the abnormal flow condition on-line, SCE has elected to shutdown Unit 2. Plant Operators initiated the shutdown at about 2155 PST on February 14, 2005. SCE in reporting this occurrence in accordance with 10CFR50.72(b)(2)(i). "At the time the shutdown was initiated, Unit 2 was operating at about 100% power. Unit 3 continues to operate at about 100 % power. The NRC Resident Inspectors have been briefed on the shutdown plans and will be provided with a copy of this report." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-02-15
41409 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2004-12-27 | 2005-02-14 15:13 | 2005-02-18 | GEORGIA AGREEMENT STATE REPORT - MISSING RADIOACTIVE SOURCE The following information was received from the State via facsimile: "Description of Event: On December 27, 2004, Shaw Industries, a general licensee, contracted with Graves & Phillips Engineering & Maintenance (Alabama License Number 1291) to have four sources removed and returned to the supplier, Omhart. Upon arrival at Omhart on February 4, 2005, the package contained only three sources and one detector. Shaw Industries reported that the fourth source was possibly left on the line where it was used to measure thickness of carpet and that line was sent to a scrap metal yard on January 11, 2005. However, it is still undetermined what has happened to the missing source. "The Environmental Radiation Staff and representatives from Shaw Industries have been dispatched to the scrap metal yard to investigate the incident. The source holder was Omhart Vega Model BAL and serial number 3781 BC. Isotope: Sr-90. Amount of activity: 25 milliCuries." Georgia Event Report ID GA-05-05. * * * UPDATE FROM C. SANDERS TO J. ROTTON AT 1549 ON 02/15/05 * * * 2 personnel from the Georgia Environmental Radiation Staff, 5 representatives from Shaw Industries, and 5 representatives from Regional Recycle are scheduled to physically dismantle the trash pile on 02/16/05 where the missing source is believed to be located and conduct a thorough search for the source. The pile is approximately 40' high, 35 yards wide, and 85 yards long. Notified R1DO (Cobey) and NMSS EO (Moore). * * * UPDATE FROM L. SEALE TO J. KNOKE AT 11:18 ON 02/16/05 * * * "February 14, 2005 The Radioactive Materials Program notified the NRC Operations Center of the event. Attempts to find the source by Shaw Industries' representatives and Environmental Radiation Staff were unsuccessful. The scrap pile that may contain the source is approximately 75-100 yards long, 30-40 yards wide, and 40' to 50' high. Regional Recycling stated that there was a 99% chance that the material was destined for the steel mill across the street from their facility, that is, a 1% chance that the material would be sent to a scrap yard in Kentucky. "February 15, 2005 Environmental Radiation Staff notified the state of Alabama of the event and ongoing investigation due to Graves & Phillips Engineering & Maintenance, an Alabama licensee. Shaw Industries forwarded to the Environmental Radiation Program dose profiles and pictures of the source device received from Ohmart. Regional Recycling reviewed its records and no shipments had been sent to the Kentucky facility since November 2004. All facilities were notified of the event and pictures and descriptions of the device were sent to the facilities that may receive scrap metal from Shaw Industries. "Shaw Industries and the Radiation Program were informed by Regional Recycling (scrap yard) that they wanted to dismantle the scrap pile to try to locate the source. Shaw Industries, Regional Recycling and the Environmental Program will provide staff to facilitate the search. The search is to begin on February 16, 2005. Regional Recycling has halted their operations until the search is completed. The Radioactive Materials Program updated the NRC Operation Center on the status of the event. "February 16, 2005 Shaw Industries and the Environmental Program are currently at Regional Recycling and are visually inspecting the scrap as it is sorted by a crane. The Radioactive Materials Program updated the NRC Operation Center on the status of the event." Notified R1DO (Cobey) and NMSS EO (Essig). * * * UPDATE PROVIDED BY J. HARDEMAN TO JEFF ROTTON AT 1423 EST ON 02/18/05 * * * At 1000 EST on 02/18/05, the missing source was located at the Regional Recycling facility in a different scrap pile from the original search. The source is in the possession of Shaw Industries as of 1410 EST on 02/18/05. A representative from Ohmart will arrive at the Shaw Industries facility on 02/23/05 to perform a source inspection and leak test. Notified R1DO (Lorson) and NMSS EO (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2005-02-17
41408 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2005-02-13 19:00 | 2005-02-13 22:16 | 2005-02-13 | HIGH PRESSURE COOLANT INJECTION SYSTEM (HPCI) DECLARED INOPERABLE The following text report was received from the licensee via facsimile: "The High Pressure Coolant Injection (HPCI) system was declared inoperable on 2-13-05 at 19:00 EST due to loss of position indication to MO-2301-8 (HPCI injection valve #2) in the control room and at the system alternate shutdown panel. The other ECCS [Emergency Core Cooling] Systems remain operable. Position indication was restored after control power fuses were replaced. HPCI was returned to operable status at 21:50 EST, 2-13-05." The licensee has notified the NRC Resident Inspector and will be notifying Massachusetts Emergency Management Agency. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-02-13
41407 | 0 | MID-PACIFIC TESTING & INSPECT SVC |  |  |  |  | 2005-02-13 | 2005-02-13 12:20 | 2005-02-11 | TROXLER MOISTURE DENSITY GAUGE STOLEN FROM BED OF PICKUP TRUCK Sometime between the late afternoon on Friday, 2/11, and Sunday at 0600 HST, 2/13, a Troxler Moisture Density Gauge Model 3440, S/N 25490, and its case were stolen from the bed of the company pickup while parked in the Kalihi area of Honolulu, HI. Both the chain and cable securing the case were cut. The Model 3440 contains two (2) radioactive sources; 8 millicuries Cs-137 and 40 millicures Am-241/Be. The licensee contacted the Honolulu Police Department and will offer a reward for its return. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | HI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-02-13
41406 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-02-11 22:26 | 2005-02-12 04:09 | 2005-02-12 | POSTULATED LOSS OF AFW PUMPS FOLLOWING TORNADO DAMAGE TO CONDENSATE STORAGE TANK "Plant engineering staff discovered that the auxiliary feedwater (AFW) system discharge pressure trip protective equipment may not operate to protect the AFW pumps from condensate storage tanks (CST) failing from a tornado event. The AFW system protection design uses discharge pressure switches to protect the AFW pumps from a loss of suction pressure. The AFW system is required equipment to support a plant shutdown which is also assumed to occur as a result of a tornado. "Current analysis predicts substantial damage to the CSTs caused by a tornado. The CSTs are aligned as the AFW pumps' initial/preferred water source. The tank damage is predicted to result in a rapid, near complete, loss of water inventory due to a tornado. The CST volume loss quickly causes air to enter the pump suction piping to all three AFW pumps. Under the postulated conditions, the current discharge pressure switch design does not act fast enough to trip the pumps before significant pump damage can occur, it appears that the original design analyses failed to consider the consequences of a loss of suction source causing air to enter the pump suction. "The design basis for AFW pump discharge pressure switches, in part, is assumed to protect the AFW pumps from damage due to a tornado. Given the event postulated as described, the pressure switches may not meet this design basis assumption. Therefore, all three AFW pump discharge pressure switches were declared inoperable at 2226 on 2/11/2005. "To ensure the AFW Pumps are protected in the event of a tornado, compensatory actions were incorporated in Operating Procedure E-0-05 Response to Natural Events. At the earliest indication of a tornado threat (i.e. Tornado Watch, Warning or Strike) operators are directed to align Service Water to the AFW Pump Suction to ensure adequate NPSH In the event of a loss of the CST supply. These actions do not replace the automatic function but ensure the pumps are protected against loss of NPSH. Based on the proceduralized compensatory actions put in place, the AFW Pump Low discharge Pressure Trips were declared Operable but Non-Conforming at 0056 on 2/12/2005." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2005-02-12
41405 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2005-02-11 19:59 | 2005-02-11 23:44 | 2005-02-12 | RPS ACTUATION The following text was obtained from the licensee via facsimile: "At approximately 1959 hours Central Standard Time, Grand Gulf Nuclear Station experienced a loss of Electrical Bus 11R. This caused a loss of additional electrical buses, and a subsequent reactor scram on low reactor water [level]. The feedwater system was lost, and reactor low level 2 was reached. The Reactor Core Isolation Cooling System and High Pressure Core Spray System injected into the reactor and restored reactor water level. A primary containment, secondary containment, and drywell isolation occurred as expected. The Division 1 Diesel started and picked up the Division 1 bus. The Division 3 Diesel Generator started on the reactor low water level 2. The condenser is removing decay heat. The plant status currently is stable, with normal reactor water level and feedwater restored. All control rods inserted. The cause for the loss of Bus 11R is under investigation. Safety systems appeared to function as designed." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-02-12
41404 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-02-11 16:29 | 2005-02-11 20:29 | 2005-02-11 | AUTOMATIC REACTOR SCRAM DUE TO A LOAD REJECTION The following text was obtained from the licensee via facsimile: "At 1629 [hrs. CST] on 02/11/05, Unit 3 reactor scrammed from 100% power when the output breaker tripped causing a load reject. The breaker tripped due to a corresponding switchyard breaker 5268 tripping when a PK block was re-installed before the trip cutout (TCO) switches were placed in TCO. All rods inserted. Unit 2 was also at 100% power and was unaffected by this event. Water level lowered to +1" as expected and was recovered by normal feed water flow. All expected PCIS [Primary Containment Isolation System] isolations, Group 2 (RHR S/D [Residual Heat Removal] cooling), Group 3 (RWCU [Reactor Water Clean Up]), Group 6 (ventilation), and group 8 (TIP [Transverse Incore Probe]) were received along with the auto start of CREV [Control Room Emergency Ventilation] and the 3 SGT [Standby Gas Treatment] trains. Four MSRV's [Main Steam Safety Relief Valves] lifted momentarily to stabilize reactor pressure. "This event is reportable as a 4-hour and 8-hour Non-Emergency Notification along with a 60-day written report in accordance with 10CFR50.72(b)(2)(iv)(B), 10CFR50.72(b)(3)(iv)(A) and 10CFR50.73(a)(2)(iv)(A) as 'Any event or condition that results in a valid actuation of RPS [Reactor Protection System] and PCIS .." The plant was performing restoration from switchyard maintenance at the time of the scram. All safety relief valves that lifted properly re-seated. Decay heat is being removed via the steam bypass valves to condenser. The electrical grid is stable. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-02-11
41403 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-02-11 19:30 | 2005-02-11 19:54 | 2005-02-11 | NOTIFICATION TO NEW YORK STATE PSC INVOLVING RADWASTE SHIPMENT INCIDENT OFFSITE "Notified by Barnwell Waste Management Facility that the filter liner sent to the Facility had arrived and that they found 'waste outside the liner.' This is a violation of the Barnwell license. "This notification is made in accordance with the New York State PSC [Public Service Commission] requirements per corporate procedure. "Ref: CR-IP2-2005-00613" The licensee will inform the State of New York and had informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2005-02-11
41402 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2005-02-10 23:00 | 2005-02-11 00:16 | 2005-02-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF ELECTRICAL POWER SOURCES "Event: At 23:00 [EST] on 2-10-05, Oconee Unit 1 initiated a plant shutdown as required by its Technical Specifications. Technical Specification 3.8.1 Condition M, Required Action M.1 requires Oconee Unit 1 to enter Mode 3 by 03:06 on 2-11-05 due to Keowee Hydro Unit 2 and CT-1 inoperable. Keowee Hydro Unit 2 is inoperable due to a planned outage, with restoration in progress. CT-1 is inoperable due to experiencing a lockout at 12:12 on 2-10-05 during testing to restore Keowee. "Initial Safety Significance: Oconee Unit 1 is being shut down in accordance with Technical Specifications. Unit auxiliaries will be powered from the Standby busses and a Lee Combustion Turbine. When the turbine is tripped, the Unit will enter into the natural circulation mode of cooling due to loss of Reactor Coolant Pumps. "Corrective Action(s): 1) Restoration of Keowee Hydro Unit 2 is in progress. 2) A Unit Threat Team has been assembled and is investigating the cause of the lockout on CT-1. CT-2 cross connect is in progress to allow the unit, if tripped, to avoid loss of Reactor Coolant Pumps." The licensee notified the NRC Resident Inspector. * * * * UPDATE FROM D. NIX TO M. RIPLEY 0016 EST 02/11/05 * * * * At the time of the initial notification, Oconee reported that, at 2346 EST on 02/10/05, the CT-2 cross connect has been completed, allowing the unit, if tripped, to avoid a loss of Reactor Coolant Pumps. The power reduction to enter Mode 3 by 03:06 continues. Restoration of Keowee Hydro Unit 2 and investigation into the cause of the lockout on CT-1 remain in progress. The licensee notified the NRC Resident Inspector. Notified R2 DO (M. Widman), IRD (Crlenjak), and NRR EO (W. Beckner). * * * * UPDATE FROM J. COLLINS TO W. HUFFMAN 0045 EST 02/11/05 * * * * At 0033 EST 02/11/05, restoration of Keowee Hydro Unit 2 to operable status was completed and Technical Specification 3.8.1 Condition M, Required Action M.1 requiring Oconee Unit 1 to enter Mode 3 by 03:06 on 2-11-05 was exited. The power reduction was stopped with power at 85% at 0034 EST. Technical Specification 3.8.1, Condition A, which was entered on 1106 EST on 02/10/05, requires restoration of CT-1 by 2306 on 02/11/06. The licensee notified the NRC Resident Inspector. Notified R2 DO (M. Widman), IRD (Crlenjak), and NRR EO (W. Beckner). | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-02-11
41401 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2005-02-10 16:00 | 2005-02-10 22:56 | 2005-02-10 | RCS LEAKAGE IDENTIFIED DURING PLANT STARTUP WALKDOWNS "On 2/10/2005, St. Lucie Unit 2 was in Mode 3 returning from refueling outage SL2-15. At 0605 during plant startup walkdowns, 2 leaks were discovered on the instrument line to the 2B1 safety injection header. Closing the instrument root isolation valve to PT-3339 isolated one leak. The second leak was under the insulation and later upon evaluation it was concluded to be ASME section Xl RCS pressure boundary leakage based on its location between the reactor coolant system loop check valves. "The leakage source is from the 2B1 safety injection tank and not directly from the reactor coolant system because the first reactor coolant system loop check valve is maintaining pressure isolation. As a result this is not Technical Specification pressure boundary leakage. The pressure instrument root is downstream of the Safety Injection Tank (SIT) isolation valve and between the two reactor coolant system loop check valves. Isolating the SIT from the header isolated second leak. An engineering response team was formed and repairs are being planned. RCS heat removal is being accomplished via the Steam Generators and the Atmospheric Dump Valves. Feedwater is being supplied to the Steam Generator by the Auxiliary Feedwater System. Plant electrical loads are supplied from offsite sources through the Startup Transformers." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2005-02-10
41400 | 0 | WATTS BAR | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-02-10 17:01 | 2005-02-10 17:01 | 2005-02-10 | OFFSITE NOTIFICATION DUE TO TRITIUM SAMPLE EXCEEDING OFFSITE DOSE CALCULATION MANUAL (ODCM) REPORTING LEVEL The following information was obtained from the licensee via facsimile: "On 2/10/2005 with Watts Bar, Unit 1 operating at 100 percent Reactor Power, TVA plans to voluntarily notify the State of Tennessee's radiological and environmental health agencies and Department of Energy that a tritium sample obtained from a onsite monitoring well was confirmed to be above the Offsite Dose Calculation Manual (ODCM) reporting level for ground water samples. This result was for an ODCM required composite sample obtained over a month (12/29/04 through 1/25/05). On 2/8/2005, Chemistry confirmed this result and established a team to investigate the source of this contamination, the cause of the increased tritium levels, and the extent of where the tritium is found. Additional samples have been collected from selected monitoring wells, and the results of these tests are being analyzed. At this time, there is no indication of any offsite release, there is no threat to the public or company employees, and the situation does not pose a public health hazard. This notification is in accordance with 10 CFR 50.72, (b)(2)(xi), 'News Release or Notification of Other Government Agency'." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Decommissioned |  | Power Operation | Decommissioned |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-02-10
41399 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2005-01-18 | 2005-02-10 15:53 | 2005-02-10 | AGREEMENT STATE REPORT INVOLVING LESS THAN PLANNED DOSE FRACTION FOR CERVICAL CANCER The following is excerpted from a transmittal sent by the licensee and received on 2/3 by the State of KY concerning a medical event: "1. Licensee's name: Brown Cancer Center, University of Louisville Hospital "2. Prescribing physician's name: [Attending Physician] "3. A brief description of the event: On Tuesday, January 18, 2005 a patient was scheduled to undergo a vaginal cylinder HDR procedure using a 3.0 cm cylinder. The catheter was placed in position [under the supervision of the Attending Physician]. When the setup was complete, and upon leaving the room [the Resident Physician] noticed that the catheter was 'draped' around the patient's foot as it ran from the cylinder to the HDR machine. [The Resident Physician] 'undraped' the catheter from her foot, then all staff left the room. The treatment then ran for it's scheduled 5.5 minutes. "After the treatment was completed, the Medical Physicist removed the catheter. He noticed that the catheter appeared to not be fully inserted into the cylinder as required and estimates that it may have been withdrawn from the desired location by approximately 15 cm. He promptly informed [the Attending and Resident Physicians] and together informed [the] Chairman of Radiation Oncology. "4. Effect on the individual: This treatment was the second of three treatments prescribed. The patient is being monitored and no adverse effects to the patient are expected nor did any occur. "5. Why the event occurred: The event occurred due to the lack of a positive mechanical 'lock' of the HDR catheter to metal guide insert tube. The system uses a moveable nylon collar surrounding the catheter, which is slid into position once the catheter is placed into the metal guide insert tube. A nut is then screwed over the nylon collar forming a 'compression' fitting much like that used for compression fittings on copper-tubing. The event may have occurred when [the Resident Physician] 'undraped' the catheter which was 'draped' around the patient's foot. The nylon collar-nut compression fitting may have allowed the catheter to be pulled partially out of the metal guide tube. "6. What improvements are needed to prevent recurrence The manufacturer also offers a different type of collar-nut compression fitting utilizing a stainless steel collar that is glued onto the catheter at the appropriate distance. This constitutes a 'positive' mechanically locked position for the catheter. This alternate system is being readied for use henceforth. "7. Action taken to prevent recurrence: The catheter is now length/position marked and is checked by both the physician and the physicist prior to leaving and upon re-entering the HDR suite. A soon as the parts are assembled for the stainless steel type of collar, the HDR catheters will be switched over to the new equipment. This will provide a 'positive' lock on catheter length into the metal guide tube assembly. "8. If licensee informed the individual or individual's responsible relative or guardian, and if not, why: The patient and referring physician were informed of the situation by [the Attending Physician]. "9. Information provided to the individual or individual's responsible relative or guardian: The patient was informed that she may have received a dose lower than that prescribed to the area of intended treatment. She was informed that the treatment would not be repeated (this was the second of three treatments planned) as it was not absolutely clear if an under dose occurred. She was told that she would be carefully monitored for progress." A followup transmittal from the licensee received on 2/9 by the state of KY provided estimated dose data: "As the report described, during the treatment the source for the HDR may have been withdrawn from the desired treatment site by 15 cm. The dose desired for the 5.5 minute treatment was seven hundred and fifty (750) cGy to the site of interest. With the source offset by 15 cm, the delivered dose would have been four (4) cGy. Assuming that the source was in fact approximately 2 cm exterior to the vagina, the dose at the labia would have been one hundred (100) cGy." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2005-02-15
41398 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-01-23 | 2005-02-10 15:14 | 2005-02-24 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "On 2/10/05 at 13:35, the Shift Manager became aware of a condition that previously existed which met the Emergency Plan criteria for declaration of an Unusual Event. On 1/23/05, a Radiation Protection Technician released nitrogen into the RAF Countroom as part of an experiment. During the experiment, the atmospheric monitors in the room detected life-threatening levels of nitrogen (oxygen deficient atmosphere). This has been determined to meet the criteria for an Unusual Event per Emergency Classification Level Chart P for a release of toxic or flammable gas on site and portable monitors indicate concentrations at life threatening levels." Management became aware of the unauthorized experiment conducted by the Technician during a management review. There were no personnel injuries as a result of this incident. The licensee will inform both state/local agencies and the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (ROBB) TO NRC (HUFFMAN) AT 1907 EST ON 2/24/05 * * * "On 2/24/05 at approximately 1720 hours, it was discovered that a second incident had occurred prior to the previously reported occurrence (EN#41398) that met the Emergency Plan criteria for an Unusual Event declaration. Based on the investigation of the 1/23/05 incident, the same Radiation Protection Technician had released liquid nitrogen in the Auxiliary Building elevator, as part of the same data collection activity. The release may have been at the levels of 'Immediate Danger to Life and Health' in this separate case. This previous incident occurred on 1/22/05 at approximately 1200 hours." The licensee will inform both state/local agencies and the NRC Resident Inspector. R3DO(Lanksbury), NRR EO (Carpenter), and IRD (Kennedy) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW | [5 empty] | 0 | 2005-02-10
41397 | 0 | DOMINION |  |  |  |  | 2005-02-10 | 2005-02-10 14:23 | 2005-02-10 | PART 21 NOTIFICATION INVOLVING ABNORMAL ALLEN-BRADLEY 700RTC RELAY CONTACT RESPONSE The following information was submitted via fax: "Reason for Message: Report a Part 21 - Regarding the abnormal response of Alien-Bradley 700RTC relays when configured with the NC contact in the C5-C6 position. "Event Date: 2/8/05 "Unit Name: North Anna Power Station "Component Information (as applicable): "Manufacturer: Allen-Bradley "Part Number: 700RTC11110U1 "Description: Abnormal contact response was observed during pre-installation testing of Allen-Bradley 700RTC relays. The 700RTC relays are solid state timing relays used in several Safety Related applications at North Anna. The 700RTC relay provides a wide time adjustment. The relay has two timed contact positions and two instantaneous contact positions. The relays are ordered to a part number that specifies a certain contact arrangement, but the contacts are fully interchangeable and may be configured by the end user in any combination of Normally Open/Normally Closed (NO/NC). Removable contact cartridges mount in the contact slots. At North Anna, Allen-Bradley part number 700RTCI1110U1 is used, which is a contact configuration of NO, NC, NO, NC. "The relays were setup and tested in a NO, NO, NC, NC configuration when it was discovered that the instantaneous contact (C5-C6 position), with a NC contact cartridge installed, behaved like a timed contact. The C5-C6 position changed state according to the setting of the timer. All other contact positions worked properly. With a NO contact installed in the C5-C6 position, the contact position behaved as expected (as an instantaneous contact). Different NC contact cartridges were installed in the C5-C6 position of the relay and the anomaly still occurred. Forty-five (45) relays were tested for this anomaly. Twelve of 45 relays failed testing (C5-C6 with NC contact behaved like a timed contact). The relays were returned to Allen-Bradley for failure analysis. Allen-Bradley has duplicated the anomaly using the returned relays and one from their stock. The root cause is still under investigation. "The 700RTC relays are used as replacements for Agastat Relays in certain Safety Related applications. Over the past ten years, several 700RTC relays have been installed in various locations at North Anna. At North Anna, the 700RTC relays are purchased commercial grade then upgraded for safety related use using the commercial grade dedication process. The upgrade is performed by the North Anna Materials Verification Lab using an approved commercial grade dedication plan. Prior to identification of this anomaly, the dedication testing verified proper contact operation of the contact cartridges in the as-received configuration. The dedication process now verifies proper contact operation in all possible contact configurations. "Current and planned 700RTC relay installations were reviewed. The majority of installed 700RTC relays are configured with the contact cartridges arranged according to the 700RTC11110U1 part number (NO, NC, NO, NC). In a few locations, the contact cartridges are configured NO, NO, NC, NC. North Anna does not utilize the C5-C6 position with the NC contact cartridge in any of 700RTC locations. "Prior to installation, 700RTC relays are bench tested for satisfactory operation. "Causes: The root cause is unknown at this time, although Allen-Bradley has indicated that the sensitivity of the contact cartridges may be a factor in causing this response. "Corrective Actions: Nine of the relays that failed bench testing were sent back to Allen-Bradley for analysis. North Anna is working with Allen-Bradley to determine a cause. "Industry Notification: OE notification No. 19273 - Abnormal response of Allen-Bradley 700RTC relays when configured with the NC contact in the C5-C6 position." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2005-02-10
41396 | 0 | FRAMATOME ANP |  |  |  |  | 2005-02-10 | 2005-02-10 09:45 | 2005-02-10 | REPORTABLE DEFECT IN SIS CONTROL WIRE The following information was received via facsimile: "Basic component which fails to comply or contains a defect: The component which is defective is a SIS Control Wire. Identification of the firm constructing the facility or supplying the basic component which fails to comply or contains a defect: Framatome ANP "Nature of the defect: This issue concerns defective crimps associated with AMP Faston Flag Receptacles (with Tab-Lok features) utilized on SIS Control Wire which was supplied to STP [South Texas Project] Nuclear Operating Company. A failure of the crimp connection could cause an unwanted action or prevent a desired action that could affect the operation of a safety related system. A variety of safety related systems could be impacted depending on where the wires are used. This commercial grade product was manufactured/supplied by Eaton Electrical and dedicated/supplied by Framatome ANP for a safety-related application on DS Type Circuit Breakers. The defective wires were identified prior to installation in the plant. "The date on which the information of such a defect or failure to comply was obtained: This issue was determined to be a deviation on February 8, 2005. "In the case of a basic component which fails to comply, the number and the location of all such components in use at, supplied for, or being supplied for one or more facilities or activities subject to the regulations in this part: Framatome ANP supplied 50 SIS Control Wires to STP Nuclear Operating Company. "The corrective action which has been, is being, or will be taken; the name of the individual or organization responsible for this action; and the length of time that has been or will be taken to complete the action: Framatome ANP contacted STP Nuclear Operating Company and requested that all 50 SIS Control Wires supplied by Framatome ANP be returned. To prevent further occurrence of this problem Framatome ANP has taken a number of corrective actions in conjunction with the company supplying the commercial grade product, including additional inspection requirements in the dedication process to ensure crimps meet the manufacturers requirements." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | VA | OTH | PAR | 21.21 |  |  |  | 0 | 2005-02-10
41395 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2005-01-07 | 2005-02-10 09:30 | 2005-02-10 | AGREEMENT STATE REPORT OF RADIOGRAPHY CAMERA MALFUNCTION "Radiography operations were being performed with an AEA Technologies Model 741 camera with a 33 Ci source of Cobalt-60. The radiographers could not get the source to return to the shielded position. It was determined that a mechanical failure had occurred in the connector to the drive cable which transports the source from its shielded position into the exposure position and back again. The mechanical failure is being analyzed by the equipment manufacturer. " The Louisiana Department of Environmental Quality stated that one of the individuals involved in the event received a film badge dose of 2552 mRem. State report ID is LA050001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2005-02-15
41394 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-02-09 20:20 | 2005-02-09 22:10 | 2005-02-10 | OFFSITE NOTIFICATION DUE TO PRESS RELEASE FOR PLANT SHUTDOWN The following information was obtained from the licensee via facsimile: "STP [South Texas Project] Nuclear Operating Co. will be making a press release concerning the shut down of Unit 2. STPNOC will be sharing the press release with various locals and state government agencies and the media. "NRC was notified of the TS [Technical Specification] required shutdown on 2/9/05 (EN# 41392)" The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 1700 EST ON 2/10/05 FROM KLAY KLIMPLE TO S. SANDIN * * * "STP Nuclear Operating Company (STPNOC) issued a press release at 1503 today concerning the status of the shutdown of Unit 2. STPNOC has shared the press release with various local and state government agencies and the media. "NRC was notified of the Technical Specification required shutdown on 2/9/05 (Reference EN# 41392)." The licensee informed the NRC Resident Inspector. Notified R4DO (Blair Spitzberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-02-09
41393 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-02-09 09:30 | 2005-02-09 19:12 | 2005-02-09 | CALIFORNIA AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was obtained from California Department of Health Services, Radiation Health Branch - Berkeley / Region 3 via facsimile: "A CPN Model MC-1DRR-P moisture density gauge was run over at a construction site at Valencia Street between 14th and 15th Street in San Francisco, CA approximately at 9:30 am. The gamma source rod was in the extended position at the time of the incident. The source tip rod containing 10 [milliCuries of] Cs-137 was intact but was slightly bent and could not be retracted into the safe position. The 50 [milliCurie] Am-241/Be source was intact as designed. Mr. [DELETED] from CPN was at the site after the incident. A screen leak test performed by Mr. [DELETED] did not indicate any contamination. Gauge was picked up by CPN at the site and held for disposal." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-02-14
41392 | 0 | SOUTH TEXAS |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-02-09 12:22 | 2005-02-09 16:20 | 2005-02-09 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO UNISOLABLE PRESSURE BOUNDARY LEAK The following information was obtained from the licensee via facsimile: "On February 9, 2005, at 1222 hours [CST], South Texas Project Unit 2 commenced a reactor shutdown required by Technical Specification (TS) 3.4.6.2, 'Reactor Coolant System - Operational Leakage.' "Following investigation into an increasing containment atmosphere particulate radiation monitor trend, primary leakage (steam plume) was discovered coming from a 3/4 inch vent line off of the 'A' Cold Leg Safety Injection line. The leak is located in an area between the Safety Injection line and the first vent line isolation valve, and is therefore considered an unisolable pressure boundary leak. TS 3.4.6.2 requires that with any Pressure Boundary Leakage, the Unit must be in at least Hot Standby within 6 hours and in Cold Shutdown within the following 30 hours. At the time of discovery, the total unidentified reactor coolant system leak rate was determined to be 0.13 gpm. "The vent line pipe and weld material is stainless steel. "This notification is being made in accordance with 10 CFR 50.72 (b)(2)(i) for commencement of a TS required shutdown, and 10 CFR 50.72 (b)(3)(ii)(A) for the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded." There is no impact on South Texas Project Unit 1. The licensee has notified the NRC Resident Inspector. | 0 | 54 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2005-02-09
41391 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-02-09 12:03 | 2005-02-09 15:46 | 2005-02-09 | OFFSITE NOTIFICATION DUE TO REPORTABLE QUANTITY SPILL CONTAINED ON SITE The following information was obtained from the regulatee via facsimile: "On 2/09/05 at approximately 1025 hours [EST] , a Hazardous Material spill occurred on plant site. Utility operations was transporting a small tank (app. 320 gallon capacity) of Sodium Hypochlorite with a fork truck. The tank tipped off of the forks, hit the ground, and landed on its side causing the cap to come off. Approx. 150 gallons of Sodium Hypochlorite spilled to the ground resulting in a hazardous material spill. "At 1203 hours, the Plant Shift Superintendent notified the National Response Center and the Ohio EPA that a Reportable Quantity (RQ) of hazardous material (Sodium Hypochlorite)) was released to the ground. No material left the immediate area and clean-up of the spill is currently in process. UE2-RA-RE1030, Appendix D, section P requires a 4-hour NRC event [notification] when other government agencies are notified." There were no personnel injuries or plant equipment damaged as a result of the spill. The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2005-02-09
41390 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2005-02-09 09:20 | 2005-02-09 14:22 | 2005-04-08 | BOTH TRAINS OF THE CONTROL STRUCTURE EMERGENCY OUTSIDE AIR SUPPLY SYSTEM INOPERABLE "At 09:20 am, on February 9th, the control room declared both trains of Control Structure Emergency Outside Air Supply System (CREOASS) inoperable. The control room was notified of an inoperable boundary door that was not closed and latched and therefore would not have allowed CREOASS to perform its safety function of maintaining the Control Structure at a positive pressure if required. The door was closed and locked [at 11:15] to restore the habitability boundary. "The door has since been repaired [adjustment of latch mechanism]. "Initial investigation determined that the door had been unlocked at approximately 09:20 this morning by an elevator vendor to perform maintenance. "This is being reported as an event or condition that could have prevented the fulfillment of the safety function required to mitigate the consequences of an accident. "CREOASS was not called upon to function during the period that the door was not operable." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM LICENSEE (ROBINSON) TO NRC (HUFFMAN) @ 1328 EDT ON 4/8/05 * * * The following information was provided by the licensee (licensee text in quotes): "On 2/9/2005, PPL Susquehanna LLC reported a loss of safety function for the Control Room Emergency Outside Air Supply System (CREOASS) based on one of the Control Structure Habitability boundary doors being found partially open. Positive air pressure generated by the Control Structure HVAC System prevented the door closure mechanism from maintaining the door closed. The door was closed to restore the habitability boundary. "The event was reported as a condition that could have prevented the fulfillment of the safety function required to mitigate the consequences of an accident. "The Safety Function of the CREOASS is to provide adequate radiation protection to permit occupancy of the Control Room under accident conditions for the duration of the accident. The CREOASS accomplishes this by: 1) filtering the outside make-up air supply and 2) maintaining a positive pressure in the control structure habitability boundary to limit unfiltered air in leakage into the boundary. A subsequent engineering evaluation concluded that with the door closure mechanism providing a resistive force, CREOASS would have been able to maintain a positive pressure within the boundary and perform its safety function as described above. In conclusion, the reported condition did not result in a loss of safety function under 10CFR50.72 (b)(3)(v)(D) and is therefore being retracted." The NRC Resident Inspector and R1DO (Noggle) have been notified. | 100 | 91 | 0 | 100 | 91 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-02-09
41389 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2005-02-09 01:04 | 2005-02-09 03:31 | 2005-02-09 | TECHNICAL SPECIFICATIONS REQUIRED SHUTDOWN DUE TO LOSS OF NORMAL AND ALTERNATE POWER TO SAFETY BUS "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 9, 2005, at approximately 01:04 MST, Palo Verde Nuclear Generating Station (PVNGS) Unit 1 commenced a reactor shutdown required by Technical Specification 3.8.1. "Limiting Condition for Operability (LCO) 3.8.1 requires two independent AC sources be available. On February 6, 2005, at approximately 22:19 Mountain Standard Time (MST) a valid actuation of the Palo Verde Nuclear Generating Station Unit 1 Train 'B' Emergency Diesel Generator (EDG) occurred as a result of under-voltage on its respective safety bus (PBB-S04). EDG 'B' started and loaded as designed to energize PBB-S04. (Reference EN #41379 reported on 02/06/2005). "The loss of power to the safety bus was the result of a fault associated with 13.8KV breaker NAN-SO6J which caused breakers NAN-S06H (normal power supply), NAN-S06K (alternate power supply), and NAN-S06J (EOF & TSC Bldg power supply) to all trip open on over-current. This action resulted in the de-energization of NAN-SO6, NAN-S04, and PBB-S04. PVNGS will be unable to make repairs and restore the required second independent AC power source with the allowed 72 hour required action time frame. "The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified." | 85 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2005-02-09
41388 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-02-08 12:00 | 2005-02-08 20:36 | 2005-02-08 | CALIFORNIA AGREEMENT STATE REPORT- LOST RADIOACTIVE MATERIAL The California Radiation Health Bureau reported that a radiopharmaceutical carrier had lost 112 milliCuries of Thallium-201. The shipment of thallium was picked up at the airport in Burbank, CA and was in transport to Loma Linda, CA when it was discovered missing. The carrier had made two stops after picking up the product in Burbank, CA. The carrier reported that when they left Placentia, CA, (the second stop) their truck tailgate was closed. When they reached Loma Linda, CA, they discovered that the tailgate was open. It is believed that the package with the thallium fell out on the interstate between Placentia and Loma Linda. The carrier searched the route twice without success. The State of California did notify the California Highway Patrol of the missing package. California incident number is 020805. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-02-11
41387 | 0 | HALLIBURTON ENERGY SERVICES |  |  |  |  | 2005-02-08 11:30 | 2005-02-08 16:42 | 2005-02-15 | LICENSEE REPORTED A SHIPMENT THEY WERE TO RECEIVE IS UNACCOUNTED FOR Halliburton Energy Services had shipped a well logging source and calibrating source containing 18.5 curies of Am-241 Be and .5 curies of Am-241 from Nizhnevartovsk, Russia to Houston TX. Both sources were in a 18" dia 23" long cylindrical type "A" container which weighed 83kg. The sources went through Amsterdam to JFK in New York and cleared customs in New York on 10/09/04. After clearing customs they have not been able to track the package to any of the transport companies that were scheduled to handle it. An ongoing search is still being conducted. * * * UPDATE ON 02/09/05 @ 1751 FROM RICHARD ARSENAULT TO CHAUNCEY GOULD * * * The licensee was notified at 1621 CT that the unaccounted for sources were located at the Forward Freight facilities in Boston, MA. It appears that they were trucked to Boston after a Boston label was inadvertently placed on the package at the Newark facility of Forward Freight. The licensee stated the package appears to be intact and the are sending a rep to Boston on 2/10/05. Notified Regs 1 & 4, NMSS, PAO, DHS, DOT, DOE, IP, TAS, STP * * * UPDATE ON 02/10/05 @ 1358 HRS. EST FROM ARSENAULT TO CROUCH * * * A representative from Halliburton Energy Services has verified that the sources and packaging are intact and all source material is accounted for. Forward Air Freight is scheduled to ship the package to Halliburton in Houston, TX. Notified R1DO (Cobey), R4DO(Whitten), R4 (Cain) and NMSS (Essig). * * * UPDATE ON 2/13/05 @ 2348 EST BY S. SANDIN * * * During administrative review of this report, two (2) corrections were made; the previously shown notification time of 1921 EST was corrected to read 1642 EST, and the 10 CFR Section citation of 20.2201(a)(1)(ii) was corrected to read to show 20.2201(a)(1)(i). * * * UPDATE FROM HALLIBURTON (BROWN) TO NRC (HUFFMAN) AT 10:33 EST ON 02/14/05 * * * The licensee reported that the source has arrived in Houston and is currently enroute to the Halliburton facility and is scheduled to arrive at 1100 CST. R1DO( Lorson), R4DO (Whitten), and NMSS (Moore). * * * UPDATE FROM HALLIBURTON (BROWN) TO JEFF ROTTON AT 1601 EST ON 02/15/05 * * * The licensee reported that the source was delivered to the Halliburton facility at 1100 CST on 02/14/05 and has been satisfactorily inspected and leak tested with no problems. Notified R1DO (Cobey), R4DO (Whitten), and NMSS (Moore). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-02-08
41386 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2005-02-08 09:20 | 2005-02-08 16:45 | 2005-03-27 | STEAM-DRIVEN AUXILIARY FEEDWATER (AFW) PUMP DECLARED INOPERABLE DUE TO DESIGN ISSUE The following information was obtained from the licensee via facsimile: "At 0920 [hrs.] CST, on February 8, 2005, Fort Calhoun Station declared the steam driven auxiliary feedwater (AFW) pump (FW-10) inoperable due to discovery of a design problem with the pump turbine. The station entered the appropriate technical specification action statement at that time. The pertinent action statements for auxiliary feedwater ([T.S.] 2.5.1) read as follows: "B (Action statement): With one AFW train inoperable for reasons other than condition A, restore the AFW train to OPERABLE status within 24 hours. "C (Action statement: If the required action and associated completion times of condition A or B are not met, then the unit shall be placed in MODE 2 in 6 hours, in MODE 3 in the next 6 hours, and less than 300 [degrees] F without reliance on the steam generators for decay heat removal within the next 18 hours. "A change to the design basis is in progress to allow the pump to be made operable within 24 hours." The design problem is due to the AFW pump drains. The manufacturer states that the drain lines must drain below the level of the AFW turbine. The current configuration is that the drains are aligned to the condenser which is approximately 18 feet above the elevation of the AFW turbine. This is not a problem during normal AFW turbine operation as the condenser would most likely be in service. However, the condenser cannot be relied upon during all accident conditions that require AFW actuation. The licensee has notified the NRC Resident Inspector. *** RETRACTION - E. MATZKE TO J. KNOKE AT 11:44 EST ON 03/27/05 *** The licensee faxed the following retraction: "Fort Calhoun Station (FCS) has conducted a thorough engineering evaluation of the effects on water in the turbine exhaust housing of the steam driven feedwater pump (FW-10). It was concluded that FW-10 was able to perform its design function based on the results of the evaluation. FW-10 was determined to be operable as required during past plant operation whether or not condenser vacuum was available. "The conclusion was based on four points: 1. The preparer's experience with a multi-stage turbine that was started with water up to the centerline of the rotor and sustained no damage. 2. OPPD's strong evidence that FW-10 has been operated multiple times with some water in the casing. 3. A simple conservative analysis of the forces on a turbine blade when operated in a water submerged condition. The blade stresses were determined to be well below allowables for the loading condition presented with the blade moving through the static water volume during a startup event. 4. In addition, inspection of the turbine in 1998 and 2005 does not show any adverse indications of stress or wear. "Therefore this notification is being retracted.." The plant is presently in a scheduled refueling outage. The licensee will notify NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-02-08
41385 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2005-02-08 14:30 | 2005-02-08 16:22 | 2005-02-08 | OFFSITE NOTIFICATION MADE DUE TO AN ASBESTOS SPILL An asbestos spill that was quantified at 1430 on 2/8/05 to be approximately 10-15 pounds occurred. The spill was from old pipe lagging that came off pipes that were on an outside roof area and did not contact the ground or surrounding waterway. Reports have or will be made to the following government agencies: National Response Center, New York State Department of Environmental Conservation, and the Public Service Commission as part of the licensee's requirement. Containment and cleanup of the asbestos is in progress. The NRC Resident has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-02-08
41384 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2005-02-08 06:32 | 2005-02-08 07:12 | 2005-02-08 | UNUSUAL EVENT PER EAL 13 E DUE TO FIRE/SEVERAL MINOR EXPLOSIONS IN TEMPORARY SECURITY TRANSFORMER. The following information was provided by the licensee via facsimile: "Fire in a temporary security transformer resulted in several minor explosions. No injuries occurred. Damage was limited to the affected transformer. "Off-site notification of Miami-Dade County fire rescue was made for additional assistance. The fire was extinguished by plant personnel at 0634 prior to arrival of the county fire department. "The security computer system was not affected. Some security lighting and search equipment was affected due to switching to battery back-up power. Additional security personnel were deployed to compensate. No security threat exists, however a Security Event was declared." The State, County and the NRC Resident Inspector were notified of this event by the licensee. ***** UPDATE PROVIDED BY JAMES SPEICHER TO MACKINNON AT 0752 EST ON 02/08/05 ***** Emergency Action Level 13 E exited and the Unusual Event was terminated at 0725 EST. Notified R2DO (C. Payne), IRD (J. Crlenjak), NRR EO (J. Foster), FEMA (Chung) & DOE (DaSilva). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-02-08
41383 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2005-02-07 20:23 | 2005-02-08 00:14 | 2005-02-08 | MANUAL REACTOR TRIP DURING STARTUP DUE TO INDICATION OF MISALIGNED ROD The following information was provided by the licensee via facsimile: "While withdrawing Control Bank 'A' during the Reactor Startup, Rod B-10 indicated a rapid drop from approximately 42 steps to 17 steps on the CERPI (Computer Enhanced Rod Position Indication) panel. The reactor operator stopped withdrawal of 'A' control bank and the CERPI indication for rod B-10 remained at 17 steps. The remaining CERPIs in 'A' control bank varied from 40 to 45 steps. "The startup was terminated and the reactor was manually tripped in accordance with AP-1 and 1-E-0 [was] initiated. All systems functioned as required on the trip. Initial investigation by I & C and Engineering found no problems with the CERPI indication. Rod Drop time data from the CERPI program shows all rods in Control Bank 'A' had a drop time of 0.32 to 0.38 seconds with the exception of B-10, which had a drop time of 0.18 seconds. " An investigation is ongoing as to the cause of rod B-10 misalignment. "This notification is being made pursuant to 10 CFR 50.72(b)(3)(iv)(A). The NRC resident was notified of this event." The reactor was subcritical in the Source Range at the initiation of the event. All rods inserted fully during the manual reactor trip. S/G level is being maintained by main feedwater and decay heat removal is via the S/G PORV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-02-08
41382 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2005-02-07 15:58 | 2005-02-07 22:11 | 2005-04-07 | RESIDUAL HEAT REMOVAL SYSTEM INOPERABLE DUE TO EMERGENCY DIESEL GENERATOR TRIP DURING TESTING "This report is being made pursuant to 10CFR50.72(b)(3)(v)(B) 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat;' "This report is being made due to a trip of the Emergency Diesel Generator during testing that resulted in the RHR loops potentially becoming depressurized. This has the potential to render all RHR Shutdown Cooling unavailable and prevent the removal of decay heat. "Sequence of events (all times CST): At 12:00 [02/07/05], Shutdown Cooling was removed from service to prepare for Sequential Load testing of DG #1. This was a planned evolution. At this time decay heat was being removed by the fuel pool cooling system with 2 fuel pool cooling pumps and 2 fuel pool cooling heat exchangers. Time to boil was calculated to be 26 hours. "At 15:58, the Sequential Load Test commenced on the inoperable DG. The DG came up to speed and sequenced on the initial loads (RHR pumps, a CS pump and a SW pump). Shortly into the sequencing of the DG, the DG tripped due to a blown fuse in the DG control circuit. Sequential loading was not completed. The trip occurred between 13 seconds and 20 seconds of the sequential load. This resulted in the initial loads losing power. Procedurally, the minimum flow valves for the RHR and CS pumps were being remotely opened from the Control Room at the time the DG tripped. This resulted in low-pressure alarms on both RHR systems and one CS system. One fuel pool cooling pump was deenergized, per design, during the sequential load test. Both fuel pool cooling heat exchangers remained in service. With these conditions, the fuel pool cooling lineup does not qualify as an alternate decay heat removal method. "At 16:04, both RHR loops were declared inoperable due to depressurizing the RHR loops. At 16:02, the tripped fuel pool cooling pump was restored to operation and previous decay heat removal was restored. No unexpected rise in temperature occurred during the time that only 1 fuel pool cooling pump was in operation. This reestablished the fuel pool cooling system as an alternate decay heat removal method. "At 19:11, the B loop of RHR was returned to a standby lineup and declared operable. "At this time investigation into why the DG fuse blew is ongoing. All indications are that other equipment performed as designed." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM C. BLAIR TO M. RIPLEY 1548 EST 03/08/05 * * * The following is a correction to the original report received via facsimile (licensee text in quotes): "Instead of the minimum flow valves for RHR and CS being opened, the suppression pool inboard cooling valve for RHR and the test line recirculation valve for CS were being opened." The licensee will notify the NRC Resident Inspector. Notified R4 DO (T. Pruett) * * * RETRACTION FROM COY BLAIR TO MARK ABRAMOVITZ 3/31/2005 AT 14:40 * * * The following information was provided by the licensee (licensee text in quotes): "On 2/7/2005 at 1558 CST, Cooper Nuclear Station made an 8 hour 50.72 non-emergency notification to the NRC. The report was made pursuant to 10 CFR 50.72(b)(3)(v), 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat.' A control power failure during Emergency Diesel Generator #1 (DG) surveillance testing resulted in the loss of the Residual Heat Removal (RHR) pressure maintenance pump. This resulted in the potential de-pressurization and unavailability of all RHR Shutdown Cooling (SDC) and the ability to remove decay heat using RHR. NUREG 1022 Revision 2 defines the safety functions to be considered for Reportability under this section of the rule as being those that are listed in the regulation itself. Thus, the lost safety function being reported was 'remove decay heat'. "Plant conditions prior to the testing were: Mode 5 (Refueling) with the Reactor Vessel and Drywell heads removed and reactor water level flooded up and Spent Fuel Pool transfer gates removed. Division II RHR was in service providing SDC for decay heat removal. In preparation for the DG testing and in accordance with Technical Specifications, all RHR SDC was removed from service. With RHR SDC out of service, reactor coolant circulation was verified to be by natural circulation with operators monitoring reactor coolant temperatures once per hour. Alternate decay heat removal was provided by the credited lineup of two Fuel Pool Cooling (FPC) pumps and two FPC heat exchangers. FPC receives cooling water from the Reactor Equipment Cooling System (REC), which in turn is cooled by the Service Water System (SW). During the preparation period (approximately 4 hours) for the DG #1 testing, reactor coolant temperature was allowed to slowly go from 85 degrees Fahrenheit to 90 degrees Fahrenheit. "During load sequencing testing of DG #1, the DG tripped due to a control system failure and de-energized the Division I 4160 Volt (V) critical bus. (Note: The bus was previously de-energized for a short period of time as part of the test.) This caused the pump providing pressure maintenance for the RHR to trip potentially depressurizing the RHR loop (Division II) that had been lined up to provide SDC. A conservative decision was made to declare Division II SDC inoperable during the DG trip recovery. "If the test had proceeded as planned one RHR pump would have been running in Division I in the test mode (pumping water to the suppression pool). No RHR pumps would have been running in Division II (lined up to allow the Division I test to be conducted). DG #2 remained in normal standby lineup. Division II 4160 V bus was energized supplying power to connected loads. Due to the DG #1 trip the Division I 4160 V bus was deenergized. Shutdown Cooling using RHR could not be placed in service as a result of the test lineup established for DG #1 testing. Reactor coolant circulation was by natural circulation and reactor decay heat removal was by one FPC pump and two FPC heat exchangers. The trip of one FPC pump is expected and verified during this surveillance test. REC was operating with cooling supplied by Division II SW. "During the period of time after the DG trip and prior to the restoration of electrical power to the Division I 4160 V bus, coolant circulation continued by natural circulation with one FPC pump and two FPC heat exchangers providing decay heat removal. At approximately the time of the DG trip coolant temperature was 90 degrees Fahrenheit. Just after power was restored coolant temperature was 89 degrees Fahrenheit. Operators had adjusted REC temperatures and flows to provide additional cooling to Fuel Pool Cooling. An additional FPC pump was started to provide a two FPC pump and two FPC heat exchanger lineup for reactor decay heat removal. The small variation in coolant temperature demonstrates that the FPC lineup was adequate to provide decay heat removal. "Engineering performed an evaluation to investigate bulk water temperature response to the event with one FPC pump and two heat exchangers supplying cooling with the fuel pool gates removed. The results show extended periods of time for pool heat-up and are considered bounding. It takes 21 hours for the pool temperature to reach 150 degrees Fahrenheit and 94 hours for the bulk temperature to reach a maximum value of 182 degrees Fahrenheit. Based on this evaluation CNS concludes the maximum bulk temperature would not exceed 182 degrees Fahrenheit. "As discussed above, RHR SDC was removed from service to support Emergency Diesel Generator surveillance testing. While RHR SDC was out of service, reactor coolant circulation was provided by natural circulation. At the same time, the safety function of decay heat removal was provided by Fuel Pool Cooling. Since the decay heat removal safety function was never lost this is not a reportable event." The licensee notified the NRC Resident Inspector. Notified the R4DO (Graves). * * * UPDATE ON 04/07/05 @ 0725 BY COY BLAIR TO CHAUNCEY GOULD * * * The following is a change to paragraphs 3 and 4 of the above retraction statement "During sequential load testing of DGI, the normal expected response after loads are sequenced on, is to have an RHR pump in each division recirculating back to the suppression pool via the suppression pool cooling line. This path is established when the respective RHR pump automatically starts. During load sequencing testing of DG # 1, the DG tripped due to a control system failure and de-energized the Division I 4160 Volt (V) critical bus. (Note: The bus was previously de-energized for a short period of time as part of the test.). Due to the timing of the DG failure, both RHR pumps started and both suppression pool cooling valves were opened. Subsequently the DG tripped and the RHR pumps stopped due to no power available. The suppression pool cooling valves were unable to be closed prior to depressurizing both RHR loops. A conservative decision was made to declare Division II SDC inoperable during the DG trip recovery. "DG #2 remained in normal standby lineup. Division II 4160 V bus was energized supplying power to connected loads. Reactor coolant circulation was by natural circulation and reactor decay heat removal was by one FPC pump and two FPC heat exchangers. The trip of one FPC pump is expected and verified during this surveillance y test. REC was operating with cooling supplied by Division II SW." The NRC Resident Inspector will be informed. Reg 4 RDO(Linda Howell) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2005-02-07
41381 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-02-07 20:55 | 2005-02-07 21:42 | 2005-02-08 | PLANT HAD A FREON LEAK IN THE DRYWELL CHILLER ROOM The plant reported that there was a freon leak in the Drywell Chiller Room located in the Unit 2 Reactor Building. Maintenance was being performed on the refrigeration equipment relief valve when the gas began to escape into the room. There were six men working in the room and two were affected by the freon gas. They were treated on site and released. Oxygen content in the room was 20.5% and LEL for hydrocarbons was alarming at 19%. The drywell chiller room is secured and being cleared of the 1,200 pounds of freon gas. At this time an investigation is being made to determine the cause which may have been due to the relief valve opening or the workers removing the valve. The plant entered the NOUE due to a "toxic gas release". The NOUE will be terminated when the room is habitable. The NRC Resident Inspector was notified along with State and Local agencies. * * * UPDATE PROVIDED BY FRANK GORLEY TO JEFF ROTTON AT 0303 EST ON 02/08/05 * * * Licensee reported that the NOUE was terminated at 0245 EST after the freon had been successfully cleared from the Drywell Chiller Room. Licensee will notify the NRC Resident Inspector. Notified FEMA (Liggett), DHS (Knox), IRD (Wilson), R2DO (Payne), and NRR EO (Beckner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Refueling; FMode2: Refueling | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-02-07
41380 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-02-07 17:34 | 2005-02-07 19:46 | 2005-02-10 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) At 1734 on 2/7/2005, received an Area Radiation Monitor alarm in the reactor building basement airlock area at approximately 75Mr/hr. The valid alarm caused entry into EOP flowcharts for High Radiation in the Secondary Containment. Check of the relay room monitor showed 100 Mr/hr. Investigation showed that a failed open main steam line drain valve combined with placing hydrogen water chemistry in service caused the increasing radiation levels. A downstream steam line drain isolation valve was closed to isolate the steam flow path past the monitor. Hydrogen Water Chemistry injection rate was lowered. The Rad levels returned to about 4 Mr/hr (normal levels) following valve closure (at 1745). The EOPs were exited at 1755. After review of the event it was determined that an unusual event should have been entered at the time of the EOP entry (EAL AU2, Unexpected Increase of Plant Radiation Levels), 1734 and exited at 1745 when area radiation levels returned to normal values. This is an after the fact notification of a missed emergency classification. The NRC Resident Inspector was notified. * * * UPDATE ON 2/10/05 AT 1907 HRS. EST BY CROUCH * * * This event notification reporting criteria has been changed to comply with the guidance provided in NUREG-1022, Rev. 2, "Event Reporting Guidelines 10CFR 50.72 and 50.73". There is specific discussion that states (in part) that if a licensee discovers that a condition existed which met the emergency plan criteria but no emergency was declared and the basis for the emergency class no longer exists at the time of discovery, an actual declaration of the emergency class is not necessary. An ENS notification of the missed classification is an acceptable alternative. The Headquarters Operations Officer notified R3DO (Duncan). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW | [5 empty] | 0 | 2005-02-07
41379 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2005-02-06 22:19 | 2005-02-07 04:41 | 2005-02-07 | EMERGENCY DIESEL START DUE TO BUS DEENERGIZATION The following information was provided by the licensee via facsimile: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 6, 2005, at approximately 22:19 Mountain Standard Time (MST) a valid actuation of the Palo Verde Nuclear Generating Station Unit 1 Train `B' Emergency Diesel Generator (EDG) occurred as a result of undervoltage on its respective safety bus (PBB-S04). EDG 'B' started and loaded as designed to energize PBB-S04. "The loss of power to the safety bus was the result of a fault associated with 13.8KV breaker NAN-SO6J which caused breakers NAN-SO6H (normal power supply), NAN-S06K (alternate power supply), and NAN-SO6J (EOF & TSC Bldg power supply) to all trip open on Overcurrent. This action resulted in the deenergization of NAN-S06, NAN-S04, and PBB-S04. The PVNGS Fire Department and Auxiliary Operators responded to a report of smoke and upon arrival found no fire. The Fire Department verified the fire was completely extinguished and there were no extensions (secondary fires). "Unit 1 entered Technical Specification LCO 3.8.1, Condition 'A', for one (of two) required offsite circuits inoperable. Various other Technical Specifications LCO's were momentarily entered and exited for PBB-S04 being deenergized for approximately 7 seconds. No Emergency Plan declaration was made and none was required. "Unit 1 was at approximately 100% power, at normal operating temperature and pressure prior to and following the EDG actuation. No other ESF actuations occurred and none were required. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been notified of the ESF actuation and this ENS notification." The B EDG is providing power to PBB-S04. Due to loss of power to the TSC, the TSC Diesel started and is providing power to the TSC. The Backup EOF located in Buckeye, AZ will be used in the case of an emergency event. There were no reported injuries. There was damage to the NAN-S06J breaker and it has been isolated. The event has been entered into the site's corrective action program for determining the cause of the breaker trip and damage. This event has no effect on the operation of the other site units. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2005-02-07
41378 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2005-02-06 10:08 | 2005-02-06 17:28 | 2005-02-06 | 24 HOUR REPORT OF A SAFETY EQUIPMENT FAILURE The licensee provided the following information via facsimile: "At 1008, on 2-06-05, the Plant Shift Superintendent [PSS] was notified that at the C-360 Toll and Transfer Facility on autoclave 4, the vent line block valve, XV-434, failed to close when the control switch was operated to the closed position. A check of the valve indicator showed that the valve moved to approximately 75% of the closed position. This valve is a single isolation point (no redundant valve) for two TSR [Technical and Safety Requirements] systems: (1) The Autoclave Steam Pressure Control System and (2) The Autoclave Water Inventory Control System. The autoclave was in mode 5, an applicable TSR mode for both systems. The PSS declared the systems inoperable and TSR LCOs 2.1.3.3 and 2.1.4.3 were implemented to remove the autoclave from service and place it in mode 2 within one hour. "This event is reportable as a 24 hour event in accordance with 10 CFR 76.120.c.2.i. It was an event in which equipment is disabled or fails to function as designed when: a) The equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident; b) The equipment is required by a TSR to be available and operable and either should have been operating or should be operated on demand, and, c) No redundant equipment is available and operable to perform the required safety function. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2005-02-06
41377 | -1 | PRAIRIE ISLAND | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2005-02-05 20:46 | 2005-02-06 00:43 | 2006-06-13 | 4160 VOLT RELAYING AND METERING SINGLE FAILURE VULNERABILITY "This report is being made pursuant to 10CFR50.72(b)(3)(ii)(B). At 20:46 on 02/05/05 while reviewing Operation Experience from another Nuclear Site, it was discovered that the design of the AC Auxiliary Power System incorporates a common circuit which could result in a bus lockout preventing the re-energization of both unit one safeguards buses from either onsite or offsite power sources due to a single failure in the common portion of the circuitry. This common circuit includes various metering circuits and is also connected to overcurrent devices that feed breaker lockout relays. Should a failure occur on these common circuits, all breakers supplying power to these buses would be opened, locked out, and prevented from reclosure onto the buses. "Due to the loss of the ability to accommodate a single failure, one offsite power source ( CT11 ) has been declared inoperable and Technical Specification 3.8.1 Condition A, entered. Corrective actions are in progress to isolate the common circuit and eliminate the single point vulnerability." The licensee notified the NRC Resident Inspector. See similar events #41362 (Crystal River), #41366 (LaSalle), #41369 (Quad Cities) ,#41370 (Dresden) and #41377 (Monticello). * * * RETRACTION FROM S. SEILHYMER TO S. ROTTON AT 1140 ON 6/13/06 * * * "The event reported on February 6, 2005 (4160 volt relaying and metering single failure vulnerability, NRC Event Number 41377) is hereby retracted. Subsequent analysis has concluded that a common mode failure resulting in a simultaneous lockout of both safeguards 4160 volt Bus 15 and Bus 16 due to the common metering circuit was not a credible event in the as-found condition. The analysis showed that the required magnitude of a fire induced fault is much greater than the available fault current in any of the associated circuits. The analysis also showed that dual bus lockout due to an open circuit under non-fire induced conditions is not credible since the imbalance current will be less than the trip setpoint of the affected relays. "Thus, although the plant had been in an unanalyzed condition, that condition has now been shown to have not significantly degraded plant safety and is, therefore, not reportable under the requirements of 10 CFR 50.72(b)(3)(ii)(B). Additionally, NMC will be submitting a letter to cancel the associated LER 1-05-01." The licensee notified the NRC Resident Inspector. Notified R3DO (Louden). | 88 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-02-06
41376 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-02-03 16:30 | 2005-02-04 18:53 | 2005-02-04 | CALIFORNIA AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was received from California Radiation Health Bureau via facsimile: "A Troxler Moisture Density gauge (Serial # 27061) was run over at construction site at Mare Island, Vallejo, CA at 4:30 PM on 2/3/05. According to the RSO, the gauge operator was standing 15 feet from the gauge when a loader operated by Gilotti Construction changed course and ran over the gauge. The gauge was damaged severely and the source rod was bent and removed by the operator from it's protective lead shield. The rod and gauge were stored in a shed and CPN (gauge manufacturer) has been contacted this afternoon and will retrieve the gauge and prepare it for transport to Troxler, Inc. The RSO will be investigating this incident" The gauge contains 8 milliCuries of Cs-137 and 40 milliCuries of Am-241. At this time, there does not appear to be any personnel overexposures or spread of contamination due to this event. The State of California has requested that the worker's film badges be immediately processed as a part of the licensee investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-02-09
41375 | -1 | UNIVERSITY OF CONNECTICUT HEALTH CT |  |  |  |  | 2005-02-04 | 2005-02-04 18:00 | 2005-02-09 | MEDICAL EVENT "At 0900 hours on 2/4/05, a Nuclear Medicine Technician attempted to inject 32.7 milliCuries of Tc-99m into an implanted single lumen port located near the left breast of a female patient. The patient was scheduled for a red blood cell study. After injecting 21.1 mCi, the Tech noticed resistance and could not deliver the rest of the dose. A scan of the patient indicated the material was not metabolizing, and a localized spot was identified near the port. The Nuclear Medicine Physician, after reading the scan, determined that the dose had been delivered to a volume of 15-30 cubic centimeters of tissue around the port. The Radiation Safety Officer estimated that the committed absorbed dose to this tissue volume is on the order of 52.7 to 83.2 Rad, using MIRD dosimetry. The patient was notified by the Nuclear Medicine Physician, and the physician has indicated that there will be no deleterious effects on the patient. The NRC Operations Center was called at 1800 hours on 2/4/05, as of this time it is not certain if the internal line was crimped by the patient or the event was caused by failure of the port." * * * * RETRACTION OF REPORT ON 02/09/05 AT 1058 EST BY KEN PRICE TO MACKINNON * * * * Retracting report after discussion with NRC Region 1 Penny Lanzisera. The licensee is retracting this report because it has been determined not to be a reportable event. R1DO (Jim Trapp) and NMSS (Sandra Wastler) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | CT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2005-02-04
41374 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2005-02-04 13:37 | 2005-02-04 17:25 | 2005-02-04 | 4160 VOLT RELAYING AND METERING SINGLE FAILURE VULNERABILITY The following information was obtained from the licensee via facsimile: "On February 4, 2005, at 1337 hours, Monticello Nuclear Generating Plant discovered a potential vulnerability with 4160 VAC current sensing and protective relaying circuitry that could result in bus lockouts of both safeguards buses (#15 and #16) if a specific equipment fault were to occur. The 1AR Auxiliary Reserve Transformer source to each of the safeguards buses have current transformers used for over-current protective relaying that have common connections to facilitate a single watt-hour meter. The lack of neutral over-current trip relaying limits the event vulnerability to a case (most likely fire) of an outside voltage source contacting one or more CT phase legs that forces current through the over-current trip relays. If this forced current is of sufficient magnitude through both division over-current relays, both safeguards buses will receive lockout signals. This would make both safeguards buses unavailable. Since the 1AR transformer is not required at this time, it has been isolated from the safeguards buses, and their associated over-current relaying isolated to preclude occurrence of this event. "This event is being reported as a potential loss of safety function (10CFR50.72(b)(3)(v)(A, B, C, and D)) and as a degraded or unanalyzed condition (10CFR50.72(b)(3)(ii)(B)), The NRC Resident Inspector has been notified. See similar events #41362 (Crystal River), #41366 (LaSalle) #41369 (Quad Cities) and #41370 (Dresden). | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 0 | 2005-02-04
41373 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-02-04 07:30 | 2005-02-04 15:12 | 2005-02-04 | OFFSITE NOTIFICATION The following information was obtained from the licensee via fax: "At approximately 0730 on 2/4/05, a radiography safety officer notified the South Carolina Department of Health and Environmental Control (SC DHEC) of a violation of a radiography boundary. The violation occurred sometime between the hours of 2230 on 2/3/05 and 0030 on 2/4/05. At the time of the breech, the radiography source was stored, so no overexposure of personnel is suspected. However, the individual seen by the radiographers has not been identified to ascertain whether or not they were wearing dosimetry while within the boundary. This requires notification to the offsite agency SC DHEC since it is unknown whether or not they were monitored. The radiation safety officer was unaware and his administrative procedure did not inform him of the need for a 10 CFR 50.72 (b) 2 notification. Thus, licensed personnel did not discover that the notification had been made until 1300 on 2/4/05. At this time, licensed personnel began gathering information on the nature of the call to determine reportability. The site has assembled an event investigation team in response to the radiography boundary violation." The NRC Resident Inspector was notified as well as the South Carolina Department of Health and Environmental Control. State and local authorities will be notified of this event. The licensee will notify the NRC of any further information obtained from the investigation. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-02-04
41372 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2005-02-04 09:00 | 2005-02-04 14:38 | 2005-02-04 | 24-HOUR NOTIFICATION-BULLETIN 91-01 CRITICALITY CONTROL The following information was obtained from the licensee via email : "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched ([DELETED]) PWR fuel fabricator for commercial light water reactors. License: SNM-1107. "Time and Date of Event: February 4, 2005, 0900 hours: "Reason for Notification: Double contingency protection for non-favorable geometry (NFG) bulk containers is based on preventing moderation from entering the bulk powder blending room and by then preventing the moderator from entering the bulk containers. "Prevention of moderation from entering the bulk powder room is assured by controls such as a double roof, restrictions on firefighting combined with limits on combustible materials, limits on moderators for maintenance and cleaning, and rigorous control over powder moisture to ensure that no carts enter the bulk room that have polypaks with moisture above 0.3 wt%. "Prevention of moderator from entering the bulk container is assured by controls such as procedure requirements to ensure visual inspection of all powder before it is dumped into a bulk container and the polypak dump hood interlock system. "In order to dump a polypak into a bulk container, the operator must scan the polypak's unique barcode and place the polypak into the polypak dump hood mechanism. After the barcode is scanned, the interlock function checks the moisture data associated with the polypak to ensure it is <0.3 wt%. If the moisture results are not <0.3 wt%, the dump hood locks up, preventing further dumping of powder until the discrepancy is resolved. "During routine dumping operations, an infrared [s]ensor became misaligned in the polypak dump hood in bulk powder blending room. This resulted in a failure of the polypak dump hood interlock to finish its 'cycle' for that pack. It was expected that this sort of problem would be promptly self revealing, i.e. that the scanning of the next pack would result in an error indicating that the previous pack had not been 'consumed.' While the errors were generated, they were not readily apparent, except to an attentive operator. The barcode scanner sounded the same, the visual cues were subtle, and the dump [hood] interlock did not lock up. The operator was able to scan additional paks and dump them. The moisture database would not have been consulted for any of these paks. "In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criteria for a 24-hour notification, specifically, 'Any nuclear criticality safety incident, in an analyzed system, for which less than previously documented double contingency protection remains (multi-parameter control or single-parameter control) and less than a safe mass is involved.' and 10CFR70, specifically Appendix A.b.2 'Loss or degradation of items relied on for safety that results in failure to meet performance requirements of 10CFR70.61.' "As Found Condition: An operator found the problem after dumping the first polypak of a blend. "Summary of Activity: The affected equipment has been shut down. New programming and other improvements are being developed. "Conclusions: There was less than a critical mass of SNM involved. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed." The licensee will be notifying NRC Region II of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2005-02-04
41371 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2005-01-10 | 2005-02-04 13:38 | 2005-02-04 | LOST SEALED SOURCE The Department of Veterans Affairs reported the loss of licensed material. "The loss occurred at a medical limited-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01 VA. The permittee is VA Medical Center, Battle Creek, Michigan. "The loss was discovered by the permittee Nuclear Medicine Technologist on January 10, 2005. The Nuclear Medicine Technologist discovered that the Cs-137 sealed source [Serial number S356010-022] used for the dose calibrator calibrations and daily constancy measurements was missing. "The basis for reporting the loss is under 10 CFR 20.2201(a)(ii) in that the permittee lost permitted material in a quantity greater than 10 times the quantity specified in 10 CFR 20, Appendix C, and is still missing at this time. The actual activity was approximately 137 microCuries. "The permittee investigated the loss and concluded the radioactive material most likely ended up in a local landfill. Permittee staff performed radiation surveys of the medical center and at the landfill which did not locate the missing radioactive sealed source. "The [VHA National Health Physics Program] NHPP performed a reactive inspection on January 13, 2005, 4 days after the loss was discovered. Additional surveys performed by NHPP also failed to locate the source at the medical center. In accordance with 10 CFR 20.2201(b), a thirty-day report is pending and will be forwarded to NRC when completed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-02-04
41370 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2005-02-03 19:15 | 2005-02-04 00:23 | 2005-02-04 | 4160 VOLT RELAYING AND METERING SINGLE FAILURE VULNERABILITY The licensee provided the following report via facsimile: "On February 3, 2005 at 1915 hours, DNPS confirmed a vulnerability with a 4160 VAC relaying and metering current transformer (CT) associated with the Unit and Reserve Auxiliary Transformers (i.e., the UAT and RAT) on both Units. Although the CT is currently fully operable, failure of the CT circuitry will cause the neutral overcurrent relay to trip (and lockout) the main, reserve and tie feed breakers. These combined protective relay trips will act to trip and lock out the circuit breakers supplying feeds to buses 23 (33) and 24 (34), essentially isolating them from their normal and emergency power sources. Emergency power (i.e., the emergency diesel generator) would still be available to safety related buses 23-1 (33-1) and 24-1 (34-1), but the Containment Cooling Service Water (CCSW) system would remain without a power source. If this failure occurred during a LOCA, then the CCSW pumps may not be able to be started within ten minutes. A modification is in progress to eliminate this vulnerability. This event is being reported as a potential loss of safety function (10CFR50.72(b)(3)(v)(B)) and a degraded or unanalyzed condition (10CFR50.72(b)(3)(ii)(B))." The NRC Resident Inspector has been notified. See similar events #41362 (Crystal River), #41366 (LaSalle), and #41369 (Quad Cities). | 0 | 95 | 96 | 0 | 95 | 96 | 0 | -1 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2005-02-04
41369 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2005-02-03 18:19 | 2005-02-03 23:48 | 2005-02-04 | 4160 VOLT RELAYING AND METERING SINGLE FAILURE VULNERABILITY The licensee provided the following report via facsimile: "On February 3, 2005 at 1819 hours, Quad Cities Nuclear Power Station (QCNPS) confirmed a vulnerability with a 4160 VAC relaying and metering current transformer (CT) associated with the Unit and Reserve Auxiliary Transformers (i.e., the UAT and RAT) on both Unit 1 and Unit 2. Although the CT is currently fully operable, failure of the CT circuitry could cause the neutral overcurrent relay to trip and lockout the circuit breakers supplying feeds to safety related buses 13 (23) and 14 (24), isolating them from their normal and emergency power sources. Emergency power (i.e., the emergency diesel generator) would still be available to supply power to safety related buses 13-1 (23-1) and 14-1 (24-1), but the Residual Heat Removal Service Water (RHRSW) system may be without a source of power. If this failure occurred during a LOCA, then the RHRSW pumps may not be started within the ten minute requirement. A modification is in progress to eliminate this vulnerability. This event is being reported as a potential loss of safety function (10CFR50.72(b)(3)(v)(B)) and as a degraded or unanalyzed condition (10CFR50.72(b)(3)(ii)(B))." The NRC Resident Inspector has been notified. See similar events #41362 (Crystal River), #41366 (LaSalle), and #41370 (Dresden). | 85 | 85 | 0 | 85 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) |  |  | 0 | 2005-02-04
41368 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2005-02-03 12:27 | 2005-02-03 18:02 | 2005-02-03 | AUTOMATIC REACTOR TRIP DUE TO UNIT AUXILIARY TRANSFORMER TRIP "On February 3, 2005, at about 1227 PST, SONGS Unit 2 tripped from about 100 percent power. Preliminary information indicates that the Unit 2 Unit Auxiliary Transformer tripped on high differential current, which caused the main generator to trip and caused the Reactor Protection System to automatically trip the reactor, as expected. Auxiliary Feedwater system actuated as designed and the Unit remains stable in Mode 3 on Main Feedwater. SCE's investigation is ongoing. "SCE is reporting this occurrence in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv). "At the time of this event, SONGS Unit 3 was at about 100 percent power. The NRC resident inspectors are aware of this event and SCE will provide them with a copy of this report." All control rods fully inserted. Decay heat is being rejected to the main condenser. All ESF systems are available and the electrical grid is stable. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-02-03
41367 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-02-02 12:05 | 2005-02-03 15:28 | 2005-02-03 | CALIFORNIA AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GUAGE At 1205 on February 2, 2005, the licensee called the Brea office to report that one of their moisture density gauges had been run over by construction equipment at 1145 that morning. The gauge was damaged to the extent that they were unable to retract the source rod back into the shielded position (CPN, model 3, # M22054410 - 10 mCi Cs-137 and 50 mCi Am:Be). The incident happened at a construction site located at 3208 Quarter Horse Drive in Yorba Linda at the water reservoir. The outer gauge casing was in pieces, the rod handle was broken and the source rod was extended into the ground. The maximum dose rate with the source rod extended into the ground was 2 mrem/hr at contact measured with a Bicron microrem instrument. The dose rate when the source rod was extracted from the ground was approximately 30 mrem/hr at one foot from the rod tip. The Cs-137 end of the gauge source rod was placed in a lead pig, which was taped into place to keep the Cs-137 source shielded. The unit remains were placed in a plastic bag which was then placed into the transportation case. The device was transported to the local CPN service representative - Maurer Technical Services. Maurer Technical Services stated the sources appeared to be intact, and they took a wipe for a leak test. The wipe was sent out for counting. Alpha and beta surveys at the accident scene did not detect any contamination. Two wipes of the source housings were collected, which were counted in the Brea office on a Ludlum 3030 alpha-beta counter the next day. No contamination was detected on these two wipes. The incident apparently occurred when the construction equipment, a front end loader, changed direction to avoid a truck, and there wasn't time for the gauge operator, who was in a safe location about 15 feet from the gauge, to signal the front end loader to stop. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-02-08
41366 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2005-02-02 15:42 | 2005-02-02 20:59 | 2005-02-02 | SINGLE FAILURE VULNERABILITY IN AC AUXILIARY POWER SYSTEM "This report is being made pursuant to 10CFR50.72(b)(3)(ii)(B). At 15:42 on 02/02/05 while reviewing Operation Experience from another Nuclear Site, it was discovered that the design of the AC Auxiliary Power System incorporates a common circuit which could result in a bus lockout preventing the re-energization of both the Division 1 and Division 2 Essential Safety Feature (ESF) buses from either onsite or offsite power sources due to a single failure in the common portion of the circuitry. This common circuit includes various metering circuits such as System Auxiliary Transformer Wattmeters and Ammeters. Also connected to these metering loops are ground fault devices that feed breaker lockout relays. Should a failure occur on these common circuits, all breakers supplying power to these ESF Buses would be opened, locked out, and prevented from reclosure onto the buses. "Due to the loss of the ability to accommodate a single failure, one offsite power source and one onsite Diesel Generator have been declared inoperable and Technical Specification 3.8.1 Condition A, Condition B, and Condition E entered. Corrective actions are in progress to isolate the common circuit and eliminate the single point vulnerability." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-02-02
41365 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-02-02 10:34 | 2005-02-02 14:25 | 2005-02-02 | OFFSITE NOTIFICATIONS DUE TO OIL SHEEN ON THE DELAWARE RIVER "A report was made to the New Jersey Department of Environmental Protection (NJDEP) and the National Response Center (NRC) when a light sheen of oil was observed on the Delaware River at the south end of Artificial Island. Chemistry personnel first observed the sheen during a routine oil water separator system walk-down at 1034 hours on February 2, 2005. The oil water separator system was immediately shut down. The amount of oil that produced the sheen is estimated to be approximately two ounces. Site personnel responded and deployed an absorbent oil boom. At the present time, site personnel are investigating whether the oil sheen originated from the site oil water separator system or was residual from the November 2004 Delaware River oil spill. "This event is being reported in accordance with 10CFR50.72(b)(2)(xi)" The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-02-02
41364 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-02-01 17:00 | 2005-02-01 17:57 | 2005-02-01 | AGREEMENT STATE REPORT - NONLICENSED RADIOGRAPHY CAMERA CONFISCATED BY US CUSTOMS IN FLORIDA A private plane landed at the Tamiami airport in Miami, FL and US Customs discovered a Model 802 radiography camera with an Iridium 192 source measuring approximately 11 curies aboard. The camera belonged to a Guatemala company by the name of S.I.E. Limitada located in Guatemala City. The company was doing work in the Grand Cayman Islands for a Florida company by the name of Tampa Tank. The contract company was returning from the Grand Cayman Islands to Guatemala via Miami. US Customs has confiscated the camera and has it under their control until the State can get their people in place to take control of the device. As soon as a State representative can transport the camera to the Miami Airport it will be flown back to Guatemala City via Arrow transport. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-02-04
41363 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2005-01-30 04:10 | 2005-01-30 04:52 | 2005-01-30 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER "Loss of greater than 25% EWSS [Early Warning Siren System] due to ice storm." The majority of the sirens were lost in Fairfield and Newberry Counties. The licensee had no estimated time for restoration. The licensee informed state/local agencies and the NRC Resident Inspector. * * * Update on 01/30/05 at 1536 hours by Albert Harris to MacKinnon * * * At 0900 hours 84% of the EWSS was returned to service. At 1430 hours EWSS was declared operable after 98% of the system was returned to service. R2DO (T. Decker) notified. The licensee informed the state/local agencies and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-30
41362 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2005-01-27 18:30 | 2005-01-27 21:12 | 2005-01-28 | SINGLE FAILURE IDENTIFIED THAT COULD PREVENT RE-ENERGIZING BOTH ES BUSSES "On January 27, 2005, Crystal River - Unit 3 (CR-3) discovered an installation subject to a single failure that could prevent both Emergency Diesel Generators (EDGS) and both offsite power sources from supplying power to their respective Engineered Safeguards (ES) Busses. This is a condition contrary to 10CFR50.72 (b)(3)(ii)(B). "The installation involves the 4.16 Kv supply breakers from the offsite power transformer (OPT) and the Back-up Engineered Safeguards Transformer (BEST) which are the two required offsite power sources. From the OPT, one breaker supplies the 'A' ES Bus and a second breaker supplies the 'B' ES Bus. From the BEST, one breaker supplies the 'A' ES Bus and a second breaker supplies the 'B' ES Bus. A traditional (non-nuclear) design for such pairs of supply breakers includes current transformers that are connected to each other for each phase and a watt hour meter from those connections to monitor power. These circuits were installed around 1990 to support the coordination of the new 230 Kv breakers to supply the OPT and the coordination with the 230 Kv supply breakers for the new BEST. "Should a failure of the wire connecting the current transformers or the watthour meter occur such that the ES Bus supply breakers' lockout relays are actuated, all breakers supplying and receiving power via the ES Busses would be opened and locked out. The result is that neither EDG nor the offsite power source would be able to automatically supply power to its respective ES Bus. "CR-3 is currently disconnecting and isolating the watthour meters and removing the connection between the respective breakers' current transformers." Licensee entered Tech Spec 3.8.9.1 at 1830 hours based on single failure but considers both ES busses operable. The NRC Resident Inspector was notified of this event by the licensee. *** Update on 01/28/05 at 1655 EST from Guy McCallum to MacKinnon **** "On January 28, 2005, Crystal River - Unit 3 (CR-3) corrected the single failure vulnerability associated with the Engineered Safeguards (ES) Busses. "A permanent modification which removed the single failure vulnerability for the offsite power transformer (OPT) was completed at (0152), and the modification for the Back-up Engineered Safeguards Transformer (BEST) was completed at (0644). R2DO (T. Decker) notified. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-01-27
41361 | 0 | UNIVERSITY OF MINNESOTA |  |  |  |  | 2005-01-25 21:30 | 2005-01-27 13:00 | 2005-01-27 | MEDICAL EVENT DURING TREATMENT FOR CANCER OF THE CERVIX A patient undergoing a 31 hour treatment plan for cervical cancer received less than the prescribed dose delivered to the treatment site and a higher than intended dose to other tissue(s)/organ(s), specifically: Treatment site A: planned 1643 centiGray, delivered 821 centiGray Treatment site B: planned 465 centiGray, delivered 372 centiGray Bladder: planned 1147 centiGray, delivered 1448 centiGray Rectum: planned 1147 centiGray, delivered 2012 centiGray Treatment was delivered from 1430 hours on 1/24 and 2130 hours on 1/25 using a low dose rate tandem brachytherapy device containing three Cs-137 sources; 14 milligram Ra-equiv, 9.8 milligram Ra-equiv and 9.8 milligram-equiv. There were two additional Cs-137 ovoid sources, each 14.1 milligram Ra-equiv. The tandem device has a rod that was cut 6 cm. short such that when the tandem was positioned in the patient, the three tandem sources were not extended the proper distance inside the tandem device. The ovoid sources were properly positioned. The referring physician and patient have been informed. The radiation staff oncologist does not believe that this medical event will have any adverse effect on the patient and a new treatment plan is being prepared for the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | DOSE TO OTHER SITE > SPECIFIED LIMITS | [8 empty] | NON EMERGENCY | 3 | MN | HOS |  | 35.3045(a)(1) | 35.3045(a)(3) |  |  | 0 | 2005-01-27
41360 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-01-26 | 2005-01-26 18:00 | 2005-01-26 | AGREEMENT STATE REPORT PROVIDING INFORMATION ABOUT AN EVENT OF MEDIA INTEREST The Florida Bureau of Radiation Control provided the following report via e-mail to the NRC: "[The] West Palm Beach Fire Department received a call about an electrical fire at [a West Palm Beach business] location. There was not an active fire [when the Fire Department reached the incident site] but an electrical smell [was] in the air. While in the [incident] building location, the FPD radiation dosimeters [worn by the Fire Department responders] indicated a [radioactive] source in a storage locker. [Based on the detected radiation], a one city block was evacuated and an area around the site of ten city blocks was sealed off. " [The licensee was authorized to posses Troxler type gauges at the site for its business activities which were stored at the location where the Fire Department had responded.] "Investigators [from the Florida Bureau of Radiation Control] arrived on scene and noted proper signage on the door [of the incident location] for a temporary work site [storing Troxler type gauges]. Licensee representatives opened [the] storage container [with the Troxler type gauges] to verify that the gauges were inside [and intact]. The emergency is in the process of being terminated. The [State] of Florida will continue its investigation." There was never any actual fire or release of any radioactive material during the course of this event. Florida Report FL05-016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-01-31
41359 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-01-26 15:50 | 2005-01-26 17:46 | 2005-01-26 | POTENTIAL FOR CARBON DIOXIDE MIGRATION INTO 4160/460 VOLT SWITCHGEAR ROOMS "An Engineering Evaluation was initiated to assess the potential for CO2 [carbon dioxide] migration in the event of a CO2 fire suppression system discharge in the Salem Unit 1 and 2 - 4160 volt or 460 volt Switchgear Rooms or Lower Electrical Penetration Areas. The results presented in the evaluation conservatively identified that when CO2 systems are discharged, CO2 migration can result in concentrations in some adjacent areas that would require the use of self-contained breathing apparatus (SCBAs) for entry, or in some cases should be restricted to transit activities only. "Some of these adjacent areas are required to be accessible by operators to perform manual actions in the plant to achieve and maintain safe shutdown. Based on the time line established in the Salem Manual Action Feasibility Studies for operator actions in the response to a fire in a Switchgear Room, the ability to shutdown the plant in the event of a fire concurrent with a CO2 discharge could be impacted. "The immediate action is to isolate the CO2 system and implement the necessary compensatory measure for the inoperable CO2 system as delineated within Station Fire protection program. With the CO2 systems isolated, the ability to safely shutdown the plant in the event of a fire in these areas is restored. Additional actions are being evaluated at this time to restore the CO2 system. "This event is being reported in accordance with 10CFR50.72(b)(3)(v) and Salem Unit 2 License Condition 2.I. No ESF, ECCS or safety related equipment has been impacted by this condition. Both Units remain at 100% power. There were no personnel injuries associated with this condition." Lower Alloway Creek Township and the State of New Jersey will be notified. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | OTHER UNSPEC REQMNT |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2005-01-26
41358 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2005-01-24 | 2005-01-26 12:13 | 2005-01-26 | AGREEMENT STATE REPORT OF ADMINISTRATION OF RADIOACTIVE IODINE TO A PREGNANT PATIENT The following information is a preliminary report provided to the Ohio Department of Health Bureau of Radiation Protection concerning a patient at the Riverside Methodist Hospital in Columbus, Ohio that was administered radioactive iodine while pregnant. "It has been brought to our attention that a patient that had been treated for hyperthyroidism at our facility was in fact pregnant at the time of the administration. The patient had an uptake study performed on 11/2/04 (205 microcuries of I-123 sodium iodine) pursuant to a diagnosis of hyperthyroidism. The patient was administered 12.7 millicuries of I-131 sodium iodine on 11/16/04 as treatment. The patient was counseled by the Authorized User prior to the administration and received written consent from the patient that she was not or could not be pregnant at that time. A pregnancy test was not performed to confirm or deny this fact. "The fact that the patient was pregnant was brought to our attention when she saw her family practice physician (who was the referring physician for the uptake and hyperthyroidism treatment procedures) for complaints of abdominal pain. A radiograph of the abdomen was taken and the pregnancy discovered. This occurred sometime within the past week. The fact that the patient was pregnant was relayed to the Authorized User, who, in conjunction with the referring physician, referred the patient to a prenatal specialist to determine the age of the fetus. The specialist determined the delivery date to be 4/25/05, which meant the age of the fetus at the time of the I-131 administration was 17 weeks. This determination was made on January 24, 2005, and the RSO's staff called the [Ohio Department of Health] to report the event after gathering information for a dosimetry study at approximately 10 AM, 25 January, 2005. "The dosimetry estimate for the fetus was approximately 2.0432 rad to the whole fetus and 22,400 rad to the fetal thyroid from both the I-123 and I-131 administrations. It should be noted that the patient underwent a CT angiogram on 9/24/04 (fetal age 8 weeks), but that this dose and the abdominal x-ray taken last week were not added to the fetal whole body dose since specific technique factors were not available for these studies which were performed elsewhere. "The patient will be notified of the treatment plan for the continuation of the pregnancy today or tomorrow, once the prenatal specialist receives the dosimetry estimate the RSO provided the Authorized User. The referring physician has been in close contact with the Authorized User throughout this process." The Ohio Department of Health considers this an "Abnormal Occurrence" and will be conducting an investigation commencing this Friday (1/28/05). Ohio Dept of Health Report # 2005-001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2005-01-31
41357 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-12-13 16:15 | 2005-01-26 09:20 | 2005-01-26 | INVALID SYSTEM ACTUATION The following information was provided by the licensee: "On December 13, 2004, at 1615 hours, during clearance restoration activities following 24V DC battery maintenance, Battery 22B-1 output breaker located on 24/48V DC Distribution Panel 22B, Circuit 5 was inadvertently opened resulting in the invalid actuation of the Unit 1 logic associated with the 24V DC bus. The actuations included the Primary Containment Isolation System (PCIS) Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems) valves, the Reactor Building Ventilation System Isolation (i.e., Secondary Containment isolation), and the automatic start of both Standby Gas Treatment (SGT) System trains A and B. The actuations of PCIS Group 6 valves and Reactor Building Ventilation System Isolation were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). Additionally, SGT System trains A and B started and functioned successfully. After verification of the expected equipment responses, the breaker was reset, the actuation logic was reset, and the equipment/systems were returned to the status required by plant conditions. "Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in action request 145898. The [NRC] resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2005-01-26
41356 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2005-01-25 20:58 | 2005-01-25 23:36 | 2005-01-25 | POTENTIALLY CONTAMINATED WORKER TRANSPORTED TO OFFSITE MEDICAL FACILITY "This report is being made pursuant to 10 CFR 50.72(b)(3)(xii), 'Any event requiring the transport of a radioactively contaminated person to an offsite medical facility for treatment.' "At 20:58, Central Standard Time, Cooper Control Room was notified of an individual that was overheated and not feeling well. Cooper is currently in a refueling outage and this individual was working inside the drywell. Initial radiological surveys were started at the scene but were not completed until transportation to medical facilities was commenced. Individual was transported in Cooper Station ambulance. At the time of transport the individual was listed as potentially contaminated. Radiological surveys were completed prior to arrival at the medical facility. These radiological surveys determined that the individual was not contaminated. "NRC Resident has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2005-01-25
41355 | 0 | REGIONAL NUCLEAR PHARMACY |  |  |  |  | 2005-01-24 | 2005-01-25 13:56 | 2005-01-25 | REPORT OF LOST SEALED SOURCE The Radiation Safety Officer (RSO) for the licensee reported that a 0.089 microcurie Co-60 sealed source (manufactured by Isotope Products Lab; serial # 1030152) was found missing during a quarterly inventory at the licensee's facility. The source is used for calibration of a well counter scintillation detector and is stored in a secure location at the facility. The source was last inventoried on 12/13/04 and was discovered missing during an inventory on 1/24/05. A search was conducted throughout the facility. The RSO stated that it is believed that the source is either misplaced or may have been inadvertently disposed of. New procedures for source usage and accountability are going to be implemented. The RSO stated that the quantity of material is not reportable under 10 CFR Part 20 and the report is for information only. The RSO has also notified NRC Region 1 (Beardsley) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NJ | MAT | [5 empty] | 0 | 2005-01-25
41354 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2005-01-24 16:10 | 2005-01-24 16:28 | 2005-01-24 | UNUSUAL EVENT DUE TO UNIDENTIFIED LEAKAGE GREATER THAN 10 GPM The licensee reported that it had indications of unidentified reactor coolant leakage greater than 10 gpm which placed the licensee into an unusual event emergency action level (EAL). Indication of drywell sump level increase and pump out rate gave an approximate leak rate of 30 gpm. The licensee also indicated that drywell pressure was above the normal range. The unusual event declaration was made at 1610 EST. At 1619 EST, the licensee manually scrammed the reactor. The scram was uncomplicated with all rods fully inserting and all systems functioning as required. Decay heat is being rejected to the main condenser. There has been no ECCS injection actuation and reactor water level is being maintained by feed pumps. The licensee has no significant safety related equipment out of service. The licensee stated that there is no indication of further degradation of the leak rate and the source of the leak is still under investigation The licensee has notified the NRC Resident Inspector along with State, Local, and other government agencies. * * * UPDATE FROM LICENSEE (SKORBEK) TO NRC (HUFFMAN) AT 1640 EST ON 1/24/05 * * * At 1640 EST, the licensee upgraded to an ALERT following additional leak rate calculations that indicated the leak rate was approximately 75 - 80 gpm based on drywell sump pump out rate. The licensee's EAL for an alert is RCS leakage greater than 50 gpm. The NRC entered the monitoring mode at 1653 EST. The licensee stated that there has been no increase in drywell radiation levels and that sump water chemistry analysis is in progress. In addition to the normal government agencies notified, the NRC also notified the Canadian Nuclear Safety Commission Duty Officer (R. Chamberlaine). * * * UPDATE FROM LICENSEE (VIA MANAGEMENT BRIEFING) AT 1930 EST ON 1/24/05 * * * The licensee has indications that the leakage may not be reactor coolant leakage. Chemistry results show that the sump water radiation levels are at a level less than would be expected for RCS leakage. In addition, a secondary cooling system was found in a lineup configuration that could have masked leakage from the system. The licensee is waiting to get additional chemistry results on the presence of corrosion inhibitors in the sump water to provide additional confirmation that the leakage is not from the RCS. * * * UPDATE FROM LICENSEE (VIA MANAGEMENT BRIEFING) AT 2200 EST ON 1/24/05 * * * The licensee confirmed the presence of corrosion inhibitors in the drywell sump. In addition, based on manipulations of the Reactor Building Closed Cooling Water system and the Emergency Equipment Cooling Water system the licensee believes that the leakage is from the Reactor Building Closed Cooling Water system and not RCS leakage. The plant is stable and the licensee is continuing to cool down with pressure now at 180 psi and decreasing. * * * UPDATE FROM THE LICENSEE (STROBEL) TO NRC (VIA R3 IRC BRIEFING) AT 22:30 EST ON 1/24/05 * * * The licensee terminated its Alert and Unusual Event at 22:28 EST based on sump water chemistry, activity, and Reactor Building Closed Cooling Water System manipulations that indicate the leakage is secondary cooling water and not from the RCS. The NRC secured from the monitoring mode at 22:36 EST. Notified DHS (Belt), FEMA (Caldwell), DOE (Dasilva), EPA (Baumgartner) USDA (Sykes), and HHS( Pyles). The Canadian Nuclear Safety Commission Duty Officer (R. Chamberlaine) was also notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | ALERT | 3 | MI | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2005-01-24
41353 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2005-01-24 10:00 | 2005-01-24 16:07 | 2005-01-24 | FITNESS FOR DUTY REPORT A non-licensed plant employee was determined to be under the influence of alcohol during a test conducted for cause. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2005-01-24
41352 | 0 | US AIR FORCE |  |  |  |  | 2005-01-24 10:35 | 2005-01-24 10:42 | 2005-01-24 | TWO CHEMICAL AGENT ALARMS DISCOVERED MISSING During a routine inventory, performed every 6 months, it was discovered that two chemical agent alarms, M8A1, each containing 250 microCuries of Americium-241 were missing at Dover Air Force Base located in Delaware. US Air Force is looking for the missing chemical agent alarms. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-01-24
41351 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2005-01-20 10:00 | 2005-01-24 09:27 | 2005-01-24 | AGREEMENT STATE REPORT INVOLVING A PHARMACY SPILL OF SAMARIUM-153 The following information was submitted by the licensee to the State of Colorado in an email dated 1/21/05 at 1137 hours: "On 1-20-05 at approximately 10:00 Cardinal Health, location 48 (Colorado Springs, CO, License number 392-03) had a Sm-153 spill. Approximately 72 mCi of Sm-153 was spilled on the floor next to the main drawing station in the Lab. Our pharmacist was transferring a vial from the Berlex lead vial shield to our tungsten vial shield when the vial got away from him hitting the floor and breaking. The Pharmacist immediately notified the RSO and they started the decontamination process to minimize the risk of cross contamination into other areas of the lab. The area was segregated and the decontamination process was started. Radiacwash was used to decontaminate the area and all contaminated wipes, shoes, and associated materials were bag[ged] and placed with the Sm-153 waste. After initial decontamination was completed the area was surveyed and readings of 200 Mr/hr were obtained at the surface of the floor. Subsequent rounds of decontamination provided a reading of 50 Mr/hr. After we covered the area with padding and lead the exposure readings went down to 0.2 Mr/hr. Wipes were conducted of areas outside of the lead shielding on the floor and were found to be at background levels. We had a brief staff meeting of the pharmacists to access and evaluate the situation and to go over the proper procedures for transfer and dispensing of Sm-153 so that this incident would not be repeated. The corporate office was notified. "The material will be allowed to decay for several days, at which point a determination of the levels of impurity contamination will be assessed. The floor will be removed, if needed, to reduce the exposure rate to acceptable levels. "On 01-21-05 the Radiation Management unit of the State of Colorado, Department of Public Health was notified under section 4.52.2.2 (2) of the state regulations. A written response will be forwarded to the state within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2005-01-27
41350 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2005-01-23 12:00 | 2005-01-23 13:51 | 2005-01-23 | LOSS OF EMERGENCY NOTIFICATION SIREN CAPABILITY DUE TO LOSS OF POWER A significant portion of the emergency notification sirens (19 of 50) located in Calvert County, MD are out of service due to a Southern Maryland Electric Cooperative (SMECO) power outage. The licensee stated that power is expected to be restored by 1700 ET 01/23/05. The licensee will inform the NRC Resident Inspector. * * * UPDATE FROM PACE TO CROUCH @ 2022 HRS EST ON 1/23/05 * * * The out of service sirens have been tested and returned to service as of 2000 hrs. EST. The licensee has notified the NRC Resident Inspector. Notified R1DO (Gray). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-23
41349 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2005-01-14 | 2005-01-21 20:15 | 2005-01-24 | AGREEMENT STATE REPORT - WELL LOGGING SOURCES STUCK IN WELL BORE "Licensee reported to Radiologic Health Branch-Granada Hills (RHB-GH) that on 1/14/05 two well-logging sealed sources became stuck in a well bore at a depth below 5,800 feet. The sources involved are a 1.7 Curie Cs-137, GSR-J, source and a 16 Curie Am-241/Be, NSR-F, source. For the last week the 'fishing' company, Baker Hughes, has been attempting to retrieve the sources. They will continue to do so over the weekend but, if [this is] not successful, the sources will be deemed irretrievable. This occurred on the 'Oxy Elk Hills' well site, about 10-15 miles northeast of Taft, CA, North of Hwy 119. The well is designated '16A-32SRD1.' The rig is designated 'Nabors 472.' If deemed irretrievable the well will likely be sealed in place with a cement plug. Licensee will provide update after weekend and follow with written report." * * * UPDATE FROM SALGADO TO RIPLEY 1355 ET 01/24/05 VIA FACSIMILE * * * The correct well designation is 316A-32S RD-1. Notified R4 DO (Runyan) and NMSS EO (Gersey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-01-26
41348 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-01-20 23:53 | 2005-01-21 08:19 | 2005-01-21 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE BASED ON INABILITY TO VERIFY HPCI KEEP FILL FUNCTION REQUIRED BY TECHNICAL SPECIFICATIONS "At 23:53 CST Unit 2 HPCI pump suction automatically transferred from the Condensate Storage Tank to the Suppression Pool. This caused HPCI to be declared inoperable due to not meeting Technical Specification Surveillance Requirement 3.5.1.1. HPCI keep fill could not be verified so HPCI was declared inoperable. "This event is being reported pursuant to 10CFR 50.72(b)(3)(v) as 'Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.'" HPCI remains inoperable pending venting of the system. The licensee is conducting an investigation to determine the root cause for the automatic transfer. The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2005-01-21
41347 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-01-19 12:51 | 2005-01-19 15:54 | 2005-01-19 | CALLAWAY AUTOMATIC REACTOR TRIP ON LOW STEAM GENERATOR LEVEL "Unit experienced an automatic reactor trip following a momentary loss of power to a process control system power supply that resulted in a low Steam Generator water level. This event is being reported in accordance with 10CFR50.72(b)(2)(iv)(B) due to an automatic Reactor Trip and subsequent Aux Feedwater actuation and Feedwater isolation. On 1/19/2005 at 12:51 CST with Callaway plant at 100% reactor power, a Reactor Trip occurred on low Steam Generator 'A' level due to an apparent momentary loss of power in Control Cabinet [Relay Panel] RP043. "A failed Primary Power Supply to RP043 replacement was in progress at the time of the trip. A momentary power spike on the in-service backup power supply caused the Main Feedwater Regulating valve [MFRV] 'A' to shut and both Main Feedwater Pumps [MFPs] went to their low speed stops. Attempts by the Reactor Operator to take manual control of 'A' MFRV and the MFPs were unsuccessful resulting in the Reactor Trip. "Following the reactor trip all systems responded as designed with no abnormal responses. "The plant is currently stable in Mode 3 with RCS pressure at 2237 psig and RCS temperature at 557.8 F. The Auxiliary Feedwater is currently supplying the Steam Generators with steam flow to the Main Condenser for decay heat removal. All control rods fully inserted. "Both NRC Resident Inspectors were contacted and responded to the Control Room. Corporate Communications will be providing public information on the plant trip to the media." | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2005-01-19
41346 | -1 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2005-01-18 12:55 | 2005-01-19 11:08 | 2005-02-16 | 24-HOUR CONDITION OF LICENSE REPORT FOR POTENTIAL NON-COMPLIANCE OF THE FIRE PROTECTION PROGRAM "The notification is being made pursuant to Unit 2 Operating License for potential non-compliance of the Fire Protection Program. "At 12:55 on January 18, 2005 following the review of Operating Experience for Wolf Creek (ENS 41327), it was discovered that the pilot lines to the manual pneumatic actuator pilot lines on the Halon bottles for the Halon System for the Auxiliary Equipment Room were incorrectly piped. In accordance with TRM 3.7.6.4 a continuous fire watch was established in the area. "This event resulted in a condition that could have rendered the Halon System for the Unit 2 Auxiliary Equipment Room inoperable during a fire. The Unit 1 Auxiliary Equipment Room Halon System was not affected and remained operable. "At this time the cause of this condition is not currently known, and an investigation is ongoing." NRC Resident Inspector was notified of this event by the licensee. HOO NOTE: See Ens # 41326 and 41327 for similar reports. * * * UPDATE AT 1059 ON 02/16/05 FROM MARK CRIM TO W. GOTT * * * "The notification is being made to retract the ENS 41346 Rev 0 reported on 1/19/05 pursuant to Unit 2 Operating License for a potential noncompliance of the Fire Protection Program. "At 12:55 on January 18, 2005 following the review of Operating Experience for Wolf Crook (ENS 41327), it was discovered that the pilot lines to the manual pneumatic actuator on the main and reserve Halon cylinders for the Unit 2 Auxiliary Equipment Room Under Floor Halon System were incorrectly piped. In accordance with TRM 3.7.6.4, a continuous fire watch was established in the area.. Immediately following the event, it was believed that the condition could have rendered the Unit 2 Auxiliary Equipment Room Under Floor Halon System inoperable during a fire. On January 19, 2005 Limerick corrected the piping to meet the vendor design for the manual-pneumatic actuators associated with the Unit 2 Auxiliary Equipment Room Under Floor Halon System. "On January 26, 2005 Chemetron performed a functional test of the Halon System for Callaway with the incorrect pilot line piping and discovered that Halon injected properly with a 2 second delay (See IEN 2005-001). Callaway had a similar Halon system configuration as Limerick Unit 2 Auxiliary Equipment Room Under Floor Halon System (same make and model number manual-pneumatic actuators and cylinder heads). An evaluation of the test report concluded that the Limerick Unit 2 Auxiliary Equipment Room Under Floor Halon System would have actuated in the event of a fire. "In conclusion, despite the pilot line piping error, the Unit 2 Auxiliary Equipment Room Under Floor Halon System would have remained operable and would have completed it's suppression function during a fire. Therefore, there was no violation of the Unit 2 Operating License Section 2.C.(3) for the Fire Protection." The licensee will notify the NRC Resident Inspector. Notified R1DO (E. Coby). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2005-01-19
41345 | 0 | GREEN BAY PACKAGING |  |  |  |  | 2005-01-19 10:30 | 2005-01-19 11:08 | 2005-01-19 | FIXED GAUGE OHMART INSTRUMENT SHUTTER LAMP INDICATOR FAILURE At approximately 10:30 EST on 1/19/05, an Ohmart fixed gauge with a source BAL holder located on an OD-120 scanning platform experienced failure of the shutter lamp indicator circuit. The licensee suspects failure of the micro switch. The source holder contains 300 millicuries of Kr-85 gas. The gauge is used to scan a 60" wide paper web for coating thickness. The licensee confirmed that the shutter is closed. The service company, i.e., Honeywell Measurex located approximately 2 hours driving distance from their facility, has been contacted for repairs. This particular gauge had the source holder, including the shutter, replaced on 11/11/04. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2005-01-19
41344 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2005-01-19 02:37 | 2005-01-19 05:54 | 2005-03-23 | EMERGENCY DIESEL GENERATORS DECLARED INOPERABLE DUE TO AN UNANALYZED CONDITION "The environmental temperature of the tornado missile enclosure for the Emergency Diesel Generators during an accident condition when all three testable rupture disks open is expected to exceed the limiting temperature for the structural concrete. A detailed analysis of the capability of the tornado missile enclosure concrete to meet that standard cited in the USAR section 3.8.3.3.7 has not been located. At 0237 on 19 January 2005, Division 1,2 & 3 Diesel Generators were declared inoperable. Actions of Technical Specification 3.8.2 were directed and compliance verified." NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 03/23/05 @ 1524 BY KEN MEADE TO CHAUNCEY GOULD * * * RETRACTION The following information was provided by the licensee by fax: "An 8-hour notification was made on January 19, 2005, in accordance with 10CFR50.72(b)(3)(ii)(B), for an unanalyzed condition and 10CFR50.72(b)(3)(v)(D), for the loss of the accident mitigation safety function. This report was made after declaring division 1, 2, and 3 diesel generators inoperable because the tornado missile enclosure concrete analysis demonstrating compliance with USAR section 3.8.3.3.7 could not be located. Compensatory measures were taken to protect the concrete and vent lines in the area while an analysis was performed." "The required analysis was performed by a contract engineering firm. On March 23, 2005, the analysis was owner accepted with comments for incorporation into the final report. None of the comments affected the conclusion of the analysis. This analysis confirmed that the concrete enclosure, as originally designed, supported operability of the diesel generators and their support subsystems." "Modifications are being implemented to improve the design margin of the safety related enclosure under accident conditions with the testable rupture disks open. These design modifications are improvements and were not required for past diesel generator operability." "Since the operability of the diesel generators and their support subsystems were not affected, there was no unanalyzed condition that significantly degraded plant safety, nor was there a loss of safety function. Since there was no reportable condition, ENF 41344 is retracted." The NRC Resident Inspector was notified. Notified RDO (Kozak) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2005-01-19
41343 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2005-01-17 07:25 | 2005-01-18 16:50 | 2005-01-18 | NORTH CAROLINA AGREEMENT STATE REPORT - DAMAGED TROXLER The following information was reported by facsimile. The North Carolina Department of Environment and Natural Resources reported a damaged Troxler moisture density gage during construction activities in Reidsville, NC. The NC Radiation Protection Section dispatched a health physicist to the site, the health physicist secured the damaged gage on site and conducted radiation exposure surveys to access the status of the radioactive sources. All indications and surveys support that no radiological damage occurred to those workers involved and no damage was incurred to the environment. Damage to the gage resulted in a potential loss of shielding. If the gage is mishandled the source rod will pull out. The gage was secured and the sliding block was closed. Stakeholders and responsible parties were contacted and are arranging to have the gage appropriately transferred to the manufacturer for further evaluation. Troxler Model # 3430, S/N 34504 Radiological Information: Cs-137 10 milliCi S/N 77-1449 Am/Be 40 milliCi S/N 47-29961 Survey Results: Background: 20 microR/hr three inches from gage: 8 milliR/hr After gage removed: 20 microR/hr (no indication of contamination) NC Incident Report: 05-01 The license number was not provided. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2005-01-21
41342 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2005-01-17 08:58 | 2005-01-17 17:58 | 2005-01-17 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST OF LICENSED OPERATOR The licensee reported a confirmed positive fitness for duty test for drugs [random] of a licensed operator. The individual's unescorted access has been revoked. A work performance investigation is underway. The licensee has notified the NRC Resident Inspector and will be notifying the New Jersey Bureau of Nuclear Engineering. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2005-01-17
41341 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2005-01-17 05:45 | 2005-01-17 16:16 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * LOSS OF FIRE MONITORING CAPABILITY The following information was received by the licensee via facsimile: I. Event Description "On Monday, January 17, 2005, at approximately 0545, Security personnel manning the Central Alarm Station notified the Emergency Team captain [Redacted] that they were unable to detect any information from the facility fire protection system and the system operability was in question. Compensatory measures were put in place: the e-team patrolled the facility with a special emphasis placed on radiologically controlled areas. The system was restored at 0956." II. Evaluation of the Event "10 CFR 70.50(b)(2) states that the NRC must be notified of an event within 24 hours followed by a 30-day written report if the following condition is met: "An event in which equipment that meets all of the following three conditions is disabled or fails to function as designed: [10CFR70.50(b)(2)] "(1) The equipment is required by regulation or license condition to prevent releases exceeding regulatory limits, to prevent exposures to radiation and radioactive material exceeding regulatory limits, or to mitigate the consequences of an accident; and "(2) The equipment is required to be available and operable when it is disabled or fails to function; and "(3) No redundant equipment is available and operable to perform the required safety function. "License SNM-42, Chapter 1, Section 1.9.2 requires that: "Fire detectors be installed and maintained in controlled areas. These detectors will alarm in the continuously manned NPD security alarm station." The system malfunction in the Central Alarm Station prevented them from being continuously monitored. "Evaluations have been performed to determine that the system is not an IROFS and that regulatory limits will not be exceeded by [DELETED]. While SARs 15.9, 15.10, and 15.11 currently list the smoke detectors as IROFS, an evaluation was performed in December, 2004 which determined that these systems were not required to be IROFS and they are in the process of being removed from the ISA Summary. "The equipment was required to be available and operable when it failed to function. Also, redundant equipment was not available; however, compensatory measures were utilized. The emergency team was dispatched to patrol the facility and monitor for local alarms and system activations. Special emphasis was placed on controlled areas. Compensatory measures were in place within 15 minutes of notification of the system loss. III. Notification Requirements "The event is reportable due to: "Although the fire system monitoring is not an IROFS, it is required by the license to mitigate the consequences of an event in a controlled area. Also, it was required to be functional when the communications loss occurred and a redundant system was not available to perform the required safety function. Based on this, notification is required to the NRC within 24 hours followed by a 30-day written report. IV. Status of Corrective Actions: "The equipment has been returned to service and is functioning. An investigation of the event is underway." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
41340 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2005-01-15 | 2005-01-15 14:11 | 2005-01-15 | UNSPECIFIED REQUIREMENT The following information was provided by the licensee via facsimile "On January 15, 2005 at 0750, it was determined that Containment Isolation Valve CC-V-1095 was inoperable due to a post maintenance retest not being performed. The valve was declared inoperable and Technical Specification 3.6.3, Action a. was entered. The valve was satisfactorily retested and restored to OPERABLE status at 1042 on January 15, 2005. A routine preventive maintenance activity was performed on the valve's power supply on January 13, 2005. However, the valve was not stroke tested in accordance with the requirements of Technical Specification Surveillance Requirement 4.6.3.1. This report is made pursuant to the requirements of Section 2.G. of the Seabrook Station Operating License for the violation of the requirements of the Technical Specifications." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2005-01-15
41339 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2005-01-15 02:12 | 2005-01-15 05:08 | 2005-01-15 | MANUAL REACTOR SCRAM DUE TO RECEIVING A MAIN GENERATOR ALARM At 0212 plant operators inserted a manual reactor scram and tripped the main turbine while at 100% power due to indications and alarms of a generator field ground fault. All rods fully inserted and there were no indications of any relief valves lifting. The reactor water level is being controlled within the normal band with feed pump "C" and reactor pressure is being controlled with bypass valves at 800-1090 psig. Also the "A" heater drain pump tripped during the reactor scram due to the water level in the third port heater. The licensee is investigating the cause. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-01-15
41338 | 0 | COOK | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-01-14 10:00 | 2005-01-14 18:58 | 2005-01-14 | FITNESS FOR DUTY A non-licensed employee was determined to be under the influence of illegal drugs during a random test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2005-01-14
41336 | 0 | BROWNS FERRY | 1 |  |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2005-01-14 13:57 | 2005-01-14 16:30 | 2005-01-14 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST The licensee reported a confirmed positive fitness for duty test of a contractor foreman working at unit 1. The test was for cause. The individual's plant access has been terminated. A work performance investigation is in progress. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2005-01-14
41335 | 0 | FRAMATOME ANP |  |  |  |  | 2005-01-14 | 2005-01-14 14:10 | 2005-01-14 | PART 21 REPORT The following information was provided by Framatome ANP "The turbine generator load rejection with failure of the turbine bypass valves to open event (LRNB) is a potentially limiting anticipated operational occurrence (AOO) considered in establishing the MCPR operating limit and confirming that the linear heat generation rate (LHGR) limits are adequate. Framatome ANP analyses for the LRNB event assume that the load rejection will initiate a fast closure of the turbine control valves (TCV) at all power levels. Some plants have indicated that the fast closure of the TCV is not initiated below a plant specific power level. The fast closure of the TCV initiates a scram and minimizes turbine over speed. If a fast closure of the TCV does not occur, the TCV will close at a slower rate, scram will be delayed, and the turbine will over speed. This may increase the severity of the event. The turbine overspend may result in an increase in recirculation pump speed that will also increase the severity of the event." The affected plants LaSalle Unit 2 Cycle 10 and Browns Ferry Unit 3 Cycle 12 have been notified. A set of revised operating limits, which are appropriate for the conditions when a fast closure of the TCV does not occur, have been provided to the affected plants. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2005-01-14
41334 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2005-01-14 01:39 | 2005-01-14 12:24 | 2005-01-14 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM On January 14, 2005 at 0139 hours, the Clinton Power Station balance-of-plant computer became inoperable and caused the loss of the Safety Parameter Display System. The computer was temporarily restored at 0608 but became inoperable again at 0615, and remains inoperable while troubleshooting and repairs are in progress. The event is reportable due to the major loss of emergency assessment capability per 10CFR50.72(b)(3)(xiii). The NRC Resident Inspector has been notified. * * * UPDATE FROM LICENSEE (SHEFFIELD) TO NRC (HUFFMAN) AT 20:20 EST ON 1/14/05 * * * At 12:50 CST, repairs to the plant process computer were completed and the Safety Parameter Display System fully restored. The licensee will notify the NRC Resident Inspector. R3DO (Phillips) was informed. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-14
41333 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2005-01-14 09:55 | 2005-01-14 10:30 | 2005-01-14 | LICENSEE REPORTED A FIRE IN THE TURBINE BUILDING The licensee reported that an NOUE was declared at 10:10 due to a fire in the Turbine Building. The fire started approximately at 09:55 and was extinguished at 10:16. The licensee has not yet assessed the damage to the equipment. Offsite assistance was requested but not used. No emergency equipment was affected and there was no adverse affect on plant operations. The cause of the fire was due to an electrical short. The NRC resident Inspector was notified and state and local will be notified. * * * UPDATE AT 1700 ON 01/14/05 FROM T. ARNETT TO W. GOTT * * * At 1605, the licensee secured from the unusual event. Notified R1DO (P. Krohn), IRD (P. Wilson), NRREO (W. Ruland) and TAS (Hahn). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2005-01-18
41332 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-01-13 | 2005-01-13 17:19 | 2005-01-13 | AGREEMENT STATE REPORT OF STOLEN TRAILER CONTAINING IODINE-125 KITS The State of Florida Bureau of Radiation Control reported information received from Los Angeles County Radiation Management concerning a truck-trailer that was stolen in Miami. Included in the cargo of the stolen trailer were approximately 100 RIA (believed to stand for radioimmunoassay) kits containing an estimated 113 microcuries of Iodine-125. The State of Florida reported that the licensee for the kits is "Diagnostic Products" located in the State of California but had no additional information. The State of Florida will ensure that law enforcement is informed about the radioactive material included in the theft of the trailer. The State of Florida incident report number is FL05-009. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-01-18
41331 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2005-01-13 11:30 | 2005-01-13 16:01 | 2005-01-16 | OFFSITE NOTIFICATION DUE TO FLOOD WATCH The following information was provided by the licensee via facsimile. "On January 13, 2005, at 1300 [CST] hours, Clinton Lake level reached 694 feet - 0 inches (mean sea level). Normal lake level is 690 feet - 0 inches. Per Clinton Power Station (CPS) procedure 4303.02, "Abnormal Lake Level." the CPS Main Dam - Emergency Action Plan requires that a "Flood Watch" be declared. This resulted in a notification to the DeWitt County Sheriff's Department that occurred at 1218 hours. A four-hour notification to the NRC is required due to the notification of an offsite government agency. (Reference 10CFR50.72(b)(2)(xi)). At 1235, the lake level was 694 feet - 3 inches and continuing to rise due to the heavy rains received in the area for the past several hours. Sandbagging has begun as a precautionary measure in the screen house, per CPS procedures." The licensee notified the NRC Resident Inspector. * * * UPDATE FROM LICENSEE (SHELTON) TO NRC (HUFFMAN) AT 17:49 EST ON 1/16/05 * * * The following information was provided by the licensee via facsimile: "On January 15, 2005 at 1115 hours, Clinton Lake level reached normal lake level of 694 feet- 0 inches (mean sea level). Per Clinton Power Station (CPS) procedure 4303.02, "Abnormal Lake Level," the CPS Main Dam - Emergency Action Plan allows termination of the "Flood Watch." This resulted in a notification to the DeWitt County Sheriff's Department that occurred at 1636 hours on January 16, 2005. Per Exelon Reportability Manual, Reportable Event ENV 3.32, "Emergency Action Plans - Cooling Lakes/Ponds," a four-hour notification to the NRC is required due to notification of an offsite government agency. (Reference 10CFR50.72(b)(2)(xi)). Current lake level is 693 feet - 0 inches (mean sea level) and lowering. Inspections have identified no damage due the heavy rainfall or associated elevated lake level." The licensee will notified the NRC Resident Inspector. R3DO (Phillips) notified. | 92 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-01-13
41330 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2005-01-13 09:49 | 2005-01-13 13:32 | 2005-01-13 | ENTRY INTO TECHNICAL SPECIFICATION REQUIRED SHUT DOWN DUE TO LOSS OF ESSENTIAL BUS The following information was provided by the licensee via facsimile: "At 0849 hours on January 13, 2005, during testing of Essential Bus D1 (Undervoltage Units monthly functional test) [the] Potential Transformer secondary fuse blew. This caused an Essential 4160 VAC Bus D1 undervoltage condition. Emergency Diesel Generator #2 auto started due to the undervoltage condition on Essential Bus D1. This auto start of EDG #2 is reportable IAW [in accordance with] 10CFR50.72(b)(3)(iv)(a). "[The licensee entered] into Technical Specification 3.0.3 with a loss of Essential 4160 VAC Bus D1 [with] plant shutdown required within 1 hour if the Essential Bus and DC battery chargers 2P and 2N are not restored. "At 0949 hours, [the licensee] commenced plant shutdown to comply with Technical Specification 3.0.3. The initiation of the plant shutdown is reportable IAW 10CFR50.72(b)(2)(i). [At] 1049 hours, [the license] re-energized Essential 4160 VAC Bus D1 and verified battery chargers 2P and 2N energized. "[At]1051 hours, [the licensee] exited Technical Specification 3.0.3 and stopped plant shutdown. "[The licensee also noted that] at 0855 hours, EDG #2 was shutdown when the #2 Service Water pump did not start. [At] 1144 hours, Service Water Pump #2 [was started and the licensee] declared Service Water Loop 2 OPERABLE." The license has notified the NRC Resident Inspector, will notify local government agencies, and expects to make a press release. | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-01-13
41329 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-01-13 05:04 | 2005-01-13 13:18 | 2005-03-15 | PARTIAL LOSS OF OFFSITE COMMUNICATIONS AND ENS The following information was provided by the licensee via facsimile: "At approximately 05:04 CST on 01/13/2005, CaIlaway Plant became aware of a partial loss of commercial out-going offsite communication ability and the ENS, HPN, and ERDS lines. Contact [capability] was established with the NRC Operations Center via commercial phone lines. Internal and in-coming [commercial] communications are not affected and a number out-going lines are available for emergency use. Callaway is currently reassigning available out-going lines to emergency facilities. Backup communication methods to offsite State and Local agencies remains available. ENS communication will be conducted via commercial phone lines to the NRC Operations Center. "At approximately 05:30 CST Callaway was notified that the communications failure was the result of a severed fiber optic cable at an unknown location. At approximately 09:45 CST Callaway was informed that approximately 4000 feet of fiber optic cable was lost when a bridge near St. Louis, MO., collapsed due to flood waters. At this time there is no estimate for the completion of repairs, but the condition is expected to last up to one week due to inaccessibility resulting from rising flood waters." The licensee has notified the NRC Resident Inspector, State, and local government agencies. * * * UPDATE ON 03/15/05 @ 1711 BY JUSTIN HILLER TO CHAUNCEY GOULD * * * The following information was provided by the licensee via facsimile: The licensee received confirmation at 11:21 CST on 3/15/2005 that permanent repairs were completed to fiber optic lines supporting offsite communications including ENS, HPN and ERDS lines at 06:00 CST on 03/13/2005. This repair replaces a temporary repair established at approximately 14:24 CST on 1/13/2005, and includes the preventive measure of burying the lines below the river bed to prevent subsequent washouts. In addition, the original notification is being corrected to reflect that the fiber optic lines were washed-out from beneath the bridge as opposed to the bridge having collapsed as was originally reported to the licensee. The NRC Resident Inspector was updated. Notified Reg 4 RDO Farnholtz | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-13
41328 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2005-01-13 00:30 | 2005-01-13 02:55 | 2005-01-13 | AGREEMENT STATE - FLORIDA BUREAU OF RADIATION CONTROL - DAMAGED TROXLER GAUGE The Florida Bureau of Radiation Control (Dave Ferguson) called to report a damaged Troxler gauge, with a source strength of 8 mCi Cs-137 and 40 mCi Am-241, is being quarantined in a church parking lot by the St. Lucie police department. An employee of the licensee, Ardaman & Associates, had the gauge in his truck when he was involved in an accident at 1501 SW Floresta Dr. St Lucia, FL. The impact of the crash caused the Troxler instrument to be ejected from the truck causing damage to the handle. The employee was air lifted to the local hospital in critical condition. Dave Ferguson requested the St Lucie police protect the public from the confiscated Troxler gauge by setting a protective boundary of 15 feet. Mr. Ferguson stated the proper authorities should be picking up the damaged gauge within a 2.5 hour period. * * * UPDATE FROM THE FLORIDA BUREAU OF RADIATION CONTROL ON 1/13/05 VIA E-MAIL * * * The licensee took possession of the gauge around 05:00 am on 1/13/05. The report from the State indicates that the gauge came out of its case but was undamaged. The R1DO (Kinneman) and NMSS EO (Essig) has been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2005-01-17
41327 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-01-12 19:45 | 2005-01-12 22:26 | 2005-02-16 | 24 HOUR CONDITION OF LICENSE REPORT REGARDING HALON SYSTEM- ACTUATOR CONNECTION ERROR The following information was received via facsimile from the licensee: "Based upon information provided by Callaway on 1/12/05, it was determined that the manual pneumatic actuators on the Halon suppression systems are piped incorrectly which may result in the inability to actuate the Halon suppression systems manually or automatically. "Each manual pneumatic actuator has clearly marked "A" and "B" ports. Per the M-658 vendor manual series & drawing M-658-00025, the "A" port shall be connected to the actuation pilot manifold or top of cylinder valve and the "B" port shall be connected to the solenoid valve. A field walk down was performed and in all but one case, the manual pneumatic actuator has been piped in the opposite configuration. "This effects the Halon suppression system protecting the ESF switchgear rooms, the Rod Drive MG Set room, the North Electrical Penetration room, the South Electrical Penetration Room, the Switchgear & Switchboard rooms, and the Control Room cable trenches & chases. "Based upon preliminary evaluation, it appears that the Halon suppression systems are inoperable." Fire watches were implemented for the affected areas. The licensee notified the NRC resident inspector. **** UPDATE AT 11:42 ON 02/16/05, E. TAYLOR TO J. KNOKE **** This event report is retracted based on the following information provided from Wolf Creek by facsimile: "Investigation - Informational tests conducted by the Vendor (Chemetron) and witnessed by Wolf Creek, Callaway, and NRC personnel on January 26, 2005 determined that the Halon systems would have properly actuated in the as-found incorrect configuration (port 'A' and 'B' connections reversed). The only identified difference in the actuation sequence between the tests conducted in the incorrect configuration versus the correct configuration is a delay of less than 2 seconds from the time the solenoid received the discharge signal until the first cylinder actuated. There is no regulatory or National Fire Protection Association standard or guideline that places a time requirement on this interval. This very slight time delay would have had no effect on the designed function of the Halon suppression system to extinguish a fire. Additional details are provided in the Chemetron report, "Report on Actuation Arrangements for Halon Extinguishing System Units," (Wolf Creek correspondence 05-00072) that includes the test procedure and results. "Regulatory Evaluation - Guidance for reporting to the criterion of 10 CFR 50.73(a)(2)(ii) is provided in section 3.2.4 of NUREG 1022, "Event Reporting Guidelines 10 CFR50.72 and 50.73." This guidance states that an LER is required for a seriously degraded principal safety barrier or an unanalyzed condition that significantly degrades plant safety. "Operating License Condition 2.C(5)(a) states the following: The Operating Corporation shall maintain in effect all provisions of the approved fire protection program as described in the SNUPPS Final Safety Analysis Report for the facility through Revision 17, the Wolf Creek site addendum through Revision 15, and as approved in the SER through Supplement 5, subject to provisions b & c below. "Conclusion: - Based upon the information provided, the Halon suppression system would have operated to extinguish a fire. This condition is not considered reportable to the requirements of 10 CFR 50.72(b)(3)(ii)(B), 10 CFR 50.73(a)(2)(ii), nor is it a violation of the Operating License Condition 2.C(5)(a). Consistent with this conclusion, ENS notification number 41327 for this event is to be retracted. Notified R4DO (Whitten). NRC Resident Inspector will be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-01-12
41326 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-01-12 13:30 | 2005-01-12 21:48 | 2005-02-23 | 24 HOUR CONDITION OF LICENSE REPORT REGARDING HALON SYSTEM ACTUATOR PORT CONNECTION ERROR "At 1330 on January 12, 2005, station personnel identified an error in connection of pilot lines to the manual-pneumatic actuator on halon bottles required for fire suppression. The vendor was contacted to confirm the configuration. The vendor indicated that the halon bottles would not properly discharge if the pilot lines were not properly connected. "The system engineer inspected the halon systems. It was determined that five of six fire areas protected by halon systems were affected. Fire watches were implemented for the affected fire areas." Affected areas: A-27, Load Center/MG set Room, main - correct, reserve - 1 valve correct/1 valve incorrect A-17, South Electrical Penetration Room, main - correct, reserve - incorrect A-18, North Electrical Penetration Room, Main - correct, reserve - correct C-9, ESF Switchgear room 1*, main - incorrect, reserve - incorrect C-10, ESF Switchgear room 2*, main - incorrect, reserve - incorrect C-27, Control room cable trenches/chases**, bottle 1 - correct, bottle 2 - incorrect "The main bank is sufficient to suppress a fire in a fire area. * One halon system protects both of the fire areas. ** One halon bottle will provide general area coverage. The second bottle ensures sufficient halon concentration for upper portions of the cable chases in the control room. "The design and licensing basis for the fire protection system does not require consideration of a fire in more than one fire area at a time. No degraded fire barriers between the above fire areas were identified which would have allowed a fire to affect more than one of the fire areas at a time. "Repairs were immediately initiated to correct the condition. As of 2010 CST, the repairs have been completed for the affected fire areas and restored to operable status." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM H. BRADLEY TO W. GOTT AT 1225 ON 2/23/05 * * * "Investigation - Informational tests conducted by the Vendor (Chemetron) and witnessed by Wolf Creek, Callaway, and NRC personnel on January 26, 2005 determined that the Halon systems would have properly actuated in the as-found incorrect configuration (port 'A' and 'B' connections reversed). The only identified difference in the actuation sequence between the tests conducted in the incorrect configuration versus the correct configuration is a delay of less than 2 seconds from the time the solenoid received the discharge signal until the first cylinder actuated. There is no regulatory or National Fire Protection Association standard or guideline that places a time requirement on this interval. This very slight time delay would have had no effect on the designed function of the Halon suppression system to extinguish a fire. Additional details are provided in the Chemetron report, 'Report on Actuation Arrangements for Halon Extinguishing System Units,' (Correspondence ULNRC 05-121) that includes the test procedure and results. Halon system function is to establish sufficient halon concentration for sufficient time to suppress a fire. This capability was not lost with the delay in actuation. "Regulatory Evaluation - Guidance for reporting to the criterion of 10 CFR 50.73(a)(2)(ii) is provided in section 3.2.4 of NUREG 1022 rev 2, 'Event Reporting Guidelines 10 CFR50.72 and 50.73.' This guidance states that an LER is required for a seriously degraded principal safety barrier or an unanalyzed condition that significantly degrades plant safety. "Operating License Condition 2.C(5)(c) states the following: The Operating Corporation shall maintain in effect all provisions of the approved fire protection program as described in the SNUPPS Final Safety Analysis Report for the facility through Revision 15, the Callaway site addendum through Revision 8, and as approved in the SER through Supplement 4, subject to provisions d below. "Conclusion: - Based upon the information provided, the Halon suppression system would have operated to extinguish a fire. This condition is not considered reportable to the requirements of 10 CFR 50.72(b)(3)(ii)(B), 10 CFR 50.73(a)(2)(ii), nor is it a violation of the Operating License Condition 2.C(5)(c). Consistent with this conclusion, ENS notification number 41326 for this event is to be retracted." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-01-12
41325 | 0 | US ARMY |  |  |  |  | 2005-01-05 | 2005-01-12 16:36 | 2005-01-12 | TWO LOST M43A1 CHEMICAL AGENT DETECTORS CONTAINING AM-241 SEALED SOURCES On 1/5/05 during maintenance activities at the Oregon National Guard Camp Withycombe located in Clackamas, OR, two (2) M43A1 Chemical Agent Cells [reg. device #1129-D-102S] were discovered missing. Each missing Chemical Agent Cell contained an Am-241sealed source of 250 microCuries. The serial numbers for the two (2) missing sources are Z03-C-12123 and Z03-C-05051. An exhaustive search of the maintenance area including the low-level waste disposal facility was conducted with negative results. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2005-01-12
41324 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2005-01-11 05:30 | 2005-01-12 12:01 | 2005-01-20 | AGREEMENT STATE REPORT INVOLVING STOLEN TROXLER GAUGE During the time frame of 11:00 pm on January 11, 2005 and 5:30 a.m. on January 12, 2005, a Troxler Model 3430 portable gauge containing 9 mCi of Cs-137 and 44 mCi of Am-241/Be was reported stolen. The serial number on the Troxler gauge is not known at this time. The device was reported as fully locked, with all sources in the storage positions. The Nevada Health Division, Radiological Health Section, was notified by the licensee on January 12, 2005 at approximately 7:00 a.m. The individual involved was instructed by corporate RSO to notify local police. No other information is known at this time. An investigation is being conducted. Event Report ID No. NV-05-001 ***** UPDATE AT 13:08 EST ON 1/19/05 FROM S. MARSHALL TO M. ABRAMOVITZ ***** The initial information incorrectly identified the gauge as Troxler, Model 3430. The correct Troxler Model is 3450, Serial # 000863. The Event Report ID No. NV-05-001 was incorrect, it should have read Event Report ID No. NV-05-002. The gauge was found on Friday, 01/14/05, by a private citizen on the curb at a local supermarket. The citizen called the licensee to advise them of the location of the gauge. The licensee will leak test the gauge before returning it to service. Notified R4DO (Clark), NMSS (Essig), and TAS (Hahn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2005-01-17
41323 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2005-01-11 07:19 | 2005-01-11 09:20 | 2005-01-11 | AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE TRIP "At 0719 EST, Vogtle Unit 1 tripped from 100% power due to a Turbine Trip/P9 Reactor Trip, RPS actuation. Initial investigation indicates that Generator relaying was involved. The investigation is ongoing. "As expected for the trip, both Motor Driven Auxiliary Feedwater pumps and the Turbine Driven pump started on Lo-Lo Steam Generator level and AMSAC. All equipment actuated as expected except the Group A Pressurizer Heaters tripped. Technical Specification 3.4.9 Condition B was entered." All control rods fully inserted. Decay heat is being removed via the steam dumps to the main condenser. The electrical grid is stable. The licensee notified the NRC Resident Inspectors. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-01-11
41322 | -1 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2005-01-10 13:45 | 2005-01-10 14:57 | 2005-02-07 | OFFSITE NOTIFICATION TO FEDERAL ENERGY REGULATORY COMMISSION "At 1345 on 1-10-2005, the Federal Energy Regulatory Commission (FERC) Local Engineer was notified by voice mail message of a failure of the North Anna Spillway Emergency Diesel (1-EE-EG-4) during a surveillance PT. 1-EE-EG-4's voltage regulator would not control voltage. The cause of the failure is unknown at this time. This failure only affects the hydro project and there is no impact on station operation. The FERC notification was made per 18CFR12.10(a)." The licensee has notified the NRC Resident Inspector. * * * RETRACTION FROM MICHAEL WHALEN TO JEFF ROTTON AT 1200 EST ON 2/7/05 * * * The following information was provided by licensee via facsimile: "At 1457 hours on January 10, 2005, a 4 hour non-emergency notification was made to the NRC Operation Center as a result of an Offsite Notification to other government agency (i.e- FERC due to an inoperable spillway diesel) in accordance with 10 CFR 50.72 (b)(2)(xi). NRC guidance in NUREG -1022, Event Reporting Guidelines 10 CFR 50.72 and 50.73, provides discussion and notification examples intended to set a threshold that ensures reporting when an issue is safety significant. Some notifications to other government agencies may have little or no significance and may not be reportable to the NRC. "Although the project safety device was inoperable and therefore reportable to FERC there was no safety significance since normal power was available throughout the time the device was out of service. "Based on the discussions in NUREG - 1022, Section 3.2.12 for the notification in question, the North Anna Station Nuclear Safety Operating Committee has determined a NRC Notification was not required because there was no safety significance and is therefore being retracted. The licensee notified the NRC Resident Inspector. Notified R2RDO (Charlie Payne). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2005-01-10
41320 | 0 | SAN ONOFRE | 1 | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2005-01-09 19:45 | 2005-01-10 00:56 | 2005-01-11 | SAN ONOFRE EMERGENCY OPERATIONS (EOF) INACCESSIBLE DUE TO ROAD FLOODING The following information was received from the licensee via e-mail: "On January 9, 2005, at about 1945 PST, the access road to the SONGS MESA facilities became flooded after several days of rain. The San Onofre Emergency Operations Facility (EOF) is located at the MESA and because of the flooding, is inaccessible to passenger vehicles. While the EOF itself is operable, in the event of an Emergency at San Onofre, SCE would direct EOF emergency responders to the alternate EOF located in Irvine, California. SCE is reporting this occurrence to the NRC in accordance with 10CFR50.72(b)(3)(xiii). "At the time of this occurrence, Unit 2 was operating at about 100% power and Unit 3 was operating at about 65% power. SCE will notify the NRC resident inspectors about this occurrence and will provide them with a copy of this report." * * * UPDATE PROVIDED BY C. WILLIAMS TO JEFF ROTTON AT 1418 EST ON 01/10/05 * * * "On January 10, 2005 at about 0143 PST, flooding had dissipated sufficiently for one lane to be passable; at 0615 PST, both lanes were passable. In the event of an Emergency at San Onofre, there is no longer a need to redirect emergency responders to the alternate EOF located in Irvine, California. This report is to advise the NRC of this change in EOF access status. Also note that it is continuing to rain at SONGS and this status is subject to change. "At the time of this report, Unit 2 was operating at about 85% power and Unit 3 was at about 80% power. SCE has informed the NRC resident inspectors and will provide them with a copy of this report." Notified R4DO (Bywater). * * * UPDATE PROVIDED BY C. WILLIAMS TO HOWIE CROUCH @ 0425 EST ON 01/11/05 * * * "On January 11, 2005, at about 0041 PST, the access road to the SONGS MESA facilities again became flooded after several days of rain (reference NRC Operations Log Number 41320). The San Onofre Emergency Operations Facility (EOF) is located at the MESA and because of the flooding, is inaccessible to passenger vehicles. While the EOF itself is operable, in the event of an Emergency at San Onofre, SCE would direct EOF emergency responders to the alternate EOF located in Irvine California. SCE is reporting this occurrence to the NRC in accordance with 10CFR50.72(b)(3)(xiii). "At the time of this occurrence, Unit 2 was operating at about 85% power and Unit 3 was at about 80% power. SCE will notify the NRC resident inspectors about this occurrence and will provide them with a copy of this report." Notified R4DO (Bywater). * * * UPDATE 1430 EST ON 1/11/05 FROM CLAY WILLIAMS TO S. SANDIN * * * "On January 11, 2005, at 0125 PST, Southern California Edison (SCE) reported that the access road to the SONGS MESA facilities had again flooded after several days of rain and that the SONGS Emergency Operations Facility (EOF) was inaccessible to passenger vehicles (NRC Operations Log Number 41320). "On January 11, 2005 at about 0535 PST, flooding had dissipated sufficiently for the road to be passable. In the event of an Emergency at San Onofre, there is no longer a need to redirect emergency responders to the alternate EOF located in Irvine California. This report is to advise the NRC of this change in EOF access status. "At the time of this report, Unit 2 was operating at about 85% power and Unit 3 was at about 81% power. SCE has informed the NRC resident inspectors and will provide them with a copy of this report." Notified R4DO (Russ Bywater). | 0 | 100 | 65 | 0 | 100 | 65 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Decommissioned | Power Operation | Power Operation | Decommissioned | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-10
41319 | 0 | PALISADES | 1 |  |  | [1] CE | 2005-01-09 11:27 | 2005-01-09 13:42 | 2005-01-09 | MANUAL REACTOR TRIP DUE TO LOWERING MAIN CONDENSER VACUUM "The Palisades reactor was manually tripped from approximately 75% power at 1127 hours EST due to lowering main condenser vacuum. Prior to the reactor trip, power was lowered from 100% to 75% in accordance with off-normal procedures in an effort to restore condenser vacuum. The reason for the loss of condenser vacuum is not understood and is being investigated. At 1135 hours an automatic actuation of the auxiliary feedwater system occurred, as designed, to maintain steam generator levels. The atmospheric steam dump valves opened per design on reactor trip, however one dump valve did not fully re-close until instrument air was manually isolated to it. Reactor decay heat is being removed via steaming through the turbine bypass valve to the main condenser. Reportable under 10CFR50.72(b)(2)(iv)(B) and (b)(3)(iv)(A)." After the reactor trip, Main Condenser vacuum rose to 25 inches - sufficient for using the Turbine Bypass valves for removing decay heat. All rods inserted on the manual reactor trip. The electric grid is stable. Licensee notified NRC Resident Inspector. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2005-01-09
41318 | 0 | WHITING CORPORATION |  |  |  |  | 2005-01-05 | 2005-01-07 14:47 | 2005-01-07 | OVERSTRESS CONDITION ON "SINGLE FAILURE PROOF" CRANE TROLLEYS "On January 5, 2005 as a part of a crane re-rate analyses and study Whiting Corporation identified an overstress condition on some hoist equalizer plates and welds. This condition is limited to the hoists of some redundant (single failure proof) cranes. "Whiting Corporation has performed a preliminary review and have isolated the problem to the family of redundant trolleys also known as single failure proof trolleys. No other types of cranes are affected. It has not been established at this time which specific redundant trolleys are impacted. This assessment will require a cases by case review. "Whiting Corporation have or are attempting to contact these customers directly to notify them of this circumstance. These are the only potentially impacted customers. "The hoist units identified above, are to be inspected as follows and then limited to 50% of rated capacity until such time as the units can be evaluated and/or upgraded. The following specific serial numbers can be operated at 100 Tons (SN 10403, 10388, 10389, 10510). SN 10698 is currently being evaluated and is limited in capacity by other factors being addressed with the customer. The area to visually inspect, for cracks in the plates or welds, is the assembly, adjacent to the rope termination, at each end of the equalizer arm, that the nut on the rope fitting bears against. Suspicious visual indications of potential cracks can be further examined by Magnetic Particle testing if warranted. A lack of any visible cracks during visual examination will allow the unit to be placed in operation at the 50% reduced capacity. Please note no reports of field failures or cracks have been reported as of the issuance of this notice. "The following is a list of the family of redundant (single failure proof) cranes that will require a detailed evaluation. Niagara Mohawk Power - Nine Mile Point -125 Ton Exelon Corporation (Commonwealth Edison) - Dresden Station -125 Ton Exelon Corporation (Commonwealth Edison) - Quad Cities Station -125 Ton Dominion Nuclear Connecticut-North East Utilities-Millstone (Believed to be Unit 1 in Waterford)-Reactor Room Entergy Nuclear (Vermont Yankee) - Vernon Station - Reactor Room-110 Ton Neb. Public Power - Cooper Nuclear Station - Reactor Room -100 Ton Exelon Corporation (Philadelphia Electric) - Peach Bottom -125 Ton (2) (AEP) (Indiana Michigan power) - D. C. Cook Station -150 Ton Carolina Power & Light - Brunswick Station -125 Ton Southern Nuclear (Alabama Power) - Farley Plant - 125 Ton Energy Northwest (WPPSS) -Hanford Unit # 2 - Reactor Room -125 Ton Progress Energy (PGN) (Carolina Power & Light) - Robinson Station -125 Ton Mississippi Power & Light - Grand Gulf Station -150 Ton (2) Long Island Lighting - Shoreham Station -125 Ton Constellation Nuclear (Niagara Mohawk Power) - Nine Mile Point Station -125 Ton AEP (Indiana Michigan power) - D. C. Cook Station -150 Ton Indiana Michigan power - D. C. Cook Station - 20 Ton" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2005-01-07
41317 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2005-01-07 17:00 | 2005-01-07 19:18 | 2005-01-07 | LOSS OF A FIRE SAFE SHUTDOWN SUCCESS PATH "On January 07, 2005, conditions were discovered where a postulated fire could cause the loss of a fire safe shut down success path. Wolf Creek is in Mode 1, at 100 % power. "During reviews associated with post fire safe shutdown reanalysis work, Wolf Creek personnel discovered that power and control cables for Boron Injection tank (BIT) inlet valve EMHV8803A could be damaged by a fire in Fire area A-1. This valve is needed because the A train is the protected train for this fire area. This does not meet our commitments to 10 CFR50 Appendix R.III.G as reflected in our approved Fire Protection Plan. "Following a fire in the plant that requires a plant shutdown the function of the CCP and Bit Inlet valve is to inject borated water into the reactor to maintain reactor water inventory. A fire in this fire area (A-1) has the potential to cause the above-mentioned valve to not function properly and cause a loss of the capability to maintain inventory. Based on the guidance provided in NUREG 1022, Revision 2, this situation meets the criterion of 10 CFR 50.72(b)(ii)(B) for an 8 hour ENS notification, as it relates to being in an unanalyzed condition. "The licensee has implemented a 1-hour fire watch in this fire area. "The licensee has notified the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2005-01-07
41316 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2005-01-07 16:00 | 2005-01-07 17:30 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FAULTY PROGRAMMABLE LOGIC CONTROLLER (PLC) FOR OXIDE DISSOLUTION OPERATION The Nuclear Fuel Services, License # [DELETED], reported that a faulty PLC evoked an event that degraded the safety conditions of the plant. Their comments are described below in a statement/answer format. The statement is cited first and the answer follows. "Actual or potential health and safety consequences to the workers, the public, and the environment, including relevant chemical and radiation data for actual personnel exposures to radiation or radioactive materials or hazardous chemicals produced from licensed materials (e.g., level of radiation exposure, and duration of exposure): "There were no actual health and safety consequences to workers, the public, or the environment. There were also no personnel exposures to radiation, radioactive materials, or hazardous chemicals produced from licensed materials. The potential Nuclear Criticality Safety (NCS) consequences for workers were low given the very low likelihood of adding a sufficient mass of a more reactive/incorrect material type to the system. "The sequence of occurrences leading to the event, including degradation or failure of structures, systems, equipment, components, and activities of personnel relied on to prevent potential accidents or mitigate their consequences: "On January 7, 2005, it was determined that the Programmable Logic controller (PLC) for the oxide dissolution operation had a negative holdup value. Upon investigation, a negative holdup value in the PLC results in the PLC using an artificially high mass limit. This could allow the system mass limit to be exceeded. The PLC is an item relied upon for safety and is credited as one of the mass controls in the safety basis. "Discuss whether remaining structures, systems, equipment components, and activities relied on to prevent potential accidents or mitigate their consequences are available and reliable to perform their function: "The remaining activities relied on to prevent potential accidents are available and reliable to perform their function. Operations personnel verified that the correct material type and quantity was added to the system. "Actions taken in response to the event: "The operation was shutdown until compensatory measures can be put in place. "Safety Significance of Event: "The safety significance was low for the event given the very low likelihood of adding a sufficient quantity of a more reactive/incorrect material type to the system. A more reactive/incorrect material type was not added to the system. It should also be noted that this other/incorrect material type is not present in the facility. "Brief scenario of how a criticality could occur: "In order for a criticality to occur, multiple occurrences of an excessive amount of a more reactive/incorrect material type would have to be added to the system. "What are the controls or control systems and the failures or deficiencies? "The controls were limitations on the mass and material types input into the system. The PLC is used to control the mass input into the system. The PLC for the oxide dissolution operation had a negative holdup value. Upon investigation, a negative holdup value in the PLC results in the PLC using an artificially high mass limit. This could allow the system mass limit to be exceeded. The PLC is an item relied upon for safety and is credited as one of the mass controls in the safety basis "What are the corrective actions taken and when was each implemented? "On January 7, 2004, the operation was shut down. Compensatory measures are in the process of being developed." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
41315 | 0 | BOEHRINGER INGELHEIM |  |  |  |  | 2004-12-07 | 2005-01-07 11:22 | 2005-01-07 | REPORT OF LOST NICKEL-63 FOIL STRIP The licensee reports that it discovered an Aerosol Technology Machine (manufactured by CH Technologies Incorporated, Westwood NJ) was missing from its inventory. The machine is used to eliminate static electricity and contains a 10 milliCurie Nickel-63 foil strip. The machine was last confirmed to be present around October 2003 when it moved out of a laboratory space into a hallway. It is possible that the machine was disposed of but the licensee is still searching for the device. The licensee has notified NRC Region 1 (Tom Thompson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2005-01-07
41314 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2005-01-07 | 2005-01-07 09:26 | 2005-01-07 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Nebraska reported that 19 tritium exit signs that were held under general license by Albertsons Grocery Store are missing from a store location in Omaha. The signs were manufactured by NRD, Inc., Model T-4001, with each sign containing 19.8 Curies of tritium in 1991. The State was informed in October of 2004 by Albertsons that the Omaha store had been sold to a "No Frills" supermarket chain. The State contacted "No Frills" in November 2004 and was informed that the signs could not be located. Investigation determined that the signs were removed by Albertsons in 2002 when the store was remodeled and replaced with electrical exit signs. The Albertsons store manager at the time of the remodeling was not aware of what was done with the signs. The State also confirmed that with NRD, Inc. that the signs had not been returned to the manufacturer. The State believes that the signs were probably sent to a landfill and plans to close the investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2005-01-12
41312 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-12-29 12:00 | 2005-01-06 20:35 | 2005-01-06 | THEFT OF 10 MILLICURIES OF CADMIUM 109 FROM PERSONAL VEHICLE "Licensee reported to Radiologic Health Branch-Granada Hills (RHB-GH) the theft of an XRF fluorescence device from a parked private vehicle the night of 12/29/04 from a residence in Long Beach, CA. "The device is a Nitton, Model XL-309, S/N U823NR4869, containing a radioactive sealed source, special form, 10 mCi nominal, Cadmium 109. "The device was parked overnight in a private vehicle on 12/29/04 in front of a garage facing an alley. The device was in the care of an employee of the licensee after being used for a lead paint testing job in Paramount. The device was stored in the trunk of the vehicle. The employee noticed the vehicle had been broken into the next morning but did not notice the device missing until after reporting to work. Employee claimed that the alarm system was defeated. Upon discovery that the device was missing, the employee notified the employer and a police report was made by phone to the Long Beach Police Dept., East Division (Police Report No. 040106759, 562-570-5880), The device was in its transport case. RHB-GH is initiating an investigation." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2005-01-11
41311 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2005-01-06 07:45 | 2005-01-06 13:00 | 2005-01-06 | LOSS OF POWER TO OFFSITE SIRENS GREATER THAN 1 HOUR DUE TO INCLEMENT WEATHER "At about 07:45 hours CST on January 6, 2005, greater than 25% of the Clinton Power Station (CPS) offsite sirens were out of service. 17 of 44 sirens were not available for greater than 1 hour due to inclement weather. "DeWitt County was notified of the sirens being unavailable. At approximately 09:11 hours on 1/6/2005, 10 sirens were returned to service when power was restored to the area." The licensee is investigating the actual cause for the sirens being out of service. The seven sirens remaining out of service are in the process of being restored. The licensee has notified LLEA and the NRC Resident Inspector. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-06
41310 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2005-01-06 01:12 | 2005-01-06 04:01 | 2005-01-06 | MANUAL REACTOR SCRAM DUE TO REACTOR RECIRCULATION PUMP TRIP "At approximately 0106 on 1-6-05, Reactor Recirculation Pumps A and B down-shifted from fast to slow speed which resulted in reactor power decreasing from 100% to approximately 46%. As operators started to reduce power using control rod insertion, Reactor Recirculation Pump A tripped to 'off.' At 0112 on 1-6-05, a manual reactor scram was inserted due to operating under undesirable power to flow conditions. At approximately 0119, the operators were unable to start the Motor Feedwater Pump, Reactor Core Isolation Cooling system was manually started. Level control was established using a Reactor Feed Pump Turbine and Reactor Core Isolation Cooling. The Main Steam Isolation Valves were closed to limit cooldown. Reactor level is being controlled with the Reactor Core Isolation Cooling System and safety relief valves are available for reactor pressure control. "The cause of the Reactor Recirculation Pumps down-shifting and the subsequent trip of Reactor Recirculation Pump A is still under investigation. The cause of the Motor Feedwater Pump failure to start is likewise under investigation." All control rods fully inserted. The lowest reactor level reached was 154 inches above TAF. The electrical grid is stable and ESF systems remain available. Reactor pressure and level are being maintained by the Reactor Core Isolation Cooling system. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2005-01-06
41309 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2005-01-06 07:00 | 2005-01-05 17:06 | 2005-01-20 | MODIFICATION TO PROCESS COMPUTER THAT WILL IMPACT ERDS AND SPDS "The Plant Process Computer System (PPCS) will be taken out of service for an approximate 2 week period to implement a planned modification. The current PPCS is being replaced and the computer outage is required to allow cutover to the new PCCS. During this time period ERDS and SPDS will not be available. Also, a small portion of the plant annunciator system (Trouble Light Alarms) will not be available. Regulatory Guide 1.97 Category 2D Containment Temperature and Category 3D Component Cooling Water Temperature indicators will not be available in the Control Room, although other instrumentation is available to monitor these parameters. "This is an 8-hour reportable event per 10 CFR50.72(b)(3)(xiii) Major Loss of Assessment Capability. The operation of plant systems will not be affected due to this planned action. ERDS and SPDS parameters will be monitored by control board indications. Compensatory actions have been developed." The PPCS outage is expected to commence around 0700 CST on 1/6/05. The licensee has informed the NRC Resident Inspector. * * * UPDATE ON 1/20/05 AT 1724 FROM J. ROBB TO W. GOTT * * * The Plant Process Computer System was restored at 0005 CST on 01/20/05. ERDS and SPDS are now available. The licensee notified the NRC Resident Inspector. Notified R3DO (A.M. Stone). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE | INFORMATION ONLY |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-05
41308 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2005-01-02 | 2005-01-05 09:26 | 2005-03-15 | TEXAS AGREEMENT STATE REPORT: STOLEN TROXLER MOISTURE DENSITY GAUGE "The gauge was locked and secured to the technician's company pickup truck. The technician had taken the gauge to his residence for storage.. The technician discovered the gauge was missing from the truck and determined that the lock securing the wire rope cable which secured the transport case had been cut. The gauge and transport case along with other tools from the vehicle are missing. A police report was filed with the Houston Police Department. The gauge is a Troxler Model 3430, Serial No. 31792, containing two sealed sources: Cs-137, nominal 8 millicuries, Serial No 750-6702, and Am-241/Be, nominal 40 millicuries, Serial No. 47-1785. The Licensee issued a memorandum on January 3, 2005 to all personnel regarding gauge storage and transport procedures. "Licensee is planning to offer a reward and will publicize through the local media." Texas Incident ID No: I-8196 * * * UPDATE FROM TEXAS (K. VERSER) TO M. RIPLEY 1654 EST 03/15/05 * * * The State provided, via email, details of interviews held with the licensee along with a listing of proposed corrective actions to prevent recurrence of this and similar incidents. Contact the NRC Headquarters Operations Officer for details. Notified R4 DO (T. Farnholtz) and NMSS EO (G. Janosko) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-01-10
41307 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2005-01-04 12:30 | 2005-01-04 18:32 | 2005-01-18 | SITE HAD 86.2% OF THEIR EMERGENCY ALERT SIRENS INOPERABLE "At 1230, 1/4/05, while performing a weekly test of alert sirens utilized in the prompt public notification system, it was determined that the twenty five sirens actuated by the Callaway County Emergency Operation Center (EOC) would not operate. There are a total of twenty nine alert sirens distributed among four counties and failure of the twenty five sirens actuated by Callaway County equates to a loss of 86.2 % of the alert sirens. During the period when the faulted sirens were unavailable, the back-up automated telephone calling service Community Alerting Network System (CANS) and the tone alert radio system were available and the Callaway County EOC was instructed to perform local route notifications as a backup method of notification. At 1345, 1/4/05, the twenty five Callaway County actuated sirens were restored and all twenty nine alert sirens were tested satisfactorily." "Initial investigation indicates a computer software problem related to the feedback system. This caused a failure to occur in a circuit at the Callaway County radio tower and in the back-up manual system. The system vendor is researching the failure experienced and expects to provide a failure determination report by 1/5/05. Final corrective actions will be developed based upon the information provided by the vendor." The NRC Resident Inspector and local agencies were notified and the State will be informed. * * * RETRACTION FROM LICENSEE (OLMSTEAD) TO NRC (HUFFMAN) AT 1440 EST ON 1/18/05 * * * The following information was provided by the licensee via facsimile: "On 1/4/05, EN # 41307 was made from the Callaway Plant Control Room reporting 25 sirens actuated by the Callaway County Emergency Operations (EOC) would not operate. The Root Cause Analysis Team determined during their investigation that a siren failure did not occur. Analysis of the computer logs and interviews with the Callaway County Emergency Management Director (EMD) and the siren vendor revealed the sirens were not activated. Investigation by the siren manufacturer and testing of the siren system verified that the sirens would have sounded if they had been activated. "Prior to activating the sirens, the county Emergency Management Director (EMD) attempted to poll the sirens. This poll locked up on the first siren. The EMD and the Siren Technician assumed the locked up polling of the sirens also locked up the siren activation program and therefore did not attempt to sound the sirens. Subsequent investigation by the siren manufacturer indicated that the sirens would activate even with the system polling function locked up. "On 1/14/05, testing of the system in a locked up polling configuration confirmed that the sirens would have sounded if activated. As indicated in the previous notification, all sirens were successfully sounded at 1345 on 1/4/05, when given the first signal to activate. "During an emergency activation, the written instruction direct that the sirens be activated without first polling the sirens. Personnel responsible for siren activation are not responsible for siren testing and would not have hesitated to activate the sirens, had there been an actual event. Therefore, a siren activation failure did not occur. The sirens remained capable of activation if required. This notification is being retracted." The NRC Resident Inspector, State, and local government agencies have been notified by the licensee. R4DO (Clark) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2005-01-04
41306 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2005-01-01 05:00 | 2005-01-04 10:47 | 2005-01-04 | AGREEMENT STATE REPORT OF TRUCK CRASH RESULTING IN MINOR CONTAMINATION AND LOSS OF RADIOPHARMACEUTICAL VIALS A truck carrying radiopharmaceuticals for Cardinal Health had an accident on Eastbound Route 50 near the Cape St. Claire exit in Annapolis MD. Police, Fire Department and an ambulance responded to the scene. The licensee's Radiation Safety Officer (RSO) also responded. Survey indicated contamination over an area of approximately 100 feet. It was determined that an 8 mCi vial of Tc99 MAA had been damaged and spilled during the accident. The Maryland Department of Environment and Hazmat were summoned. The area was decontaminated with a high-powered water spray. However, further investigation determined that an ammo can containing two vials of TC99m and TC99 MAA was missing at the accident scene. The two vials had a total activity of 566 mCi as of 0400 on 1/01/05. An extensive search of the area was unable to locate the ammo can with the two missing vials. Neither the licensee nor the Maryland Department of Environment believe that the vials pose any health risk since the Tc99m has a 6 hour half life. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2005-01-07
41305 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2004-12-21 | 2005-01-03 13:07 | 2005-01-03 | AGREEMENT STATE REPORT OF A LOST COBALT- 57 SOURCE The State Licensee, Advanced Radiology, located at the PET Center at North Arundel Tate Center in Glen Burnie, MD reported that a Model BM06 Gamma Reference Standard calibration device containing 5.66 milliCuries of Co-57 source is missing. The source has not been located and is believed to have been inadvertently disposed of in the trash by housekeeping when they made unauthorized entry to the hot lab. As a corrective action the hot lab door lock was changed. The State of Maryland responded on 12/30/04. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2005-01-06
41304 | 0 | PALO VERDE |  | 2 | 3 | [1] CE,[2] CE,[3] CE | 2004-12-31 10:42 | 2004-12-31 15:15 | 2004-12-31 | PLANT HAD AUTO START AND LOADING OF TWO EMERGENCY DIESEL GERERATORS "On December 31, 2004, at approximately 10:42 Mountain Standard Time (MST) a valid actuation of the Palo Verde Nuclear Generating Station Unit 2 Train A Emergency Diesel Generator (EDG) and Unit 3 Train B EDG occurred as a result of undervoltage on their respective safety buses. Both EDGs started and loaded as designed. "The loss of power to the two safety buses was the result of the deenergization of Startup Transformer X01 when Westwing transmission line #2, one of seven 525 kV transmission lines at the Palo Verde switchyard, relayed off. Prior to the event, maintenance and testing were in progress on Westwing Line #1. The apparent cause of the event was inadvertent operation of an adjacent Line #2 protective relay while testing Line #1. "Both Units 2 and 3 entered Technical Specification LCO 3.8.1 Condition A for one (of two) required offsite circuits inoperable. Normal offsite power was restored to each safety bus in Units 2 and 3 (at 11:45 MST), the LCO exited and the Unit 3 EDG returned to standby. During shutdown of the Unit 2 A EDG following successful loading of the Safety bus, the EDG was declared inoperable due to a Jacket Water leak and LCO 3.8.1 Condition B was entered. No Emergency Plan declaration was made and none was required. "Both units were at approximately 100% power, at normal operating temperature and pressure prior to and following the EDG actuations. No other ESF actuations occurred and none were required. No major equipment was inoperable prior to the event that contributed to the event. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The NRC Resident Inspector has been notified of the ESF actuation and this ENS notification." | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-12-31
41303 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-12-27 | 2004-12-31 10:52 | 2004-12-31 | MILITARY RADIO WITH RADIUM-226 FOUND IN SCRAP METAL BIN On Monday, December 27, 2004 the Agency was contacted by the Emergency Management Coordinator, for Waco-McLennan County with concerns over a metallic box retrieved from a scrap metal recycling bin. This item was first noted as being radioactive by a scrap metal firm under the name of Lipschitz on Elm Street in Waco who purportedly has sensitive scintillation detectors to screen in-coming scrap. Once the item was returned to the City of Waco landfill, the Emergency Management Coordinator confirmed that one end of the two part metal device or container was indeed emitting radiation at a rate of 2mR/hr at an unspecified distance as measured with a yellow CVD meter obtained from the local haz-mat team. State personnel responded on Tuesday, December 28, 2004 to the landfill and performed extensive surveys of the grounds, personnel, and equipment that may have come in contact with the device. All results were negative as measured with a pancake GM and the surface dose rate of 10mR/hr was recorded. After triple bagging, the device was brought to the State's Austin office. Trace amounts of removable contamination was noted only on the inside of the cover for the controls of the rad/rec/trans which was labeled with the following data: Type CKB-43069-A, Radio-Transmitter-Receiver, Model Maw-1,Serial #784, NAVSHIPS 91529A. Radium-226 was confirmed as the radionuclide present by spectral analysis on Thursday, December 30, 2004. The State is seeking contact within the Navy who will assist in appropriate disposition. Texas Incident # I-8194. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-01-05
41302 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-31 03:15 | 2004-12-31 06:27 | 2005-01-03 | LOSS OF EMERGENCY NOTIFICATION SIRENS "Loss of 21 emergency notification sirens due to a loss of power. A rain storm in San Luis Obispo county resulted in a loss of a local substation. This substation supplies power to 21 of [over 400] emergency sirens. Investigation and repair of the substation is in progress." This siren outage eliminates emergency notification siren coverage in one specific area. The local sheriff department has been notified to implement alternate notification protocols until the sirens in that area are operable. The licensee will notify the NRC Resident Inspector. * * * UPDATE FROM DIABLO CANYON (J. WELSCH) TO M. RIPLEY 0945 EST 12/31/04 * * * Power was restored to the substation and the 21 affected emergency notification sirens have been returned to service. The licensee will notify the NRC Resident Inspector. Notified R4 DO (T. Farnholtz). * * * UPDATE FROM DIABLO CANYON PARKER TO MACKINNON 1620 EST 01/03/05 * * * Correction: Total number of emergency sirens at Diablo Canyon site is 131 sirens not 400 sirens. R4DO (Linda Smith) notified. The NRC Resident Inspector was notified of this update. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-31
41301 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2004-12-30 23:55 | 2004-12-31 02:03 | 2004-12-31 | HYDRAZINE RELEASE TO SETTLING POND EXCEEDED ALLOWED RELEASE RATE "At 2355 on 12/30/04, the National Response Center was notified that the environmental release limit for hydrazine had been exceeded. A maximum of 3.8 pounds of hydrazine was released over an 8 hour period which exceeded the reportable quantity of one pound in 24 hours. A feed and bleed of the condensate system was in progress in preparation for plant startup. The release limit was exceeded due to a higher than expected concentration of hydrazine in the condensate system. The cause of the event is under investigation. The hydrazine addition was secured and draining of the system has been terminated. All of the hydrazine has been contained in a settling pond within the protected area." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-31
41300 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-12-23 15:30 | 2004-12-30 11:25 | 2004-12-30 | AGREEMENT STATE LOST RADIOACTIVE SOURCE "University of Mass - Amherst called [Massachusetts Radiation Control Program] to report a missing Ni-63 source in an ECD detector. A Varian Model 3700 gas chromatograph [GC] machine was due for leak testing on 11/15/04. The unit could not be found and was presumed missing. The unit's ECD contained a Ni-63 source (8 milliCurie) and had serial number A3240. In Sept / Oct of 2004, laboratory equipment was moved and / or sent to the trash. It is suspected that the missing GC was mistakenly sent out for disposal at that time, and in Nov. 2004, the licensee determined the unit was missing." The calibration date of the source activity was not known at the time of the report. The last known confirmed inventory of the device was when the last leak test was performed in May 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2005-01-04
41299 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-29 14:00 | 2004-12-29 16:37 | 2004-12-29 | LOSS OF COMMUNICATIONS TO SITE DUE TO FIBER OPTIC LINE CUT At approximately 1400 CST all commercial and FTS 2000 telephone communications to and from Byron Station was lost due to a fiber optic cable cut 20 miles North of the plant, near Rockford, Il. Licensee can contact the NRC Headquarters Operation Officer via a Control Room cell phone. NRC Headquarters Operation Officer is unable to call the site using the cell phone because incoming calls are routed through Rockford, Il. Licensee stated that the line problem is being worked on. NRC Resident Inspector has been notified of this event by the licensee. * * * Update 12/29/04 at 2139 EST by Koeplin to MacKinnon * * * Commercial and FTS telephone service returned to service. Licensee will notified the NRC Resident Inspector. R3DO (C. Lipa) & NRR EO (Pat Hiland) notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2004-12-29
41298 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-12-28 22:46 | 2004-12-28 23:51 | 2004-12-29 | MANUAL REACTOR TRIP DUE TO GENERATOR EXCITER COOLING WATER LEAK "Unit 3 unplanned Manual Reactor trip from 70% due to Generator Exciter cooling water leak. Leak caused voltage regulator transfer to manual. Cooling water leak was isolated after the manual reactor trip. Water was noted in the 3B 4kv safety related bus room affecting 3B Residual Heat Removal Pump breaker. This component is considered inoperable pending corrective action. Plant is stable in mode 3. "Auxiliary Feed Water actuated automatically, as expected, and operated normally following the reactor trip." All control rods fully inserted. The MSIV's were manually closed to prevent excessive RCS cooldown and decay heat is being removed via the atmospheric steam dumps. Unit 4 was unaffected. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-12-29
41297 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2004-12-27 17:20 | 2004-12-27 18:49 | 2004-12-28 | MANUAL REACTOR TRIP FOLLOWING PROBLEM WITH STEAM GENERATOR WATER LEVEL CONTROL The licensee reported a "manual reactor trip due to low steam generator level caused by feedwater control system malfunction." The licensee stated that it manually tripped the reactor with steam generator water level at approximately 40% and decreasing. Steam generator water level control was restored following the trip using auxiliary feedwater. All rods fully inserted on the trip. No safety or relief valves lifted. Auxiliary feedwater was manually actuated and decay heat is currently being discharged via the atmospheric dump valves. Unit 1 is at full power and unaffected and the grid is stable. The plant was in no major LCOs at the time. All systems functioned as required. The licensee is still investigating the feedwater control system malfunction. The NRC Resident Inspector has been notified. * * * UPDATE FROM LICENSEE (WILLIAMS) TO NRC (HUFFMAN) AT 1818 ON 12/28/04 * * * "The original notification stated that decay heat was being discharged via the atmospheric dump valves post-trip when the decay heat removal mechanism being used was steam dump to the condenser via the steam bypass control system. Additionally, although the auxiliary feedwater system was used to deliver water to the steam generators post-trip, the main feedwater system was available for this function. The investigation into the feedwater malfunction is still in progress." The NRC Resident Inspector has been informed. R2DO (Moorman) notified. | 0 | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-12-27
41296 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-12-27 00:31 | 2004-12-27 01:02 | 2004-12-27 | UNUSUAL EVENT DECLARED DUE TO FIRE INSIDE PROTECTED AREA LASTING GREATER THAN 10 MINUTES "Fire within the Protected Area lasting more than ten minutes. The Unusual Event was declared at 00:31 EST. The fire was located in the small arms locker in an out-building within the Protected Area. The fire was extinguished at 00:49 EST. Darlington County Fire Department responded." Onsite security detected smoke and heard ammunition rounds discharging from a locked door small arms locker located in the Protected Area. Security reported the fire and onsite fire personnel responded. At 00:49 EST the fire was declared extinguished and a fire watch was set. No personnel were injured in this event. Darlington Fire Department was called and responded to the site, however, by the time they arrived the fire was put out and they, therefore, did not enter the Protected Area. Security believes this to be an isolated event with no evidence of malevolent actions. The Licensee notified state and local agencies and the NRC Resident Inspector. * * * UPDATE ON 12/27/04 AT 02:03 EST FROM B. STOVER TO J. KNOKE * * * At 01:30 on 12/27/04 the Licensee terminated the Unusual Event. The Licensee indicated the fire has been out for 41 minutes. All on-site small arms lockers were inspected by security and no evidence of any damage or tampering was found. The LLEA was not called for this event, however, they did respond when the Darlington Fire Department responded. The LLEA did not enter the Protected Area. As a precautionary follow-up measure the Licensee requested the Darlington County Sheriff's office send an arson investigator to the scene. The Licensee notified state and local agencies and the NRC Resident Inspector. Notified R2DO (Julian), NRR (Johnson), IRD (Wilson), FEMA (Steindurf), and DHS (Akers). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-12-27
41295 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-12-26 09:04 | 2004-12-26 12:48 | 2004-12-26 | LOSS OF COMMUNICATIONS/RESPONSE CAPABILITY "At 0804 hours EST, on December 26, 2004, at the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, a partial loss of non-vital offsite power occurred causing the inoperability of the Emergency Response Facility Information (ERFIS) computer system for greater than one hour. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), among others. At 0852, the remaining non-vital offsite power was lost resulting in the disabling of the primary Emergency Operating Facility (EOF). The off-site alternate EOF remained operational. Power to the primary EOF was restored at 0913 and the ERFIS computer system was restored to operable status at 1010 hours on December 26, 2004. "As required by plant procedures, appropriate assessment of plant conditions, notifications, and communications could still have been made through alternate methods during the time that the ERFIS computer system was inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remained available to assess plant conditions, make notifications, and accomplish required communications, as necessary." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-26
41294 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2004-12-26 09:18 | 2004-12-26 09:32 | 2004-12-26 | UNUSUAL EVENT DECLARED DUE TO LOSS OF CONTROL ROOM SAFETY SYSTEM ANNUNICATOR PANELS A&B Fermi Unit 2 declared an Unusual Event at 09:18 EST when the computer software to all Safety System annunciators in the Control Room failed. The reactor was operating at 100% power in Mode 1. Control Room Operators monitored plant conditions by looking at applicable hardware gauges in the Control Room. No transient conditions within the plant occurred during this event. Licensee is investigating whether the periodic testing of the "Auto Start" on the DC Main Turbine LO Pump caused the software to malfunction. Course of action by Licensee to restore the annunciator system was to reboot the computers. Licensee notified state and local agencies and NRC Resident Inspector. *** UPDATE ON 12/26/04 AT 10:35 EST FROM P.FALLON TO J.KNOKE "Reactor is stable at 100% power, safety related annunciators are operating normally on both normal and backup computers. A corrective action document is being submitted to investigate a connection between the DC Main Turbine LO Pump switch and the loss of annunciators." At 10:29 EST the licensee terminated the Unusual Event with both normal and backup computers for the safety related annunciators operating normally. Licensee informed the state/ local agencies and the NRC Resident Inspector. Notified R3DO (Kozak), NRR (Johnson), IRD (Wilson), FEMA (Sullivan), and DHS (Gomez). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0
41293 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2004-12-25 06:52 | 2004-12-25 08:55 | 2004-12-27 | UNIT 2 MANUALLY TRIPPED TO REMOVE FAILING CONDENSATE PUMP FROM SERVICE "Manual reactor trip due to condensate pump failure. All systems functioned as required post trip. The plant is currently stable in Mode 3." On 12/25/04 Unit 2 at St. Lucie experienced a high amperage reading on a condensate pump. Visual observation of the pump indicated blistering paint at the electrical connections. The condensate pump was taken out of service and Unit 2 was manually shut down. Decay heat is being removed via normal means to the condenser. The AFW system started as expected. All rods inserted correctly and all systems functioned as designed. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM ST. LUCIE (BASHWINER) TO NRC (HUFFMAN) AT 1239 EST ON 12/27/04 * * * The licensee called to provide some additional information concerning this event: 1) The manual trip of Unit 2 was due to the failure of the 2B condensate pump. 2) The condensate pump failure was a result of a failed termination of the "A" phase motor lead to the field cable. 3) The failure of the motor lead is considered a random event and does not have an generic implications. The licensee also noted that the reactor power had actually been reduced to 95% immediately prior to the manual trip. The NRC Resident Inspector and R2DO (Julian) have been notified. * * * UPDATE AND CLARIFICATION FROM BASHWINER TO CROUCH @1346 EST ON 12/27/04 * * * The following information was obtained from the licensee via facsimile: "This notification is an amended notification to the original notification of unit trip and RPS actuation due to failure of 2B condensate pump. "The amended notification includes an 8-hour notification non-emergency 10 CFR 50.72 (b)(3)(iv)(A) to identify Aux Feedwater Actuation automatically actuated post manual reactor trip on 12/25/04. "Specified System Actuation per 50.72 (b)(3)(iv)(B)(6) AFAS [Auxiliary Feedwater Actuation System]." The licensee notified the NRC Resident inspector. R2DO (Julian) notified of this update. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-12-25
41292 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2004-12-25 07:36 | 2004-12-25 08:50 | 2004-12-25 | UNIT 4 MANUALLY TRIPPED DUE TO LOWERING CONDENSER VACUUM "Manual reactor trip at 21.5" Hg and lowering. AFW initiated and operated as designed." On 12/25/04 Unit 4 at Turkey Point experienced a declining vacuum in the main condenser. When the condenser vacuum reached 21.5 Hg, manual trip criteria was reached and the plant was manually shut down. Decay heat is being removed via the Atmospheric Steam Dumps. There is no known primary to secondary tube leakage. The AFW system started as expected. All rods inserted correctly and all systems functioned as designed. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-12-25
41291 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-12-24 09:27 | 2004-12-24 13:49 | 2004-12-24 | LOSS OF RESPONSE CAPABILITY - EMERGENCY OFFSITE FACILITY "On 12/24/04 at 9:27 CST the Callaway Plant declared the Emergency Offsite Facility (EOF) Inoperable due to the ventilation system not operating in the Filtration Mode. This was discovered during normal watchstation rounds and followup evaluation of the capabilities of the ventilation system. The HVAC system was initially discovered to not be operating, subsequent evaluation indicated that the HVAC system would not operate with the unit in the Filtration Mode. "The Backup Emergency Offsite Facility (EOF) is still available to support the Emergency Plan." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-24
41290 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-12-23 23:54 | 2004-12-24 03:07 | 2004-12-24 | REACTOR SCRAM FOLLOWING DOWN SHIFT OF BOTH RECIRC PUMPS FROM FAST TO SLOW SPEED "At 2345 on 12/23/04 both reactor recirc pumps down shifted from fast to slow speed which resulted in reactor power reducing from 100% to 44%. At 2354 an automatic scram occurred from the activation of the Oscillation Power Range Monitor (OPRM) instrumentation. After the scram all safety systems responded as designed. Cause of the reactor recirc pump downshift is still under discovery." All rods fully inserted. No safety relief valves lifted during the transient. The licensee was in no major LCO at the time. Pressure control is via the steam bypass valves. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 44 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-12-24
41289 | 0 | FRAMATOME ANP |  |  |  | URANIUM FUEL FABRICATION | 2004-12-23 | 2004-12-23 20:03 | 2004-12-23 | EXTERNAL RADIATION LEVELS GREATER THAN LIMITS On a shipment received from Hope Creek, one of eight packages had a high radiation level on the bottom of the package. The radiation level was 236 millirem/hour. The packages contained nuclear service equipment. Packages were offloaded and placed in a secure area of the plant. The package has not been opened. Framatome has notified Hope Creek and will notify the shipper. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(2) |  |  |  | 0 | 2004-12-23
41288 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-23 14:10 | 2004-12-23 17:46 | 2004-12-23 | LOSS OF COMMUNICATIONS "Test results for the 12/23/04 weekly McGuire Nuclear Station silent siren test performed by the counties located in the McGuire EPZ indicated a failure of 50 out of the 67 sirens. This failure involved all of the sirens located in 2 of the 4 counties located in the EPZ who have the capability to activate these sirens. This failure occurred at 1410 on 12/23/04 and is believed to be due to 'Tropospheric Ducting (TD) radio frequency interference (RFI). A strong weather front was moving through the area at the time of the testing and is believed to be the cause of the TD RFI. Interference cleared at 1425 and subsequent retest by all four affected counties were completed with a 100% success rate with all siren test indications normal. Due to the short period of time of the unavailability and the prompt restoration of function, backup route alerting was not established. Long-term resolution of this RFI problem is being developed." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-23
41287 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-12-21 | 2004-12-23 17:05 | 2004-12-23 | AGREEMENT STATE REPORT "It was reported to Radiological Health Branch (RHB), Granada Hills that a Texas licensee, Gamma Surveys, a Division of Global Process Diagnostics, Inc. ( Gamma Surveys) , was conducting density level measurements using sealed sources under reciprocity at the Conoco Phillips Corporation refinery in Carson, CA, the evening of 12/21/04. Special form sealed sources containing radioactive material are employed for "gamma scanning," diagnostic evaluation, typically density or level measurements, of industrial processes or equipment. At about 1900 one such source, 287 mCi, Co-60, contained in a collimating device at the end of a stainless-steel, stranded cable, was being lowered down the outside of a large, cylindrical "distillation vessel, " designated FR-1 Flasher Column, 200 ft. high and 28 ft. in diameter. Stiffening rings which protrude about 18 inches externally encircle the vessel at various heights. As the source is being lowered down the side of the vessel, the operator located at the top of the vessel must manually "shake" the cable to get the source over the protruding stiffening rings. On this occasion, the collimating device with the Co-60 source broke at the cable during this shaking to get it over a stiffening ring 20 feet from the top. The source came to rest on the stiffening ring, in the " unshielded" condition, where it remained overnight. However, Gamma Surveys indicated that the area was cleared of personnel and cordoned off. Radiation surveys were taken at the ground level showing no appreciable dose rates, approximately 0.04 mR/hr. "The next day, 12/22/04, Gamma Surveys proposed a recovery plan to lower an operator in a man-basket down to the source to manually put the source back in its shielded condition ( normal practice) and then attach a replacement cable to the collimating device so that it may be reeled back into its shielded container at the top of the vessel for subsequent evaluation and repair of the damaged system. After consultation with RHB staff and the RSO for Gamma Surveys, this plan was effected. By about 5 PM, 12/22/04, the source recovery was completed without problems. An investigation has been initiated to follow-up." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-12-28
41286 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2004-12-23 06:14 | 2004-12-23 13:45 | 2004-12-23 | LOSS OF RESPONSE CAPABILITY "At 0614 hours on December 23, 2004, Davis-Besse activated station isolation procedures due to heavy snow and blowing snow. This is being reported as a loss of response capability under 10CFR 50.72 (b)(3)(xiii) due to the potential inability of local authorities to perform an evacuation. Minimum Emergency Response staffing is being maintained at the site. The state of Ohio and Ottawa and Lucas Counties have confirmed that they are currently capable of performing their emergency plan responsibilities." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-23
41285 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-12-22 12:15 | 2004-12-23 09:46 | 2004-12-23 | CONFIRMED POSITIVE FITNESS FOR DUTY TEST OF A LICENSED SUPERVISOR "The licensee reported a confirmed positive [random] fitness for duty test of a licensed supervisor. The individual has been removed from licensed duties and denied access to the facility. A work performance investigation has been completed. Worked performed by the individual has been verified to meet all standards and compliances." The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 26.73 |  |  |  | 0 | 2004-12-23
41284 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2004-12-22 11:00 | 2004-12-23 08:52 | 2004-12-23 | AGREEMENT STATE REPORT OF TROXLER GAUGE RUN OVER BY A TRUCK The Maryland Department of Environment Radiological Health Program reported that a Troxler moisture density gauge (Model 3430) was run over by a dump truck at a construction site in Prince Georges county (near the intersection of highway 410 and 295). The gauge contained an 8 milliCurie Cs-137 and 40 milliCurie Am-241/Be source. A representative of the Maryland Radiological Health Program responded to the scene and conducted a test for leakage and contamination. The gauge source was determined to be undamaged and in the shielded position. The gauge was packaged for transport and will be sent to the Troxler repair facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2004-12-28
41283 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-12-16 | 2004-12-22 18:22 | 2004-12-22 | AGREEMENT STATE REPORT - MISSING POLONIUM-210 SOURCES "During the semi-annual inventory of General License radioactive material at Barrick Goldstrike Mines it was found that two NRD 2U500 sources with original activity of 500 micro-curies of Polonium 210 per source were not located where they are supposed to be. These sources are used in analytical laboratory as static eliminators on balance scales. They were installed in April 2004 and were accounted for during the semi-annual inventory conducted in June 2004. An investigation is being conducted by the licensee in an attempt to locate the missing sources and to determine how they were lost. "Notification [from licensee] received in writing [letter dated 12/16/04] on December 22, 2004. "Consequences: These are generally licensed static eliminators with no public health impact anticipated." Nevada Event Report ID No. NV-04-010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-12-27
41282 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-09-30 | 2004-12-22 17:41 | 2004-12-22 | AGREEMENT STATE EVENT Pomona Valley Hospital reported in a December 9, 2004 letter to the State that seven I-125 seeds had been lost. The State received this letter December 14, 2004, & LA County received the letter December 21, 2004. Pomona reported that on October 14, 2004 while packaging excess I-125 seeds for return to the manufacturer, the dosimetrist discovered a shortage of seven seeds from a prostate implant done on Sept 30, 2004. They resurveyed the operating room & waste containers, but could not find the sources. They think the seeds were accidentally washed down the drain when the top part of the Mick Applicator cartridge was washed. They are obtaining additional information, such as the activity of the seeds. However, these seeds are normally about 0.3-0.4 mCi each, so seven seeds would be more than the one mCi I-125 that requires immediate reporting. They are reporting this as a loss that required immediate notification, but based on the information currently available, it appears unlikely that the loss could have resulted in exposure to persons in unrestricted areas. CA 5010 Number: 122204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-12-27
41281 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-12-22 15:00 | 2004-12-22 15:45 | 2004-12-22 | OFFSITE NOTIFICATION MADE TO PENNSYLVANIA EMERGENCY MANAGEMENT AGENCY (PEMA) An ambulance was called to the site because a plant employee, not in the power plant but in an onsite office building, complained of chest pains. The individual was taken by the ambulance to Berwick Hospital. PEMA was notified of this by the licensee. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-22
41280 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-22 13:07 | 2004-12-22 15:03 | 2004-12-22 | RPS ACTUATION DUE TO STEAM GENERATOR LOW LEVEL SIGNAL "Unit 2 reactor trip due to 2C steam generator LO-2 reactor protection signal. Auxiliary Feed Water actuated as expected. No additional malfunctions or unexpected plant response. Cause of LO-2 steam generator reactor protection signal under investigation. "This is a 4 hour notification of an RPS actuation per 10 CFR 50.72(b)(2)(iv)(B). The 8 hour notification of Auxiliary Feed Water system actuation per 10 CFR 50.72 (b)(3)(iv)(B) is being made under this same telephone call." The licensee notified the NRC Resident Inspector. All control rods fully inserted. Decay heat is being removed to the main condenser via the turbine by-pass valves. The electrical grid is stable. * * * UPDATE FROM F. EHRHARDT TO M. RIPLEY 15:55 ET 12/22/04 * * * The licensee has determined that the RPS and Auxiliary Feed Water actuations were the result of an actual low level in the 2C steam generator. The cause of the low level is under investigation. The NRC Resident Inspector was informed. Notified R3 DO (L. Kozak). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-12-22
41279 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-12-22 04:55 | 2004-12-22 13:53 | 2004-12-23 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via Email: "Licensee called to report one of their Troxler 3430 gauges (serial number 23691- 8 mCi Cs-137 / 40 mCi Am 241/Be) had been stolen along with the vehicle it was in. The gauge was reported to be locked in the enclosed SUV which was parked outside of the Riverside office this morning [12/22/04]. The gauge user came out to his vehicle at about 0445, shortly after transferring the gauge from the storage facility to his vehicle, and discovered the vehicle had been stolen. A report was filed with the Riverside Police Department (P304357039)." * * * UPDATE FROM R GREGER TO W GOTT AT 1419 ON 12/23/04 * * * "This gauge was recovered approximately noon yesterday [12/22/04], the same day it was stolen, when the stolen truck was recovered. The gauge was still in its transportation case in the truck and apparently had not been accessed." Notified NMSS (T Essig), R4DO (Spitzberg), TAS (J Foster) (email), and faxed to Mexico. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-12-27
41278 | 0 | SCI ENGINEERING |  |  |  |  | 2004-12-22 10:30 | 2004-12-22 13:20 | 2004-12-22 | DAMAGED HUMBOLDT MOISTURE DENSITY GAUGE. Representative of SCI Engineering located in St. Charles, MO reported the following incident: At approximately 1030 CST at a commercial job site in Warrenton, MO., a caterpillar truck ran over a Humboldt Model # 5100C moisture density gauge. The Humboldt case was cracked. The area around the damaged gauge has been roped off (50 feet from the gauge). The licensee did not know if the source rod had been broken off. R. M. Wester & Assoc. should be arriving shortly to take surveys and then take appropriate action based on their survey results. The gauge contains 11 millicuries of Cesium-137 and 40 millicuries of Am-241/Be. As far as the licensee knows there is no release. Warrenton is located about 30 miles West of St. Louis off of Interstate Highway 70. * * * Update at 1447 EST on 12/22/04 by William Guerdan to MacKinnon * * * R. M. Wester completed surveys and the results of the surveys are: no leaks and no contamination of the gauge. Both sources are intact and the area around the gauge is clean. The vehicle that ran over the gauge is also clean. R. M. Wester & Assoc. have taken possession of the gauge and they will take back to their St. Peter, Mo. office and perform a leak test of the gauge. Leak test of the gauge should be completed by the close of business today, 12/22/04. R3DO (L.Kozak) and NMSS (S. Wastler) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2004-12-22
41277 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2004-12-22 04:55 | 2004-12-22 09:30 | 2004-12-22 | REACTOR SCRAM AND ECCS INJECTION FOLLOWING OPENING OF TURBINE BYPASS VALVES "At approximately 04:55 on December 22, 2004, Unit 2 experienced a malfunction of Electro-Hydraulic Control (EHC) system resulting in opening of main turbine bypass valves and resultant loss of reactor pressure. The reactor automatically shutdown on RPS with the completion of a Group I isolation signal (Reactor pressure 850 prig and Reactor mode switch in RUN) resulting in a closure of the Main Steam Isolation Valves (MSIVs). Reactor level lowered to (ECCS) initiation set-point of -48 inches and High Pressure Coolant Injection (HPCI) system and Reactor Core Isolation Coolant (RCIC) system automatically initiated and restored level. When reactor level lowered below the 1 inch set-point, Group II and III Primary Containment Isolation System (PCIS) signals initiated. All Unit parameters are stable and RPS/PCIS/ECCS systems performed as designed. MSIVs remain closed. Reactor level and pressure are stable with HPCI and RCIC systems in control. Group I, II, and III isolations have been reset. The EHC malfunction is presently under investigation by Station Management." All systems functioned as required. The reactor water level is now at 23 inches and stable and the licensee is conducting a slow depressurization to Mode 4 to investigate the EHC system malfunction. The level transients experience during the scram would be expected with the closure of the MSIVs. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2004-12-22
41276 | 0 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2004-12-20 15:30 | 2004-12-21 15:48 | 2004-12-21 | SUSPECTED FAILED FUEL ASSEMBLIES "Arkansas Nuclear One (ANO) was verbally notified at 1530 CST on 12/20/04 by Framatone ANP, Inc. that a secondary review of preliminary results of fuel UT data evaluations resulted in conservative reclassifications of assemblies as now being suspect of containing a failed pin. This verbal notification was documented in subsequent correspondence received from Framatone on 12/21/04. Specifically, rods are now suspected of being failed in ANO Unit 2 fuel assemblies AKC401, AKC504, AKD001, AKF103, and AKF110, which were previously identified as clear of fuel failures based on re-scan data as determined in the preliminary report. The identified assemblies were loaded in Holtec Cask Numbers 10, 11, 12, and 13, during the November and December, 2004 cask loading campaign. "Appendix B, Section 2.1.1, of the Certificate of Compliance (CoC) Number 1014 for the Holtec HI-STORM 100 allows for the loading of "intact" fuel assemblies. Based on the new information from Framatone, the suspect fuel assemblies do not meet the requirements of "intact". Section 2.2 of the Holtec CoC requires a 24-hour Notification for the failure to meet fuel specifications or loading conditions." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW | [5 empty] | 0 | 2004-12-21
41275 | 0 | TEXAS A&M UNIVERSITY |  |  |  | 1000 KW TRIGA (CONVERSION) | 2004-12-21 12:45 | 2004-12-21 14:47 | 2004-12-21 | UNUSUAL EVENT DECLARED DUE TO A GRASS FIRE. A small grass fire started near Texas A&M Gamma Shack and headed away from the Gamma Shack and away from Texas A&M TRIGA Reactor Confinement building (located 100 yards away from the fire). The grass fire did not threaten the Gamma Shack or the Reactor Confinement building. Licensee entered an unusual event per Standard Operating Procedure Section 9, Procedure D.1 (major fire - major fire is a fire that cannot not be extinguished with one fire extinguisher). The reactor was scrammed at 1249 CST and all 5 rods fully inserted into the core (reactor was at 1000 KW when it was scrammed). Local Fire Department and local police responded. Fire Department extinguished the fire. No damage to the Gamma Shack. Gamma Shack is used to store cesium-137 and cobalt-60 calibration sources (sources were stored down in their respective wells). Licensee exited the Unusual Event at 1347 CST after the fire was extinguished by the local fire department. The TRIGA reactor will be restarted later this afternoon. No releases or injuries due to the fire. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | EMERGENCY DECLARED | [9 empty] | UNUSUAL EVENT | 4 | TX | NPR |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-12-21
41274 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-12-17 22:30 | 2004-12-21 12:10 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * CRITICALITY CONTROL Sequence of occurrences: On December 17, 2004, materials were transferred to a storage area without being transferred thru a particular device as required by the Standard Operating Procedure (SOP). This device prevents a more reactive/incorrect material type from being transferred. Prior to the addition of materials to the system, operations personnel verify that the correct materials are added to the system. The device prevents a more reactive/incorrect material type from entering the storage area. Remaining activities relied on: The remaining activities relied on to prevent potential accidents are available and reliable to perform their function. Operations personnel verified that the correct material type was added to the system. Also, the addition of a more reactive/incorrect material type was specifically evaluated and determined to be subcritical. Actions taken in response to the event: A root cause investigation was initiated as a result of the event. Transfers were suspended until compensatory measures can be put in place. Safety significance of event: The safety significance was low for the event given the very low likelihood of adding a more reactive/incorrect material type to the system. A more reactive/incorrect material type was not added to the system and the addition of a more reactive/incorrect material type was specifically evaluated and determined to be subcritical. Brief scenario of how a criticality could occur: In order for a criticality to occur, multiple occurrences of an excessive amount of a more reactive/incorrect material type would have to be added to the system; and, the material would have to be transferred without use of the particular device. What are the controls or control systems and the failures or deficiencies? The controls were limitations on material types input into the system and the use of a particular device when transferring materials to a storage area. Materials were transferred to the storage area without being transferred thru the particular device as required by the Standard Operating Procedure (SOP). The Nuclear Criticality Safety Evaluation (NCSE) for the area credited the device as a passive control device. The act of transferring the materials thru the device should have been credited as an administrative control since operations personnel have the ability to bypass the device if the procedure is not followed correctly. What are the corrective actions taken and when was each implemented? A root cause investigation was initiated on December 21, 2004 after discovery of the event. Material transfers were suspended on December 21, 2004 until compensatory measures can be implemented. Actual or potential health and safety consequences: There were no actual health and safety consequences to workers, the public, or the environment. There were also no personnel exposures to radiation, radioactive materials, or hazardous chemicals produced from licensed materials. The potential Nuclear Criticality Safety (NCS) consequences for workers were low given the actual materials involved and the very low likelihood of adding a more reactive/incorrect material type to the system. A more reactive/incorrect material type was not added to the system and the addition of a more reactive/incorrect material type was specifically evaluated and determined to be subcritical. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.74 APP. A |  |  |  | 0 | 2008-05-11
41273 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-11-17 | 2004-12-21 09:45 | 2004-12-21 | AGREEMENT STATE EQUIPMENT MALFUNCTION The following report was received via facsimile: "Central Testing Company had a camera malfunction on November 17, 2004. When the radiographer tried to crank out the source to make his first exposure he realized that the camera would not allow him to. He notified Central Testing of the problem. The camera was returned to SPEC and they replaced the locking mechanism on the camera. The camera is now functioning properly." LA Event Report ID - LA040013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-12-24
41272 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-11-29 | 2004-12-21 09:45 | 2004-12-21 | AGREEMENT STATE EQUIPMENT FAILURE The following report was received via facsimile: "A INC IR-100 camera with serial number 4475 with 55 Curies of IR-192 was involved in an equipment failure. The exposure device locked before the pigtail was completely retracted into the locked position. The camera was surveyed and found no high or unusual readings. The radiographer was unable to unlock the camera to pull the source completely back so the device was sent to SPEC. SPEC removed and cleaned the lock assembly. SPEC stated that the malfunction was probably due to sand and dirt in the locking mechanism. The written notification was received on December 10, 2004." LA Event Report ID- LA040015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-12-24
41271 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-10-25 14:00 | 2004-12-21 09:45 | 2004-12-21 | AGREEMENT STATE MEDICAL EVENT The following information was received via facsimile: "At 2:00PM on October 25, 2004, Saint Mary's Diagnostic Center reported that a Myoview dose was not showing the heart, but the sternum was viewable, indicating that the dose may have been MDP (bone agent). The syringe was retrieved from the customer and test confirmed the dose was MDP. The cause of the error was improper drug selection when filling the prescription. An in-service was conducted for the importance of detail when filling prescriptions and dispensing doses to correct the problem. The written notification was not received until December 13, 2004." LA Event Report ID - LA040014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-12-24
41270 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2004-12-17 12:00 | 2004-12-17 20:12 | 2004-12-17 | STANDBY EMERGENCY DIESEL GENERATOR DECLARED INOPERABLE. A work request identified a local trouble alarm on the standby generator (standby emergency diesel generator). Maintenance investigation of the trouble alarm was in progress when the control card for the standby generator failed (card controlled the frequency and voltage of the generator). Failure of this card disabled the generator from operating properly. The standby generator was declared inoperable and production personnel immediately stopped production of licensed material that was supported by the standby generator. At 1800 CST the standby generator was repaired and tested. The standby generator is considered fully operable at the time of this report. An investigation has been initiated to find why the control card failed. A 30 day reported will be released. NRC Region 2 (Jay Henson) was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2004-12-17
41269 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2004-12-17 11:09 | 2004-12-17 16:40 | 2005-01-05 | WATERLEG PUMP DISCHARGE CHECK VALVE IN HPCS SYSTEM FAILED TO OPEN "During the performance of the High Pressure Core Spray system (HPCS) quarterly pump and valve operability test, the waterleg pump discharge low pressure alarm was unable to be cleared. It was determined that the waterleg pump discharge check valve had failed to open to provide keepfill flow. "The HPCS system had been declared [inoperable at 0818 for a planned surveillance activity. At 1109, the low pressure alarm came in as expected, but was not able to be cleared. Subsequent mechanical agitation of the waterleg pump discharge check valve caused the valve to open and the low pressure condition to clear. "Tech Spec 3.5.1 is applicable. Entry time 0818 on 12/17/04. "Action is to restore HPCS to Operable within 14 days." NRC Resident Inspector was notified. * * * UPDATE ON 01/05/05 @1211 BY KEN MEADE TO CHAUNCEY GOULD * * * RETRACTION "An 8 hour notification was made on December 17, 2004, in accordance with 10CFR50.72(b)(3)(v)(C) and 10CFR50.72(b)(3)(v)(D). The report was made due to a potential loss of the High Pressure Core Spray (HPCS) system safety function as a result of the loss of keep-fill pressure." "The water-leg pump discharge check valve was determined to be the most likely cause of the loss of keep-fill pressure and was replaced. A preliminary investigation has determined that the water-leg pump discharge check valve had sufficient corrosion products (on the rising stem) to cause the valve disk to stick. With the check valve not able to fully open, the system low pressure alarm was activated." "The lowest system pressure, about 24 psig, was determined to be just below the alarm setpoint of 27 psig. The alarm setpoint includes a 10 psig margin between receipt of the alarm and the pressure at which the piping would start to void. The pressure, 24 psig, was equivalent to the static head provided by the Condensate Storage Tank (CST) to the HPCS system. This alignment is the method used to maintain the system filled when the water-leg pump is unavailable." "The 24 psig system pressure was adequate to maintain the system full. Since the system pressure was adequate and the HPCS system was maintained full, the safety function of the system was not adversely affected. Since the safety function was not affected, there is no reportable condition and Event Notification 41269 is retracted." The NRC Resident Inspector was notified. | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-12-17
41268 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2004-12-17 10:53 | 2004-12-17 14:54 | 2004-12-17 | OFFSITE NOTIFICATIONS MADE DUE TO SPILL OF APPROXIMATELY 1400 POUNDS OF SULFURIC ACID "On 12/17/2004 at approximately 10:53 MST, Palo Verde Nuclear Generating Station (PVNGS) notified the Department of Transportation/US. Coast Guard National Response Center of a sulfuric acid spill to the ground at the Water Reclamation Facility. The source of cooling water for PVNGS is treated sewage effluent. The effluent is conveyed to the site through approximately 35 miles of pipeline, and treated in the onsite water reclamation facility to meet plant water quality requirements. The acid spill has no impact to the radiological health and safety of the workers or the public. "The spill is estimated at 1400 pounds. The reportable quantity is 1000 pounds. The sulfuric acid is classified as a CERCLA Hazardous Substance and EPCRA Extremely Hazardous Substance. The release has been isolated and the apparent cause is a leak in an underground section of pipe. There were no injuries and no known or anticipated acute or chronic health risks. The National Response Center report number is 744571. The Arizona Department of Environmental Quality was also informed at 10:51 MST. "There was no impact to the three generating units from the spill at the Water Reclamation Facility which is located at a separate part of the Owner Controller Area. All 3 PVNGS Units are operating at approximately 100% in Mode 1. "The NRC Resident has been notified of the event and this notification." | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-17
41267 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-12-15 07:00 | 2004-12-15 14:00 | 2004-12-15 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM PUMP BEARING OIL PLUG FOUND LOOSE "The oil plug on the HPCI booster pump bearing was discovered to be loose at approximately 2100 [CST] on 12/14/2004. Upon discovery, the plug was re-tightened. The plug may or may not have fallen out had the HPCI system initiated. "HPCI is operable, but subsequent evaluation has determined this to be reportable because, at the time of discovery, HPCI operation could not be assured. Event investigation is on-going." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-12-15
41266 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-12-15 | 2004-12-15 13:55 | 2004-12-23 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via facsimile: "The driver/operator of a company vehicle transported the nuclear moisture density gauge to his residence in Cedar Hill, Texas, rather than return it to permanent storage. The gauge was missing when the operator prepared to leave his residence this morning [12/15/04]. The stolen gauge is an older Troxler Model 3401B that was re-built into a Model 3411B, Serial No. 12990 containing two Special Form, sealed sources: Cs-137, nominal 8 millicuries, Serial No. 501337, and Am-241/Be, nominal 40 millicuries, Serial No. 47-8300. The gauge was removed from the company truck by cutting the security chain sometime during the hours of darkness. Both the gauge and the transport container were taken. "The licensee is thinking of offering a reward and posting it both in the local newspaper and in advertising on a local news channel. Reward, if offered, will be no questions asked for return of the gauge." Texas Incident No: I-8193 * * * UPDATE FROM RAY JISHA TO W GOTT AT 1517 ON 12/23/04 * * * At 2300 on 12/21/04, Dallas Fire Department found the stolen gauge intact in a shopping cart in a shopping center parking lot. The gauge was returned to the Reed engineering group. Notified NMSS (T Essig), R4DO (Spitzberg), TAS (J Foster) (email), and faxed to Mexico. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-12-20
41265 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-12-15 10:06 | 2004-12-15 11:38 | 2004-12-15 | OFFSITE NOTIFICATION - MILITARY FLARE FOUND IN WATER "At 10:06 hours, Surry Power Station requested outside assistance from the Commonwealth of Virginia, State Police to remove an unknown device which was found floating in the water near the Surry Power Station Circulating Water Intake facility. The unknown device measures 2 inches in diameter and is approximately 14 inches long. It was marked with the following information: 'white phosphorus - contact military or law enforcement.' It is believed this is not an explosive device but a military flare. "In addition, notification was made to the Surry County Sheriff department at 10:10 hours. "The Virginia State Police in turn have notified the Navy EOD at Little Creek for assistance. This is being reported in accordance with 10 CFR50.72, (b) (2) (xi)." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-15
41264 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-11-22 | 2004-12-15 11:15 | 2004-12-15 | POTENTIAL NON-CONSERVATISM IN BUTTERFLY VALVE TORQUE PREDICTIONS UNDER COMPRESSIBLE FLOW CONDITIONS. Issue: By letter dated October 26, 2004, Electric Power Research Institute (EPRI) notified affected members in accordance with 10 CPR 21.21(b), of a non-conservatism in the [software product of] EPRI Motor Operated Valve Performance Prediction Methodology (PPM), Versions 1.0 through 3.2, to predict total required dynamic torque under compressible flow conditions for actuators for butterfly valves with single disc offset designs. As explained in the error notice, the non-conservatism could be as much as 45 percent. This non-conservatism could potentially jeopardize the design basis operation of associated safety related applications. Southern Nuclear Company (SNC) subsequently performed an engineering evaluation based on the EPRI notification as it related to Vogtle Electric Generating Plant (VEGP). The assessment did not identify any instances where the PPM had actually been used for such purposes at VEGP. Corrective Action: This issue has been entered into the SNC Corrective Action Program. SNC will evaluate the restrictions, adjustments, and recommendations regarding use of the EPRI MOV PPM, Versions 1.0 through 3.2, that were communicated in EPRI PPM Software Error Notice 2004-2. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 21.21 |  |  |  | 0 | 2004-12-15
41263 | 0 | PALISADES | 1 |  |  | [1] CE | 2004-11-04 09:17 | 2004-12-15 09:36 | 2004-12-15 | INVALID SYSTEM ACTUATION - SAFETY INJECTION On November 4, 2004, at 0917 hours EST, an inadvertent actuation of the left train of the safety injection system was initiated. The invalid actuation occurred during a system surveillance test, when a screwdriver that was being used to lift a lead slipped, causing a short circuit between the terminal being disconnected, and an energized terminal directly in front of it. As a result, all left train safety injection system equipment activated as expected for existing plant conditions. The resident inspector was notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-12-15
41262 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2004-12-14 15:00 | 2004-12-14 23:09 | 2004-12-15 | AGREEMENT STATE REPORT OF PORTABLE NUCLEAR GAUGE LOST DURING TRUCK CRASH A representative from the North Carolina Radiation Materials Branch called to report the loss of a Humboldt Portable Nuclear Gauge (Serial #254; Model 5001) due a severe truck crash on or near highway 52 close to Winston-Salem NC. The accident occurred around 15:00 on 12/14/04. The gauge is believe to have a 10 milliCurie Cs-137; 40 milliCurie Am-241,Be source. A truck carrying the gauge had an accident and rolled multiple times. It is believed that the gauge was ejected and probably in brush or woods in the vicinity of the crash site. A search was conducted until dark and will resume tomorrow (12/15/04) at around 0600. The licensee for the gauge is a company named Engineering Techtonics licensed by NC. The State of NC has contacted the RSO for the company. * * * UPDATE FROM L COX TO W GOTT AT 0814 ON 12/15/04 * * * The gauge was recovered at 0742 EST 12/15/04 and is in the possession of the licensee. The gauge was still in its transport case. The case was still locked, the gauge was still locked, and there was no visible damage to the gauge. Radiation surveys of the area are normal. The licensee plans to ship the gauge to the manufacturer for further inspection. Notified NMSS (J Hickey) and R1DO (K Jenison). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2004-12-17
41261 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2004-12-14 18:43 | 2004-12-14 23:22 | 2004-12-14 | OSWEGO COUNTY PROMPT NOTIFICATION SYSTEM OUT OF SERVICE FOR GREATER THAN ONE HOUR "Oswego County Prompt Notification System was out of service greater than 1 hour. Time out of service 12/14/03 at 1843 [EST]. Time returned to service 12/14/04 at 2305 [EST]." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-14
41260 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2004-12-14 18:43 | 2004-12-14 20:03 | 2004-12-14 | OSWEGO COUNTY PROMPT NOTIFICATION SYSTEM OUT OF SERVICE FOR GREATER THAN ONE HOUR "Notified by [deleted] of the Oswego County Warning Point that the tone alert system (prompt notification system) was out of service for more than one hour as of 18:43 on 12/14/04. This requires a notification to the NRC for a major loss of notification capability in accordance with 10CFR50.72. The notification [from the County Warning Point] occurred on 12/14/04 at 19:07 via the RECS line (Radiological Emergency Communications System). Route Alert has been verified available [as backup to the tone alert system] and actions to restore [the tone alert system] are in progress." The licensee states that the malfunction on the prompt notification system only rendered the tone alert radio system inoperable. The emergency sirens are not affected. The licensee has notified the NRC Resident Inspector and Oswego County authorities. The licensee has also notified the Fitzpatrick nuclear power plant. * * * UPDATE FROM NINE MILE POINT (D. MOORE) TO NRC (HUFFMAN) AT 23:06 EST ON 12/14/04 * * * The prompt notification tone alert system was restored to operable at 21:45 EST on 12/14/04. Fitzpatrick and Oswego county are informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-14
41259 | 0 | NATIONAL RESPONSE CENTER |  |  |  |  | 2004-12-14 15:45 | 2004-12-14 17:10 | 2004-12-14 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The National Response Center reported that the licensee reported to them that a moisture density gauge was run over by a bulldozer at a construction site in Springfield, MO and that the area had been isolated. In contacting the licensee, the RSO stated that the extent of damage to the gauge (Model 3440 Troxler 8 mCi Cs-137 and 40 mCi Am-241:Be) was as of yet unknown. The licensee plans on requesting local fire department Haz Mat Team assistance in performing surveys and will contact Troxler for information on recovering and returning the gauge. The licensee will be providing an update with additional details and status. * * * UPDATE FROM E. HODGE (RSO) TO M. RIPLEY 2013 EST, 12/14/04 * * * The licensee reported that the Springfield, MO Fire Department responded to the construction site, assisted in returning the damaged gauge to its transportation case, and performed a radiation survey of the gauge and the area where it was damaged. No area contamination or apparent source leakage was noted. The area has been cleared for access, and the gauge is being returned to the licensee's laboratory in Branson, MO where source leak testing will be performed prior to shipment to the manufacturer. Notified R3 DO (Lanksbury) and NMSS EO (Leach). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2004-12-14
41258 | -1 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2004-12-13 15:12 | 2004-12-14 14:55 | 2005-01-05 | CRITICALITY MONITORING DOSIMETERS NOT CONFIGURED CORRECTLY "On December 13, 2004, in preparations for new fuel receipt inspection activities, it was determined that the Electronic Dosimeters (Eds) that were previously used to meet criticality monitoring requirements of 10 CFR 70.24, were not configured correctly. Specifically, the dose rate alarm function of the Eds had been disabled. It is unknown at this time if the Eds had previously been used in this in-correct configuration during two previous new fuel receipt inspection activities. Based on the potential that the requirements of part 70.24 were not met, this event is being reported pursuant of part 70.50(b)(2), 'An event in which equipment is disabled or fails to function as designed.'" The Electronic Dosimeters were immediately re-configured correctly and new fuel receipt inspection activities will recommence. The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 01/05/05 AT 1039 EST BY ROBERT URRELL TAKEN BY MACKINNON * * * "The licensee performed an analysis that concluded that a monitoring system capable of detecting a criticality per 10 CFR 70.24 (a)(2) was in place during new fuel receipt. Specifically, the analysis demonstrated that the electronic dosimeters worn by the radiological workers involved adequately monitored for a criticality event." Therefore the licensee retracts the above event notification. R3DO (Sonia Burgess) & NMSS (Linda Gersey) notified. The NRC Resident Inspector was notified of this retraction by the licensee. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFETY EQUIPMENT FAILURE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 70.50(b)(2) |  |  |  | 0 | 2004-12-14
41257 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-12-14 11:45 | 2004-12-14 12:45 | 2004-12-14 | REACTOR MANUALLY TRIPPED DUE TO FIRE ON UNIT 3 HP TURBINE " U3 manually tripped (Shift Manager decision). Fire in U3 HP turbine near bearing housing (offsite assistance not required). All plant equipment functioned as designed." A fire broke out near the #2 bearing housing on Unit 3 HP turbine and lasted about 9 minutes in length. Exact character of fire was not available at time of reporting. No unusual vibration readings or visual indications were observed prior to fire. Onsite fire brigade personnel responded to the turbine area without assistance of offsite emergency personnel. Five minutes into the event Unit 3 reactor was manually tripped. Nine minutes into the event, shift supervisor declared the fire was out. Fire personnel indicated the fire was "easily" put out. Licensee is evaluating action to be taken. When Unit 3 reactor was manually tripped, all rods inserted fully. No primary or secondary power relief valves actuated. AFW activated as expected. Licensee chose to close the MSIV to slow down the cooldown rate. Presently, decay heat is being removed via the steam dump into the atmosphere. Fire did not affect operational ability of Unit 4 or cause instability on the electrical grid. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-12-14
41256 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-12-13 | 2004-12-13 17:36 | 2004-12-13 | CONTAINMENT PENETRATIONS NOT CLOSED DURING FUEL HANDLING OPERATIONS Event: "During refueling operations, containment penetrations providing direct access from the containment atmosphere to the outside atmosphere, closed by manual valves, was not maintained during fuel movement. - On 12/4/04 the five containment closure valves in question were verified closed during the initial establishment of conditions to perform refueling. - On 12/7/04 a steam drain valve checklist was performed in preparation for establishing vacuum which opened the five valves required to be closed by containment closure for fuel handling. - On 12/12/04 during performance of the 100 hour refueling containment closure checklist five containment closure valves were found in the OPEN position. These five valves are to be tagged closed during the time when refueling containment closure is required. - On 12/12/04 at approx 2100 a question as to if refueling containment closure was established on the steam generators was raised. It was investigated. And determined at 1245 on 12/13/04 that refueling containment closure was not established on the inside or outside of containment for the steam generators. " Initial Safety Significance: "This event is being reported as a condition which could have prevented the fulfillment of the safety function of structures that are needed to control the release of radioactive material. The requirements on containment penetration closure ensure that a release of fission product radioactivity within containment will be restricted from escaping to the environment. "Section 15.11.2.2 of the Oconee UFSAR addresses a Fuel Handling Accident inside Containment. The 1977 analysis concludes that the worst case release is appropriately within 10 CFR 100 limits but does not take any credit for containment. For this event the potential flow rate would be restricted due to the size of the open valves, the diameter of the piping from one open 3/4 inch valve in the Containment building to the four open 2 inch valves and one 3 inch valve in the Turbine Building, and the absence of a significant differential pressure. "Oconee wishes to note that a TS amendment incorporating Alternate Source Terms has been approved, but is currently awaiting implementation, which would only require refueling containment closure during movement of recently irradiated fuel (i.e. fuel moved within 72 hours of criticality). This event began on day 59 of the current refueling outage. Thus the potential for a significant release of radioactive material as a result of a postulated fuel handling accident during this time period was greatly reduced." Corrective Actions: "At the time of discovery fuel handling operations were no longer in effect. On 12/13/2004 at 1245 it was determined that refueling containment closure was not established, fuel handling operations were complete at 0358 on 12/13/2004." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode3: Refueling; FMode3: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-12-13
41255 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-12-10 16:15 | 2004-12-13 15:35 | 2004-12-23 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE On December 10, 2004, (Friday), the Licensee had dispatched operator [deleted], for a job with a Troxler 3440, Serial No. 33733, containing two sealed Special Form sources: 8.0 mCi (nominal) Cs-137, Serial No 750-9391, and 40.0 mCi (nominal) Am-241/Be, Serial No 47-22867. Upon completion of the job the operator was returning to the company office, he decided to stop by the Wal Mart store in Harris County, Texas. Upon returning to his company truck, Ford F150 fleetside, License Plate No. [deleted], he determined that the gauge was missing from the tiedown location. Looking into the bed of the truck he noted that the cable securing the gauge to the truck had been cut and was laying in the bottom of the truck bed near the tailgate, still locked into place. The operator reported the incident to his supervisor and was advised to report the incident to the Harris County Constable's Office - Precinct #4. While he was making the report, Case No 0412101909, the company R.S.O. reported the incident to the Texas Department of State Health Services (DSHS) on-call duty officer. Due to the R.S.O. being at home, he did not have the source Serial Numbers. The source serial numbers were reported to the Agency on Monday afternoon at 1:15 p.m. Licensee is considering offering a reward and announcing the loss to local media. Texas Incident No.: I-8191 * * * UPDATE FROM RAY JISHA TO W GOTT AT 1517 ON 12/23/04 * * * A technician from another company was offered the gauge for sale. The technician consulted his supervisor who told him to purchase the gauge. The gauge was determined to be the stolen gauge from Stork. The gauge was intact and was returned to Stork. An update will be provided to the local law enforcement. Notified NMSS (T Essig), R4DO (Spitzberg), TAS (J Foster) (email), and faxed to Mexico. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-12-16
41253 | 0 | GEORGE WASHINGTON UNIV. MED CTR |  |  |  |  | 2004-12-10 | 2004-12-13 08:49 | 2004-12-13 | POSSIBLE INCORRECT READING OF WIPE SAMPLES FROM A SCINTILLATION COUNTERS A radiation safety technologist on the licensee's staff recorded the liquid scintillation counting results of two package inspection wipe samples when the scintillation counter could not have produced this data. The technologist had no credible explanation for this, and has resigned to pursue a different career unrelated to radiation safety or radioactive material. In this circumstance, it is highly unlikely that any measurable dose was received by anyone, since the lab staff handles each radioactive vial with great care, and stores it safely after pickup from the RSO lab or delivery by the RSO staff. Also, not one package received from 1/1/01 on, was contaminated above DOT's safety limit, or even 2% of that limit. Any box that is contaminated is kept in radwaste. To prevent any recurrence of such undocumented records, the licensee has increased the direct supervision of the package opening procedure by the Radiation Safety Officer, who will also sign or initial the scintillation counter printout sheets of the wipe test results henceforward. The licensee believes that the technologist's resignation, and the RSO review of the wipe test printout sheets, will prevent any inaccurate or undocumented entries in these important NRC records in the future. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | DC | HOS | [5 empty] | 0 | 2004-12-13
41252 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-12-10 13:17 | 2004-12-10 17:34 | 2004-12-16 | REACTOR SCRAM DUE TO LOSS OF VITAL INSTRUMENT BUS "At 1317 [hrs CST] on December 10, 2004, an automatic actuation of the reactor protection system (RPS) occurred resulting in a reactor scram. The apparent cause of the event was loss of a vital instrument bus due to a fault in a nonsafety related vital inverter. This inverter provides power to selected control room instrumentation and controls. This resulted in the loss of feed water level control. "Reactor level is being maintained by the High Pressure Core Spray System. The feed water system is not available. Reactor pressure is being controlled through the main turbine steam bypass system to the condenser. The condenser is available and being used as the heat sink. The residual heat removal system was operated in suppression pool cooling mode to provide a means of rejecting water from the suppression pool [water input from High Pressure Core Spray System minimum flow line]. The plant is currently stable, and being maintained in hot shutdown. Systems responded as expected based on the initiating event. Reactor Core Isolation Cooling is not being used pending evaluation of a system alarm that is currently being investigated. Investigation of the initiating fault is being pursued in order to recover the vital bus and feed water level control." It has been preliminarily determined that the loss of instrument power resulted in the Main Feedwater regulating valve failing as-is and the "B" Reactor Recirculation Pump shifting down in speed. The reduction in reactor power with constant feed flow resulted in a high reactor vessel water level, producing a direct reactor scram signal at the High Level 8 setpoint. The licensee has notified the NRC Resident Inspector. * * * UPDATE FROM G. HUSTON TO M. RIPLEY AT 2025 EST 12/10/04 * * * "At 1657 CST [on 12/10/04], reactor level control was restored to the normal Feedwater and Condensate Systems. The High Pressure Core Spray System was restored to the normal standby lineup. Investigation into the cause of the reported RPS actuation continues. Investigation into the Reactor Core Isolation Cooling System alarms has resulted in declaring this system inoperable." The licensee will notify the NRC Resident Inspector. Notified R4 DO (L. Smith), NRR EO (M. Tschiltz) and IRD Manager (S. Frant) * * * UPDATE TO W GOTT AT 0016 EST ON 12/12/04 * * * "The final determination of the cause of the scram was determined to be due to the B recirc pump downshift and subsequent power to flow scram on APRM flux." The licensee will notify the NRC Resident Inspector. Notified R4DO (L Smith) * * * UPDATE TO JOHN MACKINNON FROM HUSTON AT 1332 EST ON 12/16/O4 * * * "The Reactor Core Isolation Cooling System was returned to available status at 0343 on 12/11/2004 and was restored to operable status at 2200 on 12/11/2004." The licensee notified the NRC Resident Inspector. Notified R4DO (Kriss Kennedy). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-12-10
41251 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-12-10 07:06 | 2004-12-10 15:35 | 2004-12-10 | COLORADO AGREEMENT STATE REPORT - LOST SOURCE FROM A TROXLER MOISTURE DENSITY GAUGE Colorado Department of Public Health and Environment received a report from a licensee, Ground Engineering Consultants, that they had possibly lost a Model 3440 Troxler Moisture Density Gauge containing an 8 milliCurie Am: Be source and an 8 milliCurie Cs-137 source. The technician transporting the gauge failed to properly secure the gauge in the back of his vehicle. When the technician discovered the gauge missing, he backtracked and found pieces of the gauge on Arapahoe Road in metropolitan Denver. At the time of discovery, the licensee determined that the sources were intact in the shielding base on radiation surveys. Upon further investigation, it was discovered that the Cs-137 source was missing. The licensee and technicians from the State of Colorado are currently searching the area for the lost source. The State of Colorado will provide an update on the results of the search. * * * UPDATE FROM STROUD TO CROUCH ON 12/10/04 @ 1744 HRS EST * * * Colorado Department of Public Health and Environment (CDPHE) informed the Operations Center that attempts to locate the missing source have proven unsuccessful. CDPHE Public Affairs has issued a press release to inform the public of the missing source and how to proceed if the source was found. CDPHE will provide an update to this event as necessary. Notified R4DO (Smith), NMSS EO (Giitter), HQPAO (Burnell and Brenner). R4PAO (Dricks) and DHS.. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-12-15
41250 | -1 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-09 02:04 | 2004-12-09 07:48 | 2004-12-14 | RPS ACTUATION WHILE SHUTDOWN DUE TO FAILED FUSE "During performance of Surveillance Testing on Intermediate Range Nuclear detector, a control power fuse blew. The plant was in Mode 3, and received a Reactor Trip signal which opened the Reactor Trip Breakers. All rods were on the bottom prior to the trip signal. Testing of Intermediate Range. Detectors has been suspended pending investigation. The plant remains in Mode 3." The licensee will inform the NRC resident inspector. * * * RETRACTION FROM L. PARKER TO M. RIPLEY 2013 EST, 12/14/04 * * * "This is a retraction of NRC Event # 41250 'RPS Actuation While Shutdown.' "On December 9, 2004, at 0204 PST, with Unit 2 in Mode 3 (Hot Standby), during testing of Intermediate Range Nuclear Detectors, a control power fuse blew, resulting in an actuation signal, and causing actuation of the Reactor Protection System (RPS). The reactor trip breakers opened, however, since all rods were fully inserted, no rod motion occurred. At 0448 PST, this event was reported as an eight hour non-emergency notification per 10 CFR 50.72 (b)(3) (iv)(A). "Based on a subsequent review of the event against NUREG-1022 Rev. 2, the actuation was confirmed to be INVALID due to a blown fuse and not an actuation of the intermediate range neutron flux detector. "Furthermore, with the unit in Mode 3 with all rods on the bottom, the RPS actuation had no effect, as the safety function had already been completed. "Therefore, the event is not reportable under 10 CFR 50.72 or 10 CFR 50.73, and the event notification is retracted." The licensee notified the NRC Resident Inspector. Notified R4 DO (G. Pick) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-12-09
41249 | 0 | HOSPITAL ALEJANDRO OTERO LOPEZ |  |  |  |  | 2004-12-08 | 2004-12-08 12:36 | 2004-12-23 | LOST BRACHYTHERAPY SEEDS Licensee notified NRC that they have been performing an inventory of their I-125 brachytherapy seeds from 8/26/03 until 12/07/04. In September, the licensee discovered 4 seeds were missing along with a lead container. The licensee conducted a thorough search and interviewed hospital personnel that had access or used the brachytherapy seeds for patient treatment. Using a calculated activity range of 0.224 - 0.368 millicuries per seed with a possible decay factor of 4 half lives would give an estimated total remaining activity of 0.09 millicuries. As a preventive measure against future losses the licensee has placed a locked container in the Nuclear Medicine Hot Lab, and the licensee has restricted access to the locked container to only the lab physicist. * * * UPDATE 1120 EST ON 12/9/04 FROM DR. FERRER TO S. SANDIN * * * The following information was submitted by the licensee via fax: "On the last quarter, we did an inventory for disposal of our Institution storage of brachytherapy seeds I-125 used for therapy in prostate carcinoma. "All seeds that were not used we gathered for disposal. Upon taking a visual inventory of all the seeds, 4 seeds were missing. "A thorough inventory of 32 seeds was done for the storage period, from August 26, 2003 to September 10, 2004. And immediately preventive measures were taken. "Prevention of reoccurrence - Immediately a locked container was placed in the storage area - Nuclear Medicine Hot Lab. The personnel of brachytherapy were required to place seeds inside the locked container. Our physicist will be the only authorized individual allowed to remove the un-used seeds. This will minimized the number of people that will handle the seeds. "We underwent a thorough search and interview the related personnel, from OR personnel, nurse staff, brachytherapy and nuclear medicine staff. This process took approximately 60 days. During the process we also found out that a lead container was missing and we re-started the searching process. "We calculated the dose range of 0.224 mCi / seed to 0.368 mCi / seed and with a possible decay factor of 4 half lives - for an approximately total activity of 0.09 mCi. "The incident was reported on December 08, 2004 ( 12:04 PM - EST)." Notified R1DO (Anderson) and NMSS (Essig) * * * UPDATE 0930 EST ON 12/23/04 FROM DR EDUARDO PASCUAL TO S.SANDIN * * * During remodeling, the four (4) missing I-125 seeds were found in a lead container inside the hot lab. Notified R1DO (Conte) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PR | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-12-08
41248 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-12-07 | 2004-12-07 18:54 | 2004-12-07 | AGREEMENT STATE REPORT FROM CALIFORNIA ON STOLEN TROXLER GAUGE "On December 7, 2004 at noon, the [Radiation Safety Officer] RSO contacted the [State of California Radiological Health Branch] Office to report a nuclear density gauge (Troxler model 3440, serial #15945) with a nominal 40 mCi Am:Be source (serial #47-11302) and a nominal 8 mCi Cs-137 source (serial #50-4969) had been stolen out of a locked construction trailer at Blossom Housing site off of Flynn Springs Road in the County of San Diego sometime between 11 am on Monday, December 6, 2004 and 7 am on December 7, 2004, when the theft was discovered. The gauge was last seen by the gauge user when he locked it up on Friday [12/03/04] at 3:30 pm in a trailer owned and used only by Geocon, Inc. A job foreman with another company reported he had noticed the trailer was locked shortly before he left the job site on Monday, December 6, 2004 at 11 am. Besides being inside the locked trailer, the case containing the gauge was locked with a padlock and the case was chained and locked to the trailer. The dead bolt lock on the trailer door had been drilled out and the gauge, gauge case, chain and lock, along with the door lock had been removed from the premises. A police report was filed with the San Diego County Sheriff's office (case #04084256A). "A reward will be offered for the return of the nuclear gauge. "The FBI was apparently informed of the theft by the San Diego Sheriff's office, as the licensee reported receiving a call from the FBI." The California report number for this event is 120704. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-12-10
41247 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-06 08:13 | 2004-12-06 14:25 | 2004-12-06 | RANDOM FITNESS FOR DUTY TEST A non-licensed supervisor tested positive for alcohol during a random drug and alcohol fitness for duty test. A review of the employee's work was performed and the individual's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.73 |  |  |  | 0 | 2004-12-06
41246 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-12-05 21:35 | 2004-12-06 00:17 | 2004-12-06 | AUTOMATIC TURBINE TRIP/REACTOR TRIP DUE TO MOISTURE SEPARATOR REHEATER (MSR) HIGH LEVEL TRIP SIGNAL. "Reactor Trip caused by Turbine trip. Turbine trip caused by a Moisture Separator Reheater 1B high level. Maintenance personnel were working in vicinity of level switches at time of trip. Root cause investigation in progress. All systems operated as designed on Reactor trip." Maintenance personnel working in the vicinity of Moisture Separator Reheater 1B were setting up radiography equipment when the MSR 1B high level trip was generated. All rods fully inserted. Both Motor Driven Auxiliary Feedwater pumps actuated as expected. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Catawba Unit 2 is operating at 100% power and the electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-12-06
41245 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-12-05 10:15 | 2004-12-05 15:54 | 2004-12-05 | REACTOR COOLANT LEAKAGE OUTSIDE OF CONTAINMEMT "This is an 8-hour notification being made to report exceeding the design basis for the reactor coolant leakage outside of containment. The event is being reported under paragraph (b)(3)(v) of 10CFR50.72. "On 12/05/04 at 1015 the control room was notified of leakage from a gasketed flange area on the 11 Residual Heat Removal Heat Exchanger. The leak rate has been conservatively quantified at 0.68 gpm, which is greater than the UFSAR limit of 2100 cc/hr (0.009 gpm) for ECCS leakage outside containment. "With leakage greater than the UFSAR allowed limits, GDC-19 limits for control room habitability cannot be assured. Actions are in progress to torque the flange bolts to reduce the leakage. "The licensee has notified the NRC Resident inspector of this event. "Salem Unit One is in Mode 4 with the Residual Heat Removal system in service removing reactor decay heat. No ECCS system actuations occurred. No one was injured as a result of the leak." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-12-05
41244 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-12-04 06:50 | 2004-12-05 07:42 | 2004-12-05 | HIGH PRESSURE TRANSMITTER FAILURE "At 0650 on 12-04-04, the Plant Shift Superintendent (PSS) was notified of a failure of the C-333A Autoclave 1 North High Cylinder Pressure System (HCPS). During a normal cylinder heating cycle an operator noted that the cylinder pressure, read on a recorder in the Operations Monitoring Room (OMR), unexpectedly fell from 70 to 0 psia. The PSS declared the system inoperable and TSR LCO 2.2.4.14B actions were implemented to place the autoclave in Mode 2 (autoclave open, non-applicable mode). The High Cylinder Pressure System (TRS 2.2.4.14) is designed to minimize the potential of a primary system failure (cylinder rupture) during a pressure increase event by automatically isolating the steam supply to the autoclave prior to reaching the Maximum Allowable Working Pressure (MAWP) of the cylinder. The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(1); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specific limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. "The NRC Resident Inspector has been notified of this event." PGDP Problem Report No. ATR-04-4819, PGDP Event Report No. PAD-2004-28. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-12-05
41243 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2004-12-04 04:17 | 2004-12-04 05:07 | 2004-12-04 | AUTOMATIC REACTOR SCRAM DUE TO AN AUTO VOLTAGE REGULATOR TRIP "On December 4, 2004 at 0417 [EST], the Reactor Scrammed as the result of an AVR [Automatic Voltage Regulator] trip. AVR Channels A and B were both operating at the time. The AVR trip caused a Main Generator trip which caused a Main Turbine trip. The Main Turbine trip causes a direct Reactor SCRAM on Turbine Valve position. RPS functioned properly and all rods inserted [fully]. MSIVs remain open with Reactor Level being maintained in the normal band of 173 to 214 inches. Reactor Pressure is being maintained with the Main Turbine Bypass valves. Isolations expected for Reactor Level 3 occurred and have been reset." Previous to the reactor scram, the AVR alarm was being monitored. All other safety systems functioned as required. Similar event occurred 09/04/04 (EN#41017). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 56 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-12-04
41242 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2004-12-03 22:30 | 2004-12-04 02:50 | 2004-12-07 | EARLY WARNING SIREN SYSTEM FAILURE "Actual failure was 100% (106 sirens) due to loss of power to station on-site/off-site radio repeaters. Failure occurred at 22:30 12-03-04. System was restored on temporary power at 23:06 12-03-04. State and local counties notified of failure at 23:26 12-03-04. System returned to normal power a 01:00 12-04-04. Station resident inspectors notified (J. Zeiler and M. King). System verified communications at 92% availability" | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-12-04
41241 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-12-03 15:55 | 2004-12-03 17:13 | 2004-12-03 | PRESS RELEASE REGARDING PLANT SHUTDOWN TO REPAIR SECONDARY STEAM PRESSURE INSTRUMENT LINE "At 1555 hours on 12/03/04, Indian Point Unit 2 commenced a plant shutdown at 200 MW/Hour. Plant shutdown will be completed within 5 to 6 hours. This shutdown is due to a crack on an unisolable secondary steam pressure instrument line on the H.P. [high pressure] turbine (PT-412B). The reactor is expected to remain critical at approximately 4% power on auxiliary feedwater. The plant is expected to be restarted within 24 hours following repair to the (3/4 inch) instrument line." The licensee noted that the crack was visually observed during rounds but was not yet blowing steam. The licensee plans to issue a press release. The licensee has notified the NRC Resident Inspector. | 53 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-03
41240 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-02 19:30 | 2004-12-02 21:39 | 2004-12-02 | PRESS RELEASE CONCERNING THE PLANNED SHUTDOWN OF THE SALEM UNITS DUE TO AN OIL SPILL "PSEG Nuclear announced, via a press release, that based on Delaware River conditions and the potential for oil from the Athos I oil tanker spill to reach the plant circulating and service water intake structures, it has been decided to take both units at the Salem Nuclear Generating Station offline. Hope Creek Generating Station is currently offline in a refueling outage. PSEG Nuclear currently plans to begin reducing power on both Salem Units on Friday December 3, 2004. PSEG Nuclear is continually monitoring river conditions and tracking the progress of the oil spill. Today, PSEG Nuclear began placing booms around the water intake structures at both Salem and Hope Creek nuclear generating stations. The boom is a barrier placed approximately 18 inches deep in the water and is relatively effective in controlling the spread of oil that is on top or close to the surface. However, since the oil spilled in the Delaware River was crude oil, it is expected that the heavier oil might be suspended in the river at varying depths, increasing the potential that oil could reach the plant intake structures. Since the potential exists to adversely impact the plant cooling systems if oil was entrained in the plant cooling water, both Salem 1 and 2 are going to be shutdown. "This report is being made due to the press release and the possibility that this release will generate public interest. No power reduction has been started at this time. At this time there has been no adverse impact noted on either Salem Unit 1 or 2 due to the oil spill. No injuries have resulted from this condition." The licensee will notify the NRC Resident Inspector, LAC Township, and representatives of the states of NJ and Delaware. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-02
41239 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-12-02 17:30 | 2004-12-02 20:10 | 2004-12-02 | TECHNICAL SPECIFICATION SHUTDOWN DUE TO LOSS OF THE DIVISION 2 125 VDC BATTERY CHARGER "On December 2, 2004, at 17:30 p.m. CST, River Bend Station commenced a plant shutdown required by Technical Specifications. This action was made necessary by the loss of the Division 2 safety-related 125 volt battery charger. The cause of the failure has not been determined. Actions are ongoing to restore the charger to service. "The pertinent Technical Specification action statement was entered at 1236 CST on 12/02/2004, and requires the plant to be in Mode 3 by 0036 CST on 12/03/2004 and Mode 4 by 0036 CST on 12/04/2004. This event is being report in accordance with 10CFR50.72(b)(2)(i)." The licensee added that the Division 1 electrical system is available and fully capable of supporting all reactor safety-related protective functions. The licensee is still trouble shooting the cause of the charger malfunction. The licensee has notified the NRC Senior Resident Inspector. | 77 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-12-02
41238 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-12-01 11:00 | 2004-12-02 16:00 | 2005-05-05 | PERSONNEL CONTAMINATION FROM SEALED SOURCE RUPTURE The following information was received via facsimile from the Texas Department of State Health Services Radiation Branch: "A contamination incident occurred at NSSI the morning of December 1, 2004. The incident involved the breaching of a sealed source as it was being removed from a device. The source involved was a 50 mCi Am-241Be source that was a part of a water salinity test device. "The NSR-N source is inside an 8 inches long aluminum tube of about 1.5 inches diameter and is held in the center of the tube by two concentric tubes inserted from each end of the primary tube and pinned in place. The aluminum tube also contains a neutron detector to measure the backscatter neutrons when measuring the water in the device. In preparation for disposal of the source, the neutron tube is removed and discarded and the aluminum tube holding the source is removed from the water device. "At the time of the incident, two persons were involved: The person operating the saw and the health physics monitor. A third person was in the machine shop area and about 4 feet away doing other work. "The source rupture was noted immediately and health physics support was called to the area. Health physics personnel conducted initial surveys and removed the three personnel from the area. The involved personnel were surveyed out of the area, suited in PPE [personal protected equipment] and were escorted to the hot lab shower area. Nose wipes were collected for assay and each of the personnel showered to remove contamination and surveyed. (Water from this shower is captured in a tank for recovery and treatment.) After completing the release surveys, the involved personnel were released and sent home. " The Texas Department of Health was contacted by the Headquarters Operations Center and added the following information. The source was apparently mispositioned in the tube and was cut by a band saw during the extraction process. Two of the individuals that were contaminated had nasal smears of 0.1 and 0.2 nanocuries. The third individual did not have any indication of contamination in the nasal smear. The contaminated individuals are scheduled to receive whole body counts. *** UPDATE FROM K. VERSER TO J. KNOKE AT 15:03 ON 3/25/05 *** The following was emailed as an update to Event 41238: "Decontamination efforts are performed and coordinated by specialized team and monitored each week by DSHS staff. To date some 50 pallets of materials and equipment has been removed from the warehouse. These items were surveyed by agency staff with using alpha scintillation and taking random swipes. More than 90% of these items have been decontaminated with the remainder being shipped for disposal at appropriate facilities. An order impounding all sources of the model involved in the event have been impounded in place since December 10, 2004. All 50mCi Am/Be sources have been properly inventoried and ten of them were allowed to be sent to another licensee for removal and inventory. These were individually identified in the presence of agency staff. No contamination has been found outside of the warehouse and airborne activity inside is far below permissible levels and is being monitored with continuous air monitors (CAM)s. All that remains is a small, heavily contaminated area and that should be cleaned up in a couple of weeks. NSSI will survey and perform final decontamination of the building after which, Agency staff will perform a thorough survey to verify decontamination is adequate." Notified R4DO (Pick) and NMSS (Gillen) * * * UPDATE FROM K. VERSER TO P. SNYDER AT 12:48 ON 5/5/05 * * * The State provided the following information via email: "Additional information received from Licensee, indicates two of the employees involved in the initial event, received Committed Effective Dose Equivalent exposures exceeding the annual limit. One employee, designated HP received 5.82 Rem and the other, designated Operator, received 10.7 Rem. In the letter transmitting this information, the licensee indicated it would be 3-4 weeks before the personnel monitoring supplier would have dose data from personnel monitors for the employees. Texas has requested additional information from the licensee regarding methodology used to determine CEDE for the employees. The licensee is also being required to submit the estimated Total Effective Dose Equivalent for each of the employees involved in the incident. "Texas is continuing its investigation of this incident and will send a final report when the investigation is complete." Notified R4DO (Pruett) and NMSS (Hickey) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-12-07
41237 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2004-12-01 15:00 | 2004-12-02 16:14 | 2004-12-02 | DAMAGED GAUGE On the morning of December 2, 2004, the Agency received telephone notification from BP Amoco Chemicals in Decatur, Alabama, that on December 1, 2004 at 3:00 pm, the shutter handle of one their fixed gauges containing radioactive material had broken. The company is licensed to possess and use the device under their Alabama Radioactive Material License No. 256. The shutter of the gauge, an Ohmart model SH-F2-45, serial number 4789GK containing 500 millicuries of Cesium-137 was in the closed position and when the licensee attempted to open the shutter, the shutter was found to be stuck and in the process of trying to open the shutter, the shutter handle broke. The handle is used to lock the shutter in place. Because the shutter was stuck in the closed position, no overexposure of personnel occurred. The device has been isolated and an Ohmart representative has been contacted to package the device and return the unit to Ohmart for repair. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2004-12-07
41236 | -1 | CHRIST HOSPITAL |  |  |  |  | 2004-12-01 11:00 | 2004-12-02 13:46 | 2004-12-02 | MEDICAL EVENT - GREATER THAN PERSCRIBED DOSE TO AN ORGAN At 1100 EST on 12/01/04 a patient was to receive 4.5 milliCuries Thallium - 201 (Tl-201) and then 3 millicuries Technitium-99M (Tc-99M). The first dose was administered but instead of administering the technetium, a second dose of Thallium was administered. The patient and physician were informed. No adverse affects are expected. The hospital is conducting an investigation as to the cause of the improper administration. * * * RETRACTION FROM L BELDCAMP TO W GOTT AT 1640 ON 12/02/04 * * * After consulting with NRC Region 1, the licensee determined that this is not a reportable event because Thallium is not an NRC regulated isotope. Notified R1DO (Trapp) and NMSS (Janosko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-12-02
41235 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-12-01 13:30 | 2004-12-01 15:27 | 2004-12-01 | OFFSITE NOTIFICATION DUE TO LUBE OIL SPILL ONSITE "At 1330 12/1/04, Catawba determined that the SC Department of Health and Environmental Control (SCDHEC) will be notified of a leak of used oil from the Used Lube Oil Storage Tank. This is an underground storage tank and the leak is not currently active because the system has been secured. An unknown quantity of oil has leaked into the immediately surrounding ground and is currently contained in the soil. Visual observations have not identified any oil leakage into the environment. The used oil is not classified as a hazardous material." The licensee will inform the States of North Carolina, South Carolina, the counties of York, Gaston and Mecklenburg and has informed the NRC resident inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-12-01
41234 | 0 | US NAVY |  |  |  |  | 2004-11-29 | 2004-12-01 11:55 | 2004-12-01 | LOST RADIOACTIVE MATERIAL GREATER THAN 10 TIMES THE LIMIT On 12/22/03, six hand held vapor tracer explosive detectors were sent from the Naval Surface Warfare Center (NSWC) in Crane, IN and received by the Fleet Industrial Supply Center (FISC) in Everett, WA in the beginning of Jan 04. The vapor tracers were then sent to the Todds Pacific Shipyard for delivery to the USS Shoup and the USS Ingraham. Todds Pacific Shipyard denies ever receiving the vapor tracers from FISC. The USS Shoup did receive 5 vapor tracers in Jan 04 and transferred 2 to Todds Pacific Shipyard since only 3 were needed. The remaining 2 vapor tracers were delivered to the USS Ingraham. The licensee is reporting the loss of one vapor tracer between FISC and Todds Pacific Shipyard. The vapor tracer contains a 8 millicurie Ni 63 source. A search for the lost vapor tracer was conducted at the NSWC, FISC, Todds Pacific Shipyard. Wanted posters were also posted to alert personnel of the missing device. On 11/22/04, NSWC exhausted all likely possibilities for finding the lost devise and declared the vapor tracer lost. Licensee contacted NRC Region 2 representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | WA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-12-01
41233 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-11-30 07:49 | 2004-11-30 15:03 | 2004-11-30 | FITNESS FOR DUTY REPORT A licensed employee was determined to be under the influence of alcohol during a random test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC resident operator. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2004-11-30
41232 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-11-30 08:50 | 2004-11-30 10:22 | 2005-01-11 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO DROPPED CONTROL ROD "During low power physics testing, Shutdown Bank B, rod E-11 dropped from 227 steps (ARO [all rods out] 230) to 135 steps. Technical Specification 3.0.3 was entered. Unit 3 Reactor was tripped at 0920 and stabilized in mode 3." The licensee will notify the NRC Resident Inspector. See also similar event EN # 41229 11/29/04. * * * UPDATE AT 1838 EST ON 1/11/05 FROM MICHAEL KOHL TO S. SANDIN * * * "The purpose of this update is to clarify that the reactor was not critical at the time of reactor trip. The dropped rod added sufficient negative reactivity to render the reactor subcritical prior to the manual reactor trip. "The cause of the dropped rod was an intermittent contact in a pin connector associated with rod E-11." The licensee will inform the NRC Resident Inspector. Notified R2DO (Landis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-11-30
41231 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-11-29 13:50 | 2004-11-29 16:22 | 2004-11-29 | OFFSITE NOTIFICATION DUE TO 50 GALLON HYDRAULIC OIL SPILL ONSITE "On 11/29/04, a leased mobile crane discharged approximately 50 gallons of hydraulic oil through a faulted line as maintenance contractors were performing pre-operational checks. The oil spill was confined to the compacted shell rock ground area beneath the crane. Immediate actions were taken to clean and remove the spilled oil using absorbent material and by removing saturated soil. The magnitude of the spill required off-site notification to the Florida Department of Environmental Protection (FDEP) and to the St. Lucie County Health Dept." The licensee will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-11-29
41230 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2001-09-25 17:00 | 2004-11-29 14:07 | 2004-11-29 | MEDICAL MISADMINISTRATION DUE TO IMPROPER POSITIONING OF IMPLANT DEVICE "Abstract - Female patient undergoing vaginal implant therapy on September 25, 2001. 'T-bomb' applicator loaded with 3 Cs-137 sources, each 19.73 mg RaEq [milligram Radium Equivalent] (49.92 mCi each, total activity 149.75 mCi). Implant performed 8:30 AM on 9/25/01. Status of implant placement made by nurse at 10:42 AM, and again at 2:10 PM. When physician checked patient at 5:00 PM on 9/25/01, implant was found outside of patient adjacent to her vaginal area. Physician did not report incident to Radiation Safety Officer, thus Licensee did not report incident to State. Estimate of total absorbed dose to the surface of the affected area was 7.55 Gy [Gray], this includes a dose of 0.74 Gy that comes from the normal implant itself. "Consequence of exposure - Tissue necrosis in affected area." The cause of the misadministration is still under investigation. A contributing factor was the failure to periodically check the implant placement. The patient was informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-12-02
41229 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-11-29 00:09 | 2004-11-29 01:36 | 2005-01-11 | TECHNICAL SPECIFICATIONS REQUIRED SHUTDOWN DUE TO DROPPED CONTROL ROD "Dropped rod E-11 in Shut Down Bank 'B' at 2334 on 11/28/04 while performing Low Power Physics Testing after refueling. Shutdown bank not fully withdrawn with dropped rod placed Unit 3 in Tech Spec Action Statement 3.0.3. RX trip breakers were opened at 0009 [11/29/04]. Unit 3 entered 3-EOP-E.O, Reactor Trip or Safety Injection, the unit was placed in Mode 3 and transitioned to 3-EOP-ES-0.1, Reactor Trip Response and then into 3-GOP-301. All plant equipment responded as required and the unit remains stable in mode 3 while the Rod Control failure is investigated." The licensee notified the NRC resident inspector. * * * UPDATE AT 1838 EST ON 1/11/05 FROM MICHAEL KOHL TO S. SANDIN * * * "The purpose of this update is to clarify that the reactor was not critical at the time of reactor trip. The dropped rod added sufficient negative reactivity to render the reactor subcritical prior to the manual reactor trip. "The cause of the dropped rod was an intermittent contact in a pin connector associated with rod E-11." The licensee will inform the NRC Resident Inspector. Notified R2DO (Landis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-11-29
41228 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-11-26 13:56 | 2004-11-26 15:59 | 2004-11-27 | OFFSITE NOTIFICATION OF CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION At 1356 on 11/26/04, after conducting an inspection of a chemical storage room, two personnel reported feeling ill (headache, stomachache) while reporting a condition of haze and fumes in the chemical storage room to the Control Room. The personnel were transported to an onsite facility, evaluated by the Haddam Neck EMT and transported to the local hospital. The licensee notified the Connecticut Department of Environmental Protection (DEP). The Haddam Neck Fire Department is awaiting the Connecticut DEP personnel arrival prior to entering the storage room for an assessment of the condition. The licensee is also preparing a Press Release for later today. The licensee is notifying NRC Region 1 personnel. * * * UPDATE FROM K SMITH TO KNOKE AT 1830 ON 11/26/04 * * * At 18:03 on 11/26/04, the licensee reported that the chemical fumes in the chemical storage room were determined to be from a toilet bowl cleaning solution. One of the chemicals that made up this cleaner was hydrochloric acid, which leeched out into some surrounding papers, and started to fume. The HAZMAT personnel from Connecticut DEP neutralized the chemical spill and licensee terminated the event at 17:30. PA Region 1 Duty Officer (Neil Sheehan) was contacted and informed of the update. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-11-26
41227 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-11-26 13:22 | 2004-11-26 14:29 | 2004-11-26 | RPS ACTUATION DUE TO TURBINE TRIP CAUSED BY LOSS OF STATOR COOLING WATER At 1322 EST on 11/26/04, the Indian Point Unit 2 Reactor automatically shutdown due to a turbine generator trip resulting from a loss of stator cooling water. All systems responded as expected, no PORV's opened. The reactor is currently shutdown with all control rods inserted. Temperature is being maintained in Mode 3 with the steam dumps. AFW was initiated and is being used to maintain SG levels. Investigation into the loss of stator cooling water is ongoing. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 92 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-11-26
41226 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-11-26 00:25 | 2004-11-26 03:22 | 2004-11-26 | SAFETY INJECTION ACCUMULATOR ISOLATION VALVES FOUND CLOSED AND THEIR BREAKERS LOCKED OFF. "During plant startup following a Refueling Outage, the Reactor Coolant System was pressurized greater than 1000 psig with the Safety Injection Accumulator Isolation Valves (SI-20A and SI-20B) closed and their breakers locked off. This is contrary to the plant Technical Specification requirement to open the valves and lock out their breakers prior to the Reactor Coolant System exceeding 1000 psig. The Safety Injection Accumulators are required to inject into the Reactor Coolant System to mitigate the consequences to a LOCA. This is conservatively being reported under 10CFR50.72(b)(3)(v)(D) as "Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." "At the time of discovery, Reactor Coolant System pressure was approximately 1090 psig and Reactor Coolant System temperature was approximately 440 deg. Fahrenheit. Approximately three minutes after the condition was discovered, the SI Accumulator Isolation Valves were opened and their power breakers were locked out." The STA discovered the problem while reviewing Technical Specification's and Plant Conditions. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Intermediate Shutdown; FMode1: Intermediate Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-11-26
41225 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2004-11-25 15:45 | 2004-11-25 16:50 | 2004-11-26 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM "On November 25, as of 1545 hours, the Station's Plant Process Computer (PPC) had been in a failed state for greater than eight hours. Previous to this, at 0745 hours, the PPC experienced an unexpected hardware failure. This computer feeds the Safety Parameter Display System (SPDS) for both Units. This failure is considered a major loss of emergency assessment capability. Troubleshooting and repairs are in progress." This failure affects the transmission of ERDS data and applicable emergency response personnel have been notified of the change in their reporting status if an emergency event is declared due to the loss of ERDS. The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY DARIN TO JEFF ROTTON AT 1205 EST ON 11/26/04 * * * At 1040 CST on 11/26/04, Information Technology personnel restored the Station's PPC to the point where the SPDS and ERDS are both fully functional for both units. The licensee notified the NRC Resident Inspector. | 85 | 85 | 0 | 85 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-11-25
41224 | -1 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2004-11-24 12:20 | 2004-11-24 20:01 | 2004-12-14 | ECCS LOOPS DECLARED INOPERABLE IN SUPPORT OF LONG TERM ACCIDENT MITIGATION "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On November 24, 2004, at approximately 12:20 Mountain Standard Time (MST), Palo Verde Nuclear Generating Station Unit 3 was operating at 0% power at approximately normal operating temperature and pressure when 3 of the 4 ECCS injection check valves were identified to be in a degraded condition. While performing normal torque verifications on the bonnet bolts for these check valves, it was identified that the graphoil seals were degraded in that the seal material had extruded past the retaining ring. Although there was no evidence of actual leakage associated with these valves, the long term integrity of the valves during post accident operation could not be assured. As a result, the Operators conservatively declared both trains of ECCS inoperable per LCO 3.5.3 and 3 of 4 Safety Injection Tanks inoperable per LCO 3.5.1, requiring entry into LCO 3.0.3. Operations also declared both RCS loops inoperable per LCO 3.4.5. A cooldown and depressurization of the RCS is in progress to Mode 5. "Unit 3 was preparing for Mode 2 entry following a refueling outage when the degraded check valve seals were identified. "Engineering continues to evaluate this condition. "There were no RPS/ESF actuations, and none were required. "There were no structures, systems or components that were inoperable at the start of event that contributed to the event. "This condition did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. This condition did not adversely affect the safe operation of the plant or health and safety of the public. "The NRC Resident Inspector has been notified of this condition and this ENS notification." * * * RETRACTION FROM DAN MARKS TO BILL HUFFMAN AT 14:52 EST ON 12/14/04 * * * "Engineering has determined that these RCS PIV's (Pressure Isolation Valves) were always capable of performing their safety function. "The extrusion of the graphite seal material for the check valves did not affect the capability of the RCS PIV check valves safety function and did not present a danger to the pressure boundary of the RCS. It was estimated that no more than about 5% of the graphite material was extruded. The loss of this small amount of packing material, did not challenge the integrity of the seal. This is based on industry experience and the results of Palo Verde tests. Also, the functionality of the SI check valves disc was not compromised since the internal disc to seat clearances achieved were within the range desired. Nevertheless, the seals for valves SIEV227, 237 & 247 were replaced while in Mode 5 to add additional margin to the joint design. "LCO 3.0.3 and the other impacted LCO entries (3.4.5, 3.5.1, 3.5.3) were conservative and were not required. "Therefore, this 10CFR50.72(b)(3)(v)(D) notification, ENS ID # 41224 of 11/24/2004, 20:01 ET, is retracted and no followup LER will be submitted for this event. "The NRC Resident Inspector has been notified of the retraction and this notification." R4DO (Pick) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-11-24
41223 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-11-23 13:25 | 2004-11-24 13:39 | 2004-11-24 | FAILURE OF UF6 RELEASE DETECTION SYSTEM DUE TO LOSS OF ELECTRICAL POWER "At 1325 [CST] on 11-23-04, the Plant Shift Superintendent (PSS) was notified of a failure of the C-310 High Voltage UF6 Release Detection System. The High Voltage UF6 detection system was disabled due to loss of power. Power was lost when a circuit breaker was tripped to de-energize an auxiliary substation that faulted and caused a fire. This High Voltage UF6 Release System is designed to activate alarms to alert operators in the event of a UF6 release. The PSS declared the system inoperable and TSR LCO 2.3.4.4.A actions were implemented to post a continuous smoke watch in the affected area. The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. "In addition, the loss of power caused the Low Voltage UF6 Detection System to isolate the C-310 withdrawal positions as designed. The substation fault and subsequent fire did not result in a release of radioactive material. "The Senior NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-11-24
41222 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-08-30 | 2004-11-24 09:34 | 2004-11-24 | TEXAS AGREEMENT STATE REPORT - ABANDONED WELL LOGGING SOURCE "On August 30, 2004, Schlumberger Technology Corporation was logging the Allar #1 well, operated by Famcor Oil, Inc., API # 42-407-30612, located in San Jacinto County, Texas. The well logging tool string became stuck during logging operations in the 11,998 foot well. The source string is below 3,319 feet of drill pipe stuck in sand-shale and sand-shale interfaces. Multiple attempts at recovery were conducted between 10/22/2004 and 10/29/2004. The Licensee notified the Agency of probable abandonment on 10/28/2004. The tool string contained two sealed radioactive well logging sources. The Licensee has not informed the Agency of the manufacturer of the sources. However, the 16 Curie Am-241/Be Neutron source, Model NSRF, Serial No G5053, is stuck and cemented in place at 8,326 feet [mine depth (MD)] , and the 1.7 Curie Cs-137 Density source, Model GSRJ, Serial No. Al 927, is stuck and cemented in place at 8,339 feet MD. Both sources were last leak tested on April 3, 2004, and were current on the date the sources became stuck in the well bore. Two-hundred feet of red oxide dyed cement is spotted on top of the stuck drill pipe from 4,984 feet to 4,750 feet. A used drill bit was placed as a deflection device at 4,750 feet. An additional 208 feet of cement was place on top of the drill bit, with the top of the cement located at 4,550 feet. The job was completed on October 30, 2004. A required plaque was ordered on November 19, 2004, and will be placed on the well head when received." Texas Incident No. I-8185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-11-29
41220 | 0 | XENOGEN BIOSCIENCES |  |  |  |  | 2004-11-23 | 2004-11-23 15:56 | 2004-11-23 | REPORT OF THEFT OR LOSS OF LICENSED MATERIAL The following information is excerpted from an email submitted by the licensee describing in detail the circumstances and conclusions concerning the missing rad material: . . II. DESCRIPTION OF LOSS OF LICENSED MATERIAL Radioisotope: Phosphorous-32 Chemical Form: Deoxycytidine 5'-Triphosphate [alpha-32P] Physical Form: Aqueous Solution Amount: Xenogen appears to be missing material from 2 separate vials as outlined below: 1. 150 µCi (15 µl of material at 10 µCi/µl) from a vial sent from GE HealthCare (formerly Amersham Biosciences) to Xenogen Biosciences on November 4, 2004. This vial was received at Xenogen Biosciences on Friday, November 5, 2004. The supplier's catalog number for the material is AA0005-1 mCi and the lot number for the material received is AC0445. The quantity requested was 1000 µCi (37 MBq) under Purchase Order No. 36348. This vial was designated internally within Xenogen Biosciences as vial No. 491. 2. 100 µCi (10 µl of material at 10 µCi/µl) from a vial sent from GE HealthCare (formerly Amersham Biosciences) to Xenogen Biosciences on November 11, 2004. This vial was received at Xenogen Biosciences on Friday, November 12, 2004. The supplier's catalog number for the material is AA0005-1 mCi and the lot number for the material received is AC0446. The quantity requested was 1000 µCi (37 MBq) under Purchase Order No. 36348. This vial was designated internally within Xenogen Biosciences as vial No. 492. Activity: 3000 Ci (111TBq)/mmole . . V. PROBABLE DISPOSITION OF THE LICENSED MATERIAL INVOLVED As of November 23, 2004, our current hypothesis is that the volume discrepancies (loss) of material in vials 491 and 492 were due to two conditions. First, the material appears to be evaporating in the vials. Second, any evaporated moisture that condensed on the lid of the vial is not being concentrated through centrifugation prior to removal of material by research associates. Evidence that supports this conclusion is listed below: 1. We have found that when this material is separated into 5 µl aliquots, placed in screw cap tubes with o-rings, and stored at 4°C for several days, the liquid evaporates and a dried and visible red pellet forms (concentrated dye). In addition, the volume of the pellet appears to be less than 1 µl (visual inspection). However, when the tube is centrifuged after storage, the full volume reappears in the bottom of the tube and can be confirmed by using a pipetting device. The experiment mentioned above was performed using one vial of 1000 µCi of Redivue[TM] [alpha-32] deoxycytidine 5'-Triphosphate (dCTP) from GE Healthcare that was received at Xenogen Biosciences on Friday, November 19, 2004. This vial was designated internally as vial 493. Volume discrepancies were first noticed on Monday, November 22, 2004. 2. The occurrence of volume discrepancies in vial 491 and 492, along with a similar incident involving vial 486, which was reported to the U.S NRC on October 13, 2004, coincides with the recent switch (July 2004) by Xenogen from [alpha -32P] dCTP supplied by PE Life Sciences to material supplied by GE Healthcare. Unlike the material supplied by PE Life Sciences, the material from GE Healthcare is not kept frozen during transit and storage, but rather at 4 degrees Celsius. Hence, the material is subject to evaporation and condensation at the top of the vial. 3. Upon arrival, we have found that these vials need to be centrifuged in order to collect the material at the bottom of the vial. If the vials are not centrifuged, we are unable to verify that the volume sent is correct. Because it was determined that the volume of both vials was correct prior to any removal of material, we have eliminated the possibility that an incorrect volume was shipped to our facility by GE Healthcare. 4. During the November 18 meeting with the researchers, one employee notified [the RSO] with the EHS department, that he failed to make a log entry for which he removed 50 µCi from vial 492. Other than this particular instance, there is no further evidence that a research associate or scientist removed material from vial 491 and 492 and failed to record this removal in the Isotope Inventory Log. Importantly, this discrepancy has been accounted for in the total amount of material missing from vial 492 as detailed in this report. 5. There appears to be no evidence that the volume discrepancies are due to inaccurate pipetting devices. Last month, all three P-20 pipetman that are used by users to remove radioactive material from P-32 vials were checked for accuracy by [the RSO]. Importantly, this evidence does not rule out the possibility a user had the pipettor accidentally set to a higher volume prior to removal or that the user did not use the pipetting device correctly. 6. There is no evidence that an employee or visitor intentionally stole licensed material from vial 491 and 492. Because of the number of employees (approximately 65) at the facility, employees, in general, know one another and work in an environment where they are likely to observe any unusual behavior. In addition, there are relatively few visitors come to the facility. Furthermore, the refrigerator that is used to store the vials of P-32 material is locked with a combination lock. Only users of radioactive material have access to this combination. Moreover, the room (Radioisotope Laboratory) is locked by a punch combination lock. Only users of radioactive material have access to this combination. All employees, whether they are a user or nonuser of radioactive material, receive training that explicitly informs them that it is a crime to remove radioactive material from the facility. 7. There is no evidence that a research associate or scientist recorded an inaccurate amount of material withdrawn from vial 491 or 492 because all employees who used vial 491 and 492 verified, through interviews conducted by [the RSO], that the amount of material indicated on the Isotope Inventory Log is the amount that was intended to be used. 8. There is no evidence that the loss was due to spillage because: a. There were no reports of a spillage by anyone who worked with the material; b. The amount of material presumed missing would have easily been detected through our weekly monitoring program by swipe analysis using a Liquid Scintillation Counter. Furthermore, 100 µCi would have easily been detected from monitoring conducted with a GM survey meter by other employees who used the Radioisotope Laboratory over the time in question. VI. EXPOSURE OF INDIVIDUALS TO RADIATION Following an intensive survey of the laboratory area and other sections of the building, there is no indication of radiation exposure to individuals due to the unaccounted material. VII. ACTIONS TAKEN TO RECOVER MATERIAL At this time, our current hypothesis is that the volume discrepancies with vials 491 and 492 are due to two conditions: 1) evaporation of material within the vial and 2) lack of centrifugation of vials prior to removal of material. Hence, it is not anticipated that the material will be found. More importantly, if it is true that the lost volume was due to evaporation, then radioactivity may not be actually missing. Again, the Radiation Safety Officer does not believe that any employee, or non-employee, unlawfully removed licensed material from vial 491 and 492. . . . . VIII. PROCEDURES OR MEASURES THAT WILL BE ADOPTED TO ENSURE AGAINST A RECURRENCE OF THE LOSS OR THEFT OF LICENSED MATERIAL. The company has implemented the following Standard Operating Procedures immediately to insure that 1) the material is not being removed by a user without correct documentation; 2) the material is not being taken or removed for purposes other than those purposes outlined in Materials License 29-30350-01; and 3) the proper amount of material is being used in each experiment. 1. Every commercial vial of P-32 entering the facility and which will be used for DNA/RNA labeling experiments will be separated into 5 µl aliquots (or the volume typically used for one reaction) at the time the package is surveyed and its contents verified. The aliquots will be consecutively numbered for tracking purposes. Aliquots will be stored in Eppendorf tubes and these tubes will be stored in shielded centrifuge test tube racks. The rack will be made of acrylic and will be a solid-block design with drilled wells. One rack will hold aliquots from only one source vial (e.g. Shielded rack reads "vial no. 500" . Eppendorf tubes within read 1-20). 2. A user should use the lowest consecutive numbered aliquot when removing an aliquot from the rack for use. 3. [The RSO] (or his designee) will check daily the supply of P-32 aliquots and determine if there are any inconsistencies with the number of aliquots versus the number used by researchers based on the Isotope Inventory Log (or equivalent). In addition, all pipetting devices used during the handling or dispensing of P-32 will be calibrated immediately by a commercial vendor, unless recently calibrated in the last 2 months. As mentioned earlier, [the RSO and another individual] met with all users of P-32 at the Cranbury Facility on November 18, 2004 to make them aware of the problem, to review pipetting techniques, and to train them on the new SOPs. HOO Note: See similar Event Report #41126. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-11-23
41219 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2004-11-23 10:02 | 2004-11-23 14:20 | 2004-11-23 | AUTOMATIC REACTOR SCRAM DUE TO TURBINE TRIP "At 1002 on 11/23/2004 with Unit 3 @ 100% power, a full reactor scram signal (RPS) was received due to a Turbine Trip. Unit 2 was also @ 100% power and was unaffected by the event. Reactor water level lowered to approximately -30 [inches] as expected and was recovered with normal feed water flow. All expected PCIS ISOLATIONS, Group 2 (RHR S/D Cooling), Group 3 (RWCU), Group 6 (Ventilation) & Group 8 (TIP) were received along with the auto start of CREVS and the three SBGT Trains. One PCIS Scram Discharge Volume Drain (85-37F) failed to close but the flowpath did isolate. The Unit remains Shutdown and an investigation is underway to determine the cause of the Turbine Trip and resulting Reactor Scram. "This event is reportable as a 4-hour & 8-hour Non-Emergency Notification along with a 60 day written Report in accordance with 10CFR50.72(b)(2)(iv)(B), 10CFR50.72(b)(3)(iv)(A) & 10CFR50.73(a)(2)(iv)(A) as 'Any event or condition that results in valid actuation of RPS & PCIS . . . " The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-11-23
41217 | -1 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2004-11-23 09:45 | 2004-11-23 12:07 | 2004-12-21 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO FAILURE OF SPDS The Safety Parameter Display System (SPDS) is not transmitting data to the Technical Support Center. The cause of the failure is unknown at the present time. The Computer Support Group is attempting to restore transmission capability. The licensee will inform the State of Arkansas as a courtesy and has informed the NRC Resident Inspector. * * * RETRACTION FROM R. SCHELDE TO J. MACKINNON 1523 ET 12/21/04 * * * "On 11/23/2004, at 1207 EST, Arkansas Nuclear One notified the NRC Operations Center that the Safety Parameter Display System (SPDS) was not transmitting data to the Technical Support Center (TSC) for a time period greater than 1 hour. Subsequent investigation determined that the SPDS was, in fact, operable during the time it was believed to be inoperable. Specifically, the Ramtek display was in service and updating normally during the time that SPDS was suspected to be inoperable. Although the SPDS consoles in the TSC were inoperable during this time, data was retrievable via the SPDS monitor touch screens." The licensee notified the NRC Resident Inspector. Notified R4 DO (B. Spitzberg) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-11-23
41216 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-11-22 17:30 | 2004-11-23 03:01 | 2004-11-23 | INADVERTENT ISOLATION OF THE REACTOR CORE ISOLATION COOLING SYSTEM "This ENS notification is made to report that on November 22, 2004 at 17:30 PST the Reactor Core Isolation Cooling (RCIC) system was rendered inoperable when its inboard steam supply containment isolation valve inadvertently closed during the performance of a routine surveillance procedure. The surveillance procedure was stopped and plant operators entered the appropriate Technical Specification Action Statements. The RCIC system was restored to its normal standby lineup and declared operable two hours and three minutes after the isolation. "NRC guidance in NUREG 1022 (Rev. 2), 'Event Reporting Guidelines,' and NRC Regulatory Issue Summary (RIS) 2001-14, 'Position on Reportability Requirements for Reactor Core Isolation Cooling System Failure,' indicates that RCIC failures are not reportable unless the RCIC system is specifically credited in the plant's Final Safety Analysis Report for mitigating the consequences of a Control Rod Drop Accident (CRDA). Columbia Generating Station has determined that the current licensing basis and docketed correspondence is not clear regarding RCIC credit for CRDA mitigation. Proposed FSAR changes were recently submitted by Energy Northwest to the NRC that would clarify that RCIC is not credited for CRDA mitigation. However, the NRC staff has not yet approved these proposed changes. Therefore, Columbia Generating Station has decided to conservatively report this event under 10 CFR 50.72(b)(3)(v)(D). A follow-up LER will be issued under 10 CFR 50.73(a)(2)(v)(D)." The licensed has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-11-23
41215 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-11-22 15:10 | 2004-11-22 18:27 | 2004-11-22 | PORTION OF PRIMARY INSTRUMENT LINES NOT ALIGNED TO SECONDARY CONTAINMENT "At 15:10 on 11/22/2004 Operations was notified of a condition that could have prevented the ability of Secondary Containment to control and monitor the release of radioactive material. "Three primary system instrument lines have approximately a 20-foot run in an area that is not normally aligned to Secondary Containment. This area has been realigned to Secondary Containment until an analysis of this design can be completed. This has been determined to be reportable under 10CFR50.72(b)(3)(v)(C). "Unit 1 is at 15% power with the main generator off line for unrelated repairs." The licensee notified the NRC Resident Inspector. | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-11-22
41214 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2004-10-07 20:55 | 2004-11-22 14:38 | 2004-11-22 | 60-DAY REPORT DUE TO AN INVALID ACTUATION OF ECCS AND EDGs DURING SURVEILLANCE ACTIVITIES "The purpose of this report is to provide a telephone notification under 10CFR50.73(a)(2)(iv)(A) for an invalid actuation of the Emergency Core Cooling Systems and the Emergency AC Electrical Power Systems. As allowed by 10CFR50.73(a)(1) this notification is being made via an ENS phone call. "On October 7, 2004, James A. Fitzpatrick (JAF) was in a refueling outage with the reactor cavity flooded and the spent fuel pool gates removed. At approximately 2055, during the performance of an instrument surveillance procedure (ISP-5-7) for 'Remote Shutdown Reactor Vessel Pressure Indicator Calibration' a pressure perturbation was introduced to the sensing lines while returning 02-3PI-60A to service. The pressure perturbation resulted in an invalid actuation of the Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generator (EDG) initiation logic. The initiation logic functioned as designed, 'A' and 'B' Core Spray Pumps and 'A', 'B', 'C', and 'D' RHR pumps started and injected into core, and EDGs 'A', 'B', 'C' and 'D' started but did not close to the emergency buses since there was no loss of off site power. "Operations personnel verified plant conditions, secured ECCS injection and secured the EDGs. The event was entered in the plant corrective action program via Condition Report CR-JAF-04-04457. Preliminary investigation has identified valve manipulation to restore pressure indicator 02-3PI-60A to service as the cause of a pressure perturbation in a shared sensing line, which caused the level transmitters sharing the same line to detect a low reactor water level condition. All systems that actuated operated per their design. "As a result of the injection, water overflowed to the skimmer surge tanks and into the reactor building drain system as designed, resulting in contamination of sections of the reactor building. No personnel contaminations or unexpected exposures occurred as a result. A recovery plan was developed and implemented to minimize the impact and to recover the affected plant areas. "In addition, signals were received for HPCI and RCIC initiation, SBGT initiation, Recirc pump trip and Alternate Rod Insertion (ARI). Due to outage activities, these systems were removed from service and protective tagged, and thus the systems did not respond. Although not required by 10 CFR 50.73 JAF will submit a voluntary LER to address this event in greater detail. "The NRC Sr. Resident Inspector was notified." The licensee also informed the State of New York. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-22
41213 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-11-20 11:40 | 2004-11-20 14:56 | 2004-11-20 | UNEXPECTED AUTOMATIC REACTOR TRIP DURING SURVEILLANCE TESTING WITH SI INJECTION "On 11/20/2004 at 1140 EST during the performance of 14421-2 'Solid State Protection System And Reactor Trip Breaker Train B Operability Test' an automatic Reactor Trip occurred and a Safety Injection occurred a short time thereafter. The Reactor Trip was caused by an error made in the performance of the 14421-2 procedure. The operator working with a peer checker mistakenly placed the 'A' train multiplexer test switch in the 'A + B' position instead of the 'B' train one. The 'B' train multiplexer test switch was still in the inhibit position. When the 'A' Train multiplexer switch went through the inhibit position, it caused the second general warning which tripped the reactor. The Safety Injection is believed to have been caused by a failure of the loop 2 Reactor Coolant Average Temperature which impacted the Steam Dump control system. The Steam Dumps did not close as expected during the Reactor Trip response and Pressurizer pressure lowered below the Safety Injection System setpoint and a Safety Injection was actuated. "All systems operated as expected during the Safety Injection and Reactor Trip. All the Control Rods fully inserted on the Reactor Trip. The Main Steam Lines were isolated by the operator due to the lower than expected decrease of the Reactor Coolant System Average Temperature. Both Motor Driven AFW pumps started as expected as did the Turbine Driven AFW pump. All ECCS pumps started as expected on the Safety Injection. The Containment Coolers all started in low speed on the Safety Injection as expected. Both Diesel Generators started on the Safety Injection actuation. The Containment Isolation systems isolated containment as expected. During the recovery from the Safety Injection pressurizer level did reach 100%, but the Pressurizer PORVs were not required to open to control Pressurizer pressure." Unit 2 is currently stable in mode 3 removing decay heat via the Atmospheric Steam Dumps. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2004-11-20
41212 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-11-19 16:22 | 2004-11-19 19:01 | 2004-11-19 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO A STEAM LEAK ON AN INSTRUMENT ISOLATION VALVE INSIDE CONTAINMENT The following information was obtained from the licensee via facsimile: "On November 9, 2004, NMC personnel performed a containment entry for Point Beach Nuclear Plant Unit 2 to locate and identify the source of a secondary steam leak. A leak was suspected due to increased pumping of the Unit 2 containment sump 'A'. A steam leak was identified on the body of valve 2MS-465D. This valve is an isolation valve for main steam flow transmitter 2FT-465. For containment isolation considerations, the main steam system is considered to be a closed system inside containment. The steam leak discovered on 2MS-465D cannot be isolated from containment penetration P-1, the main steam line penetration. Accordingly, we declared Technical Specification Condition 3.6.3.C not met. (This condition is applicable to penetration flow paths with only one containment isolation valve and a closed system) and entered TSAC [Technical Specification Action Condition] C.1. The required action for this condition is to isolate the affected penetration flow path with a completion time of 72 hours. In order to repair this valve wall leak, it will be necessary to shutdown and cooldown PBNP Unit 2. Accordingly, at 1622 CST we initiated a reactor shutdown of PBNP Unit 2. Since we anticipate that we would be unable to [meet] the allowed completion time for this TSAC, we have determined that this reactor shutdown is required by the Technical Specifications and is reportable in accordance with 10 CFR 50.72.(b)(2)(i)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-11-19
41211 | 0 | US ARMY |  |  |  |  | 2004-11-17 12:00 | 2004-11-19 15:08 | 2004-11-19 | UNPLANNED CONTAMINATION DUE TO A BROKEN M1A1 COLLIMATOR During an exercise conducted in May 2004 at Camp Shelby, MS an M1A1 Collimator, NSN 1240-00-332-1780, containing 10 Curies Tritium was removed from service, i.e., possibly broken, and double-bagged for storage. The device was subsequently transported from Camp Shelby to Shelbyville, TN and ultimately forwarded to the Combined Support Maintenance Shop of the TN National Guard located in Smyrna, TN for repair. A routine pre-maintenance wet swipe test indicated contamination levels as high as 619,094 disintegrations/min using a liquid scintillation meter. This corresponds to an activity of 0.27 microcuries. Two TN National Guard staff have submitted samples for bioassay. The results will be available on Monday, 11/22. Radiation surveys conducted at the Shelbyville and Smyrna, TN storage locations were negative. The device is currently double-bagged in the low level rad waste storage area of the Combined Support Maintenance Shop awaiting disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2004-11-19
41210 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2004-11-18 | 2004-11-19 12:36 | 2004-12-08 | AGREEMENT STATE REPORT INVOLVING A THERAPY MISADMINISTRATION The following information was provided via email from the Radioactive Materials Branch Director, Division of Radiological Health, MS State Dept. of Health: "On November 18, 2004, licensee's RSO notified Division of Radiological Health/MS State Dept. of Health, of a Iodine-125 therapy misadministration. The prescribed treatment was for 145 gray to the prostate gland; however, due to an error concerning the coordinates, the treatment area was partially missed and resulted in a greater than 10 gray treatment to the rectum. The isotope was Iodine -125, 88 seeds with average activity of .300 millicuries, total activity of 26.8 millicuries. The patient was notified of the error and agreed to have the treatment performed again with no problems occurring. The RSO notified DRH after discussing the error with the authorized user and agreeing on corrective actions to prevent reoccurrence. At the present time, this is all the information we have received. I will update as soon as possible." * * * UPDATE PROVIDED BY SMITH TO JEFF ROTTON AT 1738 EST ON 12/08/04 * * * The following update information was provided via email from MS State Department of Health: "The cause of the misadministration appears to be a misinterpretation to an ultrasound image which resulted in the needle being inserted in the wrong area. This caused a lower dose to be administered to the prostate gland greater than 20 % dose of the prescribed dose. Corrective actions will require a fIuoroscopticimage to verify the coordinates and confirm needle placement." Notified R1DO (Anderson) and NMSS EO (Giitter) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2004-11-24
41209 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2004-11-19 08:07 | 2004-11-19 12:25 | 2004-11-19 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP ON MAIN GENERATOR TRIP The following information was obtained from the licensee via facsimile: "1. SYSTEMS AFFECTED: Reactor trip, Aux feed water actuation. "2. ACTUATIONS AND THEIR INITIATING SIGNALS: Reactor trip - Loss of Load Turbine Trip, Aux Feed Water (AFW) - 21% [on the narrow range indication] in Steam Generators. "3. CAUSES: Reactor tripped due to an undetermined cause in the main generator end of the secondary plant. AFW started as expected on EFAS [Emergency Feedwater Actuation Signal] at 21% from a trip at 100%. "4. EFFECT OF EVENT ON PLANT: Plant is stable at 545F [and] 2250 [psi] hot standby conditions and will remain here until cause determination made as to cause of trip. "5. ACTIONS TAKEN OR PLANNED: Maintain hot standby conditions for post trip review. "CONTINUATION SHEET: 1) Remain in Mode 3 for cause determination post-trip review to provide actual mode required. 2) Estimate restart date pending cause determination and any repairs required. 3) All rods inserted, no primary or secondary reliefs lifted, electrical grid stable, all safety systems performed as expected, no effect on Unit 3. Electrical power supplied from offsite power." Decay heat removal is via steam dump to condenser. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-11-19
41208 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2004-11-19 10:03 | 2004-11-19 11:37 | 2004-11-19 | AGREEMENT STATE REPORT OF A STOLEN RADIOGRAPHY CAMERA The State of Kentucky Radiation Control Branch reported a stolen radiography camera AEA Model 880D with a 40 Curie Ir-192 source (Camera Serial#D1121; Source Model 424-9; Source Serial #16663-B). The Camera is owned and licensed to H&H X-Ray Services that has an office located in East Point, Kentucky. The camera was located in the radiographer's truck which was in the town of Corbin, Kentucky in preparation for a job. The radiographer lent the truck to the assistant radiographer on Wednesday night (11/17/04). The assistant radiographer did not return with the truck all day Thursday. Without any contact with the assistant radiographer since Wednesday night, the radiographer reported the truck and camera stolen this morning (11/19/04). The local police believe they saw the truck parked at a home in the Corbin area. The camera was locked in the truck but the assistant radiographer has a key to the camera so the current status is unknown. The State has notified NRC Region 1 (Sheri Minnick). In addition to the other Federal agencies notified above, contacted the National Response Center (Ms. Jones). * * * UPDATE 1420 EST ON 11/21/04 FROM CLYDE SLAUGHTER (RSO - H&H X-RAY SERVICES, INC.) TO S.SANDIN * * * The abandoned vehicle containing the radiography camera was recovered in Wise, VA after the assistant radiographer contacted another company employee providing information as to its location. Mr. Slaughter inspected the camera and found no indication of tampering. The camera is enroute to the East Point, KY office and will later be returned to the West Monroe, LA main facility. The licensee informed the KY Department of Homeland Security (Lt. Joe England). Notified R1DO(Dimitriadas), NMSS(Gillen), IRD(Wessman), TAS Duty Officer(Whitney), NSIR(Weber, Zimmerman), Chairman Diaz(Fragoyannis), EDO(Hsia), DHS(Evans), DOE(Smith), EPA(Baumgartner), USDA(Comeau), HHS(Miller), FEMA(Caldwell) and FBI. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2004-11-24
41207 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-11-18 16:30 | 2004-11-18 18:59 | 2004-11-18 | BOTH TRAINS OF RADIATION MONITORING AUTOMATIC ISOLATION FEATURES DISABLED DURING REFUELING OPERATIONS The following information was obtained from the licensee via facsimile: "At 1630 [hrs CST] the control room was performing head lift and pre-rod drive unlatching checkout and discovered R-12 (Containment Radiation Monitor) would not isolate reactor ventilation isolation. Investigation found that work on Engineered Safeguards Features pre-startup logic test had defeated both Train A and B automatic isolation signals to [Reactor Building Ventilation]. This test was started and signals defeated at 0803 [hrs.] and 0804 [hrs.]. Refueling evolutions, upper internals lift and rod latching were performed. Technical Specifications require auto-isolation capability for [Reactor Building Ventilation] during refueling ops. "Both R-12 and R-21 would respond to high radiation and manual isolation of Reactor Building Ventilation was still available. "Currently, refueling operations are stopped until auto-isolation of Reactor Building Ventilation is restored." The licensee has determined that no increased gaseous or particulate radiation levels existed while the auto-isolation features were defeated. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-11-18
41206 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2004-11-18 15:52 | 2004-11-18 18:15 | 2004-11-18 | AGREEMENT STATE REPORT - LEAD PAINT ANALYZER MISSING AND THEN RECOVERED An employee of the North Carolina Department of Environmental Health [NCDEH], Environmental Health Services reported to his supervisor on 11/18/04 that his Niton XRF lead paint analyzer device was missing or stolen from the trunk of his car. After retracing his travels going back to the last time he used the device on 11/09/04, it was discovered that he had inadvertently left the device in the parking lot of the Union County Health Department where he had earlier performed a lead investigation. An Union County Health Department employee had found the locked device on 11/09/04 in the parking lot and secured it in their building. The device will be retrieved by a NCDEH employee on 11/19/04. The device contains 14 milliCuries of Cadmium-109. The device serial number is U1399. The sealed source serial number is NR4649. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2004-11-23
41205 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-09-18 17:35 | 2004-11-18 10:52 | 2004-11-18 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "At 1735, 9/18/04, Callaway Control Room received an alarm on K0008 (Fire Protection Alarm and Control Workstation) for the Communication Corridor Lobby 2047 elevation. Initial investigation found significant smoke in the area of the Communication Corridor Elevator Room. During the investigation, a report was received in the Control Room that a small fire had occurred on the roof and had been extinguished. At 1743, the Callaway Fire Brigade was activated to investigate the source of the smoke. Upon arriving at the scene, no flames were observed and the Brigade began removing visquene [plastic] to facilitate observing additional areas within the room. At this time, small flames were observed and plant Emergency Alarm Level (EAL) 3E, 'Fire within the Protected Area boundary not extinguished within 15 minutes of verification' 15-minute time limit was entered. The fire was extinguished using a single powder type extinguisher and declared out at 1754. At 1910, an Operator reported that the Communication Corridor fire had reflashed. The Fire Brigade was reactivated and the fire was extinguished at 1919 using a single powder type extinguisher. After determining the temperature of the elevator room ceiling was 250 degrees F, water was applied to the ceiling from inside the room and from the roof above. After verification that the fire was extinguished, a continuous fire watch was established for both the affected room and roof area. Initial evaluation of the fire event concluded that the fire was extinguished within 15 minutes of discovery, and due to the size and location of the fire, the fire did not pose any safety significance. No safety systems had been impacted, Control Room habitability was not impacted, no safety system functions were required, and no safety functions were lost. Based upon this evaluation, it was decided that in accordance with guidance provided by EAL 3E, declaration of an Unusual Event was not required. Upon further review of the event associated with NRC Integrated Inspection Report 05000483/2004004, at 0925, 11/18/04, it was determined that a fire existed from the initial alarm at 1735 and lasted longer than 15 minutes. Because the initial fire lasted longer than 15 minutes, an Unusual Event should have been declared in accordance with plant Emergency Alarm Level 3E, 'Fire within the Protected Area boundary not extinguished within 15 minutes of verification.' Per guidance given in NUREG 1022, Revision 2, Section 3.1.1, 'Immediate Notifications', an ENS notification is being made within one hour of discovery of the event. No actual declaration of the emergency class will be made since the event has been concluded and the basis for the emergency no longer exists." The licensee will inform both state and local agencies and has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW | [5 empty] | 0 | 2004-11-18
41204 | 0 | PRAIRIE ISLAND |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-11-17 20:50 | 2004-11-17 23:46 | 2004-11-18 | TECHNICAL SPECIFICATION REQUIRED SHUT DOWN DUE TO BOTH TRAINS OF CONTAINMENT COOLING SYSTEM FAN COIL UNITS INOPERABLE "Initiation of a Unit 2 shutdown commenced at 2050 on November 17, 2004, as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 because both trains of containment cooling were declared inoperable as of 1615. Each train of Prairie Island's Containment Cooling System includes two containment fan coil units (CFCUs), for a total of four CFCUs. TS 3.6.5 requires two trains of containment cooling to be operable. Leakage from the 23 CFCU was determined to render one train of containment cooling inoperable at 1551. At 1615, the 22 CFCU (one of two CFCUs in the opposite train of containment cooling) was also determined to be leaking rendering the second train of containment cooling inoperable. Two CFCUs are fully capable of removing the design basis heat load; however, as the two remaining operable CFCUs are in different trains, neither train of containment cooling could be considered operable. Both inoperable CFCUs have been isolated to restore containment integrity and facilitate repairs. TS LCO 3.6.5 does not have a Condition for both containment cooling trains inoperable, therefore TS LCO 3.0.3 was entered." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-11-18
41203 | 0 | DEPARTMENT VETERANS AFFAIRS |  |  |  |  | 2004-11-17 12:00 | 2004-11-17 15:22 | 2004-11-17 | REMOVABLE RADIOACTIVE SURFACE CONTAMINATION Department of Veterans Affairs, National Health Physics Program report the following information: "I am calling to report packages that exceeded the limits for removable radioactive surface contamination. The packages were received between 0700 to 1200, November 17, 2004, by the permittee (VA Medical Center, Salem, Virginia) authorized under the master license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. "The basis for reporting the loss is under 10 CFR 20.1906(d)(1) in that the packages, ammo boxes being used to deliver radioactive materials, had approximately 28, 70, and 110 DPM per centimeter squared removable radioactive contamination on the outside. "The contamination was identified as Technetium-99M. "The Cardinal Health Nuclear Pharmacy Services delivered the packages. The status of whether the vendor delivery vehicle was exclusive use was not determined. "The permittee Radiation Safety Officer notified the vendor about the package and has taken appropriate health and safety steps to prevent any possible spread of contamination." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2004-11-17
41202 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-11-14 03:30 | 2004-11-16 12:55 | 2004-11-16 | STATE OF NEVADA AGREEMENT STATE REPORT: TROXLER MOISTURE DENSITY GAUGE STOLEN. On November 16, 2004, Krazan & Associates, Inc., California Radioactive Material License # 4247-10, reported to the Nevada Health Division Radiological Health Section that one of their Troxler Moisture Density Gauges (Model # 3430, serial # 21922) was stolen. The gauge was stolen on November 14, 2004, between 0330 am and 0700 am PST from a job site in Reno, Nevada. Reno, Nevada Police Department was notified. Cause & contributing factors: Security measures defeated. Troxler Moisture Density Gauge Model # 3430 contains 9 millicuries of cesium-137 and 44 millicuries of Am:Be. State of Nevada Event Report ID No. NV-04-009. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-11-19
41201 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-11-16 09:27 | 2004-11-16 10:16 | 2004-11-16 | UNUSUAL EVENT DUE TO FIRE IN RCA GREATER THAN 15 MINUTES Licensee reported hot work activities associated with demolition activities were completed at 1545 EST on 11/15/04. The fire watch had secured at 1615 on 11/15/04 after the hot work was completed for the day. At 0713 EST on 11/16/04 the smell of smoke was detected in the containment foyer. The hot work from the previous day had ignited wood cribbing and other demolition material in the containment building. The containment building was at a negative pressure and no release occurred. The fire was confirmed to be out at 0925. The fire was extinguished by the onsite fire brigade. There were no injuries to personnel. The Haddam Neck Fire Department responded to the scene, but was not required to extinguish the fire. The licensee notified the CT Department of Environmental Protection, the CT State Police, and will be contacting the NRC Region 1 Site representative. * * * UPDATE PROVIDED BY REID TO ROTTON AT 1116 ON 11/16/04 * * * Licensee reported that they exited the Unusual Event at 0927 - the same time that they declared the NOUE. The licensee will notify the NRC Region 1 Site Representative. Notified R1DO (Jenison), NMSS (Miller), IRD (Nieh), NRR (Reis ), DHS ( Haselton), FEMA (Sullivan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-11-16
41200 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-11-16 07:40 | 2004-11-16 10:10 | 2004-11-16 | " On 11/16/04, at approximately 0740 [CST] the KNP [Kewaunee Nuclear Plant] Shift Manager was informed that the Kewaunee/Point Beach External Communications Manager received a phone call from the Milwaukee Journal/Sentinel inquiring about an individual that was taken to the Two Rivers Aurora Hospital for a heat stress related condition. This was previously reported on 10/30/04 under Event #41163. The Communications Manager provided information to the individual from the Milwaukee Journal/Sentinel. " This notification is being made to inform the NRC of information provided to the media." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-11-16
41199 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-11-15 16:11 | 2004-11-15 21:22 | 2004-11-15 | RANDOM DRUG TEST: CONFIRMED POSITIVE On 11/08/04, a contractor on his last day of work at the site was given a random drug test. November 15, at 1611 EST a confirmed positive drug screen results for the contractor was received. The contractor worked at the Vogtle site from 07/15/04 through 11/08/04. He held unescorted access for inside the Protected are but as far as the licensee knows this person never entered any vital areas. No action taken since his badge was terminated on his last day of work which was 11/08/04. This information will be entered into the PAD system. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2004-11-15
41197 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-11-15 18:15 | 2004-11-15 19:00 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * WET OFFGAS (WOG) LINE CALCULATION WAS NOT PERFORMED. "Raffinate column WOG Vent [DELETED] is not sized appropriately to handle flow in the event of overflowing of [DELETED] combined with a loss of DI water pressure and a failure of DI water valve when transferring SNM material from sump columns ([DELETED] or [DELETED] using [DELETED]). This would prevent transferring SNM material into an unfavorable geometry tank. The WOG line is specified as IROFS [DELETED] and is listed as [DELETED] in the Recovery Deionized Water Nuclear Criticality Safety Evaluation Risk Indexing Supplement. Setpoint analysis was believed to be completed on all Recovery WOG lines. It was determined that this WOG line calculation was not performed at November 15, 2004. As such, IROFS [DELETED] was not reliable and available on [DELETED] and [DELETED] transfers to [DELETED] which occurred on October 28, November 2 and November 11, 2004. [DELETED] has been taken out of service. A follow-up memo to Operations will be provided to prevent the use of the pump and [DELETED]." Defense in-depth measures that were available are as follows: 1. Pumping operations did not overflow [DELETED]. 2. Deionized water line to [DELETED] was pressurized [DELETED]. 3. Administrative Control listed in the NCSE specified that the operator shut valve [DELETED] upon a loss of DI water pressure. This control is flowed down into the operating procedure. 4. Valve [DELETED] listed as a configuration controlled item was available to be closed upon a loss of pressure in the DI water line. 5. The WOG line was positioned lower than the DI water input line and listed as a configuration controlled item as such. There are no actual potential health and safety consequences to workers, the public or the environment due to defense in depth and configuration control items in place. In additional, overflow [DELETED] did not occur [DELETED]. What is the safety significance of the event? Not in compliance with 10CFR70.61. However criticality was not a concern due to defense-in-depth controls and configuration control equipment installed at the time. Brief scenario(s) of how criticality could occur: Transfer of SNM during a backflow scenario into DI water line and subsequent unfavorable geometry tankxx-001. What is the control(s) or control system(s) and the failure(s) or deficiencies? IROFS[DELETED] WOG line on [DELETED]. What are the corrective actions taken and when was each implemented? [DELETED] has been taken out of service on 11/15/04. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 05/11/08 BY P. SNYDER * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | ADDITIONAL REPORTING REQUIREMENTS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.74 APP. A |  |  |  | 0 | 2008-05-11
41196 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-11-11 17:00 | 2004-11-15 13:54 | 2004-11-15 | STATE OF NEVADA AGREEMENT STATE REPORT: STOLEN TROXLER MOISTURE DENSITY GAUGE. On November 11, 2004, at 1700 hours PST, a Troxler Model number 3440 (serial number 30887) moisture density gauge was stolen from a transport vehicle in Las Vegas, Nevada. Landmark Testing of Las Vegas, NV is the license holder of the gauge. The gauge contains 8 millicures of Cesium-137 and 40 millicuries of Americium-241:Be. Las Vegas Metro Police Department was notified of the stolen gauge. Cause and Contributing Factors: The security measures for securing the gauge to the transport vehicle were defeated. Corrective Actions: Licensee conducted additional training regarding transportation requirements. Nevada Event Report ID No. NV-04-008. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-11-18
41195 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-11-12 15:00 | 2004-11-12 15:20 | 2004-11-12 | UNUSUAL EVENT The licensee had carbon dioxide release in the turbine lube oil bay affecting normal access. There was no unplanned radioactive release. There was no indication of a fire. There were no personnel injuries or equipment damage. At 1540 11/12/04, the NRC made the decision to remain in the Normal Mode. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM J BITONTI TO W GOTT AT 1556 ON 11/12/04 * * * At 1540 Perry remains in an unusual event. The carbon dioxide release was not due to a fire. The licensee is ventilating the area to restore normal access. The fire department has been requested and is currently on site. There are no abnormal elevated radiation levels detected out the plant vents requiring consideration of offsite protective actions. Notified R3 (Lipa). * * * UPDATE AT 1651 ON 11/12/04 FROM J BITONTI TO M RIPLEY * * * At 1636 EST the licensee secured from the Unusual Event. Normal access has been restored to the area and a fire watch established until the fire suppression system is restored to normal. The licensee notified the NRC Resident Inspector. Notified R3DO (Ring), IRD (Wessman), NRR (Reis), NSIR (Weber), DHS (Reed), and FEMA (Biscoe) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-11-12
41194 | 0 | COOK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-11-12 11:18 | 2004-11-12 14:59 | 2004-11-12 | FITNESS FOR DUTY A non-licensed contract supervisor tested positive for drugs during a followup test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 63 | 0 | 100 | 63 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MI | POW |  | 26.73 |  |  |  | 0 | 2004-11-12
41193 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2004-09-28 01:00 | 2004-11-12 10:58 | 2004-11-12 | INVALID SPECIFIED SYSTEM ACTUATION DUE TO BUS VOLTAGE DIP DURING RECIRC MG START "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Unit 2 Primary Containment Isolation System (PCIS). "On 9/28/04, at approximately 0100 hours [EDT], a Group III Outboard PCIS isolation occurred during the start of the 2B Recirculation Motor / Generator (M/G) Set. The Recirculation M/G Set was being started to perform post-maintenance testing during the refueling outage subsequent to work involving the Recirculation M/G Set. This outboard isolation resulted in the closure of various valves associated with the Reactor Building / Refueling Floor Ventilation Systems and the start of the 'B' Standby Gas Treatment Fan. All equipment operated as designed. The isolation occurred as a result of a voltage dip on the 2B Reactor Protection System (RPS) / PCIS power supply while on its alternate feed at the time that the 2B Recirculation M/G Set was started. The 2B RPS / PCIS power supply was on the alternate feed in preparation for planned testing of the Emergency Diesel Generators (LOCA-LOOP testing). This RPS / PCIS power supply alternate feed was fed from the same startup transformer that the 2B Recirculation MG Set is fed from. The voltage dip from the start of the large Recirculation M/G Set was sufficient to cause the protective relaying on the 2B RPS /PCIS alternate feed power supply to shed the power supply from the 2B RPS / PCIS bus. Deenergization of the bus caused the Group III Outboard PCIS isolation. A ½ RPS scram signal was also generated. Just prior to the start of the 2B Recirculation M/G set, Operations personnel were briefed on the probability of the isolation and were prepared to take prompt action to reset the isolation and ½ Scram. The 2B RPS / PCIS power supply was returned to its normal power supply (i.e. 2B RPS M/G Set) and the Group III PCIS and the ½ Scram was promptly reset by 0105 hours. This issue has been entered into the Corrective Action Program (CR 257503). "The NRC Resident Inspector has been informed of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-12
41192 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2004-09-18 03:57 | 2004-11-12 10:58 | 2004-11-12 | INVALID SPECIFIED SYSTEM ACTUATION DUE TO OFF SITE POWER SOURCE FAST TRANSFER "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Units 2 and 3 Primary Containment Isolation Systems (PCIS). "On 9/18/04, at approximately 0357 hours [EDT], the 343SU offsite-power source tripped resulting in a fast transfer of expected 4 kV emergency busses to the alternate offsite power source. The fast transfer resulted in system isolations on both units due to the affect on the PCIS instrumentation logic. The system isolations are an expected occurrence for a fast transfer. The isolations involved various process lines such as Reactor Water Cleanup (RWCU) and Containment Atmospheric Control (CAC) / Containment Atmospheric Dilution (CAD). The Units 2 and 3 PCIS isolations were reset by approximately 0420 hours in accordance with procedures. All required isolation valves operated as designed. "The offsite power source (343SU) was lost as a result of a momentary deenergization of the 220-34 Newlinville Transmission Line to clear a ground fault. The fault was approximately 29 miles from the PBAPS site and was caused by a lightning strike to a transmission tower near the Newlinville substation. Field inspections of the 220-34 Transmission Lines and Towers were performed and it was identified that there was a flash mark on the tower insulator confirming the lightning strike. It was determined that the protective relaying for the 220-34 Newlinville Transmission Line operated as designed. The 343SU offsite power source was returned to service by approximately 2115 hours on 9/18/04. This issue has been entered into the site Corrective Action Program (CR 254392) for evaluation and implementation of further corrective actions. "The NRC Resident Inspector has been informed of this notification." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-12
41191 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-11-11 04:10 | 2004-11-11 09:36 | 2004-11-11 | EMERGENCY OFFSITE FACILITY DECLARED INOPERABLE DUE TO VENTILATION FAILURE "On 11/11/04 at 04:10 [CST] the Callaway Plant declared the Emergency Offsite Facility (EOF) Inoperable due to the ventilation system would not operate in the Filtration Mode. This was discovered during a normally scheduled preventive maintenance (PM) performed every two months. The Ventilation system was being placed in the Filtration Mode and a required damper (D-3) did not open. "The Backup Emergency Offsite Facility (EOF) is still available to support the Emergency Plan." The licensee in completing repairs on Damper D-3 prior to completing the ventilation system test. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-11-11
41190 | 0 | GREEN BAY PACKAGING COMPANY |  |  |  |  | 2004-11-11 06:30 | 2004-11-11 09:26 | 2004-11-11 | STUCK OPEN SHUTTER ON PAPER THICKNESS RADIATION GAUGE The licensee's RSO reported an OHMART OD-120 paper thickness measuring gauge malfunction that resulted in the gauge shutter remaining open. The gauge contains a 300 millicurie Krypton-85 source. The RSO has cordoned off the area around the gauge and contacted a repair contractor. The measured radiation level was 1.6 millirem per hour at a distance of 1 foot from the gauge. The RSO stated the gauge is routinely serviced and maintained. The last time the gauge experienced a problem with the shutter was May 13, 1999 (due to a screw jam). The RSO was uncertain as to the specific CFR reporting criteria but during discussions with the RSO he concluded that that 10 CFR 30.50(b)(2) is likely to be the applicable CFR reporting requirement. The RSO also planned to notify the Virginia Department of Health Radiological Health Program. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2004-11-11
41189 | -1 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-05-16 12:00 | 2004-11-10 14:21 | 2005-12-14 | AGREEMENT STATE REPORT FROM TEXAS: EQUIPMENT FAILURE THERAPY DEVICE AT HOSPITAL "On October 28, 2004, during a routine inspection of the Licensee, an Agency inspector discovered equipment discrepancies involving a Nucletron Selectron Model 106 Low Dose Rate (LDR) therapy device that indicated equipment failures which had not been reported to this Agency. A series of eight equipment failures interrupted patient treatments between May 16, 2004 and June 4, 2004. Radiation doses for the patients were not ascertained. No patient was injured. The Licensee failed to report the failures to this Agency within 24-hours and in writing within 7-days. The Licensee failed to forward these discrepancies to its Radiation Safety Committee (RSC) for resolution. The Licensee failed to prepare written directives for any patient treated on the LDR therapy device. No doses were listed in the treatment plan or in the patient's record. The Licensee indicated that corrective action would be cessation of operation of the LDR therapy device." Texas Incident No.: I-8179 * * * UPDATE FROM HANSON TO KNOKE AT 17:27 ON 12/13/05 * * * The State provided the following information via email: "A letter was sent to the licensee on 9/14/05 from Robert Free [State] informing the licensee that Condition 21 on their Texas License L01837, required them to report as follows: "The licensee shall cease treatment of patients when any safety related system of a LDR device is found inoperative, to include the source drive mechanisms treatment timing system, safety interlocks and radiation field alarms. The licensee shall report to the Deputy Director, Emergency Response and Incident Investigation, any malfunction that requires the termination of patient treatments for more than 24 hours and submit a written report of the incident and corrective actions within seven calendar days. "The response letter from the licensee dated 10/04/05, stated that there were actually 5 events affecting a total of patients; on 3 of these events there were 2 patients being treated simultaneously with the same LDR machine. In each case the attending physician was either on the premises or notified immediately. The physician either deemed the treatment received was sufficient or the treatments were rescheduled, some within 3 hours. It was discovered by the licensee that during the investigation of these events that severe thunderstorms preceded all LDR malfunctions. It was the conclusion that the LDR had functioned as designed by detecting the significant change in power & shut itself down. No misadministrations occurred. "The manufacturer replaced the column, interface board, printer mechanism and power supply. The LDR has not been used in the past 12 months. In August 2005 the decision was made to take the LDR machine out of service." Notified R4DO (Johnson) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2005-12-16
41188 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-11-10 09:00 | 2004-11-10 11:22 | 2004-11-10 | OFFSITE NOTIFICATION OF RELEASE OF UNKNOWN SUBSTANCE INTO DISCHARGE CANAL The licensee reported that approximately 1000 gallons of "rain water" was being discharged into the licensee's storm drain. The licensee's storm drains discharge into the discharge canal. The licensee noticed a frothing and foaming at the discharge canal as the rain water container was being pumped out. The pumping was discontinued and the licensee is attempting to analyze what substance was in the rain water that might be causing the foaming condition. At this time, the licensee has no information on what substance was discharged or the quantity of the substance that was discharged. The licensee was unable to state how much of the 1000 gallons of rain water had already been discharged. The licensee's discharge canal has a slick boom at the end of the canal but no other mechanism to prevent release of the unknown substance. The licensee notified the Coast Guard, the National Response Center, and the Connecticut Chemical Spill Unit. The licensee also planned to notify the NRC Regional Inspector for the site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-11-10
41187 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-11-09 23:39 | 2004-11-10 04:05 | 2004-11-10 | ACTUATION OF THE EMERGENCY AC ELECTRIC POWER SYSTEM "On November 9, 2004 at 2339 hours, an actuation of the emergency AC electrical power system occurred. While in a refueling outage a planned evolution was in progress to tie 480V Bus 3A to 480V Bus 6A using the tie breaker. A Bus under-voltage condition occurred when the Normal supply breaker was opened to bus 6A. When the normal supply breaker was opened, the tie breaker also opened causing a loss of power to bus 6A. With bus 6A deenergized an under-voltage signal was generated. 21 and 22 Emergency Diesel Generators automatically started and supplied bus sections 5A, 2A, and 3A. 480V Bus 6A remained deenergized because 23 Emergency Diesel Generator was out of service for planned maintenance. As a result, Residual Heat Removal cooling was lost for 5 minutes until power was restored and 21 Residual Heat Removal Pump was started. In addition, normal Spent Fuel Pool Cooling was lost for 39 minutes until 21 Spent Fuel Pool Pump was started. An activity is in progress to determine why the tie breaker opened when the normal supply breaker to Bus 6A was opened. "On November 10, 2004 at 0058 hours unit 2 was returned to its normal 480V lineup. "At the time of the event, refueling outage 16 was in progress on Unit 2 with all fuel assemblies installed in the core after refueling with the Reactor Vessel Head and Upper Internals removed. "This results in a condition that resulted in a valid actuation of the emergency AC electrical power systems which is reportable under 10 CFR 50.72(b)(3)(iv)(A)." The loss of the 21 spent fuel pool cooling pump resulted in a 3 degree rise in spent fuel pit temperature. The loss of the 21 RHR pump resulted in no appreciable increase in reactor coolant temperature. The licensee will be notifying the New York Public Service Commission of this incident and has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-11-10
41185 | 0 | POTLATCH CORPORATION |  |  |  |  | 2004-11-09 07:30 | 2004-11-10 00:33 | 2004-11-10 | ACCIDENTAL EXPOSURE FROM PAPER MILL RADIOACTIVE GAUGE The radiation safety officer (RSO) for the licensee reported that he discovered a mass thickness measuring gauge (NDC Model # 1107 containing an 80 milliCurie Am-241 sealed source) removed from its normal location with its shutter open and people working in the vicinity. The gauge is normally mounted on machinery and used to measure paper thickness for the licensee's pulp mill operations. The mill operation was apparently shut down at approximately 0730 a.m. on 11/09/04 for maintenance. Evidently, the radioactive gauge shutter was not closed when the operation was shut down. Furthermore, the gauge was then moved from its mounted location an placed near a walkway as part of the maintenance activities. The licensee's RSO discovered the condition at approximately 3:30 pm on 11/09/04 and immediately closed the shutter on the gauge. The RSO stated that the shutter on the gauge is opened and closed procedurally without any automatic safety closure when not in operation. The RSO also stated that there are numerous signs and postings that alert personnel to inform and involve the RSO when any activities take place that are in the vicinity of the gauge. The RSO stated that investigation is just beginning and that details or estimates on potential exposures have not yet been determined. The RSO noted that the maintenance crew in the area consisted of 10 (or less) people. Based on preliminary discussions, it is estimated that the maximum exposure to the gauge was less than 0.5 hours at a distance of 6 to 12 inches. None of the maintenance personnel were wearing dosimetry so all exposures will have to be estimated. The RSO reported this event without a specific CFR report category. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | ID | MAT | [5 empty] | 0 | 2004-11-10
41184 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2004-10-07 02:44 | 2004-11-09 15:45 | 2004-11-09 | INVALID SYSTEM ACTUATION "The purpose of this report is to provide a telephone notification under 10 CFR50.73(a)(2)(iv)(A) for invalid actuation of emergency AC electrical power systems. As allowed by 10 CFR50.73(a)(1), this telephone is being made in lieu of submitting a written LER. "On October 7, 2004, James A. FitzPatrick was in a refueling outage with the reactor cavity flooded and the spent fuel pool gates removed. At approximately 0244, Surveillance testing was in progress on the LOCA initiation logic for the 'A' and 'B' RHR Pumps. Technicians had aligned the initiation circuit for testing in accordance with Surveillance Test ST-2F. When the test signal was applied to the circuit the 'A' and 'B' RHR pumps started as expected. The 'A' and 'C' Emergency Diesel Generators (EDGs) unexpectedly auto started but did not load onto the emergency bus. There was no loss of power to the emergency busses and thus no need for the EDGs to load and power the emergency busses. Operations personnel verified plant conditions and secured the EDGs. "Condition Report CR-JAF-2004-04426 was initiated and an investigation into the unexpected start of the EDGs was conducted. It was determined that a relay malfunction in the test circuitry resulted in the failure to 'block' the EDG auto start signal. The EDGs started as designed based on the response to the unblocked test signal in the start logic. Since there was no actual need for the EDGs to start and the start was the result of a test signal that should have been blocked by the failed relay it was determined that the EDG start was based on an invalid signal. This notification is being made pursuant to 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(1)." The state of New York will be notified of this event by the licensee. The NRC Senior Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-09
41183 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-09-15 09:14 | 2004-11-09 13:52 | 2004-11-09 | INVALID ACTUATION OF CONTAINMENT VENT ISOLATION VALVE "The following information is provided as a 60 day telephone notification to NRC under 10 CFR 50.73(a)(1) in lieu of submitting a written LER to report a condition that resulted in an invalid actuation of the WBN [Watts Bar Nuclear] Train A Containment Vent Isolation signal. NUREG1022 Revision 2 identifies the Information that needs to be reported as discussed below. "(a) The specific train(s) and system(s) that were actuated. "On September 15, 2004, at 0914 EDT, a Train A Containment Vent Isolation (CVI) signal was received when the A Train Containment Purge Radiation Monitor momentarily spiked above the High Radiation Trip set-point. The B Train Containment Purge system was in operation at the time of the CVI signal and automatically shutdown as designed. "(b) Whether each train actuation was complete or partial. "The actuation was considered complete. The CVI signal for Train A automatically isolated the containment ventilation system as designed. The A Train Containment Purge Radiation Monitor was removed from service and considered inoperable due to no supporting indication of actual radiation by redundant radiation monitors or recorded trend data. "(c) Whether or not the system started and functioned successfully. "Train A Containment Vent Isolation signal automatically actuated and functioned successfully. The CVI signal was not in response to an actual plant condition. Maintenance on the Train A Containment Purge Radiation Monitor, revealed a loose connection in the detector cable. The radiation monitor was repaired and returned to service and the containment ventilation air cleanup unit was also returned to service." The NRC Resident Inspector was notified of this by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-09
41182 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-11-05 | 2004-11-09 11:10 | 2004-11-09 | AGREEMENT STATE REPORT DUE TO LOSS OF IODINE-125 CALIBRATION SEEDS "On Monday morning, 8 November 2004, the licensee reported a loss of 16 Iodine-125 calibration seeds, Amersham Model 6711, total of 193 mega Becquerel (5.216 milliCi), packaged in 2 vials. The vials contained 6 and 10 seeds respectively. Each vial was inside a lead shield. "The missing calibration seeds had been received on 5 November. They arrived in the same package as medical therapy seeds. The licensee's medical physicist removed the therapy seeds and placed them into secured storage assuming that the calibration and therapy seeds were all contained in the vials the physicist was removing. However, the calibration seeds were reported by the vendor to have been in additional vials associated with the foam packing material. The cardboard package and packing foam is routinely sent to the licensee's recycle center once the licensed material has been removed. This probably happened (including the calibration seeds) some time shortly after the physicist opened the package on 5 November. "On 8 November, the medical physicist realized the calibration seeds were not with the therapy seeds. The physicist reported their loss to the licensee's Radiation Safety Officer. Licensee staff surveyed the receipt area, the recycle center as well as the corridors connecting the areas and other likely spots. The lost material has not been located. The waste material had apparently been removed from the facility on 7 November. It is likely the lost material went to the landfill on 7 November. The licensee is still investigating. The licensee will send the department a formal report when their investigation is complete. "Contributing factor: The licensee failed to perform an acceptable package receipt survey. "Corrective actions: Will be addressed during the department's investigation. "No media contact: None yet. " WA Event Report # WA-04-066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-11-12
41181 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2004-09-28 13:02 | 2004-11-08 11:05 | 2004-11-08 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION FROM LOSS-OF-POWER TO REACTOR PROTECTION SYSTEM (RPS) BUS 2A "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of general containment isolation signals affecting more than one system. "On September 28, 2004, with Unit 2 operating at 100% thermal power, at 1302 hours CDT during maintenance work associated with protective relaying on 480 VAC Shutdown Board 2A, the board was inadvertently tripped. Associated RPS motor-generator (MG) set 2A lost power, and RPS bus 2A, which is powered from this MG set, was de-energized. Primary Containment Isolation System (PCIS) logic circuits powered from this bus lost power, and PCIS logic Groups 2, 3, 6, and 8 were actuated. "The following actuations/isolations occurred: "Group 2: Isolation of the Pressure Suppression Chamber head tank pumps [and] Drywell Floor and Equipment Drains "Group 3: Isolation of the reactor water cleanup system. "Group 6: Initiation of the Standby Gas Treatment System [and] Initiation of Control Room Emergency Ventilation [and] Isolation of the reactor zone and refuel zone normal ventilation system. "Group 8: This logic isolates the Traversing Incore Probes (TIP) if they are inserted. The TIPs were not inserted at the time of this event. "All equipment responded in accordance with the plant design. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for resolution. "The NRC senior resident inspector has been notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-08
41180 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2004-09-25 18:14 | 2004-11-08 11:05 | 2004-11-08 | INVALID PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION FROM LOSS-OF-POWER TO REACTOR PROTECTION SYSTEM (RPS) BUS 3B "This 60-day telephone notification is being made under reporting requirements specified by 10 CFR 50.73 (a)(2)(iv)(A) to describe an invalid actuation of general containment isolation signals affecting more than one system. " On September 25, 2004, with Unit 3 operating at 100% thermal power, at 1814 hours CDT, a voltage regulator problem occurred on RPS motor-generator (MG) set 3B. The associated RPS circuit protectors sensed an undervoltage condition and opened, thereby de-energizing RPS bus 3B. Primary Containment Isolation System (PCIS) logic circuits powered from this bus lost power, and PCIS logic Groups 2, 3, 6, and 8 were actuated. "The following actuations/isolations occurred: "Group 2: Isolation of the Pressure Suppression Chamber head tank pumps, Drywell Floor and Equipment Drains Isolation. "Group 3: Isolation of the reactor water clean-up system. "Group 6: Initiation of the Standby Gas Treatment System, Initiation of Control Room Emergency Ventilation, Isolation of the reactor zone and refuel zone normal ventilation systems. "Group 8: This logic isolates the Traversing Incore Probes (TIP) if they are inserted. The TIPs were not inserted at the time of this event. "All equipment responded in accordance with the plant design, with the exception that Unit 2 refuel zone ventilation system supply inboard isolation damper 2-DMP-064-0006 failed to close. The series damper, 2-DMP-064-0005, fully closed, therefore there would have been no impact to secondary containment integrity had this been an actual event. The damper's failure to close resulted from a sticking solenoid valve which was subsequently replaced. "There were no safety consequences or impacts on the health and safety of the public. The event was entered into TVA's corrective action program for resolution. " The NRC senior resident inspector has been notified." | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-11-08
41179 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2004-11-07 16:35 | 2004-11-07 21:04 | 2004-11-07 | "A" AUXILIARY FEEDWATER (AFW) PUMP MANUALLY STARTED DUE TO DECREASING STEAM GENERATOR WATER LEVEL. "The 'A' motor driven AFW pump was manually started in response to lowering Steam Generator (SG) level. The plant was in Mode 1 with reactor power at approximately 7%, preparing for startup of the turbine generator. Steam Generator Feedwater flow to the Steam Generators was being supplied by the main feedwater system through the main feedwater regulating bypass valves operating in automatic control. The operating crew observed a lowering trend in 'C' Steam Generator level. Upon reaching the lower end of the procedurally established normal control band (time=1633), the operating crew took the following actions in accordance with plant procedures: (1) the associated feedwater regulating bypass valve was taken to manual control to attempt restoration of normal SG level, (2) the 'A' motor driven AFW pump was manually started (time= 1635) to supply AFW to the SG and (3) reactor power lowered to reduce steam demand. These actions resulted in the restoration of 'C' SG level to normal. Normal operating SG level is 57%. Lo Lo Steam Generator Level Trip occurs at 25%. The lowest SG level observed during the evolution was approximately 43%. The cause of the irregular Feedwater control is currently being investigated. The plant is currently at approximately 2.5% power with all Steam Generator levels at normal operating levels. No automatic ESF Actuations occurred. The NRC Senior Resident was informed." | 2 | 0 | 0 | 7 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Startup | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-11-07
41177 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2004-11-07 06:20 | 2004-11-07 06:20 | 2004-11-29 | LOSS OF SPDS AND ERDS DUE TO PLANNED MAINTENANCE "The Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) were removed from service while implementing a planned modification to replace the Visual Annunciator System, Iso-Mimic display system, and support planned maintenance on uninterruptible power supplies. SPDS and ERDS will be returned to service in approximately 14 days. During this period, any out of service indication on the SPDS can be obtained by control board indications. The Emergency Notification System will remain operable. These conditions are reportable in accordance with 10 CFR 50.72(b)(3)(xiii). The NRC Resident inspector has been notified. The plant is in Mode 4, Reactor Coolant Temperature is 115 deg and Div. 1 RHR is in shutdown cooling." * * * UPDATE 1340 EST ON 11/29/04 FROM DAVID COSEO TO S.SANDIN * * * "This is an update to Event No. 41177. ERDS and SPDS have been restored following design change implementation on the Annunciator System. The plant remains in Mode 4 completing outage activities to support startup." The licensee will inform the NRC Resident Inspector. Notified R3DO (Ken O'Brien). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-11-07
41176 | 0 | SURRY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2004-11-06 02:52 | 2004-11-06 03:17 | 2004-11-06 | NOTICE OF UNUSUAL EVENT DUE TO A FIRE IN THE UNIT 1 TURBINE BASEMENT The licensee declared an Unusual Event due to an onsite fire not under control for greater than 10 minutes. The fire was in the "A" water box internal coating. Maintenance was performing cutting operations in the water box when the fire started. There were no injuries. The fire was fought by the onsite fire brigade and outside assistance was not required. The fire lasted 18 minutes. A reflash watch has been posted.. Unit 1 was shutdown at the time of the fire and shutdown cooling was not affected nor was any safety-related equipment. Unit 2, operating at 100% power, was not affected by the fire. The NRC did not change response mode due to this incident. The licensee will be notifying the NRC Resident Inspector. * * * UPDATE FROM MOSCOE TO SANDIN AT 0337 EST ON 11/06/04 * * * The Unusual Event was terminated by the licensee at 0321 hrs. EST. The termination criteria was the fire was out and a reflash watch stationed. Notified DHS, FEMA, IRD (Wessman), R2DO (Cahill) and NRR (Lyons). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-11-06
41175 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2004-11-05 09:11 | 2004-11-05 14:22 | 2004-11-05 | INADVERTENT LOSS OF "B" TRAIN SITE POWER DURING TESTING "At 09:11 a.m. CST on November 5, 2004, an inadvertent "B" Train Loss of Site Power occurred when the normal power supply breaker to the 1G 4160V bus opened during testing. The 1B Emergency Diesel Generator started and powered up the 1G 4160V Bus as required and the Loss of Site Power Sequencer started all "B" Train LOSP Loads as required. Abnormal Operating Procedures for the LOSP and Loss of Train "A" or "B" Train RHR were completed as required for the event. The "A" Train RHR pump was manually started to provide core cooling and circulation flow as required for Mode 6. Core alterations were in progress for reload which were suspended immediately upon the event "Systems which did not function as required: Upon the auto start signal for the 1B Motor Driven Auxiliary Feedwater Pump, the 4160V power supply breaker tripped open. The flag on the breaker indicated it was due to a time delay over current on one of the phases. Investigation into this problem is in progress." Spent Fuel Pool cooling was not lost because it was being powered from "A" Train. Site power was restored to "B" Train 4160V bus at 0959 CST. An event investigation is being performed by the licensee. The NRC Resident Inspector has been informed of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-11-05
41174 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2004-11-05 07:05 | 2004-11-05 12:03 | 2004-11-05 | EMERGNECY SIRENS FOUND INOPERABLE DUE TO EQUIPMENT MALFUNCTION "Indian Point Emergency Center (IPEC) Units 2 & 3 are making an eight-hour non-emergency notification in accordance with 10CFR50.72(b)(3)(xiii). On November 5, 2004, at 0705 hours during a routine daily check it was discovered that 88 of 156 sirens were in communication failure due to equipment malfunction that occurred at approximately 1950 hours on November 4, 2004. At 0710 hours on November 5, 2004 the equipment malfunction was corrected and all but one siren was returned to service. The one siren out of service is unrelated to the event." State and Local counties were notified of the loss of the emergency sirens. The licensee has been notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-11-05
41173 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-11-04 10:54 | 2004-11-04 11:11 | 2004-11-04 | UNUSUAL EVENT DECLARED DUE TO A TOXIC GAS RELEASE AFFECTING NORMAL OPERATIONS At 1054 EST on 11/04/04, the licensee declared an Unusual Event due to an acidic water spray in the Water Treatment Building affecting normal access. Licensee entered EAL MU-1, Toxic Gas detected within the Protected Area that impacts normal operations. There were two personnel in the building at the time of the leak, one Non-licensed operator and his supervisor. The Non-licensed operator was overcome by fumes and became nauseous and was taken to the onsite dispensary. The non-licensed operator was treated and taken to the local hospital. The supervisor did not seem to be affected, but he has been taken to the onsite dispensary for any necessary treatment. No unplanned release has occurred and no protective action recommendations are applicable at this time. The acidic water spray made contact with a 480 Vac panel in the building and has caused an electrical ground. Equipment in the building that may potentially affect plant operation if damaged are the clearwell pumps. The clearwell pumps supply seal water for the Main Circulating water pumps, and the non vital service water pumps. The licensee notified the NRC Resident Inspector and made all state and local government emergency management notifications. * * * Update on 11/04/04 at 1338 EST by Rick Wiles taken by MacKinnon * * * Atmospheric conditions in the area have been confirmed to be normal. Slippery conditions and acid hazard still exist on the floor. Licensee is still in an Unusual Event. NRC Resident Inspector has been notified of this update. R3DO (S. Burgess) notified. * * * Update on 11/04/04 at 1512 EST by Rick Wiles taken by MacKinnon * * * Unusual Event terminated at 1502 EST. Surrounding Counties and the State of Ohio were notified by the licensee that the Unusual Event was terminated. NRC Resident Inspector notified of the termination of the Unusual Event. R3DO (Sonia Burgess), NRR EO (Terry Reis), IRD (Dick Wessman), FEMA (Austin) and DHS (Lee) notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-11-04
41172 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-11-02 16:30 | 2004-11-02 17:35 | 2004-11-04 | AGREEMENT STATE REPORT INVOLVING IMPROPER RADIOACTIVE MATERIAL SHIPMENT On 11/02/04 the Florida Bureau of Radiation Control was notified by U.S. Customs at the Fort Lauderdale Executive Airport of the arrival of an aircraft from the Bahamas " . . . Carrying [a] RAM holder 650L (depleted uranium) with a depleted Ir-192 source [approximately 10 curies]. [The] pilot initially said that he had nothing to declare. Customs investigator's dosimeters alarmed when they examined the plane and they subsequently found the holder. The pilot then claimed that Bahamas Oil Refining Co. paid him to fly the holder to Ft. Lauderdale and send it to owner via FedEx. He then made a false statement that the holder was empty. The pilot was not hazmat qualified, was not licensed to handle RAM, and did not have proper shipping papers. The holder was impounded. [The] owner [AEA Technology, Inc.] provided proper shipping papers and had the item shipped back to them. This office [Florida Bureau of Radiation Control] will take no further action on this incident." Incident Number: FL04-150 A conference call was established between the NMSS EO (Tom Essig) and the FL BRC Representative (Jerry Eakins) to discuss the situation. During followup on 11/4/04, it was determined that the initial notification constituted an Agreement State Report. Notified RDO (David Silk), NMSS EO (Sandra Wastler) and TAS Duty Officer (Aaron Danis). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-11-09
41171 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-11-02 17:35 | 2004-11-03 13:11 | 2004-11-03 | 24 HOUR BULLETIN 91-01 REPORT INVOLVING TANKER TRUCK ASSAY RESULTS EXCEEDING VALUES "DESCRIPTION: 11/2/04 at 1735 the Plant Shift Superintendent (PSS) office was notified of a tanker truck located outside the east corner of the X-700 has uranium results at 322.0 +/- 64.4 PPM and 4.87 +/- 0.49 U-235 assay. No NCSA applies to this operation. This is reportable per NRCB 91-01 as a 24 hour event. "SAFETY SIGNIFICANCE: Very Low Safety Significance. The amount and concentration of uranium involved cannot possibly achieve a critical configuration. "POTENTIAL CRITICALITY: There are no criticality pathways involved due to the limited mass and concentration of material. "CONTROLLED PARAMETERS: No NCSA was established for this operation, so there are no control parameters. However, the limited mass and concentration of the solution does not warrant double contingency control because a criticality is not credible. "NUCLEAR CRITICALITY SAFETY CONTROLS: No NCSA controls were established for this operation. "CORRECTIVE ACTIONS: Upon discovery the PSS office directed entering an anomalous condition. Additional samples are being taken to confirm results. Contents of tanker are to be removed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2004-11-03
41170 | 0 | ABBEY METAL CORPORATION |  |  |  |  | 2004-06-16 | 2004-11-03 11:21 | 2004-11-05 | GENERAL LICENSED RADIOACTIVE MATERIAL LOST DURING BUILDING FIRE During a fire in the licensee building on 06/16/04, a XMET model 2000 instrument, serial # 500577 was destroyed completely. The instrument probe (serial # 501888) contained two sealed sources, 20 millicuries Cd-109 and 30 millicuries Am-241. The local fire department and Hazmat team responded to the scene. The licensee RSO conducted a survey and found no contamination or radiation. NRC Region 1 office was notified on 6/30/04. * * * UPDATE PROVIDED BY LAURA ZIEGLER TO JEFF ROTTON ON 11/05/04 AT 1115 EST * * * Oxford Instruments voluntarily made the report for Abbey Metal Corporation on 11/03/04 after discussions with that company. The Event Notification has been updated to reflect that the Reporting Organization should be Abbey Metal Corporation, the company that owned the device destroyed in the fire under a general license. The device was originally sold to Abbey Metal Corporation by Metorex, Inc. Oxford Instruments recently purchased Metorex, Inc and was attempting to close out all previously existing open items. Notified R1DO (Silk) and NMSS EO ( Sandra Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-11-03
41169 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-11-03 03:10 | 2004-11-03 05:15 | 2004-11-04 | OFFSITE MEDICAL TREATMENT FOR INJURED CONTAMINATED WORKER "On 11/03/04 at approximately 0256 hrs, a refueling bridge operator was injured when his gloved right hand became entangled in the refuel bridge mast during the performance of core alterations. The moving mast sections crushed two of the operator's fingers, and the bridge was immediately shutdown by the spotter. An irradiated fuel bundle had just been removed from the reactor core at the time of the incident, and was being raised to the full up position for transport to the spent fuel pool. The refueling SRO directed the bridge power be turned on to lower the mast slightly and release the operator's hand. The bridge operator was escorted off of the refuel floor by radiation protection and site medical personnel. A bridge relief crew completed the movement of the irradiated fuel bundle to its target location in the spent fuel pool, and core alterations were stopped pending completion of an accident investigation. "The injured bridge operator was contaminated with approximately 5000 counts per minute on the injured hand, and was transported offsite by radiation protection and site medical personnel at approximately 0310 hrs. The operator was subsequently de-contaminated inside of the ambulance under the care of the emergency room physician, and the contaminated material was returned to site inside the ambulance. Once decontaminated, the operator was admitted to the Salem Memorial Hospital emergency room in Salem, New Jersey." The licensee informed the Lower Alloways Creek Township and the NRC Resident Inspector and does not plan a press release. * * * UPDATE PROVIDED BY LITKETT TO JEFF ROTTON ON 11/04/04 AT 0938 EST * * * Update to the details in the initial report second paragraph provided via fax: "The injured bridge operator was released from the Radiologically Controlled Area as un-contaminated with the exception of 5000 disintegrations per minute noted on a cotton liner on his right hand. Site medical personnel, accompanied by a radiation protection technician, transported the individual off-site at approximately 0310 hrs. The cotton liner was subsequently removed from the injured hand in the ambulance under the guidance of the emergency room physician and radiation protection supervisory personnel [after the ambulance arrived at the hospital]. No residual contamination was noted on the skin, and all contaminated material was returned to site inside the ambulance. The operator was then admitted to the Salem Memorial Hospital emergency room in Salem, New Jersey." The licensee notified the NRC Resident Inspector. Notified R1DO (Silk). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-11-03
41168 | 0 | DIABLO CANYON |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-11-02 11:05 | 2004-11-02 20:22 | 2004-11-02 | UNPLANNED DIESEL GENERATOR START ON A VALID BUS UNDERVOLTAGE SIGNAL "On November 2, 2004, at 11:05 PST, with Diablo Canyon Unit 2 in Mode 6 (Refueling), Emergency Diesel Generator (EDG) 2-1 auto started on an unplanned actuation signal from a valid 4160 volt Bus G undervoltage signal. All equipment responded as designed. After the EDG started, the auxiliary feeder breaker opened, and loads were automatically sequenced onto the EDG. At the time of the event, test equipment was being connected in preparation for an instrumented manual test start of EDG 2-1 prior to maintenance. "On November 2, 2004, at 1708 PST, operators transferred Bus G to auxiliary power and shutdown DG 2-1. "Prior to the event, Bus G was being supplied by auxiliary power, with startup power cleared for planned maintenance. Bus G was being prepared to be cleared for maintenance, therefore, required equipment was in-service on the other buses. Buses F and H were unaffected by this event and remain operable on auxiliary power, with EDG 2-2 (Bus H) and 2-3 (Bus F) operable. The following decay heat removal trains are powered from Bus G: Residual Heat Removal Pump 2-1 remained in standby, Component Cooling Water Pump 2-2 started on the transfer to EDG, and Auxiliary Saltwater Pump 2-2 re-started. "Unit 2 is in day 9 of a refueling outage, with the reactor head removed, the refueling cavity filled, and the upper internals installed with rods latched. "Unit 1 was unaffected and continues to operate in Mode 1 (Power Operation) at 100 percent power. "The cause of the Bus G undervoltage signal is being investigated." The licensee stated that no undervoltage was seen on any other equipment but the undervoltage relays on Bus G did sense an undervoltage. Residual Heat Removal was unaffected by the event. Bus G has been returned to its pre-event configuration and is considered operable. The other EDGs were fully operable at the time of the event and there were no significant LCOs at the time. All systems functioned as required. The licensee has notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-11-02
41167 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-11-02 14:00 | 2004-11-02 17:36 | 2004-11-02 | UNANALYZED CONDITION - INADEQUATE CABLE SEPARATION "On 11/2/04 at 1400, Seabrook Station determined that a potential scenario involving a fire could result in the loss of the Train A and Train B centrifugal charging pumps (CCP). During a fire, inadequate cable separation could result in the spurious closure of one of two series volume control tank (VCT) outlet valves. This would result in a loss of suction to the operating CCP and eventual loss of the pump. The second CCP is assumed to be lost as a result of the same fire. This condition was concluded to be reportable pursuant to 10CFR50.72(b)(3)(ii)(B) as a condition that resulted in the plant being in an unanalyzed condition that significantly degrades plant safety. "Compensatory measures include establishing a roving fire watch in the affected fire zones, operator briefings, and limiting combustible material in the affected fire zones." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-11-02
41166 | 0 | MALLINCKRODT |  |  |  |  | 2003-11-02 | 2004-11-02 09:45 | 2004-11-02 | MISSING DEPLETED URANIUM SHIPPING SHIELD "The licensee reported that an empty 18kg depleted uranium shipping shield could not be located. The shield was supposedly shipped from North Carolina Pharmacy in Greensboro, NC to Mallinckrodt (NRC Materials License #24-04206-01 Docket Number 030-00001), however, no record of delivery was found. After one year of searching, Mallinckrodt has declared the material "lost" as of 11/02/04. "Description of the lost source of licensed material Radionuclide: Depleted Uranium shield Physical Form: Solid (Mo-99 generator shielding encased in stainless steel housing) Activity: 18 kilograms Manufacturer: Manufacturing Science Corporation (Oakridge, TN) Model Number: L33200, Serial Number: 002771 "The depleted Uranium shield described above was incorporated into a Mo-99 DTE generator and subsequently distributed to the North Carolina Nuclear Pharmacy located in Greensboro, North Carolina (North Carolina Department of Environment and Natural Resources Radioactive Materials license #041-0780-1). As of the date of this letter the shield containing the depleted Uranium has not been located. All efforts, including contacting couriers and searches at both Maryland Heights and the Greensboro pharmacy have been unsuccessful. "With the tracking system that is currently in place at Maryland Heights as well as the delinquency notification program, we are able to track the shield when assigned to a shipment and upon its return. Based on these facts, the shield receipt by the customer has been verified, however the shipment from the pharmacy to Maryland Heights could not be verified. The in house tracking system at Maryland Heights shows that the shield was not returned and its disposition at this time is unknown with any degree of certainty. "Exposure of individuals and the possible Total Effective Dose Equivalent to persons within unrestricted areas, as a result of the loss of the licensed material, is deemed minimal due to the relatively low activity, and physical nature of the source (i.e., solid, steel-encased source). "Site personnel will continue searching for the missing depleted Uranium shield by conducting additional search exercises. In the spirit of ALARA, searching through containers of long-lived radioactive waste materials is not being considered at this time. Additionally, the VP of regulatory affairs for Cardinal Health was contacted concerning this issue. His efforts were also unsuccessful in locating the shield. "A full evaluation of the Depleted Uranium accountability and tracking program is in progress through a team approach. This six sigma approach will result in corrective actions that will strengthen the return process and prevent reoccurrence. The scheduled completion of this six sigma project is March 2005." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-11-02
41165 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-11-01 16:44 | 2004-11-01 23:44 | 2004-11-02 | EMERGENCY DIESEL GENERATOR AUTOMATIC START "At 1644 [11/01/04], with River Bend Station in Mode 5 (Refueling), voltage on offsite power line Reserve Station Service (RSS) No. 2 was lost. This offsite power line is the 230 KV power supply to the Division 2, 4160 volt safety related electrical bus. The Division 2 emergency diesel generator (EDG) automatically started and loaded on a loss of voltage to the 4160 volt safety bus. "At the time of the event, Division 2 Residual Heat Removal (RHR) was in the fuel pool cooling assist mode and the pump secured due to the loss of power. It was subsequently restarted and continues to provide the shutdown cooling function. "The following systems were isolated as a result of this event: Reactor Water Clean-up, Alternate Decay Heat Removal, and Floor Drains. "Investigation of the cause of the event is ongoing." There was no impact on spent fuel pool level or temperature. At the event reporting time, power to the bus was still being provided by the Division 2 EDG with plans to restore normal power shortly. The licensee informed the NRC Resident Inspector. See also similar event EN # 41164 of 10/31/04. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-11-02
41164 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-10-31 22:56 | 2004-11-01 02:13 | 2004-11-01 | PLANT HAD AUTO START OF THE DIVISION 1 EMERGENCY DIESEL GENERATOR "Undervoltage conditions were experienced on Division 1 emergency switchgear with subsequent start and load of the respective diesel generator [EDG]. A preliminary investigation indicates that an unexpected undervoltage signal was generated when technicians inadvertently contacted the wrong terminals during preparations for the respective division ECCS surveillance testing. All systems and equipment responded as required." Power is still being provided (as of event reporting time) by the Division 1 EDG while they are working to restore normal power. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-11-01
41163 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-10-30 14:43 | 2004-10-30 16:11 | 2004-10-30 | CONTAMINATED, INJURED PERSON TRANSPORTED OFFSITE The following information was obtained from the licensee via facsimile: "At 1405 [hrs. CDT], Shift Manager was notified that a contract individual in containment had collapsed and needed EMT [Emergency Medical Technician]. "At 1410, Shift Manager called for an ambulance and individual was transported out of containment. "At 1443, he [the injured person] was transported offsite to the hospital. Shift manager notified hospital of individual being contaminated. HP [Health Physics technician] identified minor contamination on the hair on the back of his head, ~200 cpm [counts per minute]. Shift Manager also contacted State Department of Health and Family Services [Radiation Protection Section]." The patient's status is unknown at this time but appears to be heat stress related. The contamination appears to be the result of a co-worker catching the patient when he was falling down. Plant Health Physics personnel attempted to decontaminate the patient but were unsuccessful. The patient was transported to Two Rivers Hospital in Two Rivers, WI. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-10-30
41162 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2004-10-26 11:30 | 2004-10-29 18:25 | 2004-10-29 | AGREEMENT STATE REPORT - MEDICAL EVENT "This event involved an HDR brachytherapy unit [Varian Medical Systems, Inc. Model GammaMed plus, serial number E159; with sealed source Model GammaMed 232, serial number 24-07-4445-004-082504-11622-71 (connector serial number D24E445)]. The female patients larynx cancer treatment plan called for four HDR brachytherapy treatments. On October 26, 2004, two HDR brachytherapy treatments were given. Before the third treatment was to be given, on October 27, 2004, an error was discovered. The prescribing physician stopped the treatment until dosimetry information was completed. The third treatment was not given. The error was caused because a circular tool was used to mark the treatment site. The diameter of the circle was used when the radius should have been applied. As a result, the area treated was 2 cm away from the defined locus instead of 1 cm. The total source length treated was 11 cm, (approximately 1 cm diameter cylinder surrounding the brachytherapy source placed inside a tracheotomy tube). The prescribed dose was 500 cGy (centiGray) to the entire 11 cm length. The worse case patient dose scenario was that the patient received 2,756 cGy at one dwell position out of 23 dwell positions along the 11 cm treatment length. The dose delivered would have been 551% greater than the prescribed dose at the position respective to the worst-case scenario. The licensee does not anticipate any adverse health affects to the patient. The Utah Division of Radiation Control is currently investigating this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2004-11-03
41161 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2004-10-22 14:00 | 2004-10-29 16:52 | 2004-10-29 | AGREEMENT STATE REPORT During the interlock check of a JL Shephard Model 1 Number 68-10 Irradiator, the source rod was lifted with the machine in the off position, indicating a failure of the interlock. Exposure determinations of the technicians present indicated an exposure less than reportable limits. An investigation is in progress. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2004-11-03
41160 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-10-29 16:00 | 2004-10-29 16:25 | 2004-10-29 | UNANALYZED CONDITION DISCOVERED IN 480 VOLT SWITCHGEAR ROOM The following information was obtained from the licensee via facsimile: "On October 29, 2004, at approximately 1600 hours, control room operators were informed by engineering personnel that raceways were located closer than 20 feet from the redundant division without being protected by a fire barrier wrap in accordance with the requirements of 10CFR50 Appendix R, Section III.G.2. "In 480 volt switchgear room E7, Brunswick is committed to maintaining redundant safe shutdown circuits by a minimum of 20 feet with no-intervening combustibles, unless the circuits are protected by a one-hour fire barrier wrap. Two conduits containing Division II circuits were identified closer than 20 feet to their redundant counterparts with no wrap installed. "The [NRC] Resident Inspector has been notified. "INITIAL SAFETY SIGNIFICANCE EVALUATION "The initial safety significance of this condition is considered to be minimal. When the condition was recognized, impairments were established in accordance with the fire protection program and compensatory measures were implemented. In addition, fire detection systems in the affected area have been verified to be operable. The affected area is maintained as a combustible free separation zone. "CORRECTIVE ACTIONS "Impairments have been initiated and appropriate compensatory measures established. The root cause and additional corrective actions are being documented in accordance with the corrective action program." | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-10-29
41159 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2004-10-29 | 2004-10-29 15:10 | 2004-11-02 | AGREEMENT STATE REPORT "On October 29, the radiation safety officer (RSO) for Bard Brachytherapy, Mr. Ed Zduenk called the Division to report an excessive radiation level from a package that they had received. Federal Express had delivered a container that was shipped by Northwest Hospital, Randallstown, Maryland on October 26, 2004. The maximum measured radiation level on the surface of the package was 500 milliRem/h. At a distance of 3 feet, the measured radiation level was indistinguishable from background. "After verifying that the package was intact and undamaged, the RSO proceeded to take measurements in the delivery vehicle. No elevated radiation levels were noted. With the package repositioned in the vehicle as described by the driver, additional measurements were made. There were no elevated readings detected on the exterior of the truck nor at the driver's position. As such, the RSO estimated the driver's exposure to be minimal from handling the package and briefly working at the rear of the delivery vehicle. The carrier was subsequently contacted with this information as well. "After the package was accepted and moved to a safe location at the facility, additional measurements were taken. The maximum dose rate measured at 1 foot was 10 milliRem/h and at 2 feet was 2 milliRem/h. The container was expected to have 112 sealed sources of I-125 with an actual activity of 0.476 milliCurie each for a total of 53.3 milliCurie. After the package was opened and its contents inventoried, it was determined that all of the sources were accounted for. When the package was opened, the RSO observed that the lid of the interior primary shielded container was not in its expected position. Although some of the sources remained in the shielded container, the other sources were only in their shielded applicator. No sources were 'loose' in the box. "Considering the shipper, the state of Maryland was notified of this event. This item is still open pending investigation to determine the cause of the event." IL report number IL040068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2004-11-03
41158 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-10-29 09:45 | 2004-10-29 14:33 | 2004-10-29 | CRITICALITY CONTROL REPORT "At 0945 on 10/29/04, the Plant Shift Superintendent was notified that NCSE/A 3972-11 did not establish the necessary moderation controls for the sump in the C-360 elevator pit to ensure that double contingency is maintained if a UF6 release occurs in the transfer room. The sump is an unfavorable geometry. The C-360 basement transfer room is small and relatively air-tight once placed in containment resulting from a UF6 release. A credible UF6 release in the Transfer Room could consume all moisture in the room and leave gaseous UF6 available to react directly with pre-existing liquids in the elevator sump. Over an extended period of time this reaction could support a uranium concentration that results in a critical configuration. The current configuration of the sump does not prevent less than an always safe slab depth of 3.5 inches of solution in the sump. "CORRECTIVE ACTIONS: Stop fissile operations in the C-360 transfer room until the necessary NCS controls for double contingency can be ensured for the sump in the elevator pit." The regulatee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-10-29
41157 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-28 13:14 | 2004-10-28 17:46 | 2004-10-28 | EMERGENCY SIRENS INOPERABLE "At 1314 EDT on 10/28/04, all 34 of the Mecklenburg County ANS sirens failed a scheduled weekly test. The silent test checks only the radio circuitry involved in actuating the sirens. This test failure was attributed to a phenomena known as 'Tropospheric Ducting,' which is essentially radio frequency interference on the frequencies utilized for siren control. At 1448 EDT on 10/28/04, the radio frequency interference had cleared and the siren test was repeated with 100% success rate. The remaining 33 sirens in the other four EPZ counties were tested satisfactorily in the same time frame." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Power Operation |  | Cold Shutdown | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-10-28
41156 | 0 | SCIENTECH LLC |  |  |  |  | 2004-10-28 | 2004-10-28 14:37 | 2004-10-28 | POTENTIAL DEFECT UNDER 10CFR21 "Investigation of failures of two NUS instruments modules revealed that the Kepco power supplies used in the current output circuit failed. Further investigation by the manufacturer of the power supplies revealed that these failures were due to a manufacturing error - in some cases, a surface mount capacitor had been installed with reverse polarity. The capacitor is lightly loaded and takes up to 1000 hours fail, so this problem will not usually be detected by functional testing or normal burn-in tests. The Kepco power supply with the failure is model number FCP-032K. Kepco has identified the manufacturing period of risk for the FCP-032K power supplies as being from April 2003 through July 2004; the period during which the surface mount capacitor was manually installed during a conversion to new automated manufacturing facilities. Not all Kepco FCP-032K power supply components are affected by this problem, nor are other Kepco power supply models." The affected facilities are: Fitzpatrick, Indian Point 2 and 3, Pilgrim, Beaver Valley, Duane Arnold, and Watts Bar. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | ID | OTH | PAR | 21.21 |  |  |  | 0 | 2004-10-28
41155 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-10-28 10:03 | 2004-10-28 10:52 | 2004-10-28 | UNUSUAL EVENT DECLARED DUE TO A TOXIC GAS RELEASE IN THE SECURITY CENTER "At 1003 [hrs] on October 28, 2004, an Unusual Event was declared at the Hope Creek Generating Station in accordance with EAL 9.4.1.b due to an uncontrolled release of freon gas from a chiller located in the top floor of the PSEG Nuclear Security Center. Although the top floor of the security center is a normally locked security area, access restrictions to the top floor of the security center were imposed by the Site Protection (or Fire) Department with breathing apparatus required. This was due to freon concentrations of 2000 ppm at the site of the leak, which exceed the threshold limit value of 1000 ppm. No injuries resulted from the freon leak and no access restrictions were imposed to the main entry/exit level of the security center or the basement (where maximum freon levels were 100 ppm or 10% of the TLV and 1000 ppm respectively). The TLV represents a concentration acceptable for 40 hrs per week, 50 weeks per year occupancy. As of 1040 [hrs] freon levels in the top floor of the security center are 0 ppm." The licensee informed state/local agencies and the NRC Resident Inspector. * * * UPDATE FROM M. SHAFFER TO H. CROUCH AT 1324 ON 10/28/04 * * * Hope Creek secured from Unusual Event at 1316. The leakage has stopped, the machine has been evacuated of freon and normal personnel access has been restored. The licensee notified the NRC Resident Inspector. Notified R1 (R. Blough), NRR (T. Reis), IRD (P. Wilson), DHS (A. Costa and M. Cohen), and FEMA (K. Sweetser). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-10-28
41154 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-28 00:52 | 2004-10-28 03:29 | 2004-10-28 | MANUAL REACTOR TRIP AFTER SHUTDOWN BANK DROPPED INTO CORE "At 0052 on 10/28/04 the Unit 2 reactor was manually tripped after an electrical fault caused Shutdown Bank D control rods to drop into the core. An automatic start of the Auxiliary Feedwater system occurred when water levels in all four Steam Generators reduced to the Lo-Lo level setpoint. A letdown isolation occurred on Lo Pressurizer level resulting from the cooldown of the primary system after the Auxiliary Feedwater system start. Reactor Coolant system temperature has been recovered and the plant has been stabilized at Hot Shutdown conditions." The licensee stated that there were no complications during the trip. All systems functioned as required. No significant safety systems were out of service when the trip occurred. No primary or secondary relief valves lifted during the transient. Decay heat is currently being removed using aux feedwater to the steam generators steaming to the main condenser. Tave dropped to a low point of 540 degrees F during the transient. The reactor was manually tripped in approximately 18 seconds after the shutdown bank dropped. The licensee plans to remain in mode 3. The licensee will notify the NRC Resident Inspector. The licensee will also notify state and local authorities in North and South Carolina. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-10-28
41153 | 0 | DEPARTMENT VETERANS AFFAIRS |  |  |  |  | 2004-10-26 | 2004-10-27 18:16 | 2004-11-10 | LOST RADIOACTIVE MATERIAL RSO for the VA Medical Center, New Orleans, LA was notified at 0900 CDT on 10/27/04 of a missing shipment of I-125 (10 millicuries) that had been received by that facility on 10/26/04. The RSO is conducting an investigation into the missing radioactive material. * * * UPDATE AT 1500 ON 11/10/04 M. SIMMONS TO W. GOTT * * * "The radioactive material was I-125 as sodium iodide, liquid form, shipped in a shielded vial containing 10 millicuries in a volume of less than 1 milliliter. The RAM was to be used in a biomedical research lab. "The permittee investigated the loss and concluded the radioactive material most likely ended up in a local landfill. "The permittee notified the local landfill operations staff of the event. The permittee and landfill operations staff performed radiation surveys of the landfill. The radiation surveys did not locate the missing radioactive material. "The NHPP performed a reactive inspection one week after the loss was discovered. "The initial inspection results confirm the radioactive material is most likely buried at the local landfill and is not recoverable. According to witnesses, the probable cause of the event is the shipping box was not correctly labeled as containing radioactivity." Notified NMSS (Moore), R3DO (Ring), and R4DO (Gody). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-10-27
41152 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-09-15 09:11 | 2004-10-27 15:21 | 2004-10-27 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "In accordance with the requirements and guidance of 10 CFR 50.73(a)(1), a telephonic report of an invalid signal affecting containment isolation valves in more than one system is being submitted. This report is being made under 10 CFR 50.73(a)(2)(iv)(A), automatic actuation of a system listed in paragraph (a)(2)(iv)(B), in lieu of a written LER. "At 0911 hours, on 09/15/2004, while operating at full power, the plant experienced a loss of power to eight process radiation monitors. The loss of power was caused by the failure of an internal radiation monitor system power supply, PS-100. The affected radiation monitors actuated, where applicable, their associated safety and non-safety related components. The safety related components affected included eight containment isolation valves and the plant's auxiliary building special ventilation system equipment. The containment isolation valves were: "- 4 steam generator blowdown system isolation valves (inside and outside containment isolation valves for each of the plant's two, 'A' and 'B' steam generators). "- 4 steam generator sampling system isolation valves (inside and outside containment isolation valves for each of the plant's steam generators' sample system lines). "All the components affected operated as designed. The effect on plant operation was not significant. The power supply was replaced and the ventilation systems, sampling and blowdown piping systems were realigned to normal. "The power supply failure and subsequent closure signal to the noted containment isolation valves is an example of an invalid signal. No full or partial containment isolation signal was generated. None of the valve closures were needed to mitigate the consequences of the power supply failure. The investigation to determine the cause of the power supply failure continues." The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-10-27
41151 | 0 | MCGUIRE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-19 20:20 | 2004-10-27 13:55 | 2004-10-27 | INVALID TURBINE DRIVEN AUXILIARY FEEDWATER ACTUATION "On October 19, 2004, McGuire Nuclear Station Unit 2 experienced an inadvertent actuation of the Turbine Driven Auxiliary Feedwater (TDCA) Pump. This event occurred when the steam supply valve to the pump failed open due to low pressure in the nitrogen supply to the valve's actuator. Further evaluation determined that the inadvertent actuation of the TDCA Pump was not in response to actual plant conditions or parameters satisfying the requirements for actuation of the pump. Since the TDCA Pump was not started in response to a valid signal, this represented an invalid actuation reportable per the requirements of 10 CFR 50.73 (a) (2) (iv) (A). However, as per 10 CFR 50.73(a)(1), McGuire is providing a telephone notification of this invalid actuation instead of submitting a written LER. "The following additional information is being provided as part of the telephone notification of this event: - The Unit 2 TDCA Pump actuated and injected water into all four of the Unit 2 Steam Generators - The actuation of the Unit 2 TDCA Pump was successful and complete." The licensee stated the total injection time was approximately 16 minutes and that a very small power increase was observed during the event. The NRC Resident Inspector has been notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-10-27
41150 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2004-10-26 13:56 | 2004-10-27 13:05 | 2004-10-27 | RANDOM FITNESS FOR DUTY TEST Illegal drug use was detected during a random drug test of a non-licensed employee. The employee's access to the plant has been terminated. Contact the HOO for additional details. The NRC Resident Inspector was notified by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2004-10-27
41149 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-10-26 17:30 | 2004-10-27 10:37 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * FAILURE OF SAFETY SYSTEM CAUSING UNFAVORABLE GEOMETRY The licensee reported a transfer of low concentration HEU solution from favorable to unfavorable geometry was initiated upon sampling data that was not representative of the solution. The solution has been determined to be above the transfer concentration limit. Verification of HEU concentration is an administrative "item relied on for safety" (IROFS) for the accident sequence. The remaining IROFS for the accident sequence is an inline radiation detector that automatically closes redundant block valves. This system performed as designed. The system was placed in a safe shutdown condition and the solution remains in a favorable geometry. Mass is controlled in the unfavorable geometry tank by limiting the volume and concentration of transfers into it. The failed control is administrative sampling and verifying the concentration is below the limit. The licensee states the solution will be reprocessed to lower concentration prior to discharge. The licensee has informed the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | LOSS OR DEGRADED SAFETY ITEMS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | PART 70 APP A (b)(2) |  |  |  | 0 | 2008-05-11
41148 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-08-02 17:00 | 2004-10-26 19:56 | 2004-10-26 | AGREEMENT STATE REPORT - SAFETY EQUIPMENT FAILS TO FUNCTION Summary report of fax provided by State of California On August 2, 2004 at 5:00 pm PDT, a licensee employee was irradiating electrical parts using the Low Dose 142-MA Self Contained, Shielded Panoramic Irradiator. This device uses a Cobalt- 60 (Co-60) source with an activity of 2 Curies. The licensee employee was able to bypass the interlock to the chamber while the chamber was irradiating. The employee was wearing a film badge and holding his ring badge in his hand (not on finger) while working with the chamber. The film badge was first used on August 2, 2004. The ring and film badges were collected and immediately shipped for analysis. The source of radiation within the chamber is a sealed Co-60 (2 Curies) source and is exposed by raising and lowering the source rod. Raising the rod activates the door interlock and exposes the source within the chamber. The licensee intended to place a product into the chamber and failed to notice that the source rod was up, and pulled open the door while the interlock was activated. The safety interlock failed and was unsuccessful in keeping the doors locked. The door was immediately closed (exposure time approximately 3 seconds) On August 4, 2004, the licensee contacted a Health Physics consultant and performed a calculation to estimate the possible exposure level. They used the Gamma Constant for Co-60, the exposure time, distance, and activities that were involved. During the afternoon of August 4, 2004, J. L. Shepherd inspected the equipment and determined that the interlock was defective and advised that they install an alternate interlock that is sturdier. They returned on August 5, 2004 and installed the new interlock. Wear on the interlock arm caused the ultimate failure on August 4, 2004, and was most probably caused by repeated attempts by the operators of the irradiator to forcibly open the cavity lids while the source was in the "Irradiate" position. The replacement arm has been redesigned and strengthened to avoid the recurrence of a problem of this nature in the future. California preliminary exposure estimate to the operator's hands is less than 200 millirem while licensee calculation showed exposure received to be approximately 2-3 millirem. Incident remains open until receipt of documentation of monitoring device exposure and copies of the physicist's calculations. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-10-29
41147 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-10-25 22:00 | 2004-10-26 10:49 | 2004-10-26 | OHIO AGREEMENT STATE REPORT OF A STOLEN TROXLER MOISTURE DENSITY GAUGE "Stolen Troxler moisture density gauge. Model 3401B, Serial # 13437. Contains Cesium-137 (8 millicuries) and Americium-241/Beryllium (40 millicuries) sources. Ohio License # 31210310000. Gauge was stolen from back of pick-up truck outside a motel on west side of Cleveland, Ohio. Gauge was in locked transfer case with radioactive material labels on outside. Case was chained to bed of pick-up truck. Theft occurred sometime between 10 PM Monday, 10/25/04 and 7 AM Tuesday, 10/26/04. Theft was discovered when worker returned to truck in morning to begin work day. Police have been notified. Awaiting additional information and police report from licensee. Initial report made to Bureau at 8:40 AM on 10/26/04. Information is current as of that time." Reference Number: OH2004-104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2004-10-29
41146 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-10-21 15:00 | 2004-10-25 19:10 | 2004-10-25 | AGREEMENT STATE REPORT - STOLEN RADIOACTIVE SOURCES Received via email from Washington Department of Health, Office of Radiation Protection "The licensee possesses and uses sealed sources for calibrating nuclear medical instrumentation. Two sources, Cobalt-57 and Americium-241 each assay activity of about 74 megabecquerel (2 millicurie), were contained in lead pigs kept in the service technician's toolbox. The toolbox was reported as "probably" locked. The toolbox was not secured in the vehicle. The vehicle was parked in the driveway of the technician's home. The toolbox and two boxes of spare parts were reported stolen. The theft was reported to Liberty Lake Police Department between 3:00 and 4:00 p.m. [PDT]." Washington Event Report #: WAC 246-221-240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-10-28
41145 | 0 | FOUNDATION ENG. SCIENCE |  |  |  |  | 2004-10-18 12:00 | 2004-10-25 09:58 | 2004-10-25 | TROXLER GAUGE STOLEN FROM THE BACK OF A PICKUP TRUCK An employee of Foundation Engineering Science, Newport News, Virginia, checked out a Troxler Model number 3430 moisture density gauge to be used on a worksite located in Norfolk, Virginia. The individual stopped off at Wal-Mart in Norfolk, Virginia, and went inside to get some items. When he arrived back he found the Troxler moisture density gauge missing. He went back into Wal-Mart and viewed a video tape taken by the Wal-Mart security camera. Two individuals in a truck were seen taking the gauge. Norfolk police were contacted and a police report was made (did not have police report number). It is unknown at this time if the gauge was chained and locked to the bed of the pickup truck (company policy is to chain and lock the gauge to the bed of the pickup truck). The Troxler moisture density gauge stolen model number is 3430 and its serial number is 29129. This information was relayed to Troxler and they have entered this information into their data base. The gentleman making the report did not know if a reward had been announced for the recovery of the gauge. Troxler Model 3430 source strengths are typically (8 millicuries of cesium-137 and 40 millicuries of Am-241/Be). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-10-25
41144 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-23 20:23 | 2004-10-23 21:43 | 2004-10-23 | OFFSITE NOTIFICATION TO SOUTH CAROLINA OSHA A Catawba employee suffered an apparent heart attack while at work and was transported offsite to a local hospital at 1745 EDT on 10/23/04. The employee subsequently passed away at the hospital. No contamination was involved; the employee was working in the Unit supervisor's office. The licensee is required to make an offsite notification to South Carolina OSHA within 8 hours. The licensee also notified state and local authorities for the states of SC and NC as well as the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-23
41143 | 0 | MASSACHUSETTS RADIATION CONTROL |  |  |  |  | 2004-08-31 | 2004-10-22 15:26 | 2004-10-22 | AGREEMENT STATE REPORT OF MEDICAL MISADMINISTRATION "Patient scheduled to receive template-guided transperineal prostate interstitial brachytherapy for clinical localized prostate cancer was to receive 72 I-125 seeds, instead received 47 seeds resulting in underexposure of greater than 20%." "The cartridges carrying 15 seeds each were loaded into a 'Mick' applicator. Transrectal ultrasound was used for localization of the prostate and implant needles; fluoroscopy was used very little during the procedure to minimize staff exposure. As each seed was injected into the prostate, it was recorded both on paper and in computer system and final tabulation was 77 seeds were implanted. However, x-rays taken after the procedure showed only 47 seeds had been implanted, although distribution appeared satisfactory." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | HOS | [5 empty] | 0 | 2004-10-22
41142 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2004-10-08 18:31 | 2004-10-22 11:00 | 2004-10-22 | PART 21 REPORT: AUXILIARY RELAYS FAILURE "In accordance with 10CFR21.21(d)(3), initial notification of a reportable defect is being made by James A. Fitzpatrick (JAF). "The failure of two General Electric (GE) IRMA auxiliary relays in a short period of time were identified in the corrective action system as a potential common mode failure. Initial troubleshooting revealed that both relay coils indicated open. There was no evidence of any obvious cause for the coils to open circuit (e.g. discoloration, smell, physical damage). Both relays are normally de-energized relays located in a mild environment in the relay room (controlled humidity, no vibration at the panels, no local heat source that could cause accelerated aging). Both relays were installed in 1988 along with 21 other relays. A total of 33 relays were purchased from GE with the same lot/date code. "An extent of condition review was conducted. By checking the continuity of related relay coils, two other coil failures were detected. A failure analysis of the relays was performed. The failure mode was determined to be an open in the coil due to corrosion of the coil wire. This open in the coil will prevent the relay from changing state as the relay is energized. An independent laboratory concluded that the coil insulation was damaged and that the under lying wire was damaged during coil manufacture. The damage allowed the copper wire to corrode over the years to the point of failure. "These HMA relays were installed in multiple Emergency Core Cooling Systems (ECCS) and other systems. Each component was evaluated to determine the specific impact on the respective system. The systems affected included: Residual Heat Removal (RHR, the Low Pressure Coolant Injection (LPCI) mode of operation), Emergency Diesel Generators (EDGs), Automatic Depressurization System (ADS), Reactor Core Isolation Cooling (RCIC), Core Spray (CS), and High Pressure Coolant Injection (LPCI). "JAFs evaluation concluded that a substantial safety hazard existed in that there was a potential for a major deficiency/major degradation of essential safety-related equipment, specifically for the RHR (LPCI mode of operation) and HPCI systems. "No other safety functions would have been lost for the other identified systems. "Component and Supplier: GE HMA Type auxiliary relays GE Part No. 12HMA124A2 GE Dwg No. DA137C6164P001 Date Code 14VC; 8836 Serial #s: D88542-0001D R02 through D88542-0033D R02 "All were purchased as safety-related from GE under JAF PO # 88-5628 "All installed safety-related relays from this lot were replaced during the recent refueling outage." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 21.21 |  |  |  | 0 | 2004-10-22
41141 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-10-19 | 2004-10-20 10:08 | 2004-10-20 | AGREEMENT STATE REPORT - THREE WELL LOGGING SOURCES ABANDONED DOWNHOLE "Well: Mako Steward A-37 State Tract #1, Galveston, County, Texas 9,150 ft. downhole (bottom of well) "Well logging string became stuck in a 6 3/4" wellbore over the weekend. Attempts to 'fish' for the sources was unsuccessful with the fishing tool becoming stuck in the wellbore above the well logging tool string. The tool string contains three sealed sources: an 18 curie Am-241/Be; a 2 curie Cs-137; and a 0.8 microcurie Cs137. The sources were declared abandoned late on October 19, 2004. The Licensee is preparing to seal the well with red dyed cement and placement of a deflection device in the wellbore. The tool string is sitting at the bottom of the well at 9,150 feet downhole. Source manufacturers and serial numbers are currently unavailable." Texas Incident No. I-8175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-10-25
41140 | -1 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-10-19 17:30 | 2004-10-20 01:35 | 2004-10-26 | STANDBY EMERGENCY ELECTRICAL POWER PATHS INOPERABLE FOR 41 MINUTES "The Keowee Hydro Units provide the emergency power source for the Oconee Units. At 0357 on 10/19/04, Keowee Unit 1 (and the overhead emergency power path) was declared inoperable in order to perform scheduled maintenance. At 1730, Keowee Unit 2 (and the underground emergency power path) was declared inoperable due to the loss of breaker control power associated with Keowee Unit 2 auxiliaries. At 1811, as required by Technical Specification 3.8.1 condition I, both standby buses were energized from a Lee Combustion Turbine via an isolated power path. At 1828, a Operability Verification of Keowee Unit 2 to the overhead emergency power path was performed with all acceptance criteria met. At 1904, Keowee Unit 2 to the overhead emergency power path was declared operable. Technical Specification 3.8.1 condition I was exited. "Initial Safety Significance: Between times 1730 to 1811, both on site emergency power paths were inoperable. During this time period a condition existed that could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. "Corrective Action(s): At 1828, an Operability Verification of Keowee Unit 2 to the overhead emergency power path was performed with all acceptance criteria met. At 1904, Keowee Unit 2 to the overhead emergency power path was declared operable. Technical Specification 3.8.1. condition I was exited. A team is established to investigate the loss of breaker control power associated with Keowee Unit 2 auxiliaries." The licensee will notify the NRC Resident Inspector. * * * RETRACTION FROM TODD TO HUFFMAN AT 1428 EDT ON 10/26/04 * * * "The Keowee Hydro Units (KHUs) provide the emergency power source for the three Oconee Units. On 10/20/04 at 0135 Oconee made a notification to the NRC of a loss of safety function. Reference Event Number: 41140. The event was due to an unexpected failure on KHU 2. At the time of the event, KHU 1 was out of service for planned maintenance and was in the early stages of testing for return to service. "Each KHU can be aligned to either an overhead or an underground power path to supply emergency power to Oconee. At 1730, KHU 2 and the underground emergency power path were declared inoperable due to the loss of breaker control power associated with KHU 2 auxiliaries while aligned to the underground path. By the Oconee Technical Specification 3.8.1 Bases, this breaker (ACB-8) is required to be operable in order to consider KHU 2 operable while aligned to the underground path. Since KHU 2 did not meet the TS configuration, and since KHU 1 testing was not complete, both trains were inoperable and the event was reported as a loss of safety function. At 1811, as required by Technical Specification 3.8.1 condition I, both standby buses were energized from a Lee Combustion Turbine via a dedicated power path. KHU 2 was re-aligned to the overhead path and its associated auxiliary power breaker (ACB-6). The event was terminated at 1904 when KHU 2 was declared operable to the overhead emergency power path after completion of an Operability Verification test. "Justification for conclusion that there was no loss of safely function while KHU 2 was declared inoperable (approximately one hour duration): "KHUs are capable of 'black start', i.e. starting and operating on battery power alone. Therefore, if there had been an event resulting in an emergency start signal during the one hour interval of vulnerability, KHU 2 would have been able to start and operate for approximately one hour with the loss of control power to ACB-8. Operations procedures include guidance to close breaker ACB-8 manually using a maintenance closure handle. These steps would have been performed approximately 30 minutes into the postulated event. Based on the results of testing and troubleshooting of ACB-8, Oconee has concluded that ACB-8 could have been closed manually and, once closed, would have successfully provided auxiliary power for the duration of any event. "Thus Oconee concludes that KHU 2 should be considered available, with reasonable expectation for performing its safety function during this event. Therefore Oconee has concluded that this event was not a reportable loss of safety function and Event Number 41140 is withdrawn." The resident inspector and R2DO (Bonser) have been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-20
41139 | -1 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2004-10-19 18:30 | 2004-10-19 23:37 | 2004-10-28 | HIGH PRESSURE COOLANT INJECTION (HPCI) INOPERABLE DUE TO CONTROLLER SIGNAL CONVERTER TROUBLE. "On October 19, 2004 at approximately 1830 hours CDT, Unit One was performing QCOS 2300-05, Quarterly HPCI Pump Operability Test. This was being performed to prove operability following maintenance work on various valves and the turning motor gear unit. At this time when the HPCI turbine was rolled, the HPCI Signal Converter Trouble alarm was received. The HPCI Flow Controller demand controlled at approximately 7250 gpm instead of controlling at the desired 5600 gpm. HPCI was determined not to be operable and was shutdown per procedure. Due to the unexpected behavior of the HPCI Flow Controller, at this time it is not certain if the HPCI will meet its safety function. Therefore, we are reporting this event under 10 CFR 50.72 (b)(3)(v)." Licensee entered Tech Spec 3.5.1.(f) 14 day Limiting Condition of Operation (LCO) for HPCI. Reactor Core Isolation Cooling (RICI) is operable. All other Emergency Core Cooling Systems (ECCS) and the Emergency Diesel Generators (EDG) are fully operable if needed. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION J. DAVIS TO W. GOTT AT 1819 ON 10/28/04 * * * "The purpose of this report is to retract the ENS report made on October 19, 2004 at 2237 CDT (ENS #41139). The initial report was made following HPCI operability testing in accordance with QCOS 2300-05, Quarterly HPCI Pump Operability Test. When the HPCI turbine was rolled, the HPCI Signal Converter Trouble alarm was received. The HPCI Flow Controller failed to control at the desired 5600 gpm (instead, the system ramped to 7250 gpm). Due to the unexpected behavior, it was not certain at the time if HPCI could have met its design basis requirements. However, a subsequent review of this event has determined that HPCI would have performed its safety function. The Signal Converter failed in a manner that prevented automatic flow control, but did not prevent HPCI from initiating and ramping to full flow (i.e., the turbine high speed stop). In this condition, HPCI would have met corresponding Technical Specifications and Accident Analysis requirements. The circuit board was replaced and the Signal Converter and flow controller feedback loop were re-calibrated. The Unit 1 HPCI turbine's automatic flow control was successfully tested on October 20, 2004." The Licensee notified the NRC Resident Inspector. Notified R3DO (R. Garner) | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-19
41138 | 0 | COMPUTALOG WIRELINE |  |  |  |  | 2004-10-19 21:30 | 2004-10-19 23:10 | 2004-10-19 | LOSS OF WELL LOGGING SOURCE OFF SHORE During well logging operations on a fixed platform in the Gulf of Mexico, the well logging tool separated from the wireline and fell overboard in approximately 40 feet of water. The well logging tool has a 45 millicurie Cs-137 source attached. Licensee is going to coordinate with NRC Region 4 and State of Louisiana personnel to identify a source/tool recovery team to search for the radioactive source. There is a slight possibility that the tool could be caught on the platform substructure that is normally inaccessible by personnel. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | TX | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-10-19
41137 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-10-19 22:10 | 2004-10-19 23:03 | 2004-10-19 | UNUSUAL EVENT DECLARED DUE TO UNEXPLAINED DECREASE IN SPENT FUEL POOL WATER LEVEL "An uncontrollable decrease in water level in the spent fuel pool occurred. All fuel assemblies remained covered. Current plant conditions DO NOT threaten public safety. Level decrease is secure. Valve lineup caused level decrease to BWST. Approximately 24 feet above fuel maintained. Secured fuel transfer canal drain lineup." Unit 3 is currently defueled. The licensee was attempting to perform a spent fuel pool makeup while there was another valve lineup in progress which drained the deep end of the fuel transfer canal. This exposed some piping that allowed a flow path from the spent fuel pool to the BWST and resulted in the transfer of slightly less than 1 ft. level in the spent fuel pool, or approximately 10,000 gallons. Operators immediately recognized the decrease in spent fuel pool level and took appropriate steps to secure other activities in order to identify the drain path. This included securing the RCB wash downs in progress inside containment to eliminate a source for the observed increase in RB sump levels and secured equipment drain downs in progress in the Aux Building to eliminate these as a source for the observed increase in the high activity waste tank level. Spent fuel pool level decreased from 0.3 ft above to about 0.7 ft below the normal. During the transient, a 24 ft. level was maintained above the spent fuel. No increase in radiation levels following the decreasing in water level was observed. The licensee had recently started three spent fuel pool cooling pumps and due to a decrease in spent fuel pool temperature some shrinkage had occurred. The drain down to the BWST was initiated at approximately 2115 hours. At 2130 hours, Operators recognized the problem and entered the applicable Abnormal Procedure. At 2210 hours the Licensee declared an Unusual Event and took actions to secure the valve lineup which allowed the drain down. These actions were completed by 2215 hours at which time the Unusual Event was terminated. By 2224 hours a level increase due to makeup was observed. Current spent fuel pool level is - 0.15 ft and increasing. The Licensee will continue makeup until the level reaches + 0.5 which is estimated to occur at approximately 0100 hours on 10/20/04. No offsite radioactive release occurred. The licensee will inform the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Refueling; FMode3: Refueling | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-10-19
41136 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2004-10-05 | 2004-10-19 16:15 | 2004-10-25 | AGREEMENT STATE REPORT INVOLVING SHIPMENT OF PACKAGES WITH REMOVABLE CONTAMINATION "On October 18, the licensee called the Division [Tennessee Division of Radiological Health] to report that a shipment brokered by Duratek from their facility in Memphis, TN on September 29 arrived at Laguna Verde Power Station near Veracruz, Mexico on October 5 with three boxes exceeding the removable contamination limits of 49CFR173.443. The boxes contained contaminated equipment, to be used at the Power Station during an outage. The equipment was contaminated with mixed fission/activation products. There was no contamination found on the truck. The boxes were decontaminated onsite." Tennessee Event report ID No.: TN-04-151 * * * UPDATE FROM TENNESSEE DIVISION OF RAD HEALTH TO BILL HUFFMAN AT 16:30 EDT ON 10/25/04 * * * "This event was reported on 10/19/04 as exceeding the removable contamination limits of 49 CFR 173.443. The licensee has investigated the incident which involved three boxes of GE Nuclear equipment shipped from the licensee to Laguna Verde Nuclear Plant in Mexico. The investigation has shown that this shipment did not violate applicable regulations for international shipments of radioactive materials and most likely did not violate the limits for shipments under the US DOT regulations. The latter statement is qualified. Because the data from Laguna Verde is not sufficient to make any other determination. The area averaging and the smear removal efficiencies were not determined. The investigation has revealed that the shipment violated Laguna Verde's acceptance procedures for loose contamination." NMSS EO ( Miller), R1DO (Cahill), and R4DO (Sanborn) have been informed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2004-10-22
41135 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-06-03 | 2004-10-19 16:37 | 2004-10-20 | AGREEMENT STATE REPORT - MULTIPLE PATIENT OVEREXPOSURE "A verbal report was received on July 20, 2004, which reported patient doses in excess of 50 Rem to the wrong physical area on treatments involving a Nucletron HDR Microselectron brachytherapy device, Model 080.000, Serial No. 9072. Four patients received wrong doses due to a 7.5 centimeter error in source location from the intended treatment site/plan. Details were vague due to discussion over the phone. A written report would follow. "The written report date August 2, 2004, was received by this agency on August 6, 2004. The report failed to give details needed by this agency. An Agency investigator was assigned to investigate this incident on August 6, 2004. The investigation conducted on August 18, 2004, determined that an error in catheter length was entered by two different registered therapists as 920 millimeters versus the default and actual length of the catheter of 955 millimeters. The 75 millimeter or 7.5 centimeter error resulted in two sources: a 12.3 curie (02/16/2004) Ir-192 source, Serial No. D35AO131 and a new Ir-192 source installed on 07/08/2004, Serial No. D35A0605, 10.5 curies being positioned outside of each patients body. The error was discovered after one of the four patients developed skin erythema. The patients were to receive boost treatments of 500 centiGray per fraction from the HDR unit to the prescribed location with the total number of fractions varying from 3 to 7 in the physician's written directive. The patients were all being treated for inter uterine cancer. The patients received fractional treatments with the error which varied from 1-5 fractions. Make-up treatments were required on three of the patients to achieve the correct dosage to the treatment site. Some patients received both correct and incorrect treatments from the same therapists. "The error was discovered on July 8, 2004, when one patient complained of tenderness in one leg. The physician determined that the patient had erythema on her leg, several centimeters from the planned treatment site. The physician's investigation determined the error in catheter length on July 14, 2004, and ordered make-up treatment for his patient on July 15, 2004. A total of four female patients, three radiation oncologists, and three radiation therapists were involved in the treatments and required corrective treatments to three of the four patients. The hospital was reluctant to release dose data on the patients due to concerns of HIPAA privacy standards. After explanation of allowable disclosure to this agency, the Licensee provided the data on October 4, 2004. "Patient #1 received a non-target tissue dose of 800 rad superficial and 250 rad deep over a three week period. She suffered skin erythema which was treated over a few weeks with rest and a topical ointment. After the erythema was resolved she resumed normal follow-up treatment for her initial disease. Patient #2 received a non-target tissue dose of 400 rad superficial and 150 rad deep over a one week period and exhibited no abnormal reactions. She immediately resumed normal follow-up treatment for her initial disease. Patient #3 received a non-target tissue dose of 1100 rad superficial and 300 rad deep over a three week period. She exhibited no abnormal reactions and resumed normal follow-up treatment for her initial disease. Patient #4 received a non-target tissue dose of 1800 rad superficial and 350 rad deep over a seven week period. She suffered skin erythema and was treated with rest and topical ointment. After the erythema was resolved, she resumed normal follow-up treatment for her initial disease. This is an abnormal occurrence." Texas Incident # I-8145. * * * UPDATE FROM J. OGDEN TO M. RIPLEY 0825 ET 10/20/04 * * * "The correct catheter length is 995 mm vs. the entered length of 920 mm. A difference of 75 mm or 7.5 cm." Notified R4 DO (Whitten) and NMSS EO (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-10-22
41134 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-19 05:28 | 2004-10-19 12:35 | 2004-10-19 | LOSS OF NORMAL POWER SUPPLY TO "2E" SWITCHGEAR RESULTED IN AFW AUTOSTART "Unit 2 experienced an autostart of Auxiliary Feedwater System (AFW) and Emergency Diesel Generator 'B' following transfer of the '2E' Switchgear to Alternate Power Supply. "Normal Power Supply (XST1) experienced a loss of power, causing the '2E' Switchgear to slow transfer to the -2 Breakers from the Alternate Power Supply (XST2). "The AFW (MDAFWP [Motor-driven Auxiliary Feedwater Pumps] 'A' and 'B' and TDAFWP [Turbine-driven Auxiliary Feedwater Pump]) autostarted due to Sequencer Operations. "The EDG 'B' autostarted on low voltage condition but did not supply power to the affected '2E' bus. The EDG 'B' cooling water was provided by the service water system. "Power was restored to XST1 at 0606 CDT. The cause of the EDG 'B' autostart is under investigation. The cause of the loss of power to XST1 is under investigation. Power was reduced to 98.2% to ensure Nuclear Power <100%. All other systems functioned as required. Local NRC Resident was informed." | 0 | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-10-19
41133 | 0 | ST. VINCENT HOSPITAL |  |  |  |  | 2004-10-11 | 2004-10-19 12:05 | 2004-10-21 | MEDICAL EVENT INVOLVING FRACTIONATED DOSE DELIVERY LESS THAN PRESCRIBED On 10/11/04 a 49 year old female patient received the first of two treatments for endometrial cancer. A total dose of 700 centiGray was prescribed to be delivered in two (2) 350 cGy fractions using a 1500 mm length catheter containing a 7.035 curies Ir-192 source (duration 189 seconds). Due to an error on the part of the Health Physicist, the 995 mm length catheter was used. This resulted in a calculated dose of less than 1 cGy to the thigh at a distance of 505 mm from the intended site. There are no expected adverse consequences. Both the patient and prescribing physician were informed. A new treatment plan has been developed and the patient rescheduled. Corrective actions are to be determined. The licensee informed Region 3 (Mike Lafranzo). * * * UPDATE ON 10/21/04 @ 1246 BY ED WROBLEWSKI TO CHAUNCEY GOULD * * * The following text is an updated corrected version of the above initial report which was submitted by the licensee after consulting with Region 3. On 10/11/04 a 49 year old female patient received what was to be the first of two High Dose Rate (HDR) treatments for endometrial cancer using a remote afterloading unit. The physician planned two fractions of 350 cGy for a total of 700 cGy at 0.5 cm from the GYN cylinder (2.0cm) wall using a 7 Ci Ir-192 source. The GYN cylinder is connected to the HDR unit using a 1500 mm transfer tube. A treatment of 189 seconds with an active length of 5 cm was to be treated with an indexer position of 1500 mm. Due to an error on the part of the medical physicist, an indexer length of 995 was programmed into the treatment unit. This resulted in the source not entering the patient. The source remained positioned in the transfer tube for the treatment duration at an estimated distance of 35-50 cm from the patient's skin. This resulted in a calculated dose between 1.4 - 4.3 R to the patient's skin. There are no expected adverse consequences. Notified Reg 3 RDO (Julio Lara) and NMSS EO (Sandra Wastler) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-10-19
41132 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-08-22 04:50 | 2004-10-19 08:50 | 2004-10-19 | 60 DAY REPORT - INVALID ACTUATION OF SPECIFIED SYSTEM "This 60-day optional report as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10 CFR 50.73(a)(2)(iv)(A) to describe an invalid actuation of a specified system, specifically the Nuclear Service Water System (NSWS). "During TSM 158 work associated with W/O 98686671 a SPOC Relief Supervisor inadvertently caused a ground when disconnecting test meter leads from an energized circuit. This ground resulted in an unplanned RN [Nuclear Service Water] swap to the SNSWP [Standby Nuclear Service Water System]. "At 0450 on 8/22/04, a lo-lo level signal was received for B Train RN Pit and this initiated a swap to the SNSWP for both A and B trains. Prior to this event, both trains of RN had been aligned to the SNSWP on 8/16/04 for maintenance, and remained on the SNSWP due to 1RN-4B degraded condition (PIP C-04-3937) "The lo-lo level signal did initiate a start of all four RN Pumps (1B and 2B started; 1A and 2A were already operating). RN crossover valves 1RN-53B and 1RN 54A closed as expected, separating RN trains A and B. Flow was manually initiated through all four NS Heat Exchangers to attempt to meet RN pump minimum flow demands. This was a complete actuation for Train B and the system performed as designed for existing plant conditions. This event was entered into the site corrective action program for resolution (PIP C04-04056). "At 1629 on 8/22/04, a lo-lo level signal was received for B Train RN Pit and this initiated a swap to the SNSWP for both A and B trains. Prior to this event, both trains of RN had been aligned to the SNSWP on 8/16/04 for maintenance, and remained on the SNSWP due to 1RN-4B degraded condition (PIP C-04-3937). RN system response was as expected. The lo-lo level signal did initiate a start of all four RN Pumps (1B and 2A started; 1A and 2B were already operating). RN crossover valves 1RN-47A and 2RN-47A closed as expected, and return header isolation valves 1RN-53B and 1RN-54A closed as expected, separating RN trains A and B. "Flow was manually initiated through all four NS heat exchangers to attempt to meet RN pump minimum flow demands. The reasons for the inadvertent actuation was a blown fuse. Performed Troubleshooting Plan to I/R Cause of Fuse HA-1 in 1EATC6 blowing under W/O #98686856-01 and 03. No cause for the fuse blowing on 2004-08-22 could be found. All data obtained under the plan were well within normal values. "Thermography data indicate the fuse temperature was about 3 Deg F above ambient. The current through the fuse is 1.3 Amps. (Fuse HA-1 is a FLQ-3) Current alarm HF in 1EATC6 was calibrated, and was found in tolerance. No change in current through the fuse was noted during the calibration of the current alarm. The current alarm was cycled 5 times. "This was a complete actuation for Train B and the system performed as designed for the existing plant conditions. This event has been entered into the site specific corrective action program for resolution. (C04-4060)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-10-19
41131 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2004-10-18 18:15 | 2004-10-18 21:53 | 2004-10-18 | OFFSITE NOTIFICATION DUE TO RAW SEWAGE SPILL "On 10/18/04 at 1815 EDT, a spill of untreated raw sewage from a damaged sewage pipe from the Site Management Building occurred. The sewage entered a storm drain and was therefore released to the Susquehanna river. SE-6, 'Pollution Incident Protection Procedure', was entered. The quantity of the spill is estimated at less than 200 gallons and the duration was approximately 1 hour. Per SE-6, the following were contacted: National Response Center, PA Department of Environmental Protection Region III, MD Department of the Environment. Downstream users are in the process of being informed of the spill. The storm drain path to the river has been covered, absorbent pads are being used to collect the spillage, and the damaged sewage piping is being temporarily repaired." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-18
41130 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-10-18 14:30 | 2004-10-18 17:35 | 2004-10-18 | UNACCOUNTED FOR SPECIAL NUCLEAR MATERIAL "In 1991, four unirradiated nuclear instrumentation (NI) detectors (includes detector, cable, and connector) were identified as being damaged. These four NI detectors were dispositioned by cutting the detectors from the cable and placing these detectors in a small Special Nuclear Material (SNM) container which then had tamper seals applied. The remaining cables and connectors were disposed of as trash. On October 6, 2004, the small SNM container was moved from its normal storage location to another plant location in preparation for disposal and was opened to verify the contents on October 7, 2004. The actual contents of the container were three NI connectors (not detectors) and one NI detector. Therefore, three NI detectors containing SNM were identified as unaccounted for. "The contents of this SNM container have been periodically inventoried since 1991 verifying that the tamper seals are intact in accordance with the site SNM inventory procedure, and in March 2004, a periodic SNM inventory was performed in accordance with Exelon SNM inventory procedure. As allowed by the Exelon SNM inventory procedure, however, the contents of the small SNM container were not inspected since the tamper seals were intact. A search of the normal NI detector storage location was performed and it was verified that the unaccounted for detectors were not in another container. "The other NI detectors in the storage area were accounted for by performing a serial number inventory. Only the three NI detectors missing from the small SNM container are unaccounted for. The total mass of U235 in the unaccounted for SNM was much less than one gram. The actual total mass was determined to be approximately 6 milligrams. It has been determined that the U235 activity of the unaccounted for SNM was greater than 10 times the activity listed in 10CFR20, Appendix C. The actual U235 activity was determined to be 0.012 microcuries, which exceeds 10 times the Part 20 Appendix C activity (i.e., 0.010 microcuries). Therefore, this loss of SNM is reportable in accordance with the requirements of 10 CFR 20.2201(a)(1)(ii). Both the NRC Resident and IEMA Resident were notified. "CPS records are being reviewed to determine the actual disposition of the NI cables that were disposed of in 1991." | 91 | 0 | 0 | 91 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN LNM>10X |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-10-18
41129 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2004-10-18 07:41 | 2004-10-18 15:07 | 2004-10-18 | UNPLANNED EMERGENCY DIESEL START "At 0741 [EDT], an unplanned actuation of an ESF system occurred due to the unplanned start and loading of the 'A' Emergency Diesel Generator (EDG). The plant was in a refueling outage in Mode 5 with the Reactor Coolant System (RCS) depressurized. The 'B' Emergency Safety Bus was operable and protected. The 'A' EDG started when the feeder breaker to the 'A' train Emergency Safety Bus opened unexpectedly, de-energizing the bus. The 'A' Emergency Diesel Generator (EDG) started and re-energized the bus as designed, and the 'A' Safeguard Sequencer initiated loading of the bus. Two anomalies occurred during re-energization of the 'A' emergency bus loads. Bus 1A3-SA, which provides power to various safety related load centers and supplies support system loads, did not re-energize. Additionally, the 'A' Emergency Service Water (ESW) pump did not start. The cause of the initial bus feeder breaker opening, and the cause of the subsequent equipment failures is under investigation. Bus 1A3-SA was manually re-energized at 1029. The 'A' ESW pump was manually restarted at 1054." The 'A' EDG cooling water was provided by the service water system which was not affected by the trip. The 'A' RHR pump was in service to provide Shutdown cooling and the pump tripped when the 'A' Train Emergency Safety Bus was deenergized. Reactor plant temperature rose from 116 to 122 degrees F in the four minute period prior to the restart of the 'A' RHR pump. 'A' RHR pump was restarted at 0745, and 'B' RHR pump was started at 0843 as a backup. Shutdown cooling was transferred to the 'B' Shutdown cooling loop at 1343 and the 'A' RHR pump was secured. The licensee notified the NRC Resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-10-18
41128 | -1 | PALISADES | 1 |  |  | [1] CE | 2004-10-16 17:30 | 2004-10-17 01:03 | 2014-11-19 | REACTOR VESSEL HEAD NOZZLE CRACKING "On 10/16/04, with the Plant in Mode 6, Nuclear Management Company identified through wall cracks in the inconel buttering adjacent to the J-weld on reactor head penetrations 29 and 30. Ultrasonic examinations of the reactor vessel head were being performed in accordance with the First Revised Order, EA-03-009. The ultrasonic examinations identified leak path detection indications. Therefore, in accordance with the Order, a bare metal visual inspection of the exterior of the reactor head was performed. No evidence of leakage was discovered. A dye-penetrant examination was then performed. The dye-penetrant exam showed minor surface indications that required further examination. Following minor excavation of the weld surface, the through wall cracks were identified. "This condition was determined to be reportable at 1730 EST for penetration 30, and at 1915 EST for penetration 29. "This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A). "Reactor head penetrations 29 and 30 will be repaired prior to placing the reactor vessel head back in service. "The licensee notified the NRC Resident Inspector." * * * RETRACTION ON 11/19/14 AT 1434 EST FROM TERRY DAVIS TO DONG PARK * * * "On October 17, 2004, Nuclear Management Company notified the NRC, via non-emergency event report 41128 that leak path detection indications had been identified in two reactor pressure vessel head control rod drive mechanism nozzle penetrations at Palisades. At that time, the probable cause of the identified indications was believed to be primary water stress corrosion cracking (PWSCC). As a result, event report 41128 was made in accordance with 10 CFR 50.72(b)(3)(ii)(A) as a condition that resulted in a principle safety barrier being seriously degraded. "Based on a recently completed engineering evaluation that compared the indications found in 2004 to the indications identified in subsequent examinations, it was determined the indications originally discovered in 2004 were embedded welding indications, caused by the original welding process. "Since the indications identified in 2004 were not caused by PWSCC, serious degradation of a principle safety barrier did not exist. Consequently, the reporting criterion of 10 CFR 50.72(b)(3)(ii)(A) is not applicable. Therefore, event report 41128 is being retracted. In addition, Palisades Licensee Event Report (LER), 2004-002, 'Leak Path Indications Identified in Reactor Pressure Vessel Head Nozzle Penetrations,' is being cancelled." The licensee has notified the NRC Resident Inspector. Notified R3DO (Peterson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-10-17
41127 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-10-15 22:15 | 2004-10-16 00:57 | 2004-10-16 | SPURIOUS ACTUATION OF ONE OFF-SITE EMERGENCY PLAN SIREN "At 2215 [CDT] on 10/15/04, the Prairie Island Control Room was notified by the Pierce County Sheriff's Department of a spurious actuation of one EP siren. The siren is located near Highway 63 and County KK. The siren was de-activated by the Pierce County Sheriff personnel. "There is no event in progress and no risk to the health and safety of the public. Members of the public notified the sheriff's department of the malfunctioning siren. "The siren remains de-activated, is the only non-functional siren, and is expected to be repaired by Nelson Communication on 10/16/04. No further actions are required." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 0235 ON 10/16/04 FROM D. SMITH TO M. RIPLEY * * * "At 0100 on 10/16/04, the same EP siren spuriously re-actuated. The siren was again de-activated by Pierce County Sheriff's personnel. The repair company, Nelson Communication, also dispatched an individual to verify the siren was properly deactivated to preclude additional spurious actuations." The licensee will notify the NRC Resident Inspector. Notified R3DO ( R. Lanksbury) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-16
41126 | 0 | XENOGEN BIOSCIENCES |  |  |  |  | 2004-10-05 | 2004-10-15 15:16 | 2004-10-15 | MISSING LICENSED MATERIAL Summary of email report provided by licensee: On 10/01/04, one vial of 1000 microcuries of Redivue (deoxycytidine 5-Triphosphate (Dctp)) was received by licensee. Concentration indicated on the vial was 10 microcuries per microliter. This material contains the radioisotope of Phosphorous 32 (P-32). Per procedure, the project leader verified that there was 90 microliters (900 microcuries) of material in the vial by pipette after delivery receipt. The project leader did notice that there was some material on the lip of the container and also on the plug that seals the vial, but this amount was not able to be quantified. On 10/05/04, the last intended use of the vial, the project leader intended to withdraw 100 microcuries when inventory records indicated that 150 microcuries should have been available. The project leader was only able to retrieve 50 microcuries (5 microliters). Both discrepancies noted above indicate a potential loss of 200 microcuries of P-32. It is believed that the original discrepancy of 100 microcuries was present in the vial but distributed around the lip and sides of the vial. The second discrepancy of 100 microcuries discovered on 10/05/04 is believed to be the result of excess material sticking to the tip of the pipette or when setting the volume of the pipette. There is no evidence of intentional removal of material from the vial or use of material without the activity being logged in the isotope inventory log. There was no indication of any contamination via the weekly swipe analysis and a survey of the laboratory area. Other sections of the building show no indication of contamination or individuals being exposed to radiation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-10-15
41125 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-10-15 | 2004-10-15 12:21 | 2004-10-15 | AGREEMENT STATE - STOLEN RADIOACTIVE SOURCES State of Florida Bureau of Radiation Control reported that licensee notified their agency of 3 missing Germanium 68 sources from their General Electric PET CT Hybrid Imaging device. The sources were discovered missing on 10/15/04. It has not been determined when the sources were last known to be in the possession of the licensee. The sources were model number B3-693, serial Number 1004-09, 4.3 millicuries; model number B2-125, serial number 1004-02, 4.3 millicuries; model number A9-313, serial number 973-87, 0.58 millicuries. Specific activity of sources is corrected for decay as of 10/15/04. The Naples Police Department is investigating the possible theft. The Florida Bureau of Radiation Control also notified the Regional Terrorism Task Force in Fort Myers and the Florida State Warning Point. Florida Incident # 04-137. * * * UPDATE PROVIDED BY JERRY EAKINS TO JEFF ROTTON @ 1515 EDT ON 10/15/04 * * * Florida Bureau of Radiation Control investigator found the sources on the licensee premises. The sources had been placed under the cushion of a supervisor's chair. Naples Police Department is continuing their investigation into any potential criminal activity. The estimated exposure to the supervisor was 60 mR based on 4 hours of exposure. Notified the R1DO (McDermott) and NMSS EO (Essig) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-10-20
41124 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-10-01 | 2004-10-15 11:08 | 2004-10-15 | AGREEMENT STATE - MEDICAL EVENT "This incident took place on October 1, 2004. A patient from Room 5206 was administered 20 millicuries of Xe-133 gas resulting in a lung dose of 0.22 Rad and an Effective Dose Equivalent of 0.028 Rad. It was then found that the orders were written for a patient in Room 5213. The order form had the wrong patient name sticker attached. The nursing station supervisor stated that they had noticed incorrect patient name stickers in the Room 5213 patient chart. It is not known how these stickers and chart orders were switched. The patient was notified of the error and the correct patient later received the Xenon scan." Event Report: LA040012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-10-20
41123 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-09-29 12:00 | 2004-10-15 09:45 | 2004-10-15 | TEXAS AGREEMENT STATE EVENT REPORT - LEAKING SOURCE "The Licensee notified the Agency of a leaking source that was discovered on September 29, 2004 and confirmed by a second leak test on September 30, 2004. The source was for a Lagus Applied Technology, Inc. Model 101 AUTOTRAC Tracer Gas Monitor (SF6), Serial No. 177. The source was described as a Model 200-EC Electron Capture Detector, Serial No. 1271 with an activity of 300 millicuries, Tritium (3H) (October 3, 1998). The current activity is an estimated 214 millicuries. The leak test detected 18,178 dpm or 0.0082 microcuries of removable activity. The second leak test conducted September 30, 2004, confirmed the source was leaking with similar results. The gas monitor was taken out of service. After removing the SF6 compressed gas bottle, the monitor containing the leaking source was packaged for return to the manufacturer. The packaged source was shipped to the manufacturer on October 6, 2004. No violations were cited." Texas Incident No: I-8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-10-20
41121 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-10-14 16:10 | 2004-10-14 18:48 | 2004-10-14 | OFFSITE NOTIFICATION FOR EXCEEDING STATE PERMIT LIMITS "At 1610 EDT on 10/14/04, Florida Power and Light Company notified the Florida Department of Environmental Protection (FDEP) that St. Lucie Station exceeded a permit allowance limitation for operating time on one of the station's administrative office building emergency diesel generators. FDEP notification was required per the general conditions of the permit. The permit allows 200 hours of run time per year. This particular generator logged 222.9 hours of run time in September 2004. The additional usage was directly related to Hurricane Frances and Jeanne. This particular generator was used to supply the South Service Building with electricity during the two hurricanes. The South Service Building housed plant support staff during the hurricanes. "This non-emergency notification is being made pursuant to 10CFR50.72(b)(2)(xi) due to FDEP notification." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-14
41120 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-10-14 13:44 | 2004-10-14 15:52 | 2004-10-14 | OFFSITE MEDICAL At 1330 EDT on 10/14/04, the control room was notified that a worker in the Containment Building had a potential neck injury. An ambulance was requested to transport the worker. The individual was taken directly from the Containment building to the ambulance and a HP Technician with a radiation detector accompanied the individual to the hospital. A contamination survey was not completed on site. At 1344, the HP Tech and worker left the site for the hospital. The Shift Manager contacted the hospital to alert them of the potential for contamination on the injured person. At 1430, HP Technician confirmed that there was no contamination present. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Refueling Shutdown; FMode1: Refueling Shutdown | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-10-14
41119 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2004-09-10 17:30 | 2004-10-14 14:40 | 2004-10-14 | INVALID ACTUATION OF STEAM DRIVEN AUXILIARY FEEDWATER PUMP "On September 10, 2004 at 1730 hours, one steam supply isolation valve (TV-1MS-105B) to the steam-driven Auxiliary Feedwater System Pump (FW-P-2) unexpectedly opened at Beaver Valley Power Station Unit No. 1, causing this pump to commence feeding all three steam generators. FW-P-2 functioned as designed with steam being supplied to the pump's steam-drive turbine. Neither of the other two Auxiliary Feedwater System motor-driven pumps were actuated at Beaver Valley Power Station Unit No. 1. This initially caused Steam Generator Water Level Deviations alarms on all three steam generators. The steam generator levels returned to their normal operating levels via the automatic level control system. After determining that there was no demand for this Auxiliary Feedwater System pump to be operating, the control room crew attempted to close TV-1MS-105B from the control room, without success. The upstream motor-operated isolation valve (MOV-1MS-105) to TV-1MS-105B was then closed to stop steam flow to FW-P-2, terminating the auxiliary feedwater flow to the steam generators. "No maintenance or tests were ongoing with the Auxiliary Feedwater System at the time. Subsequent investigation determined that this event occurred due to a failure of an instrument card within the Solid State Protection System which caused TV-1MS-105B to inappropriately open. Therefore this actuation was not initiated by a valid actuation signal. "This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) since it involved an actuation of a PWR auxiliary feedwater water system train as per 10 CFR 50.73(a)(2)(iv)(B)(6). This pump start was not part of a pre-planned sequence and did not occur with this system properly removed from service. "However, pursuant to 10 CFR 50.73(a)(1), this event is being reported via this telephone notification instead of submitting a written Licensee Event Report since the automatic actuation of the Auxiliary Feedwater System pump was not generated by a valid actuation." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-10-14
41118 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-13 15:41 | 2004-10-13 19:14 | 2004-10-13 | REACTOR COOLANT LEAKAGE OUTSIDE CONTAINMENT EXCEEDING FINAL SAFETY ANALYSIS LIMITS "This is all 8 hour notification being made to report exceeding the design basis for the reactor coolant leakage outside of containment. The event is being reported under paragraph (b)(3)(v) of 10 CFR 50.72. "On 10/13/04 at 1541, the control room was notified that tight system isolation boundaries could not be achieved on the 23 Charging pump [positive displacement pump]. The pump was tagged to support maintenance. Although the leak rate has not been quantified, it is suspected that it was greater than the UFSAR limit for ECCS leakage outside containment. "With leakage greater than the UFSAR allowed limits (greater than 3840 cc/hr), GDC-19 limits for control room habitability cannot be assured. "Actions have been completed to restore system integrity. The affected positive displacement charging pump is not a safety related pump and is not required for accident mitigation; however it is exposed to the ECCS recirculation flow path during the cold leg injection phase of the accident mitigation. "The licensee has notified the NRC Resident Inspector of this event. The local township will also be notified." The licensee stated that the leakage has been isolated; there was no indication of an increase in radiation levels during the leakage; and that the duration of the leakage was approximately 3 hours. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-13
41117 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-10-12 19:34 | 2004-10-12 19:45 | 2004-10-12 | DISCOVERY OF AFTER-THE-FACT EMERGENCY CONDITION (UNUSUAL EVENT) "During a review of post trip activities associated with MANUAL REACTOR SCRAM DUE TO A STEAM LEAK IN THE TURBINE BUILDING (Event 41110) on 10/10/04, it was determined that Technical Specifications actions requirements were inappropriately applied. With both loops of RHR in suppression pool cooling (necessary with SRV's controlling reactor pressure), procedural guidance requires that the affected loop of RHR be declared inoperable when in a secondary mode of operation. With both loops of RHR thus inoperable, the applicable Technical Specification Action TS 3.6.2.3 Action b requires that the plant be in at least HOT SHUTDOWN within 12 hours and in COLD SHUTDOWN within the next 24 hours. "In accordance with the Technical Specification, this action was entered on 10/10/04 at 1831. The required time to cold shutdown was incorrectly noted as 0631 on 10/12/04. The required time was based on the combination of the 12 hours to hot shutdown and 24 to cold shutdown (or 36 hours). Because the plant was already in hot shutdown, the action should have been to place the plant in cold shutdown within 24 hours or by 1831 on 10/11/04. "As a result of this error, planning activities and cooldown to cold shutdown condition was predicated on a target time of 0631 on 10/12/04 resulting in the plant exceeding the 24 hour AOT. This constitutes a condition prohibited by Technical Specifications. The plant achieved cold shutdown on 10/12/04 at 0509 hours. "In addition, Emergency Classification Guide (ECG) Initiating Condition 8.5 states that the inability to reach required operational condition within Technical Specification Limits and requires the declaration of an Unusual Event if the plant is not brought to the required Operational Condition within the Technical Specification required time limit. "There are no safety consequences associated with this error. There were no issues associated with the transition to cold shutdown that would have constituted an emergency condition requiring initiation of the Emergency Plan. The missed LCO and subsequent classification was based on an erroneous TS Action time and, as such, exceeding the specification occurred as a result of scheduling not plant conditions." The licensee will inform the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2004-10-12
41114 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2004-10-11 10:57 | 2004-10-11 13:51 | 2004-10-11 | LOSS OF EMERGENCY SIREN CAPABILITY FOLLOWING PLANNED SIREN MAINTENANCE "On October 11, 2004, at 1057 [hrs. EDT] , while performing modification work to support security upgrades, the radio system controller that activates the plant offsite warning system was removed from service during a pre-planned activity. At 1148, the system was rebooted but failed to perform correctly. Approximately 70 % of the sirens were communicating with the system, while plant procedures direct that less than 75 % of the offsite warning system meets the reporting threshold. At 1226, the offsite warning system capability was restored to greater than 75%. "Since the removal of the offsite notification network from service was a planned evolution, the county, state and the NRC resident inspector were notified prior to the removal from service. Appropriate compensatory measures were taken by the state and local agencies. "The cause of the event was the new Federal Signal activation frequency not reloading after the outage since it was not hard-coded into the software for the radio system controller. This caused all 27 of the Federal Signal sirens from being activated. Three other sirens had pre-existing conditions which made 30 sirens inoperable out of a total of 106. "The correct information was loaded into the software via modem and a silent siren test confirmed 93% capability at 1226. The frequency information was hard coded into the software to prevent future occurrences." The licensee notified state/local agencies and the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-10-11
41113 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2004-10-11 07:25 | 2004-10-11 13:35 | 2004-10-11 | LOSS OF SWITCHYARD WEST BUS "On 10/11/2004 at 0725 CDT, Wolf Creek Generating Station experienced a loss of the west bus in the switchyard causing a loss of power to the Startup Transformer and the 'B' Train 4.16 Kv ESFAS bus NB02. The 'B' Emergency Diesel Generator started and loaded, as expected, to supply power to the NB02 bus. The shutdown sequencer started the required components. Turbine load was reduced by the control room staff following the expected start of the steam driven auxiliary feedwater pump to maintain reactor thermal power below license limits. "Following the shutdown sequencer start of the 'B' Essential Service Water (ESW) pump it was noted the 'B' Control Room Air Conditioning unit condenser inlet end bell gasket had started leaking. The Control Room Air Conditioning unit was secured and ESW was isolated to and from the unit. All other equipment operated as required. "System Operations and Site personnel are investigating the cause of the power loss to the west switchyard bus, no cause has been identified at this time. Turbine load is being reduced to 950 MWe net per System Operations request to ensure grid stability is maintained. "The Senior Resident has been contacted concerning this issue." The licensee intends to reduce reactor power to 78-80% while investigating the cause for the loss of the west bus. There is no indication of any malevolent intent involved. The "B" EDG will maintain loads on the NB02 bus. | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-10-11
41111 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-10-11 00:20 | 2004-10-11 07:16 | 2004-10-11 | CONTAINMENT VENTILATION ISOLATION SYSTEM INOPERABLE DURING FUEL MOVEMENT The following information was obtained from the licensee via facsimile: "In accordance with 10 CFR 50.72(b)(3)(v)(D) ['Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident'], D.C. Cook Unit 2 is making an 8-hour non-emergency report. "At 00:20 [EDT] on 10-11-2004, it was discovered that neither train of the Containment Ventilation Isolation System would have automatically isolated containment purge on a high radiation signal within the containment. Also, a manual Phase A containment isolation actuation would not have isolated containment purge. "At all times, containment purge could have been isolated using individual control switches from the Unit 2 Control Room. "D.C. Cook Unit 2 Technical Specification 3.9.9 requires during core alterations or movement of irradiated fuel within the Containment that the Containment Purge and Exhaust Isolation System be operable. Technical Specification 3.9.4.c requires during core alterations or movement of irradiated fuel within the containment that each containment penetration providing direct access from the containment atmosphere to the outside atmosphere be closed by an isolation valve, blind flange, manual valve, or equivalent, OR be capable of being closed by an operable automatic Containment Purge and Exhaust isolation valve. "Technical Specification 3.0.4 requires when a Limited Condition of Operation is not met, entry into an operational mode or other specified condition in the applicability shall be made only in specified conditions. Core alterations and movement of irradiated fuel assemblies began at 14:41 on 10-09-2004, approximately 71 minutes after the Containment Ventilation Isolation System had been made inoperable. "At approximately 13:30 on 10-09-2004, breaker 2-CRID-1-7 (Reactor Protection and Safeguards Actuation Cabinet RPS-A Input Channel I & All RPS A Output) and 2-GRID-4-8 (Reactor Protection & Safeguards Actuation Cabinet RPS-B Input Channel IV & ALL RPS B) were opened and tagged as part of a clearance. This prevented the automatic actuation of both trains of the Containment Ventilation Isolation System and prevented a manual phase A containment isolation from isolating containment purge. Thereafter, at 14:41 on 10-09-04, fuel movement commenced from the reactor vessel to the Spent Fuel Pit. "At 23:25 on 10-10-2004, breakers 2-CRID-1-7 and 2-CRID-4-8 were re-closed. "At 0020 on 10-11-2004, it was discovered that during the time from approximately 13:30 on 10-09-2004 to 23:25 on 10-10-2004, the Containment Ventilation isolation system had been inoperable. "D.C. Cook Unit 2 is currently stable in Mode 6 during the Unit 2 Cycle 15 refueling outage with core offload to the Spent Fuel Pit in progress." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-11
41110 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-10-10 21:53 | 2004-10-11 00:49 | 2004-10-11 | A RPS ACTUATION SIGNAL OCCURRED DUE TO LOW REACTOR WATER LEVEL WHILE IN MODE 3 At 2153 [hrs. EDT] on October 10, 2004, the Hope Creek Generating Station experienced an automatic reactor scram signal on low reactor level +12.5 inches (Level 3) while cooling down following a manual scram. As previously reported under Event Notification 41109, the Main Steam Isolation Valves (MSIV's) were closed as the result of a steam leak in the Turbine Building. The +12.5 inch (Level 3) scram occurred from the manual closure of a Safety Relief Valve (SRV) while it was being manually operated to reduce reactor pressure. The SRV was closed when reactor level was +24 inches, resulting in a reactor level shrink. Reactor level lowered to +8 inches, and stabilized. The secondary condensate pumps immediately restored reactor level to its normal band following the scram signal. SRV's were being utilized to assist the plant cool down because the High Pressure Coolant Injection (HPCI) system had been manually taken out of service. The HPCI vacuum tank vacuum pump tripped on an overload/power failure condition, and use was not desired. The Reactor Core Isolation Cooling (RCIC) system was out of service because of a high reactor level condition, due to plant cool down. Also, the Reactor Water Cleanup (RWCU) system was out of service due to the initial manual scram that occurred at 1814 hours which prevented normal reactor level blow down. The NRC Resident Inspector was notified and Lower Alloway Creek Township will be notified. HOO note: See Event # 41109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-10-11
41109 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-10-10 18:14 | 2004-10-10 21:48 | 2004-10-11 | MANUAL REACTOR SCRAM DUE TO A STEAM LEAK IN THE TURBINE BUILDING "At 1814 [hrs. EDT] on October 10, 2004, Hope Creek Generating Station was manually scrammed due to a steam leak in the Turbine Building. All Control Rods inserted fully. Subsequent to the manual actuation of the Reactor Protection System, reactor pressure was reduced to minimize the effects of the steam leak. Degrading Main Condenser Vacuum following the scram resulted in trips of all operating Reactor Feed Pump Turbines at 10 [inches] HgA. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) Systems were manually initiated for reactor level control and the Main Steam Isolation Valves (MSIV's) were closed to isolate the leak - MSIV closure was completed prior to reaching the Main Condenser Vacuum isolation setpoint of 21.5 [inches] HgA. During plant stabilization, Reactor Water Level lowered below the RPS actuation setpoint of 12.5 inches four separate times. First, following the initial scram. Second, immediately following initiation of the HPCI and RCIC systems, when the 'A' and 'B' Reactor Water Level channels lowered to -38 inches (Level 2). Level 2 is the HPCI and RCIC actuation setpoint and Primary Containment Isolation actuation setpoint for Groups 2, 7, 8, 9, 12, 13, 14, 17, 18, 19, and 20 valves. Because only two of the four Level 2 instrument channels actuated, the isolation of these systems was channel dependent and occurred as required by the respective isolation logic. Third, following manual closure of the MSIVs. Finally, Reactor Water Level lowered below 12.5 inches following reset of the original manual scram signal which resulted in an automatic scram signal. RCIC was re-initiated manually to restore Reactor Water Level. "No personnel were injured during this event. The plant is currently stable in OPCON 3 with reactor pressure at 615 psig. Pressure control (decay heat removal) was transitioned to HPCI in pressure control mode during plant stabilization. Reactor Water Level is being maintained with the Secondary Condensate Pumps. Two loops of RHR in Suppression Pool Cooling mode are in service with Suppression Pool Temperature at 110 degrees F in compliance with Technical Specification 3.6.2.1 Action b.2. Actions to determine the cause of the steam leak and effect repairs are in progress." The licensee will inform Lower Alloway Creek Township and has informed the NRC resident inspector. * * * UPDATE ON 10/11/04 @ 0049 HRS EDT BY BAUER TO GOULD * * * On steam leak investigation, a walk down of the turbine building condenser bay determined the source of the leak to be a failure of an 8 inch moisture separator dump line. The line break is located approximately one foot from the condenser shell penetration. An additional investigation into the root cause of the failure has commenced. The NRC Resident Inspector was notified and Lower Alloway Creek Township will be notified. The Reg 1 RDO (Richard Barkley) and EO (Chris Grimes) were informed. HOO Note: See Event # 41110 | 0 | 0 | 0 | 69 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2004-10-10
41108 | -1 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-10-09 19:45 | 2004-10-10 00:51 | 2004-11-18 | REACTOR BUILDING PRESSURE DECREASED BELOW SPECIFIED LIMITS The following information was obtained from the licensee via facsimile: "On October 9, 2004 at 1945 hrs. EST, Operators discovered that Oconee Nuclear Station Unit 3 Reactor Building pressure decreased to less than the limit specified in Oconee Selected Licensee Commitment 16.6.13, 'Additional Requirements to Support Low Pressure Injection (LPI) Operability'. This initial Reactor Building Pressure is used in the NPSH Analysis for the LPI Pumps in the Sump Recirculation phase of post-LOCA operation. In addition to effecting LPl, this condition also affects the Reactor Building Spray system. Engineering Evaluation performed on May 25, 2004 identified that guidance contained within the Selected Licensee Commitment may be inadequate and as a result, the Reactor Building Spray and Low Pressure Injection systems were determined to be Operable But Degraded/Nonconforming. For the interim, until appropriate changes are made to the Selected Licensee Commitment, Engineering recommended that Oconee Operations enter Technical Specification 3.0.3 any time that the limits of Selected Licensee Commitment 16.6.13 are exceeded. "At the time of discovery, Oconee Unit 3 was cooling down for refueling outage. Unit 3 was in Mode 4 at approximately 235 degrees, 275 psig with one train of Reactor Building Spray deactivated per the Controlling Procedure for Unit Shutdown. When it was identified that the limits of Selected Licensee Commitment 16.6.13 were exceeded, Operations began increasing Oconee Unit 3 Reactor Building pressure. Oconee Unit 3 Reactor Building pressure was restored to within the limits of Selected Licensee Commitment 16.6.13 on October 9, 2004 at 2023 hrs. EST. "Initial Safety Significance: "The NPSH analysis for the Low Pressure Injection pumps in the sump recirculation phase of post-LOCA operation credit reactor building overpressure of 2.2 psig as permitted by a license amendment granted July 19, 1999 and supplemented August 19, 1999. Operation with Reactor Building pressure less than the limits specified in Selected Licensee Commitment 16.6.13 cannot ensure that 2.2 psig overpressure will always be available. "Corrective Action(s): "Actions were taken by Operations to restore Unit 3 Reactor Building pressure to within the limits of Selected Licensee Commitment 16.6.13. These actions were successful in restoring Reactor Building Pressure to within limits of Selected Licensee Commitment 16.6.13 approximately 38 minutes from time of discovery." The licensee has informed the NRC Resident Inspector. * * * UPDATE 1849 EST ON 11/18/04 FROM R.P. TODD TO HOWIE CROUCH * * * This report is retracted based on the following: "Event: Withdrawal of Event Number 41108 "On October 9, 2004 at 1945 hrs. EST, Operators discovered that Oconee Nuclear Station Unit 3 Reactor Building (RB) pressure decreased to less than the limit specified in Oconee Selected Licensee Commitment (SLC) 16.6.13, 'Additional Requirements to Support Low Pressure Injection (LPI) Operability'. This initial RB Pressure (Containment overpressure) is credited in the NPSH Analysis for the LPI and RB Spray Pumps in the Sump Recirculation phase of post-LOCA operation. Engineering recommended that Oconee Operations enter Technical Specification 3.0.3 any time that the limits of SLC 16.6.13 are exceeded. Operations exited the condition after taking actions which raised RB pressure within the SLC limit. The ENS was reported as a loss of safety function under 50.72(b)(3)(v)(D) - ACCIDENT MITIGATION. "Justification for conclusion that there was no loss of safety functions: "An engineering analysis determined that, at the time of this event, the worst case post-LOCA RB sump temperature would be approximately 170F. From a July 19, 1999 SER for the license amendment which credited containment overpressure, the NRC Staff concurred that containment overpressure credit was only needed for sump temperatures above 208F. Therefore, for the conditions which existed during this event, there was adequate NPSH, and no reportable loss of safety function existed." The licensee informed the NRC Resident Inspector. Notified R2DO (Tom Decker). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode3: Hot Shutdown; FMode3: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-10
41107 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2004-10-09 01:15 | 2004-10-09 05:13 | 2004-10-09 | HIGH PRESSURE COOLANT INJECTION SYSTEM CONDENSATE STORAGE TANK SUCTION VALVE FAILED TO AUTO-CLOSE DURING SURVEILLANCE The following information was obtained from the licensee via facsimile: "During the performance of scheduled instrument surveillance testing it was discovered that the Unit 3 High Pressure Coolant Injection (HPCI) pump suction valve from the Condensate Storage Tank (CST) would not automatically close. This valve is designed to automatically close when both Torus suction valves are fully open. The CST suction valve is required to close to support operability of the HPCI System. The CST suction valve was subsequently closed with the Torus suction valves open to allow performance of the HPCI instrumentation testing. After the completion of scheduled instrumentation testing, the HPCI system will be restored to an operable status with pump suction remaining from the Torus and isolated from the CST. The failure of the CST suction valve to auto close is being investigated." The licensee has informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-09
41106 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2004-10-08 21:20 | 2004-10-08 22:58 | 2004-10-08 | CONTOL ROOM EMERGENCY VENTILATION SYSTEM DECLARED INOPERABLE "At 2120 [hrs. CDT] on October 8, 2004, while performing the 'Control Room Emergency Ventilation System Test,' which verifies the integrity of the control room envelope, it was determined that the positive pressure requirement of greater than or equal to 0.125 inches water gauge for the control room envelope in Technical Specification Surveillance Requirement 3.7.4.4 could not be met for all specified test points. As a result, Control Room Emergency Ventilation System was declared inoperable and Technical Specification 3.7.4, Condition A was entered. "Recently completed surveillance testing has demonstrated that a positive pressure ranging from 0.056 to 0.301 inches water gauge is being maintained in the control room envelope; therefore it is expected that the safety function is being met. "However, this notification is being made in accordance with 10 CFR 50.72(b)(3)(v)(D) because the Control Room Emergency Ventilation System is a single train safety system and the Technical Specification requirement is not met. The affect of the failure to meet the Technical Specification requirements on the ability to perform the safety function is continuing to be evaluated." The licensee notified the NRC resident inspector. | 85 | 85 | 0 | 85 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-08
41105 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2004-10-08 14:10 | 2004-10-08 15:38 | 2004-10-08 | OFFISTE NOTIFICATION TO FIRE DEPARTMENT DUE TO NATURAL GAS LINE BREAK A natural gas pipeline was broken by a backhoe while digging at a location between 300 to 400 feet outside the protected area fence southwest of the plant. The licensee made offsite notifications to local fire departments and Rochester Gas and Electric which have responded to the scene and are in the process of isolating the line break. The broken gas line is 2.5 inches in diameter and the licensee does not consider the break a threat to the plant and will continue normal operation. The licensee is monitoring the situation and is monitoring for excessive natural gas concentrations. The licensee has notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-08
41104 | 0 | NORTH ANNA | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2004-10-08 13:55 | 2004-10-08 14:14 | 2004-10-08 | UNUSUAL EVENT DUE TO ACTUATION OF CARBON DIOXIDE FIRE SUPPRESSION SYSTEM IN TURBINE BUILDING The licensee experienced an apparently spurious actuation of the CO2 (carbon dioxide) suppression system in the North Anna Unit 1 turbine building (specifically the main turbine, low pressure turbine, and exciter area). The licensee responded and determined there was no fire and secured the CO2 release within two minutes. The event was classified as an unusual event per item K.13 of the emergency action levels due to onsite release of a toxic gas. The licensee has pulled the actuation fuses on the system, isolated the CO2 storage tank, and is in the process of ventilating the area. A fire watch has been posted and the licensee is checking CO2 levels throughout the area. There were no injuries as a result of the discharge and no significant operational impairment. The licensee has notified appropriate state and local authorities as required due to the declaration of an unusual event. The licensee will also notify the NRC resident inspector. * * * UPDATE 14:53 EDT ON 10/08/04 FROM DAVE NUNBERG TO BILL HUFFMAN * * * The licensee terminated the unusual event at 14:45 EDT following inspection of the turbine building and confirmation that CO2 levels did not represent a personnel hazard. R2DO (Ogle); NRR EO (Reis); NSIR IRD (Wilson); FEMA (Dunker); and the DHS senior watch officer have been notified. | 74 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-10-08
41103 | -1 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-10-08 01:50 | 2004-10-08 09:13 | 2004-10-28 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE "On 10/08/04 on Unit Two, the HPCI Valve Operability was being performed. During the course of this evolution the suction path was transferred from the Condensate Storage Tank (CST) to the Suppression Pool. When the HPCI System was aligned to the Suppression Pool the Suction Pressure decreased from 25.5 psig to 1.5 psig. With HPCI aligned to the suppression pool and with suction pressure less than 14 psig the HPCI System was declared INOPERABLE. "Investigation continues as to the cause of the low suction pressure. Preliminarily it is suspected that the Suppression Pool suction path was not adequately filled and vented following a recent tag out of that suction path for maintenance inspection activities. Investigation continues." The Licensee notified the NRC Resident Inspector. * * * RETRACTION FROM DISMUKE TO CROUCH AT 1521 EDT ON 10/28/04 * * * The following information was obtained from the licensee via facsimile: "The Unit 2 HPCI system was considered inoperable, since the technical information that would conclusively support its continued operability given the condition encountered could not be assembled within the time constraints of the reporting requirements. Subsequent to the event the system was confirmed be properly filled and vented with a negligible amount of air vented in the process. It was determined that this small amount of air was introduced to the suction piping as a result of an inspection activity performed for the HPCI suction check valve prior to the event. A limited amount of air remained in the torus suction piping causing the decrease in suction experienced during the event. Engineering reviewed the implications of the low suction pressure on the ability of the HPCI system to perform its safety function given the design of the system and the suction sources available. In each case Engineering was able to conclusively determine that the HPCI system would not have tripped due to low suction pressure had it received an automatic initiation signal and was actually operable during the time frame that Operations had conservatively treated the system as inoperable. Additionally, the effect of the trapped air being entrained in the pump suction was also analyzed, and the conclusion reached was that the air would not have prevented the pump's proper performance. Based on this information, the event reported on 10/08/2004 is not reportable." The licensee has notified the NRC Resident Inspector. The Headquarters Operations Officer notified R2DO (Bonser). | 0 | 99 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2004-10-08
41102 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2004-10-07 14:00 | 2004-10-07 20:24 | 2004-10-07 | SINGLE POINT VULNERABILITY IN EMERGENCY CONTAINMENT FILTER DOUSING SYSTEM "A single point vulnerability has been identified in the dousing system for the Emergency Containment Filter (ECF) System that could have resulted in dousing all filter units with borated water during an accident. Inadvertent dousing of the filters could adversely impact the methyl-iodide removal efficiency of the ECFs assumed in the plant safety analyses. "This condition applies to both Turkey Point units. However, it is reportable under 10 CFR 50.72 only with respect to Unit 4 since Unit 4 is currently in operation while Unit 3 is in a refueling outage. "The design deficiency has been evaluated in accordance with NRC Generic Letter 91-18. The ECFs have been determined to be operable but nonconforming and reportable under 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(C)and (D). "A design change is being prepared to correct the vulnerability on both units." The licensee has notified the NRC resident inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) |  | 0 | 2004-10-07
41101 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2004-10-07 14:00 | 2004-10-07 15:29 | 2004-10-07 | OFFSITE NOTIFICATION DUE TO AN UNSCHEDULED RELEASE The licensee provided the following information via facsimile: "[The] Maine Emergency Management Agency [was notified] of an unscheduled release that occurred during the 24 hour period ending at midnight on Thursday, 10/07/04. Maine Yankee identified a minor release of 3.18 E-6 Curies of liquid from the site. This release exceeded the value projected for this period and is therefore classified as unscheduled. The total liquid release resulted in a minor exposure value of 2.21 E-5 millirem. "The cause of the release resulted from groundwater intrusion of the outfall piping during soil remediation and failure of the clay barrier that was installed. [The] release occurred from 9/30/04 until 10/6/04. The outfall piping is being removed and the area backfilled to eliminate liquid releases via this pathway." The licensee stated that the radionuclides involved were Cesium-137, Bismuth-214, and Lead-214. The licensee has notified the NRC Region 1 (Roberts). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-07
41100 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2004-10-07 11:48 | 2004-10-07 15:03 | 2004-10-07 | AUTOMATIC REACTOR TRIP DUE TO MAIN TURBINE TRIP "At 1148 CDT on 10-7-2004, Wolf Creek Generating Station experienced on automatic reactor trip as a result of a turbine trip. Initial indications are that the trip was associated with a lightning strike in the switchyard. "All control rods fully inserted. The 'A' train of the Residual Heat Removal system and the 'A' train Class IE Safety Related Switchgear Air Conditioning Unit were out of service for scheduled maintenance at the time of this event. All other safety related equipment operated as expected. The Auxiliary Feedwater system actuated as designed. "The plant is currently stable in Mode 3 at Normal Operating Temperature and Pressure while plant personnel investigate the cause of the reactor trip and formulate the repair and restart plan. "The NRC Senior Resident inspector has been informed. A news statement relative to this event is planned." Secondary atmospheric relief valves lifted and reseated as a result of the trip, however there was no release to the environment. Decay heat is being removed via the steam dumps. The electrical grid is stable. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) |  | 0 | 2004-10-07
41099 | 0 | UPMC-MCKEESPORT |  |  |  |  | 2004-10-07 | 2004-10-07 13:37 | 2004-10-15 | POSSIBLE PERSONNEL OVEREXPOSURE The licensee reported that the exposure results received 10/07/04 for a female Nuclear Medicine Technician at the University of Pittsburgh Medical Center indicated a whole body dose of 10,857 millirem by film badge and a shallow dose of 25,100 millirem by ring badge for the period 08/01/04 through 08/31/04. Based on the actual work performed by the technician, the licensee Radiation Safety Officer suspects that the reported dose may not be valid. * * * Update on 10/13/04 at 1044 EDT JERRY ROSEN (RSO) TO MACKINNON * * * This incident occurred at the University of Pittsburgh Medical Center located in McKeesport, PA. The license number for the Medical Center is 37-00896-03. This incident did not take place at the University of Pittsburgh. R1DO (McDermott) & NMSS EO (Michele Burgess) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2202(b)(1) |  |  |  | 0 | 2004-10-07
41098 | -1 | US AIR FORCE |  |  |  |  | 2004-10-06 15:20 | 2004-10-06 16:18 | 2004-10-07 | MISSING POLONIUM SOURCE At 1520 ET on 10/06/04, Bolling Air Force Base, Washington, DC was notified that a 0.5 milliCurie Po-210 source was missing at Wright Patterson Air Force Base, Ohio. No other details were available at this time. * * * RETRACTION FROM MAJOR REFOSCO TO W. GOTT AT 0922 ON 10/07/04 * * * "Upon clarification of reporting requirements with NRC Region IV, this event is subject to 10 CFR 20.2201(a)(1)(ii) and must be reported within 30-days if the source is not found." The original report was based on the original activity of 0.5 milliCuries, whereas the current activity is 2.8 microCuries and is less than the immediately reportable activity. Notified NMSS (J Hickey), R4DO (R Bywater), and R3DO (Louden) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-10-06
41097 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-10-06 09:10 | 2004-10-06 10:42 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * SAFETY RELATED NEEDLE VALVES IN INCORRECT POSITION POTENTIAL HEALTH AND SAFETY CONSEQUENCES: "Potential vulnerability to workers and public of a high consequence event involving failure of safety controls that were designed to prevent a hydrogen explosion in the BLEU Preparation Facility U-Aluminum Dissolution gloveboxes/dissolvers. SEQUENCE LEADING TO EVENT: "Rotometers FIC-1F14A, 1C01, and 1D01 needle valves were closed on the U-Aluminum dissolver system. FIC-1C01 and FIC-1D01 or FIC-1F14A needed to be open to allow a nitrogen purge in the dissolver to protect against a Hydrogen explosion in the enclosure or at the dissolver/enclosure interface. PREVENTION OR MITIGATION: "Other controls were in place to partially mitigate a potential hydrogen explosion that was analyzed in support of the Integrated Safety Analysis for the operations at Bldg. [DELETED]. A nitrogen trickle system provides sufficient flow of nitrogen to the dissolvers during dissolution to provide 5 volumetric changeouts in 30 minutes. The trickle nitrogen flow was available for the operator to access the dissolvers one hour after dissolution. Enclosures 1C01/1C11 and 1D01/1D11 did have an air sweep to the enclosure ventilation system. Should hydrogen have leaked or migrated to the enclosure upon opening of the dissolver lid, the purge would have maintained the hydrogen concentration below the lower explosive limit. ADDITIONAL ACTIONS: "Upon discovery of valve closure, valves were immediately opened and Safety Department notified. EVENT STATUS: "Terminated." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 0 | 2008-05-11
41096 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2004-10-01 | 2004-10-06 10:28 | 2004-10-12 | AGREEMENT STATE REPORT "Riverside Technologies notified the Radiation Control Bureau with the New Mexico Environment Department that one of their density moisture gauges was stolen sometime between Friday night, October 1, and Monday morning, October 4,2004. The locked storage room was broken into and the gauge was removed from its transport container and taken from the company office in Espanola, New Mexico. The gauge was a Campbell Pacific Nuclear, Model MC-3, serial number M30069661, and containing Cesium-137 and Americium-241/Be radioactive sealed sources. The gauge was locked in the safe position." * * * UPDATE AT 11:32 HRS. EDT ON 10/12/04 FROM MEDINA (VIA E-MAIL) TO CROUCH * * * "The density/moisture gauge (CPN, model MC-3, SN 30069691) reported stolen by Riverside Technologies (NM license number DM345) on 10/4/2004 has been found. The RSO, [DELETED], called at 8:45 a.m. MST today and reported that the gauge had been left near his vehicle at his residence in Espanola. There is no apparent damage to the gauge and the source rod was still locked. The RSO will leak test the gauge to evaluate the integrity of the sources. This gauge was not being used and had been in storage since acquired from another licensee. The gauge will again be placed in storage with additional security measures being implemented at the facility." Notified TAS (Hahn), R4DO (Kennedy) and NMSS EO (Wastler). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2004-10-11
41095 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-10-05 18:30 | 2004-10-05 19:58 | 2004-10-05 | ONE OF TWO PRESSURIZER LEVEL INSTRUMENTATION CHANNELS FOUND TO BE INOPERABLE. Event reported according to operating license condition 2.G (Failure to operate the station in accordance with Technical Specification). "Seabrook has discovered that a condition existed that was prohibited by the Technical Specification (TS). Pressurizer level recorder (1-RC-LR-460), one of the two channels of pressurizer level instrumentation required by TS 3.3.3.6, Accident Monitoring Instrumentation, was inoperable for a period longer than the seven days permitted by the TS. The instrument was inoperable for approximately 60 days, from April 5, 2004, until June 4, 2004. This event is being reported in accordance with the Seabrook Station facility operating license, condition 2.G, as a failure to operate the station in accordance with the TS." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2004-10-05
41094 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-10-05 13:34 | 2004-10-05 18:48 | 2004-11-25 | INADVERTENT UNDERVOLTAGE CONDITION INITATED DIESEL LOAD SEQUENCER, ETC. DIESEL DID NOT START. "At approximately 1334, during realignment from monthly surveillance testing of the normal and alternate power supply breakers to the 10 A404 vital 4 Kv bus, an inadvertent undervoltage condition appears to have occurred. This condition resulted in initiation of the diesel load sequencer and tripping of the normal loads supplied by this bus. The undervoltage condition was momentary in nature, the load sequencer stopped upon restoration of voltage prior to starting the emergency diesel generator and operators successfully restarted the equipment that had tripped and restored the load sequencer. The D Emergency Diesel Generator is considered to be operable at this time. "The cause of the occurrence is under investigation. The plant is stable in Operational Condition 1 at 100% power. "This event is being reported in accordance with 10CFR50.72(b)(3)(iv)(A) 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) subsection 8', specifically in this case, Emergency ac electrical power systems." LAC Township notified by licensee. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION PROVIDED FROM BRADDICK TO KNOKE AT 1503 ON 11/25/04. * * * "Upon further review this event was determined to not meet the reportability requirements of 10CFR50.72. The event that caused the momentary interruption to the 10A404 vital bus (i.e., less then a second) did not result in an actuation of a listed system (Emergency ac electrical power systems, including: Emergency diesel generators (EDGs)). Because the event did not meet the NUREG 1022 reporting requirement specified in 10CFR50.72 (b)(3)(iv)(A) it has been determine to not be reportable." The NRC Resident Inspector was notified of this event by the licensee. LAC Township notified by licensee. Notified R1DO (Dimitriadis) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-10-05
41093 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2004-10-05 12:53 | 2004-10-05 17:51 | 2004-10-05 | TONE ALERT NOTIFICATION SYSTEM FOR OSWEGO COUNTY WAS DETERMINED TO BE OUT OF SERVICE. "On October 5, 2004 at 1253 the "Tone -Alert" notification system for Oswego County was determined to be out of service. This impacts the ability to readily notify a portion of the Emergency Planning Zone population for the Nine-Mile Point and James A. Fitzpatrick Nuclear Power Plants. The failure was caused by the unplanned loss of required telephone lines, the line between the transmitter and the National Weather Service. Verizon is currently working on repairs and expect that the repairs should be completed by 1700. "The loss of the "Tone-Alert" radios constitutes a significant loss of emergency off-site communications ability. Compensatory actions have been verified to be available should the prompt notification system be needed. This consists of utilizing local law enforcement personnel for 'route-alerting' of affected areas." The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE 2115 EDT ON 10/05/04 FROM JOHN MANLY TO S. SANDIN * * * The "Tone-Alert" radios were restored at 1715 EDT. The licensee will inform the NRC Resident Inspector. Notified R1DO (Barkley). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-10-05
41092 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2004-10-05 13:53 | 2004-10-05 16:18 | 2004-10-05 | TONE ALERT RADIO SYSTEM OUT OF SERVICE GREATER THAN ONE HOUR. "On October 5 at 1455 James A. Fitzpatrick was notified by Oswego County Emergency Management that the tone alert radio system had exceed 1 hour out of service at 1353 "This impacts the ability to readily notify a portion of the Emergency Planning Zone Population for the Nine Mile Point and James A. Fitzpatrick Nuclear Power Plants. The failure was caused by the unplanned loss of required telephone lines. The line between the transmitter and the national weather service. Verizon is currently working on repairs that should be completed by 1700. "The loss of the tone alert radio constitutes a significant loss of emergency off-site communications ability. Compensatory actions have been verified to be available should the prompt notification system be needed. This consists of utilizing local law enforcement personnel for 'Route Alerting' of affected areas." The state will be notified. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-10-05
41091 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-10-02 | 2004-10-04 18:16 | 2004-10-04 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE The State of CA was notified at 0830 hrs [PDT] on 10/04/04 of a reported stolen Troxler 3241C 100 microCuries Am 241/Be gauge, SN # 1537. The theft occurred from a construction jobsite over the weekend. Bolt cutters were used in the theft. Local police have been notified and a cash reward is being offered. NMED # XCA598. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-10-07
41090 | 0 | BATTELLE MEMORIAL INSTITUTE |  |  |  | ADVANCED FUEL R&D AND PILOT PLANTS | 2004-10-01 11:00 | 2004-10-04 17:50 | 2004-10-04 | CRACKS/FISSURES IN POWER AIR PURIFYING RESPIRATORS (PAPR) MOTOR/BLOWER ASSEMBLY CASINGS "Exact content of notification: Battelle is notifying NRC of a potential defect as from the manufacturer concerning the MSA equipment provided Model MM2K PAPR motor/blower assembly (Part 10022695). After limited field use at its West Jefferson, Ohio site noticeable cracks/fissures developed on some of the motor/blower casings. The manufacturer of the equipment, MSA, has been notified of the problem and several of the cracked/fissure units have been returned to MSA for testing in early September. Battelle discontinued use of the MSA Model MM2K PAP'R in mid September as a result of the observed equipment cracks/fissures at its West Jefferson, Ohio site. "Describe the event: We have been experiencing noticeable cracks/fissures of some of our MSA brand MM2K Powered Air Purifying Respirators (PAPR) motor/blower assembly casings (Part #10022695). We have not experienced any break through of the casings tied to employee exposure as evidenced by our In place personnel monitoring programs. Our original note of the circumstance was on August 25, 2004 during the re-use inspection process of the MSA MM2K PAPR by the Respiratory Protection Supervisor on site. We have field verified that our respirator cleaning and use processes are adequate and in line with the manufacturer recommendations. We again experienced a similar crack/fissures Issue with a different order of MSA MM2K PAPR motor/blower assemblies by a different vendor ordering from a different lot number in early September 2004. We have discontinued use of the MSA MM2K PAPR on site in mid September as a result of the issues we have had and have supplied MSA with several of the cracked/fissured MM2K PAPR motor/blower assembly casings for testing at their facility In Pennsylvania. MSA Is working on a solution for the identified issue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 21.21 |  |  |  | 0 | 2004-10-04
41089 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-10-04 17:30 | 2004-10-04 17:59 | 2004-10-04 | A SIGNIFICANT REDUCTION IN THE EFFECTIVENESS OF ANY SPENT FUEL OR GTCC WASTE STORAGE CONTAINMENT SYSTEM DURING USE. "A significant reduction in the effectiveness of any spent fuel storage confinement system during use " "This reportability notification addresses a potential unanalyzed condition of 18 Transportable Storage Canisters (TSCs) which are loaded with spent nuclear fuel (SNF). Seventeen of these TSCs are stored in Vertical Concrete Casks (VCCs) at the Haddam Neck Plant Independent Spent Fuel Storage Installation (ISFSI). One TSC is currently in transport operations and will be transferred to the ISFSI in the near future. "SNF clad temperature is affected by changes in the TSC internal environment that are encountered during fuel transfer operations. In order to maintain SNF clad temperatures within the analyzed limits, the time duration of certain fuel transfer activities are limited (for example, time in dewatering phase, time in vacuum drying phase and time in helium backfill phase). "The canister dewatering section of CY procedures allowed multiple blowdowns of the TSC while in the dewatering time clock. This is contrary to the NAC thermal analysis which assumes a water environment in the canister during the dewatering period. It appears that this condition is not consistent with current analysis assumptions and is therefore a potential unanalyzed condition. "NAC International (holder of the C of C) has been advised of this condition and is analyzing the TSC loading conditions. VCC outlet temperatures are within acceptable limits and there is no evidence of unusual radiation exposure in the ISFSI environs." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SPENT FUEL, HLW OR RX-REL GTCC RED. EFECT |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 72.75(c )(2) |  |  |  | 0 | 2004-10-04
41088 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-09-29 12:15 | 2004-10-04 15:16 | 2004-10-04 | AGREEMENT STATE REPORT FROM THE STATE OF TEXAS: STOLEN AND RECOVERED MOISTURE DENSITY GAUGE. "Shortly after noon on September 29, 2004, the Agency was notified by the Harris County Hazmat Team of a contaminated 55-gallon drum/Pig that had been 'spilled' on the side of the road by a Bank building several blocks from the city police station. (Deleted) and (deleted) noted the radiation markings and loaded the device into their Ford F150 truck, Texas License Plate # (Deleted). They transported the device to the Humble Police Department for assistance. Upon arrival, the Humble Police requested assistance from the Harris County Hazmat Team. Due to radiation markings on the container the Hazmat Team took readings on the container. The container was examined by two technicians dressed out in protective clothing and SCBA. When reported to this Agency there was some confusion in the initial readings obtained by the Hazmat Team. The reported level initially reported was 70 R/hr. Two Department of State Health Service's Radioactive material inspectors were dispatched to assist in the identification of the device. The bright yellow box with embossed lettering 'TROXLER' immediately identified the device as a Troxler moisture density gauge. The shipping container appeared to have a broken hinge. Initial confirmatory readings on the case indicated 1.5 millirem on the sides of the case and 9 millirem on the top of the package. Upon opening the case the gauge appeared to be intact. A brief search of the case located a calibration sheet from Texas Licensee (L02243-000) Component Sales and Services. The gauge was transported to the Regional Headquarters. After determining that the gauge was a Troxler 3430, Serial Number 23700, with two seal sources - Cs-137, Serial No 75-5786 and Am-241/Be, Serial No 47 19622. The gauge was initially reported by Troxler as belonging to the New Hampshire Department of Health. However, a later check with Component Sales and Services indicated that the gauge belonged to Texas Licensee - L05180-000, GeoScience Engineering and Testing, Inc. The Licensee was contacted and arrangements were made to pickup the gauge on September 30, 2004. During return of the gauge, the Licensee verbally reported that the gauge had been stolen while the gauge operator stopped at a Subway sandwich shop near Houston Intercontinental Airport." Texas Incident No. I-8170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-10-07
41087 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2004-10-01 07:30 | 2004-10-04 14:25 | 2004-10-04 | AGREEMENT STATE REPORT FROM THE STATE OF UTAH "The licensee's technologist accidentally administered a 400 mCi bulk dose of Tc-99m (sodium pertecthnetate) instead of 4 mCi of Cardiolite. The licensee took a number of steps to protect the patient. They administered a thyroid blocker, and they administered IV fluids and oral fluids to the patient to help flush the Tc-99m. According to the licensee's consultant, the patient received an 80 rad dose to the GI tract. "The Utah Division of Radiation Control was notified by the licensee on Friday, October 1, 2004, at approximately 10:18 a.m. MST. "The licensee notified the following: The patient, the referring physician, the Radiation Safety Officer, the Authorized User on site, the nuclear pharmacy, and a consultant." Utah Report ID No: UT-04-003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2004-10-07
41086 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-10-03 05:30 | 2004-10-03 10:46 | 2004-10-03 | PRIMARY CONTAINMENT PENETRATION ISOLATION VALVES INOPERABLE "During a review of outage clearances, it was discovered that a Caution tag out for Service Air to the Drywell was active and the valves were open. This rendered the valves inoperable and Technical Specification 3.6.1.3 action B for one penetration with two inoperable PCIVs was entered. The action was to isolate the penetration by closing one valve within one hour. The event was discovered at 0530 and the outboard valve was closed at 0655 . Since the one hour time limit was exceeded, Technical Specification 3.6.1.3 action E (Mode 3 in 12 hours and Mode 4 in 36 hours) was entered at 0630 and exited at 0655. Technical Specification 3.6.1.3 action A, which is the Tech. Spec. for one inoperable isolation valve will remain in effect. The plant entered Mode 3 at 1530 on 10/01/04. Mode 3 requires primary containment and all PCIVs to be operable. This condition of non-compliance existed from 1530 on 10/01/04 until 0655 on 10/03/04. The licensee notified the NRC Resident Inspector. | 0 | 20 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-10-03
41085 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2004-10-02 15:00 | 2004-10-02 15:22 | 2004-10-25 | REACTOR POWER BEING REDUCED DUE TO ENTERING TS 3.0.3 BECAUSE OF INOPEABLE RECIRC VENT SYSTEM At 1500 hours the plant commenced reactor shutdown from 100% power for entering T.S. 3.0.3 due to both trains of the Emergency Recirc Vent System being declared inoperable. The reactor will be in mode 2 by 2000 hours, mode 3 by 0200 hours on 10/03 and mode 4 by 0200 hours on 10/04. If the problem is corrected, they will terminate the shutdown. The NRC Resident Inspector was notified. HOO Note: see event 41084 * * * UPDATE ON 10/02/04 AT 1940 EDT FROM FREDERICK SMITH TO GERRY WAIG * * * "Update to [Event] Notifications 41084 and 41085: At 1840 [EDT] on 10/02/04 it was determined that the apparent slow response times of the Control Room Emergency Recirculation [CRER] dampers was due to a malfunctioning relay in the initiation circuit, not due to failure of the dampers. The LCO actions associated with the CRER system were exited and the actions associated with the initiation instrument were entered. Therefore the plant is no longer required to shutdown per T.S. 3.0.3. The plant shutdown has been terminated. Plant power will be returned to 100%." The licensee has notified the NRC resident Inspector. Notified R3DO (Thomas Kozak). * * * RETRACTION FROM KEN MEADE TO BILL HUFFMAN ON 10/25/04 AT 1433 EDT * * * "At 1300 on 10/02/04, results of a surveillance indicated that dampers in both trains of the Control Room Emergency Recirculation System (CRERS) were slower than allowed by Technical Specifications (TS) requiring both trains of the CRERS to be declared inoperable. With both trains inoperable, Technical Specification 3.0.3 was entered which required a plant shutdown. The shutdown was commenced at 1500. This condition was reported as required in Event Notification 41085. Additionally, with both CRERS trains inoperable, this condition was determined to be reportable as a loss of safety function (accident mitigation) and was reported as required in Event Notification 41084. "Subsequently, it was determined that the failure was the result of a defective time delay relay in the radiation monitor initiation circuit. Other inputs that would have caused the dampers to reposition in an accident were not impacted. The appropriate TS (3.3.7.1), for the radiation monitor, was entered and TS 3.0.3 was exited. The significant actions required by this TS were to restore the function within 7 days or place the system in emergency recirculation. It did not require entry into an action to shutdown. When this condition was identified, TS 3.0.3 was exited, the shutdown was terminated, and the plant was restored to full power. Since a TS required shutdown was not required, Event Notification 41085 is being retracted. The licensee has notified the NRC Resident Inspector. NRC R3DO(Gardner) has been notified. | 83 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-10-02
41084 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2004-10-02 13:00 | 2004-10-02 15:22 | 2004-10-25 | PLANT DECLARED THE EMERGENCY RECIRCULATION VENTILATION SYSTEM INOPERABLE. A surveillance test was being performed on the Emergency Recirc vent System and all six dampers on both trains failed to stroke in the required Tech. Spec. times. Therefore, both trains of the Emergency Recirc Vent System were declared inoperable and the plant entered T.S. 3.0.3. The LCO action statement requires the plant to be in mode 2 in 7 hours and mode 3 in the following six hours and mode 4 in the following 24 hours. They are currently troubleshooting the problem. The NRC resident Inspector was notified HOO Note: see event 41085 * * * UPDATE ON 10/02/04 AT 1940 EDT FROM FREDERICK SMITH TO GERRY WAIG * * * "Update to [Event] Notifications 41084 and 41085: At 1840 [EDT] on 10/02/04 it was determined that the apparent slow response times of the Control Room Emergency Recirculation [CRER] dampers was due to a malfunctioning relay in the initiation circuit, not due to failure of the dampers. The LCO actions associated with the CRER system were exited and the actions associated with the initiation instrument were entered. Therefore the plant is no longer required to shutdown per T.S. 3.0.3. The plant shutdown has been terminated. Plant power will be returned to 100%." The licensee has notified the NRC resident Inspector. Notified R3DO (Thomas Kozak). * * * RETRACTION FROM KEN MEADE TO BILL HUFFMAN ON 10/25/04 AT 1433 EDT * * * "At 1300 on 10/02/04, results of a surveillance indicated that dampers in both trains of the Control Room Emergency Recirculation System (CRERS) were slower than allowed by Technical Specifications (TS) requiring both trains of the CRERS to be declared inoperable. With both trains inoperable, Technical Specification 3.0.3 was entered which required a plant shutdown. The shutdown was commenced at 1500. This condition was reported as required in Event Notification 41085. Additionally, with both CRERS trains inoperable, this condition was determined to be reportable as a loss of safety function (accident mitigation) and was reported as required in Event Notification 41084. "Subsequently, it was determined that the failure was the result of a defective time delay relay in the radiation monitor initiation circuit. Other inputs that would have caused the dampers to reposition in an accident were not impacted. The appropriate TS (3.3.7.1), for the radiation monitor, was entered and TS 3.0.3 was exited. The significant actions required by this TS were to restore the function within 7 days or place the system in emergency recirculation. It did not require entry into an action to shutdown. When this condition was identified, TS 3.0.3 was exited, the shutdown was terminated, and the plant was restored to full power. Since a TS required shutdown was not required, Event Notification 41085 is being retracted. "The condition was also reported as a loss of safety function for the accident mitigation function of CRERS. The CRERS is automatically activated by a Loss of Coolant Accident (LOCA) signal or a Control Room Ventilation (CRV) high radiation signal. The LOCA instrumentation circuitry was not affected by the defective time delay relay and thus the damper stroke times were not impacted. The CRV airborne radiation monitor signal is considered a "diverse" signal to the LOCA signal. Since the LOCA signal would have properly initiated the CRERS and the CRV high radiation signal is redundant, there was no loss of safety function. Since there was no loss of safety function, Event Notification 41084 is being retracted." The licensee has notified the NRC Resident Inspector. NRC R3DO(Gardner) has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-10-02
41083 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-10-01 14:15 | 2004-10-01 16:30 | 2004-10-01 | DEATH OF A CONTRACT EMPLOYEE FROM AN APPARENT HEART ATTACK The following was received from the licensee via facsimile: "A 56-year old male AREVA contractor died from a heart attack. A report of potential heart attack was made at 1242 [EDT] to the control room. Off-site medical assistance was used and the contractor was transported to South Miami-Homestead Hospital at 1340 [EDT]. [The] contractor was pronounced dead at 1415 [EDT]." The licensee also reported that the individual was not contaminated and was stricken while working in a contractor trailer located near the facility administration building. The licensee has notified the NRC Resident Inspector and will be notifying the Occupational Safety Health Administration (OSHA). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-10-01
41082 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-10-01 07:30 | 2004-10-01 12:00 | 2004-10-01 | REACTOR TRIP DUE TO MAIN GENERATOR LOAD REJECTION "At 7:30 a.m. [CDT] on October 1, 2004, an automatic reactor scram occurred as a result of an electrical fault on the main generator output lines that caused a main generator trip and turbine trip. All control rods inserted. Approximately 13 minutes prior to the fault, a loss of one station service transformer had occurred. This resulted in an automatic start of the Division 1 diesel generator and a loss of power to some plant auxiliaries, including the feedwater level regulation isolation valves. "The loss of reserve station service no. 1, combined with the trip of the main generator, caused a loss of power to two condensate pumps and one main feedwater pump. The remaining two feedwater pumps tripped on low suction pressure. The reactor containment isolation cooling pump (RCIC) steam supply isolated during the scram transient, so the control room operators manually started the high-pressure core spray system (HPCS) pump for level control. The injection valve was closed as level had already reached the high water level isolation setpoint for that valve. It was later reopened manually as level approached the low level setpoint (level 2), which would have automatically opened the valve. The level 2 setpoint was reached briefly after the valve was already open. "Reactor pressure is being controlled manually with safety relief valves (SRV's). The main steam isolation valves (MSIV's) were manually closed due to lowering pressure from steam loads in the plant that could not be immediately isolated because of loss of power to their valves. RCIC is also running in CST (condensate storage tank) to CST mode, to augment pressure control. "The electrical load center which supplies power to the instrumentation and valves needed for feedwater operation was cross-tied to an alternate power source, and feedwater was restored to operation and is presently controlling reactor water level. During the event, standby service water also initiated. "This is the presently known information. Further information will be provided as the investigation continues." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2004-10-01
41081 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-08 14:45 | 2004-09-30 14:02 | 2004-09-30 | INVALID EMERGENCY FEEDWATER ACTUATION The following information was provided by the licensee via facsimile: "At 1445 [hrs. EDT] on September 8, 2004 Crystal River Unit 3 experienced an invalid actuation of the B-Train of the Emergency Feedwater System. This occurrence is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) and 50.73(a)(2)(iv)(B)(6) using the optional process described in 50.73(a)(1). A complete actuation of the B-Train of Emergency Feedwater occurred and the train started and functioned successfully. The A-Train of Emergency Feedwater was operating at the time, and it continued to operate successfully during and after the B-Train actuation." The licensee has notified the NRC resident inspector. See retraction of Event #41027 for related information. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-09-30
41080 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2004-09-29 11:00 | 2004-09-29 14:37 | 2004-09-29 | RANDOM FITNESS FOR DUTY TEST A random fitness for duty test determined that an Entergy Supervisor tested positive for alcohol. This was confirmed under the fitness for duty program at approximately 1100 hours. A work history review has been conducted and no work or behavioral issues identified. Removal of access authorization was not established. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 26.73 |  |  |  | 0 | 2004-09-29
41079 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-09-29 | 2004-09-29 14:23 | 2004-09-29 | AGREEMENT STATE REPORT - LOST MOISTURE DENSITY GAUGE "Licensee's case containing gauge [Troxler Moisture Density Gauge, Model 3411-B, Serial Number 18168, 8 millicuries Cs-137, 40 millicuries Am-241:Be] fell out of a truck while driving down the road. A fire truck just happened to be following the truck and secured the gauge. The technician noted loss and returned to the scene. Gauge and case were not damaged. The technician forgot to chain the gauge to the truck after finishing a job. The licensee will submit a written report on this incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-10-04
41078 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-09-24 | 2004-09-28 15:08 | 2004-09-28 | AGREEMENT STATE REPORT "Per Swedish Medical Center policy, post thyroid treatment patients are prescribed 74 mBq (2mCi (milliCuries)) for the treatment follow-up scan, and 185 mBq (5 mCi) for subsequent treatment if necessary. On 24 September 2004 a patient was prescribed 74 mBq (2 mCi) of NaI (Iodine-131) for a post treatment scan. Instead, 191 mBq (5.16 mCi) of NaI (Iodine-131) were administered. The prescribing physician realized that a misadministration had occurred on 27 September 2004 when the patient underwent the scan. A viable follow-up scan was able to be performed even though the misadministration had occurred. "There are multiple procedural checks in place to assure medical technicians administer the prescribed dose. Human error appears to have lead to checks not being performed prior to this event. "The Radiation Safety Officer for Swedish Medical Center notified the State of Washington, of the misadministration, on 27 September 2004. "The treating physician notified the patient on Monday, 27 September 2004, when the physician discovered the patient had been administered 191 mBq (5.16 mCi) of NaI (Iodine-131) instead of the prescribed 74 mBq (2 mCi) of NaI (Iodine-131)." Event Report Number WA-04--57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-10-01
41077 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-05-17 | 2004-09-28 12:51 | 2004-09-28 | AGREEMENT STATE LOST OHMART DENSITY GAUGE "The licensee reported that an Ohmart density gauge (Model SH-F2, Serial Number 2479GK) had last been seen during an inventory and shutter check on November 17, 2003. The gauge contained a 1.85 GBq (50 mCi), Cs-137 sealed source. Facility records indicate the device's electrical signal was lost on December 12, 2003, at 4:30 pm. At that time, a physical investigation, to investigate the signal loss, was not performed. The next routine inventory was attempted on May 17, 2004. At this time the gauge was found to be missing. "The missing gauge had measured 'weight rejects' at a remote part of the facility. Rejects are routinely sent to an eastern Washington landfill by truck. The gauge seems to have been dislodged from its angle-iron attachment, by large reject material, and then inadvertently taken to an eastern Washington landfill by the rejects truck. "Gauge measurements were not vital to operations, so the loss of signal had gone ignored until the May 17th inventory attempt. "CORRECTIVE ACTION TAKEN by licensee: 1. A special training session will be given, during the licensee's next monthly safety meeting, for those employees associated with fixed gauge operations. The training will emphasize the importance for employees to investigate when gauge process measurements are lost. 2. Special informational postings will be placed at key locations within the facility, near process control equipment receiving fixed gauge electrical signals, so facility employees shall be reminded to immediately investigate the loss of a gauging device's signal. "Isotope and Activity Involved: Cs-137, 1.85 GBq (50 mCi) "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None likely. "Lost, Stolen or Damaged? (mfg., model, serial number): Lost (or Stolen) Ohmart density gauge (Model SH-F2, Serial Number 2479GK) "DISPOSITION/RECOVERY: Searches by licensee with the assistance of department staff were performed with Ludlum Model 19, Micro R meters and other detection instrumentation. These searches were unsuccessful. "A search at the Licensee's facility in Port Townsend, Washington was conducted on May 25, 2004. A search at the landfill was performed on July 29, 2004." Event Report Number: WA-04-028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-10-01
41076 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-09-28 10:30 | 2004-09-28 13:44 | 2004-09-29 | UNUSUAL EVENT DECLARED DUE TO SEISMIC ACTIVITY "Earthquake felt at plant site [at 1015 PDT] registering 0.012 g. No damage on plant site noted. Release to the environment remains within normal operating levels, and effluent radiation monitors did not alarm. No protective action required." The Licensee notified the NRC Resident Inspector. * * * UPDATE FROM T. CHITWOOD TO W. GOTT AT 1428 EDT ON 09/28/04 * * * "Plant walk down in progress. No damage noted." The Licensee notified the NRC Resident Inspector. * * * UPDATE FROM GLENN COELZER TO MACKINNON AT 2132 EDT ON 09/28/04 Information Call: No plant damage detected by walk downs or equipment testing. R4DO (Linda Howell) notified. The Licensee will notify the NRC Resident Inspector. * * * UPDATE FROM JEFF KNISLEY TO CROUCH AT 0313 EDT ON 09/29/04 * * * Information Call: No plant damage detected by walk downs or equipment testing. The licensee notified the NRC Resident Inspector. R4DO(Howell) will be notified. * * * UPDATE FROM GLENN GOELZER TO W GOTT AT 1532 EDT ON 9/29/04 * * * The licensee terminated the NOUE at 1215 PDT. "No plant damage has been detected by plant walkdowns or equipment testing." NRC exited Monitoring at 1600 EDT Notified R4DO (L Howell), NRR (Skeen, Borchardt), IRD (Frant, Wilson), Chairman Office (Holahan), EDO (Mitchell), PAO, Dir of Comm. (Outlaw), DHS (Morison), FEMA (Caldwell), USDA (Thomas), DOE (Wyatt), NRC DOT (Crews), and HHS (R. Harlan) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-28
41075 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-09-27 | 2004-09-27 11:25 | 2004-09-30 | STOLEN TROXLER MOISTURE DENSITY GAUGE "Metal ship container was broken into and the gauge was stolen. It was last seen close of business on Friday the 24th and discovered stolen Monday the 27th. The keys were not taken. The Haines City PD has been notified. Owner will offer a $500 reward. Florida is investigating." Incident Location: HWY 27, 5 miles south of I-4 (Polk County near Haines City) Temp work storage site. Troxler: Model number 3430 [containing] 8 millicuries of cesium-137 and 40 millicuries of Am-241/Be. Serial number of the gauge is 27404. License type: Specific; 3L(1). * * * UPDATE ON 09/29/04 AT 1514 EDT FROM CHARLES ADAMS TO GERRY WAIG VIA EMAIL * * * "Stolen Troxler gauge & case were recovered undamaged by the licensee this afternoon. The source rod was still locked. A teenage boy claimed the reward and stated that he had found it Saturday night (during the hurricane) beside the side of road which runs along the orange grove right behind the storage container. When his mother saw the radiation sticker she told him to get it out of the house. He then opened up the case and found the contact information and called the licensee. He claimed that the case lock was gone when he found it." Notified R1DO (John Rogge) and NMSS EO (M. Wayne Rogers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-09-30
41074 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-26 05:05 | 2004-09-26 05:33 | 2004-09-27 | ENTERED UNUSUAL EVENT CLASSIFICATION DUE TO HURRICANE WARNING IN EFFECT "Crystal River Unit 3 site has declared an Unusual Event due to the declaration of a hurricane warning for Citrus County including the Crystal River Unit 3 site." Current wind speed on-site is 20 mph with 40 mph gusts. The licensee's current plan is to remain in power operation. The licensee notified both state and local agencies and the NRC Resident Inspector. * * * UPDATE FROM AL STERN TO MIKE RIPLEY 0349 ET 09/27/04 * * * Hurricane warning has been discontinued. Unusual Event exited at 0345 ET. The licensee notified the NRC Resident Inspector. Notified R2 Response Manager (S. Cahill), R2 DO (R. Haag), NRR EO (S. Richards), IRD Manager (S. Frant), FEMA (J. Canupp), DHS (Sr Watch Officer) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-26
41073 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-25 19:09 | 2004-09-26 02:45 | 2004-09-26 | LOSS OF EMERGENCY RESPONSE DATA SYSTEM "At approximately 2315 [EDT], September 25, 2004, the NRC Operations Center reported that their link to the Emergency Response Data System (ERDS) had been lost. It was determined that the link had been lost at 1909 [EDT] that same day based upon the logged time of the last data update. The station was in constant communications with the Operations Center at the time due to the severe weather in the area due to hurricane Jeanne. The link was restored for both units at 2344 [EDT] the same day by performing the normal initiation procedure. It is suspected that the link was lost due to a momentary transient on the FTS circuit due to the weather conditions. "The link was lost again at approximately 0103 [EDT], 9/26/04. The unit 1 ERDS link was restored approximately one hour later, troubleshooting of the unit 2 is in progress." The licensee informed the NRC Resident Inspector. HOO Note: See related ENs # 41067, 41071 and 41072. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Hot Shutdown |  | Hot Shutdown | Hot Shutdown |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-09-26
41072 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-25 23:56 | 2004-09-26 00:35 | 2004-09-26 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF OFFSITE POWER "At 2356 [EDT], September 25, 2004, off-site power was lost for both units. At the time of the event both units were in mode 4 and cooling down to meet shutdown entry conditions. The shutdown of both units was due to hurricane conditions from hurricane Jeanne. All four emergency diesels (2 per unit) started and properly loaded. Both units are stable in natural circulation cooling. Efforts continue to place both units on shutdown cooling. All systems operated as expected. The plant was already in a Notification of Unusual Event due to the Hurricane. Shutdown Cooling was established on Unit 1 at approximately 0020 EDT on 9/26/04." The licensee informed both state and local agencies and the NRC Resident Inspector. A conference call was held at approximately 0005 EDT with R2 Response Manager (Len Wert), NRR EO (Stu Richards) and IRD (Susan Frant) to discuss the loss of offsite power. The participants concluded that the NRC Monitoring Mode entered at 1515 EDT on 9/25 for the Hurricane was appropriate. * * * UPDATE 0257 EDT ON 9/26/04 FROM TOM COSTE TO S. SANDIN * * * "At 2356, September 25, 2004, St. Lucie Station, Units 1 and 2, experienced a loss of off -site power (LOOP). At the time of the LOOP all four emergency diesel generators started and loaded the safety related buses. In its initial notification of the LOOP (0035 09/26/04, EN# 41067), FPL reported that all systems had performed as expected. However, during its post LOOP walkdowns of the control room boards the control room operators determined that the 1 B Intake Cooling Water (ICW) pump had not automatically started as expected. The pump was subsequently started from the control room using the manual control switch. The cause for the failure to automatically start will be investigated and corrected prior to returning the unit to service." Notified R2 Response Manager (Len Wert) * * * UPDATE 2350 EDT ON 9/26/04 FROM R2 IRC (BENOI DESAI) TO S. SANDIN * * * At 1050 EDT both units recovered offsite power exiting the criteria for the UE based on LOOP. The licensee informed state and local agencies and the NRC Resident Inspector. HOO Note: See related ENs # 41067, 41071 and 41073. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | VALID SPECIF SYS ACTUATION |  |  | Hot Shutdown | Hot Shutdown |  | Hot Shutdown | Hot Shutdown |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-09-26
41070 | 0 | HATCH |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-09-25 01:06 | 2004-09-25 02:44 | 2004-09-25 | GROUP 2 CONTAINMENT ISOLATION ACTUATION "Received Group 2 isolation signal on Low Reactor Water Level during initiation of manual reactor scram during planned shutdown. Reactor Water Level decreased to -0.5 inches. Group 2 isolation setpoint is +3.0 inches. All Group 2 isolation valves closed as required." During the planned shutdown, all control rods fully inserted. Decay heat is being removed to the main condenser via the main turbine bypass valves, ESF and ECCS systems remain available, and the electrical grid is stable. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-09-25
41069 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-24 14:00 | 2004-09-24 17:53 | 2004-09-24 | NUREG-1022 CLARIFICATION REVISED RESULTS OF PAST STEAM GENERATOR TUBE INSEPCTIONS "On September 24,2004, the NRC published a Notice of Clarification for NUREG-1022 Reporting Guidelines for 10 CFR 50.72 and 50.73. The Notice of Clarification revised the criterion used to determine if the results of steam generator tube inspections were reportable. In this Notice of Clarification, the NRC further directed the plants to consider the results of previous steam generator tube inspections against the new criterion. "Crystal River Unit 3 (CR3) has reviewed the results of the steam generator tube inspection that occurred in the refueling outage of 2003. Specifically, the previously performed Condition Monitoring assessment of the CR3's steam generators concluded that the structural requirements were met and the as-found projected leakage values for a Main Steam Line Break were exceeded. "Previously, NUREG-1022 required that both the structural and the leakage criteria must be exceeded for this condition to be reportable. The revision to NUREG-1022 will indicate that only one of the two criteria need be exceeded to be considered reportable per 10 CFR 50.72. "Accordingly, CR3 reports per 10 CFR 50.72 (b) (3) (ii) (A) that steam generator projected leakage values for a Main Steam Line Break were exceeded. "Immediate corrective actions to reduce the projected accident leakage were completed during the 2003 refueling outage prior to plant startup." The NRC Resident Inspector was notified of this by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-09-24
41068 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2004-09-24 17:00 | 2004-09-24 17:23 | 2004-09-26 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING "Turkey Point Nuclear entered an Unusual Event due to Category 12 Natural Phenomena sub category A. Confirmed hurricane warning." The licensee notified the NRC Resident Inspector, State and Local authorities. * * * UPDATE 0723 EDT ON 9/26/04 FROM KEN HARRISON TO S. SANDIN * * * The licensee is terminating their Unusual Event as of 0715 EDT after the Hurricane Warning was lifted for Miami-Dade. The licensee informed both state and local agencies and the NRC Resident Inspector. Notified R2 Response Manager (Len Wert), NRR (Stu Richards), IRD (Susan Frant), FEMA (Austin) and DHS (SWO). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-24
41067 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-24 17:00 | 2004-09-24 17:23 | 2004-09-26 | ENTERED UNUSUAL EVENT CLASSIFICATION DUE TO HURRICANE WARNING IN EFFECT Hurricane warning in effect for St. Lucie County including Plant Site. Hurricane warning was issued by the National Weather Service. St. Lucie Nuclear Power Plant entered an Unusual Event Classification per Emergency Action Level 5B (Hurricane Warning). State and Local Officials notified by the licensee. The NRC Resident Inspector was notified of this by the licensee. * * * UPDATE AT 0838 EDT ON 9/25/04 FROM JOE HESSLING TO S. SANDIN * * * "St. Lucie Unit 1 commenced a plant shutdown at 0820 in preparation for Hurricane. St. Lucie Unit 2 will commence plant shutdown at 0900 in preparation for Hurricane. St. Lucie still in Unusual Event due to Hurricane warning." Unit 1 expects to enter mode 3 at approximately 1230 hours with Unit 2 entering mode 3 between 1300-1330 hours. Both Units will remain in mode 3 with restart dates to be determined. Highest sustained winds on-site are projected at 120 mph. Current wind speed on-site is between 14-15 mph sustained from a northerly direction. The licensee notified both state and local agencies and will inform the NRC Resident Inspector. Notified R2DO (Robert Haag), NRR (Stu Richards), IRD (Susan Frant), R4DO (William Johnson), FEMA (Erwin) and DHS-DOE Desk (left message). * * * UPDATE AT 1313 EDT ON 09/25/04 FROM DAN WEST TO JOHN MACKINNON * * * St. Lucie Units 1 & 2 have shutdown and have been removed from service. R2DO (Haag) , NRR EO (Stu Richards), FEMA (Erwin), DHS (Algen), R4DO (William Johnson), NRC Region 2 (Hufham) & IRD (S. Frant) notified. The NRC Resident Inspector will be notified of this by the licensee. * * * UPDATE AT 1413 EDT ON 09/26/04 FROM M. GRAY TO MACKINNON * * * Hurricane warning has been discontinued. Unusual Event exited at 1412 EDT. R2DO (Haag), NRR EO (Richards), IRD Manager (S. Frant), R4DO (Bill Johnson), FEMA (Austin), DHS (Travis Johnson) , DOE (Robert Turner), NRC/DOT (Crews), USDA (Lori Thomas) & DHS-DOE Desk (message left) notified. The NRC Resident Inspector was notified of this update by the licensee. HOO Note: See related ENs # 41071, 41072 and 41073. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2004-09-24
41066 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-09-24 11:55 | 2004-09-24 13:29 | 2004-09-24 | MANUAL REACTOR TRIP WITH NO COMPLICATIONS DUE TO LOWERING STEAM GENERATOR WATER LEVEL "On September 24, 2004, at 11:53 hours, operations noticed the 23 Main Feedwater (FW) regulating valve operating erratically and FW flow and 23 Steam Generator (SG) level decreasing. At 11:55 hours operations initiated a manual trip of the reactor based on the degrading condition with FW flow and SG level. All control rods fully inserted and safety equipment operated as expected. Auxiliary Feedwater started as expected, the Emergency Diesel Generators did not start as offsite power remained available. The plant is in Hot (Standby) at Normal Temperature and Pressure and there was no radiation releases. The condition is under investigation and a post trip review is being conducted." State was notified of this event by the licensee. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-09-24
41065 | 0 | SCHNABEL ENGINEERING, INC. |  |  |  |  | 2004-09-23 12:55 | 2004-09-23 15:49 | 2004-09-23 | TROXLER MOISTURE DENSITY GAUGE RUN OVER BY HEAVY EQUIPMENT. The Radiation Safety Officer for Schnabel Engineering, Inc. located in Richmond, Virginia reported the following information. Schnabel Engineering, Inc. had employees working at Norfolk Shipyard International Terminal when one of their Troxler Moisture Density Gauges was run over by heavy equipment. The gauge was in its secured position when it was run over. The source rod was slightly bent and the casing around the gauge was slightly cracked. The source was still inside the gauge when it was run over. Highest survey reading taken of the damaged gauge was 9 millirem per hour on contact. Troxler will be notified of this event and the damaged gauged will be sent back to Troxler. Information of the gauge: Model Number; Troxler 3430, 8 millicuries of Cesium-137 and 40 millicuries of Am-241/Be. Serial number of the gauge is 31970. Cesium-137 source serial number is 750-7028 Am-241 source serial number is 47-5674. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2004-09-23
41064 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-09-22 16:00 | 2004-09-22 17:14 | 2004-09-22 | OFFSITE NOTIFICATION TO MIAMI-DADE COUNTY The following information was obtained by the licensee via facsimile: "Off-site notification to Miami-Dade County Environmental Resource Management was made at 1600 EDT 9/22/2004 for an oil spill and fire at the adjacent fossil Unit 2. The fire was extinguished by fossil plant personnel." The ignition source for the fire is unknown. The oil spill was in the fossil feed pump area. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-22
41063 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-09-22 09:00 | 2004-09-22 13:40 | 2004-09-22 | CALIFORNIA AGREEMENT STATE REPORT The following information was obtained from State of California - Health and Human Services Agency, Department of Health Services, Radiologic Health Branch: "On 9/22/04 at about 9:00 am, [DELETED] (RSO) notified the RHB [Radiologic Health Branch]-Granada Hills office regarding a stolen nuclear gauge (CPN, Model MC3, [Serial Number] M37067077). The incident happened on 9/21/04 at 6:00 pm [PDT] in a jobsite located at 1621 North H St., Lompoc, CA. The nuclear gauge was taken at the back of the truck by cutting the chains that secured it. "The RSO reported the incident to the police authority and CPN Company. "This incident will be investigated further by RHB-Granada Hills office." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-09-27
41062 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-09-22 09:00 | 2004-09-22 13:09 | 2004-09-22 | EMERGENCY SIRENS INADVERTENTLY ACTIVATED The following information was obtained from the licensee via facsimile: "At approximately 0900 CDT on September 22, 2004, the Goodhue County sheriff's office inadvertently activated the Goodhue County sirens during the conduct of their weekly silent siren test. As a result of the inadvertent siren actuation, Prairie Island Nuclear Generating Plant communicated with the Goodhue County Administrator and the City of Red Wing Mayor's office, as well as a Prairie Island Indian Community representative. No press release is planned. The NRC senior resident inspector was notified." | 0 | 100 | 0 |  | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-22
41061 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2004-09-22 10:01 | 2004-09-22 13:01 | 2004-09-22 | FITNESS FOR DUTY REPORT A licensed employee was determined to be under the influence of alcohol. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2004-09-22
41060 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-09-19 | 2004-09-21 11:17 | 2004-09-21 | AGREEMENT STATE REPORT OF DAMAGE TO SOIL MOISTURE DENSITY GAUGE The following information was provided to the NRC from the Florida Bureau of Radiation Control via e-mail. A Troxler soil moisture density gauge (Model #3411-B; Serial #8598) was damaged when it was run over by a front end loader. The source rod was broken off and the cesium source was detached from the rod. Investigators searched and recovered the source. The gauge and source will be sent to Troxler for repair. No further action will be taken on this incident. The Troxler source strength is 8 millicuries Cesium-137 and 40 millicuries Americium/Beryllium. There were no personnel exposures. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-09-24
41059 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-09-20 13:45 | 2004-09-20 20:56 | 2004-09-20 | FITNESS FOR DUTY REPORT A contract employee was determined to be under the influence of illegal drugs during a reinstatement urinalysis test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2004-09-20
41058 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-09-20 08:30 | 2004-09-20 14:42 | 2004-09-20 | AGREEMENT STATE REPORT OF THEFT OF FOUR MOISTURE DENSITY GAUGES The following information was provided by the State of California Department of Health Services via e-mail: "Four nuclear moisture density gauges were stolen from a locked construction trailer near Simi Valley (Ventura County, CA) over the weekend of 9/18-19/04. In addition to the gauges, the thieves stole other equipment in the trailer belonging to the licensee (Construction Testing and Engineering) as well as construction equipment from a number of other contractor trailers at the construction site. Two of the nuclear gauges were Campbell Pacific Nuclear model MC3 (serial numbers # M390104780 and # M300105431), one was a Troxler model 3440 (serial # T34417651), and the fourth was a Troxler model 3411B (serial # T3414200). Each gauge contained small quantities of the radioactive materials cesium-137 and americium-241. While it is possible to utilize radioactive materials from a large number of such gauges to make a terrorist radioactive dispersion device (RDD), this theft does not appear to have targeted the nuclear gauges, but rather to have included the nuclear gauges in a theft motivated by the resale potential of the general construction materials that were taken. The thefts are being investigated by the Simi Valley police, who reported that there have been a number of such thefts of construction equipment that have occurred in the area, and it is possible that the equipment is resold in Mexico. "DHS/RHB [Department of Health Services Radiological Health Branch] inspected this facility within the last few weeks, and did not identify any significant security issues related to the storage of the nuclear gauges at this site. The theft was reported to the federal government (Nuclear Regulatory Commission), who reviews such reports for possible national trends. Because of the possibility that the stolen materials may be resold in Mexico, the U.S. Nuclear Regulatory Commission (NRC) was requested to notify Mexican radiological authorities of the theft." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-09-23
41057 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-09-20 09:00 | 2004-09-20 09:45 | 2004-09-20 | STOLEN SOIL MOISTURE DENSITY GAUGE The following information was received via e-mail. The theft occurred at a temporary job site. The shipping container for the moisture density gauge was found to have the hasp pried off and the case and gauge stolen. The gauge was last seen at close of business on September 17, 2004, and discovered stolen on September 20, 2004. The keys were not taken. The police have been notified. The owner is considering offering a reward. The State of Florida is investigating. The moisture density gauge was a Troxler Model 3440 (serial #25279). Source activity is listed at 8 millicuries Cesium-137 and 40 millicuries Americium-241. The Florida Bureau of Radiation Control and the State Warning Point were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-09-23
41056 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2004-09-19 09:34 | 2004-09-19 12:03 | 2004-09-19 | OFFSITE NOTIFICATION DUE TO SIREN ACTIVATION "At 0934 CDT on 9/19/2004, the Unit 1 and Unit 2 Control Rooms began receiving phone calls reporting an actuation of emergency sirens in the Russellville area. A phone call was made to the Arkansas Department of Health, who controls actuation of the sirens, and the reported that they had indications of the sirens alarming. They suspect that power fluctuations in the area led to the inadvertent alarms. This report is being made in accordance with ANO Reporting Guidelines "News Release or Government Agency Notification" and 10CFR50.72(b)(2)(xi) since there was a notification of state/county agencies of inadvertent actuation of part of the public notifications." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-19
41054 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-09-19 04:56 | 2004-09-19 07:46 | 2004-09-19 | MANUAL REACTOR TRIP IN RESPONSE TO INDICATION OF DROPPED CONTROL RODS The following was received from the licensee via facsimile: "While operating at 100% power, the Watts Bar Unit 1 reactor was manually tripped at approximately 0456 EDT on September 19, 2004, in response to an apparent four dropped rods in control bank 'B'. The cause of the dropped rods is being investigated. "Safety systems functioned as expected in response to the trip. All control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated as designed in response to the trip. One reactor coolant pump (RCP) did not transfer to its alternate power supply. "The manual actuation of the Reactor Protection System (RPS) is being reported as a four hour report under 10 CFR 50.72 (b)(2)(iv). The actuation of the Auxiliary Feedwater System (an engineered safety feature) is being reported as an eight hour report under 10 CFR 50.72 (b)(3)(iv). Notification to NRC was made by Rick O'Rear at 0744 EDT. "The NRC Senior Resident Inspector was notified of this event." The licensee also reported that the reactor is being maintained at the normal temperature and pressure for this condition. All station service electrical systems and the emergency diesel generators are available and in normal configuration. All emergency core cooling systems are available. Decay heat is being removed using steam dump to the main condenser and feedwater to the steam generators is being provided by the electric main feedwater pump. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-09-19
41053 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-18 20:09 | 2004-09-19 00:26 | 2004-09-19 | LOSS OF SAFETY PARAMTER DISPLAY SYSTEM (SPDS) "On 09/18/04, Units 1 & 2 a simultaneously lost their control room's Safety Parameter Display System monitors for approximately 70 minutes before their were returned to service. This is considered a major loss of assessment and communication capability for greater than one hour. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(3)(xiii)." The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 80 | 0 | 100 | 80 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-09-19
41052 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2004-09-17 14:34 | 2004-09-17 14:38 | 2008-05-13 | ALERT DECLARED DUE TO TORNADO WARNINGS FOR CAMPBELL COUNTY, VIRGINIA *********************************************************************************************************************************** THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. *********************************************************************************************************************************** Tornado Warnings were issued for Campbell County, Virginia and an Alert was declared at 1434 EDT. The facility activated its Emergency Operations Center, secured operations and materials, and subsequently sheltered employees. The NRC was not placed in a Response Mode. Additional notifications: EPA/NRC (Melby), HHS (Roger) * * * UPDATE AT 1521 EDT ON 09/17/04 FROM MYRTLE AKRES TO MIKE RIPLEY * * * The Tornado Warnings were cancelled, and the Alert was terminated. Notified RDO (Boland), NMSS EO (Essig), IRD Manager (Wilson), OC (Outlaw), PAO (Hayden), DHS, FEMA, DOE, EPA/NRC, USDA, and HHS. * * * UPDATE ON 05/13/08 BY J.KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. *********************************************************************************************************************************** | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 2 | VA | FUE |  | 70.32(i) |  |  |  | 0 | 2008-05-13
41051 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2004-09-17 11:15 | 2004-09-17 13:30 | 2004-09-17 | OFFSITE NOTIFICATION - COLIFORM BACTERIA FOUND IN DRINKING WATER "Positive coliform in Eagles Den drinking water [unused, onsite building]. Confirmed by backup sample." The licensee notified the Maryland Department of the Environment and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-17
41050 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-09-17 10:30 | 2004-09-17 12:19 | 2004-09-17 | LOSS OF SIREN CAPABILITY "[Oconee is] unable to activate the siren system from the Oconee Law Enforcement Center due to the loss of power. The siren system can be activated from the backup location at Oconee Nuclear Station." Oconee is working to restore power. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-09-17
41049 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-09-17 05:00 | 2004-09-17 11:45 | 2004-09-17 | LOSS OF EMERGENCY SIREN CAPABILITY AND NOTIFICATION OF OFFSITE AGENCY "On Sept. 17, 2004, with Watts Bar Unit 1 at 100% power, the main control room was notified that the 99 sirens which make up the Public Prompt Notification System were not functional. The system uses two repeaters to control the sirens. As the remnants of Hurricane Ivan were passing through the Tennessee River Valley one of the repeaters (Pone Knob) was found to be without power around midnight. The siren system operators confirmed the second repeater (Grandview) was still functioning. Approximately 5:00 a.m., however, communications were lost with the second repeater. A maintenance crew was dispatched to the second repeater on loss of communications and they determined the radio transmitter was not functioning at 0955 and Watts Bar was immediately notified. This event is reportable under 10 CFR 50.72(b)(3)(xiii) as a loss of emergency preparedness capability. . "As a result of the above siren loss, TVA notified the Tennessee Emergency Management Agency (TEMA) at 10:13a.m. Sept. 17, 2004. This government agency notification is reportable under 10 CFR 50.72(b)(2)(xi). No TVA press release is planned and TVA is not aware of any specific actions planned to be taken by TEMA. Maintenance activities to restore power to the first repeater station by the use of a portable generator are underway." The 99 sirens constitute 100% of the emergency siren capability. The licensee had no estimate for completion of repairs and restoration of the siren capability. The licensee informed the State of Tennessee and the NRC Resident Inspector. * * * * UPDATE FROM S. SMITH TO M. RIPLEY 1350 ET 09/17/04 * * * * Restoration of power by use of a portable generator has been completed, reducing the number of non-functional sirens to seven of ninety-nine. The licensee informed local and State authorities, and the NRC Resident Inspector. Notified R2 DO (A. Boland). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2004-09-17
41048 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-09-17 10:00 | 2004-09-17 11:31 | 2004-09-17 | APPARENT PRESSURE BOUNDARY LEAKAGE IDENTIFIED ON STEAM GENERATOR BOWL DRAINS "On September 16, 2004 examinations of the steam generator (SG) bowl drains (SGBDs) for the 2A, 2C and 2D SGs were performed as part of the Alloy 600 program during 2EOC13. These examinations determined that the 2C and 2D SGBDs had leakage and the leakage appeared to be pressure boundary leakage. The 2A SGBD examination determined that the ASME code acceptance limits were satisfied. An evaluation of the leakage indications determined that the leakage had existed for some time prior to the Unit 2 shutdown. The evaluation of this condition on September 17, 2004, determined that this met the reportability criteria of 10 CFR 50.72 (b)(3)(ii)(A). Unit 2 is currently in MODE 6 and this event has no impact on current plant operation. Engineering and plant management are evaluating repair methods to be completed during this refueling outage. This event is not applicable to Unit 1 because the Unit 1 steam generators are of a different design and do not have a drain line in the bottom channel head." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-09-17
41047 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2004-09-17 06:24 | 2004-09-17 10:43 | 2004-09-17 | OFFSITE NOTIFICATION TO ARMY CORPS OF ENGINEERS "Utilization of the Missouri river water in support of the dry cask storage (ISFSI) project by Hawkins Construction Company was done in violation of national permitting requirements. Two tubes were placed in the river connected to two pumps: One small line (about 2.5 in.) used to supply water for the cure wetting of the concrete pours and one large line (6-8 in.) connected to a large pump for filling of water trucks for dust suppression and other utility uses. "The United States Army Corps of Engineers, who manages the river and its utilization, requires approval of such uses through a national permitting process. "This condition was identified during a routine site and environs tour. The Omaha Public Power District environmental affairs group has contacted the Army Corps of Engineers on the issue. The use of Missouri river water by the contractor has been terminated. Another source of water will be used to complete the project." The licensee informed the U.S. Army Corps of Engineers and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-17
41046 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-09-16 23:18 | 2004-09-17 00:37 | 2004-09-17 | OFFSITE NOTIFICATION TO PUBLIC SERVICE COMMISSION The following was received from the licensee via facsimile: "Indian Point Unit 2 synchronized to the grid at 2318 on September 16, 2004. NRC notification required per Item 44 of IP-SMM-LI-108, Event Notification and Reporting, due to notification of other government agencies of Indian Point Unit 2 synchronizing to the grid. This is a 4-hour non-emergency event notification per 10 CFR 50.72 (b)(2)(xi)." The licensee will notify the NRC Resident Inspector. | 8 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-17
41045 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2004-09-16 20:10 | 2004-09-16 23:30 | 2004-09-16 | OFFSITE NOTIFICATION DUE TO OIL SPILL AND FIRE "At 2010, Turkey Point 1/2 (Fossil Plant) hazardous Material Coordinator contacted the Florida Department of Environmental Resources and informed them of an oil spill with attending fire that occurred at Turkey Point Unit 2 (Fossil Plant) on 09/16/04. "At 1654, Turkey Point Unit 2 (fossil Plant) developed an oil leak and fire on the third level burner deck. The fire was extinguished by automatic deluge system and fire team members. Less than 50 gallons of oil leaked and was contained on the third level burner deck." Turkey Point Units 3 and 4 were not affected. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-16
41044 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2004-09-16 11:30 | 2004-09-16 13:57 | 2004-09-16 | SURFACE CONTAMINATION ON RADIOACTIVE MATERIAL PACKAGE EXCEEDING LIMITS The Department of Veterans Affairs, National Health Physics Program reported a package that exceeded the limits for removable radioactive surface contamination. The package was received on September 16, 2004, by a permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. The permittee is the Clement J. Zablocki VA Medical Center, Milwaukee, Wisconsin. This event is reported under 10 CFR 20.1906(d)(1) in that the package, an ammo box being used to deliver radioactive materials, had approximately 11,000 disintegrations per minute per square centimeter removable radioactive contamination on the outside. The contamination was limited to one small spot on the ammo box exterior. The interior of the box was not contaminated. The contamination was identified as 99M-Tc. The Cardinal Health Nuclear Pharmacy Services delivered the package. The permittee Radiation Safety Officer notified the vendor about the package. There was no personnel contamination involved. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2004-09-16
41043 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-09-15 16:00 | 2004-09-16 12:17 | 2004-09-16 | POTENTIAL VIOLATION OF LICENSE CONDITION - OPERATION ABOVE LICENSED POWER LIMIT "This 24 hour Notification to the NRC Operations Center is being made per Operating License No. NPF-39, Section 2.F to report a potential violation of the requirements contained in Section 2. C of Limerick Unit 1 license. "On September 15, 2004 at 1600 Hrs. it was determined during an investigation of megawatt output differences between the two LGS Units, that LGS Unit 1 secondary plant parameters were identified as being outside of their expected range. This change occurred over several months at the rate of 0.1 %/month for a total potential error of 0.4%. This data indicates that LGS1 could possibly be above the operating license limit of 3458 MWth. Unit 1 power was reduced to 99% power to 3423 MWth as of 1618 to provide margin to licensed thermal power limit. "A written report is required within 30 days in accordance with 10 CFR 50.73." The licensee has notified the NRC resident inspector. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2004-09-16
41042 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-09-14 | 2004-09-15 11:34 | 2004-09-15 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "BBC&M Engineering, Ohio License # 31210 25 0006, reported to ODH/BRP that a Troxler moisture density gauge was stolen from a tool trailer at a temporary job site sometime during the overnight period between Tuesday evening, 9/14/04, to Wednesday morning, 9/15/04. "Other work tools belonging to the licensee were also taken from the trailer. The theft was discovered when workers returned to work on Wednesday morning. "The job site was at the I-270/SR-161 highway construction site in northeast Columbus, Ohio. Police have been notified. "The gauge was a Troxler Model 3430, Serial number 21035, containing an 8 mCi Cs-137 source and a 40 mCi Am-241 source. The gauge was stored in its locked storage case and the source was locked within the device. The storage case was stored in a locked tool trailer at the work site and was chained to the frame of the trailer. The locks to the trailer and storage case were broken and the gauge was taken from the storage case." OH report No.: OH040004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2004-09-20
41041 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-09-15 01:42 | 2004-09-15 03:13 | 2004-09-15 | NEW YORK STATE NOTIFIED THAT UNIT 2 WAS TAKEN OFFLINE FOR REPAIRS Unit 2 was taken offline for repairs to "21" Main Feed Discharge Check Valve. The licensee will maintain Unit 2 in mode 2 at approximately 2% power for the duration of repairs. The licensee informed the NY State Public Services Commission and the NRC Resident Inspector. * * * UPDATE 1045 EDT ON 9/15/04 FROM JOHN BAKER TO ARLON COSTA * * * The above report was corrected to remove inaccurate information. Notified R1DO( Doerflein) and NRR EO (Haney). | 2 | 0 | 0 | 70 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-15
41040 | 0 | WATERFORD | 3 |  |  | [3] CE | 2004-09-14 16:04 | 2004-09-14 17:32 | 2004-09-16 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WATCH IN ST. CHARLES PARISH The following information was provided by the licensee via facsimile: "Waterford 3 entered Unusual Event Emergency Classification due to the National Weather Service declaring a hurricane warning for St. Charles Parish at 1600 CDT." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 09/16/04 AT 0635 EDT FROM KENNY CAMBRE TO STEVE SANDIN * * * Waterford 3 is no longer in an unusual event [as of 0502 CDT] . Hurricane watch/warnings for St. Charles Parish has been lifted at 0400. The licensee notified the NRC Resident Inspector. Notified NRC Region 4 IRC, FEMA (Kevin Biscoe), NRR (Catherine Haney), IRD (Peter Wilson), DHS (Frank Griggs). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | LA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-14
41039 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-09-14 15:00 | 2004-09-14 16:44 | 2004-09-14 | OFFSITE NOTIFICATION TO STATE OF NEW JERSEY The following information was received from the licensee via facsimile: "Notified New Jersey Department of Environmental Protection of a planned shutdown of OCNGS [Oyster Creek Nuclear Generating Station] scheduled to commence at 2000 hrs. [EDT] on 9-14-04." The licensee has notified the NRC Resident Inspector. | 40 | 0 | 0 | 40 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-14
41038 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-09-13 15:46 | 2004-09-13 18:32 | 2004-09-13 | OFFSITE NOTIFICATION DUE TO MINOR OIL SPILL "While performing routine ditch cleaning maintenance (on Sept. 13, 2004), a faulty hydraulic hose on a bulldozer caused a small release of hydraulic oil near a drainage ditch adjacent to Braidwood Station property. The hose was intact prior to maintenance beginning on the morning of Sept. 13. "It is estimated that 10-15 gallons of oil spilled on the ground, with a very small portion of the oil (less than one gallon) going into the drainage ditch itself. The oil on the ground has been removed. A compensatory oil boom was placed downstream of the spill in the ditch to collect the small amount of oil that went into the ditch. A thorough walk down of the ditch, downstream from the spill, revealed no evidence of oil. The Station will investigate why the hose failed and what actions can be taken in the future to prevent recurrence. "Per Station procedures, official notifications were made to the Illinois Emergency Management Agency, and the National Response Center. In addition, Exelon communications notified the Village of Godley, the Godley Park District, the Village of Braceville, and the Braceville Fire Department District. Residents in the area were notified through personal visits." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-13
41037 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-09-12 15:55 | 2004-09-12 19:14 | 2004-09-12 | BOTH TRAINS OF REACTOR BUILDING SPRAY INOPERABLE FOR THREE MINUTES The following information was obtained from the licensee via facsimile: "With the 1A Reactor Building Spray (RBS) train declared inoperable, due to an inoperable ES [Engineered Safeguards] digital channel, the suction valve to the 1B RBS train was stroked closed, rendering the 1B RBS train inoperable, concurrent with the 1A RBS train inoperability. The duration of the valve stroke, and dual RBS train inoperability was 3 minutes. This dual RBS train inoperability resulted in entry into TS [Technical Specification] 3.0.3 for the 3 minute duration of the valve stroke. "At the time of this event, all three Reactor Building Cooling Unit (RBCU) trains were operable. The RBCUs provide a redundant, post-accident, containment heat removal function to the RBS trains. However, the RBS system is credited with post-accident iodine removal for the maximum hypothetical accident. Additionally, should an Engineered Safeguards actuation have occurred during the 3 minute stroke time, the RBS pumps in the 1B train would have started without the suction valve being fully open. This degraded suction flow could have impacted proper RBS pump operation in the event of an ES actuation. "The 1B RBS train suction valve stroke was completed before it was noted that the valve stroke had resulted in the inoperability of the 1B RBS train, concurrent with the inoperability of the 1A RBS train. The 1B RBS train suction valve has been returned to an open condition and the 1B RBS train is currently operable." The operations personnel were performing valve stroke time surveillances when the event occurred. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-09-12
41036 | 0 | TRANSNUCLEAR, INC |  |  |  |  | 2004-09-10 17:00 | 2004-09-12 11:37 | 2004-09-14 | MISPLACED IMPORT RADIOACTIVE SHIPMENT On September 4, 2004 a radioactive shipment, under a General Licensee, was flown into JFK Airport via Air France Flight # 6492 (flight arrived at 2345 hours). The radioactive shipment, 6 pound Bio Pack package with White Label 1 with a Transportation Index (TI) number of 0 , went through customs. On September 10, 2004 Transnuclear, Inc sent a freight truck to pick up the shipment at Air France. Air France personnel were unable to locate the package and they said that they had misplaced the package. The BioPack contains 4 sample tubes of uranium hexafluoride. The four sample tubes are LEU. Total is 0.038 kg of uranium hexafluoride of which 0.025 kg is LEU uranium. Transnuclear, Inc is supposed to ship the BioPack to Framatome ANP located in Richland, WA. * * * Update on 09/14/04 at 0926 EDT by John Mangusi taken by MacKinnon * * * Transnuclear,Inc. was notified by email that the package had been located at the JFK Air France Terminal. Transnuclear, Inc. will arrange to pick up the package and eventually deliver it to Framatone ANP located in Richland, WA. NRC (John Wray) was notified of this by John Mangusi. NRC R1DO (Larry Doerflein), NRC R4DO (Dale Powers) & NMSS EO (M. Burgess) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | NY | MAT | [5 empty] | 0 | 2004-09-12
41035 | 0 | NATIONAL RESPONSE CENTER |  |  |  |  | 2004-09-11 21:38 | 2004-09-12 02:55 | 2004-09-12 | VAN CONTAINING A RADIOGRAPHY CAMERA DESTROYED BY FIRE A van located near Well Pad Z in Prudhoe Bay, Alaska, carrying a iridium-192 radiography camera, caught fire and was destroyed. The radiography camera was housed in a fire proof container inside the van. A CANSPEC Radiation Safety Officer took surveys of the vehicle and found that there was no release. The radiography camera contained a iridium-192 source with an activity of at least 60 curies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | AK | MAT | [5 empty] | 0 | 2004-09-12
41034 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-09-02 11:30 | 2004-09-10 15:55 | 2004-09-10 | UNPLANNED CONTAMINATION EVENT Facility suffered a sewer blockage in the Waste Building on the morning of 09/02/2004. Soil waste removed to discover cause of blockage. It was immediately determined that the line was not connected to the sanitary sewer. The line has been in place for 12 years for the disposal of H-3 and C-14 waste. An estimated total of 100 millicuries of these radioactive materials have been disposed during the last 12 years. Maximum soil contamination discovered was measured at 0.1 millirem per hour. No workers or equipment were contaminated. The University immediately let a contract for cleanup of the contaminated soil and repair of the sewer line. The area was placed behind barrier tape and covered with plastic to prevent blowing or erosion. Initially, the soil was removed and barreled by a licensed Texas decontamination firm. A second break in the line was discovered near the building that may require soil removal by covered roll-off container. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-09-15
41033 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-09-09 08:45 | 2004-09-09 16:10 | 2004-09-09 | TEXAS AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE The following information was received from Texas Department of State Health Services: "At approximately 8:45 a.m. the gauge operator had just completed a density test on the site of Wheatley High School, where a new high school is being constructed, when a bulldozer, belonging to another contractor working at the job site, made a sudden and unexpected move toward the operator, who was performing calculations beside the gauge. During the movement the bulldozer operator dropped the blade of the vehicle which impacted the Troxler Model 3430, Serial No. 25129 moisture density gauge. The gauge was crushed with damage to the housing. The gauge contained two sealed sources: Cs-137, nominal 8 millicuries, Serial No. 75-7305 and Am-241/Be, nominal 40 millicuries, Serial No. 47-21337. The sources were not damaged nor leaking. The gauge control rod was in the up and locked. A survey of the area determined that no leakage where the gauge was crushed or to the blade of the bulldozer. The gauge was transported to Component Sales and Services (L02243-000) for leak testing and determination of possible repair. The gauge was determined to be not repairable. The gauge was transferred to Component Sales and Services for disposal. The gauge was last leak tested on April 4, 2004, with negative test results." Texas Incident No. I-8161. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-09-14
41032 | -1 | PRINCETON UNIVERSITY |  |  |  |  | 2004-09-01 | 2004-09-09 14:01 | 2004-09-14 | TWO TRITIUM EXIT SIGNS MISSING The two signs were discovered missing when an electrical contractor failed to turn over the exit signs to the University's Radiation Safety Officer. The signs were removed during building renovation that started in June. The contractor apparently stored the signs in a box under his desk and the box was removed and believed disposed of as trash. The licensee will follow-up in a written report. * * * RETRACTION PROVIDED BY S. DUPRE TO JEFF ROTTON ON 09/14/04 AT 1430 EDT * * * On 09/13/04 at 1014 EDT, the licensee was notified by the electrical contractor, that the missing exit signs were located in a gang box used for the Alexander Hall job and stored in the contractor's warehouse. The signs were returned to the licensee into the custody of the Environmental Heath and Safety Office, where they are currently stored awaiting return to the manufacturer. Notified R1DO (Doerflein), and NMSS EO ( Moore ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-09-09
41031 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-09-07 | 2004-09-09 11:45 | 2004-09-09 | WASHINGTON STATE AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION The following information was received from Washington State Department of Health: "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "STATUS: new "Licensee: Saint Mary Medical Center "City and State: Walla Walla, Washington "License Number: WN-M0101-1 "Type of License: Medical Combination "Date of Event: September 7, 2004 "Location of Event: Licensees facility in Walla Walla, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "The licensee's radiation safety officer notified the department that licensee staff had observed an anomaly after injecting a patient with Technetium (Tc) 99m, intended for a bone scan study. They had injected the proper patient with the apparent proper dose of 37.4 millicuries, Tc-99mHDP. When the patient returned approximately three hours later for the study, the patient showed no bone uptake but did have uptake in the liver and cardiac muscle. "Two unit doses were received on September 3rd from the nuclear pharmacy for two different patients. Both patients were injected on the same day. The second patient showed a nominal bone uptake and the study was performed per procedure. "The shipping documents and dose calibrator check indicated the dose was as ordered. The nuclear pharmacy was called and asked about the doses. The two doses had been drawn-up consecutively by the same pharmacist. The pharmacy was certain the order had been drawn, delivered and documented accurately. The licensee and pharmacy were unable to explain the anomalous first study. All information appears to corroborate that the study should have been as expected. "A repeat scan was performed. This dose localized as expected and the study gave diagnostic quality images. "On-site investigation by the department is not planned. "No media attention noted. "Notification Reporting Criteria: 10 CFR Part 35.33(a) "Isotope and Activity involved: Technetium (Tc) 99mHDP, 37.4 mCi "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): Liver and Cardiac Muscle, dose estimate to be determined, the licensee indicated that the patient should receive adverse consequences as a result of the anomaly. "Lost, Stolen or Damaged? (mfg., model, serial number): N/A "Disposition/recovery: A second study was ordered and performed as expected. "Leak test? N/A "Vehicle: N/A "Release of activity? N/A "Activity and pharmaceutical compound intended: 37.4 mCi, Tc-99mHDP "Misadministered activity and/or compound received: [as far as could be determined] 37.4 mCi, Tc-99mHDP "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual); consequences: It is anticipated that the patient will receive no adverse health effect from the anomalous dose. "Was patient or responsible relative notified? Both were notified. "Was written report provided? Yes, dated September 8, 2004. "Was referring physician notified? Yes "Consultant used? No" This event is assigned Washington event number WA-04-053 and is entered in NMED. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-09-14
41030 | 0 | MISSOURI DEPT. OF TRANSPORTATION |  |  |  |  | 2004-09-09 07:45 | 2004-09-09 10:24 | 2004-09-09 | MISSOURI DEPT. OF TRANSPORTATION PICKUP TRUCK CARRYING A TROXLER GAUGE WAS INVOLVED IN AN ACCIDENT. At 0745 CDT a Missouri Department of transportation pickup truck carrying a Troxler model # 3430 moisture density gauge was involved in an accident. The Troxler gauge was within it case locked inside a metal locked box bolted to the bed of the pickup truck. The open bed pickup truck was traveling on Route E, located between Leeton and 23rd highway in Johnson county, when it was side swiped by another vehicle. The pickup truck slid down the side of a hill. The front quarter panel of the truck was damaged and the truck's side mirror was knocked off. The occupants of the pickup truck got out of the truck and went to the back of the truck, opened the locked metal box and observed that the Troxler moisture density gauge was still in its container undamaged. The Troxler gauge contains 0.3 Gigabecquerels (GBq) of cesium-137 and 1.48 Gigabecquerels (GBq) of americium-241/Be. Nobody was injured in the accident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | TRA | [5 empty] | 0 | 2004-09-09
41029 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-09-09 04:24 | 2004-09-09 09:31 | 2004-09-09 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY At 04:24 EDT, the Control Room Super Particulate Iodine Noble Gas (SPING), Stack Monitoring System, terminal and the associated terminal in the Technical Support Center (TSC) began printing transmit and receive errors. As a result, all SPINGs were declared inoperable and associated Technical Requirements actions entered for alternate sampling. Review by Nuclear Regulatory Affairs and Shift Supervisor considers the occurrence a loss of Emergency Assessment Capability and is therefore reportable under 10 CFR 50.72(b)(3)(xiii). Licensee is taking samples every 4 hours. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-09-09
41028 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-09-09 01:06 | 2004-09-09 03:20 | 2004-09-09 | TURBINE TRIP/REACTOR TRIP "Salem Unit 2 experienced a Turbine Trip > P-9 which initiated a Reactor Trip. All rods fully inserted. Aux Feedwater auto start initiated on steam generator low-low level. The cause of the turbine trip is Generator Diff [Differential Current] or Loss of Field. Decay heat removal is via the steam dumps to the main condenser. All safety related systems are available and functioned as designed. The 500 KV breaker 2-10 was cleared and tagged prior to the trip. Upon the turbine/reactor trip, the 500KV breakers 1-9 and 9-10 opened as designed. Due to the 2-10, 1-9, 9-10 breakers being opened, the 500 KV transmission line 5037 is de-energized. Two offsite power sources are available and all 3 Emergency Diesel Generators are operable. The 5037 line will be energized following restoration from scheduled maintenance. There were no personnel injuries." The licensee stated that the NRC resident inspector and the local township were notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-09-09
41027 | -1 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-08 14:45 | 2004-09-08 18:23 | 2004-09-30 | EMERGENCY FEEDWATER SYSTEM ACTUATION "At 1445 on September 8, 2004, while in Mode 3 after an unplanned reactor trip during tropical storm Frances, Crystal River Unit 3 experienced a re-actuation of the B-Train of the Emergency Feedwater System. The Emergency Feedwater System had previously actuated during a Loss of Offsite Power experienced during Hurricane Frances and the B-Train actuation had procedurally been bypassed as part of the plant recovery. While In the process of restoring a Main Feedwater Pump to an operating condition, the signal bypassing the B-Train Emergency Feedwater actuation was momentarily removed due to unusual plant conditions present during recovery from the loss of power This resulted in the re-actuation of the B-Train of Emergency Feedwater. This condition is 8-Hour reportable per 10CFR50.72(b)(3)(iv)(B)(6). The re-actuation of the B-Train of Emergency Feedwater did not have a significant impact on plant operation and the associated equipment has been returned to a standby condition." The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM JOHN ADDISON TO BILL HUFFMAN AT 1402 EDT ON 9/30/04 * * * The following information was provided by the licensee via facsimile: "At 1823 [hrs. EDT] on 9/8/04, Crystal River Unit 3 made an 8-hour ENS notification in accordance with 10CFR50.72(b)(3)(iv)(A) and 50.72(b)(3)(iv)(B)(6) concerning re-actuation of the B-train of the Emergency Feedwater System. The Emergency Feedwater System had previously actuated during a Loss of Offsite Power experienced during Hurricane Frances and the B-Train actuation had procedurally been bypassed as part of the plant recovery. While in the process of restoring a Main Feedwater Pump to an operating condition, the signal bypassing the B-Train Emergency Feedwater actuation was momentarily removed due to unusual plant conditions present during recovery from the loss of power. This allowed for a re-actuation of the B-Train of Emergency Feedwater based on a loss of Main Feedwater Pump signal. However, the two Main Feedwater Pumps had not been operating since the loss of offsite power that occurred on 9/6/04. The A-Train Emergency Feedwater System had been operating continuously since the initial actuation on the loss of offsite power and continued to operate during and after the re-actuation of the B-Train. Re-actuation of the B-Train has been determined to be an invalid actuation in accordance with the guidance of NUREG-1022, and therefore EN 41027 is retracted." The licensee has informed the NRC resident inspector. R2DO (Lesser) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-09-08
41025 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-09-08 05:56 | 2004-09-08 08:41 | 2004-09-08 | OFFSITE NOTIFICATION - HIGH WATER FLOW FROM LAKE ROBINSON DUE TO HEAVY RAIN "On 09/08/2004, at 0556 EDT, the H. B. Robinson site reached a condition that warranted notification of local and state government agencies of conditions with potential public safety consequences. "Due to rain from Tropical Storm Frances, the Lake Robinson water level rose to levels that required opening of valves to increase the discharge flow from the lake. At 0556, the discharge flow exceeded 1100 cubic feet per second. Unit 1 (adjacent fossil unit) procedures require the notification of local and state government agencies when the discharge flow exceeds this rate, due to the potential for downstream flooding. Notification of local and state agencies began at 0557 EDT. No press or media releases have been made. "Unit 2 continues to operate and there is no threat to plant equipment or operation due to this condition." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-08
41024 | -1 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-08 01:00 | 2004-09-08 03:11 | 2004-09-09 | POTENTIAL REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAK LOCATED "At 0100 on September 8, 2004, while in Mode 3 conducting a Reactor Building walkdown after an unplanned reactor trip during Tropical Storm Frances, Crystal River Unit 3 identified a potential Reactor Coolant System pressure boundary leak located on a weld associated with a pressurizer level sensing line (upstream of reactor coolant isolation valve RCV-75). The cause of the leak is not known at this time, and the leak did not have a significant effect on plant operation. The last unidentified leak rates that were completed prior to the plant shutdown were 0.10 - 0.13 gpm. This defect in the primary coolant system is unacceptable per ASME Section XI. The condition is 8-Hour reportable per 10CFR 50.72 (b)(3)(ii)(A). The plant will be cooled down to Mode 5 and additional inspections and necessary repairs implemented. Dry boron crystal deposit are on the sensing line upstream of RCV-75 . See similar event reported by Crystal River Unit 3 on 10/04/03 (event # 40222) The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTED ON 9/9/04 AT 0424 EDT FROM LARRY MOFFATT TO GERRY WAIG * * * "At 0311 on 9/8/04, Crystal River Unit 3 made an 8-Hour ENS notification in accordance with 10CFR50.72 (b)(3)(ii)(A) concerning a potential Reactor Coolant System pressure boundary leak (Event Notification # 41024). The leak was presumed to exist based on the presence of white, crystalline material deposited on the pipe. The material has been sampled and does NOT contain boron. The presumed leak site has been cleaned and visually inspected with no evidence of a defect in the weld joint or pipe. These additional inspections have demonstrated that the material deposited on the pipe does NOT constitute pressure boundary leakage, and therefore EN 41024 is retracted." The licensee has notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-09-08
41023 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-06 11:50 | 2004-09-06 12:44 | 2004-09-06 | AUTOMATIC REACTOR TRIP FOLLOWING PARTIAL LOSS OF OFFSITE POWER "At approximately 1150 [EDT], CR3 Site experienced a 230KV 'B' Buss loss. The resultant loss of power was a loss of both non-vital 4160V busses. All RCPs tripped and a reactor trip occurred. The plant is stable on natural circulation cooling. "This report is based on the Reactor Protection System Actuation and Specified System Actuation (Emergency Feedwater)." The "B" ESF 4160KV Bus deenergized resulting in an autostart of the "B" EDG, as expected. Natural Circulation has been confirmed with both Steam Generators [SGs] receiving Emergency Feedwater [EFW] via both the Turbine-Driven and Diesel-Driven EFW Pumps. The SGs are using the Atmospheric Dumps to remove decay heat. There was no known SG tube leakage prior to the transient. The cause for the partial loss of offsite power is under investigation. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-09-06
41022 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-09-05 17:10 | 2004-09-05 17:35 | 2004-09-07 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING Crystal River declared a Notification of Unusual Event due to hurricane warning in effect for the plant and surrounding areas. All safety systems are operable. The licensee notified the NRC Resident Inspector and the State emergency response organization. * * * UPDATE AT 1027 ON 9/7/04 R TYRIE TO W GOTT * * * The licensee terminated the Notification of Unusual Event at 1017 today, 9/7/04. The basis of the termination is that the hurricane warning was lifted yesterday 9/6/04 and offsite power has been restored. Notified R2 (Pribish), NRR (Reis), IRD (Wessman), DHS (Akers), FEMA (Kuzia). | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-05
41021 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-04 23:50 | 2004-09-05 00:55 | 2004-09-05 | LOSS OF EMERGENCY COMMUNICATIONS DUE TO SEVERE WEATHER "At approximately 2350 [ET] on September 4, 2004 the ENS [Emergency Notification System] direct connection with the NRC was lost and the Emergency Data Acquisition Display System (ERDADS) link between Unit 1 and the NRC was also lost. By 0020 hours the ENS connection had been recovered [using local Florida Power and Light telephones]. The ERDADS link to unit 2 was still out of service from earlier in the day due to a failure of the modem for this circuit. It appears upon initial troubleshooting that the unit 1 modem is also now failed. The ENS and ERDADS were in active use at the time of the loss for the Unusual Event condition resulting from the severe weather conditions associated with hurricane Frances. The modems are serviced by NRC contractors. Repairs will be pursued once weather conditions allow access to the site." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Hot Standby |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-09-05
41020 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-09-04 13:45 | 2004-09-04 21:29 | 2004-09-04 | VIOLATION OF NUCLEAR CRITICALITY SAFETY CONTROL IN THE PROCESS BUILDING "At 1345 [CDT], on 09-04-04 the Plant Shift Superintendent was notified of a violation of Nuclear Criticality Safety (NCS) control in the C-337 process building. During Inspection of the RCW (Recirculating Cooling Water) line to the RCW/ R114 Differential Pressure alarm switches (DP switches) for the C-337 #5 Low Speed P&E (Purge and Evacuation) Pump, Instrument Maintenance discovered that the instrument line boss was plugged. This condition rendered both Independent DP switches incapable of performing their intended safety, violating an SRI (Safety Related Item) in Nuclear Criticality Safety Evaluation (NCSE) 039. The SRI requires that both DP alarms are to be functional while the P&E pump is Isolated from the cascade process system. The purpose of the SRI is to alert an operator to take actions within a 28 hour timeframe to prevent high moisture R-114 from leaking into the process gas system. The DP alarms had likely been nonfunctional for more than 28 hours when discovered. Clarity of the Instrument line boss was subsequently re-established and both DP alarms were returned to service. The R-114 was sampled and determined to be dry (low moisture content) within 4 hours of discovery, thereby re-establishing double contingency. "SAFETY SIGNIFICANCE OF EVENTS: While the R-114 was demonstrated to be dry, both OF alarms relied on for double contingency were disabled without the knowledge of the operators. "CONTROLLED PARAMETERS: Double contingency Is maintained by Implementing two controls on moderation. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on the DP switch alarming to alert the operator to take action to either verify the R-114 is dry or to isolate the RCW and remove the R-114 from the system in order to prevent water from leaking into the process gas system. This DP alarm was not maintained as functional. The DP alarm was put back In service and the R-114 was sampled and found to be dry. The SRI was not maintained and the control was violated but the process condition was maintained. "The second leg of double contingency is based on the independent DP switch alarming to alert the operator to take action to either verify the R-114 is dry or to Isolate the RCW and remove the R-114 from the system in order to prevent water from leaking into the process gas system. The independent DP alarm was not maintained as functional. The independent DP alarm was put back in service and the R-114 was sampled and found to be dry. The SRI was not maintained and the control was violated but the process condition was maintained. This re-established double contingency. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Both DP switches were returned to service and the R-114 was sampled and found to be dry within four hours time of discovery. "PGDP Problem Report No. ATR-04-3602; PGDP Event Report No. PAD-2004-22 "The Senior NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-09-04
41019 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-04 02:12 | 2004-09-04 05:40 | 2004-09-04 | LOSS OF COMMUNICATIONS - EMERGENCY RESPONSE DATA ACQUISITION DISPLAY SYSTEM "At approximately 02:12 on September 4, 2004, the St. Lucie Emergency Response Data Acquisition Display System (ERDADS) failed. At the time of the failure the communication link to the NRC was in use due to the unusual event classification for an approaching hurricane. The ERDADS was restarted and functioning correctly as of approximately 03:40. The NRC link to Unit 1 has been reestablished. The NRC link to Unit 2 has not been restored as of this time. There appears to be a problem with the Unit 2 modem and efforts are underway to troubleshoot and repair the problem." The Licensee notified the NRC Resident Inspector. | 42 | 0 | 0 | 42 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Hot Standby |  | Power Operation | Hot Standby |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-09-04
41018 | -1 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2004-09-04 01:56 | 2004-09-04 05:40 | 2004-09-17 | MANUAL REACTOR TRIP DUE TO STEAM GENERATOR LEVEL OSCILLATIONS "While reducing power in response to expected severe weather conditions from hurricane Frances, the reactor was manually tripped from 21% reactor power. The reactor was tripped because of significant swings in the 'B' Steam Generator level caused by erratic operation of the 'B' Feedwater Regulating Valve (FRV). All Control Element Assemblies fully inserted. Decay heat is currently being removed by Main Feedwater using the low power FRV bypass valves and Steam Bypass Control System (SBCS), maintaining RCS temperature at 532 degrees Fahrenheit. The unit will be maintained in a shutdown condition until repairs to the FRV are completed and the severe weather from Hurricane Frances abates. "All primary and secondary systems performed as expected with the exception of the SBCS. The SBCS consists of five pressure control valves, PCV-8801 through PCV-8805 with PCV-8801 a larger capacity valve and designed to open first. The remaining valves are designed to open in series with overlap through their operating ranges. PCV-8801 failed to open and PCV-8802, 8803, and 8804 did not appear to properly control RCS temperature. PCV-8805 was operated in manual to control [steam generator] pressure. The Licensee notified the NRC Resident Inspector. * * * RETRACTION FROM K. FREHAFER TO W. GOTT AT 1549 EDT ON 9/17/04 * * * "Florida Power and Light (FPL) is retracting this notification because the feedwater issues during the shutdown were not causal to the manual reactor trip. The St. Lucie Emergency Plan, requires that the units be taken offline prior to the onset of hurricane force winds onsite. In accordance with these requirements, St. Lucie Unit 2 was being taken offline prior to the arrival of hurricane Frances. Although automatic feedwater issues occurred during the downpower, the operators successfully took manual control of the main feedwater system. A reactor trip was not necessary to mitigate the condition, and continued operation and on-line troubleshooting would have been practical had the plant not been required to be shutdown for the approaching hurricane. The main feedwater control issues were not relevant factors during the planned plant shutdown/manual reactor trip. Therefore FPL is retracting this notification." The licensee notified the NRC Resident Inspector. Notified R2DO(Boland). | 0 | 0 | 0 | 0 | 21 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-09-04
41017 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2004-09-03 23:45 | 2004-09-04 02:05 | 2004-09-04 | RPS ACTUATION "On September 3, 2004, at 2345, the Reactor Scrammed as the result of an [Automatic Voltage Regulator] AVR trip relay. AVR Channel A was not operating at the time due to an earlier fault (0541, 9/3/04). The AVR trip relay caused a Main Generator trip which caused a Main Turbine trip. The Main Turbine trip causes a direct Reactor SCRAM on Turbine Valve position. RPS functioned properly and all rods inserted. MSIVs remain open with Reactor Level maintained in the normal band of 173 to 214 inches. Reactor Pressure is being controlled with the Main Turbine Bypass valves at 600 to 1050 psig. Isolations occurred as expected for Reactor Level 3." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-09-04
41015 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2004-09-03 13:30 | 2004-09-03 15:41 | 2004-09-03 | WI AGREEMENT STATE: LOSS OF CONTROL OF RADIOACTIVE MATERIAL "On Friday, September 3, 2004 at approximately 1:30 p.m., the Wisconsin Radiation Protection Section (RPS) received a telephone call from the University of Wisconsin - Madison (license number 25-1323-01) informing the section of a lost Ir-192 source that had been inadvertently shipped to the University of Arizona Medical Center, Tucson, AZ. "Preliminary Information From the Licensee "On Monday, August 30, 2004, the University of Wisconsin - Madison calibration lab had completed calibration of a Standard Imaging, Model 1000+ reentrant well chamber (ion chamber used to determine brachytherapy seed dose) and shipped it back to the chamber owner, the University of Arizona Medical Center. Shortly after arrival, the U.A. Medical Center discovered that the chamber contained a 0.4 mCi [milliCurie] Iridium-192 brachytherapy seed that had been used during calibration. The U.A. Medical Center subsequently notified the U.W. Madison of the incident on Friday, September 3, 2004. "The licensee estimates that the dose rate from an unshielded 0.4 mCi Ir-192 seed source would be approximately 0.192 mR/hr at 1 meter. The licensee believes that the chamber shielded the source so the dose rate on the surface of the shipping container was negligible." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2004-09-08
41014 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2004-09-03 12:50 | 2004-09-03 15:47 | 2004-09-03 | SC AGREEMENT STATE REPORT: STOLEN MOISTURE DENSITY GAUGE Upon returning from lunch, the King Asphalt Inc. technician noticed that the moisture density gauge had been missing from the storage box casing. The gauge was previously secured in the box casing stored on the pickup truck bed. The box locking mechanism appears to have been pried open in order to retrieve the gauge. The moisture density gauge is a Humboldt Model No.5001EZ, S/N 670, containing 11 milliCuries of Cs-137 and 44 milliCuries of Am-241:Be. A report of the stole gauge was filed with the Greenville, SC police. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2004-09-08
41013 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-09-02 14:29 | 2004-09-02 16:37 | 2004-09-02 | DIESEL FUEL SPILL IN CONTAINMENT FROM OVERTURNED EXCAVATOR Haddam Neck Plant reported that a 20 to 30 gallon diesel fuel oil spill occurred in the containment building from an overturned excavator performing decommissioning work in the containment building. The fuel oil has been contained using absorbent material and there was no release of fuel oil to the environment. No injuries occurred to any personnel. A recovery plan is being formulated by plant management at this time. Haddam Neck reported this event to the State of Connecticut - Department of Environmental Protection and to NRC Region 1 (John Wray). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-02
41012 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2004-09-02 14:15 | 2004-09-02 15:52 | 2004-09-02 | OFFSITE NOTIFICATION REGARDING RELEASE OF OXIDANT "On September 2, 2004 at 14:15 (CDT) the Duane Arnold Energy Center made notification to Mr. Mike Wade of the Iowa Department of Natural Resources regarding a release of free available oxidant (chlorine) to the Cedar River. Although, the initial indications show that this release did not exceed our NPDES discharge permit value, as stated by Mr. Wade of the IDNR, the notification to an outside government agency meets the criteria of a 4-hour notification to the NRC per 50.72(b)(2).(xi)." The licensee notified the NRC resident inspector. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-09-02
41011 | 0 | NAK ENGINEERING INC |  |  |  |  | 2004-09-02 08:38 | 2004-09-02 12:21 | 2004-09-02 | PART 21 REPORTING: HISTORY OF EMERGENCY DIESEL GENERATOR PISTON DEFECT The Nordberg single piece, ductile iron piston, a component of the Nordberg Diesel Engine (Model FS 1316HSC) Emergency Diesel Generator, has a history of sub-surface porosity problems in the upper ring belt area. This porosity has resulted in the initiation of cracks in the compression ring grooves and ultimately the separation of the piston crown from the piston skirt. Once the crown comes loose from the skirt, it can result in catastrophic damage to the cylinder head, cylinder liner, cylinder bock, connecting rod, and crankshaft. This damage can result in the loss of the safety function of the emergency diesel generator. The plant affected is owned by Progress Energy, Brunswick Nuclear Project (CP&L), Brunswick, NC. The component serial number is 1030-1328/1331, model FS 1316HSC. The manufacturer has described in details the concerns, conclusions and corrective action recommendations made regarding the current pistons in use at the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2004-09-02
41010 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-09-01 13:50 | 2004-09-02 12:43 | 2004-09-02 | HEAT BALANCE INDICATION ABOVE LICENSED VALUE "This is a 24 hour ENS notification of a failure to comply with section 2C of the license, which authorizes operation of the facility at steady-state power levels not in excess of 1930 MWth. "Description of Event: "At 13:50, upon installation of a new PC [Plant Computer] isolator Power Supply, the PCS [Plant Computer System] Heat Balance indicated 1936 MWth. Operations immediately lowered reactor power to maintain indicated power less than 1930 MWth. At 09:38 on 09/01/04, the Plant Computer System Isolator Power Supply had failed. Per procedure an admin rod block was installed and all reactivity manipulations were ceased. A prompt investigation was commenced. Initial results of the prompt investigation indicate that the PC isolator Power Supply began to degrade on 08/29. This degradation resulted in a slow lowering of indicated CRD Flow which provides input to the PCS Heat Balance calculation. Based on evaluations of the impact of the degradation, the 1930 MWth limit was exceeded on 08/30/04 at 18:41. Power peaked at 1937 MWth, to approximately 100.4%, on 09/01/04. "Immediate Corrective Actions: 1- Reduced reactor power to <1930 MWth per the heat balance 2- Verified correct all computer inputs Into the PCS Heat Balance 3 - Established a PCS Point Group for Heat Balance Inputs which are being checked twice a shift." The NRC Resident Inspector has been notified by the licensee. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2004-09-02
41008 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2004-08-31 14:00 | 2004-09-02 11:20 | 2004-09-02 | WISCONSIN AGREEMENT STATE REPORT: SOURCE FAILED TO RETRACT "On the evening of August 31, 2004 during a mammosite treatment utilizing a Varian HDR unit, the source failed to retract upon completion of the treatment time. The licensee's RSO/AMP had to enter the treatment room and retract the source manually. "The licensee subsequently contacted Varian for assistance. A service representative from Varian arrived at Aurora Baycare Medical Center on Wednesday, Sept. 1, 2004. The Varian service representative found nothing wrong with the HDR unit. However, approximately 2 cm of the connecting catheter had 'buckled' (appeared melted and twisted), possibly restricting source movement. The licensee has contacted the catheter manufacturer for assistance in analyzing the catheter to determine what may have caused it to buckle. "Preliminary dose indications by the licensee indicate that the patient received an additional amount of dose to the skin while the source was being retracted. The licensee reported that the most probable estimate of the additional skin dose is 1.0 Gy." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2004-09-07
41007 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2004-09-02 10:56 | 2004-09-02 11:20 | 2004-09-05 | NOTIFICATION OF UNUSUAL EVENT DECLARED Turkey point entered EAL 12A based on a confirmed hurricane warning from the State of Florida State Warning Point. The Licensee will notify the NRC Resident Inspector. * * * UPDATE FROM P. REIMERS TO W. GOTT AT 0611 ON 9/5/04 * * * Hurricane Warning no longer in effect for the local area. Turkey Point no longer meets any Emergency Classification and is therefore deescalating from the Unusual Event. Notified R2DO (Landis), NRREO (Case), IRD (Wessman), DHS (McKentry), FEMA (Kuzia). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-02
41006 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-09-02 10:43 | 2004-09-02 11:09 | 2004-09-05 | NOTICE OF UNUSUAL EVENT DECLARED St. Lucie declared a Notification of Unusual Event due to hurricane warning in effect for the plant and surrounding areas. The Licensee will notify the NRC Resident Inspector. * * * UPDATE ON 9/3/04 AT 2035 EDT FROM JAMES HURCHALLA TO GERRY WAIG * * * "Unusual Event update to State Warning Point at 2000 EDT. Both unit 1 and unit 2 in unusual event due to hurricane warning in effect. Unit 1 [is] currently being down-powered off line, unit 2 will commence the downpower at approximately 2100 [EDT] in preparation for the storm. Both units [are] expected off line by 0000." The licensee notified the NRC Resident Inspector, state, and local officials. Notified R2DO (Joel Munday). * * * UPDATE ON 9/05/04 AT 1804 EDT FROM JAMES CONNOR TO JEFF ROTTON * * * "As of 1720 the St. Lucie Station has terminated the Notification of Unusual Event for both units due to the downgrade of Hurricane Frances to a tropical storm warning for the local area. Both units are stable [Mode 3] and sustained no damage from the storm." The licensee notified the NRC Resident Inspector, State and local emergency response organizations. Notified R2DO (Munday), NRREO (Case), IRD (Wessman), DHS (Livingston), FEMA (Eaches). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-09-02
41005 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-09-01 12:45 | 2004-09-01 17:12 | 2004-09-01 | UNANALYZED CONDITION DUE TO APPENDIX R CRITERIA NOT SATISFIED FOR SAFE SHUTDOWN EQUIPMENT "Unanalyzed condition due to missing fire barrier and inadequate separation involving power supply cables for RHR and Core Spray pumps. During a review of the site Appendix R program, NMC Engineering personnel discovered that the credited Monticello Division I RHR Pump and Core Spray Pump power cables pass through a Division II fire area. A fire in this room could potentially damage both divisions of post-fire safe shutdown equipment. "This condition is reportable under 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety due to the lack of required separation of post-fire safe shutdown trains. As a compensatory action an hourly fire watch has been established in accordance with the Monticello Fire Protection Program. "The licensee informed the NRC Resident Inspector." The licensee is continuing their evaluation to determine the extent of the condition. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-09-01
41004 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2004-07-31 13:56 | 2004-09-01 14:14 | 2004-09-01 | INVALID PCIS ACTUATION "This notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) to provide the NRC with information pertaining to the invalid Primary Containment Isolation System (PCIS) Group III actuation signal that affected containment isolation valves in more than one system. "On July 31, 2004 at 1356 [EDT] with the reactor at full power, the power supply that provides power to the Reactor Protection System (RPS) Channel 'A' of the Reactor Building Ventilation Exhaust Rad Monitor and RPS Channel 'A' of the Refuel Floor Rad Monitor was momentarily lost causing an invalid PCIS Group III actuation. Operators immediately verified the plant response to the loss of RPS 'A', backed up the Group III actuation manually, walked down the control room panels, shifted RPS 'A' bus to the alternate power supply, secured 'A' RPS MG set and restored the affected plant equipment to a normal line-up. The following systems were observed to have performed as follows: "The PCIS functioned successfully providing a complete Group III isolation. Both trains of the Standby Gas Treatment System started and operated as designed. "The PCIS Group Ill isolation involved isolation of valves in the following systems: Drywell Air Purge and Vent, Drywell and Suppression Chamber Main Exhaust, Suppression Chamber Purge and Vent, Containment Air Compressor Suction Valve, Exhaust to Standby Gas Treatment, Containment Purge Supply and Makeup, Containment Air Sampling, Air Dilution Subsystem Valves, Vent Subsystem Valves, and Containment Air Dilution Vent System MOV VG-22 A/B. "Repairs were subsequently made to the 'A' RPS power supply and the system was returned to normal status. This event has been entered into Entergy Nuclear Vermont Yankee's Corrective Action Program." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-09-01
41003 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-09-01 00:05 | 2004-09-01 07:46 | 2004-09-01 | MANUAL REACTOR TRIP DUE TO OSCILLATING STEAM GENERATOR WATER LEVEL "On September 1, 2004, at 00:01 hours, operations noticed the 22 Main Feedwater (FW) regulating valve operating erratically and FW and 22 Steam Generator (SG) level oscillating. Operators placed the 22 Main FW regulating valve in manual and attempted to control FW flow and SG level but were unsuccessful. A Nuclear Plant Operator (NPO) in the plant reported water hammer in the Auxiliary Building that contains the FW regulating valves. At 00:05 hours operations initiated a manual trip of the reactor based on the degrading condition with FW flow and SG level. All control rods fully inserted and safety equipment operated as expected. Auxiliary Feedwater started as expected, the Emergency Diesel Generators did not start and offsite power remained available. The plant is in Hot (Standby) at Normal Temperature and Pressure and there was no radiation release. The 22 Main FW regulating valve was discovered to be partially stuck open. At 00:19 hours operations isolated the 22 FW flow path by closing the 22 FW line motor operated valve (MOV) BFD 5-1. The condition is under investigation and a post trip review is being conducted." State of NY was notified of this event by the licensee. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE AT 1113 ON 9/1/04 FROM B. ROKES TO W. GOTT * * * "After further review of the reporting guidelines and discussion with the NRC R1, Licensing concluded the event notification should be reported under 10CFR50.72 (b)(1)(iv)(B) for a 4-hour report. A Condition Report was initiated for the late notification." Notified NRR (Reis) and R1DO (Henderson). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2004-09-01
41002 | 0 | PALISADES | 1 |  |  | [1] CE | 2004-08-31 07:18 | 2004-08-31 09:38 | 2004-08-31 | RPS ACTUATION DUE TO FIRE IN 2B CONDENSATE PUMP "At 0718 EDT, the reactor was manually tripped from approximately 95% power following notification to the control room of a fire associated with condensate pump 2B. Initially, upon notification of smoke at the condensate pump, a rapid down power had been commenced, wherein reactor power was reduced from 100% to approximately 95% power. "An automatic actuation of the auxiliary feedwater system also occurred as designed to maintain steam generator water level following the reactor trip. "The fire was extinguished in less than 10 minutes. The local fire department was notified, responded to the site as a precautionary measure, but was not used in extinguishing the fire. All systems functioned as designed. The reactor is stable in mode 3." Decay heat is being removed with the steam generators discharging steam to the main condenser. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-08-31
41001 | 0 | C. W. THOMAS INC |  |  |  |  | 2004-08-09 07:00 | 2004-08-31 08:46 | 2004-08-31 | LOST GENERAL LICENSED POLONIUM SOURCE The Ionizing Static Tip of a General Purpose Air Gun (Model number P-201-001, Serial number A2DH072) was discovered missing on 8/9/04. A thorough search of the work area was conducted, but the tip could not be found. It is speculated that the gun was dropped and the tip was dislodged from the gun and was subsequently swept up and disposed of in the trash. The tip is a Polonium-210 source with approximately 1.6 milliCuries. The gun was leased from NRD Advanced Static Control Systems. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-08-31
41000 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2004-07-01 | 2004-08-30 14:49 | 2004-08-30 | GEORGIA AGREEMENT STATE REPORT - MEDICAL EVENT On July 01, 2004 the licensee had three patients scheduled for I-131 treatments. Two patients were scheduled to receive less than 33 milliCuries and one patient was scheduled to receive 100 milliCuries. One of the patients scheduled to receive less than 33 milliCuries was administered 100 milliCuries instead. The patient was allowed to leave the facility without the proper instructions being given. The authorized user who signed the written directive was at the facility when the dose was administered. The temporary RSO was at South Fulton Hospital and he was notified. The patient was notified and was given the proper instructions prior to release and the referring physician was notified. On 07/19/04, a written copy of this event was received by the [Georgia] Department [of Natural Resources], including measures taken to prevent recurrence. Incident was not discovered by licensee until after patient had left with her children. On 7/26/04, the Department received report from the medical physicist consultant hired by licensee that no overexposures or affects from radiation would have been received by patient's children. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2004-09-02
40999 | 0 | US ENGINEERING LAB |  |  |  |  | 2004-08-29 07:00 | 2004-08-30 12:41 | 2004-08-30 | STOLEN TROXLER MOISTURE DENSITY GAUGE A Troxler moisture density gauge Model # 3411, Serial # 7142 containing 10 millicuries Cs-137 and 50 millicuries Am-241:Be was stolen when the automobile that is was stored in was stolen. The gauge was locked inside its case in the trunk of the automobile at the time of the theft. The licensee has notified the local police department. * * * UPDATE 1830 EDT ON 8/30/04 FROM BILL CSASZAR (NJ DEP) TO S. SANDIN * * * The stolen vehicle was recovered in Irvington, NJ. HAZMAT and the bomb squad on on-scene with plans to x-ray the transport container that has the Troxler gauge inside as a precautionary measure. Notified R1DO(Henderson), NMSS(Brach) and TAS(Whitney). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-08-30
40998 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2004-08-30 08:35 | 2004-08-30 11:42 | 2004-08-31 | UNIT 1 MANUALLY SCRAMMED DUE TO OSCILLATING REACTOR VESSEL WATER LEVEL "Nine Mile Point, Unit One is initiating a 10 CFR 50.72 (b) (2) (iv) (B) 4-Hour Non-Emergency notification based upon insertion of a 'MANUAL' scram that occurred at 08:35 on Monday, August 30, 2004. "At time of transient, plant was operating in Mode 1, Power Operating Condition, at 99.7% of rated power. "At 08:25 on Monday, August 30, 2004, Operators noted oscillations on 13 Feedwater flow control valve (FCV) while in 'AUTOMATIC' mode of operation (normal mode of operation for this equipment). Operators took "MANUAL" control of 13 FCV per Plant Operating Procedures. 13 FCV oscillations continued while in the 'MANUAL' mode, and a decision was made to insert a 'MANUAL' scram at 08:35. All control rods fully inserted and the plant responded as designed to the scram. "At 08:44, the scram signal was reset per procedure. "Currently, plant is in Mode 2, Hot Shutdown Condition with cooldown in progress. Plant is transitioning to Mode 3, Cold Shutdown Condition, per Plant Operating Procedures." At the time the manual scram was inserted, Reactor Vessel Water Level (RVWL) was 67 inches and decreasing (automatic scram setpoint is 53 inches). The 13 FCV is on the discharge of the turbine-driven feedwater pump. Decay heat is currently being removed by the main condenser via the steam bypass valves. All ECCS and safety-related equipment is available, if needed. At the time of the transient there was no plant maintenance on-going which could have been a contributing factor. The licensee informed the NRC Resident Inspector. * * * UPDATE ON 8/30/04 AT 2358 EDT FROM M. MINNICK TO J. ROTTON * * * "The notification sent to the NRC on 8/30/04 at 11:42 was found to be incomplete. As a normal and expected response to a manual scram at high power, the High Pressure Coolant Injection System (feedwater) automatically initiated during the transient following the manual scram. This should have been reported as an 8 hour Non-Emergency 10CFR50. 72 (b) (3) (iv) (A) notification." The licensee notified the NRC Resident Inspector. Notified R1DO (Henderson). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-08-30
40997 | 0 | ATLANTIC GEOTECHNICAL SERVICES |  |  |  |  | 2004-08-30 | 2004-08-30 07:35 | 2004-09-17 | STOLEN TROXLER GAUGE Licensee technician reported to Richland, VA police that his vehicle (SUV) was stolen from his home possibly early this morning and that a Troxler gauge model 3430 (S/N 30179) was stored in the vehicle. The gauge was double locked in its casing and contains a Cesium 137 source (S/N 750-1869, current activity 7.4 millicuries) and a Americium 241:Beryllium source (S/N 47-271-56, current activity 39.7 millicuries). The licensee is contacting the Richland police once again to raise their awareness that this gauge contains radioactive materials. * * * UPDATE 1000 EDT ON 9/17/04 FROM EDITH POPP TO S. SANDIN * * * The stolen Troxler gauge was recovered intact late in the evening of 9/16/04 and returned to the custody of the licensee. The licensee verified that there were no leaks. Notified R1DO (Doerflein) and NMSS (Miller). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-08-30
40996 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-08-29 19:28 | 2004-08-30 02:54 | 2004-08-30 | ALARM INDICATION OF INOPERABLE REACTOR WATER CLEANUP SUPPLY ISOLATION VALVE "On 08/29/04 at 1928 hours [EDT], an alarm was received in the control room indicating the reactor water cleanup (RWCU) high differential flow isolation channel for the outboard RWCU supply isolation valve was inoperable. At the time, the channel functional test for the inboard RWCU high differential flow isolation channel was being performed. During the channel functional test, power to the inboard isolation valve is removed to permit continued RWCU system operation while the isolation function is tested. With the outboard isolation actuation instrumentation channel inoperable and the inboard isolation valve deenergized, in the event of a break in the RWCU system, the required isolation function may not be completed. "This event is being reported in accordance with 10CFR50.72(b)(3)(v)(C) as a condition that could have prevented the fulfillment of a safety function. "In accordance with Technical Specification requirements, the RWCU system was removed from service and the inboard and outboard supply Isolation valves were closed." There is no immediate impact on water chemistry and the licensee is investigating the cause of the original failure as well as possible long term degradation of the reactor water chemistry. The licensee notified the NRC Resident Inspector and will notify the local township authorities of this incident. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-08-30
40995 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2004-08-28 01:46 | 2004-08-28 07:38 | 2004-08-28 | FAILURE OF THE PLANT PROCESS COMPUTER DUE TO LOSS OF POWER SUPPLY At approximately 01:46 (CDT) on August 28, 2004, the Duane Arnold Energy Center plant process computer (PPC) failed due to a lost power supply. This computer system provides the control room with its Safety Parameter Display System (SPDS), the Emergency Response Data System (ERDS) and MIDAS. With the loss of the PPC, and specifically the subsequent loss of SPDS, ERDS, and MIDAS representing a major loss of emergency assessment capability, the reportability criteria of 10CFR50.72(b)(3)(xiii) was met. No other control room indications, or communication systems were affected by this computer outage. They expect to have a new power supply at the site by noon today and installed within two hours after arrival. The NRC Resident Inspector will be notified. * * * UPDATE PROVIDED BY DICK FOWLER TO JEFF ROTTON AT 1302 ON 08/28/04 * * * The Duane Arnold Energy Center plant process computer (PPC) power supply has been replaced and operation of the PPC has been restored. The licensee has notified the NRC Resident Inspector. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-28
40994 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-08-27 08:50 | 2004-08-27 12:36 | 2004-08-27 | OFFSITE NOTIFICATIONS MADE TO SPILLAGE OF PHOSPHONIC ACID 15 gallon spill of blulab 7016 acid anti-scalant (used for Circulating Water System) of which 5 gallons was caught in a bucket and approximately 10 gallons spilled of which 1 or 2 gallons ended up into the lake. Licensee notified the National Response Center and the Texas Commission of Environmental Quality. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-27
40993 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2004-08-27 06:58 | 2004-08-27 12:20 | 2004-08-27 | CONTRACT SUPERVISOR TESTED POSITIVE FOR ALCOHOL A contract supervisor tested positive for alcohol during a for-cause test. The individual's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2004-08-27
40992 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-07-20 | 2004-08-27 11:09 | 2004-08-27 | POSSIBLE RADIATION EXPOSURE FROM A LEVEL DETECTION DEVICE It has been determined that during a painting and insulation replacement: job on the exterior of the D-15 vessel at the Solvents Plant at Dow's Plaquemine manufacturing complex, a radiation shield was not locked out on a 500 mCi Cs-137 radiation source used for level detection. The zone of potential exposure was approximately 3 inches wide by 14 inches long on the external top of the tank. The work that was being performed was in such a manner that there could have been a possibility of hand or arm exposure. During the six day period it was determined that up to 16 persons had the potential to be exposed while completing the insulation replacement. A conservative estimate of 5 minutes total continuous exposure time over this period at a distance of 5 inches from the source yield a potential exposure of 421 mrems. A two minute total continuous exposure at a distance of 14 inches would yield a potential exposure of 31 mrems. The cause of the incident was failure to lock out a radiation shield prior to commencement of work. Lock out procedures for the facility have been reviewed and strengthened to prevent reoccurrence. Medical screening was performed on all potentially exposed personnel and the results were reviewed with the personnel. No effects were observed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-09-01
40991 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-07-01 | 2004-08-27 10:01 | 2004-08-27 | LICENSEE REPORTED FAILURE OF A RADIOGRAPHY CAMERA On July 1, 2004 while Bayou Testers was performing quarterly inspections, they noticed that the case on a INC-100 industrial radiography camera was split open. The exposure devise was taken out of operation and sent to Source Production and Equipment (SPEC). The devise contained approximately 10 Ci of Ir-192. SPEC informed the licensee that the cause of the case splitting was corrosion of the depleted uranium shield, which caused it to swell and tear the weld. SPEC informed the licensee that this occurrence was not unusual. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-09-01
40990 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-08-05 | 2004-08-27 09:35 | 2004-08-27 | INCORRECT DOSE ADMINISTERED TO A PATIENT A misadministration occurred on August 5, 2004. The patient was an uncooperative 20 year old Down's Syndrome who was to be injected with 20 mCi of Tc-99m MDP for a bone scan. While attempting to restrain the patient the technologist mistakenly reached for and injected a 4.2 mCi DMSA renal scan dose. The patient was notified of the error and subsequently injected with the correct dose. The misadministration did not exceed the 5 rems effective dose equivalent or the 50 rems dose equivalent to any organ. The technologist was been counseled to obtain assistance when performing such administrations in the future. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-09-01
40989 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2004-08-27 08:15 | 2004-08-27 09:12 | 2004-08-27 | THE LICENSEE REPORTED EXTERNAL RADIATION LEVELS ON A PACKAGE EXCEEDING THE LIMITS OF 10CFR 71.47. The event occurred at a medical broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-OIVA. The permittee is VA Medical Center, Durham, North Carolina. The event occurred on August 27, 2004, and was discovered at 8:15 AM EDT on the same day. The basis for the event is under 10 CFR 20.1906(d)(2) in that a package received in the nuclear medicine service of the: VA Medical Center, Durham, North Carolina measured 250 mrem/hr at a point on the external surface of the package. Photon Imaging Corporation (a commercial radiopharmacy located in Raleigh, North Carolina) delivered the package containing a Tc-99m baulk vial to the nuclear medicine service of the VA Medical Center, Durham, North Carolina. .A survey of the surface of the delivery container indicated a point on its external surface that measured 250 mrem/hr and 4 mrem/hr @) 1 meter. Wipe surveys, however, did not indicate any removable contamination. Upon inspection of the package, it was discovered that the cap of the shield containing a baulk dose of Tc-99m of 137.6 mCi had inadvertently fallen loose and was no longer shielding the vial. There was no indication that the vial itself was damaged or that any of the Tc-99m had leaked into the package. The permittee user does not anticipate any adverse medical effects to patients, staff or members of the public. The permittee immediately notified the commercial vendor. The Department of Veterans Affairs will evaluate the circumstances related to the event and submit a written report to NRC Region 3, within 15 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 1 | NC | HOS |  | 20.1906(d)(2) |  |  |  | 0 | 2004-08-27
40988 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-07-21 | 2004-08-26 15:28 | 2004-08-26 | AGREEMENT STATE REPORT - LOST OR STOLEN GAUGE The following information was received via facsimile: "On July 21, 2004 a Niton Analyzer with serial number 6067 with 40 milliCuries of Fe-55 and 30 milliCuries of Am-241 came up missing. The security department was notified immediately. Every effort was made to locate the analyzer but it could not be found. Signs were posted at all clock stations and exit gates. Security also checked the employees when they were leaving the yard." Louisiana Report # LA040008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-08-31
40987 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-04-20 | 2004-08-26 15:20 | 2004-08-26 | AGREEMENT STATE REPORT - INCORRECT MEDICAL TREATMENT SITE The following information was received via facsimile: "The incident occurred on April 20, 2004 at the Tulane Cancer Center. The patient was being treated for cervical cancer. The Nucletron Source Position Simulator had previously been repaired by the service technician by providing a replacement screw. During measurement of correct catheter position with the device, the simulator cable became stuck resulting in underestimation of the required distance. This erroneous number was entered into the Nucletron HDR unit. The 9050 milliCurie source of Ir-192 did not extend to the desired location but remained outside the patient for approximately 2 minutes at 2.6 centimeters from the skin. The dose estimate for this was 270 R. The patient was notified and the treatment plan modified. As of July 21, 2004 there is no effect on the patient. To prevent reoccurrence the procedure was modified to test for looseness in the Source Position Simulator prior to use." Louisiana Report # LA040007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-08-31
40986 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-08-20 16:00 | 2004-08-26 11:21 | 2004-08-26 | AEA TECHNOLOGY REPORTED RECEIVING A LEAKING SOURCE FROM ONE OF THEIR CUSTOMERS AEA reports that an AEA Model PDM.1002.Hn Series static eliminator device, containing approximately 3 millicuries of polonium-210 was returned from a customer and found to be leaking. A wipe survey of the NRD, Inc. Model P-001 foil sealed source contained in the device measured 0.008 microcuries of polonium-210. Wipe survey of the outside package detected no contamination. The device was received from AEA's customer, Hank Graff Chevrolet in Davidson, MI. on August 19, 2004. AEA contacted the sealed source manufacturer, NRD, Inc. AEA Technology QSA, Inc. (AEA) sealed the source in a plastic bag and the immediate area was checked for further contamination. No contamination other than what was on the source was found. AEA contacted the source manufacturer, NRD, Inc. An investigation is pending. The Agency will notify the U.S. NRC and the State of New York as applicable to the device customer site and source manufacturer site jurisdiction. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-08-31
40985 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2004-08-24 10:05 | 2004-08-25 09:44 | 2004-08-25 | 24 HOUR 91-01 RESPONSE BULLETIN An incorrect valve line-up caused a batch from the solvent extraction system to be pumped to the uranyl nitrate bulk storage tank without having the necessary sample results for grams U-235 per liter, percent free acid, and pH. It was determined that approximately 38 gallons of uranyl nitrate at 4.6 grams U-235, 8 percent free acid, and a pH of 1 was pumped to the bulk storage tank. These parameters meet the requirements for an authorized pumpout. The bulk storage tank contained approximately 1600 gallons of uranyl nitrate at approximately 1.4 grams U-235 per liter, 11.6 percent free acid, and a pH of 1. Double contingency protection for the bulk storage tank is based on concentration control. Concentration control is based upon maintaining uranyl nitrate that is pumped to the tanks at less than 5 grams U-235/liter. The pH is maintained at a value of less than 2 to ensure that the uranyl nitrate stays in solution. The percent free acid is maintained at greater than 4 percent to ensure that the uranyl nitrate stays in solution and depresses the freezing temperature of the solution to prevent concentration by freezing. It has been determined that less than previously documented double contingency protection remained for the system and that greater than a safe mass was involved, but a sufficient number of controls that were lost were restored within 4 hours. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criteria for a 24-hour notification. Summary of Activity All pumpouts to bulk storage tanks were stopped immediately upon recognition. This action was initiated by operators monitoring system performance. Samples for grams U-235/liter, pH, and %free acid were taken to ensure the tanks were in specification. Before the end of the shift, sample results for grams U-235/liter, pH, and %free acid were confirmed to be acceptable. At the beginning of each shift, operators are being informed of the incident. The procedure is being modified immediately to incorporate an additional peer check. Independent locks will be installed to require separate individuals to unlock the valve prior to pumpout. Conclusions Loss of double contingency protection occurred. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. Notification was the result of an event, not a deficient NCS analysis. A causal analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2004-08-25
40983 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2004-08-24 09:17 | 2004-08-24 17:36 | 2004-10-08 | HIGH PRESSURE CORE SPRAY (HPCS) DECLARED INOPERABLE At 1128 hours on 8/23/04, the Division 3 Essential Switchgear Heat Removal System (VX) was removed from service and declared inoperable for performance of system flow verification and balance. The test includes an as found flow check on the Division 3 Essential Switchgear Heat Removal System Condensing Unit, rendering the Division 3 VX safety-related chiller 1VX06CC INOPERABLE. The non-safety VX subsystem remained OPERABLE during the test. "At 0917 hours on 8/24/04, the non-safety Division 3 VX Heat Removal Supply Fan 1VX04CC, tripped due to the breaker for the safety-related fan being removed for replacement. The Main Control Room received alarm 5042-6A, Auto Trip Pump/Fan. Since both the safety and non-safety subsystems of VX were unavailable Operators declared the High Pressure Core Spray (HPCS) System inoperable per Technical Specification 3.7.2, Action A.1. "At 1153 hours, the breaker replacement was complete, 1VX04CC was restored to service, and the HPCS System was declared OPERABLE. "The VX System maintains safety-related switchgear, battery and inverter room, and cable spread areas within the design temperature limits of the equipment. The VX system is support system for the HPCS System. With both subsystems of the VX System out of service, the HPCS System may not have been capable of performing its safety function to provide Emergency Core Cooling, aid in depressurization and maintain reactor vessel water level following a loss of coolant accident. "An engineering evaluation is currently in progress to determine if the HPCS System would have been capable of performing its safety function with both safety and non-safety subsystems of VX out of service. "This issue is being reported in accordance with 10CFR50.72(b)(3)(v)(D), as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function needed to mitigate the consequences of an accident." The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION FROM BILL CARSKY TO BILL HUFFMAN AT 17:47 EDT ON 10/08/04 * * * "Upon further review of this event, additional analysis has been performed which bounds the design bases heatup of the associated rooms cooled by the Division III Essential Switchgear Heat Removal System (VX). This analysis concludes that the areas cooled by the Division 3 VX subsystem would not have exceeded design temperatures while the cooling was secured, prior to cooling recovery, and that the supported systems remained operable. "Based upon this additional analysis, it can be reasonably concluded that the safety function of High Pressure Core Spray, as a single train safety system, was fulfilled. Therefore this event is not reportable and Event #40983 is being retracted." The NRC Resident Inspector was notified of this retraction by the licensee. R3DO (Clayton) has been notified. | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-08-24
40982 | 0 | GENERAL ELECTRIC COMPANY |  |  |  |  | 2004-08-24 | 2004-08-24 17:36 | 2004-09-30 | PART 21 REPORTABLE CONDITION AND 60-DAY INTERIM REPORT NOTIFICATION: NON-CONSERVATIVE SAFETY LIMIT MINIMUM CRITICAL POWER RATIO Global Nuclear Fuel (GNF) and GE Nuclear Energy (GENE) have determined that the current GNF process for determination of the Safety Limit Minimum Critical Power Ratio (SLMCPR) can result in a non-conservative SLMCPR. GENE has historically used a non-conservative SLMCPR impact of 0.01 as the threshold for reportability under 10CFR21. A preliminary screening evaluation has been completed for all plants operating with a SLMCPR calculated by GNF to determine those that have a nonconservative impact of 0.01 or greater. Verification has been completed for those plants that the screen showed to have a non-conservative SLMCPR impact of 0.01 or greater. Verification has not been completed for the plants that the screen showed had an impact of less than 0.01 or were unaffected, thus requiring a 60-Day Interim Report notification pending verification completion. The plants for which GNF calculates the SLMCPR are identified [below]. Those plants for which the preliminary screen indicated that the current SLMCPR is unaffected are identified as a 60-Day Interim Report. Upon completion of verification (assuming the results of the screen are confirmed) the status of these plants will be changed to Not Reportable. GENE will provide a follow-up report to the NRC by September 29, 2004. The plants for which the current SLMCPR is non-conservative by 0.01 or greater are identified as a Reportable Condition under 10CFR21.21(d). These plants will take action to address the Reportable Condition. GNF has notified all plants that have been confirmed to be affected. The plants that have a non-conservative SLMCPR for current plant operation will take action to mitigate the potential impact. Depending on the specific circumstances, mitigating actions to protect the SLMCPR may include increasing the OLMCPR to assure compliance with the low flow calculated SLMCPR. In some cases sufficient conservatism may exist in the OLMCPR at low flow to bound the increased SLMCPR. Each affected plant will notify the NRC and take appropriate action if their Technical Specifications are affected. There are no actions necessary for the plants that are unaffected pending completion of verification. If, in the course of verification, GNF determines that there is an impact, the affected utility will be notified immediately. GNF will complete the verification and GENE, will provide a follow-up letter to the NRC by September 29, 2004. Affected and 60-Day Interim Notification Plants: 60-Day Interim Report: Clinton, Oyster Creek, Brunswick 1, Brunswick 2, Nine Mile Point 2, Fitzpatrick (60-Day interim report for current operation, Reportable Condition for SLMCPR licensing submittal), Pilgrim, Vermont Yankee, Dresden 2, Dresden 3, LaSalle 1, LaSalle 2, Limerick 1, Limerick 2, Peach Bottom 2, Peach Bottom 3, Quad Cities 1, Quad Cities 2, Perry 1, Duane Arnold, Monticello, Hope Creek, Hatch 1, Hatch 2, Browns Ferry 2 Reportable Condition: Nine Mile Point 1, Fermi 2, Fitzpatrick (60-Day interim report for current operation, Reportable Condition for SLMCPR licensing submittal), Cooper. * * * UPDATE FROM JASON POST (VIA FAX) TO CROUCH @ 2354 HRS. EST ON 09/29/04 * * * In part, the update reads: "The evaluation for the potentially unaffected plants has now been completed. The results of the screening calculation have been confirmed: this is not a reportable condition for the plants that were previously identified as a 60-Day Interim Report notification in MFN 04-081" (See above). Notified R1DO(Rogge), R2DO(Lesser), R3DO(Kozak), R4DO(Howell) and NRREO(Hodges). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | PAR | 21.21 |  |  |  | 0 | 2004-08-24
40981 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-08-24 13:30 | 2004-08-24 16:48 | 2004-08-24 | NORTH PLANT VENT RADIATION MONITOR SKID TEST CONNECTION VALVE INADVERTENTLY LEFT OPEN. "On Tuesday 8/24/04 at 1330 hours, a test connection valve on the North Plant Vent radiation monitor skid was identified to have been inadvertently left open. This configuration issue appears to have occurred sometime on 8/19/04 following corrective maintenance on the North Plant Vent radiation monitor skid. With this valve left open, the process flow path for the skid was effectively diluted as room air was drawn into the normal process flow from the North Plant Ventilation ductwork. The physical location of the valve left open on the skid was such that the High/Low Noble Gas Range Monitors Iodine Sampler and Particulate Sampler would have been affected by this oversight. Technical Specification section 3.3.7.5 for Accident Monitoring as well as Offsite Dose Calculation Manual section 3.3.7.11 would have been applicable for the condition described. The preplanned alternate method of monitoring (sampling) the parameters was not established. This is in contrary to the requirements of Technical Specifications and the Off Site Dose manual. This condition has been corrected and the North Plant Vent radiation monitor skid is currently operable. Though alternate sampling capability was available, it was not recognized that it was required. Should an accident have occurred during the time that the valve was open emergency assessment capability would have been compromised. This report is being made under Hope Creek Event Classification Guide RAL# 11.7.1.c in accordance with 10CFR50.72(b)(3)(xiii)." Local authorities will be notified of this by the licensee." The NRC Resident Inspector will be notified of this event by the licensee. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-24
40979 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2004-08-10 | 2004-08-24 08:52 | 2004-08-24 | MEDICAL MISADMINISTRATION The following information was received from the State of Alabama Department of Public Health via facsimile: "SUBJECT: Licensee identification of I-131 Misadministration. "By telefax notification on August 17, 2004, Northeast Alabama Regional Medical Center (Alabama Radioactive Material License No. 315) notified the State of Alabama of a misadministration involving Iodine-131. "In the telefaxed report, the licensee indicated that the event occurred on August 10, 2004 and was discovered on August 12, 2004. The dose prescribed was 25 microcuries of I-131 and the dose administered was 3.0 millicuries. Based on the information supplied by the licensee, it appears that the imaging technologist misunderstood the referring physician's request and the dose was not approved by the authorized user. The licensee indicated in their report that there was no apparent effects to the patient. Corrective measures included reinstructing personnel and ensuring that all procedures are approved by the authorized user. "At this time, the Office of Radiation Control is requesting additional information from the licensee. Once made available, the information will be supplied via the NMED database system." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2004-08-27
40978 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2004-08-23 09:00 | 2004-08-23 17:37 | 2004-08-23 | EMERGENCY DIESEL GENERATOR START FAILURE The emergency diesel-driven backup power generator failed to automatically start during routine weekly testing. Production was shutdown in the Feeds Material Building while resolving the problem. The start failure was determined to be the result of a failed electronic card associated with the fuel supply solenoid valve. Because the solenoid can be over-ridden, the diesel generator remains capable of manual start. The licensee notified NRC Region 2 (J. Hensen) and local NRC Inspector (B. Bartlett). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2004-08-23
40977 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2004-08-23 13:22 | 2004-08-23 17:20 | 2004-08-23 | EMERGENCY SIRENS DID NOT ACTIVATE "At 1322 hours during routine testing it was discovered that Monroe County Emergency Sirens (24 of 96 total) did not activate from the Monroe County Emergency Command Center . The affected sirens were tested and restored to operable status from an alternate site at 1404 hours." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-23
40976 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-08-19 16:30 | 2004-08-23 12:55 | 2004-10-18 | NEVADA: AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE "1. Event Report ID No. NV-04-005 "2. License name, address, license No: Geotek, Inc.; 8835 S. Escondido Street, Suite A; Las Vegas, Nevada 89119-3 828, 00-11-0348-01 "3. Nature of Event, Date and time of occurrence: Theft of a portable moisture/density gauge on 8/19/04, about 4:30 pm. "4. Date notified of event by licensee or non-licensee: August 20, 2004 "5. Radionuclide, activity: Cesium 137-10 millicuries and Americium 241-50 milliCuries "6. Any exposures (indicate short and long-term effects): Unknown "7. Sealed source, device, etc. (make, model #, serial #): CPN-131 sealed source, CPN Model MC-3 gauge, serial number M34125837 "8. Leak test information, if applicable: Unknown "9. Equipment (make, model #, serial #), and clear description of any equipment problems: See # 7 above "10. Persons involved, consequences: (Deleted), no consequences known "11. Transportation, identify shipper, package type and ID No.: N/A "12. Abnormal Occurrence (Y/N): N "13. Cause and contributing factors: The chain, securing the gauge case in the truck, was cut with bolt cutters and the gauge in its case was stolen "14. Notifications: patient, physician: N/A "15.Licensee corrective actions: Will perform investigation to determine root cause "16.Provide status through resolution (update record when found) "17. Notifications, local police, FBI and other States; as needed: Clark County Metropolitan Police "18. Enforcement Actions: Under investigation "19. Identify any possible generic safety concerns: N/A "20. Potential for others to experience the save event: Unknown "This incident was reported to Ms. Linda McLean, NRC Region IV, on 8/20/04 by telefax." * * * UPDATE AT 1906 EDT ON 10/18/04 FROM LARRY BOSCHULT TO S. SANDIN VIA FAX * * * "The gauge was discovered in Las Vegas on October 8, 2004, apparently left at a job site. The man who found the gauge recognized what it was from past work experience. The gauge was stored at a fire station until it could be picked up by the owner. The gauge was not in a case but appeared OK and the shutter was closed. The owner confirmed pickup of the gauge on October 12, 2004." Notified R4DO (Jack Whitten) and NMSS (Bill Reamer). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-08-26
40975 | 0 | DOMINION GEOTECHNICAL |  |  |  |  | 2004-08-20 11:00 | 2004-08-23 09:34 | 2004-08-23 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The licensee reported that a Troxler Moisture Density Gauge, Model 3411, Serial Number 13101, was damaged when it was run over by a soil compacting roller. The gauge suffered a cracked housing and a bent handle but the source is retracted into the shield. The gauge contains 8 milliCuries of Cs-137 and 40 milliCuries of Am:Be. Leak test results are pending. Radiation readings taken 1 meter away from the gauge indicated 50 microRem/hr and reading taken on contact were 1.5 milliRem/hr. The gauge is currently stored at the licensee's facility awaiting transfer to the vendor for repair or disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2004-08-23
40974 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2004-08-22 10:10 | 2004-08-22 14:23 | 2004-08-23 | REACTOR TRIP DURING SURVEILLANCE TEST "At 1010 CDT on 8-22-2004, during the performance of STS IC-211B, 'ACTUATION LOGIC TEST TRAIN B SOLID STATE PROTECTION SYSTEM,' Control Room operators received a reactor trip concurrent with power range flux lo [low] setpoint trip and intermediate range hi [high] flux reactor trip alarms. "All safety-related equipment operated as required. The Steam Dump valves, which function to remove excess heat as the secondary systems shutdown, did not initially operate as expected, resulting in the operation of the Steam Generator Atmospheric Relief Valves (ARVs) to control Reactor Coolant pressure for approximately three minutes following the reactor trip, at which time the Steam Dump valves responded as expected and the ARVs closed. The Steam Dumps are currently operating correctly in automatic. "The Auxiliary Feedwater System actuated as designed. "The plant is currently stable in Mode 3 at Normal Operating Temperature and Pressure while plant personnel investigate the causes of the reactor trip and formulate the repair/ restart plan. "A press release is planned." During the reactor trip, all control rods fully inserted. The electric plant is in a stable shutdown plant lineup. Plant personnel also intend to investigate the unusual response of the steam dump valves. The licensee has notified the NRC Resident Inspector. * * * Update on 08/23/04 at 1635 EDT by Steven Gifford taken by MacKinnon * * * "Upon data review related to the operation of the Steam Dump valves and the Atmospheric Relief Valves (ARVs), plant staff has determined that the ARVs and Steam Dump valves operated as expected. The Steam Dump valves opened immediately following the reactor trip, as designed, due to the difference between their setpoint and the Reactor Coolant System (RCS) temperature at the time of the reactor trip. The Steam Dump valves remained open for approximately 20 to 30 seconds, at which time the RCS temperature had decreased to a value within the control range for the Steam Dump valves, causing them to close. The opening of the ARVs was in response, as designed, to the increase in Steam Generator pressure that resulted from the turbine trip shortly after the reactor trip." NRC R4DO (Tom Farnholtz) notified. The NRC Resident Inspector was notified of this update by the licensee | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-08-22
40973 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2004-08-21 20:00 | 2004-08-22 01:12 | 2004-10-12 | ACCIDENT MITIGATION - HIGH PRESSURE COOLANT INJECTION SYSTEM FLOW CONTROLLER MALFUNCTION The following information was provided by the licensee via facsimile: "[The] High Pressure Coolant Injection (HPCI) flow controller malfunctioned resulting in the inability of the HPCI to perform its safety function as a single train system under 10 CFR 50.72 (b)(3)(v). The failure mode for the flow controller is suspected to be a power supply issue, however, the cause has not been confirmed at this time. Unit 2 is in a 14 day technical specification [T.S.] limitation which if exceed results in a unit shutdown ( T.S. 3.5.1 Condition C)." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 10/12/04 @ 0835 BY FOSS TO GOULD * * * RETRACTION The purpose of this notification is to retract a previous report made on 8/22/04 at 0112 hours (EN# 40973). Notification of the event to the NRC on 8/22/04 was initially made as a result of declaring the Unit 2 High Pressure Coolant Injection (HPCI) system inoperable when unexpected conditions were found during performance of routine control board checks of HPCI. Specifically, it was observed by the Reactor Operator that the HPCI flow controller would not properly respond to faceplate manipulations. Initially, it was believed that the flow controller power supply may have failed and therefore, the flow controller could not perform its intended function. The HPCI system was not operating at the time of the discovery. Since the initial report, Engineering has determined that the HPCI system was capable of performing its safety function. Although it was determined that the HPCI flow controller faceplate was defective, the set point of the flow controller and the flow controller's ability to automatically control system flow for a design basis event was not affected. A failure analysis of the faceplate was performed. It was determined that keypad contacts on the faceplate were the cause of the degraded faceplate function, but these keypad Contacts did not prevent the flow controller from performing its design function. The flow controller faceplate was replaced by 1410 hours on 8/22/04 (CR 246290). The NRC resident has been informed of the retraction. Notified the Reg 2 RDO (Ogle) | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-08-22
40971 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-08-18 12:00 | 2004-08-20 18:41 | 2004-08-20 | AGREEMENT STATE REPORT- THERAPEUTIC MISADMINISTRATION Therapeutic misadministration from HDR [High Dose Rate brachytherapy]. Patient was scheduled for three HDR retreatments for cancer between the urethra & bladder wall. The treatment dose/fraction was supposed to be 300 cGy [centiGray] to a 7 mm radius distance from the source, & the length of the treatment plan was 3 cm. They used a Varian catheter & measuring wire. When they inserted the measuring wire, they thought they were at the end of the catheter, but they were actually about 20 cm short. The source for two treatments, on August 18 and 19, was actually located about 10 cm from the end of the penis, exterior to the body. They estimate the tumor site only got about 10 cGy, and the penis may have received approximately the same dose it would have received had the source been inserted into the correct location. The root cause appears to be an error on the part of the medical physicist. The patient is 93 years old, and both the radiation oncologist and the primary care physician believe he should not be told. The third treatment was performed correctly, and they have scheduled him for two additional treatments. They believe there will be no impact on the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-08-25
40970 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-08-20 12:15 | 2004-08-20 17:48 | 2004-08-20 | RAILROAD ACCESS PROCESS RADIATION MONITORS ACTUATION CAPABILITY WAS INADVERTENTLY DEFEATED At 12:15 PM on 8/20/04, it was discovered that actions performed on 7/16/04 in support of Dry Fuel Storage activities to defeat the Railroad Access Area Radiation Monitor alarm horn had also defeated the actuation capability of the Railroad Access Process Radiation monitors. Per Technical Specifications, the process monitors are required to be operable "during movement of irradiated fuel assemblies within the Railroad Access Shaft, and above the Railroad Access Shaft with the Railroad Access Shaft Equipment Hatch open." Contrary to the Tech Spec requirement, two loaded Dry Fuel Storage Casks were lowered in the Railroad Shaft, one on 8/2/04 and the second on 8/16/04, with the radiation monitors inoperable. During this period the automatic isolation and re-alignment of Reactor Building Zone lll, automatic start of Reactor Building Recirculation Fans, and the automatic starts of SGTS and CREOASS would not have actuated from a HI-HI Radiation condition in the Railroad Access Shaft. Actual radiological conditions observed during the transfer of the casks in the railroad shaft would not have resulted in the need for system actuation. All other instruments in the Reactor Building ventilation system which actuate these systems were operable as required by Tech Specs. The jumpers which defeated the actuation capability were removed on 8/20/04 at 1400 [hrs.]. This event is considered reportable under 50.72(b)(3)(v)(C) as a loss of safety function. The NRC Resident Inspector was notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNCNTRL RAD REL |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(C) |  |  |  | 0 | 2004-08-20
40969 | 0 | TACOM |  |  |  |  | 2004-08-13 01:30 | 2004-08-20 17:32 | 2004-08-20 | US ARMY RADIOACTIVE MATERIAL INVOLVED IN A FIRE. On August 13, 2004 and aircraft hanger located on Fort Wainwright, East of Fairbanks, burned to the ground. Three chemical detectors containing a total activity of 70 millicuries of Nickel-63 were stored inside a metal wall locker within the aircraft hanger. The aircraft hanger has been cordoned off and a US. Army Radiation Safety Officer (RSO) is on the scene. One ICAM, and Two M22 Acada chemical detectors were stored in the metal wall locker. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 4 | AK | MAT |  | 30.50(b)(4) |  |  |  | 0 | 2004-08-20
40967 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-07-28 | 2004-08-18 15:21 | 2004-08-18 | SOURCE TRAIN DID NOT RETRACT "After IVB therapy the source train did not retract due to a kink in the IVB catheter, did not retract to the remote Beta-Cath device. The IVB catheter was immediately withdrawn and placed in the Novoste emergency plexiglass storage safe and then in the IVB storage room. No overexposure was received by the patient or attending staff. Novoste has been notified of the malfunction. The Novoste Beta Cath was returned to the manufacture on August 2, 2004. The IVB manufacturer is Novoste Beth Cath, source Sr-90, 1.71 GBq (46 millicuries). Transfer device Serial No. 92917, and Source train Serial No. ZA543. The device was packaged and returned to the manufacturer on August 2, 2004. This agency did not receive notice of the event within 24-hours" Texas Incident No.: I-8155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-08-23
40965 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-08-17 13:15 | 2004-08-17 15:30 | 2004-08-17 | OFFSITE NOTIFICATION - POSSIBLE DISCHARGE PERMIT VIOLATION At 1145 EDT the Chemistry Tech sampled the Rad Waste Service water overboard line. The sample showed less than 0.02 milligrams per liter (mg/l) residual chloride. The Chemistry Tech adjusted up the chlorination rate. At 1315 a second sample yielded a result of 0.29 mg/l residual chloride. The tech immediately secured the Chloride system, and sampled the intake canal. The results were less than 0.02 mg/l residual chloride. Oyster Creek is monitoring for any environmental impact. The change in residual chloride may not correlate to the increase in chlorination rate, therefore sample error is possible and is under review. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 08/17/04 AT 2123 EDT BY JEFF DOFTAL TAKNE BY MACKINNON * * * "This is a follow-up to an earlier notification made at 15:30 today. Based upon further investigation the Potential NJPES Violation was found to be valid. The residual intake Cl - (Chloride) concentrations were found to be 0.29 mg/l. This is in excess of the 0.2 mg/l limit. The over chlorination event lasted for approximately 2 hours." R1DO (Todd Jackson) notified. The NRC Resident Inspector will be notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-17
40964 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-08-17 05:28 | 2004-08-17 11:46 | 2004-08-17 | MANUAL REACTOR SCRAM DUE TO TRIP OF REACTOR FEEDWATER PUMP "A" ON LOW SUCTION PRESSURE. "With a reactor startup in progress at 0528 PDT, operators at Columbia Generating Station inserted a manual reactor scram when the operating Reactor Feed Water (RFW) pump RFW-P-1A tripped. Reactor power was approximately 20% at the time of RFW pump trip. The cause of the RFW pump trip was due to low suction pressure; the cause of the low suction pressure is currently under investigation. The Reactor Core Isolation Cooling (RCIC) system [was manually started and] was used to maintain reactor vessel water level until reactor pressure was reduced to within the capacity of the condensate booster pumps (500 to 600 psi). The RCIC system has been returned to a standby lineup. The reactor is in Mode 3 (Hot Shutdown) with both reactor recirculation pumps running at minimum speed (15 Hertz). Decay heat is being rejected to the main condenser via auxiliary steam loads. All ECCS systems are operable. All emergency diesel generators are operable. No Safety Relief valves lifted during the scram." The NRC Resident Inspector was notified of this event by the licensee. See similar event number 40959 that occurred on 08/15/04. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-08-17
40963 | 0 | HUMBOLDT BAY | 3 |  |  | [3] GE-1 | 2004-08-17 08:30 | 2004-08-17 11:40 | 2004-08-17 | "REPORT OF MISSING SPECIAL NUCLEAR MATERIAL "This is a non-emergency Event Notification in accordance with 10 CFR 74.11 to inform the NRC of missing special nuclear material of low strategic significance. On July 16, 2004, Pacific Gas, and Electric (PG&E) notified the NRC of a material accountability discrepancy involving a portion of a spent fuel rod used at the Humboldt Bay Power Plant (HBPP) Unit 3 (reference NRC Event Notification 40877). The discrepancy in plant records called into question the location of three approximately 18-inch segments that were cut from a single spent fuel rod in a used fuel assembly (A-49) in 1968. PG&E initiated a comprehensive search of the on-site HBPP spent fuel pool (SFP), a review of plant and nuclear materials shipping records, and interviews with present and former employees and contractors to resolve the material accountability discrepancy and locate the unaccounted for fuel segments. "On August 17, 2004, at 08:30 PDT, the HBPP Plant Staff Review Committee (PSRC) reviewed the results of the search of the SFP to-date and concluded that the search of the most likely locations for the unaccounted for fuel segments (storage containers within the SFP) and all easily accessible spaces in the SFP was thorough and complete and that the search had not located the unaccounted for fuel segments in the SFP. The PSRC also reviewed the results to-date of the in-progress review of plant records, interviews, and nuclear material shipping records and concluded that the relevant information obtained did not definitively identify the on-site or off-site location of the unaccounted for fuel segments. Though it remains probable that the unaccounted for fuel segments will ultimately be found in the SFP or shown to have been shipped to a facility licensed to reprocess or store nuclear materials, PG&E is conservatively considering these segments as missing and making this 1-hour non-emergency event notification in accordance with 10 CFR 74.11. "PG&E will be issuing a press release later today describing the current status of this issue. "PG&E has embarked upon a 'phase II' search of the remaining less-accessible SFP areas and will continue its review of plant records, nuclear materials shipping records (plant and waste repository records), and interviews of plant personnel to definitively locate the missing fuel segments. A supplemental LER will be provided to the NRC when the segments are located or when the phase II search is concluded. "No evidence has been uncovered to support the possibility of theft or diversion of the unaccounted for fuel segments. Due to the high radioactivity of the material, to be handled safely, the segments would have to be encased in a heavy shielded container that would have to be moved with special handling equipment designed for this purpose, precluding an abrupt loss. Since plant start-up, HBPP has been equipped with a system of radiation monitors for the refueling building (where the SFP is located) with alarm setpoints that are capable of alerting plant personnel of the movement of highly radioactive material should the fuel segments have been removed from the SFP without being in a shielded container. This could not have occurred casually without plant staff or security personnel observing the movement. "Because the three approximately 18-inch segments are not readily identifiable in the SFP, three possible scenarios exist. The highest probability is that the fuel segments are in a SFP area that is not readily accessible, and will be located during a more detailed search of these locations. The second highest probability is that the fuel segments were shipped offsite to an appropriately controlled and restricted facility for either analysis or reprocessing. The least probable location, but not yet capable of being ruled out, is that the fuel segments were inadvertently included in a shipment to a licensed, monitored, and restricted LLRW facility. Since these possible locations are licensed, monitored and restricted radiological control areas, the public health and safety has not been adversely affected. "For additional information, refer to licensee event report (LER) 2004-001-00,'Three Missing Fuel Rod Segments,' dated August 16, 2004, and submitted in accordance with 10 CFR 20.2201(b)(2)(ii), (Reference H BL-04-020). "NRC personnel at headquarters and in Region IV have been notified of the status of this issue." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOST/STOLEN SNM | LOST/STOLEN LNM>10X | OFFSITE NOTIFICATION |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 74.11(a) | 20.2201(a)(1)(ii) | 50.72(b)(2)(xi) |  | 0 | 2004-08-17
40962 | 0 | GENERAL ELECTRIC NUCLEAR ENERGY |  |  |  |  | 2004-08-16 16:00 | 2004-08-16 16:04 | 2004-10-11 | PART 21 60-DAY INTERIM NOTIFICATION: NARROW RANGE WATER LEVEL INSTRUMENT LEVEL 3 TRIP This letter provides a 10 CFR21(a)(2) 60 - Day Interim Report notification regarding a potential issue with the Level 3 trip from the narrow range water level instruments that initiate reactor scram. A conservative evaluation by GE Nuclear Energy (GENE) has determined that water level instruments may indicate high by as much as 8 inches, should the reactor water level drop below the dryer seal skirt. At issue is whether with the actual water level as much as 8 inches lower than indicated, the top of active fuel (TAF) will be uncovered for the limiting loss of feedwater event due to 1. Actual water level being lower than indicated when the Level 3 trip occurs, or 2. Failure of the Level 3 trip to occur if water level drops below the narrow range instrument variable leg tap prior to reaching the Level 3 trip setpoint. Because TAF is a Technical Specification Safety Limit, TAF uncovery for a loss of feedwater event would be a Reportable Condition. However, it would not lead to a significant safety hazard due to multiple automatic and passive protection features of a BWR. GENE has completed analysis for BWR 2/3 plants and determined that this is not a reportable condition (i.e., the TAF safety limit is protected). GENE has not completed the analyses for BWR /4-/6 plants. For these plants, GENE has determined that actual water level being lower than indicated by up to 8 inches when the Level 3 trip occurs does not lead to TAF uncovery. However, for these plants GENE has not determined if water level could drop below the narrow range instrument variable leg tap prior to reaching the Level 3 trip setpoint. Therefore, this letter is issued as a 60 - Day Interim Notification under 10 CFR21.21(a)(2) to the BWR/4-/6 plants listed in Attachment 1. The potentially affected plants are being concurrently notified of this situation by a GENE Safety Communication letter. GENE is committed to complete the evaluation by October 11, 2004. Attachment 1 Plants List Below: (Affected Plants - Evaluation incomplete) Clinton, Brunswick Units 1 & 2, Nine Mile Point Unit 2, Fermi Unit 2, Columbia, Fitzpatrick, Grand Gulf, River Bend, La Salle Units 1&2, Limerick Units 1 & 2, Peach Bottom Units 1 & 2, Perry, Cooper, Duane Arnold, Susquehanna Units 1 & 2, Hope Creek, Hatch Units 1 & 2, Browns Ferry Units 1 (plant is in an extended shutdown),2 & 3. * * * UPDATE TO HUFFMAN FROM B. BAHN (FOR J POST) AT 16:16 EDT ON 10/11/04 * * * "GENE has now completed the evaluation and has determined that all BWR/2/3/6 and ABWR plants, and most BWR/4-5 plants are not susceptible to the condition that could result in a failure of the Level 3 trip to occur. These plants are identified as Not Reportable in Attachment 1 [of GENE Part 21 final report to the NRC dated October 11, 2004]. However, for some BWR/4-5 plants, GENE does not have sufficient information to determine if the condition exists that could result in a failure of the Level 3 trip to occur. These plants are notified, as a Transfer of Information under 10CFR21.21(b), as identified in Attachment 1 [of GENE Part 21 final report to the NRC dated October 11, 2004]." The plants where insufficient information for a final determination have been identified by GENE as Columbia, Susquehanna 1 and 2, Browns Ferry 2 and 3. Notified R1DO (Barkley), R2DO(Ogle), R3DO (Clayton) and R4DO (Bywater) and NRR (Hodge). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NC | OTH | GEN | 21.21 |  |  |  | 0 | 2004-08-16
40961 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2004-08-15 13:20 | 2004-08-16 13:25 | 2004-08-16 | AGREEMENT STATE REPORT - LEAKING RADIOACTIVE SHIPMENT "Background: T-hopper containers holding approximately 5 tons of depleted UF4 were packaged for shipment to Nevada Test Site (NTS) as radioactive low specific activity waste. The T-hoppers are over packed in a sealand box holding either two or three T-hoppers depending on the total weight. The shipment package is prepared by spreading an absorbent material around the floor to absorb any condensation. After placement of absorbent, bags of vemiculite are added to fill void space. Sealands are loaded onto flat-bed trucks or pin-type trailers, one sealand per truck. NTS shipments #PDL-04-161, #PDL-04-163, #PDL-04-164, #PDL-04-165, and #PDL-04-166 left the Paducah site on Friday, August 13, 2004, via Tri-State Motor Transit. Each truck was loaded with one sealand. The T-hoppers and all internal materials were surveyed prior to leaving the site and no contamination was found. "Incident and Response Chronology: At approximately 1030 hrs. on Sunday, August 15, 2004, the driver of the truck carrying shipment #PDL-04-161 reported finding a small quantity of a white, granular solid and a clear, gel-like material on the bed of the truck. The truck was stopped in Rio Puerco, New Mexico at a truck stop off Interstate 40 (I-40) West. The driver notified the Paducah Bechtel Jacobs Company (BJC) Transportation Specialist who instructed him to remain at his current location. The Transportation Specialist notified Paducah BJC Waste Generator Services personnel at 1130 hrs. Paducah team consisting of the Project Manager, Waste Generator Services, and Health Physics was assembled to determine appropriate actions. "At approximately 1100 hrs on August 15, 2004, the BJC Transportation Specialist received a call from the driver of shipment #PDL-04-163 reporting similar conditions. This driver was located at Gallup, NM, Exit 16 off of I-40 West. Two other trucks carrying shipments #PDL-04-164 and #PDL-04-166 arrived at Gallup shortly after Paducah received the notification from the first driver. The drivers of these trucks were also instructed to remain in Gallup. Upon inspections by the drivers, one truck, shipment #PDL-04-164, also had material on the bed of the truck. At approximately 1400 hrs. the driver of the fifth truck, shipment #PDL-04-165, was contacted. He was located in Flagstaff, AZ and instructed to remain there. Upon inspection, the driver of this truck also reported seeing the white, granular solid and clear gel-like material. "At 1330 hrs. BJC Oak Ridge Waste Operations personnel notified the Oak Ridge ETTP Park Shift Superintendent (PSS) who initiated emergency response actions. At approximately 1500 hrs, the DOE Region 2 Radiological Assistance Program (RAP) Coordinator notified Paducah that teams of radiological technicians from DOE sites in the area were being dispatched to survey the trucks. A DOE Region IV RAP Coordinator notified Paducah that he would make notifications to the State Police in AZ and NM. "Environmental, Safety and Health Impact: None Identified at the time of the initial report. Based on the initial information from the truck drivers, the description of the material matches that of the absorbent material (Quik-Solid) placed in the containers to absorb any condensation that might form. This material in non-hazardous." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2004-08-19
40960 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-08-16 10:28 | 2004-08-16 12:18 | 2004-08-16 | TRANSFER EMPLOYEE OFFSITE DUE TO ELECTRICAL SHOCK An employee received an electrical shock while working on temporary power on the north side of the unit 2 turbine building. He was transported to the Carolina Medical Center. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-16
40959 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-08-15 13:03 | 2004-08-15 19:24 | 2004-08-15 | MANUAL REACTOR SCRAM DUE TO REACTOR FEEDWATER PUMP TRIP "With a reactor startup in progress at 1303 PDT, operators at Columbia Generating Station inserted a manual reactor scram when the running Reactor Feedwater (RFW-P-1A) pump tripped. Reactor power was approximately 18% at the time of RFW-P-1A trip. The cause of the RFW-P-1A trip was a high RFW Turbine Drain Tank (MD-TK-1) level; the cause of the MD-TK-1 high level is under investigation. The Reactor Core Isolation Cooling (RCIC) was used [manually started] to maintain reactor vessel water level until reactor pressure was reduced to within the capacity of the condensate booster pumps; the RCIC system has been returned to a standby lineup. The reactor is in mode 3 with both reactor recirculation pumps running at minimum speed (15 Hertz). Decay heat is being rejected to the main condenser via auxiliary steam loads. "One control rod that indicated full-in immediately after the scram lost full-in indication eleven seconds after the scram. This control rod indicated full-in again 84 seconds after the scram. "This ENS notification is made pursuant to 10 CFR 50.72(b)(2)(iv)(B)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 18 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-08-15
40958 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-08-15 13:22 | 2004-08-15 15:15 | 2004-08-15 | OFFSITE NOTIFICATION MADE DUE TO INADVERTENT EMERGENCY SIREN ACTUATION "On August 15, 2004, at approximately 1322 hours, the Brunswick site identified an inadvertent actuation of 1 offsite evacuation siren. There are a total of 36 sirens located in Brunswick and New Hanover Counties, NC. The siren in alarm is located in Brunswick County and was in an alarm condition from 1258 until 1341. In accordance with Brunswick operating procedures, the warning points (Brunswick County, New Hanover County and NC State EOC) have been notified of the inadvertent siren actuation. The remaining 35 sirens are operable. INITIAL SAFETY SIGNIFICANCE EVALUATION: "Minimal safety significance. The loss of the single siren will not significantly impact the public notification system. The remaining sirens in both Brunswick and New Hanover Counties have been verified to be operable. CORRECTIVE ACTIONS: "The siren was silenced at 13:41 EDT on August 15, 2004. The cause of the inadvertent actuation will be determined and the siren will be repaired. "The (NRC) resident inspector has been notified." | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Hot Shutdown | Power Operation |  | Hot Shutdown | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-15
40957 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-08-15 04:05 | 2004-08-15 08:50 | 2004-08-15 | AUTOMATIC REACTOR SCRAM FOLLOWING PARTIAL LOSS OF OFFSITE POWER "At 0405 on August 15, 2004, River Bend Station had a loss of 230Kv Line #353 (RSS #2, Port Hudson) feeding the plant's switchyard. This resulted in a generator trip and a reactor scram. Feedwater tripped on a Reactor vessel Level 8 signal. RCIC is operating to control reactor vessel level. SRVs were used to manually control pressure. Mechanical vacuum pump (ARC A) would not start to control condenser vacuum. The MSIVs were manually isolated in anticipation of a Group 6 isolation (low vacuum). There was no ECCS initiation. Power was restored to the mechanical vacuum pump ARC B. Vacuum was restored and main steam lanes are in use for pressure control. We are still investigating the root cause. "The following ESF actuations occurred: "- Division II Diesel Generator "- Standby Gas Treatment System "- Annulus Mixing System "- Control Building Ventilation System." The licensee will inform the NRC Resident Inspector. * * * UPDATE ON 8/15/04 AT 1340 EDT FROM JAMES BOYLE TO GERRY WAIG * * * "River Bend Station is currently in Mode 3, Hot Shutdown. During the event, offsite power was maintained through Reserve Station Service Line #1 to Division 1 safety related equipment and 'A' balance of plant (BOP) non-safety related equipment. The 230 KV line from the plant's switchyard (RSS Line #2) that was lost during the event has been recovered and the Division 2 bus has been restored to its normal power supply. The Division 2 diesel generator has been secured from operation [and has been placed in standby] "During, the event, main condenser vacuum was restored from the main control room by starting the 'B' mechanical vacuum pump. Feedwater Pump 'A' remained available during the event. The circulating water supply to the main condenser remained in operation throughout the event. RCIC [Reactor Core Isolation Cooling] remains in service for reactor vessel level control. The ESF [Emergency Safety Feature] systems have been secured and placed in standby. A root cause team has been assembled to address the cause of the initial failure of the 230 KV Line #353." The licensee has notified the NRC Resident Inspector Notified R4DO (Linda Smith) and NRR EO (Cynthia Carpenter) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-08-15
40956 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-08-14 20:45 | 2004-08-14 21:41 | 2004-08-14 | LOSS OF SAFETY PARAMETER DISPLAY SYSTEM At 2045 [EDT] on 08/14/2004, Computer Maintenance personnel discovered the Unit 2 SPDS computer was not updating properly. A review of history identified that the SPDS computer had stopped updating at 1109 [EDT] on 8/14/2004. The Control Room was notified. Computer Maintenance was successful in resetting the SPDS computer at 2100 [EDT], and it is now properly operating. Since the Unit 2 SPDS computer system was unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and reportable under 10CFR50.72(b)(3)(xiii). The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-14
40955 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-08-14 12:25 | 2004-08-14 19:05 | 2004-08-14 | LOSS OF SEVERAL OFFSITE EMERGENCY PREPAREDNESS SIRENS DUE TO ADVERSE WEATHER "On August 14, 2004, at approximately 1225 hours [EDT], Brunswick began losing the function of several offsite emergency preparedness sirens as a result of adverse weather conditions associated with Hurricane Charley. There are a total of 36 sirens located in Brunswick and New Hanover Counties, NC. The total number of inoperable sirens peaked at 25. As of 1825 hours [EDT], all but 6 sirens located in Brunswick County have been returned to operable status. At present, all inoperabilities have been the result of loss of AC power. The Brunswick County Emergency Operations Center is aware of the condition of the sirens and maintenance activities are in progress to restore the siren capabilities. Other communications with local, state, and federal emergency response organizations have not been affected. The initial safety significance of this condition is considered to be minimal. Unit 1 is currently in Mode 3 and Unit 2 is operating in Mode 1 under normal parameters. State and county emergency response officials are aware of the condition and compensatory measures are in place to provide warning to the affected areas if required. The licensee has notified the NRC Resident Inspector. | 69 | 96 | 0 | 69 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-14
40954 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-08-14 12:59 | 2004-08-14 15:47 | 2004-08-14 | RPS ACTUATION DUE TO LOSS OF OFFSITE POWER "On August 14, 2004, at approximately 1259 hours [EDT], the unit scrammed due to a loss of offsite power. The cause of the loss of power has not been determined at this time. The four emergency diesel generators started as required and properly aligned to the emergency buses. All control rods properly inserted. "The initial safety significance of this condition is considered to be minimal. All safety systems function properly with the exception of 1 B Standby Gas Train. The 1 B Standby Gas Train tripped due to an overheat condition. Safety significance of this failure is minimal since the 1A Standby Gas Train operated properly and Reactor Building Ventilation System isolated. The plant is in a stable condition. "Troubleshooting activities are in progress to determine the cause of the event and corrective actions." Received Group II, VI, and VIII PCIS isolations due to the loss of power. The MSIVs are closed and the licensee manually started RCIC for reactor level control and HPCI for reactor pressure control. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 69 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-08-14
40953 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-08-14 13:08 | 2004-08-14 13:40 | 2004-08-14 | NOTICE OF UNUSUAL EVENT EMERGENCY DECLARED DUE TO LOSS OF OFFSITE POWER Licensee declared an Unusual Event at 1308 EDT on 08/14/04. Unusual Event was declared due to a Loss of Offsite Power which occurred due to a Lockout trip of the Station Auxiliary Transformer. All four emergency diesel generators started and loaded properly. On the reactor trip, all rods fully inserted. They received Group II, VI, and VIII PCIS isolations due to the loss of power. The MSIVs are closed and the licensee manually started RCIC for reactor level control and HPCI for reactor pressure control. The licensee in activating the Emergency Response Organizations. No offsite assistance required. The licensee notified the NRC Resident Inspector, State and local Emergency response organizations. * * * UPDATE PROVIDED TO JEFF ROTTON FROM KEITH HANZ AT 1727 EDT ON 08/14/04 * * * Licensee declared termination of the Unusual Event at 1713 EDT on 08/14/04 after restoring offsite power to the Station Auxiliary Transformer, BOP and Emergency Buses. The licensee notified the NRC Resident Inspector. Notified R2DO (Julian), R4DO (Smith), IRD (Nieh), NRR EO (Carpenter), DHS (Doyle), and FEMA (Sullivan) | 0 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-08-14
40952 | -1 | GRAND GULF | 1 |  |  | [1] GE-6 | 2004-08-14 10:25 | 2004-08-14 14:44 | 2004-09-02 | GRAND GULF STANDBY SERVICE WATER "C" AND HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE "During underwater inspection of the Standby Service Water 'C' system, four piping supports were found with considerable degradation. As a result, the Standby Service Water 'C' and High Pressure Core Spray systems were declared inoperable per Technical Specifications (TS). High Pressure Core Spray is a single - train system that performs a safety function." The licensee entered the applicable sections of TS 3.7.2, High Pressure Core Spray Service Water System, and TS 3.5.1, High Pressure Core Spray. The licensee has notified the NRC Resident Inspector. * * * RETRACTION ON 9/2/04 AT 1610 EDT FROM MICHAEL LARSON TO ARLON COSTA * * * "Reactor Plant Event Number 40952 was reported on August 14, 2004 at 1344 for an inoperable Standby Service Water 'C' and High Pressure Core Spray system due to degraded Standby Service Water 'C' lateral piping supports. This event is hereby retracted. "The retraction is based on engineering evaluations and calculations performed that determined that the Standby Service Water 'C' and High Pressure Core Spray System were both OPERABLE and capable of performing their intended safety function. The engineering evaluation and calculations concluded that even without the degraded lateral piping supports, the Standby Service Water 'C' piping maintained its structural integrity and would have performed its intended safety function." The licensee notified the NRC Resident Inspector. Notified R4DO (W. Jones). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-08-14
40951 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-08-13 18:20 | 2004-08-13 19:04 | 2004-08-14 | NOTICE OF UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING Licensee declared Unusual Event due to a Hurricane Warning being issued by the National Weather Service for Brunswick County, NC which includes the Brunswick site. No protective actions are required at this time. No emergency facilities have been activated at this time. No offsite assistance requested. The licensee has notified the NRC Resident Inspector. * * * UPDATE PROVIDED AT 1426 ON 08/14/04 TO JEFF ROTTON FROM KEITH HANZ * * * Licensee terminated the Unusual Event at 1403 EDT on 08/14/04 due to the lifting of the hurricane warning in Brunswick County, North Carolina. The licensee has notified the NRC Resident Inspector. Notified R2DO (Julian), R4DO (Smith), IRD (Nieh), DHS (Inzer), FEMA (Eaches). | 67 | 96 | 0 | 67 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-08-13
40950 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-08-13 10:30 | 2004-08-13 15:23 | 2004-08-13 | CONTROL ROOM EMERGENCY ZONE BOUNDARY OUTSIDE DESIGN BASIS "On 08/13/2004 at 1030 CDT the Kewaunee Shift Manager was notified the control room emergency zone (CREZ) boundary was outside assumed design basis for an unknown amount of time. This is an eight hour non-emergency reportable under 10 CFR 50.72(b)(3)(v)(D), Accident Mitigation. "On 08/12/2004 at 1915 [CDT], the local operator reported to the control room that he found a control room emergency zone (CREZ) boundary door in the unlatched open position. The local operator immediately ensured the door was secured in the latched closed position. Per Kewaunee's barrier control procedure the Shift Manager requested an evaluation be performed to determine the impact of potential air in leakage on the control room post accident dose consequences. "On 08/13/2004 at 1030 CDT, the engineering staff reported that based on engineering judgment the unfiltered in leakage that could have entered the CREZ would likely exceed that assumed in the post accident dose analysis. Based on this judgment, the in leakage would have prevented the Control Room Post Accident Recirculation System from mitigating the dose consequences to the control room staff to values less than those determined in accident analysis. "At the time of discovery the local operator immediately secured the boundary door rendering the CREZ boundary operable. This event has been entered in the Kewaunee corrective action process to investigate the cause of the door being in the open position. No other safety related equipment was out of service at the time of discovery." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-08-13
40949 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-08-13 08:36 | 2004-08-13 12:56 | 2004-08-13 | FITNESS-FOR-DUTY REPORT INVOLVING A LICENSED OPERATOR A licensed employee was determined to be unfit for duty based on current requirements for unescorted access. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee HAS informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 26.73 |  |  |  | 0 | 2004-08-13
40948 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-08-13 08:00 | 2004-08-13 11:22 | 2004-08-13 | LOSS OF THE SAFETY PARAMETER DISPLAY SYSTEM (SPDS) FOR GREATER THAN 8 HOURS "At 08:00 on 8/13/04 Computer Maintenance personnel discovered the Unit 1 SPDS computer was not updating properly. A review into the history identified that the SPDS computer had stopped updating at 21:00 on 8/12/04. The Control Room was notified. The computer group was successful in resetting the SPDS computer and is now properly operating. "Since the Unit 1 SPDS computer system was unavailable for greater than 8 hours, this is considered a loss of Emergency Assessment Capability and therefore reportable under 10CFR50.72(b)(3)(xiii)." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-13
40947 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2004-08-11 10:45 | 2004-08-13 11:03 | 2004-08-13 | KENTUCKY AGREEMENT STATE NOTIFICATION University of Louisville Hospital physicians were injecting a prescribed treatment of Yttrium-90 (Therasphere) 3.32 GBq (GigaBecquerel) into a patient's liver and only 0.72 Gbq was actually administered (22%). The licensee is investigating the cause of the misadministration. Initial investigation points to a tubing extension modification made to carry the dose to the targeted organ since the majority of the flow remained in the tubing. Hospital physicians have used the equipment 5 to 6 times without any incident. The licensee will send the tubing back to the manufacturer for further investigation. The physician notified the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2004-08-18
40945 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-08-12 23:00 | 2004-08-12 23:25 | 2004-08-13 | UNUSUAL EVENT DECLARED DUE TO HURRICANE WARNING FOR HURRICANE CHARLEY Licensee declared an Unusual Event due to the notification of a Hurricane Warning for the site area from the National Weather Service. The unit will be required to shutdown if Category 3 hurricane winds are experienced on site. Presently Hurricane Charley is exhibiting Category 2 winds (105 MPH). The licensee has notified the NRC Resident Inspector, State and Local Emergency management organizations. * * * UPDATE AT 0930 ON 8/13/04 BY A. COSTA * * * The Agency entering Monitoring Mode at 0800 on 8/13/04 and Region 2 is in the lead. Notified IRD management and the following federal agencies: DHS, FEMA, DOE, EPA (NRC), USDA and HHS. * * * UPDATE ON 8/13/04 AT 2127 EDT FROM JAMES HUFFHAM TO GERRY WAIG * * * The agency exited the Monitoring Mode at 2127 EDT on 8/13/04. Notified the following federal agencies: DHS (Akers), FEMA (Sullivan), DOE (Pauley), EPA (NRC) (Layman), USDA (Mahar), and HHS (Hogan). Additionally, the following NRC staff were notified: H. Nieh, R. Orchard, S. Frant, P. Wilson, M. Weber, C. Jackson, R. Hogan, W. Outlaw, S. Gagner, L. Smith (R4DO). * * * UPDATE ON 8/13/04 AT 2155 EDT FROM MIKE KELLY TO JEFF ROTTON * * * The licensee reported that hurricane Charley has cleared their service territory and that Crystal River 3 exited the Notice of Unusual Event (NOUE) on 8/13/04 at 2141 EDT. Notified the following federal agencies: DHS, FEMA. Additionally, the following NRC staff were notified: H. Nieh, R. Borchardt, S. Frant, P. Wilson, M. Weber, C. Jackson, R. Hogan, W. Outlaw, S. Gagner, L. Smith (R4DO). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-08-12
40944 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-07-27 | 2004-08-12 18:13 | 2004-08-12 | AGREEMENT STATE REPORT - DAMAGED TROXLER MOISTURE DENSITY GAUGE Taken in part from email sent from Washington Department of Health "The licensee reported that a Troxler moisture/density gauge, Model 3430, Serial Number 19736 was damaged while in use. The gauge was backed over by a water truck while the source rod was extended into the road surface. The gauge contained two sealed sources, (Cs-137, 0.296 GBq [8 milliCuries] and Am-241:Be 1.48 GBq [40 milliCuries]). The licensee stated the gauge had been placed on the surface with the source rod in a test hole. The licensee was looking for a new test location when the truck damaged the gauge. "The licensee attempted to retract the Cs-137 source into its shielded position but could not. The operator placed the end of the probe back in the test hole and waited for help. A manufacturer's representative arrived at about 10:30 a.m. to assist the licensee. He surveyed the area and found that the highest reading was 50 mR/hr directly beside the gauge with the rod in the ground. A second attempt was made to retract the source rod into the shielded position. This resulted in moving all but the last ½ inch inside the shield. At this point the source rod with shield was placed in a five gallon bucket and filled with dirt and rock while the transport box was made ready. "Both the Cs-137 and Am-241:Be sources appeared to be intact and undamaged. The representative attempted again to move the Cs-137 source into the shielded position. This attempt was successful. The Cs-137 source rod/shield assembly and Am-241:Be source were placed into the transport box and more dirt and rock were added. The box was then locked and chained inside the licensee's truck. "Dose-rate measurements were taken and noted to be 10 mR/hr at 6 inches from the box. The driver's side of the cab measured about 2 mR/hr. The licensee was instructed to park the vehicle, not to leave it unattended and not to drive it until additional shielding could be located. The representative took possession and transported the gauge to a storage area where it was secured. A leak test was performed and found to be negative. The representative will ship the gauge for disposal." Washington State event report #WA 04-044. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-08-17
40943 | 0 | NY STATE DEPARTMENT OF HEALTH |  |  |  |  | 2004-08-10 | 2004-08-12 17:12 | 2004-08-12 | AGREEMENT STATE REPORT - CONTAMINATED BRACHYTHERAPY SEEDS "A New York State Department of Health licensee reported on 8/10/04 that prostate seed implant needles were found to be contaminated during a post implant radiological survey in the operating room. Two post implant urine samples from the patient were saved and were found to be contaminated as well. Radiograph of the prostate post implant indicated all seeds were implanted. Hospital staff believed that the contamination was attributable to the implant procedure as the patient had not received a diagnostic nuclear medicine procedure and there was no evidence of any other source for the contamination. The radiation oncologist contacted the patient and was able to administer KI [Potassium Iodide] later in the day, and he will evaluate the need for ongoing treatment with KI. "New York State Department of Health staff went to the hospital on 8/11/04 to investigate this incident. Confirmatory measurements were made and the plastic needle packing tray, needles, lead pouch and urine samples were found to be contaminated. A third urine sample was obtained from the patient on 8/11/04, which also is contaminated. The radiation oncologist who performed the procedure stated that there were no problems with the needles or the implant procedure. The needles were examined and no bends, crimps or damage were observed. The hospital, has notified the pharmacy that had provided the preloaded sterile needles. NRC Region 1 staff were contacted by phone and were given the name of the pharmacy. "The Radiation Safety Officer took the initial urine sample to another New York State Department of Health licensee on 8/11/04 for nuclide identification and rough quantification using a HPGe detector. The isotope in the urine was identified as I-125 and the activity was estimated to be 34 nanocuries per cc (volume of urine sample collected was 200 cc). The patient's urine samples will be sent to DOH Wadsworth Laboratories for analysis. Future samples are expected to be collected and analyzed. "The brachytherapy seeds were manufactured by Mills Biopharmarmaceuticals, Inc., sold by Mentor MBI (Oklahoma City, OK) and loaded into needles by the pharmacy. Brachytherapy seed specifics are: Model: 125SL Lot Number: 042814 Batch Number: IB040142N Seed activity on 8/10/04: 0.405 millicuries" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2004-08-17
40942 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-08-10 | 2004-08-11 13:26 | 2004-08-11 | AGREEMENT STATE REPORT - WELL LOGGING SOURCE LOST IN WELL DURING TRAINING The following is taken from a facsimile sent by the Agreement State (Texas) "Event description: After well logging operations on the afternoon of August 10, 2004, the well logger was removing the source from the tool on the training well. The tool was not fully engaged with the source. When the source cleared the logging tool, the well logger bumped the source into the deflector, causing the source to drop from the handling tool. The deflector performed properly and deflected the source, an 18 curie Am/Be (neutron) source downhole. This is the Atlas No. 2 well, an un-cased hard-rock well located on the Baker Hughes property for training of Baker Hughes staff. The source is a GammaTron Model DA20, Serial No 36313. The source is known to be at the bottom of the 5750 foot well. The training well is currently full of fluid. The operator is going to replace the fluid with clear fluid and begin 'fishing' operations. The wellbore is 8-7/8 inches and this source with nose plug is 9 inches in length." TX Incident # I-8152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-08-16
40941 | -1 | US ARMY |  |  |  |  | 2004-07-28 09:20 | 2004-08-11 12:06 | 2004-08-17 | MARINE CORP TRITIUM DEVICE INCIDENT "On 28 July 2004, at approximately 0920 hours, the installed Tritium-in-Air monitor for the Tritium Instrument Repair Room (TIRR) at Maintenance Center Albany [(MCA), Georgia] abruptly alarmed. "On 27 July 2004, the six counter sources (0.45 Curies each/2.7 Curie total) contained within the gear box of an M137 panoramic telescope had been replaced. The M137 unit was placed on an alignment fixture on the morning of 28 July. "Upon alarm actuation, the TIRR and the Optics/Fire Control Shop were evacuated. Assembly of personnel was in a common area exterior to the shop. The MCA radiation protection assistant (RPA) and the Base radiation safety officer (BRSO) were summoned. Entry into the TIRR was made with the use of a Johnston Labs Model 111 portable tritium-in-air monitor. Suspicions were satisfied when the portable tritium-in-air monitor indicated 30-microCuries/m3 of tritium gas in the immediate vicinity of the test fixture and mounted M137 panoramic telescope. The TIRR utilizes a negative pressure ventilation system, which is directly ducted to the environment. The door to the TIRR was opened and within approximately one-half hour, the gaseous tritium levels had been reduced to background. The M137 was double bagged and placed within the TIRR vent hood. "Two workers were present in the TIRR when the evacuation alarm sounded. The shop supervisor entered the area to assess the accuracy of the alarm condition. These three individuals were sent to the on-base medical clinic for urine collection. Samples were taken at time zero plus four hours, time zero plus eight hours, and for the-twenty-four hour period immediately following the time zero plus eight hour sample. The primary worker received a slight uptake of gaseous tritium. Dose calculations for that uptake proved the uptake to be [statistically] less than 0.0 milliRem. The other worker and the supervisor showed no evidence of any tritium uptake. Contamination wipes revealed no contamination of the test fixture or the wall." * * * UPDATE 1120 EDT ON 8/17/04 FROM T. GIZICKI TO S. SANDIN VIA FAX * * * The licensee is retracting this report based on the following: "This note is to rescind the incident report number 40941. The event occurred at a Marine Corp Base in Albany, GA. The initial call into the NRC Operation Center on 10 August, 2004, stated that this was a potential incident under Part 30.5. "After further review of the incident we have concluded and concurred with by Mr. Darrel Wiedeman, Region III, that the release of tritium was very minimal resulting in no closure of work areas, no surface contamination of work areas, or radiation dose to employees involved. The event therefore is determined to be non-reportable." Notified R1DO(Jackson), R2DO(Julian), R3DO(Clayton) and NMSS (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2004-08-11
40940 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-08-11 08:30 | 2004-08-11 10:15 | 2004-08-11 | OFFSITE NOTIFICATION OF STATE AGENCY REGARDING POTENTIALLY OIL CONTAMINATED SOIL "On August 11, 2004, at approximately 0830 AM CDT, a non-Emergency notification was made to the Wisconsin Department of Natural Resources regarding a discovery, on August 4, 2004, of diesel fuel odor in soil at the Point Beach Nuclear Plant [PBNP]. The source of the odor is believed to be oil contaminated soil caused by a past accidental environmental release of fuel oil. "This condition was identified while digging holes for a new fence on the northwest side of the plant as part of the PBNP security upgrade. During the excavation, an odor reminiscent of diesel fuel was noted to be emanating from the dirt that was dug up in one area. The dirt from the holes was dry with no obvious fuel oil present. No diesel fuel odor was noted from water and soil at the outfall of a drain in the vicinity of this area. "The quantity of diesel contaminated soil is unknown. NMC plans to conduct an investigation to determine the nature and extent of contamination and to ultimately conduct remediation as appropriate." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-11
40939 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-08-10 18:30 | 2004-08-10 21:42 | 2004-08-12 | AGREEMENT STATE REPORT - LOST/STOLEN MOISTURE DENSITY GAUGE "A moisture density gauge, model CPN MC-3, containing approximately 8 milliCuries of Cs-137 and 30 milliCuries of Am-241 was lost from the back of a pickup truck while traveling from a jobsite in Carlsbad, CA to the company home office in San Diego. The jobsite was on Cassia Road (Thomas Guide, page 1127, D4-E4). It was reported that the gauge was inadvertently left in the back of the pickup truck without being put into the transportation case, neither the gauge nor the transportation case were secured to the truck, and the truck tailgate was left down. Both the gauge and the transportation case apparently fell out of the truck in the first few miles of travel. The driver noticed the tailgate down shortly after turning onto Palomar Airport Road from El Camino Real (Thomas Guide, page 1127, E2). The driver back tracked and found the case but not the gauge. Local law enforcement authorities were notified, and the RSO went to the scene to assist in attempting to locate the gauge." * * * UPDATE ON 8/11/04 AT 1900 EDT FROM ROB GREGER TO GERRY WAIG * * * Mr. Greger reported that the lost gauge was recovered about 1 block from the jobsite today at approximately 1300 PDT. Additional recovery details will be provided tomorrow, 8/12/04. Notified R4DO (Linda Smith), NMSS (Daniel Gillen), TAS (Aaron Danis), Mexico (CNSNS) by facsimile. * * * UPDATE ON 8/12/04 AT 1509 EDT FROM ROB GREGER TO GERRY WAIG VIA FACSIMILE* * * "The gauge was recovered around 1 pm on 8/11/04. It had apparently fallen from the truck a short distance from the construction site. Someone apparently found it and placed it on an adjacent sidewalk. An adjacent business owner (DELETED) noticed the gauge on the sidewalk in front of their business at the end of the day 8/10/04. When the gauge was still there the next morning, they called the phone number of a gauge service company (Mauer Technical Services) listed on a sticker on the gauge, and reported that the gauge was apparently abandoned. Mauer contacted the company that owned the gauge (Christian Wheeler Engineering), who recovered the gauge. When found, the gauge was locked with the source in a shielded position. There was no apparent damage to the gauge. "California RHB authorities will be pursuing enforcement action with Christian Wheeler Engineering for the loss of the gauge. "Some details of the loss that were initially reported to California RHB apparently were incorrect. The attached Investigation form has been revised to reflect our current knowledge of this matter." [See Below] "A moisture density gauge, model CPN MC-3, containing approximately 8 mCi of Cs-137 and 30 mCi of Am-241 was lost from the back of a pickup truck while traveling between jobsites in Carlsbad, CA on 8/10/04. The truck left a jobsite on Cassia Road (Thomas Guide, page 1127, D4-E4) with the gauge. It was reported that the gauge was inadvertently left in the back of the pickup truck without being put into the transportation case, and with the truck tailgate was left down. Within a couple miles of travel, the driver noticed the tailgate down while he was driving on El Camino Real (Thomas Guide, page 1127, E2). The driver back tracked, but could not find the gauge. Local law enforcement authorities were notified, and the RSO went to the scene to assist in attempting to locate the gauge." Notified R4DO (Linda Smith), NMSS (Daniel Gillen), TAS (Matt Hahn) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-08-13
40938 | 0 | EARTH ENGINEERING, INC. |  |  |  |  | 2004-08-10 15:30 | 2004-08-10 17:28 | 2004-08-10 | DAMAGED TROXLER DENSITY GAUGE At approximately 1530 ET on 08/10/04, a Troxler density gauge (Model # 3440, S/N 35192, 8 milliCuries Cs-137 and 40 milliCuries Am-241/Be) was run over by a compactor at a construction site in Upper Chichester, PA. The gauge source rod was bent, preventing retraction of the source point into its shield. The licensee secured the area and performed radiation surveys. No external contamination was found. The licensee has contacted Troxler who will send a shipping container for returning the gauge for repair. In the interim, the licensee plans on transporting the gauge to their facility in East Norton, PA. Established a conference with NMSS (D. Gillen) and Region 1 (E. Ulrich) who provided advice to the licensee on transporting the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2004-08-10
40937 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-08-05 | 2004-08-10 14:51 | 2004-08-10 | AGREEMENT STATE REPORT - IODINE-125 CONTAINER MISTAKENLY DISPOSED OF AS TRASH The following information was received via email: "Approximately 2.5 milliCuries of I-125 was apparently mistakenly disposed to normal trash on 08/05/04. The lost I-125 was received in a single container along with a second container of approximately 2.5 milliCuries of I-125. Normally only one container is received at a time. However, this time two containers were shipped in a single package. The shipping department extracted one of the two containers from the incoming shipping package, and then dumped the remainder of the packing materials to normal trash, apparently including the second container of I-125. "The loss was discovered 08/09/04 when the radiochemists went to utilize the I-125, and one-half of the shipment was missing. The licensee verified with the shipper that two individual containers were sent in the same package, which also agreed with the activity listed on the shipping papers. The licensee's trash was picked up early morning 08/09/04, and when contacted by the licensee, the trash hauler reported that the trash had already been dumped in a local landfill. "Radiation levels at one foot from the shielded container were approximately 0.11 millirem/hour based on measurements made of the package that was still onsite. The shielded container holding the lost I-125 was sealed shut, and is not expected to open with normal trash hauling." California Event # 080904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-08-13
40936 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2004-08-09 08:30 | 2004-08-10 10:22 | 2004-08-10 | SPILL OF I-131 RESULTING IN CONTAMINATION On 08/09/04, Cardinal Health reported to the Wisconsin Department of Health and Family Services- Radiation Protection Section that the Cardinal Health Nuclear Pharmacy located in Madison, WI had a spill of approximately 50 milliCuries of an I-131 sodium iodide solution at approximately 0830 CDT on 08/09/04. Under Wisconsin regulations, HFS 157.13(17)(b)(1)(b), the licensee is required to report this within 24 hours. This preliminary report describes what the licensee initially reported. The licensee will provide a formal written report within 30 days as required by subsection (c) of the same section of the regulations. The spill occurred while transferring a stock bottle from a glovebox to a fume hood. The lead pig containing a vial of 50 milliCuries of I-131 slipped from the individual's hands, hit the floor and spilled some or all of the contents on the floor and adjacent areas. The pharmacy RSO evacuated the area and cleaned the spill to the extent possible. The vial and pig were double bagged and placed in the fume hood. Fixed contamination was covered with lead sheets and general radiation levels are less than 1 mR/hr. A spot on a door in the restricted area reads 10 mR/hr and they are attempting to decontaminate it. Pharmacy staff will pull air samples and will collect thyroid counts on all affected personnel. The pharmacy continues to operate. The Wisconsin Department of Health and Family Services dispatched a two person radiation survey team to the Cardinal Health Nuclear Pharmacy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2004-08-13
40935 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-07-01 | 2004-08-10 09:20 | 2004-08-10 | LOST TRITIUM EXIT SIGN "The Department [of Public Health for Colorado] received notification from a company that a generally licensed exit sign containing tritium was lost. The company, State Farm Mutual Insurance Company, located in Greeley, Colorado 80638, stated that the sign was discovered missing, in July of 2004. The sign was taken down during a remodeling project in 1996, and was supposedly placed into storage. However, recent attempts to locate the sign have been unsuccessful. A representative from the company stated that they now believe the sign was disposed of at the landfill along with the rest of the construction debris. The sign is a Brandhurst (SRB) Luminexit, Model B100, S/N 552371, that contained about 25 curies of tritium when new (1993). The sign was obtained under the provisions of a general license." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-08-13
40934 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-08-08 18:00 | 2004-08-09 17:53 | 2004-08-09 | WASHINGTON AGREEMENT STATE REPORT ON LOST TROXLER GAUGE "Licensee reported a theft of a Troxler Nuclear moisture/density gauge model 3430, serial number 23717. The theft occurred at approximately 6:00 p.m. Sunday August 8, 2004 at the Licensee's address, 1120 West Lincoln Avenue, Yakima, Washington. "A gauge operator working for the licensee placed the transport box with the gauge in the bed of an open pick-up truck and secured the handle of the gauge to a tie-down in the truck with a single lock and chain. The operator was also the driver of the transport vehicle. The vehicle was parked near the rear entry of the Licensee's facility. The driver went back inside the facility and left the truck unattended for approximately 20 minutes. When he returned, he discovered the chain had been cut and the locked transport box with the locked gauge inside had been stolen. "At approximately 6:30 p.m. the Licensee notified both the local police department and the Washington State Department of Health, Office of Radiation Protection emergency hotline to report the event. "The Licensee reported that they performed a visual search in the immediate area of their facility in case the perpetrator dropped the box with gauge in a dumpster or other concealed location. "No media attention. Isotope and Activity involved: 1.48 GBq (40 mCi) Am-241:Be and a 0.296 GBq (8 mCi) Cs-137 source. The Cs-137 source serial number is 75-5803 and the Am-241Be: source serial number is 47-1963. "Police notified 6:30 p.m. August 8, 2004 of the theft of the gauge. The police report number is 04-13612. The gauge has not been recovered. "The licensee reported the last leak test performed was March 29, 2004. "The gauge was stolen from the bed of an open 2002 Chevy S-10 pick-up truck. The gauge was in the manufacture's Type A transport box." Washington Event Report No.WA-04-046. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-08-12
40932 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2004-08-08 22:00 | 2004-08-08 22:15 | 2004-08-08 | TECH SPEC SHUT DOWN DUE TO EMERGENCY DIESEL GENERATOR FAILURE "On August 2, 2004, at 0200, Emergency Diesel Generator (EDG) 12 was removed from service for scheduled maintenance. During surveillance testing, the EDG scavenging air blower failed on this Fairbanks Morse diesel. Repairs will not be completed within the 7 day LCO, which expires at 0200 on August 9, 2004. A plant shutdown commenced at 2200 hours on August 8, 2004, per TS 3.8.1, Condition C.1." The Licensee notified the NRC Resident Inspector. | 99 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-08-08
40931 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2004-08-04 13:00 | 2004-08-06 15:11 | 2004-08-06 | AGREEMENT STATE REPORT "Event description: The licensee called to report a fire in the depleted uranium (DU) machining bay. The fire spread into the ventilation duct and filter housing. The fire was contained inside the ventilation duct and filter housing. The fire blistered the paint on the ventilation ducting and Torit filter housing and breached the ventilation system filters (bag and HEPA). A minor release to the environment occurred through the stack. Visible smoke was observed coming through the stack for a 6 - 8 minute period until the ventilation blast gate was closed. Air sample data indicated the uranium in air concentration in the machining area was 2% DAC. The air effluent concentration through the stack was 15% of the effluent limit. Personnel were evacuated from the DU machining area and from the office areas. Production at the grinder will not restart until the cause of the fire is known and corrective actions can be taken to prevent reoccurrence. A written report will be submitted to the Division. Report number: TN-04-105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2004-08-11
40930 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-08-05 | 2004-08-06 14:01 | 2004-08-06 | AGREEMENT STATE - RECOVERED DEVICE CONTAINING RADIOACTIVE MATERIAL "On August 5, 2004, the Arkansas Department of Health, Radioactive Materials Program, recovered a device containing radioactive material from a scrap metal yard in Dumas, Arkansas. Radiation readings at contact with the port opening are 60-70 mR/hour. It appears that the shutter is open and the source is in the open position. Radiation readings at one meter from the port opening are 0.15 mR/hour. "Analysis by the Department's Radiochemistry Laboratory identify the isotope as Krypton-85. The activity is unknown. The device is 4 inches (wide) by 3.5 inches (height) by 6.5 inches (length). The device is mounted on 10 inch diameter steel plate. There are no radiation markings or labeling on the device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2004-08-11
40929 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-08-03 | 2004-08-06 11:35 | 2004-08-06 | AGREEMENT STATE REPORT INVOLVING DETECTION OF A PLATED SOURCE LEAK "This report is sent in compliance with RH 4.58. On August 3, 2004, we received notification from our monitoring service that a wipe of a licensed plated source tested positive for leakage. The wipe was taken on June 30, 2004. The source is a 3 milliCurie, Curium 244, plated source, manufactured by Isotope Products Lab, model number AFR244-3M. We inspected the source and confirmed that it was leaking. The plated surface appears to be slightly corroded. A leak test conducted on December 30, 2003, did not detect any leakage, so the leakage started sometime during the ensuing 6 months. "The source was stored inside a plastic box. The box was in a plastic baggy. The baggy was in a storage cabinet in Meyer Hall Laboratory 147. We removed the plastic baggy and all its contents including the leaking source. This material was placed in a sealed plastic jar and is in storage in our Hazardous Material Management Facility. "We surveyed the area around the storage location with a thin window pancake GM detector and found no obvious contamination. We have also taken numerous wipes in and around the storage location. These will be analyzed by Liquid Scintillation Counting to determine if further decontamination is necessary. The storage cabinet has been placed off-limits until analysis of wipes is completed. "Interviews with faculty members and graduate students indicate that no one has touched the source during the last six months. "We will report the leak to the manufacturer." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-08-11
40928 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-08-06 08:17 | 2004-08-06 11:08 | 2004-08-06 | OFFSITE NOTIFICATION TO OTHER GOVERNMENT AGENCIES CONCERNING EMERGENCY RESPONSE MESSAGE NOT MARKED DRILL "This is a notification made under 10CFR 50.72(b)(2)(xi) as a media sensitive event. At 0817 an inadvertent telephone communication to site ERO responders was made. The telephone notification erroneously reported that a security event had occurred at the Prairie Island Nuclear Plant, that the ERO was being activated, and that responders were to report to the back up EOF. No security event has occurred at the Prairie Island Nuclear Plant. Local media has been notified regarding the inadvertent notification and that no security event has occurred at the Prairie Island Nuclear Plant. No news release is planned." This erroneous notification occurred during a training exercise for Security Emergency Communicators. The notification that went out to ERO responders did not identify the message as a drill message. Licensee notified the NRC Resident Inspector, State and Local Emergency Response organizations and local governments. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-06
40927 | 0 | BATTELLE MEMORIAL INSTITUTE |  |  |  | ADVANCED FUEL R&D AND PILOT PLANTS | 2004-08-04 09:00 | 2004-08-05 16:41 | 2004-08-05 | THE LICENSEE VIOLATED LICENSE CONDITION 10 CFR 20.1703(a) On 08/04/04 @ 0900 CDT workers were assigned to perform activities in the High Energy Radiation Cell (HEC) were observed using their new style of powered air purifying respirator (PAPR) in a configuration that is not approved by the manufacturer. The assigned crew, two laborers and a HP Tech, were instructed to pull out of the HEC. The crew spent approximately 15 minutes in the HEC. During the initial fact finding assessment it became evident that the incorrect configuration PAPR was not only restricted to the observed use in the HEC, but had been used periodically for work previously at the facility over the last few months. Individuals were questioned on the performance of prerequisite inspections and checks of the PAPR unit. Individuals stated that they had performed the required face piece fit check (negative pressure method) and flow test of the unit prior to each use. In this improper configuration, the individuals were using uncertified equipment, however, no over exposure is expected to the individuals. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2004-08-06
40926 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-08-05 08:00 | 2004-08-05 09:47 | 2004-08-05 | LOSS OF PROMPT NOTIFICATION SYSTEM "The Plant Emergency Preparedness Department contacted the NOAA weather service in Jacksonville due to an alarm on the Prompt Offsite Notification System. NOAA has confirmed that they cannot activate the Prompt Notification System which is considered a major loss of offsite notification capability. "The problem is in the Jacksonville area and the local phone service has been notified to determine the cause and repair. The loss occurred at 0800 and all state and local agencies have been notified to use alternate means of notification. "The plant was notified by the NOAA weather service in Jacksonville that ail service has been restored and the Prompt Notification System was returned to service at 0914 on 08/05/04." The licensee informed both state and local agencies and the NRC Resident Inspector. | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-05
40925 | -1 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2004-08-04 23:24 | 2004-08-05 06:58 | 2004-08-05 | LOW REFUELING WATER STORAGE TANK LEVEL "Following calibration of the refueling water storage tank (RWST) level indication, the as-left Control Room level instrument indicated 35.3 feet in the RWST. Tech Spec required level is 35.4 feet. Alternate indication including the local level indicator and the absence of a low RWST level alarm indicated adequate RWST level. A one hour Tech Spec AOT [Allowed Outage Time] was entered at 2324 EDT on 8/04/2004. Indicated level was restored to 35.4 feet at 0013 EDT on 08/05/04 and the AOT exited. "This event is being reported under 10 CFR.50.72(b)(3)(v)(D) as the indicated level of 35.3 feet could potentially constitute an event or condition which at the time of discovery could have prevented the fulfillment of the safety function of systems required to mitigate the consequences of an accident." Indicated level was restored to 35.4 feet by adding water to the RWST. Licensee is investigating the initial calibration on the level indicator. Licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BRIAN ROKES TO W. GOTT AT 1658 EDT ON 8/5/04 * * * Indian Point Unit 3 is withdrawing the 8-hour non-emergency notification made on August 5, 2004, at 0658 hours (EN Log No. 40925). The notification on August 5, reported an event or condition that could have prevented fulfillment of a safety function [10CFR50.72(b)(3)(v)(D)]. After calibration of the Refueling Water Storage Tank (RWST) level indication (LT-920), on August 4, 2004, the Control Room As-Left level instrument indicated 35.3 feet in the RWST. The Technical Specification (SR 3.5.4.2) required level is 35.4 feet. Alternate level indication including a local level indicator and the absence of a low RWST level alarm provided indication of adequate RWST level. The one-hour Allowed Outage Time (AOT) of TS 3.5.4.C was entered at 2324 hours, on August 4, 2004. Water was added to the RWST and indicated RWST level in the Control Room was restored to 35.4 feet at 0013 hours, on August 5, 2004, and the TS AOT exited. Subsequently, a calibration check of the level instrument was performed on August 5, 2004, and the instrument failed the calibration. The instrument was declared inoperable and the 7-day AOT of TS 3.5.4.13 was entered at 1231 hours. The notification is being retracted based on the engineering conclusion that the out of spec level indication was due to a failed level instrument. The RWST level was within spec as indicated by alternate level Indication including a local level indicator and absence of a low level alarm. These alternate level indication instruments are operable and within calibration. Therefore, Operations concluded the condition did not represent a RWST level below minimum TS level and the safety function of systems required to mitigate the consequences of an accident was met. Notified R1DO (Shanbaky) and NRR (Imbro). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-08-05
40924 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-08-04 08:38 | 2004-08-04 16:57 | 2004-08-04 | FITNESS FOR DUTY A licensed employee was determined to be under the influence of alcohol during a for cause test. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 26.73 |  |  |  | 0 | 2004-08-04
40923 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-04-03 12:00 | 2004-08-04 16:48 | 2004-08-04 | TEXAS AGREEMENT STATE REPORT ON STOLEN MOISTURE DENSITY GUAGE "The Radiation Safety Officer (R.S.O.), was returning to his office in a company pick-up truck Ford F250, without company markings, when he stopped at a McCoy's hardware store for a can of spray paint. He had a nuclear gauge, Troxler Model 3411B, Serial No. 10000, with two sealed radioactive sources: Cs137, Serial No. 40-7475, 8 millicuries; and Am-241/Be, Serial No. 46-1383, 40 millicuries, chained in the rear of the truck. When he returned to the truck he noticed that the gauge and case were missing from the truck bed. He states that the gauge, case and chain and lock are all missing. He reported the incident to the Hays County Sheriff's Department. A police report has been filed. A report was submitted to this Agency [Texas Department of Health] after normal duty hours by facsimile. A call to the Agency on August 4, 2004, confirmed receipt of the facsimile and reported the serial numbers of the radioactive sources. "Event Location: Hardware store between Dripping Springs and Oak Hill (Austin) TX." Texas Incident No. I-8147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-08-09
40922 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-08-04 07:15 | 2004-08-04 15:18 | 2004-08-04 | LOSS OF EMERGENCY NOTIFICATION DUE TO INOPERABLE SIRENS "At 0715 on August 4, 2004, Exelon was notified by Fulton Contracting that Braidwood Station had >[greater than] 25% of its emergency notification sirens inoperable. The cause of the inoperability [at 0626] for the sirens was due to a loss of power due to severe weather. As of 0708 on August 4, 2004, the number of inoperable sirens was less than 25%. Due to a major loss of emergency preparedness capabilities, this event is reportable per 10 CFR 50.72(b)(3)(xiii)." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-08-04
40921 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2004-08-04 10:24 | 2004-08-04 11:14 | 2004-08-04 | UNEXPECTED REACTOR TRIP DURING MAINTENANCE ACTIVITIES At 1024 EDT a reactor trip occurred during maintenance activities involving the control rod drive trip breakers. All control rods fully inserted. The unit is currently stable with decay heat removal via the main steam system through the turbine bypass valves to the main condenser. Post trip response was normal with the following exceptions noted: 1. #4 main turbine stop valve may not have fully closed. 2. A #2 Steam Generator Safety Valve may be lifting early (lifted at 1010 psi rather than the 1050 psi setpoint). 3. Turbine Bypass valve SP13A3 stuck slightly open - isolated. All offsite power lines have been verified operable and both EDGs are available in standby, if needed. The licensee informed the local sheriff's department as required whenever a Steam Generator Safety valve lifts and the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-08-04
40920 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-08-03 10:46 | 2004-08-04 04:14 | 2004-09-16 | HIGH PRESSURE CORE SPRAY RENDERED INOPERABLE DUE TO FAULTY TEST EQUIPMENT "Maintenance technicians were performing surveillance testing on the Division 3 Battery. The as-found bus voltage was approximately 139 VDC and the technicians adjusted the battery charger output voltage to 134 VDC. "At 1046, the control room received an alarm with bus voltage at 125 VDC. The High Pressure Core Spray System was declared inoperable per Technical Specification 3.8.4 with Division 3 DC Bus voltage < 130 VDC. "The maintenance technicians determined that the voltmeter used to measure the voltage was defective and actual bus voltage was adjusted to 125 VDC. "At 1105, Division 3 bus voltage was restored above 130 VDC (136 VDC) and the High Pressure Core Spray System was declared operable. The High Pressure Core Spray System was inoperable for approximately 19 minutes from when the alarm was received until the maintenance technicians restored voltage to 136 VDC. The High Pressure Core Spray System is a single train system." The licensee informed the NRC Resident Inspector. * * * UPDATE 1050 EDT ON 9/16/04 FROM PATRICK WALSH TO S. SANDIN * * * "This Notification is to retract EN# 40920, Unplanned High Pressure Core Spray (HPCS) inoperability. "On 8/4/04 at 0414 Nine Mile Point Unit 2 notified the NRC under 10CFR50.72(b)(3)(v)(D) of the inoperability of a single train safety system (HPCS) due to low battery voltage caused by use of defective test equipment. "Engineering performed an analysis of this event and concluded that the HPCS system was operable during the event and would have performed its required function. "Since, the battery charger was connected to the panel and maintaining bus voltage at or above 125 VDC, it was capable of supplying the steady state dc loads connected to the panel. Also, the battery charger was capable of maintaining the battery in a fully charged condition for the duration of the degraded condition. "Based on the above, it is concluded that the CSH system was operable during this event and the div. 3 battery was capable of performing its intended design functions if required." The licensee informed the NRC Resident Inspector. Notified R1DO (Doerflein). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-08-04
40919 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-08-03 19:30 | 2004-08-03 22:19 | 2004-08-03 | PLANT SHUTDOWN INITIATED DUE TO INOPERABLE EMERGENCY UPS INVERTER "Division 2 Emergency Uninterruptible Power Supply [UPS] Inverter is inoperable. The 24-hour completion time, for Technical Specification 3.8.7.A, has expired and Technical Specification 3.8.7.B was entered. Technical Specification 3.8.7.B requires the plant to be in Hot Shutdown by 0503 on August 4, 2004 and Cold Shutdown by 0503 on August 5, 2004. "A plant shutdown was initiated at 1930." The licensee has notified the NRC Resident Inspector. | 0 | 50 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-08-03
40918 | 0 | HIGH MOUNTAIN INSPECTION SERVICES |  |  |  |  | 2004-08-03 | 2004-08-03 18:02 | 2004-08-03 | POTENTIAL PERSONNEL OVEREXPOSURE Dr. Roy Parker, a consultant for High Mountain Inspections (a radiographer) in Casper, WY reported that Landauer, their film badge processor, informed the licensee that an employee's June badge had a deep dose reading of 121,662 milliRem when read. Landauer also stated that the badge reading was repeated with the same results. The badge was imaged to determine whether the dose was static or dynamic but the results were inconclusive. Dr. Parker also reported that 1) the employee does not exhibit any symptoms of overexposure, 2) the employee is a manager and was in the field for only 3 days in June and was not present during any abnormal occurrences, and 3) co-workers that were in the field with the employee did not have any abnormal results when their badges were processed. As a precaution, the employee will undergo appropriate blood tests to confirm/deny the reading results. Dr. Parker notified R4 Materials (Cain). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 25 REM | [9 empty] | NON EMERGENCY | 4 | WY | MAT |  | 20.2202(a)(1) |  |  |  | 0 | 2004-08-03
40917 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-07-29 | 2004-08-03 14:19 | 2004-08-03 | COLORADO AGREEMENT STATE NOTIFICATION OF URANIUM OXIDE FOUND IN PRIVATE RESIDENCE "The Colorado Agreement State program was notified by a private resident who was cleaning out his late father's basement of the existence of an unknown yellow solid material that he believed was yellowcake. Staff members of Colorado Department of Public Health and Environment have confirmed that the material is 19 lbs of uranium oxide (yellowcake) in a private residence. The deceased owner of the home worked in the uranium industry many years ago. The material is containerized and the State is assisting the widow to make arrangements for sending it to a uranium mill." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-08-06
40916 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2004-08-03 11:30 | 2004-08-03 12:28 | 2004-08-03 | NOTIFICATION MADE DUE TO PATH OF HURRICANE ALEX Hurricane "Alex" is within 500 nautical miles from Indian Point Energy Center (IPEC) with wind speed in excess of 87 knots. The licensee is tracking the hurricane and entered procedure OAP-008. The one hour non-emergency notifications was made per Technical Results Manual (TRM). The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2004-08-03
40915 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-08-02 15:58 | 2004-08-03 01:41 | 2004-08-03 | FUEL LEAK- OFFSITE NOTIFICATION TO NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION. "Salem Unit 1 experienced an underground fuel leak that required notification to the state of N.J. (NJDEP). Fuel oil was observed in a storm drain, there was not a release to the Delaware river and the storm drain system has been isolated and pumped out. The source of the leak is under investigation. There were no injuries as a result of the spill and no equipment has been declared inoperable. The bulk fuel oil storage tank has been isolated as a potential leak source." Lower Alloways Creek Township will be notified. The Bulk fuel oil storage tank makes up to Salem Unit 1 & 2 diesel storage tanks which are at full capacity. Licensee is making a contingency plan that they will not be able to use the bulk fuel oil tank and they plan to have fuel oil tank trucks come onsite Tuesday. The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-08-03
40914 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2004-07-30 21:20 | 2004-07-31 11:49 | 2004-07-31 | SUSPECTED DRUG PARAPHERNALIA FOUND IN THE PROTECTED AREA The following information was provided by the licensee via facsimile: "Drug paraphernalia [a baggie and rolling paper] was found by the turbine building operator in a trash container located on the turbine building mezzanine level. The turbine building operator was emptying the container at the time. The paraphernalia was turned over to the security shift supervisor. Security is confident, based on a veteran law enforcement officer's experience, that the empty bag found in the trash once contained an illegal substance. Further confirmation by testing will be determined on Monday. Our procedure SO-R-1 requires FCS [Fort Calhoun Station] to make a 24-hour report to the NRC per 10CFR26.73." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 7/31/04 AT 1317 HRS EDT FROM HODGSON TO CROUCH * * * "The Security Shift Supervisor was notified by the Washington County Sheriff Department that the bag with the unknown substance has been tested positive for marijuana." The licensee has notified the NRC Resident Inspector. NRC Operations Officer notified R4DO (Bywater). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2004-07-31
40913 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2004-07-30 18:45 | 2004-07-31 03:20 | 2004-07-31 | AIR VOID IN POST-LOCA RECIRCULATION PIPING SYSTEM "On July 30, 2004, at approximately 18:45 Mountain Standard Time (MST), Palo Verde Nuclear Generating Station Units 1, 2, and 3 were operating at approximately 100% power at normal operating temperature and pressure when it was discovered that a void in the post-LOCA (Loss Of Coolant Accident) recirculation piping from the containment sump may have prevented fulfillment of the safety function to remove residual heat and mitigate the consequences of a Loss of Coolant Accident. The volume of the ECCS (Emergency Core Cooling System) piping sections between the closed containment sump isolation butterfly MOVs (SIAUV0673/0674 and SIBUV0675/0676) and the associated train sump recirculation check valves (SIAV205 and SIBV206) are void of water and occupied with air (Approx. 120 cubic feet). The concern is that during a Recirculation Actuation Signal (RAS) the trapped volume of air between the isolation valves and the downstream check valve cold potentially enter the operating SI pumps (HPSI and CS), which could potentially cause cavitations and/or air binding of the pumps or possibly a water hammer event. "RAS does not occur for approximately 20 minutes, or longer following a LOCA. In accordance with Generic Letter 91-18, substitution of manual action for automatic action to open the inner containment sump isolation valves following a LOCA, but prior to the RAS setpoint will allow the void to clear, with the exception of a small section between the outer containment isolation valve and the check valve. Engineering had provided reasonable assurance that the recirculation check valve void will not result in an unacceptable void fraction forming in the HPSI/Containment Spray pump suction piping and pump. "The Control Room Operators have been briefed on the need to perform the manual Operator action to open the inboard ECCS Sump isolation valves (SIAUV673 and SIBUV675) upon receipt of a Containment Spray Actuation System (CSAS) actuation. Each Shift Crew will be briefed accordingly until the EOPs are revised to incorporate this action (will take about 24 hours to be incorporated). "Engineering continues to evaluate this condition. "There were no RPS/ESF actuations, and none were required. "There were no structures, systems or components that were inoperable at the start of (the) event that contributed to the event. "This condition did not result in any challenges to the fission product barrier or result in any releases of radioactive materials. There were no adverse safety consequences or implications as a result of this event. This condition did not adversely affect the safe operation of the plant or health and safety of the public." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-07-31
40912 | 0 | QUAD CITIES | 1 |  |  | [1] GE-3,[2] GE-3 | 2004-07-30 21:25 | 2004-07-31 01:28 | 2004-07-31 | LPCI LOOP SELECT LOGIC FOUND DEGRADED DUE TO PRESSURE INSTRUMENTS OUT-OF-TOLERANCE "On July 30, 2004 at approximately 2125 hours CDT, Instrument Maintenance personnel were performing the Unit One Reactor Low Pressure (RHR/LPCI) Calibration and Functional Test. At this time, the technicians determined that two out of the four "Reactor Steam Dome Pressure - Low" switches in LPCI loop select logic were out of tolerance high. These switches delay completion of the LPCI loop select logic during Single Loop Reactor Recirculation Pump operations (SLO) until the reactor pressure is less than 900 psig. With these switches out of tolerance high, LPCI loop select logic sensitivity was degraded, increasing the potential to select the wrong loop for injection during periods of SLO. At the time of discovery, both Reactor Recirculation pumps were in operation. "Both switches were recalibrated immediately upon discovery to within Technical Specification tolerances." The NRC Resident Inspector was notified of this event by the licensee. | 85 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-07-31
40911 | -1 | U.S. DEPARTMENT OF ENERGY |  |  |  |  | 2004-07-30 | 2004-07-30 12:39 | 2005-07-01 | PART 21 SAFETY HAZARD WITH RADECO PORTABLE AIR SAMPLER MODEL H-809VI The U.S. Department of Energy, Office of River Protection in Richland, WA has identified a potential safety issue with Radeco portable air sampler model H-809VI. This type of portable air sampler is utilized in the commercial nuclear industry. A Health Physics Technician experience a mild shock while handling a Radeco portable air sampler when the sample holder was touched. Radeco has issued a recommendation or opinion for H-809V series electrical grounding. Facilities should check sample holders on the Radeco H-809 and H-810 series samplers to assure proper grounding and no voltage on the sample holder. ** RETRACTION OF PART 21 FROM TANK FARMS (T.SMITH) TO J. KNOKE ON 07/01/05 *** "The Department of Energy (DOE), Office of River Protection (ORP) in Richland, Washington requests closure of the referenced submitted courtesy notification of a potential safety issue with RADeCO, portable air sampler, model H-809VI to the Nuclear Regulatory Commission. ORP's basis for closure of the submitted courtesy notification is as follows: "The Underwriters Laboratory (UL) concluded the RADeCO Portable Air Sampler Model H-809VI, serial Number 8499, instrument DOES NOT present a generic safety problem. The report is available by request only. "The RADeCO Portable Air Sampler instrument passed all of the UL tests. "ORP concludes the matter does not represent a reportable concern covered by 10 CFR Part 21 requirements because loss of a single air monitor because of this issue would not increase risk to public health and safety when other instruments are in place to detect atmospheric radioactivity." Notifications were provided to R1DO(White), R2DO( Bonser), R3DO(Cameron), R4DO(Clark), NMSS (Holonich), and NRR (Carpenter). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2004-07-30
40910 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-07-30 10:00 | 2004-07-30 13:58 | 2004-08-03 | ALERT DECLARED AT COLUMBIA GENERATING STATION The following information was obtained by the licensee via facsimile: "Reactor SCRAM received at 0924 [hrs] PDT. Initial indications are the scram signal was caused by RPS [Reactor Protection System] High Pressure. Following the scram, 2 [two] control rods did not immediately indicate [fully inserted]. Control room staff entered [procedure] PPM5.1.2 and took the required actions. All control rods subsequently indicated [fully inserted]. "An ALERT Classification was declared at 1000 [hrs] based on PPM 13.1.1 Criteria 2.2.A.1, 'RPS Setpoint exceeded and automatic actions failed to result in a rod pattern which alone assures reactor shutdown'. Manual actions resulted in all rods [fully inserted] and reactor power [less than or equal to] 5 percent. "All other plant systems responded as expected with the exception of a wetwell-to-drywell vacuum breaker which indicates open. Investigation into the cause of the scram and actual control rod position is ongoing. Further details will be provided when available." The licensee also reports that no relief valves lifted during the transient. Decay heat removal is via the main condenser. Reactor level is steady at 36 inches. Reactor temperature and pressure are 507 degrees and 710 psig respectively. Offsite power is available. All emergency systems are available in standby. The licensee has notified the NRC Resident Inspector of the incidents. The NRC entered Monitoring mode at 1327 hrs EDT with Region IV leading. The NRC exited Monitoring at 1530 hrs. EDT and returned to Normal mode. Notified HHS (Ayles) as well as others noted in notification block. * * * UPDATE AT 2130 HRS EDT ON 7/30/04 FROM COLEMAN TO CROUCH * * * "At 1358 [hrs.] EDT on 7/30/04, NRC was notified of an Alert at Columbia Generating Station (EN #40910). "This is a follow-up to inform NRC that the event was terminated at 1457 [hrs] (EDT) (1157 PDT). All control rods are inserted. Reactor is shutdown and water level is normal. All required emergency systems are operable. All offsite and onsite power sources are operable. Reactor pressure is normal." The licensee has notified the NRC Resident Inspector, State of Washington and local authorities of the termination. The NRC Operations Center notified R4DO(Bywater), DHS, FEMA, DOE(NRC), USDA, EPA and CDC(HHS). * * * UPDATE AT 1930 EDT ON 08/03/04 FROM M. HEDGES TO A. COSTA * * * "At 1358 EDT on July 30, 2004, NRC was notified of an Alert at Columbia Generating Station (EN #40910). A subsequent notification was made to inform the NRC that the event was terminated at 1157 PDT (1457 EDT) on July 30, 2004. "This is a follow-up to inform the NRC that Columbia Generating Station is retracting its Alert Emergency Declaration due to the following reason. Following the RPS actuation, control rod position indication for two control rods was indeterminate for approximately two minutes to the control room staff. A subsequent review of control rod position indication from the Plant Data Information System (PDIS), Rod Worth Minimizer (RWM) logs, and Auto Scram Timer (AST) data by Columbia Generating Station personnel shows that all rods were successfully inserted to the 'Full-in' position following the initial RPS actuation, assuring that the reactor was shutdown under all conditions. The Emergency Action Level for this Alert classification requires that the following three conditions be met: Any RPS set point (including manual) has been exceeded per T.S. 3.3.1.1 AND RPS actuation failed to result in a control rod pattern which alone always assures reactor shutdown under all conditions AND Manual actions (mode switch in shutdown, manual push buttons, and ARI) result in reactor power LE 5%. "Since all rods were successfully inserted without the assistance of any manual actions and within the Technical Specification required time, Columbia Generating Station staff now believes that no emergency classification should have been made, and we are retracting the Alert emergency classification from this event notification. The problem with control rod position indication following the scram is being addressed through our corrective action program." The licensee notified the NRC Resident Inspector and will notify local, State, and other Government Agencies of this update. Notified R4 DO (Runyan). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | ALERT | 4 | WA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) |  |  | 0 | 2004-07-30
40909 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2004-07-30 09:45 | 2004-07-30 12:51 | 2004-07-30 | REACTOR CORE ISOLATION COOLING (RCIC) TURBINE FAILED TO ACHIEVE DESIGN PRESSURE AND FLOW DURING SURVEILLANCE TESTING The following information was obtained from the licensee via facsimile: "During a surveillance of the Reactor Core Isolation Cooling system (RCIC), the RCIC turbine failed to achieve design pressure and flow. Other safety systems, including the High Pressure Coolant Injection (HPCI) system, are available. "This failure is believed to be due to a RCIC flow controller problem. Investigation is continuing." Design pressure/flow is 1250 psig/400 gpm. Actual pressure/flow was 1220 psig/350 gpm. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-07-30
40908 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-07-29 12:10 | 2004-07-29 15:46 | 2004-08-27 | OFFSITE NOTIFICATION DUE TO RAW SEWAGE DISCHARGE TO LAKE ONTARIO A report was received in the Unit 2 Control Room by Site personnel that raw sewage appeared to be seeping from a manhole inside the protected area. The Fire Department and Environmental Department were dispatched to the area. It was reported back to the Unit 2 Control Room that raw sewage was seeping from the manhole and filling nearby ditch and flowing to a storm sewer. Due to the leakage, Nine Mile Point entered their HAZMAT response procedure. Initial investigation for the sewage release found the sewage lift station pumps' control switch in the "OFF" position preventing the pumps from operating. The lift station pumps were restarted and the discharge from the manhole stopped. Lift station pumps continue to function properly and cleanup efforts are underway. Investigation is underway on why the lift station pump control switches were in the off position. Based upon initial calculations, it was determined approximately 3000 gallons of raw sewage was released from manhole to a nearby storm sewer which discharges to Lake Ontario. Nine Mile Point has notified the Oswego County Department of Health and New York State Department of Environmental Conservation. No hazards exist to offsite personnel and no wildlife has been adversely affected. The Licensee notified the NRC Resident Inspector, Local and State agencies. * * * UPDATE AT 1700 EDT ON 8/27/04 FROM CHRIS SKINNER TO S. SANDIN * * * The licensee is retracting this report based on the following: "Subsequent investigation has determined that approximately 400 gallons of raw sewage was released into the storm drainage ditch. There was no active flow in the storm drainage ditch at the time of the event. Samples indicate that the raw sewage did not reach the lake. The event was reclassified as a State Pollutant Discharge Elimination System Permit Upset with minor impact to the environment. Therefore, the event notification from July 29, 2004 is retracted." The licensee informed the NRC Resident Inspector. Notified R1DO (Cobey). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-07-29
40906 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2004-07-29 11:03 | 2004-07-29 12:51 | 2004-07-29 | INDUSTRIAL ACCIDENT ON THE OWNER CONTROLLED AREA The following information was received from the licensee via facsimile: "(Time 1103 hrs.[EDT]) A lawn mowing company was working outside the protected area when a mower rolled over on the individual doing the mowing. The mowing evolution was near a pond. The mower went over the edge of the pond, landing in the water. The individual operating the mower was trapped under the mower in the water. Several employees from the Davis Besse training center saw the mower in the water and pulled the individual from the water. The victim was not breathing at that time. "CPR was performed and Life Flight called. Helicopter on site at 1123 [hrs.] and transported victim to St. Vincent Hospital. Helicopter lifted off from the site at 1138 [hrs.]. The victim was breathing on her own at that time but still unconscious." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-07-29
40905 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-07-29 09:42 | 2004-07-29 12:14 | 2004-07-29 | PLANT ENTERED LCO ACTION STATEMENT DUE TO MALFUNCTION OF A SUPPRESSION CHAMBER-TO-DRYWELL VACUUM BREAKER. On July 29, 2004, at approximately 0351 hours, testing of Suppression Chamber-to-Drywell vacuum breakers commenced in accordance with Periodic Test 0PT02.3.1, "Suppression Chamber-to-Drywell Vacuum Breaker Operability Test." At 0357 hours, it was determined that vacuum breaker 2-CAC-X18D had an open indication. Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.1.6, "Suppression Chamber-to-Drywell Vacuum Breakers," Condition B was entered for one suppression chamber-to-drywell vacuum breaker (2-CAC-X18D) not indicating closed. Required Action B.1 of TS LCO 3.6.1.6 provides 4 hours to verify the vacuum breaker closed. Attempts to confirm the vacuum breaker closed were unsuccessful and at 0757 hours, TS LCO 3.6.1.6 Condition C was entered. Required Action C.1 is to be in Mode 3 (Hot Shutdown) in 12 hours and Required Action C.2 is to be in Mode 4 (Cold Shutdown) in 36 hours. Initiation of the plant shutdown required by TS LCO 3.6.1.6 commenced at 0942 hours. This condition is being reported in accordance with 10 CFR 50.72(b)(2)(i) as the initiation of any nuclear plant shutdown required by the plant's TS. INITIAL SAFETY SIGNIFICANCE EVALUATION The initial safety significance of this condition is considered to be minimal. The actual position of the vacuum breaker cannot be confirmed, however if one vacuum breaker was not closed, communication between the drywell and suppression chamber air space could occur, and as a result, there is a potential, for primary containment overpressurization due to this bypass leakage if a loss of coolant accident were to occur. The plant is currently proceeding to hot shutdown with all Emergency Core Cooling systems operable. CORRECTIVE ACTIONS Determine the required corrective actions after entry into the drywell following shutdown. The safety significance of the event will be reviewed when the actual condition of the vacuum breaker is known. The NRC Resident Inspector has been notified. * * * UPDATE ON 07/29/04 @ 1654 FROM KEN CHISM TO CHAUNCEY GOULD * * * On July 29, 2004, at 1517 hours, a manual scram was inserted to shut down the Unit 2 reactor from approximately 23 percent of rated thermal power. The reactor shutdown was implemented to meet the requirements of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.6 Required Action C.1 to be in Mode 3 in 12 hours. All control rods fully inserted into the core and no ECCS actuation occurred or relief valves lifted. Following the scram, an expected reactor vessel coolant level shrink occurred causing coolant level to decrease below the Low Level 1 setpoint. This coolant level decrease resulted in a Primary Containment Isolation Valve isolation signal to Group 2 (Drywell Equipment and Floor Drain, Traversing In-core Probe, Residual Heat Removal (RHR) Discharge to Radwaste, and RHR Process Sample), Group 6 (Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling System), and Group 8 (RHR Shutdown Cooling Suction and RHR Inboard Injection) isolation valves. The isolation signal closed all of the valves that were open at the time of the expected initiation. The plant is currently in mode 3 and proceeding with a normal cooldown to Mode 4. The NRC Resident Inspection was informed. Notified Reg 2 RDO (Tom Decker). | 0 | 46 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-07-29
40904 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-07-28 21:00 | 2004-07-29 02:15 | 2004-09-21 | UNIDENTIFIED REACTOR COOLANT SYSTEM (RCS) LEAK "This is an 8-hour notification being made to report exceeding the design basis for the reactor coolant leakage outside of containment. An unidentified reactor coolant system (RCS) leak of 1.0 gpm on Salem Unit 1 occurred on 7/28/04 at 2100 hours. It was discovered (that) a pressure instrument weld from 13 charging pump [PDP] discharge piping failed in the auxiliary building. Tech Specs for RCS unidentified leakage was entered. Station abnormal operating procedures (ABRC-001 RCS Leak) were entered and leakage monitoring program referenced. The leak was isolated closing the root valve of the instrument line (discharge pressure transmitter) by 2135 hours. The RCS leakage was outside of containment and was greater than design of 3840 cc/hr. This leakage would have exceeded the GDC-19 limits for control room habitability during the time of the leak initiation and leak isolation. 13 charging pump remained in service and the leak is locally isolated. The tech spec for RCS unidentified leakage was exited and ASME tech spec for the failed weld was entered. There were no unusual or unexpected responses. All systems functioned as required. There were no personnel injuries." A maintenance tech in the auxiliary building notified control room of a leak about the same time that control room personnel noticed that the Volume Control Tank level was decreasing approx. 0.3gpm. The area around the Positive Displacement Pump (PDP) was roped off and the leak was isolated. Airborne levels in the roped off area was 8000 cpm (from 2130 to 2200 hours). Nobody was evacuated from auxiliary building. At 0040 hours airborne samples were within normal limits. The area around # 13 PDP is still roped off until the surface contamination is cleaned up. Lower Alloways Creek Township will be notified of this by the licensee. The NRC Resident Inspector will be notified of this event by the licensee. * * * RETRACTION FROM SAUER TO CROUCH AT 1543 HRS. EDT ON 9/21/04 * * * The following retraction was obtained from the licensee via e-mail: "On July 28, 2004, it was discovered that a pressure instrument weld from 13 charging pump developed a leak into the auxiliary building. An 8-hour call to the NRC was made for exceeding the ECCS leakage outside containment (Event Number 40904). "The leak was self-revealing, in that the area radiation detectors as well as the fire protection sensors detected it. The leak was identified and isolated by closing the manual root valve for the instrument line in approximately 35 minutes from discovery. "Section 5 of Appendix A of Regulatory Guide 1.183 states that engineered safeguards feature (ESF) systems that recirculate sump water outside of the primary containment are assumed to leak during their intended operation. The guidance indicates that this release source includes leakage through valve packing glands, pump shaft seals, flanged connections, and other similar components. The guidance further indicates that this release source may also include leakage through valves isolating interfacing systems. The leak that was identified and isolated shortly after discovery was a piping system failure and not the type of leakage that is considered to be a release source for which the radiological consequences should be analyzed. Therefore, further review of the event indicated that identified leak did not challenge the limits of 10CFR100 for offsite releases and 10CFR50 Appendix A General Design Criterion 19 (GDC-19), thus event report 40904 is withdrawn." The licensee has notified the NRC Resident Inspector of the retraction. The Headquarters Operations Officer notified R1DO (Caruso). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2004-07-29
40903 | 0 | MADIGAN ARMY MEDICAL CENTER |  |  |  |  | 2004-07-08 | 2004-07-28 13:20 | 2004-07-28 | MEDICAL EVENT INVOLVING UNINTENDED DOSE TO EMBRYO/FETUS A female patient undergoing treatment for Graves disease received 26.6 millicuries I-131. The patient received counseling and a pregnancy test on 7/8/04 (negative results) prior to treatment. Subsequent to treatment the Hospital was informed by her husband that a home pregnancy test showed positive. The Hospital contacted the patient and scheduled a second pregnancy test on 7/23/04. The test results confirmed the pregnancy on 7/24/04. The prescribing physician has been informed. The preliminary assessment performed by the Hospital concluded that this medical event would most likely result in either a spontaneous abortion or have no impact on fetus development, i.e., at this stage in the pregnancy (zygote) the thyroid has not developed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 4 | WA | HOS |  | 35.3047(a) |  |  |  | 0 | 2004-07-28
40902 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-07-28 08:00 | 2004-07-28 09:52 | 2004-07-28 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "Event: At 08:00 hours Oconee Unit 1 initiated a unit shutdown per Technical Specification (TS) 3.0.3. Unit 2 initiated shutdown at 0900 [ET]. It is expected that Unit 3 will initiate shutdown at 1000 hours. Target for entry into Mode 3 is 1300 hours on all units. At 0129 hours all three Oconee units received a number of alarms related to power to the 230 KV switchyard (SWYD) battery chargers. At 0200 hours Operations determined that both AC power sources to the SWYD battery chargers required by TS 3.8.3 had tripped and declared entry into TS 3.0.3 because no specific condition of TS 3.8.3 applied. Evaluation for potential applicability of other reporting criteria is still in progress. "Initial Safety Significance: The SWYD batteries currently have normal voltage (being monitored hourly) but are NOT considered operable per TS 3.8.5 at this time, which would also require TS 3.0.3 entry. However, if voltage drops too low the ability to remotely operate SWYD power circuit breakers would be affected, which would impact SWYD isolation capability. Local manual operation would still be possible, and operations personnel are stationed in the SWYD as a contingency. "Corrective Action: 1. Maintenance has identified a fault in a power transfer switch. Actions have been completed to isolate the fault and restore power to the battery chargers. 2. Measurements of battery voltages are being taken hourly. A surveillance will be performed to verify TS 3.8.5 compliance after the charger power supply is restored. 3. Shutdown of Oconee units will follow schedule above unless power and battery voltages are restored sooner (as expected)." The electrical grid is stable and standby emergency power remains operable. The NRC Resident Inspector has been informed. The licensee does not intend to make any State, local or other Federal notifications or issue any press release at this time. * * * UPDATE AT 1400 EDT ON 7/28/04 FROM PHIL NORTH TO S. SANDIN * * * At 0945 EDT both SWYD battery chargers were energized to restore battery parameters. At 1205 EDT the affected batteries were declared operable and all three (3) Units exited their respective LCOs. Units 1, 2, and 3 are currently holding at 80%, 84% and 89% power, respectively, and will commence power escalation after review and closeout of their paperwork. Notified R2DO (Decker). | 92 | 95 | 100 | 100 | 100 | 100 | -1 | -1 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-07-28
40901 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-07-27 10:00 | 2004-07-28 08:58 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * [DELETED] FIRE IN OFF-GAS SYSTEM Ignition of off-gas process line during disassembly of processing equipment. A small flame occurred for a period of several minutes inside ventilated containment. The fire was extinguished by Operations personnel. Slight damage occurred to plexiglass surface and prefilter element. Filtration in ventilation system is intact and operational. Radiological hazard involved a quantity of highly enriched Uranium > 0.2 microCuries. There was no loss of containment and no injury to personnel. Health Physics, Fire Safety, and Nuclear Criticality safety personnel responded and performed evaluation to ensure safe shutdown of operation. Repairs are being made to the off-gas [DELETED] involved and recovery is underway. All surveys showed no evidence of occupational exposure, contamination, or environmental release. Investigation is being conducted to determine the cause of the fire and the [DELETED] other off-gas process [DELETED] will be inspected for similar problems. Licensee notified NRC Resident Inspector. Licensee does not intend to make any State, local or other Federal notifications or issue any press release at this time. * * * UPDATE ON 05/11/08 BY J. KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | FIRE/EXPLOSION | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 70.50(b)(4) |  |  |  | 0 | 2008-05-11
40900 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-06-25 | 2004-07-27 14:55 | 2004-08-06 | AGREEMENT STATE REPORT INVOLVING A STOLEN/RECOVERED RADIOGRAPHY CAMERA The following information was provided by the State of Washington to the NRC via email: "This is notification of an event in Washington State as reported to or investigated by the WA Department of Health, Office of Radiation Protection. "STATUS: new "Licensee: Northwest Inspection "City and State: Richland, Washington "License Number: WN-IR065-1 "Type of License: Industrial Radiography "Date of Event: 25 June 2004 (reported July 26) "Location of Event: Spokane, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention): "The licensee's radiation safety officer reported that they had had a radiography vehicle stolen, with a radiography exposure device secured inside (device and source information not yet known). The Radiographer, at the end of the day, had left the radiography vehicle unattended while that Radiographer entered a work-site office to complete paperwork. The Assistant Radiographer had left the work-site earlier when actual radiography had concluded. "During the brief time the vehicle was unattended, reported to be about 2 minutes, the vehicle was taken. The Radiographer called the police and the radiation safety officer when the vehicle was noticed missing. "A short time later, reported to be about 30 minutes, a Spokane area resident noticed the truck, stuck by the side of the road. The resident used licensee identification, from the outside of the vehicle, to contact the licensee. The licensee had the resident call local police. The police secured the vehicle. Later, the licensee recovered the vehicle. The locked camera storage/transportation container had not been disturbed. "No Media attention noted. "Notification Reporting Criteria: 10 CFR, Part 20.2201(a)(1)(ii) "Isotope and Activity involved: Not yet known "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): None, N/A "Lost, Stolen or Damaged? (mfg., model, serial number): Stolen (briefly), camera and source information is not yet known. "Disposition/recovery: Recovered without additional incident. "Leak test? Not yet known "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) "The vehicle is a combination of pick-up truck with industrial trailer. The trailer serves as the darkroom and camera storage. No placards since package was a Yellow II. Type B package inside a convenience over-pack. "Release of activity? None, N/A "Event Report # WA-04-043" * * * UPDATE VIA EMAIL 8/6/04, 1743 EDT SCROGGS TO GOTT * * * "Status: Close (reported as new July 27, 2004) "The licensee has provided the following additional information: The camera, INC Model IR-100 device, Serial Number 4694, DU leak test on 26 January 2004, test was negative. The source, Ir-192 (68 curies on 25 June 04), INC Model 32, Serial Number F959, sealed source leak test 11 May 2004, test was negative." Notified R4DO (Runyan) and NMSS (Holonich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-07-30
40899 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2004-05-30 10:40 | 2004-07-27 14:37 | 2004-07-27 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES DUE TO PARTIAL LOSS OF 120 VAC MODULAR POWER UNIT 2 LOADS "This 60-day optional verbal report, as allowed by 10 CFR 50.73(a)(1), is being made to describe an unplanned, invalid actuation of specified systems, specifically the Primary Containment Isolation System. Since this event meets the definition of an invalid actuation, this notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) in lieu of a Licensee Event Report. "On May 30, 2004, at approximately 10:40 am EDT, while the plant was operating at 100% power, a voltage regulator failed on Division 2 120 VAC Modular Power Unit No. 2 (MPU-2) which resulted in blown fuses and the loss of a number of loads from one of the three MPU-2 distribution cabinets. Since only one of the three distribution cabinets was lost, the isolations that occurred were only a portion of the isolations that would have occurred if all of the MPU-2 loads had been lost. "This caused containment isolations by Division 2 Drywell Pneumatic supply valves (Primary Containment Isolation Group 18) and by Torus Water Management system outboard isolation valves (Primary Containment Isolation Group 12). Division 2 Secondary Containment Isolation Logic was also actuated, and the reactor building ventilation isolated. The Division 2 Standby Gas Treatment System automatically started. All equipment controlled by the affected circuits was determined to have responded to the loss of MPU-2 Cabinet 2 power as expected. "Operators implemented applicable response procedures. The MPU was returned to service, and isolation signals were reset. Reactor power was not affected by this event. "The NRC Resident Inspector was notified of this event by the licensee." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-07-27
40898 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-07-26 | 2004-07-27 12:42 | 2004-07-27 | AGREEMENT STATE REPORT INVOLVING STUCK IRRADIATOR SOURCE Yesterday, July 26, 2004, Colorado State University, a Colorado licensee, notified the Department that a source used in one of their panoramic irradiators became stuck in the exposed position during a routine service check. The University's Radiation Safety Officer locked and posted the irradiator room to prevent further entry. The room was designed for irradiator use, so, there is no potential for exposures to staff or members of the public. The maker of the irradiator, JL Shepherd, was notified, and a plan is being developed to manually move the source to the shielded position. Location: Colorado State University, Fort Collins, Colorado License: Colorado # 002-27 Irradiator: JL Shepherd Model #354 Source: Amersham, Cs-137, 21.7 Ci | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-07-30
40897 | 0 | SAN ONOFRE | 1 |  |  | [1] W-3-LP,[2] CE,[3] CE | 2004-07-24 10:00 | 2004-07-24 18:20 | 2004-07-24 | ADVANCED HORIZONTAL STORAGE MODULE BOLT FAILURE "On July 24, 2004, at about 1000 PDT, SCE [Southern California Edison] personnel were tightening two seismic restraint bolts on Advanced Horizontal Storage Module (AHSM) Number 10 at the Unit 1 ISFSI [Independent Fuel Storage Installation] when one of the bolts failed. SCE had placed the storage canister into AHSM No. 10 on July 18, 2004 and was tightening the restraint as specified in the final safety analysis report, after the module had reached thermal equilibrium. "SCE plans to replace the failed bolt with another bolt manufactured under the same Certificate of Compliance and will tighten the seismic restraints within the period allowed by the FSAR (one week from initial placement of the storage canister). SCE's evaluation of the failed bolt is ongoing. "SCE has notified the NRC resident inspectors about this occurrence and will provide them with a copy of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SPENT FUEL, HLW, RX GTCC DEFECT |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 72.75(c )(1) |  |  |  | 0 | 2004-07-24
40896 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2004-07-23 11:00 | 2004-07-23 17:46 | 2004-07-23 | WASHINGTON - AGREEMENT STATE NOTIFICATION OF LEAKING SOURCE "The Licensee's Radiation Safety Officer reported at about 11 AM on July 23, 2004, that they had discovered a leaking Cobalt 57 source. The source was new. It had been taken from storage and placed into the work area for leak test prior to being placed into an XRF device. The leak test initially read 11,000 counts per minute (cpm). The source was cleaned to 416 cpm and replaced into a second shielded storage container and then sealed. The original container was wiped and found to be clean. The source work area had minor amounts of contamination and was decontaminated by the licensee. The source storage locker had not been contaminated. "This source was part of a 13 source lot received May 18, 2004, from Isotope Products Laboratories. Upon arrival, all 13 sources passed a leak test. This source was the last of the 13 to be readied for use. The previous 12 sources also passed a leak test prior to being placed into their respective XRF devices. The licensee contacted the manufacturer to report the event. The licensee is waiting the manufacturer suggested course of action regarding disposal. Presently, there has been no media attention. "Isotope and Activity involved: Cobalt 57, 12.52 millicuries (as of May 2004). "XRF source, Model PHI-0106, S/N B7-461. "WA Event Report # WA-04-042." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-07-28
40895 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-05-26 16:22 | 2004-07-23 11:10 | 2004-07-23 | 60 DAY INVALID AUTOMATIC ACTUATION REPORT: CONTAINMENT ISOALTION VALVES IN MORE THAN ONE SYSTEM "On May 26, 2004 at 16:22 hours and inadvertent primary containment isolation signal was initiated following restoration from a surveillance test on the 2A Reactor Enclosure ventilation exhaust duct radiation monitor. The isolation was due to a fuse failure that caused isolation signals on Group 6A, 6B, 6C, and 7A primary containment isolation valves (PCIVs). The Unit 2 reactor enclosure ventilation isolated. The 2A standby gas treatment system (SGTS) and 2A reactor enclosure recirculation system (RERS) trains initiated. The instrument gas compressor suction valve and the 2A instrument gas header supply valve closed. The containment nitrogen inerting valve and the 2A instrument gas header supply valve closed. The containment nitrogen inerting block valve closed. The containment atmospheric sample valves received an isolation signal but were in a closed position prior to the event. All system functioned as designed during the event. "The laboratory analysis of the fuse determined that the most probable cause of the event was an age related degradation of the fuse that reduced its current carrying capacity. The fuse was operating under steady state conditions for approximately 30 seconds prior to the failure. A fuse replacement plan was in progress prior to the event due to prior age related failures of this type of fuse. The fuse replacement plan will be evaluated to ensure the current schedule is adequate. "Component data: Type: Fuse Manufacturer: Bussmann Model number: MIN-5" The NRC Resident Inspector was notified of this event by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-07-23
40894 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2004-07-22 07:00 | 2004-07-22 14:32 | 2004-07-22 | NEBRASKA AGREEMENT STATE REPORT ON STOLEN TROXLER GAUGE "The State of Nebraska - Department of Roads, reported that a Troxler Model 3400 Series, Serial No. 28779 portable gauge containing 9 millicuries of Cesium-137 and 44 millicuries of Americium-241:Beryllium was stolen from the licensee's vehicle parked at the licensee's facility. The gauge was in its original carrying case. At this time, it has not been confirmed if the gauge or the carrying case was locked at the time of the event. The gauge and its carrying case were removed from the licensee's pickup bed. The pickup bed did have a locked solid bed cover, and it appeared that the bed cover was pried open to gain access to and remove the gauge carrying case. The licensee also reported the stolen gauge to the Nebraska State Patrol (NSP) this morning between 07:00-07:30. The NSP is investigating the event. Follow-up information will be provided to NRC on the recovery of the stolen gauge and entered into NMED." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2004-07-27
40893 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2004-07-22 09:42 | 2004-07-22 13:52 | 2004-07-22 | GAP DISCOVERED IN CONTROL ROOM ENVELOPE "During Control Room Boundary investigations a gap in the control room envelope was discovered that exceeded the assumptions of the plant toxic gas analysis. The assumptions for the control room radiological analysis were met with the consideration for the use of Kl. The gap size was determined to be approximately 103 square inches versus an analysis assumption of 58.9 square inches. The gaps were immediately repaired." The licensee suspects that the gap has existed for 20 or more years and was discovered during a control room heating, ventilation, air-conditioning (HVAC) upgrade. The license has notified the NRC Resident Inspector of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-07-22
40892 | 0 | DANVILLE REGIONAL MEDICAL CENTER |  |  |  |  | 2004-07-15 14:00 | 2004-07-22 13:30 | 2004-07-22 | LESS THAN PRESCRIBED DOSAGE TO ORGAN A patient was prescribed placement of 74 seeds of Iodine 125 to the prostate. Only 38% of the volume of the prostate received the prescribed dose of 160 grays. The radiation oncologist used poor technique in placing the iodine seeds in the prostate. There were no other safety issues related to this incident. The patient has been contacted and will come in for consultation. The licensee will review this incident and will follow up with a written report, if required. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-07-22
40891 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-07-22 07:10 | 2004-07-22 13:15 | 2004-07-22 | LOSS OF POWER TO PRIMARY AND BACKUP OFFSITE SIREN SYSTEM "At 0710 hrs on 7/22/04 it was discovered by the Salem County 911 Center dispatcher that the primary and backup Alert Notification System (offsite siren system) activation controllers (computers) had lost power. The Salem County Siren computers are the activation controllers for all 34 offsite sirens located in the New Jersey portion of tile 10-mile EPZ. The 37 Delaware Sirens wore not affected. As per instructions, siren technicians were notified at 0748 hours and responded to the 911 Center at 0815 hours. Power was restored to the primary computer at 0835 hours. Subsequent investigation and troubleshooting has determined the following: "Exact time of power loss is unknown. Last know/verified computer availability was at 1104 on 7/21/04 when a biweekly siren test was successfully completed. An automatic siren poll scheduled for 0645 on 7/22 did not occur which indicates that the loss of power occurred sometime between 1104 on 7/21 and 0645 on 7/22/04. "Cause of loss of power was determined to be a failed UPS unit that both the primary and backup siren computers were powered from. The failed UPS was removed and primary computer re-powered directly from 911-center normal 120-volt house power. A siren poll was done and. The siren system was declared back in service at 0835 hours on 7/22/04. "Two separate UPS units will be connected to the Siren activation computers by the end of day today, 7/22/04." The licensee notified State of New Jersey and the NRC Resident Inspector. | 100 | 23 | 0 | 100 | 23 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-22
40890 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-07-21 20:20 | 2004-07-22 00:57 | 2004-07-22 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN: NON-VITAL COMPONENT COOLING WATER LEAK INSIDE CONTAINMENT "On July 21, 2004, with Unit 1 operating in Mode 1 (Power Operation) at approximately 100 percent power, a non-vital component cooling water (CCW) leak was identified inside containment. It was conservatively concluded that the leak could potentially disable both vital CCW loops, and thus the LCO for Technical Specification (TS) 3.7.7 "Vital CCW System" would not be met. Given there is no associated action for both vital loops inoperable, operators entered TS 3.0.3 at 1900 PDT, a unit shutdown was commenced at 20:20 PDT. "The leak was identified at a cracked weld to the RCP 1-3 lube oil cooler, and is estimated at approximately 0.1 gallons per minute. While the leak is in the non-vital CCW loop and is stable, not currently a challenge to the function of the CCW system, and is not damaging plant equipment, based on the potential for the condition to rapidly degrade under loading such as a seismic event, operators applied TS 3.7.7. "It is planned to place Unit 1 in Mode 3 (Hot Standby), restore both vital CCW loops to OPERABLE status by isolating the CCW supply to the RCP 1-3 lube oil cooler, and exit TS 3.0.3. The unit will be returned to service following repair of the cracked weld." Reactor Coolant Pump (RCP) 1-3 CCW pipe diameter is 3 inches. Leak was first noticed by increasing containment sump level. Personnel entered containment and discovered the cracked weld on the 3 inch CCW piping. The maximum leak if the CCW pipe completely shared off would be greater than 200 gallons per minute (CCW system can handle a maximum leak rate of approximately 200 gallons per minute). The other three Reactor Coolant Pump CCW lube oil cooling piping were checked and no leaks were discovered. All emergency core cooling systems and the emergency diesel generators are fully operable if needed. The electrical grid is also stable. At 2357 EDT Unit 1 was at a power level of 50% and decreasing. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-07-22
40889 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-07-21 11:55 | 2004-07-21 19:32 | 2004-07-29 | EOF DECLARED INOPERABLE DUE TO UNACCEPTABLE AIR FLOW RATES IN FILTRATION MODE "At 1155, 7/21/04, Callaway Plant declared the Emergency Offsite Facility (EOF) inoperable due to unacceptable air flow rates when the ventilation system was in the Filtration mode. Normally the ventilation system is designed to operate with a positive pressure in the EOF in order to prevent in-leakage of unfiltered air. During regularly scheduled maintenance, it was discovered that if a fume hood exhaust fan was operated with the EOF ventilation in the Filtration mode, it was possible to develop a negative pressure condition within the EOF. A station Work Request has been generated and ventilation equipment has been aligned so that a positive pressure can be maintained until the problem has been corrected." The licensee noted that regularly scheduled maintenance is performed on a yearly frequency. The licensee informed the NRC Resident Inspector. * * * UPDATE ON 07/29/04 @ 1640 BY EURMAN HENSON TO CHAUNCEY GOULD * * * RETRACTION 7/29/04: A review was conducted of both the test data obtained on 7/21/04 and the methodology utilized. This review determined that the methodology was incorrect and resulted in unsatisfactory test data. The test was performed again on 7/23/04 with satisfactory results. Based upon this information, it was concluded that the EOF had not been inoperable as initially reported and this Event Notification is being retracted. The NRC Resident Inspector was notified. Notified Reg 4 RDO (Russ Bywater) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-21
40888 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2004-07-21 09:00 | 2004-07-21 13:20 | 2004-07-21 | 4-HOUR 91-01 NRC BULLETIN NOTIFICATION DUE TO ADU IN NON-FAVORABLE GEOMETRY NITROGEN ACCUMULATOR TANK "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (less than or equal to 5.0 wt.% U-235) PWR fuel fabricator for commercial light water reactors. "License: SNM-1107. Time and Date of Event: July 21, 2004, 0900 "Reason for Notification: During a highly unusual upset condition on Conversion line 3, ADU powder backed up in the elevator and hot oil dryer. Subsequently, the ADU backed up into the dryer filter housing, crushing stainless steel filter frames and opening a path via dual flexible lines to a non favorable geometry nitrogen accumulator tank. The tank normally serves as a nitrogen gas accumulator/heater to provide heated nitrogen to pulse/clean the bag filters in the dryer filter housing. No similar event has ever occurred in the history of the facility. "In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (b.3), this event satisfies the criteria for a 4-hour notification, specifically, any determination that a criticality safety analysis or evaluation was deficient, or that a particular system was not previously analyzed. "As Found Condition: 10.5 kg of dry material (primarily ADU) was removed from the nitrogen accumulator tank. "Summary of Activity: - The affected line remains shutdown until all equipment is cleaned out. - The nitrogen accumulator tanks on all other Conversion lines have been inspected. No evidence of ADU powder has been found. "Conclusions: - This particular tank was not previously analyzed for criticality safety. - There was less than a critical mass of SNM involved. - At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. - The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. - A causal analysis will be performed." The licensee will inform the NRC Headquarters Criticality Specialist and the NRC Region 2 Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2004-07-21
40887 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2004-07-21 11:20 | 2004-07-21 12:46 | 2004-07-21 | LOSS OF PUBLIC NOTIFICATION SYSTEM DUE TO LOSS OF NORMAL AND EMERGENCY POWER SUPPLY "Vermont Yankee was notified by it's radio & siren vendor that the Ames Hill NOAA transmitter was inoperable between 1930 hours on 7/20/04 and 1055 hours on 7/21/04 due to a loss of normal power and a failure of it's backup generator. This failure caused the Public Notification System (PNS) to be inoperable during the period which is considered a major loss of emergency response capability." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-21
40886 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-07-21 05:12 | 2004-07-21 11:11 | 2004-07-21 | BOTH CONTROL ROOM VENTIALTION (CRV) SYSTEMS INOPERABLE. Both control room ventilation systems were inoperable due to a seal failure on the in service control room ventilation unit. A 24 hour Limiting Condition of Operation (LCO) was entered at 0512 CDT. (V-EAC-14A) "A" CRV tripped and "B" CRV was isolated for planned maintenance. "B" CRV (V-EAC-14B) was unisolated and restored to service at 0545 CDT (33 minutes later) and the 24 hour LCO exited at 0600 CDT. The plant remains in a 30 day LCO for one train of the CRV being inoperable. Control room temperatures increased slightly during CRV inoperability and are within normal operating band at this time (Temp increased 5 degrees F). State and Local were notified of this by the licensee. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-07-21
40885 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2004-07-20 18:18 | 2004-07-20 20:36 | 2004-07-20 | 4-HOUR NOTIFICATION REQUIRED BY TECHNICAL SPECIFICATIONS "At 1818 the predicted post trip voltage on the 161 KV incoming line went into alarm on the PCM MINT program. The alarm was validated using OI-EG-3 and by conversation with the system operator. The predicted voltage was 160.4 KV. AOP-31 Section 1 'grid instability' was entered. Per the AOP, at less that 160.7 KV, the incoming line and T1A3 and T1A4 are considered inoperable. Technical Specification 2.7(2)c was entered. This is a 72 hour LCO and requires a 4 hour notification to the NRC. Both diesel generators are operable. "The system operator took actions to raise the 161 KV system voltage. At 1831, the predicted post trip voltage was 160.9 KV and the LCO was exited. The line was inoperable for 13 minutes. "At 1834 the voltage was 161.1 KV and AOP-31 was exited." The licensee attributes the dip in line voltage due to heavy demand. The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2004-07-20
40884 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-07-20 15:39 | 2004-07-20 18:00 | 2004-07-20 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY EXCEEDING 8 HOURS "Scheduled work activity on Plant Computer System resulted in loss of emergency assessment capability exceeding 8 hours." The licensee informed the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-20
40883 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-07-15 07:30 | 2004-07-20 13:13 | 2004-07-20 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "Moisture density gauge believed to be stolen during a stop at Lowes, Plano, Texas, to pickup parts. The operator claims that the chain or lock was cut. The chain and lock were not left behind. The gauge is a Troxler Model 3440, Serial No. 33851 with two sealed sources: Cs-137, 8 millicuries, Serial No. 750-9505 and Am-241/Be, 40 millicuries, Serial No. 47-3391. Both sources were last leak tested June 1, 2004. Driver left Lowes and proceeded to a convenience store across the parking lot for a carton of cigarettes. Upon returning to the truck the gauge was noted as missing. The vehicle was a company truck: white, Ford Ranger, #51, with green logos on both sides. "Media attention: None known. Licensee is contemplating offering a reward for return of the gauge." The Plano Police Department was notified of this incident. Texas Incident No.: I-8144. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-07-23
40882 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2004-07-20 03:44 | 2004-07-20 04:04 | 2004-09-10 | ALERT DECLARED DUE TO HIGH OFFGAS EFFLUENT ALARM PEGGED HIGH AND UNABLE TO CONFIRM WITHIN 15 MINUTES At 0344 hrs. EDT, the licensee declared an Alert under Emergency Action Level HA.1. The initiating event was a pegged high off gas ventilation effluent radiation monitor and inability to obtain a confirmatory sample within 15 minutes. Only the gaseous channel failed high. The particulate and iodine channels remained reading normally. When plant chemistry technicians were able to obtain samples (an initial and back-up), they were negative with no activity greater than background detected. The plant management and operations team is currently evaluating their exit strategy for the Alert. The plant remains stable at 100% power, operating at normal operating parameters. The NRC entered monitoring mode at 0438 hrs. in response to this event. Notified DOC (Outlaw), DOE (Wyatt), USDA (Brzostek), EPA(NRC) (Baumgartner), and HHS (Phillips). The NRC Resident Inspector was notified and is present in the control room. * * * UPDATE FROM RALPH DAVIS TO JEFF ROTTON AT 0907 HRS ON 07/20/04 * * * The licensee terminated the Alert at 0901 hrs. EDT. The basis for the termination was that samples taken at the site boundary were negative, samples taken locally at the skid indicated no activity, and the licensee determined that the radiation monitor equipment was faulted. The NRC Resident Inspector was notified by the licensee. The licensee notified the State of Ohio (Collins), Ashtabula County, OH, Geauga County, OH and Lake County, OH. The NRC exited monitoring mode at 0914 hrs. EDT. The NRC Operations Center notified DHS (Everett), FEMA (Biscoe), DOE (Smith), EPA(NRC) (Jones), USDA (Comeau), HHS (Molina), HQPAO (Brenner), DOC (Outlaw) and RIVDO (Farnholtz). * * * RETRACTION FROM MEADE TO CROUCH AT 1637 EDT ON 9/10/04 * * * The following retraction was received from the licensee via facsimile: "Update to Emergency Plan Alert Event Notification 40882 Retraction "This is a follow-up notification to inform the NRC that Perry Nuclear Power Plant (PNPP) is retracting an Alert Emergency Declaration reported on July 20, 2004. Emergency Action Level HA.1, 'Any unplanned release of gaseous radioactivity to the environment that exceeds 200 times the ODCM [Offsite Dose Calculation Manual] Control limit for 15 minutes or greater', was entered based on an invalid reading due to a failed instrument. "The Offgas Vent Pipe Gaseous Radiation Monitor had pegged offscale high. The post-accident high range Offgas Vent Pipe Gaseous Radiation Monitor, which monitors the same process stream, had started in response to the offscale reading and was indicating low, which did not correspond to the offscale readings. The radiation monitors for Offgas pre-treatment and post treatment process streams were both reading normally for the plant conditions. Other plant and process radiation monitors, post accident high range monitors, and area radiation monitors did not indicate increased radiation levels to support the off-scale Offgas Vent Pipe Gaseous Radiation Monitor. Aside from the one offscale radiation monitor, there were no corresponding indications that there was a release in progress. "The Shift Manager took actions based on the offscale reading. In addition to the radiation monitor reading, the entry criteria for the Emergency Action Level (EAL) required entry into an Alert, unless gaseous effluent levels were verified by chemistry sample analysis methods to be less than the ODCM limits within 15 minutes. These results were not provided within 15 minutes, therefore the Shift Manager declared the Alert. "Troubleshooting confirmed that the Offgas Vent Pipe Gas instrument reading was invalid. The Emergency Plan directs classification of events based on valid indications. At no time was there any unplanned release that would have required taking any emergency plan actions. "Therefore, the entry criteria in the EAL were not met and the Alert emergency classification is being retracted." The licensee notified the NRC Resident Inspector of this retraction. Notified NRREO (Reis), R3DO (Hills) and IRD (Nieh). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | ALERT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-07-20
40881 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-07-19 18:04 | 2004-07-19 21:27 | 2004-07-19 | OFFSITE NOTIFICATION DUE TO RECOVERY OF DROWNING VICTIM ON OWNER CONTROLLED PROPERTY "On 7/18/04 at 02:15, Dresden personnel were informed that a pontoon boat in the Kankakee River was near the Dresden Station intake log boom, outside the owner controlled area, and that two individuals had fallen off the boat. Immediate rescue efforts by local law enforcement and rescue agencies rescued one individual, and the second individual was not found. At 04:46, rescue efforts were halted due to excessive fog in the area. "On 7/19/04 at 18:04, the dead body of the second individual was discovered surfaced in the middle of the Kankakee River. The dead body subsequently went under the surface and was drawn into the Dresden owned intake log boom. The body was removed from the owner controlled area by Coal City rescue, the Grundy County Sheriff, Grundy County Coroner, and Dresden Station security. The individual was deceased prior to entering the owner controlled area and did not drown on-site. "This report is being made in accordance with 10CFR50.72(b)(2)(xi) because of the other government notifications made and potential media involvement. "The NRC Resident has been informed." | 0 | 99 | 99 | 0 | 99 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-07-19
40880 | 0 | UNIV OF MICHIGAN |  |  |  | 2000 KW POOL | 2004-07-19 10:30 | 2004-07-19 16:54 | 2004-07-19 | FAILURE OF CABLE DRIVE MECHANISM TO LOWER TABLE FULLY INTO THE POOL OF THEIR IRRADIATOR The licensee, the University of Michigan at Ann Arbor, reported that they had a failure of the cable drive mechanism in their irradiator. While they were lowering the table into the pool, the mechanism failed after being lowered to the level where the high radiation light went out. The activity of the Cobalt 60 sources in the irradiator is 8,763 curies. The table was then remotely manually lowered into the pool to a level where there was no measured exposure detected by their ion chamber detectors. The current exposure rate at the surface is 1mr/hr. The room will be secured until the person in charge of the irradiator returns from vacation. Only the HP has keys to the room. There were no injuries or overexposures during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | FAILED CABLE/DRIVE | [9 empty] | NON EMERGENCY | 3 | MI | NPR |  | 36.83(a)(4) |  |  |  | 0 | 2004-07-19
40879 | 0 | GLOBAL X-RAY AND TESTING CORP. |  |  |  |  | 2004-07-19 | 2004-07-19 10:52 | 2004-07-19 | RADIOGRAPHY CAMERA SOURCE FAILED TO RETRACT The licensee was operating approximately 100 miles offshore performing gamma radiography on new pipeline. After taking a camera shot, the crew attempted to retract the 58 Curie Ir-192 source back into the shield when the source failed to retract. The crew isolated the area and contacted the RSO. The RSO flew out to the site and was able to retract the source into the shield. The camera and controls was returned to the vendor, AEA Technologies, for inspection and repair. There was no personnel injuries or over-exposures due to this event. The licensee notified NRC Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | LA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2004-07-19
40878 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2004-07-16 13:45 | 2004-07-16 17:27 | 2004-07-16 | THE PLANT LOST PUBLIC PROMPT NOTIFICATION CAPABILITY "At approximately 1345 CST on 7/16/04, Cooper Nuclear Station was informed by Emergency Preparedness officials of Nemaha County that the radio transmission tower that provides signals to activate tone alert radios within the 10-mile Emergency Planning Zone (EPZ) was not functioning. Tone alert radio is relied on by approximately 650 households in the EPZ, who are not in audible range of sirens for notification of an emergency at CNS. Based on a total EPZ population currently estimated at 4600 persons (who are alerted principally by sirens and the tone alert radio), this is considered to be a major loss of the Public Prompt Notification system capability, and is reportable under 10CFR50.72(b)(3)(xiii). "Investigations are ongoing. The cause appears to be an inadvertently severed telecommunications cable to the tower. There does not appear to be any evidence of sabotage. It is expected that repairs will be completed by 1800 CST on 7/16/04. During the interim, compensatory measures have been verified to be in place via state and local emergency planning officials for backup route alerting for personnel within the 10-mile EPZ." The NRC Resident Inspector was notified along with State and Local agencies * * * * UPDATE FROM A. OHRABLO TO M. RIPLEY 2257 ET 07/16/04 * * * * "At 2035 CST the Cooper Control Room was informed that the radio transmission tower has been repaired and tested satisfactorily. The cause was inadvertent severing of the telecommunications cable during digging. The NRC Resident will be informed." Notified R4DO (D. Powers) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-16
40877 | 0 | HUMBOLDT BAY | 3 |  |  | [3] GE-1 | 2004-07-16 13:00 | 2004-07-16 14:04 | 2004-07-16 | PRESS RELEASE WILL BE ISSUED AT 1300 PDT ON 7/16/04 ON THE MATERIAL ACCOUNTABILITY DISCREPANCY INVOLVING A PORTION OF A SPENT FUEL ROD USED AT HUMBOLT BAY POWER PLANT UNIT 3. This is a non-emergency Event Notification made in accordance with 10 CFR 50.72(b)(2)(xi) to inform the NRC that a press release will be issued shortly informing the public of a nuclear material accountability discrepancy involving a portion of a spent fuel rod used at Pacific Gas and Electric's (PG&E) Humboldt Bay Power Plant (HBPP) Unit 3. HBPP Unit 3 has been shut down since 1976 and in SAFSTOR since 1988. In the process of reviewing records and verifying the contents of the spent fuel pool (SFP) in preparation for loading materials into dry cask storage, PG&E has identified a discrepancy in plant records that calls into question the location of three segments of a portion of a single spent fuel rod removed from assembly A-49 in 1968. Meeting records produced in 1968 indicate that the segments have been stored in the SFP since 1968. However, 1969 plant shipping records indicate that the entire A-49 assembly was included as part of a larger shipment of several spent fuel assemblies sent for offsite reprocessing in 1969. The 1969 shipping records make no mention that one rod had been removed from the A-49 assembly that was shipped. A more detailed review of records and a complete search of the SFP is underway to establish and verify the location of the three fuel rod segments. Since 2003, PG&E plant personnel have been conducting a complete review of plant records and cataloging the contents of the SFP in preparation for the planned decommissioning of the plant, including the transfer of spent fuel into an onsite Independent Spent Fuel Storage Installation. On June 23, 2004, plant personnel found Onsite Review Committee (OSRC) meeting minutes dated October 2, 1968, that described cutting one fuel rod from fuel assembly A-49 into three 18 inch segments that were placed into a small container (1 -1 /2 inch, schedule 40 pipe) in preparation for shipment to the Battelle Memorial Institute in Columbus, Ohio, for analysis. The meeting minutes further state that the shipment to Battelle was subsequently cancelled and the small container with the three 18-inch fuel rod segments was returned to the SFP, with the specific location in the SFP unidentified. The minutes also state that the remnants of the 84 inch long fuel rod from which the three 18-inch segments were cut were placed in the central storage container within the SFP. On June 25, 2004, after further research, PG&E found shipping records indicating that on August 6, 1969, the entire A-49 fuel assembly was shipped to Nuclear Fuel Services Inc. (NFS) in West Valley, New York, for reprocessing. No mention was made in the shipping record that a rod had been removed from the A-49 fuel assembly. This contradicts the OSRC meeting minutes that indicate one fuel rod from A-49 remains in the SFP. Further review of records did not resolve the discrepancy, so on June 28, 2004, PG&E verbally notified the Nuclear Regulatory Commission, Region IV office of the potential discrepancy in records and the uncertainty regarding the specific location of the fuel rod removed from A-49. On July 7, 2004, PG&E began a physical search of the central storage container in the SFP for the remnant portions of the A-49 rod, as well as the three 18-inch segments. On July 9-11, 2004, PG&E identified what appears to be the remnant portions of the A-49 rod in the central storage container in the SFP as specified in the 1968 OSRC meeting minutes. However, the three 18-inch segments were not found in the central storage container. PG&E is continuing with a thorough search of the remaining storage containers in the SFP as well as other possible areas in the SFP where the three fuel rod segments may be located. The search is a painstaking process performed under tight procedural guidance that could take at least several weeks to complete. NRC inspectors have been onsite during the week of July 12 and are fully aware of the status of these inspections. In addition, PG&E is continuing its review of plant records as well as interviewing plant personnel who were onsite during the 1968-1969 period to find further evidence that may expedite location of the three fuel rod segments. This notification also satisfies the 30-day notification requirement of 10 CFR 20.2201(a)(1)(ii). If ongoing searches fail to confirm the location of the material, a subsequent written report will be made in accordance with 10 CFR 20.2201(b). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-07-16
40876 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-07-16 10:00 | 2004-07-16 14:10 | 2004-07-16 | TECHNICAL SPECIFICATION SHUTDOWN/LOSS OF SINGLE SAFETY FUNCTION "A Unit shutdown was initiated at 1100 [ET 07/16/04] to comply with Technical Specifications. The High Pressure Coolant Injection (HPCI) System was declared inoperable at 1000 on 7/16/04 due to an inability to demonstrate that it is capable of meeting its design flow and pressure requirements identified during an extent of condition review being conducted in conjunction with an ongoing Safety System Design Inspection. Concurrently, the `D' Emergency Diesel Generator (EDG) was inoperable due to an in-progress surveillance. This rendered the `D' Low Pressure Coolant Injection (LPCI) subsystem and `B' Core Spray subsystem inoperable resulting in entry into Technical Specification 3.0.3 requiring within 1 hour initiating action to place the unit in at least startup within the next 6 hours, hot shutdown within the following 6 hours and cold shutdown within the subsequent 24 hours. "Power ascension was in progress with reactor power at 95%. Power ascension was suspended. Preparations for power reduction were initiated. Actions were taken to restore the `D' EDG to an operable, standby alignment, which was complete at 1145 rendering `D' LPCI subsystem and `B' Core Spray subsystem operable. Technical Specification 3.0.3 was exited. No power reduction was conducted. "The HPCI system remains inoperable constituting a condition that could have prevented the fulfillment of a safety function. The investigation is ongoing including a determination of the need for any physical modifications that may be required. "Prior to the event, the `C' Station Service Water pump, `D' Filtration Recirculation, Ventilation System recirculation fan, and `B' Primary Containment Instrument gas compressor were out of service for scheduled maintenance. There were no personnel injuries as a result of this event. "The NRC Resident inspector was notified of this event." | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-07-16
40875 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-07-15 19:44 | 2004-07-15 22:18 | 2004-07-15 | MANUAL TRIP FROM 8% POWER DUE TO LOWERING WATER LEVEL ON 23 STEAM GENERATOR During plant start up, a manual Reactor trip was initiated in response to lowering water level on 23 Steam Generator. All systems responded as required. All control rods fully inserted and no ECCS actuated or relief valves lifted. Both motor driven auxiliary feedwater pumps (21 and 22) started as expected on the low level signals from 23 Steam Generator. The steam driven auxiliary feed (23) pump was not required to start and remained in standby. Decay heat is being removed via the main steam dump system to the main condenser. The reactor is currently at normal operating temperature and pressure. No major equipment was unavailable at the time of the trip. No personnel injuries occurred as a result of this event. The cause of the low steam generator level is being investigated. The NRC Resident Inspector was notified along with Lower Alloway Creek Township. The States of New Jersey and Delaware will be notified. | 0 | 0 | 0 | 0 | 8 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-07-15
40874 | 0 | PALO VERDE | 1 | 2 | 3 | [1] CE,[2] CE,[3] CE | 2004-07-14 16:30 | 2004-07-15 17:17 | 2004-07-15 | ALL THREE UNITS EXCEEDED THE MAXIMUM POWER LEVEL SPECIFIED IN THEIR OPERATING LICENSE "Palo Verde Nuclear Generating Station Units 1, 2, and 3 determined that the Maximum Power Level specified in Operating License Condition 2.C(1) was exceeded in the past due to a nonconservative feedwater flow input in the secondary calorimetric calculation since installation of ultrasonic feedwater flow measurement (UFM) instrumentation in Units 1 and 3 in 1999 and 2000 in Unit 2. On 06/09/2004, the vendor (Caldon) notified Palo Verde via a letter that there may be an error of up to one to one and one-half percent in the flow measurement. As a compensatory measure, all three units reduced power and removed the UFM from service. Feedwater flow venturis are used for measurement with the UFM out of service. Engineering evaluation concluded on 07/14/2004 the maximum Palo Verde specific calorimetric error was approximately 38.76 Mw in Units 1 and 3 and 39.90 MW in Unit 2 or approximately 1 %. The error resulted in core power levels above the Operating License limit of 3876 MW thermal in Units 1 and 3 and the Operating License limit of 3990 MW thermal In Unit 2 while the UFM was in service. This report is being made because a review of historical operating data revealed that the Maximum Power Level was exceeded. The Palo Verde safety analyses bound a power level of 102%. Power level did not exceed the safety analysis. No ESF actuations occurred and none were required as a result of the miscalibration. There were no other structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were Involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The NRC Resident Inspector was notified. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Hot Standby | Power Operation | Power Operation | Hot Standby | Power Operation | NON EMERGENCY | 4 | AZ | POW | [5 empty] | 0 | 2004-07-15
40873 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-07-14 13:00 | 2004-07-14 23:45 | 2004-07-15 | CRITICALITY CONTROL 24-HOUR (BULLETIN 91-01) REPORT "At 1300 [CDT] on 7/14/04, the Plant Shift Superintendent (PSS) was notified that a cylinder, which was to be washed, was determined to contain heel material. The cylinder had been filled a single time with natural material at Honeywell (2/2001) since its last wash in 8/1999. An examination of the associated Nuclear Material Control and Accountability (NCM&A) data and cylinder card indicated that the only other filling was in 9/1982 with depleted material at C-315. The cylinder was fed to the cascade in 9/2003 at C-337-A. "A total of 4 gas over solid samples were taken of the cylinder and all indicated that the cylinder contains material. Nuclear Criticality Safety Evaluation 085 and Nuclear Criticality Safety Analysis 400-012 establish double contingency to ensure that a fissile cylinder is not washed in the non-fissile cylinder wash facility. "The NRC Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATR 04-2756; PGDP Event Report No. PAD 2004-019; Responsible Division: Operations. "SAFETY SIGNIFICANCE OF EVENTS: "NMC&A showed this cylinder contained a heel of around 8 lbs. Gas over solid sampling determined this non-fissile cylinder contained fissile material and could not be washed. Although the cylinder was not washed, an unlikely failure occurred that allowed fissile material to enter a cylinder controlled as non-fissile. "CONTROLLED PARAMETERS: "The process condition relied upon for double contingency for this scenario is enrichment. "NUCLEAR CRITICALITY SAFETY CONTROL OR CONTROL SYSTEMS AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: "The first leg of double contingency relies on a gas over solid sample of the cylinder to demonstrate that the cylinder contains non-fissile material prior to washing. "The second leg of double contingency relies on an argument that back- or cross-feeding at C-337A is unlikely to result in a significant amount of fissile material to be transferred to the cylinder. Since fissile material was found in the cylinder after it was fed at C-337A, this unlikely argument appears to have failed. However, the cylinder was not washed, maintaining this parameter. "Although the parameter was maintained, double contingency is based on two controls on one parameter and one of the controls (unlikely argument) failed. Therefore double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: "1. Correct NMC&A database for this cylinder to show the correct assay in the cylinder and that the cylinder is fissile." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-07-15
40872 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-07-13 10:30 | 2004-07-14 16:02 | 2004-07-14 | AGREEMENT STATE REPORT FROM THE COMMONWEALTH OF MASSACHUSETTS Thermal Electron found a torn window on a DMC Thickness measurement gauge while performing preventative maintenance on the gauge. The DMC thickness measurement gauge is licensed to Allegheny Rodney which is located in New Bedford, MA. The model number for the DMC measurement gauge is SR-U2. The serial number for the gauge is J3013T. The gauge contains a 50 milliCurie strontium-90 source. There is no sign of contamination and there is no expected exposures at this time. The Commonwealth of MA is sending someone out on 07/15/04 to investigate this problem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-07-19
40871 | 0 | UNION HOSPITAL |  |  |  |  | 2004-03-29 | 2004-07-14 15:05 | 2004-07-14 | SHIPMENT OF IODINE-125 IMPLANTATION SEEDS FOUND TO BE ONE SEED SHORT OF EXPECTED On 03/29/04, the licensee received a shipment of I-125 prostate implantation seeds (0.587 millicuries unshielded activity per seed) from the manufacturer, Amersham Biosciences of Chicago, IL. The shipment records indicated that 102 seeds were shipped. Upon receipt, the licensee performed an inventory of the shipment which confirmed that only 101 seeds were actually present (one of the pre-loaded cartridges contained 14 seeds rather than 15 as expected). The cartridges were still sealed and sterile-wrapped indicating that the missing seed was not the result of tampering or damage during shipment. Amersham replied to the licensee's inquiry on 05/21/04 indicating that their records indicated that the shipment did contain 102 seeds. Corrective actions for improved shipment accounting are being developed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-07-14
40870 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2004-07-14 01:35 | 2004-07-14 07:35 | 2004-07-14 | AUTOMATIC REACTOR TRIP FOLLOWING A MAIN GENERATOR TRIP The following information was received from the licensee via facsimile: "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On July 14, 2004, at approximately 01:35 Mountain Standard Time (MST) Palo Verde Unit 2 experienced a Main Generator Trip immediately followed by an automatic Reactor Trip. The reactor was at approximately 100% power and normal operating temperature and pressure prior to the event. The cause of the Main Generator Trip was most likely the result of electrical storm conditions present at the site at the time of the trip. Unit 2 was at normal operating temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. Heat removal was maintained to the condenser via the steam bypass control system. This was an uncomplicated reactor trip, No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 2 Is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The [NRC] Senior Resident Inspector was informed of the Unit 2 reactor trip." No primary or secondary power-operated or manual relief valves lifted as a result of the plant transient. Units 1 and 3 were unaffected by the trip on Unit 2. Offsite power was maintained to Unit 2 safety busses throughout the event. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-07-14
40869 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-07-14 00:45 | 2004-07-14 03:55 | 2004-07-14 | RPS AND CONTAINMENT ISOLATION ACTUATION DUE TO LOW RPV LEVEL "On July 14, 2004, at 0045 CDT, the Clinton Power Station experienced a drop in RPV [Reactor Pressure Vessel] level from nominally 30 inches to the Level 3 (the RPS and Isolation setpoint). At this time control rods were fully inserted [see Event Notification - #40868], however, the containment isolation valves associated with this setpoint were open, and these valves automatically closed successfully. "Level was restored to normal by automatic makeup from the condensate system. "There were no other malfunctions. The cause for the level drop is being investigated." The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-07-14
40868 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-07-13 16:10 | 2004-07-13 18:57 | 2004-07-13 | AUTOMATIC REACTOR SCRAM DUE TO POSSIBLE ADVERSE WEATHER "On July 13, 2004 at 1610 CDT, the Clinton Power Station 345 KV unit output breakers GCB 4506 and 4510 opened resulting in a turbine control valve fast closure. This caused a reactor protection system actuation and reactor scram. Clinton was in Mode 1, operating at 95% rated thermal power when the event occurred. A tornado warning was in effect at the time of the event and weather conditions were degrading in the area surrounding the plant. The exact cause of the trip of the unit breakers is not yet known. "All systems responded as expected following the scram with the exception of Reactor Recirculation pump A which tripped off instead of downshifting to slow speed on a reactor water level 3 signal. "The unit is currently in Mode 3 with reactor pressure vessel level and pressure in their normal bands." Recirculation Pump "A" remains secured until the licensee completes their investigation. All control rods fully inserted following the scram. The Main Condenser is in service removing decay heat. All ECCS equipment including the EDGs are available, if needed. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-07-13
40867 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2004-07-13 18:00 | 2004-07-13 18:54 | 2004-07-13 | ENTERGY LOCATES SPENT FUEL SEGMENTS AT VERMONT YANKEE "On April 21, 2004 Vermont Yankee made a notification regarding a news release of an accountability discrepancy of SNM. This was event # 40694. "Today as a result of the continuing search for the two pieces of spent fuel, the two pieces were located in a unique 40 inch aluminum cylinder within the spent fuel pool. The licensee has issued a news release regarding the discovery of the two pieces. The news release is attached: "5:25 pm 7/13/04 "Vernon, VT--- Entergy workers at the Vermont Yankee nuclear power plant today located the missing spent fuel rod segments in the plant's spent fuel pool. The two pieces were stored in a unique 40-inch aluminum cylinder, which is unlike a typical storage container but is similar to several other aluminum structures and tools in the pool. "Entergy VY Site Vice President Jay Thayer credited interviews with former employees and contractors, intense research of records and documents dating back more than 25 years, and video tapes of the pool that were recently taken. "Said Thayer, 'Our search team designed a detailed search plan that explored every possibility from three different angles. They looked visually with the cameras, they searched the documents, and they talked to people who were on the scene 25 years ago. The team deserves a tremendous amount of credit.' "'We earlier had checked all the containers in the pool, but when we learned that General Electric had designed and sent a pipe-like cylinder for the fuel-rod pieces, we rechecked the videotapes. That's when we noticed that what was previously thought to be part of an existing in-pool structure could very well be the canister that GE sent here.' "Workers used remotely operated tools to open the canister and insert a small high-resolution video camera that confirmed the presence of the fuel segments, which are nine inches and seventeen inches long and about the diameter of a pencil. "Thayer also credits the resident NRC inspectors at Vermont Yankee and William Sherman, the Vermont Public Service Department's nuclear engineer, for their contributions to the investigation. "'These folks had full and open access to the process every step of the way and they provided valuable insights and guidance.'" "Thayer said the policies and procedures for record keeping and documentation of activities in Vermont Yankee's spent fuel pool have been revised to ensure accurate record keeping. 'We want to make sure this doesn't happen again,' he said." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-07-13
40866 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-07-13 14:40 | 2004-07-13 18:30 | 2004-07-13 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE At 1440 PDT on 7/13/04, the California Radiologic Health Branch was notified by the Assistant Radiation Safety Officer for Stacey and Witbeck that their one and only gauge was stolen along with some other goods from a Conex box, container car, which was located at a construction site at Bascomb and SW Expressway in San Jose. The stolen gauge was a Troxler 3440, Serial Number 750-8909 containing 9 millicuries Cs-137 and 44 millicuries Am-241. The gauge was in a locked construction site in a locked Conex box. Bolt cutters and a torch were used to open the Conex box. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-07-16
40865 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-07-13 13:05 | 2004-07-13 14:53 | 2004-07-13 | AUTOMATIC REACTOR TRIP ON LOW LOW STEAM GENERATOR WATER LEVEL. "An automatic Reactor Trip occurred on 21 Steam Generator low low level. The cause is currently under investigation. All systems responded as required. All control rods fully inserted. All auxiliary Feedwater pumps started as expected, on the low level signals and the steam driven auxiliary feed (23) pump was secured by procedure. Currently the steam dump system is rejecting heat to the main condenser for reactor coolant system temperature control, currently at normal operating temperature and pressure. No major equipment was unavailable at the time of the trip." All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed and the electrical grid is stable. The Licensee is investigating the cause of Steam Generator "21" low low water level. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-07-13
40864 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-07-06 | 2004-07-12 14:38 | 2004-07-12 | AGREEMENT STATE REPORT INVOLVING LOST WELL LOGGING SOURCE "After performing services to determine the oil/water contact interface and the gas/oil interface levels the wireline with the source was being retracted. The wireline was attached to 1 11/16" tool in the salt dome. During retraction, the source evidently got hung on entry to the hole to the surface. It is felt that the crew was inattentive or possibly did not use proper procedure. The 'stuck' source broke loose of the wireline at the established weak point of connection between the tool and the wireline. Retrieval of the source is deemed unrecoverable. This is the second incident of this type in the same field. The source is a Gulf Nuclear, Model CSV-F74, Cs-137, 100 millicurie source. The probable depth of this source is estimated at approximately 4,000 feet. Investigation on site continues. A written report will be submitted to this Agency [Texas Department of Health]." Texas Incident No.: I-8142 Event Location: Bryan Mound Strategic Petroleum Reserve, Brazoria County, Texas, Well # BM 104B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-07-15
40863 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-07-10 | 2004-07-12 09:29 | 2004-07-12 | TEXAS AGREEMENT STATE REPORT ON DOSE TO THE PUBLIC FROM EXPOSED SEALED SOURCE "Full investigation has been started by Schlumberger. Many details missing from initial notification. Crew using a CAPSTAR rig, without a floor were working a well site in Pecos County, Texas, from the Midland office (Subsite 042). During the evening of probably 07/09/2004 the rig was moved to a new site. When setup for work it was determined by the well loggers that a sealed 1.7 curie Cs-137 source was missing from their tool. They went back to the last site and discovered the source in a pile of mud that was located 10-15 feet from the rig location. It is suspected that the source was missing for 24-36 hours. Suspect dose to the public to the rig crew/roustabouts. The logging crew was badged. No estimates are currently available. A Schlumberger management team has been dispatched from Houston (Subsite 000) to assess dose and investigate this incident. Investigation is ongoing." TX Incident No.: I-8141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-07-15
40862 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2004-07-10 22:35 | 2004-07-11 01:31 | 2004-07-11 | AUTOMATIC REACTOR SCRAM DUE TO AN UPSCALE TRIP ON INTERMEDIATE RANGE MONITORS "On 07/10/2004 at 2235 [CST], during Browns Ferry Unit 2 startup activities, as IRMs [Intermediate Range Monitors] were being ranged up, an upscale trip on IRM E (RPS [Reactor Protection System] A Channel) and IRM F (RPS B Channel) was received, resulting in a full reactor scram. Mode Switch was in STARTUP, Mode 2 at time of trip. IRMs were on ranges 6 and 7, and reactor pressure was approximately 950 psig. All systems responded as designed, all control rods are at full-in. No ECCS [Emergency Core Cooling System] or PCIS [Primary Containment Isolation System] actuation set points were reached. This is reportable as 4 hour ENS [Emergency Notification System] report per 10CFR50.72(b)(2)(iv)(B), 'Any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical except when the actuation results from and is part of pre-planned sequence during testing or reactor operation.' It is also reportable as an 8 hour ENS report per 10CFR50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B). (1) Reactor protection system (RPS) including: Reactor scram and reactor trip.' Also reportable as a sixty day written report per 10CFR50.73(a)(2)(iv)(B). "Mode Switch is presently in shutdown, Mode 3. Investigation is still on going. NRC Resident [Inspector] was notified at approximately 2310 [CST]." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Startup; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-07-11
40861 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-07-10 05:59 | 2004-07-10 08:40 | 2004-07-10 | LOSS OF COMMUNICATION AT THE TECHNICAL SUPPORT CENTER DUE TO SCHEDULED MAINTENANCE "During performance of planned maintenance, the Technical Support Center (TSC) will be without power. These maintenance activities, including electrical isolation and restoration are expected to last approximately 18 hours. Contingency plans for emergency [response] situations have been established. "This event is reportable per 10 CFR50.72(b)(3)(xiii) since this constitutes a loss of an emergency response facility for the duration of the evolution. "Region IV was notified of this planned outage." The licensee notified the NRC Resident Inspector. * * * UPDATE PROVIDED BY H. BRADLEY TO JEFF ROTTON AT 1745 EDT ON 7/10/04 * * * Maintenance in the TSC has been completed and power was restored at 1458 CDT. The licensee will notify the NRC Resident Inspector. Notified R4DO (Clark). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-10
40860 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-07-08 15:50 | 2004-07-09 17:45 | 2004-07-09 | 24 HOUR NRC BULLETIN 91-01 LOSS OF CRITICALITY CONTROL "At 1550, on 07-08-04 the Plant Shift Superintendent was notified that three centrifugal compressor impellers were received as part of a shipment from Portsmouth GDP. The existence of the impellers was not recognized as being part of this shipment and, as a result, applicable NCS [Nuclear Criticality Safety] controls were not implemented. NCSA GEN-20 requires receipt of documented NDA [Non Destructive Analysis] inspections of equipment prior to receipt (unloading) in the shipping/receiving area and completion of a second NDA prior to removing the equipment from the shipping/receiving area to a location within the plant. The purpose of this control is to ensure that equipment containing greater than a safe mass will not be received from offsite. "The three centrifugal compressor impellers have subsequently been characterized as a group, by NDA, to be less than the safe mass assuming 100 wt.% 235U. "SAFETY SIGNIFICANCE OF EVENTS: NDA measurements have been completed and the results indicate less than a safe mass of uranium. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR): In order for a criticality to be possible, greater than a critical mass of uranium would have to be present in the equipment in a configuration favorable for a criticality. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): Double contingency is maintained by implementing two controls on mass. "ESTIMATED AMOUNT ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The group of equipment contains less than the safe mass assuming 100 wt.% 235U. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEMS) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on the review of characterization results prior to receipt (unloading) at PGDP. Characterization results were not reviewed prior to receipt. The three centrifugal compressor impellers have subsequently been characterized as a group, by NDA, to be less than the safe mass assuming 100 wt.% 235U. Although, the NCS controls were violated, the parameter was maintained. "The second leg of double contingency relies on an independent NDA measurement prior to release from the shipping/receiving area. NDA characterization did not occur prior to release from the shipping/receiving area. The three centrifugal compressor impellers have subsequently been characterized as a group, by NDA, to be less than the safe mass assuming 100 wt% 235U. Although, the NCS controls were violated, the parameter was maintained. "Although the parameter was maintained, double contingency is based on two controls on one parameter. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED : "1. Post equipment according to CP2-MA-MT1034. Completed 07/09/04 "The NRC Resident lnspector has been notified of this event. "PGDP Problem Report No. ATRC-04-2682, PGDP Event Report No. PAD-2004-18; Event Worksheet #40860 Responsible Division: Maintenance" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-07-09
40858 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2004-07-08 22:32 | 2004-07-09 02:21 | 2004-07-09 | REACTOR SCRAM DUE TO A TURBINE GENERATOR LOAD REJECTION SIGNAL The following information was received from the licensee via facsimile: "On 7/08/2004 at approximately 2232 hours CDT, Browns Ferry Unit 2 scrammed due to a Turbine Generator Load Reject Signal. All systems responded as required to the scram signal. No ECCS initiations occurred as a result of this event. Reactor Water Level lowered to the Low Level setpoint which generated a redundant SCRAM signal and initiated the Primary Containment Isolation System (PCIS) function for PCIS groups 2 (Primary Containment), 3 (RWCU) [Reactor Water Clean Up], 6 (Secondary Containment), and 8 (TIP system) [Transverse Incore Probe]. As expected, Main Steam Relief Valves (MSRVs) opened due to the high reactor pressure (maximum value observed was 1137 psig) as a result of the Main Turbine / Generator Trip. Reactor Water level was restored to normal via the Reactor Feedwater system and all PCIS isolations have been reset. The cause of the Load Reject Signal is still under investigation at this time. "This event is reportable under 10CFR50.72(b)(2)(iv)(B), 'Any event or condition that results in a valid actuation of the Reactor Protection System (RPS) when the reactor is critical' and also under 10CFR50.72(b)(3)(iv)(A), 'Any event or condition that results in a valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B)'. This event also requires a 60 day written report in accordance with 10CFR50.73(a)(2)(iv)(A)." All control rods inserted during the scram. All Main Steam Relief Valves have properly reset. Decay heat is being removed from the reactor via main turbine bypass valves to the main condenser. Pressure is being maintained at normal operating pressure. The electrical grid is stable. Unit 3 was not affected by the scram on Unit 2. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-07-09
40857 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2004-07-08 13:00 | 2004-07-08 15:42 | 2004-07-08 | TENNESSEE AGREEMENT STATE REPORT: STOLEN MOISTURE DENSITY GAUGE "Terracon Consultants reported a Troxler moisture density gauge, Model 3430 SN 26411, containing 8 milliCuries of Cesium-137 and 40 milliCuries of Americium-241;Beryllium was stolen from the locked cab of a pickup truck parked at a hotel in Memphis, TN. The door of the truck was damaged and the locked container removed. State Department of Radiological Health (DRH) inspectors are onsite investigating at this time." Tennessee DRH notified US NRC Region 1, Memphis Police Department, Mississippi Division of Radiological Health, Arkansas Radiation Control, FBI, and Tennessee Emergency Management Agency. A press release was also issued by the Tennessee DRH. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2004-07-13
40856 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-06-15 | 2004-07-08 13:38 | 2004-07-08 | COLORADO AGREEMENT STATE REPORT: REMOVABLE SURFACE CONTAMINATION ABOVE LIMITS Removable surface contamination test on two sealed sources removed from the same instrument exceeded the 0.005 microCuries limit specified in RH 4.16.5. The first source is a Nickel-63 source, serial number F6499, activity: 13,200 microCuries, activity reference date: 08/31/93, Instrument ID: ECD1, swipe test results - 0.031 microCuries. The second source is a Nickel-63 source, serial number F2069, activity: 13,200 microCuries, activity reference date 05/29/91, Instrument ID: ECD1, swipe test results - 0.018 microCuries. "The sources were immediately removed from use and the instrument tagged 'out of service.' The usual vendor for cleaning and re-certification of the ECD sources was contacted and is considering options for repair or replacement. The sources will remain under the control of the Radiation Safety Officer until this determination is made. A decision will likely be made within two days, as the repair of the affected instrument is a high priority. "Additionally, the cabinet that houses the sources in the instrument was swiped, as well as the employee's workstation in the immediate vicinity. These tests showed no removable contamination above the method detection limit of 50 picoCuries." Colorado Report # I04-20. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-07-13
40855 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2004-07-07 17:00 | 2004-07-07 19:07 | 2004-07-07 | NRC BULLETIN 91-01 - 4 HOUR REPORT The following was submitted via email: "Reason for Notification A canvas lined cart was found in the UF6 [Uranium Hexafluoride] bay. The cart dimensions met the criteria for a non favorable geometry [NFG] container however slits had been cut into the bottom of the cart. The presence of the slits makes it questionable as to whether or not this is a true NFG. Taking a conservative approach and assuming that the cart is an NFG, its presence in the Chemical area is prohibited by SNM-1107, Section 6.1.4 without a nuclear criticality safety analysis. "In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (b.2), this event satisfies the criteria for a 4-hour notification. Specifically, any determination that a criticality safety analysis or evaluation was deficient, or that a particular system was not previously analyzed; and that less than two unlikely, independent, and concurrent changes in process conditions would be required before a criticality accident would be possible. "As Found Condition An NCS [Nuclear Criticality Safety] Engineer was notified by a member of the EH&S [Environmental Health and Safety] Department that a canvas cart was in the UF6 bay. The canvas cart had several slits approximately five inches in length cut in the bottom that would preclude the build-up of liquid materials. There was no process equipment in the general area where the cart was located. There was no SNM [Special Nuclear Material] in the cart and the cart was not a part of any existing process. "Summary of Activity -The cart was dismantled immediately. -NCS notified NRC Region II of the cart. "Conclusions -This particular system was not previously analyzed for criticality safety. -There was no SNM involved. -At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. -The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. -A causal analysis will be performed." The Licensee notified Region 2 (Ayres, Crespo). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2004-07-07
40854 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-05-07 | 2004-07-07 13:40 | 2004-07-07 | AGREEMENT STATE - LEAKING SEALED SOURCE "On May 6, 2004, a leak test sample from a Hewlett Packard 5890 Gas Chromatograph, with ECD Model # 19233, was leak tested for source Serial No. L6180 [Nickel - 63, current activity 13.48 milliCuries]. The initial leak test resulted in removable activity of approximately 9250 disintegrations per minute (dpm) or 0.0042 microCuries, near leak test limits. A second test was repeated on May 7, 2004, which resulted in 194,000 dpm or 0.087 microCuries of removable activity on the vent tube, which was well above the leak test limit. Minor removable contamination (approximately 100 counts per minute (cpm)) was detected on the interior of the case, the inlet tube sample (approximately 100 cpm), and the vent tube cap (approximately 1750 cpm). The source was confiscated by the University's radiation safety staff to a secure location at the Radiation Safety Office. The last leak test was conducted on December 17, 2003, with results indicating no contamination. The source will be returned to the manufacture or disposed of as radioactive waste. The direct cause of the loss of the source's integrity is not known. The written report was received by this agency May 17, 2004, but was not delivered to Incident Investigation until July 7, 2004. No violations have been cited. This incident was closed July 7,2004." TX Incident number I-8138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-07-12
40853 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-07-06 10:08 | 2004-07-06 17:16 | 2004-07-06 | GREATER THAN 25% OF THE EMERGENCY SIRENS FOUND TO BE INOPERABLE 26 of 89 of Catawba's sirens failed a low growl activation test at 1008 EDT 07/06/04. Upon activation of the quarterly full cycle test at 1152 EDT 07/06/04, only 3 of the 26 failed to operate properly. Greater than 25% of the sirens were inoperable for more than one hour (one hour and 44 minutes). Investigation is in progress as to determine why the low growl test was unsuccessful. The licensee notified the States of South Carolina and North Carolina of this event. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-07-06
40852 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-07-04 14:30 | 2004-07-05 09:34 | 2004-07-05 | AGREEMENT STATE REPORT REGARDING WELL LOGGING SOURCE ABANDONMENT BY STATE LICENSEE Texas Incident #: I-8136 Event Location: Hidalgo County, Texas(TDH, Public Health Region 11) at the Guerra #25 operated by Edge Petroleum API #: 42-215-33214 On July 4, 2004, the Licensee notified this Agency of the loss of three radioactive sources on a well logging tool-string in Hidalgo County, Texas, at the Guerra #25 well (API # 42-215-33214) operated by the Edge Petroleum Company. The string contained three sources, manufacturer and Serial Nos. are not available at this time. The sources are: 0.8 microcurie Cs-137; 2.5 curie Cs-137; and an 18 curie Am-241/Be. The sources are abandoned in a well with a total depth of 9,034 feet. The top of the tool-string is located at 5,697 feet and fishing attempts have not allowed recovery. A minimum of 200 feet of red tagged cement has been poured to secure the string in place. Negotiations with the Texas Railroad Commission continue for the placement of a deflection device in the well. The Licensee will be ordering a plaque for emplacement on the wellhead. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-07-08
40851 | 0 | NEW YORK CITY BUREAU OF RAD HEALTH |  |  |  |  | 2004-06-30 18:30 | 2004-07-02 15:24 | 2004-07-02 | AGREEMENT STATE REPORT FROM THE NEW YORK CITY BUREAU OF RAD HEALTH On 06/30/04 a portal monitor at JFK airport alarmed. US Customs opened a box from China and found 15 dice and a small cylindrical object (about 24 mm in diameter by 5 mm in height). Three of the 15 dice were found to have a contact radiation reading of 15 millirem per hour. The small cylindrical object outside radiation reading was in the microcurie range. The cylindrical object was found to contain a substance that had strontium-90 mixed in it. The State of New York Health Department after talking with Department of Energy Radiation Assistance Program (RAP) believe that this substance is used to mark dice. The New York City Bureau of Rad Health is continuing their investigation of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NY | OTH | AGR |  |  |  |  | 0 | 2004-07-07
40850 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-07-01 | 2004-07-01 11:09 | 2004-07-01 | STOLEN TROXLER GAUGE The following information was received via e-mail: "Tech was working late and took the gauge home chained to the bed of the pickup. It was last seen at 10:30 p.m. on June 30 and was not there at 5 a.m. July 1. The chain had been cut and the box with the gauge was gone. The keys were not taken. Licensee has been advised to offer a reward for the return of the gauge. Florida is investigating." Additional Information: Florida Incident No: FL04-097 Incident location: 581 Oleander Road Lake Worth, Fl 33462 A.A. Engineering and Testing, Inc. 860 Jupiter Park Drive Jupiter, Fl 33458 Soil Moisture Density Gauge: Troxler Model 3430, S/N 26474 Isotope: Cs-137 (8 millicuries) ; Am-241:Be (40 millicuries). **UPDATE on 07/01/04 at 1530 EDT from Charles Adams (emailed) entered by MacKinnon *** The gauge was found by a citizen who claimed that he had found the gauge last night at a Home Depot. The citizen met a licensee representative at a gas station and traded the gauge for $100. The lock to the case had been cut, but the trigger lock was intact and the gauge was undamaged. Florida continues it's investigation. NRC Region 1( Cliff Anderson), NMSS (Linda Gersey) & TAS (Danis) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-07-06
40849 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-06-30 | 2004-06-30 17:27 | 2004-06-30 | FLORIDA AGREEMENT STATE REPORT - STUCK RADIOGRAPHY SOURCE "Radiography was being performed at a steel fabrication shop when it was determined that the source could not be returned to the shielded position. The source was determined to be at the end of the tube. The camera was dragged to an isolated area and a 2 [milliRem/Hr] boundary was established. The crew (2 men) received about 130 [milliRem] exposure. The lab manager was called and responded. The guide tube was disconnected and the source shook from the tube. Using 4 [foot-long] tongs, the source was replaced in the exposure device. The lab manager received 2 Rem exposure during this process. The crank-to-source connections were subsequently inspected with the Amersham go-no go gauge and found acceptable. Subsequent device operations have been faultless. Florida is investigating." The source is 51.6 Curies of Iridium-192. The radiography camera belongs to Certified Testing Laboratories, Inc. of Orlando, FL. The State of Florida incident number is FL04-094. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-07-05
40848 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-02-27 | 2004-06-30 14:42 | 2004-06-30 | LOUSIANA AGREEMENT STATE REPORT - MEDICAL EVENT The following information was obtained from the Louisiana Department of Environmental Quality: "On February 27, 2004, Woman's Hospital in Baton Rouge, LA ordered a 2 [milliCuries] capsule of I-131 [Iodine-131]. When the dose was sent it was 2.8 [milliCuries] which is greater that 10% of the prescribed dose. A verbal order was given to administer the dose to the patient. Woman's Hospital notified Cardinal Health of the irregularity on March 1, 2004 when they received the dose. The RSO [Radiation Safety Officer] notified the corporate office by fax of the irregularity but that person was not there and it went unnoticed until March 31, 2004. Cardinal Health notified LDEQ [Louisiana Department of Environmental Quality] on March 31, 2004 which was over the ten day limit for notifications. The facility was cited for not notifying LDEQ within ten days. Cardinal Health changed their procedures so that two people are notified of events, and the new pharmacist that made the dose received additional training on policies and procedures." Louisiana State Event Report ID number is LA040006. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-07-05
40847 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2004-05-22 04:29 | 2004-06-30 11:00 | 2004-06-30 | INVALID ACTUATION OF DIVISION 1 PRIMARY CONTAINMENT ISOLATION DUE TO LOSS OF A RPS BUS The following information was received from the licensee via facsimile: "On May 22, 2004, at approximately 4:29 am EDT, while the plant was operating at 100% power, the normal power supply to the Division 1 Reactor Protection System (RPS) bus was lost. This caused the actuation of the Division 1 primary containment isolation logic circuit. This was an event that resulted in the actuation of a general containment isolation signal affecting more than one system. However, as this event meets the definition of an invalid actuation (i.e., not a response to an actual plant parameter exceeding a trip setpoint), this notification is being made in accordance with 10CFR50.73(a)(1) in lieu of a Licensee Event Report. "Operators implemented the applicable response procedures, and shifted Division 1 RPS to its alternate power supply. The containment isolation signal was reset, and systems were restored to normal alignment. Reactor power was not affected by this event. "All safety related equipment controlled by the affected circuits responded to the loss of Division 1 RPS as required, with one exception. The Division 1 control building emergency filtration train should have automatically initiated, but did not. Subsequent troubleshooting discovered a failed relay in its control circuitry. This defect would not have prevented the Division 2 control building emergency filtration train from performing its safety function. "It was determined that a relay coil in the control circuitry for the Division 1 RPS motor-generator set failed. This caused the main output contactor on the MG set to open, interrupting power to the bus. Repairs were completed on June 3, 2004, and the Division 1 RPS bus was then shifted back to its normal power supply." The licensee has notified the NRC Resident Inspector of this notification. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-06-30
40846 | 0 | QUAD CITIES | 1 | 2 |  | [1] GE-3,[2] GE-3 | 2004-06-28 01:47 | 2004-06-28 03:19 | 2004-06-28 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE FELT AT THE SITE "On June 28, 2004 at 0147 CDT, the Control Room was notified that an earthquake was felt on site by Security Personnel. Both units 1 & 2 remain on line and stable with no abnormalities and no physical or structural damage identified. The Plant seismograph DID NOT trigger." An unusual event was declared at 0151 CDT. The licensee notified the NRC Resident Inspector, State and local authorities. NOTE: See related EN#40844 and EN#40845. * * * UPDATE ON 6/28/04 0436 EDT FROM RON RUSTIK TO ARLON COSTA * * * "On June 28, 2004 at 0318 CDT, the Unusual Event has been terminated. A complete tour of all plant vital and protected areas was performed with no physical or structural damage verified. Security performed an inspection of outside areas of plant property and noted nothing unusual." The licensee notified the NRC Resident Inspector, State and local authorities. Notified by e-mail: Susan Frant (IRO), Thomas Kozak (R3 DO), Frank Gillespie (NRR EO), Pat Hiland (Reg3), and Geoffrey Grant (R3). Also notified FEMA (Erwin Casto) and DHS (Andy Akers). | 84 | 85 | 0 | 84 | 85 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-06-28
40845 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2004-06-28 01:21 | 2004-06-28 03:14 | 2004-06-28 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE REGISTERED ON SITE SEISMIC MONITORS At 0111, received a Strong Motion Seismic Alarm and received calls from numerous personnel onsite and offsite that they felt ground motion. A GSEP Unusual Event was declared at 01:21 due to a confirmed seismic event Emergency Action Level HU-4. A walk down of various plant areas including the Dike is in progress to determine if any equipment was affected or damaged. During the event, some spurious alarms were received which cleared with exception of the seismic alarm. The seismic alarm will be reset after Station Engineering reviews the seismic data. They observed a 1" water level spike that immediately returned to normal on main control room suppression pool water level recorder and plant process computer. At this time we have received no reports of equipment damage and walk downs are continuing. The earthquake measured 4.5 on the Richter Scale and was approximately 10 miles north of Ottawa, IL. Ottawa is located 10 miles NW of the site. Both Units remained on line and stable. The NRC Resident Inspector will be notified and the state was notified. NOTE: See related events 40844 and 40846. * * * UPDATE ON 6/28/04 AT 0530 EDT FROM D. COVEYOU TO A. COSTA * * * "This is an update to Event Number 40845. At 0355 CDT the Unusual Event, entered due to confirmed seismic event, was terminated. A walk down of various plant areas has been completed. No equipment damage was identified. The NARS [Nuclear Accident Reporting System] notification for termination was completed at 0405." The licensee notified the NRC Resident Inspector, the State and local authorities. Notified by e-mail: Susan Frant (IRO), Thomas Kozak (R3 DO), Frank Gillespie (NRR EO), Pat Hiland (Reg3), and Geoffrey Grant (R3). Also notified FEMA (Erwin Casto) and DHS (Andy Akers). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-06-28
40844 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-06-28 01:15 | 2004-06-28 03:07 | 2004-06-28 | UNUSUAL EVENT DECLARED DUE TO EARTHQUAKE FELT AT THE SITE "The Station declared an Unusual Event [at 01:30 CDT] due to a felt earthquake and confirmation from other sites. The site seismic recorder did not register an event. No damage has been noted at this time. Inspections will continue." The licensee notified the NRC Resident Inspector and State authorities. NOTE: See related EN#40845 and EN#40846. * * * UPDATE ON 06/28/04 @ 0726 BY RILEY RUFFIN TO C GOULD * * * Plant walk downs were performed and no damage was observed during the walk downs. The UE was terminated at 0555 CDT. The licensee notified the NRC Resident Inspector, the State and local authorities. Notified by e-mail: Susan Frant (IRO), Thomas Kozak (R3 DO), Frank Gillespie (NRR EO), Pat Hiland (Reg3), and Geoffrey Grant (R3). Also notified FEMA (Erwin Casto) and DHS (Andy Akers). | 0 | 98 | 98 | 0 | 98 | 98 | 0 | -1 | -1 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-06-28
40843 | 0 | WHITING CORPORATION |  |  |  |  | 2004-06-26 | 2004-06-26 11:30 | 2004-06-26 | PART 21 NOTICE FOR WHITING CRANES Based on a recent Engineering study of Whiting Crane SN 10698 at Robinson Station we have identified an overstress condition on the slack line load sensing structural frame interior plate welds. This condition is limited to the main hoist of a few redundant (single failure proof) cranes having capacities of 125 tons. They have reviewed trolley drawings for all redundant trolleys and have isolated the problem to 3 Whiting cranes SN 10388, 10389 (Brunswick Station) & 10698 (Robinson Station). Based on their records no other cranes are affected. These cranes must be limited to operating at 59 tons (47% of rated capacity) until the appropriate repairs are made. If customers have a concern related to cranes at their facility or require additional information they can direct their request to whiting-nuclear@whitingcorp.com or to the Whiting Corporation 10 CFR 21 hot line at 708-587-2550. Include your name, title, mailing address, e-mail address, phone #, fax #, Whiting Crane serial number, earliest critical lift date, and any specific requests. The company will reply upon completing any necessary research and based on the dates of the earliest critical lift. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | IL | OTH | PAR | 21.21 |  |  |  | 0 | 2004-06-26
40842 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-06-25 10:50 | 2004-06-26 09:58 | 2004-07-02 | PLANT EXCEEDED LCO ACTION STATEMENT LIMITS "FPL Energy Seabrook is currently in the action statement for Technical Specification 3.3.3.10 due to the inoperability of both Waste Gas Oxygen Monitors. The Oxygen Monitors are currently functional but inoperable. The action statement requires that grab samples be collected at least once per 4 hours. On June 25, 2004 at 10:50 it was recognized that the elapsed time between 2 required samples had exceeded the 4 hour requirement by 30 minutes. Pursuant to the requirements of Facility Operating License No. NPF-86, paragraph 2.G., FPL Energy Seabrook is reporting the late completion of the requirements of an action required by the Station's Technical Specifications. An investigation is being conducted in accordance with the Station's Corrective Action Program." The NRC Resident Inspector will be notified. * * * RETRACTED ON 7/2/04 AT 1257 EDT BY PAUL DUNDIN TO GERRY WAIG * * * "On June 26, 2004, FPLE Seabrook reported to the NRC (event # 40842) that 4 hours and 30 minutes elapsed between obtaining waste gas system grab samples required by the action statement of TS 3.3.3.10 for inoperable waste gas oxygen monitors. Since the action statement requires obtaining grab samples every 4 hours, this condition was considered reportable under paragraph 2.G of the facility-operating license. "Following further review of this condition, FPLE determined that the requirements of the action statement were met. The oxygen concentration of the waste gas system was monitored and recorded in station logs within the required 4-hour interval. As a result, FPLE Seabrook is retracting the 24-hour notification of June 26, 2004." The licensee has notified the NRC Resident Inspector. Notified R1DO (Clifford Anderson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW | [5 empty] | 0 | 2004-06-26
40841 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-06-25 13:10 | 2004-06-25 21:15 | 2004-06-28 | AGREEMENT STATE REPORT - LOST TROXLER GAUGE The following was emailed from the CA Department of Health Services: "On June 25, 2004, one of the gauge users stopped at a gas station [in Encinitita, CA] to get gas. The gauge user came out of the gas station building to find his truck had been stolen with the gauge in the back of the truck inside a camper top. The gauge was inside the case. The case was secured to the bed of the truck by a chain that had been passed through the case handle and returned back to the tie down. The case was latched and locked, the gauge handle was locked with a key lock secured through the gauge handle. A police report was filed with the San Diego County Sheriff's office. A notification and reward will be given to the local paper. The gauge user was asked to notify us immediately if the truck and gauge were recovered. The gauge is a Troxler model 3411B, serial number 5275, containing 8 mCi [milliCuries] Cs-137 and 40 mCi [milliCuries] Am241:Be sources. The gauge was last leak tested on 5/16/04, with no excessive leakage detected." CA Report number 032504 Emailed to TAS (Hahn) and faxed to Mexico's national Commission of Nuclear Safety and Safeguards. * * * UPDATE 1640 EDT ON 6/28/04 FROM ROBERT GREGER TO S. SANDIN * * * The following update was provided via email: "This stolen gauge was recovered unharmed, along with the vehicle in which it was being transported at the time of its theft. We received the report of the recovery this morning from the licensee." Notified R4DO Jack Whitten) and NMSS (Roberto Torres). Emailed and faxed update to Mexico's national Commission of Nuclear Safety and Safeguards. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-06-30
40840 | -1 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-06-24 15:00 | 2004-06-24 18:52 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * REMOVABLE SURFACE CONTAMINATION GREATER THAN THE LIMITS Nuclear Fuel Services (NFS) received a shipment of natural uranium [DELETED] from CAMECO [DELETED]. When the receipt survey was begun, one of the 55-gallon drums was found to be contaminated on the bottom. The survey result was 455 disintegrations per minute (DPM)/100 square centimeters. [The limit is 220 DPM/100 sq cm.] Access to the drum was restricted by placing it into a roped off area. The remaining drums are being surveyed. [DELETED] drums were received and four have been surveyed. Access to all of the drums has been restricted until they are surveyed. Since the contamination was found after the delivery truck had been released, the consignor has been notified of the event and has been requested to check the truck for contamination. The licensee notified the NRC Resident Inspector and the State of Tennessee. * * * RETRACTED ON 7/1/04 AT 1641 EDT FROM GILBERT ROSENBERGER TO GERRY WAIG * * * "Nuclear Fuel Services, Inc. (NFS) wishes to withdraw the Notification of an Event which was made on June 24, 2004 at 1852 hours. The event number was #40840. "The immediate event notification was made because NFS' procedure required an immediate notification in the event a package was received and was found to be contaminated in excess of 220 DPM/100 square centimeters of alpha activity. This procedure was intended to implement the requirements of 10 CFR 20.1906(d)(1). "The material involved in this event was natural uranium, which is a low toxicity alpha emitter as defined by 49 CFR 173.403. 49 CFR 173.443, which is referenced by 10 CFR 71.87(i) which in turn is referenced by 10 CFR 20.1906(d)(1), gives the non-fixed radioactive wipe limit for this material as 22 DPM/square centimeter. This limit converts to 2,200 DPM/100 square centimeters of alpha activity, which is considerably more than the 455 DPM/100 square centimeters of alpha activity which precipitated this incident. A repeat survey confirmed this contamination level and found no other elevated shipping packages. "To prevent a recurrence of this notification, NFS is revising procedure NFS-HS-A-50, rev. 12 to provide a differentiation between alpha emitters and low-toxicity alpha emitters. The licensee has notified the NRC Resident Inspector (via email and voice mail) and the State of Tennessee. Notified R2DO (Carolyn Evans) and NMSS EO (Scott Moore). * * * UPDATE 05/11/08 BY J KOZAL* * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | TN | FUE |  | 20.1906(d)(1) |  |  |  | 0 | 2008-05-11
40839 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2004-06-24 | 2004-06-24 15:47 | 2004-06-24 | AGREEMENT STATE REPORT - TRACTOR TRAILER LEAKING RADIOACTIVE MATERIAL The following was sent via facsimile from the North Carolina Department of Environment and Natural Resources: "At approximately 1:00 PM on June 24, 2004 the NC Radiation Protection Section received notification of an ongoing radiological event in Henderson County NC. A tractor trailer truck carrying Uranium Nitrate Hexahydrate Solution was identified as leaking material at a reported 10-20 drops per hour. The leak was discovered at a DMV weigh station and appropriate action has been taken including response by local Haz Mat Teams. Radiological readings at the site have been reported as a maximum of 0.3 mr/hr and the background was reported to be 0.03 mr/hr. The spill is considered isolated and contained and the highway remains open. No contamination of individuals is suspected. The ongoing event is being investigated by multiple organizations including State Law Enforcement, NC Radiation Protection Section, US Nuclear Regulatory Commission, local Haz-Mat teams and others. The responsible party -the shipper- has dispatched a response team from Knoxville, TN and is expected to be on site by approximately 3:00 PM on June 24 to begin corrective action and recovery procedures." NC Incident No. 04-22. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2004-06-29
40838 | 0 | AGILENT TECHNOLOGIES |  |  |  |  | 2004-05-24 | 2004-06-24 12:13 | 2004-06-24 | LOSS OF NICKEL-63 SOURCE On March 18, 2004, Agilent Technologies of Wilmington, DE shipped a 15 milliCurie Nickel-63 (Ni-63) source to their Germany distribution center for shipment to the end-user, AVT McCormick in Cochin, India. The package was shipped out of the Germany distribution center via Air Express on April 12, 2004. When the package was received by the end-user, the source could not be found in the package. According to the end-user, the package received did not have any damage or indication of being opened previously. The sealed source was for an electron capture detector. Nickel-63 is a beta emitter. The licensee has notified Region 1 (Modes). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DE | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-06-24
40837 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-06-23 17:00 | 2004-06-23 19:36 | 2004-06-24 | UNANALYZED CONDITION RELATED TO FIRE PROTECTION CABLE SEPARATION "This is being reported under 50.72(b)(3)(ii) - Unanalyzed Condition, 50.72(b)(3)(v) - event or condition that could have prevented fulfillment of a safety function, and Catawba License Condition 2F - violation of License Condition 2.C.5 - Fire Protection Program. This report applies to Catawba Unit 2. "On 6/23/04 an original design deficiency related to fire protection cable separation criteria was discovered. The condition relates to a postulated fire in the 'A' Train 4160 Volt Essential Bus switchgear room (ETA). The 'A' and 'B' Train Volume Control tank (VCT) outlet valves are in series providing the normal suction source for the centrifugal charging pumps (standard Westinghouse design). Cables related to the 'A' Train Volume Control Tank outlet valve are in the same fire area as the switchgear for the 'A' Train centrifugal charging pump. Therefore, if a hot short closes the VCT outlet valve, with the 'B' pump running, both centrifugal charging pumps could be rendered inoperable. "Additional switchgear related to component cooling, and power cables for our Standby Shutdown Facility (backup reactor coolant pump seal cooling), are also located in this fire area. An all consuming fire scenario in ETA Switchgear Room could cause a temporary loss of seal cooling to at least 2 of 4 reactor coolant pumps. The actual distance between the ETA switchgear and SSF cables is approximately 20 ft; therefore the probability of an actual fire resulting in a loss of seal cooling is very low. "The unanalyzed condition only exists when the 'B' centrifugal charging pump is in operation (both units currently have 'A' centrifugal charging pump in operation). "This situation is analogous to a degraded fire rated assembly such that an all consuming fire in one area would affect multiple trains of safe shutdown equipment. Per our Fire Protection Program we are establishing appropriate fire watches as a remedial action until the issue is resolved. "Catawba is currently evaluating if a similar concern exists on Unit 1. A follow-up report will be issued if necessary." The licensee will notify the applicable counties and states and has notified the NRC Resident Inspector. * * * UPDATE FROM McCONNELL TO GOTT AT 1636 ON 6/24/04 * * * "On 6/23/04 an original design deficiency related to fire protection cable separation criteria for Unit 2 was discovered. "The report stated that Catawba was evaluating if a similar concern existed on Unit 1 and that a follow-up report would be issued if necessary. "A similar but slightly different condition exists on Unit 1. For Unit 1 the Standby Shutdown Facility (backup seal cooling) cables go through the Train "B" 4160 Essential Switchgear Room (1ETB) rather than 2ETA on Unit 2. This means that for Unit 1, an all consuming fire scenario in 1ETB Switchgear Room could cause a temporary loss of seal cooling. "This situation is analogous to a degraded fire rated assembly such that an all consuming fire in one area would affect multiple trains of safe shutdown equipment. Per our Fire Protection Program we are establishing appropriate fire watches as a remedial action until the issue is resolved." Notified R2DO (Haag) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) |  |  | 0 | 2004-06-23
40836 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-06-23 14:25 | 2004-06-23 19:05 | 2004-06-23 | OFFSITE NOTIFICATION AND MEDIA INTEREST IN FIRE IN CAFETERIA At 1425 PDT, a grease fire started in the cafeteria which is in the protected area. The fire was extinguished by onsite fire fighting personnel. The fire reflashed and was again extinguished. Due to the reflash, the California Department of Forestry was notified for offsite fire assistance. Offsite fire fighting personnel responded. There were no injuries. There has been one media inquiry. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-06-23
40835 | 0 | AGERE SYSTEMS |  |  |  |  | 2004-05-23 | 2004-06-23 10:52 | 2004-06-23 | THE LICENSEE IS MISSING 2 TRITIUM EXIT SIGNS Agere Systems reported they are missing two Safetylite Corp Tritium exit signs model SLX 60 with current calculated activity of 6.8 curies each. The signs were last seen 12/03 when they were removed from their location at the Reading PA. facility and placed in a secure area at that site. This site is being closed and while performing inventory the licensee discovered the 2 signs missing approximately 5/23/04. Construction workers, however, did have access to the area and it is assumed that the signs may have been discarded or taken by the construction workers. The licensee has made and still making a complete search of the facility and posting signs for the return of the signs. Region 1 has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-06-23
40834 | 0 | POTOMAC HOSPITAL |  |  |  |  | 2004-06-21 12:15 | 2004-06-22 16:49 | 2004-06-22 | MEDICAL EVENT Thallous Chloride (4 mCi of Tl-201) was injected into a patient without a prescription. A technician asked the patient before administering the dose if he/she was the person on the prescription. The patient responded positively. The technician administered the dose to the patient without checking the patient's wrist-band identification to confirm the patient's identity. The Thallous Chloride was prescribed to a different patient in preparation for an X-ray examination of the heart. The physician notified the patient that he/she inadvertently received a 4 mCi dose of Thallous Chloride. The physician determined that no medical treatment was required to treat the effects of the misadministered dose. The technician has received counseling, a copy of the hospital's identification policy, and a written warning as a corrective measures action. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 1 | VA | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2004-06-22
40833 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-06-22 09:00 | 2004-06-22 15:25 | 2004-06-22 | HIGH PRESURE COOLANT INJECTION SYSTEM INOPERABLE DUE TO MAINTENANCE "On June 21, 2004, at approximately 0830 hours, testing of High Pressure Coolant Injection (HPCI) system instrumentation commenced per Maintenance Surveillance Test 2MST-HPC128R, 'HPCI Reactor Water Level Channel Calibration And Functional Test.' At 0900 hours, it was determined that the instrumentation would require corrective maintenance and Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.5.1, 'Emergency Core Cooling System (ECCS) Instrumentation,' Condition C was entered for HPCI system Reactor Vessel Water Level - High instrument channel 2-B21-LTN017B-2. Required Action C.2 of TS LCO 3.3.5.1 provides 24 hours for the channel to be returned to operable status. On June 22, 2004, at 0900 hours, the instrument channel was not returned to operable status due to continuing maintenance activities to calibrate the channel. Therefore, Condition G of TS LCO 3.3.5.1 (Required Action and associated Completion Time of Condition C not met) was entered and the High Pressure Coolant Injection (HPCI) system was declared inoperable in accordance with TS LCO 3.3.5.1 Required Action G.1. "TS LCO 3.5.1. "ECCS - Operating," Condition D was entered for the HPCI system being declared inoperable. The Reactor Core Isolation Cooling (RCIC) system was verified operable per Required Action D.1. Required Action D.2 of TS LCO 3.5.1 requires the HPCI system to be returned to operable status within 14 days. The [NRC] Resident Inspector has been notified. "The initial safety significance of this condition is considered to be minimal. The HPCI System is still available during maintenance activities. The RCIC system, as well as all other required ECCSs, are operable at this time. "Maintenance activities and post maintenance testing were completed at 14:55 on June 22, 2004 allowing the HPCI System to be restored to an operable status." | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-06-22
40832 | 0 | LIMERICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-06-22 13:13 | 2004-06-22 15:10 | 2004-06-22 | AUTOMATIC REACTOR SCRAM FOLLOWING AN ELECTRICAL YARD MANIPULATION "Unit 2 reactor scrammed at 13:13 [EDT] following an electrical yard manipulation. The reactor scram occurred as a result of an RPS [Reactor Protections System] actuation following an automatic trip of the main turbine from a generator lockout. All control rods inserted [fully]. The plant is stable [in mode 3]. No ECCS [Emergency Core Cooling System] or safety relief valve actuations have occurred. This report is being made pursuant to 50.72(b)(2)(iv)(b). At this time the plant is stable, as expected. An investigation is in progress to determine the reason for the electrical fault." All plant systems functioned as required and decay heat removal is being performed via bypass to the main condenser. The licensee notified local and State authorities and the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-06-22
40831 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2004-06-21 18:00 | 2004-06-22 10:58 | 2004-07-08 | MISSISSIPPI AGREEMENT STATE REPORT: TROXLER GAUGE RUN OVER BY A BULLDOZER. On 06/21/04 at 1800 CDT an Alabama licensee, Gallet Associates, had one of their Troxler gauges; Model # 3401, gauge serial number 12283; run over by a bulldozer in Flowood, Mississippi. The rod was broken off. Surveys taken of the rod was 10 mRem/hr at one foot. The gauge has been stored and the licensee will call Troxler. The gauge contained 8.6 milliCuries of Cesium-137 and 40 milliCuries of Am-241/Be. State of Mississippi assigned event for this incident is MS-04-005 * * * UPDATE VIA EMAIL FROM B. SMITH TO JEFF ROTTON AT 1205 EDT ON 07/08/04 * * * "Damaged gauge and Cesium-137 source picked up by AEA Technology (QSA) from Mississippi Division of Radiological Health office for transport back to AEA facility located in Baton Rouge, LA. AEA will handle disposal of sources." Notified R1DO (Holody) and NMSS EO (Essig). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2004-06-25
40828 | 0 | BROWNS FERRY |  |  | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2004-06-18 12:04 | 2004-06-18 16:31 | 2004-06-18 | OFFSITE NOTIFICATION - EMPLOYEE FATALITY The following information was obtained by the Licensee via facsimile: "A TVA employee at Browns Ferry Nuclear Plant was transported by ambulance to Athens-Limestone hospital, where he was later pronounced dead after becoming ill at work on Friday, June 18, 2004. The employee was part of a team of engineers inspecting a motor control unit inside the Unit 3 Reactor Building when he complained of shortness of breath. Emergency medical personnel in Browns Ferry's Fire Operations organization were called to respond and transferred the employee to the Athens-Limestone hospital ambulance service, which took him to the hospital in Athens. The engineering team was taking photographs and thermal images of the motor control unit while it was in operation. The medical emergency was not related to the operation of Unit 3 reactor. "This event is being reported pursuant to 10CFR 50.72(b)(2)(xi) as 'Any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made. Such an event may include an onsite fatality or inadvertent release of radioactively contaminated materials'." The employee was not contaminated. The Licensee has notified OSHA. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-06-18
40827 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2004-06-18 06:50 | 2004-06-18 07:48 | 2004-06-21 | UNUSUAL EVENT DECLARED DUE TO A MAIN TRANSFORMER FIRE LASTING FIRE LONGER THAN 10 MINUTES. Main transformer fire caused a load rejection/automatic reactor scram. All rods fully inserted into the core. Offsite power is being supplied through their startup transformers. Offsite fire department, Vernon, responded with three fire trucks and one ambulance. Main transformer fire was extinguished at 0751 EDT. There were no personnel injuries. All emergency core cooling systems and their emergency diesel generators are fully operable if needed. Reactor vessel water level is being maintained at its proper level via the condensate and feedwater system. Both recirculation pumps tripped. Licensee is looking into the reason why the recirculation pumps tripped. There was no release of radioactivity from the plant. Licensee notified the states of New Hampshire, Vermont , Massachusetts and local surrounding counties of the declaration of an unusual event. The NRC Resident Inspector was on scene when the event occurred. * * * UPDATE FROM LAURIE TKACZYK TO JEFF ROTTON AT 1301 HRS. EDT ON 06/18/04 * * * At 1245 hrs. EDT, the Licensee terminated the Unusual Event. The basis for the termination was that the fire is out, a reflash watch is established and the plant is stable. The hydrogen in the generator is depressurized and the plant is currently purging the generator with carbon dioxide. The licensee has notified the NRC Resident Inspector. The Headquarters Operations Officer has notified R1DO (Dimitriadis), NRR EO (Reis), FEMA, DHS, DIRO (Wessman), HQPAO (Gagner), DIRO (Andrews), R1 (Blough and Wiggins). * * * CLARIFICATION TO INITIAL EVENT NOTIFICATION FROM DAVID HALLONQUIST TO HOWIE CROUCH AT 1402 HRS. EDT ON 6/21/04 * * * The Licensee has amended the initial report statement: "There was no release of radioactivity from the plant." to read "There was no release of radioactivity related to this event". The licensee has notified the NRC Resident Inspector. Headquarters Operations notified R1DO (Dimitriadis) and NRR EO (Reis). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | VT | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-06-18
40826 | 0 | YANKEE ROWE | 1 |  |  | [1] W-4-LP | 2004-06-17 12:40 | 2004-06-17 15:53 | 2004-06-17 | OFFSITE NOTIFICATION TO VERMONT DEPARTMENT OF PUBLIC SAFETY Three 55 gallon drums of sand, each impregnated with 1.73 microCuries Cs-137, were shipped to Yankee Rowe from Atlanta, Georgia via Federal Express. The specific activity of the material is 32 picoCuries per gram. Upon arrival at Yankee Rowe, a hole in one of the drums was noticed and about 70 pounds of sand was determined to be missing. About 3 pounds of material was recovered from the shipping truck. The hole appeared to be caused by a fork lift puncture. The specific activity of the material is less than the Department of Transportation reportable quantity. Yankee Rowe contacted state of Vermont and notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-06-17
40825 | 0 | RUTLAND REGIONAL MEDICAL CENTER |  |  |  |  | 2004-06-07 | 2004-06-17 13:47 | 2004-06-17 | MEDICAL EVENT A 19 year old female was diagnosed with Grave's Disease of the thyroid. Consultation with an authorized user (a physician) was requested for consideration of Iodine-131 ablation of her thyroid gland. After this consultation, the patient wished to undergo radioactive iodine ablation of her thyroid gland. The physician completed a prescription in which his written directive was an order for 12 microCuries of Iodine-131. The word "micro" was written using the Greek alphabet letter. The technologist ordered 12 milliCuries of Iodine-131. The technologist received 12.5 milliCuries and this amount was administered orally on 4/7/04. The licensee became aware of this misadministration on 6/7/04 during their quarterly quality maintenance review. The licensee's review of this case with the physician revealed that his intent was to have ordered a 12 milliCurie dose. The physician wrote microCurie by mistake, as a microCurie dose would have been inappropriate for the clinical indication. There were no untoward affects from this administration. At this time, it is not known if the patient has been notified. Licensee RSO will provide that information at a later time. The licensee has reviewed this case and the sequence of events. The following action has been taken. The preprinted prescription form was modified such that after the blank where the authorized user enters the name of the isotope and the dose, the words "microCurie" and "milliCurie" will be written next to each other. The authorized user will need to circle one of the choices. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-06-17
40824 | -1 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-06-17 05:21 | 2004-06-17 06:17 | 2004-10-28 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE While changing out a light bulb in the Unit 1 HPCI room, the surveillance operator noticed that the bolts for the HPCI pump discharge check valve, 1E41-F005, bonnet on pressure seal were loose. All six bolts could be turned by hand. HPCI was declared inoperable until an investigation is performed. The bolts were properly torqued and HPCI pump run is complete and sat. Licensee entered Technical Specification 3.5.1 (14 day Limiting Condition of Operation). All other Emergency Core Cooling Systems are fully operable including the Reactor Core Isolation Cooling System. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION FROM DISMUKE TO CROUCH AT 1700 EDT ON 10/28/04 * * * The following information was obtained from the licensee via facsimile: "A subsequent investigation revealed that a hot torque of the Unit 1 HPCI pump discharge check valve (1E41-F005) was performed during the 165 psig pump operability surveillance test which was performed following reassembly during the Unit 1 refueling outage. During this surveillance, the pump discharge pressure and thus internal pressure on the pressure seal cover, is maintained between 265 and 305 psig. However, during the rated pressure run, the pump discharge pressure achieved is required to be greater than or equal to 1135 psig. This difference in internal pressure (1135-305 = 830 psig minimum), acting on the bottom of the pressure seal cover, forced the pressure seal cover to move upward toward the cover retainer, compressing the pressure seal more tightly. As the pressure seal cover moved toward the cover retainer, the retainer bolts also moved upward, but the cover retainer remained stationary, due to gravity. Therefore, the retainer bolts were no longer torqued against the retainer cover, creating the 'as found' condition. It is site and vendor (Flowserve) experience that once the pressure seal cover is wedged upward, sufficient friction exists between the pressure seal cover, the pressure seal, and the valve body to prevent the pressure seal cover from relaxing the sealing force on the pressure seal once the valve internal (system) pressure is removed. Furthermore, no gap existed between the head of any of the retainer bolts and the retainer cover. The sealing function of the pressure seal was never lost, and the valve would have performed its design function while the retainer bolts were in the 'as found' 'finger tight' condition. Therefore, the valve remained operable at all times when the HPCI system was required to be operable following the Unit 1 refueling outage. This was further substantiated by the fact that no leakage was observed during the rated pressure pump operability run on 3/14/04. Following discovery of the 'finger tight' condition, the retainer bolts were cold torqued to the appropriate value (370 ft-lbs) by Maintenance personnel on 6/17/04. A HPCI pump surveillance was then performed and a hot torque of 370 ft-lbs was performed immediately after the system was shutdown. "Tampering was considered as a possible cause for the loosened bolts, but no evidence could be found to support these bolts being loosened intentionally. All evidence available suggests that the bolts were loosened by internal pressure, which is consistent with vendor experience. "Based on the above information this event is not reportable, and this notification serves to withdraw the previous notification made on 6/17/2004." The licensee has notified the NRC Resident Inspector. The Headquarters Operations Officer notified R2DO (Bonser). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-06-17
40823 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-06-17 00:22 | 2004-06-17 03:38 | 2004-06-17 | TECH SPEC REQUIRED PLANT SHUTDOWN DUE TO EMERGENCY CORE COOLING SYSTEM INOPERABLE At 0338 EDT on 06/17/04, the licensee reported that at 0321 EDT on 06/14/04, the licensee identified that the Salem Unit 1 #12 charging pump was declared inoperable due to an inoperable discharge check valve. Repairs to the check valve are not expected to be completed by 0321 EDT on 06/17/04. At 0022 EDT on 06/17/04, the licensee commenced a shutdown of Salem Unit 1 from 100% power to comply with Tech Spec 3.5.2, Emergency Core Cooling System Inoperable (72 hour LCO). #15 service water pump and #11 auxiliary building exhaust fan have been declared inoperable for scheduled maintenance. There were no personnel injuries or radiological occurrences associated with this event. This event has no effect on Salem Unit 2 which is at 100% power. The licensee notified the NRC Resident Inspector and plans to notify State and Local officials. | 48 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-06-17
40822 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-06-16 14:59 | 2004-06-16 18:27 | 2004-06-16 | EMERGENCY SIRENS INADVERTENTLY ACTIVATED During a weekly growl test of the Point Beach Nuclear Plant (PBNP) emergency sirens on June 16, 2004, the Manitowoc County sirens were inadvertently activated at 1459 CDT. PBNP is investigating the cause of this event. The sirens were activated for approximately one minute. As a result of the inadvertent actuation, the Village of Mishicot, the City of Two Rivers, Manitowoc County, and Kewaunee County, Wisconsin were notified. There was no impact to the plant as a result of the activation of the sirens. The alert notification system remains operable. This report is being submitted in accordance with 10 CFR 50.72(b)(2)(xi) as a result of the notifications made. The Resident Inspector was notified | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-06-16
40821 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2004-06-16 14:00 | 2004-06-16 15:52 | 2004-08-16 | 24 HOUR NOTIFICATION OF PLANT EXCEEDING ITS POWER LIMIT At 1400 hours on June 16, 2004, it was confirmed that the plant had operated in excess of its licensed maximum power limit of 3758 megawatts thermal by about two (2) megawatts thermal. The power limit was determined to have been exceeded due to a feedwater temperature RTD being replaced on May 24, 2004, without having installed a matching transmitter. This error caused a non-conservative input into the core power calculation resulting in a small error. The error allowed the power to be about two (2) megawatts above the limit while indicating that it was within requirements. This condition occurred during two periods on 06/14/04 and 06/15/04. On 06/14/04 the first occurrence lasted for approximately 7 hours. The second occurrence lasted for 16 hours commencing on 06/14/04 and terminating on 06/15/04. The licensee identified this condition on 06/15/04 @ 1130 and the condition was corrected on 06/15/04 @ 1315. This notification is being submitted in accordance with PNPP Operating License Condition 2.F, as a potential violation of the Maximum Power Level specified in PNPP Operating License The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM K Russell to W Gott at 1356 on 8/16/04 * * * "A 24 hour notification was made on June 16, 2004, in accordance with [Perry Nuclear Power Plant] PNPP Operating License Condition 2.F, a potential violation of the maximum power level specified in PNPP Operating License Condition 2.C(1). At the time of discovery, maximum licensed power level was determined to have been exceeded by about 2 megawatts thermal as a result of a feedwater resistance temperature detector (RTD) being replaced without installing a matching transmitter. The feedwater temperature provided by this RTD provides an input to the core power calculation and was initially determined to have caused an error in the calculation of about 3.1 megawatts. "Subsequently, as-found calibration data was taken that determined the RTD loop error was smaller than initially calculated. The resultant error in thermal power was calculated to be 0.1 megawatts. Review of the power history using the recalculated thermal power error resulted in a determination that the maximum licensed power level was not exceeded. Since the maximum licensed power level was not exceeded, this notification retracts ENF 40821. This retraction was discussed with the Resident NRC Inspector." Notified R3DO (Clayton) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW | [5 empty] | 0 | 2004-06-16
40820 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-06-16 09:45 | 2004-06-16 10:11 | 2004-06-16 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY "At 0945 on 6/16/04, the uninterruptible power supply to the Technical Support Center was removed from service for pre-planned maintenance. As a result, the plant Safety Parameter Display System (SPDS) and the Technical Support Center (TSC) computer system are inoperable. This event is a major loss of emergency assessment capability and is reportable under 10CFR50.72(b)(3)(xiii). The expected duration of the maintenance is between 4 and 8 hours." This pre-planned maintenance also made the ERDS inoperable. The Licensee has notified the NRC Resident Inspector. * * * UPDATE ON 06/16/04 @ 1707 BY MIKE GUILL TO C GOULD * * * UPDATE SPDS and the TSC computer were returned to service at 17:04 on 06/16/04. The NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-06-16
40819 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2004-04-25 01:05 | 2004-06-15 09:14 | 2004-06-15 | INVALID SYSTEM ACTUATION "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of specified systems, specifically the Units 2 and 3 Primary Containment Isolation Systems (PCIS). "On 4/25/04, at approximately 0105 hours, the 343SU startup source tripped resulting in a fast transfer of expected 4 kV emergency busses to the alternate offsite power source. The fast transfer resulted in a half PCIS Group II isolation on both Units 2 and 3 as expected. The half isolation of PCIS Group II resulted in outboard isolation valves closing on Unit 2 and inboard isolation valves closing on Unit 3. The isolations involved various PCIS Group II process lines such as Reactor Water Cleanup (RWCU), Containment Atmospheric Control (CAC) / Containment Atmospheric Dilution (CAD) and Containment Instrument Nitrogen. The Units 2 and 3 PCIS isolations were reset by approximately 0130 hours in accordance with procedures. All required isolation valves operated as designed. "The offsite source (343SU) was lost as a result of a ground fault. Subsequent investigation determined that a raccoon had climbed a takeoff tower where the startup source transitions from an aerial line to underground cabling. The associated equipment was located in a small fenced area near the plant. The offsite source was inspected, tested and returned to an operable condition by approximately 2220 hours on 4/25/04. This issue has been entered into the site Corrective Action Program (CR 216811) for evaluation and implementation of further corrective actions." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-06-15
40818 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2004-06-14 07:41 | 2004-06-14 17:14 | 2004-06-14 | LICENSEE DECLARED OFFSITE POWER INOPERABLE DUE TO DIP IN GRID FREQUENCY "On June 14, 2004 at 0741 PDT, the offsite power grid connected to San Onofre experienced a system disturbance. Grid frequency dipped to about 59.7 Hz or slightly lower, and then recovered about three minutes later. Plant Operators declared offsite power inoperable. Southern California Edison is conservatively reporting this event in accordance with 10 CFR 50.72(b)(3)(v)(D). The diesel generators for both Units 2 and 3 were operable during this event. At the time of this report, Units 2 and 3 continue to operate at about 100% power." The NRC Resident Inspector was notified. NOTE: see events 40814, 40815 and 40816 | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-06-14
40817 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-06-14 07:35 | 2004-06-14 13:48 | 2004-06-14 | FAILURE OF SUPERVISOR TO PASS A FITNESS FOR DUTY TEST At 0735 on 06/14/04 a Dominion Virginia Power supervisor tested positive as a result of pre-access Fitness for Duty testing. The NRC Resident Inspector has been notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.73 |  |  |  | 0 | 2004-06-14
40816 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2004-06-14 07:44 | 2004-06-14 11:39 | 2004-06-14 | UNUSUAL EVENT DUE TO REACTOR TRIP DUE TO LOSS OF OFF SITE POWER On June 14, 2004, at approximately 07:44 Mountain Standard Time (MST) all three units at the Palo Verde Nuclear Generating Station experienced automatic reactor trips coincident with a grid disturbance and loss of offsite power in the Palo Verde Switchyard. Unit 3 declared a NOTIFICATION OF UNUSUAL EVENT at 07:53 MST due to a loss of offsite power to essential buses for greater than 15 minutes. The NOTIFICATION OF UNUSUAL EVENT was terminated at 12:07 MST. Unit 3 received an automatic Main Steam Isolation System ESF actuation. Due to the loss of offsite power, the Emergency Plan Technical Support Center (TSC) was unavailable. The Unit 2 Satellite TSC was to be staffed by the Emergency Response Organization in response to the loss of assessment capability. Power to the TSC has since been restored. The unit was at normal operating temperature and pressure prior to the trip. All CEAs inserted fully into the reactor cores. All Emergency Diesel Generators (EDGs) (2 per unit) associated with the unit started as expected in response to the loss of offsite power to their safety buses. The offsite power grid had several perturbations for approximately one hour following the event but has been stable since. LCO 3.8.1, AC Sources - Operating, was entered as a result of this event. Heat removal is to atmosphere via atmospheric dump valves in natural circulation. Main steam safety valves may have lifted for a brief time. Restoration of forced reactor coolant circulation is pending assurance that the offsite power grid can reliably support the load. No major equipment was inoperable prior to the event that contributed to the event. The Unit is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant NRC Resident Inspector was notified. FBI Jeff Muller and Mr. Rosales (Mexican National Commission of Nuclear Safety and Safeguards {CNSNS}) were notified. * * * Update at 1815 @ 06/14/04 * * * Notified Reg 4 RDO (Graves), NRR (Bateman), DHS (Lee), FEMA (Canupp), DOE (Sal Moroni), EPA (Stalcup), EPA (Crews), HSS (Davidson), and Mexico (Rosales) Note: see related events 40815 , 40814 and 40818 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode3: Power Operation; FMode3: Hot Standby | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2004-06-14
40815 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2004-06-14 07:44 | 2004-06-14 11:39 | 2004-06-14 | UNUSUAL EVENT DECLARED DUE TO REACTOR TRIP DUE TO LOSS OF OFF SITE POWER On June 14, 2004, at approximately 07:44 Mountain Standard Time (MST) all three units at the Palo Verde Nuclear Generating Station experienced automatic reactor trips coincident with a grid disturbance and loss of offsite power in the Palo Verde Switchyard. Unit 1 declared a NOTIFICATION OF UNUSUAL EVENT at 07:53 MST due to a loss of offsite power to essential buses for greater than 15 minutes. The NOTIFICATION OF UNUSUAL EVENT was terminated at 12:07 MST. Unit 1 manually initiated a Main Steam Isolation System ESF actuation by procedure. Due to the loss of offsite power, the Emergency Plan Technical Support Center (TSC) was unavailable. The Unit 2 Satellite TSC was to be staffed by the Emergency Response Organization in response to the loss of assessment capability. Power to the TSC has since been restored. The unit was at normal operating temperature and pressure prior to the trip. All CEAs inserted fully into the reactor cores. All Emergency Diesel Generators (EDGs) (2 per unit) associated with the unit started as expected in response to the loss of offsite power to their safety buses. The offsite power grid had several perturbations for approximately one hour following the event but has been stable since. LCO 3.8.1, AC Sources - Operating, was entered as a result of this event. Heat removal is to atmosphere via atmospheric dump valves in natural circulation. Main steam safety valves may have lifted for a brief time. Restoration of forced reactor coolant circulation is pending assurance that the offsite power grid can reliably support the load. No major equipment was inoperable prior to the event that contributed to the event. The Unit is stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant NRC Resident Inspector was notified. FBI Jeff Muller and Mr. Rosales (Mexican National Commission of Nuclear Safety and Safeguards {CNSNS}) were notified. * * * Update at 1815 @ 06/14/04 * * * Notified Reg 4 RDO (Graves), NRR (Bateman), DHS (Lee), FEMA (Canupp), DOE (Sal Moroni), EPA (Stalcup), EPA (Crews), HSS (Davidson), and Mexico (Rosales) Note: see related events # 40814, 40816 and 40818 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 4 | AZ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2004-06-14
40814 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2004-06-14 07:44 | 2004-06-14 11:39 | 2004-06-14 | ALERT DECLARED - REACTOR TRIP DUE TO LOSS OF OFF SITE POWER On June 14, 2004, at approximately 07:44 Mountain Standard Time (MST) all three units at the Palo Verde Nuclear Generating Station experienced automatic reactor trips coincident with a grid disturbance and loss of offsite power in the Palo Verde Switchyard. Unit 2 declared an ALERT Emergency Plan classification at approximately 07:54 due to a loss of AC power to essential buses reduced to a single power source for greater than 15 minutes such that any additional single failure would result in a station blackout. Subsequently, at 09:51 Unit 2 downgraded the Emergency Plan classification to a NOTIFICATION OF UNUSUAL EVENT when AC power was restored from a single essential bus to both essential buses. Units 1 and 3 declared a NOTIFICATION OF UNUSUAL EVENT at 07:53 MST due to a loss of offsite power to essential buses for greater than 15 minutes. The NOTIFICATION OF UNUSUAL EVENT was terminated for all 3 units at 12:07 MST. Unit 1 and 2 manually initiated a Main Steam Isolation System ESF actuation by procedure. Unit 3 received an automatic Main Steam Isolation System ESF actuation. Due to the loss of offsite power, the Emergency Plan Technical Support Center (TSC) was unavailable. The Unit 2 Satellite TSC was to be staffed by the Emergency Response Organization in response to the loss of assessment capability. Power to the TSC has since been restored. The Emergency Plan ALERT declaration includes staffing of the Joint Emergency New Center to address expected media interest. All three units were at normal operating temperature and pressure prior to the trip. All CEAs inserted fully into the reactor cores. All Emergency Diesel Generators (EDGs) (2 per unit) associated with each of the 3 units started as expected in response to the loss of offsite power to their safety buses. Unit 2's train "A" EDG started, but did not indicate volts or amps and was manually shutdown. The offsite power grid had several perturbations for approximately one hour following the event but has been stable since. LCO 3.8.1, AC Sources - Operating, was entered in each unit as a result of this event. Heat removal is to atmosphere via atmospheric dump valves in natural circulation. Main steam safety valves may have lifted for a brief time. Restoration of forced reactor coolant circulation is pending assurance that the offsite power grid can reliably support the load. No major equipment was inoperable prior to the event that contributed to the event. All 3 units are stable at normal operating temperature and pressure in Mode 3. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant NRC Resident Inspector was notified. FBI Jeff Muller and Mr. Rosales (Mexican National Commission of Nuclear Safety and Safeguards {CNSNS}) were notified. * * * Update at 1815 @ 06/14/04 * * * Notified Reg 4 RDO (Graves), NRR (Bateman), DHS (Lee), FEMA (Canupp), DOE (Sal Moroni), EPA (Stalcup), EPA (Crews), HSS (Davidson), and Mexico (Rosales) NOTE: See events 40815, 40816 and 40818 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | OFFSITE NOTIFICATION | VALID SPECIF SYS ACTUATION | IMode2: Power Operation; FMode2: Hot Standby | ALERT | 4 | AZ | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(xi) | 50.72(b)(3)(iv)(A) | 0 | 2004-06-14
40813 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2004-06-14 06:26 | 2004-06-14 10:56 | 2004-06-14 | FAILED DATA SERVER FOR EMERGENCY RESPONSE DATA SYSTEM "At 0626 [CST] on June 14, 2004; the Plant Data System (PDS) data server for the NRC Emergency Response Data System (ERDS) link was found to have failed at 0204 on June 11, 2004. The data server was rebooted, PDS software initiated and ERDS capability restored at 0745 on 6/14/04. Total time out of service was 3 days, 5 hours and 41 minutes." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-06-14
40812 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2004-06-14 | 2004-06-14 10:13 | 2004-06-14 | ILLINOIS AGREEMENT STATE REPORT - SOURCE MISSING IN SHIPMENT One of five packages being shipped on 6/3/04 from Honeywell Corporation in Phoenix, AZ did not arrive at the licensee's facility as scheduled on 6/4/04. The package consisted of a 7-10 gallon steel drum containing 10 Curies of Pm-147 as sealed sources. The sources were removed from industrial gauging devices being disposed of. * * * UPDATE ON 6/14/04 AT 1542 EDT FROM D. PERRERO TO A. COSTA * * * Fed-Ex located the missing shipment in Pittsburgh and arrangements are being made to forward it to ADCO Services Inc, at Tinley Park, IL. Notified NMSS (Essig), R3DO(Louden) and TAS (Whitney). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2004-06-17
40811 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2004-06-12 20:29 | 2004-06-13 02:23 | 2004-06-13 | EMERGENCY DIESEL STARTED AND LOADED ON BUS UNDERVOLTAGE SIGNAL "At 2029 on 6/12/2004, the normal incoming feed (1DA) to the plant opened on an undervoltage signal. At the time of the event a severe thunderstorm was in progress. The 'A' Emergency Diesel Generator started and loads sequenced on as designed. The 'A' Residual Heat Removal pump started but did not inject any water into the Reactor Coolant System. The 'A' Emergency Feedwater Pump started and ran for approximately seven minutes. Other plant equipment also responded as expected. "The plant transferred back to offsite power at 2252. A follow-up LER will be provide in 60 days." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-06-13
40809 | 0 | GARDIAN AUTOMOTIVE INC |  |  |  |  | 2004-06-11 | 2004-06-11 15:54 | 2004-06-11 | LOST OR STOLEN POLONIUM - 210 STATIC ELIMINATOR On 6/11/04 a Polonium - 210 static eliminator source was reported missing by the user of the source in Indiana. The source is 1.3 millicurie (current activity determined by the licensee, NRD) and was last used on 5/13/04 in a paint spray application. The source was received by the user on 5/15/03. The user has reviewed the "tracking form" and has interviewed employees in an unsuccessful effort to locate the source. The user notified the source licensee, NRD, 2937 Alt Ave, PO Box 310, Grand Island, NY 14072 of the missing source on 6/11/04. The user has implemented a once-per-shift verification check sheet to maintain accountability of their other static sources. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IN | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-06-11
40808 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-06-11 15:10 | 2004-06-11 16:01 | 2004-06-11 | OFFSITE NOTIFICATION OF OIL LADEN WATER INTO STORM DRAIN Oil was spilled on the asphalt in the Protected Area and was cleaned up. Recent rains pulled out the percolated oil laden water which entered the storm drain. Less than one gallon of oil entered the storm drain. The source of the oil spill (possibly from a vehicle) is under investigation. The licensee notified the NJ Department of Environmental Protection, National Response Center, Environmental Protection Agency and the U.S. NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-06-11
40807 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2004-06-10 15:00 | 2004-06-11 14:36 | 2004-06-11 | AGREEMENT STATE NC - NOTIFICATION OF EQUIPMENT FAILURE DUE TO METAL FATIGUE "The licensee [Flowserve US Inc.] performing Booth IR has an automatic IR setup that uses source switches to stop the extension of the source for IR operations. The source switch at the end of the guide tube failed and the source [Ir-192] extended beyond the end of the guide tube and got stuck. The licensee contacted Amersham (the manufacturer of the camera) for advice. By following Amersham's suggestions the licensee was able to remotely retract the source back into the guide tube, and from there to retract the source back into the camera in the fully shielded position. The licensee intends to have the source leak tested as soon as possible and said they would submit a complete report within 30 days." No one was injured or overexposed during this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2004-06-16
40806 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-04-12 15:43 | 2004-06-11 12:58 | 2004-06-11 | 60-DAY NOTIFICATION OF INVALID ACTUATION OF SAFETY INJECTION SIGNAL "On April 12, 2004, Salem station made an 8 hr report titled ACCIDENT MITIGATION - COMMON CONTROL ROOM EMERGENCY AIR CONDITIONING SYSTEM per 10 CFR 50.72(b)(3)(v) (Event number 40670). This report was the result of an invalid Unit 1 Safety Injection signal during troubleshooting/testing of Train 'B' of Solid State Protection. During the troubleshooting a card was moved from one slot to another, when the card was inserted into the new slot a safety injection signal was generated. The failed part of the card (a malfunctioning isolator card) was not used in its prior position, thus the failed circuit remained undetected. "Further investigation determined that the safety injection signal was invalid; it was not the result of a plant condition requiring the protective action. Therefore this event is not reportable per 10CFR50.72(b)(3)(iv)(A) 'Any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section, except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.' This event is reportable as it 60-day phone call in accordance with 10CFR50.73(a)(2)(iv)(A)(1) 'Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section, except when: (1) The actuation resulted from and was part of a pre-planned sequence during testing or reactor operation; or (2) The actuation was invalid..' "Licensee event report 311/04-003 is being submitted to report the loss of accident mitigation capability for Unit 2. Event number for reference 40670." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-06-11
40805 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-04-23 05:53 | 2004-06-10 16:37 | 2004-06-10 | PADUCAH GASEOUS DIFfUSSION PLANT - RESPONSE BULLETIN 91-01 24 - HOUR REPORT "At 1550 on 6-09-04, the Plant Shift Superintendent was notified of a failure of a Safety Related Item (SRI) relied upon in Nuclear Criticality Safety Evaluation (NCSE) 052 'Enrichment Cascade During Normal Operations at the Paducah Gaseous Diffusion Plant.' At 0553 hours on 4-23-04, when responding to alarms on Cell 6 in Building C-310, the second bank of motors could not be shut down using the manual motor trip system. Operators opened the Transformer Secondary Breaker (TSB) as an alternate means to shut down the motors. The manual motor trip system is credited to mitigate/minimize the consequences or extent of a Hot Metal Reaction (HMR). "PGDP Problem Report No, ATRC-04-2299; PGDP Event Report No. PAD-2004-17; Event Worksheet [NRC Event Number]: # 40805, Responsible Division: Operations. "SAFETY SIGNIFICANCE OF EVENTS: Minimal. There are multiple methods capable of shutting down equipment suspected of undergoing a HMR. The compressor motors were shut down using one of these methods. The shutdown was accomplished within 2 minutes. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIOS) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to occur, the equipment would have had to be involved In the initiating event of a HMR. There were no indications of a HMR. Additionally, the HMR event would need to have occurred with a significant inventory of UF6 present. The event was in the purge cascade having UF6 concentrations in the ppm range. Therefore, there is no credible pathway to criticality for this incident. "CONTROLLED PARAMETERS (MASS, MODERATION. GEOMETRY, CONCENTRATION, ETC): This scenario is singly contingent based on moderation control. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The event was in the purge cascade having UF6 concentrations in the ppm range at an enrichment of less than [DELETED] wt % 235U. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: This scenario is singly contingent based on moderation control. The scenario indicates that it is unlikely for a significant HMR to occur resulting in a cooler/cascade breach with subsequent sprinkler activation based on historical operations. The manual motor trip system is credited to mitigate/minimize the consequences or extent of a HMR. The credited trip failed to perform its intended function. Although the credited trip failed, alternative methods were used to shutdown the cell, thereby satisfying the intent of the administrative portion of the control. Also, no HMR, cell breach, or sprinkler activation occurred. Although the SRI failed, the moderation parameter was maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The cell was shut down using alternate means within 2 minutes. The manual motor trip system was declared inoperable at 0700 on 4-23-04 and repaired. "The NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-06-10
40804 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-06-10 13:13 | 2004-06-10 16:11 | 2004-06-11 | AUTOMATIC REACTOR TRIP WHILE PERFORMING SCHEDULED SOLID STATE PROTECTION TESTING A Unit 2 automatic reactor trip occurred while the licensee was performing planned periodic testing on train "A" solid state protection. All control rods fully inserted into the reactor core. The Auxiliary Feedwater Pumps automatically started as expected immediately following the reactor trip due to low-low level in the steam generators. The unit is being maintained stable in mode 3 and heat sink is being performed via steam dump to the condensers. All other systems functioned as required. The cause of the reactor trip is under investigation. The licensee notified the NRC Resident Inspector. *** UPDATE ON 6/11/04 AT 12:23 EDT FROM B. BROWN TO A. COSTA * * * "This is an update to event notification 40804. At 1313 hours on June 10, 2004, North Anna Unit 2 experienced an automatic trip from 100 percent during the performance of 2-PT-36.1A (Train 'A' Reactor Protection and ESF Logic Actuation Logic Test). The cause of the reactor trip, was determined to be an incorrect configuration of the cell switch (52h contract) on 'A' Reactor Bypass Breaker, 2-EP-BKR-BYA. The incorrect cell switch configuration resulted in a turbine trip signal being generated during testing which resulted in a reactor trip signal being generated in the 'B' train Reactor Protection System. The Auxiliary Feedwater System actuated in response to the event. "Control room personnel responded to the event in accordance with emergency procedure E-0, Reactor Trip or Safety Injection. The control room team stabilized the plant using ES-0.1 Reactor Trip recovery. The lowest Reactor Coolant System (RCS) pressure during the event was 1988 psig and the lowest RCS temperature was 549 degrees. No human performance issues were identified during this event. "A non-emergency four-hour report was made to the NRC operations center at 1611 hours pursuant to 10CFR50.72(b)(2)(iv)(B) for an actuation of the Reactor Protection System while critical. An eight-hour report was also made to the NRC in accordance with 10CFR 50.72(b)(3)(iv)(A) due to the Auxiliary Feedwater Pump starts (Engineering Safety Features Actuation). The Reactor Protection System, AMSAC [ATWAS Mitigating System Actuation Circuit], and the Auxiliary Feedwater System operated properly in response to the event. During the Unit 2 reactor trip, a blown output fuse on a logic card (that feeds the permissive for arming the Steam Dumps from loss of load) prevented the Main Steam Dump Valves from opening in Tavg Mode as expected. The Steam Generator Power Operated Relief Valves (PORVs) lifted and operated to control RCS temperature until transferring Steam Dump control to the Steam Pressure Mode. The fuse was replaced. "A post trip review was conducted at 1500 hours on June 10, 2004. The cell switches on the Reactor Trip Bypass breakers have been repaired and post maintenance testing has been completed. Management approval was granted to start-up Unit 2. North Anna Unit 2 is currently in Mode 1 and is preparing to be placed on-line." The licensee notified the NRC Resident Inspector. Notified R2DO (Lesser) and NRR EO (Bateman). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-06-10
40803 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-06-09 14:30 | 2004-06-10 13:16 | 2004-06-10 | NEVADA AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE A Campbell Pacific Nuclear Density Gauge, Model #MC-3 (Serial #37117979) containing 50 millicuries Am-241/Be and 10 millicuries Cs-137, was stolen from a transport container in North Las Vegas, Nevada. The transport container was secured in a truck, but the gauge was not locked in the transport case. The licensee notified the North Las Vegas Police Dept. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-06-15
40802 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-06-10 02:05 | 2004-06-10 05:36 | 2004-06-10 | OFFSITE NOTIFICATION MADE DUE TO INADVERTENT EMERGENCY SIREN ACTUATION "One emergency response siren (Number 10 Brunswick County) located in Southport, NC inadvertently actuated at 0205, apparently due to a lightning strike, and was silenced at 0312. The Brunswick County, New Hanover County and North Carolina State Emergency Operation Centers (EOC) were notified of the inadvertent actuation. The Brunswick County 911 Center received calls from local residents reporting the siren actuation. "Initial Safety Significance Evaluation: Minimal safety significance. The loss of the single siren will not significantly impact the public notification system. The remaining sirens in both Brunswick and New Hanover Counties have been verified to be operable. "Corrective Actions: The siren was silenced at 0312 on June 10, 2004. The cause of the inadvertent actuation will be determined and repaired." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 96 | 0 | 100 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-06-10
40801 | 0 | SCI ENGINEERING |  |  |  |  | 2004-06-08 14:15 | 2004-06-09 17:26 | 2004-06-09 | DAMAGED MOISTURE DENSITY GAUGE An equipment operator backed up a vehicle (Bobcat) over a moisture density gauge at a construction project site located near the intersection of White Gate and West Clay streets in Saint Charles, Missouri. The density gauge was damaged but the gauge probe (rod) containing the source was inserted into the ground during the accident. The licensee followed emergency procedures and contacted their contractor to perform radiation surveys of the area. Initial measurements indicate that the sources are not leaking. Further leak tests will be performed on the damaged gauge. The licensee is planning on packaging and shipping the damaged density gauge to the manufacturer. The moisture density gauge is manufactured by Humboldt, series 5001 containing 10 millicuries of Cs-137 and 40 millicuries of Am-241:Be. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2004-06-09
40800 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-06-08 | 2004-06-09 14:43 | 2004-06-09 | MASSACHUSETTS AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE On the afternoon of 06/08/04, a Troxler moisture density gauge (model/serial number not yet known) was run over by a pickup truck at a construction site in Rayham, MA. The source rod was detached but not bent. The area was cordoned off and the licensee RSO was notified. The RSO arrived, positioned the source rod back into the gauge, secured the gauge and performed a radiological survey with negative results. The results of a source leak test are pending. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-06-14
40799 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-06-08 19:00 | 2004-06-09 11:54 | 2004-06-09 | ARKANSAS AGREEMENT STATE REPORT - MISSING AND THEN FOUND MOISTURE DENSITY GAUGE The following information was provided via email: "At 7:00 p.m., June 8, 2004, Materials Testing of Arkansas, Inc., Arkansas Radioactive Materials License Number ARK-859-BP-03-02, notified the Arkansas Department of Health, of a missing Troxler Electronic Laboratories, Inc., Model 3430 moisture density gauge, serial number 26636, containing 44 millicuries of Americium-241: Berylium, and 9 millicuries of Cesium-137. The licensee stated that the gauge had fallen out of the truck during transport from a job site in Conway, Arkansas. "The Conway Police Department, Faulkner County Sheriff's Office, Arkansas State Police and the Arkansas Department of Emergency Management were notified. "At 7:00 a.m., June 9, 2004, Materials Testing of Arkansas, Inc. reported the gauge had been recovered and was being returned to the storage location. The gauge was recovered by another Arkansas Radioactive Material Licensee who secured the gauge overnight. The gauge does not appear to have been tampered with or damaged. "The Department is investigating the incident and will provide follow-up information upon receipt of the licensee's formal notification report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2004-06-14
40797 | 0 | WILLIAM BEAUMONT HOSPITAL |  |  |  |  | 2004-06-08 14:25 | 2004-06-08 17:03 | 2004-06-08 | MEDICAL EVENT AT THE WILLIAM BEAUMONT HOSPITAL IN ROYAL OAK, MI On Tuesday, June 8, 2004 at 2:25 p.m., a patient was scheduled for an I-131 thyroid uptake with an oral dose between 5 and 20 microcurie. Instead, the patient was administered 915 microcurie (34 MBq), which resulted in an absorbed dose of 2675 rad to the thyroid (assuming a 55% radioactive iodine uptake) and 81 rad effective dose equivalent. Each Month the Radiopharmacy prepares an oral solution of sodium iodide I-131 for uptake doses which are pipetted into individual patient dose vials. The sodium iodide I-131 uptake solution for June contained 12 microcurie per milliliter (ml) in a total volume of 300 ml. The Radiopharmacy technologist prepared the uptake dose by pipetting one ml of solution into the patient vial, which, should have yielded a dose of approximately 12 microcurie. The pipette that the Radiopharmacy technologist used to prepare this dose had been used earlier in the day to prepare therapeutic doses of I-131, and was labeled as the therapy pipette. The Radiopharmacy technologist did not realize that she had picked up the pipette labeled for therapy and assumed it was the pipette used for preparing the uptake doses. Usually the uptake pipette is stored in a shielded vial in the far right corner of the fume hood, but in this case, the therapy pipette was located in the far right corner. The Radiopharmacy technologist assayed the dose in the dose calibrator and noted that the reading was too high for an uptake dose. This caused the staff to question which pipette was used, and they confirmed that the therapy pipette was used. The Radiopharmacy staff discarded the dose in accordance with radioactive waste procedures, and proceeded to draw another uptake dose with the pipette labeled for uptakes. One milliliter was drawn and assayed in the dose calibrator and read 0.915 mCi/ml. The Radiopharmacy technologist accepted the dose thinking that it was really 9.15 microcurie instead of 0.915 millicurie. The computer program is set up to accept I-131 uptake doses on the basis of correct volume and since the volume was within the acceptable range of 1 ml, the computer printed a label for the dose and it was dispensed. The nuclear medicine technologist followed the procedure for confirming the dose prior to administration by checking the patient name, ID number, the I-131 uptake procedure and circling the dose. She looked at the dose printed on the label and thought that the dose was 9.15 uCi instead of the what was printed on the label (0.915 mCi), and administered the dose to the patient. The Radiopharmacy technologist became concerned about using the wrong pipette and contacted the Radiopharmacist, who then discovered the error. The therapy pipette contained residual millicurie amounts of therapeutic I-131 solution which contaminated the I-131 uptake dose. B. Why the Event Occurred The root cause was determined to be the lack of an adequate double check of the I-131 uptake dose prior to administration. A pipette contaminated with 2 millicurie I-131 was inadvertently used to prepare the uptake dose. The Radiopharmacy computer was programmed to detect volume errors, but not activity errors, so it accepted the dose and printed the label. The Radiopharmacy technologist did not detect the error when she assayed the dose for this second redraw, because she assumed that the activity displayed 9.15 uCi, rather than the actual activity displayed, which was 0.915 mCi. The nuclear medicine technologist who double checked the dose mistook the 0.9 mCi for 9 uCi on the dose label and administered the dose. She had been working in an imaging room, but was needed to cover the thyroid uptake room near the end of the work shift. This may have contributed to the error made when confirming the dose. C. The Effect on the Patient The absorbed dose to the thyroid was 2675 rad (assuming a 55% radioactive iodine uptake) and the effective dose equivalent was 81 rad. The patient is expected to return to William Beaumont Hospital tomorrow (6/9/04) for treatment with I-131 for hyperthyroidism. The additional dose given for the uptake is a fraction of the dose that will be administered for therapy. The patient is not expected to have any adverse effects. D. What improvements are Needed to Prevent Recurrence A complete investigation was conducted to determine the root cause of the medical event. A new pipette will be used for each I-131 uptake patient dose, which will prevent the cross contamination. The computer will be re-programmed to accept uptake dose activity (ie., 5 - 20 microcurie) rather than volume. The computer will not print a label for the uptake dose unless the activity is within the predefined range. The radiopharmacy staff have been trained not to over-ride the failsafe mechanisms of the computer. The nuclear medicine technologist will be retrained in the dose verification process prior to a dose administration. Both the Radiopharmacy technologist and the nuclear medicine technologist will review the dose units (i.e., microcurie, millicurie, MBq) and pass a test. E. Actions Taken to Prevent Recurrence 1. A new pipette will be used for each I-131 uptake patient dose, which will prevent the cross contamination. 2. The computer will be re-programmed to accept uptake dose activity (i.e., 5 - 20 microcurie) rather than volume. The computer will not print a label for the uptake dose unless the activity is within the predefined range. 3. The nuclear medicine technologist will be retrained in the dose verification process prior to a dose administration. 4. Both the Radiopharmacy technologist and the nuclear medicine technologist will review the dose units (i.e., microcurie, millicurie, MBq) and pass a test. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-06-08
40796 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2004-06-04 13:00 | 2004-06-08 12:33 | 2004-06-08 | ARIZONA STATE LICENSEE REPORTED A MISSING I-125 SEED The State of Arizona has been informed of a missing source by two State Licensees (Walter O. Boswell Hospital lic # AZ-07-138 and Amersham Health lic # AZ-07-346). The missing source is an Iodine-125 seed containing 0.225 millicuries of Iodine-125. The seed was loaded into a shipping container by two employees of Licensee 1. Both employees independently described and certified the loading of the seed into the shipping container. Licensee 2 received the package but did not locate the seed that was supposed to be inside. This is information from the 30 day report, pursuant to Arizona rules equivalent to 10CFR20.2201(a)(ii). The seed was first detected missing April, 18, 2004. The Agency has opened an active investigation into the circumstances of the loss of this seed. Initial surveys at each Licensee failed to locate the missing seed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2004-06-11
40795 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2004-06-07 14:58 | 2004-06-07 20:57 | 2004-06-07 | REACTOR TRIP DUE TO MAIN TURBINE ELECTRO-HYDRAULIC CONTROL SYSTEM FAILURE "On June 7, 2004, at approximately 14:58 Mountain Standard Time (MST) while at 99% RTP [rated thermal power], Palo Verde Unit 3 experienced an apparent electro-hydraulic control (EHC) system fault resulting in Combined Intercept Valve (CIV) closure. This plant upset was followed by a Reactor Power Cutback System (RPCS) initiation. Several seconds later the Reactor automatically tripped on Lo DNBR from approximately 65% RTP. Unit 3 was at normal temperature and pressure prior to the trip. All CEAs [control rod assemblies] inserted fully into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. The Emergency Diesel Generators did not start and were not required. The offsite power grid is stable. No significant LCOs have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. "Unit 3 is stabilized at normal temperature and pressure at approximately 565 degrees F and 2250 psia in Mode 3. The reactor coolant system remains in normal forced circulation with heat removal via the steam bypass control system to the condenser and feedwater from the non-essential auxiliary feedwater system. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The Senior Resident Inspector was informed of the Unit 3 reactor trip and this notification. The Senior Resident Inspector was on-site at the time of the reactor trip." | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-06-07
40794 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-06-05 11:00 | 2004-06-07 13:28 | 2004-06-07 | COLORADO AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE The following information was received by facsimile: "At approximately 11 am on 6/5/04, a watering truck on a housing development construction project near Fort Collins, Colorado (County Roads 11, and 52), ran over a Troxler moisture density gauge (Troxler model 3430; Serial # 28846) owned by Terracon (Colorado Specific License #664-02). The gauge was being used for soil compaction measurements but was in the safe (up) position when it was run over. The technician responsible for using the gauge was reported to be in close proximity to the gauge at the time of the incident but may have had the gauge to his right and not in direct frontal view. As a result of the incident, the index rod was knocked off and the source rod above the unit casing was bent at a 90 degree angle but remained attached to the unit. The gauge casing was described to be mostly intact (i.e. not fully crushed) with the exception of damage to the display. Discussions with the RSO indicated that the gauge source was believed to have remained within the internal shielding following the incident. "The RSO for Terracon reported to the scene at approximately 11:50 am (6/5/04) and performed initial radiation measurements of the gauge. The initial radiation measurements on scene indicated values of approximately 1.0. millirem/hour on/near the surface of the gauge and 0.2 [millirem/hr] at 1 meter. The gauge was placed in the transport case and returned to the Terracon main offices located at 301 North Howes, Fort Collins, CO, 80521. The damaged gauge (in the case) was placed in an outbuilding located near the main office and was secured and the area posted per the RSO. The Department mandated that a leak test be performed prior to shipment of the gauge to a repair facility - results are pending. "Based upon the nature of the incident and the position of the source and rod as, described by the RSO, the source is believed to be intact with no release to the environment or personnel or public exposure. A written report from the licensee is expected within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-06-10
40793 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2004-06-04 18:00 | 2004-06-04 20:14 | 2004-06-04 | LICENSEE REPORTED A 4 HOUR 91-01 RESPONSE BULLETIN Material accumulation discovered in a 55-gallon drum. The 55-gallon drum was used as a knock-out pot for moisture condensate during high-pressure nitrogen drying of clean UF6 cylinders undergoing re-certification. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (b.2), this event satisfies the criteria for a 4-hour notification. Specifically, any determination that a criticality safety analysis or evaluation was deficient, or that a particular system was not previously analyzed; and that less than two unlikely, independent, and concurrent changes in process conditions would be required before a criticality accident would be possible. During a normal process hazards assessment an NCS Engineer was informed of a 55-gallon drum in the cylinder re-certification process. The drum was found to contain approximately 28 kilograms of dry material. Laboratory analyses determined a maximum concentration of 53.5 weight percent uranium in the form of uranyl fluoride. This corresponds to a uranium mass of approximately 15 kilograms. UF6 cylinders contain virtually no uranium at the time they undergo drying in the cylinder re-certification process. Preliminary investigation has revealed that the drum was inspected from 1993 to 1996 and repeatedly found to contain no solid accumulation before the inspections were discontinued. Cylinder re-certification was not in operation at the time of discovery. NCS formally notified Operations not to operate cylinder re-certification. The drum was removed from the system and inspected. The material was removed from the drum, sampled, and analyzed. This particular system was not previously analyzed for criticality safety. Much less than a critical mass was involved. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) has determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2004-06-04
40792 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2004-06-03 14:00 | 2004-06-04 15:15 | 2004-06-04 | AGREEMENT STATE MEDICAL MISADMINISTRATION The South Carolina Department of Health and Environmental Control was notified on Friday, June 04, 2004 of a possible medical rnisadministration notification which was reported by the Radiation Safety Officer for the Cancer Center of the Carolinas. A Cs-137 brachytherapy radiation dose was administered to a patient where the calculated administered dose differed from the prescribed dose by more than 20%. This apparently occurred when the radiation source was not fully extended to the end of the application catheter. The event is under investigation and updates will be made through the national NMED system as they become available. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2004-06-09
40791 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2004-06-04 04:45 | 2004-06-04 08:21 | 2004-06-04 | MANUAL REACTOR TRIP DUE TO INTAKE STRUCTURE SEAWEED FOULING San Onofre Nuclear Generating Station (SONGS) experienced a large influx of seaweed that required securing one of the four running Circulating Water (CW) pumps. When conditions continued to degrade, the Operations Department decided to manually trip the unit. During the trip, all control rods inserted into the core. No manual or power-operated relief valves lifted during the transient. Decay heat is being removed via the atmospheric dump valves. There is no known primary-to-secondary leakage. The Operations staff is maintaining the unit at normal operating pressure and temperature. The electrical grid is stable. Currently, only one CW pump is running. Unit 2 is unaffected and is not experiencing a seaweed influx at this time. The licensee has informed the NRC Resident Inspector | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | M/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-06-04
40790 | 0 | FLEIS AND VANDERBRINK |  |  |  |  | 2004-06-03 18:00 | 2004-06-03 19:52 | 2004-06-03 | VEHICLE ACCIDENT WHILE CARRYING A NUCLEAR GAUGE A pickup truck used by the licensee during inspection services loaded with a Troxler gauge was involved in an accident. The pickup truck hit a tree and its top came loose, along with its contents, landing in an area away from the pickup. A Troxler gauge, inside its storage box, was one of the items tossed out of the pickup truck. The pickup truck caught on fire after the accident. The technician was injured during the accident and was subsequently taken to a local hospital in Springport, MI. The burnt pickup truck was hauled away to a storage place along with the top with its contents. The Troxler gauge is inside its storage box and does not appear to be damaged. The gauge is a Troxler Model 3430, S/N 75-6542, 8 millicuries Cs-137 and 40 millicuries of Am-241/Be. The licensee's Radiation Safety Officer intends to retrieve the gauge, perform a leak test and return the gauge to the manufacturer. The licensee was requested to call the Operations Center with an update of the leak test results. * * * Update on 06/09/06 at 0850 EDT by Paul Galdes to MacKinnon * * * Troxler gauge passed its leak test. R3DO (M Parker) & NMSS ( Linda Psyk) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MI | OTH | GEN |  |  |  |  | 0 | 2004-06-03
40789 | 0 | ALABAMA RADIATION CONTROL |  |  |  |  | 2004-06-03 06:30 | 2004-06-03 08:37 | 2004-06-04 | ALABAMA AGREEMENT STATE REPORT ON STOLEN GAUGE "At 4:07 p.m. Gary Brunson of the Alabama Department of Transportation called and reported that a Campbell Pacific gauge, Model MC3, Serial # M32076686 had been discovered stolen from their Guntersville, Alabama Project Office at approximately 6:30 this morning, Thursday, June 3, 2004. Brunson stated the device contained approximately 10 mCi of Cs-137 and 50 mCi of Am-241/Be. "Brunson further stated he had delayed notifying the Agency until he had a copy of the police report from the Guntersville Police Department, who had investigated the theft. Someone had apparently climbed the fence, then broke into the testing lab building and took a nuclear density gauge and an air flow meter. A Troxler Model 4640 nuclear gauge was sitting beside the Campbell Pacific gauge but was not taken. Because both an air gauge and a density gauge were taken, Mr. Brunson believes the thief was taking something to sell and not taking something from which a radioactive source could be removed, or else they would have taken both nuclear gauges. "Mr. Brunson agreed that if the device is not located by mid morning tomorrow, Friday, June 4, 2004, that he would work with the Agency to distribute an information notice on the missing device to area law enforcement agencies." * * * UPDATE 1143 EDT ON 6/4/04 EMAIL FROM J. MCNEES TO W. GOTT * * * The First Division Office located in Guntersville, AL reported the incident, but the project was in Huntsville, AL, which is part of the First Division. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | AL | OTH | AGR |  |  |  |  | 0 | 2004-06-08
40788 | -1 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-06-03 12:45 | 2004-06-03 12:47 | 2004-06-30 | PART 21 NOTIFICATION OF FAILURE OF SPRING CHARGING FUNCTION IN CIRCUIT BREAKER "Limerick has completed the 10CFR Part 21 evaluation of the failure of the spring charging function on an Asea Brown Boveri (ABB) Model HK circuit breaker. The investigation determined that the primary contributor to the failure was the replacement of ABB latch reset torsion spring number 195205A00 with a weaker spring that was supplied with the breaker overhaul kit number 716656T104. Secondary contributors to the failure were normal wear on additional parts in the operating mechanism. "ABB supplied a six-turn latch reset torsion spring and a five-turn latch reset torsion spring under spring part number 195205A00 and overhaul kit number 716656T104. The spring of concern is a six-turn spring that does not provide as much force as the original six-turn or five-turn spring. When informally tested during the investigation the six-turn spring provided approximately 66 ounces of force and the five-turn spring provided approximately 102 ounces of force. The original six-turn spring provided a force of 88 ounces. "Limerick's evaluation concluded that installation of the replacement six-turn latch reset torsion spring could create a substantial safety hazard depending on the breaker's application. Therefore, this notification is being submitted pursuant to the requirements of 10CFR21.21(d)(3)(i). The required 10CFR21.21(d)(3)(ii) 30-day written notification will provide more detail when submitted. ABB evaluation of this issue is still in progress." The licensee notified the NRC Resident Inspector. * * * RETRACTION ON 6/30/04 @ 1451 HRS. EDT FROM GAMBLE TO CROUCH * * * "This is a retraction of the Part 21 initial notification made per 10CFR21.21(d)(3)(i) on 6/3/04 at 12:47 EDT (EN# 40788). The issue involved an in-service malfunction of the closing spring charging function of an Asea Brown Boveri (ABB) Model HK circuit breaker following replacement of the latch reset torsion spring (ABB number 195205A00) during breaker maintenance. The spring was supplied with ABB overhaul kit number 716656T104. "Upon further review of the Part 21 reporting requirements it has been determined that this issue does not require reporting. NUREG-1022 Rev.2 'Event Reporting Guidelines 10CFR50.72 and 50.73' provides guidance for Part 21 reporting in section 5.1.8. The NUREG section references a federal register notice (56 FR 36081, July 31, 1991) in footnote 18, which provided notification of an amendment to 10CFR Parts 21 and 50. The amendment was intended to reduce duplicate reporting of defects. "The notice provides the following guidance for components that have been installed in operating plants: "Operating license holders can reduce duplicate evaluation and reporting effort by evaluating deviations in basic components installed in operating plants which produce events which could meet the criteria of 50.72 and 50.73. If the evaluation of events using the criteria of 50.72 and 50.73 results in a finding that the event is reportable and the event is reported via these sections, then as indicated in 21.2(c), the evaluation, notification, recordkeeping, and reporting obligations of part 21 are met. If the event is determined not to be reportable under 50.72 or 50.73, then the obligations of part 21 are met by the evaluation. "The evaluation using the criteria of 50.72 and 50.73 resulted in a finding that the event was not reportable. There was no reasonable expectation of preventing fulfillment of a safety function, no equipment was declared inoperable, and the principle safety barriers were not seriously degraded. "Therefore, this event is not reportable using the criteria of 50.72 and 50.73 and the Part 21 evaluation obligation is met." The licensee has notified the NRC Resident Inspector of this retraction. The Headquarters Operations officer notified R1DO (Barkley), R2DO (Evans), R3DO (Gardner), R4DO (Whitten), and NRR (Dennig). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 21.21 |  |  |  | 0 | 2004-06-03
40787 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-06-02 12:30 | 2004-06-02 15:10 | 2004-06-02 | PLANT SHUTDOWN WAS INITIATED TO COMPLY WITH TECH SPEC. 3.6.1.1. PRIMARY CONTAINMENT INTEGRITY. "At 1230 hours the service water isolation valve to the Turbine Building Area (1SW26) was declared inoperable due to the inability to close the valve. This condition was identified while investigating a low service water pressure in the turbine building during start up activities from the Salem 1 sixteenth refueling outage. "With 1SW26 inoperable, Technical Specification 3.6.1.1 requires that the inoperable valve be restored to operable within one hour or be in hot standby within the next 6 hours and in cold shutdown in the next 30 hours. Since the valve cannot be restored to operable within the one hour action statement time, PSEG commenced a unit shutdown at 1330 hours. "It is expected that repairs can be performed while in hot standby conditions. "This report complies with the reporting requirements of 10 CFR 50.72 (b)(2)(i)." The NRC Resident Inspector was notified of this event by the licensee. | 9 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-06-02
40786 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2004-06-01 19:15 | 2004-06-02 00:42 | 2004-06-02 | HPCI DECLARED INOPERABLE "High Pressure Coolant Injection [HPCI] system was declared inoperable due to failure of alarm 'HPCI Turbine Exhaust Drain Pot Hi Level' to clear. The level switch associated with the alarm is the suspected failed component. When the line is drained there is evidence of water flow but the alarm does not clear. There are no other indications of the exhaust drain line filling with water. "As a precautionary measure, the HPCI auxiliary oil pump has been placed in pull-to-lock, which will prevent the auto initiation of HPCI. HPCI will be manually started when required and proper operations assessed to ensure the exhaust line is intact. Hourly draining of the HPCI turbine exhaust drain line has been instituted based on the previously established frequency of the alarm. "HPCI is considered available. "All remaining ECCS systems are operable. "The NRC Senior Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-06-02
40785 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-05-30 11:37 | 2004-05-30 18:40 | 2004-06-15 | HIGH PRESSURE CORE SPRAY SYSTEM INOPERABLE "The High Pressure Core Spray (HPCS) system was declared inoperable due to the pump's failure to meet the flow requirement specified in TS Surveillance Requirement 3.5.1.4. This surveillance is normally performed on a quarterly basis in accordance with the plant's In-service Testing (IST) Program. The flow values measured during the performance of this surveillance were below both the normal and alert ranges. This test had also been run on 5/27/04 with results in the alert range; HPCS system instruments had been vented between the two tests to rule out the possibility that the results were due to measurement errors. "Upon declaring the HPCS pump inoperable, TS 3.5.1 Action B was entered. In accordance with Action B, the Reactor Core Isolation Cooling (RCIC) system was verified to be operable. With the RCIC system verified operable, Action B provides a 14-day completion time to restore HPCS to an operable status. "All other Emergency Core Cooling Systems (ECCS) were operable during this event. This event is being reported as an event or condition that could have prevented the fulfillment of a safety function credited for mitigating the consequences of an accident. The HPCS system is a single train system at Columbia." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 06/14/04 @1752 BY MIKE BRANDON TO C. GOULD * * * RETRACTION On May 30, 2004, Energy Northwest provided an 8-hour notification pursuant to 10 CFR50.72(b)(3)(v)(D). This notification reported the apparent failure of the High Pressure Core Spray (HPCS) system's pump to meet the flow requirements of Surveillance Requirement (SR) 3.5.1.4. Upon the apparent failure to satisfy this SR, Energy Northwest entered Action B of Technical Specification (TS) 3.5.1 (14 day completion time) and initiated actions to investigate the cause of this apparent failure. This investigation determined the cause of this apparent failure was due to an anomaly in the processing of the pressure and flow input signals and the instrumentation used for documenting the results of the surveillance. Additional testing using alternative instrumentation determined the HPCS pump was fully capable of providing flow within the existing acceptance criteria of the plant's In-service Testing (IST) Program and thus capable of satisfying the SR. This investigation determined that no actual degradation of the pump existed that would have caused a valid failure of the SR. This was an instrumentation issue only. The HPCS system would have been capable of performing its specified safety function in the as-found condition and was capable of fully satisfying the SR. Therefore, this condition would not have prevented the fulfillment of a safety function and is therefore not reportable under 10CFR50.72. The HPCS system was declared OPERABLE on June 03, 2004 at 22:59 PDT. The NRC Resident Inspector was notified. | 65 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-05-30
40784 | 0 | NORTH ANNA |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-29 02:02 | 2004-05-29 09:55 | 2004-05-29 | CONTROL ROD POSITION INDICATION FAILURE DURING HOT ROD DROP TEST "During performance of Hot Rod Drop Testing [and] when withdrawing 'D' Control banks, a failure of Group 1 Position Indication was identified. Entered action of Technical Requirement Manual [TRM] 3.1.3 and opened the Reactor Trip Breakers within 15 minutes per action [statement] of TRM 3.1.3." After the Reactor Trip Breakers were opened all Group 1 "D" Control Rods fully inserted into the core. There were no reactivity concerns since the reactor was borated with adequate shutdown margin. The failure of the position indicator has been identified and repaired. There were no other issues associated with this incident and the licensee will proceed with Hot Rod Drop Testing while at 0% reactor power and Mode 3. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-05-29
40783 | 0 | ROTORK CONTROLS INC |  |  |  |  | 2004-05-28 | 2004-05-28 15:51 | 2004-06-03 | PART 21 NOTIFICATION - VALVE ACTUATOR SWITCH MECHANISMS "Basic Component Affected Rotork NA1 switch mechanism assemblies manufactured between 1978 (post 78 build) and November 2001 supplied either as a spares item or fitted in an NA1 type Electric Valve Actuator. Customers supplied with potentially affected actuators manufactured between January 1998 and November 2001, were previously notified individually of this condition and may have completed the risk assessment and corrective action detailed below. This report extends the affected time frame, potentially affecting actuators not identified on the original notifications. "Rotork NA4, NA5, NA1E and NAE5 type Electric Valve Actuators are not affected. "Nature of the Defect and Associated Safety Hazard It has recently been identified that the molded (PPS) components within the switch mechanism assembly have a low level of crystallinity and it cannot be confirmed that they are to the same specification as those originally tested and qualified at Wyle in 1978 (refer test report 43979-1 Rev A). Effect on Functionality The report provides a detailed explanation of the effect on function depending on the valve position and open/close action. "NA4 and NAS type Electric Valve Actuators have a maximum ambient temperature rating of 70 deg C (160 deg F) and are not affected. NA1 type Electric Valve Actuators have the same ambient temperature rating but can be subject to a loss of coolant accident (LOCA). The condition reported will only affect Valve Actuators in plant locations where: 1) the LOCA and Operational temperature specifications, as defined in the Design Basis Document for each facility and location, could result in the switch mechanism components exceeding 80 deg C (176 deg F) and 2) The switch mechanism fitted was manufactured between 1978 and November 2001 and 3) The actuator is exposed to the two conditions outlined in section 2.0 of the report." * * * UPDATE AT 1200 EDT ON 6/03/04 TO S. SANDIN VIA FAX * * * A revision to this report changes the Rotork model number from NAE5 to NA5E. Notified R1DO (Jenison), R2DO (Fredrickson), R3DO (Lanksbury), R4DO (Sanborn), NMSS Part 21 Coordinator (Torres) and NRR Part 21 Coordinator (Hodge) via fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | NY | OTH | PAR | 21.21 |  |  |  | 0 | 2004-05-28
40782 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2004-05-27 19:00 | 2004-05-28 12:48 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * 24-HOUR NOTIFICATION - [DELETED] CRITICALITY DETECTOR FAILED ROUTINE TEST "At approximately 19:00 P.M. on May 27th, one of two criticality detectors for [DELETED] failed a routine source check. The failure resulted in the detector not being able to give a High alarm, which resulted in a loss of criticality detector coverage for [DELETED] at the [DELETED] at BWX Technologies. This situation presents no risk to the public or workers, since the [DELETED] have not had any fuel since February 20, 2001. The last time the [DELETED] criticality detectors were source checked (successfully) was on April 11, 2004. However, [DELETED] was authorized for fuel operations, therefore, criticality detectors were required to be functional. This loss of criticality detector coverage is required to be reported to the NRC within 24 hours per 10CFR70.24 and 10CFR70.50(b)(2)." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2008-05-11
40781 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-05-28 11:15 | 2004-05-28 12:43 | 2004-05-28 | FLORIDA AGREEMENT STATE REPORT - STOLEN DENSITY GAUGE A Troxler Moisture Density Gauge, Model #3440 (Serial #27071 containing 40 millicuries Am-241/Be and 8 millicuries Cs-137) was stolen from the licensee's truck at a construction site in Miami, FL. A chain locking the gauge to the truck was cut. The licensee notified the Miami Police Dept. who are investigating. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-06-01
40780 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-05-27 06:30 | 2004-05-27 13:15 | 2004-05-27 | AUTOMATIC SAFETY INJECTION FUNCTION INADVERTANTLY BLOCKED "This 8-hour notification is being made to report that in Mode 4, during the start-up of Salem Unit 2, the Automatic Safety Injection function was identified blocked. At 0140 hours on 5/27/04, Salem Unit 2 transitioned from Mode 5 to Mode 4. In Mode 4, Automatic Safety Injection is required per Technical Specification 3.3.2.1. At 0630 hours on 5/27/04, it was discovered that both trains of the Automatic Safety Injection logic were blocked. Technical Specification 3.0.3 was entered. At 0635, Automatic Safety Injection was reinstated to both trains of Safety Injection and Technical Specification 3.0.3 was exited. Salem Unit 2 is currently in Mode 4 with reactor coolant temperature at 320 degrees and reactor coolant pressure at 320 psig. The Reactor Coolant System is being cooled by the 21 Residual Heat Removal loop. During the time period that Automatic Safety Injection was blocked, the required ECCS Pump was available in compliance with Technical Specification 3.5.3. Additionally, the following equipment status existed: 21 Reactor Coolant Pump was cleared and tagged for an oil leak repair, and 22BF19 Main Feed Regulating Valve was cleared and tagged closed for positioner repairs. "There were no personnel injuries or radiological occurrences associated with this event." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-05-27
40779 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-05-27 10:20 | 2004-05-27 10:57 | 2004-05-27 | OFFSITE NOTIFICATION MADE DUE TO EXTERNAL CONTAMINATION FOUND ON CONTAINER SHIPPED BY LICENSEE The following information was received by the licensee via facsimile: "Contamination levels in excess of USDOT [U.S. Department of Transportation] and Barnwell [South Carolina] limits found on a shipment when it reached its destination. (Sea Land Container). "No personnel contaminations were reported." The licensee was informed by Barnwell of the contamination event. Apparently, the temperature difference between Connecticut and South Carolina caused condensation to form inside the Sea Land container. The condensation puddled inside the container and then leaked out onto the trailer bed. Contamination was found by Barnwell personnel upon receipt of the trailer. The licensee informed the State of Connecticut Department of Environmental Protection representative on site and NRC Region 1 (John Wray). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | SURFACE CONTAM LEVELS > LIMITS |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) | 20.1906(d)(1) |  |  | 0 | 2004-05-27
40778 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-05-27 00:33 | 2004-05-27 01:21 | 2004-05-27 | AUTOMATIC REACTOR SCRAM WHILE PERFORMING SCHEDULED SHUTDOWN "During a reactor shutdown for scheduled maintenance, a full reactor scram was generated from the Nuclear Instrumentation System. "IRMs [Intermediate Range Monitoring detectors] 13, 14 and 18 spiked causing scram signals in both RPS [Reactor Protection Systems]. "All systems functioned properly post scram, all operator actions were correct. Holding reactor pressure at 900 psig to perform leakage inspection. Following [the leakage] inspection [operations intend] to proceed to cold shutdown." All control rods inserted fully into the core and excess decay heat is currently being diverted to the main condenser, as necessary. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-05-27
40777 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-05-26 16:00 | 2004-05-26 17:55 | 2004-05-26 | OFF SITE NOTIFICATION "This event is being reported under 10CFR50.72(b)(2)(xi) as an item of public interest and an event for which other government agencies have been notified. "At 1600 on 5/26/2004, the operations Shift Manager was notified by the Security Shift Supervisor that an individual [truck driver] had been arraigned by a LLEA [Local Law Enforcement Agency] judge for prohibited items (drug paraphernalia) which were discovered during a routine entrance search of personnel and vehicles. The items were discovered outside the protected area [and] were determined to not pose a threat or attempted threat. The LLEA was called and responded to the site access area and removed the individual to the local barracks, where he was subsequently arraigned on a misdemeanor. The individual's name has been removed from the Susquehanna LLC visitors list. "The Manager of Nuclear Security briefed NRC Region #1 Inspector, Dana Caran, concerning the incident." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-05-26
40776 | 0 | IDAHO STATE UNIVERSITY |  |  |  | 0.005 KW AGN-201M #103 | 2004-05-24 09:00 | 2004-05-26 09:38 | 2004-05-26 | BREACH OF PRIMARY FISSION PRODUCT BARRIER During routine annual maintenance, a fueled control rod was determined to have a cladding failure. The control rod end cap weld was broken and the fuel in the fueled control rod had been exposed. A preliminary radiological assessment was performed and showed negligible release. There was minimum surface contamination isolated to the area of the breach. Radiation readings on contact were less than 20 millirem/hour. All air sample concentrations were well below 10CFR20 Derived Air Concentration (DAC) limits. Licensee notified the NRC Program Manager for Non Power Reactors and the Region 4 RA. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 4 | ID | NPR | [5 empty] | 0 | 2004-05-26
40775 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2004-05-25 10:30 | 2004-05-25 20:02 | 2004-05-25 | LICENSEED EMPLOYEE TESTED POSITIVE DURING A RANDOM DRUG TEST. A licensed employee was administered a random drug test. He tested positive for an illegal substance. The Medical Review Officer reviewed the test results with the licensed employee. His access was immediately terminated for the protected area and he was placed on investigatory suspension. Contact the Headquarters Operations Officer for details. The NRC Resident Inspector will be informed by the licensee. | 0 | 99 | 100 | 0 | 99 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 26.73 |  |  |  | 0 | 2004-05-25
40774 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-05-24 15:00 | 2004-05-24 17:12 | 2004-05-24 | DEGRADED CONDITION DUE TO EMERGENCY SERVICE WATER FAILURE "Emergency Service Water "A" (ESW ) Pump failure resulted in inoperability of all Div 1 ECCS systems at 0150 on 05/21/04 [See event notification 40767]. A plant shutdown was initiated with mode 4 [cold shutdown] achieved at 0619 on 05/23/04. During the disassembly and inspection of ESW A pump, a failed coupling on the pump shaft was found to be the cause of the failure. An Operability Determination [OD] was requested on ESW B at 1330 on 05/24/04 since both pumps had the identical coupling design and the pumps had similar run times. At 1500, the Design Engineering Manager informed the control room that engineering could not return a completed OD within the allotted time that could justify continued ESW B operability. The control room Shift Manager than declared the ESW B pump inoperable. This results in a condition that could have prevented the fulfillment of a safety function, specifically the removal of residual heat." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | POT RHR INOP |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(v)(B) |  |  | 0 | 2004-05-24
40772 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-23 05:26 | 2004-05-23 06:21 | 2004-05-23 | TECHNICAL SPECIFICATIONS REQUIRED COOLDOWN "Based on the inoperability of Unit 2 Auxiliary Feedwater (reference EN # 40771) due to an underground leak, Unit 2 has initiated a plant cooldown from Hot Shutdown (547F) to Cold Shutdown (<200F). This notification is being made pursuant to 10 CFR 50.72(b)(2)(i) for the 4-hour notification of a Technical Specification Required Shutdown." This event notification is required per licensee's Administrative procedures. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-05-23
40771 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-22 21:30 | 2004-05-22 22:29 | 2004-05-22 | AUXILIARY FEEDWATER SYSTEM DECLARED INOPERABLE DUE TO UNDERGROUND LEAK "There is sufficient reason to believe that the buried auxiliary feedwater piping associated with Unit 2 is degraded and leaking and thus as a conservative measure it is declared inoperable. This operability determination is based on not having a reasonable assurance that the auxiliary feedwater piping can continue to perform its intended function under all design basis events including seismic events. Approximate leakrate is 8 gpm. Makeup is sufficient at this time to maintain desired level in the affected tank. Further efforts to determine the exact leak location are ongoing. This notification is being made pursuant to 10 CFR 50.72(b)(3)(v)(D) for the 8-hour notification of a condition that could have prevented the fulfillment of the safety function of systems or structures that are needed to mitigate the consequences of an accident." Emergency Condensate Storage Tank level was decreasing and water has been detected coming from a conduit in the Safeguard Building. Licensee is in Tech Spec 3.0.1 (30 hours to get below 350 degrees F and 450 psig). The NRC Resident Inspector was notified of this event by the licensee. See EN #'s 40770, 40769 & 40768 for Surry Unit 2 related problems. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-05-22
40770 | -1 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-21 21:46 | 2004-05-22 15:06 | 2004-05-26 | UNANALYZED CONDITION DUE TO AUXILIARY FEEDWATER NOT BEING IN COMPLIANCE WITH JUSTIFICATION FOR CONTINUED OPERATION (JCO). "At 2146 hours on 05/21/04, Unit 2 entered a 30 Hr. clock to Cold Shutdown (CSD) in accordance with T.S.3.0.1 due to Auxiliary Feedwater (AFW) not being in compliance for Continued Operation (JCO) SC 03-002 configuration. Auxiliary Feedwater was declared inoperable at 2146 hours. During post trip recovery, Emergency Procedure, 2-ES-0.1, directed that the six (6) AFW motor operated valves (MOVs) be checked opened after securing the AFW Pumps. This is contrary to the AFW JCO, which requires four (4) MOVs out of six (6) to be closed for AFW to remain Operable. At 0040 hours on 5/22/04 the correct valve alignment in accordance with the JCO was established and the 30 hour TS 3.0.1 clock was exited. "This event is reportable in accordance with 10CFR50.72(b)(3)(ii)(B); any event or condition that results in the Station being in an unanalyzed condition that significantly degrades plant safety. "The NRC resident has been notified." The licensee found out about this event today during event investigation. See Surry Unit 2 events 40769, 40768 and 40771. * * * RETRACTION FROM WOODZELL TO CROUCH ON 05/25/04 @ 2347 EDT * * * The following information was received from the licensee via facsimile: "At 1506 hours on 5/22/04, Surry Power Station made an 8-hour Non-Emergency Notification in accordance with 10CFR50.72 (b)(3)(ii)(B) for an unanalyzed condition due to Auxiliary Feedwater (AFW) not being aligned in accordance with Justification for Continued Operation (JCO) SC 03-002 for 2 hours and 54 minutes following a reactor trip. (Event Number 40770). "Upon further analysis, this event was determined not to be immediately reportable. Based on calculations performed by Dominion Nuclear Safety Analysis in Engineering Transmittal ET NAF-04-0045, Rev 0, a risk-based period of time was calculated to allow operations personnel a defined period of time to realign the AFW system in accordance with this JCO. Operators must not exceed 150 hours to restore the acceptable JCO configuration during all modes where AFW is required to be operable. Since the amount of time the system was not in the JCO alignment was less than 150 hours, plant risk increase was maintained less than the limits specified in Regulatory Guide 1.177. "This notification is being made to retract the report made on 5/22/04 based on the above discussion. The NRC resident has been notified." The NRC Headquarters Operations Officer notified R2DO (Ayres). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-05-22
40769 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-21 21:08 | 2004-05-22 00:28 | 2004-05-22 | AUTOMATIC REACTOR TRIP DUE TO GENERATOR LEADS FAILURE "Unit 2 Reactor tripped at 2108, first out is F-E-2, 500KV leads differential lockout relay trip. "This notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) for 4-hour notification of RPS Activation and 10 CFR 50.72(b)(3)(iv)(A) for 8-hour notification of automatic actuation of AFW. Plant responded as expected with the exception of 'C' SG AFW flow indication. The 'C' SG level responded normally to Unit conditions. The NRC resident has been notified of this event and is on site. Notification was made to NRC duty officer upon declaration on NOUE[See EN#40768], which was declared based on EAL Tab K-6 for 'Confirmed report of unplanned explosion within Protected Area or Switchyard.' An electrical fault was observed in the 500 KV switchyard and is currently being investigated. No further damage has been detected in the switchyard. The NOUE, which was declared at 2116, has been terminated as of 2256." Reactor shutdown with all control rods fully inserted. Electric plant is in a normal shutdown mode lineup. The other operating unit was unaffected by this event. Decay heat is being removed to the main condenser using the condenser steam dump valves. See Surry Unit 2 event # 40770 & 40771. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-05-22
40768 | 0 | SURRY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-21 21:16 | 2004-05-21 21:36 | 2004-05-21 | UNUSUAL EVENT DECLARED At 2108 hours a main generator lead failed (exploded) causing a generator lead differential lockout/turbine trip/reactor trip. All rods fully inserted into the core. Both Motor Driven and the Turbine Driven Auxiliary Feedwater Pumps started as expected and are supplying water to the steam generators. Electrical power is being supplied from offsite and all systems are operating as expected. The reactor tripped at 2108 hours and a report of a fire in the switchyard was reported to Control Room at 2109 hours. Fire Brigade was dispatched and the fire was reported out at 2142 hours. Reflash fire watch has been set. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. Surry Unit 1 remains at 100% power. Licensee notified State and Local officials of their declaration of an Unusual Event. The NRC Resident Inspector was notified of the event by the licensee. * * * UPDATE ON 5/21/04 AT 2310 EDT FROM CHARLES YOUNG TO G. WAIG * * * The licensee terminated the NOUE at 2256 EDT. Damage appears to be confined to the main generator leads with one lead missing and some damage to other leads. The plant is stable with RCS temperature at 547 degrees Fahrenheit, 2235 psia. The NRC Resident Inspector will be notified of the NOUE termination by the licensee. Notified R2DO (Jay Henson), NRR EO (Edwin Hackett), DIRO (Tom Andrews), FEMA (David Barden), DHS (Robert Bozzo). See EN 40769 , 40770 & 40771 for related Non Emergency notifications. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-05-21
40767 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-05-21 16:00 | 2004-05-21 16:11 | 2004-05-21 | TECHNICAL SPECIFICATION SHUTDOWN Emergency Service Water "A" (ESW) Pump failure results in inoperability of all Div 1 ECCS systems. The plant entered the Limiting Condition for Operation for the ESW inoperability at 0150 on 05/21/04. The action times for Tech Spec 3.7.1 are as follows: restore ESW to operable status within 72 hours, if this cannot be accomplished be in Mode 3 (Hot Shutdown) in the following 12 hours and Mode 4 (Cold Shutdown) in 36 hours. Reactor power was reduced at 1600 to begin the shutdown process. Division 2 and 3 ECCS are fully operable. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-05-21
40766 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-04 14:57 | 2004-05-21 15:58 | 2004-05-21 | 60 -DAY REPORT: INVALID ACTUATION OF THE "E" EMERGENCY DIESEL GENERATOR On 04/04/04 at 14:57 hours, the "E" Emergency Diesel Generator unexpectedly started in the emergency mode of operation during performance of Unit 1 LOCA/LOOP surveillance testing. The diesel generator started in response to a false loss of offsite power signal that occurred after an electrical test jumper was incorrectly installed in panel 1A201. While the procedure directed installation of the jumper across the field side of states links T5-10 and T5-12, the jumper was instead installed across the panel side of the links. When link T5-10 was opened per procedural direction, a false LOOP signal was sent to the "E" diesel generator start circuit. The "E" emergency diesel generator successfully started and properly responded to the complete train actuation signal. The diesel was shutdown following the incident. No other plant equipment was affected by this jumper use error. At the time of this event, Unit 1 was in Mode 5 and Unit 2 was in Mode 1. Both Units continued in Modes 5 and 1, respectively. Surveillance testing was successfully completed on 04/05/04. The consequences of this event were limited to the unplanned start of the "E" emergency diesel generator. The diesel generator started and functioned in accordance with its design. This event comprises an invalid actuation of an emergency AC electrical power system and is therefore being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a 60- day telephone notification per the provision of 10 CFR 50.73 (a)(1). The NRC Resident Inspector was notified of the 60- day report notification by the licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-05-21
40764 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-05-21 13:15 | 2004-05-21 14:50 | 2004-05-21 | TECHNICAL SPECIFICATION SHUTDOWN A unit shutdown was commenced to comply with the technical specification for containment integrity. A service water isolation valve supplying the turbine generator area lost power when the 2B vital bus 230v transformer failed at 1147 on 5/21/04. This results in entry into a restore in 1 hour or hot shutdown in 6 hours LCO (3.6.1.1) since the valve cannot be isolated and maintain the unit in service. The failure of the transformer is currently under investigation. A power reduction of 20% per hour is currently in progress. Other equipment affected by the transformer loss, various containment isolation valves, 2B emergency diesel generator, 22 chiller, 22 and 24 containment fan coil units, and 23 and 24 service water pumps. Prior to the event the only safety related equipment out of service was the service 23 service water pump that was out for planned maintenance. There were no personnel injuries as a result of this event. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 60 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-05-21
40763 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2004-05-20 11:00 | 2004-05-21 12:28 | 2004-05-21 | MISSISSIPPI AGREEMENT STATE REPORT: LEAKING SOURCE Description of Incident: Approximately 11:00 central time on 5-20-04, The Division of Radiological Health, MS State Dept. of Health, was notified that a leaking Cesium 137 source was found when a consultant was preparing sealed sources for disposal. The leaking source was found in the bottom of a storage container (original pig from Du Pont) that was used to store a Du Pont Merck Model NER-401H 592 microcurie Cs-137 dose calibrator source. The leaking source was found after the dose calibrator source had been removed from the storage pig and determined to be free of contamination. The leaking source was discovered in a crack at the bottom of the storage pig and was in excess of .005 microcuries removable contamination. A consultant stated that the leaking source appeared to be about the size of a pencil lead. Instead of trying to remove the contaminated source from the pig, he put epoxy in the pig to seal it in place to ready it for disposal. He estimated that the source was probably used as a check source. The dose calibrator source was originally purchased from Du Pont Merck in 1982. All tests for leakage/contamination were negative for over 20 years. It is our belief that the leaking source was in the pig when it was purchased from Du Pont Merck. The licensee had never been licensed for any other Cs-137 sources. Describe clean-up actions: Consultant had removed all sources and completed close-out surveys and wipes for termination of license. List Radiation measurements taken: Consultant stated that survey readings at top of storage pig were approximately 0.2 mRem/hr. List any other actions required of DRH: follow up as required and notify NMED. Case Closed: Yes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2004-05-26
40762 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-05-20 14:35 | 2004-05-21 08:47 | 2004-05-21 | CORPORATE HEADQUARTERS NON-LICENSED EMPLOYEE TESTED POSITIVE DURING URINALYSIS A non-licensed supervisory employee with normal work location at corporate headquarters tested positive during a random urinalysis test. The employee's access to Braidwood, Byron, Clinton, Dresden, LaSalle and Quad Cities nuclear power stations has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee will notify the NRC Resident Inspectors for the above sites. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2004-05-21
40761 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2004-05-20 09:00 | 2004-05-20 12:47 | 2004-05-25 | NEW MEXICO AGREEMENT STATE REPORT: STOLEN 12 MILLICURIE COBALT-57 SOURCE (USED IN A PAINT ANALYZER) Radiation Safety Officer for Acme Environmental, a New Mexico radioactive material licensee, in Albuquerque, NM, called the Program Manager for the NM Radiation Protection Program, at approximately 0900 MST May 20, 2004 , to report a stolen 12 milliCurie Cobalt-57 source. The cobalt-57 source was contained in a RMD LPA-1XRF lead paint analyzer. The paint analyzer was in a container in the rear seat of a 1996 Dodge Dakota stretch cab PU. The pickup was stolen from a gas station in Bernalillo, NM, while the driver was inside paying for gas. The container is not labeled, but the analyzer has a radioactive label. Police have been notified. * * * UPDATE ON 05/25/04 @10:58 FROM WILLIAM FLOYD TO C GOULD * * * The State was notified at 8:30 A.M. on May 25, 2004, by the RSO of Acme Environmental in Albuquerque, NM, that the lead paint analyzer containing a 12 mCi Co-57 source has been retrieved. The device was in the back seat of a pickup truck stolen at a gas station in Bernalillo, NM, on May 20, 2004. Police raided a home in the East Mountain area (east of Albuquerque) on May 24 and found the device. The stolen truck has not yet been located. Another stolen vehicle was found at the home, however. The analyzer has been returned to Acme Environmental and will be leak tested. Notified Reg 4 RDO (M Runyan), NMSS EO(R Torres), TAS (D Perez) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2004-05-25
40760 | 0 | SAINT LUKES HOSPITAL |  |  |  |  | 2004-05-18 13:00 | 2004-05-19 12:30 | 2004-05-19 | SURFACE CONTAMINATION ON BOX GREATER THAN THE LIMIT Saint Luke's Hospital in Meridian, ID received a box from Radio-Pharmacy of Boise, ID which had surface contamination of 50,000 counts per minute by wipe of I-131. The box has been placed in waste storage to allow the contamination to decay away. Wipes of the area indicated that none of the contamination spread. There was no personnel contamination. Radio-Pharmacy of Boise, the originator of the shipment, was notified of the contaminated box and indicated that they had a spill of I-131 on 5/18/04. Radio Pharmacy of Boise reported that event separately to the NRC (See Event Notification 40759). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 20.1906(d)(1) |  |  |  | 0 | 2004-05-19
40759 | 0 | CARDINAL HEALTH SYSTEMS |  |  |  |  | 2004-05-18 09:00 | 2004-05-19 12:24 | 2004-05-20 | UNPLANNED CONTAMINATION EVENT DUE TO SPILL OF IODINE-131 On 5/18/04 at 0900 hrs. MST, a radio pharmacist at Cardinal Health System's Radio pharmacy of Boise was preparing a vial of I-131 when the pig assembly failed and the pig and vial dropped to the floor, shattering the vial. Approximately 58 milliCuries of I-131 was spilled. The radio pharmacist was contaminated on his legs. The licensee is currently collecting data to determine the skin dose to the pharmacist who decontaminated himself under the phone directions of the headquarters health physics technicians. Uptake data calculations are awaiting bioassay results. The pharmacist has been administered a dose of ThyroBlock as a precautionary measure. The spill occurred in the restricted hot lab area. Decontamination of the lab area has removed all loose surface contamination. All fixed contamination has been shielded. Continuous air sampling is being used to determine volatility of the spilled material. The licensee made a voice mail notification to R4DNMS (Katanic). * * * UPDATE ON 05/20/04 AT 2011 EDT BY WILLIE REGITS TAKEN BY MACKINNON * * * Preliminary findings based on initial surveys: Pharmacist region of contamination was limited to both knees and his left thumb. Max. exposed 10 square centimeters to knees was estimated to be 68 millirems. Estimated contamination to his left thumb was 6000 millirems. Two of the four individuals involved in the cleanup had elevated thyroid bioassays. One received 0.12 microcuries and the other received 0.04 microcuries. In reference to event number 40760 reported by Saint Lukes Hospital: The spill at Cardinal Health Systems was thought to have contaminated two packages. The one shipped to Saint Lukes Hospital was found to be contaminated. The second package sent to another Hospital in Boise, Idaho was found not to be contaminated. R4DO (Troy Pruett) and NMSS EO (Bob Pierson) notified of the update. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 4 | ID | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2004-05-19
40758 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-05-14 | 2004-05-18 16:31 | 2004-05-18 | FLORIDA AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received from the State of Florida Bureau of Radiation Control via e-mail: "Patient was scheduled to receive a 2 fraction treatment to the breast over a five day period - for a total ten fractions. Prior to the last two fractions the doctor went out of town. The new doctor discovered that the calculated center of the balloon was off by 4 mm. The doctor chose to cancel the ninth & tenth fractions. Subsequent calculations showed the dose received was approximately 19 [to] 35% less than prescribed, depending on axis used relative to the catheter. The patient has been notified. This office was notified the day the last two fractions were canceled on May 14. However, review of events and the dose calculations were not complete until May 18. Licensee will send a written report on this event. Examination of this report will determine future Florida actions." The fraction treatments were delivered using a Mammosite with an Ir-192, 6 Curie source. The maximum dose the patient received was calculated to be 2720 centiGray. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-05-21
40757 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-05-18 13:55 | 2004-05-18 16:04 | 2004-05-18 | POTENTIALLY CONTAMINATED INJURED PERSONNEL TRANSPORTED TO OFFSITE MEDICAL FACILITY The following information was obtained by the licensee via facsimile: "At 1355 [hrs. EDT] on 5/18/04, a vendor employee working in Unit 2's Reactor Building felt ill and passed out. Individual was transported as potentially contaminated to Oconee Memorial Hospital. Offsite medical personnel were notified to treat [the] individual as contaminated. Oconee Nuclear Station Radiation Protection Technician accompanied individual to [the] hospital to complete contamination survey. "At 1515 [hrs.], Oconee Nuclear Station Radiation Protection Technician reported from [the] hospital that the individual has been determined to not be contaminated and was not at the time he left Oconee Nuclear Station." Transport of individual was via Oconee County Ambulance. Oconee Nuclear Station first responders treated the individual until offsite medical assistance arrived. The injured person was performing work in a contaminated area. The contractor is currently in stable condition at Oconee Memorial Hospital. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-05-18
40754 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-05-15 11:54 | 2004-05-15 15:12 | 2004-05-15 | MANUAL REACTOR TRIP DUE TO DIVER ENTANGLED IN INTAKE CRIB "A Unit 2 manual reactor trip was initiated when the control room was notified that a diver was entangled in the intake crib. Divers were being used to inspect the intake crib, install buoys, and the fish deterrent system. The diver's umbilical cord became snagged and attempts to free it were unsuccessful. The Unit 2 circulating water system was secured to aid in removing the diver from the water. The diver still had breathing air available during the transient. The diver was subsequently removed from the water unhurt. "Plant systems functioned as required, including the Reactor Protection and Auxiliary Feedwater Systems. There was no Emergency Core Cooling System actuation. Note: The condenser was unavailable because circulating water was secured. This caused a loss of condenser vacuum and its use as a heat sink. The atmospheric steam dumps are currently being used for heat removal from the steam generators. The circulating water system was subsequently restored to service. This event is reportable pursuant to 50.72(b)(2)(iv)(B), any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical and 50.72(b)(3)(iv)(A), PWR auxiliary feedwater system." All control rods inserted into the core. The electrical busses are in a normal shutdown line up. The licensee notified the NRC Resident inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-05-15
40753 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-05-15 08:31 | 2004-05-15 10:18 | 2004-05-15 | POTENTIALLY CONTAMINATED EMPLOYEE TRANSPORTED TO OFFSITE MEDICAL FACILITY At 0831 EDT, an individual was transported to an offsite medical facility due to chest pains. The individual was preparing to leave a contaminated area when the chest pains occurred. His protected clothing was cut off, and he was transported via ambulance to an offsite medical facility. It was not known at the time of notification if the individual was in fact contaminated. The licensee notified the NRC Resident Inspector. * * * * UPDATED ON 5/15/04 AT 1134 EDT FROM P. NORTH TO M. RIPLEY * * * * At 1134 EDT, the licensee reported that the individual was not contaminated. Notified R2DO (Munday). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-05-15
40752 | 0 | TURKEY POINT |  | 4 |  | [3] W-3-LP,[4] W-3-LP | 2004-05-14 17:29 | 2004-05-14 18:26 | 2004-05-14 | SCRAM DUE TO LOWERING STEAM GENERATOR LEVEL At 1728 EDTon 05/14/04, while performing maintenance on Turbine 1st stage steam pressure transmitter (PT-447), feedwater regulating valve (FRV) 4A was observed to close. At 1729, an automatic actuation of RPS occurred on Low Steam Generator level in the 4A Steam Generator. This was followed shortly by a manual reactor trip by the operator. All control rods fully inserted. All 3 turbine driven AFW pumps started as expected and are supply steam generators through both feedwater supply headers. The electric plant remains in a normal lineup. RCPs are in operation transferring decay heat to the steam generators. The MSIVs are open with the steam generators discharging steam to the main condenser using the condenser steam dump valves. All steam generator atmospheric dump valves opened on the reactor trip and closed. The plant is investigating the cause of the FRV closure and intends to stay in Mode 3 until the cause is determined and appropriate repairs are made. There was no impact on the other operating unit. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-05-14
40751 | 0 | U.S. ARMY |  |  |  |  | 2004-05-13 12:15 | 2004-05-14 17:38 | 2004-05-14 | CONTAMINATION EVENT WHILE CONDUCTING MAINTENANCE "The incident occurred at Ft Carson, CO in the Direct Support (DS) maintenance Shop on 13 May 2004. It involved a M64A1 mortar sight unit containing 6.69 curies of tritium gas in sealed source form (NSN 124001-379-7953). The M64 mortar was being turned in by the 10th Special Forces for routine maintenance. It was discovered that a mechanical pin needed to be removed from the M64 in order to fix it. After fixing the pin the device was leak tested. Leak test results showed removable contamination of approximately 2.5 million dpm [disintegrations per minute] (1.12 microcuries). The RSO took immediate action upon receiving the wipe test result of the device. He double bagged the device and placed it in a secured area. Several area wipes were performed of the shop area and of areas outside the shop area. The shop area showed contamination ranging from 500 dpm to 900 K dpm. The RSO took action to remove items from the shop that were contaminated. Survey results showed that the tritium contamination did not spread outside of the machining area. Three persons were bioassayed. Bioassay results were not available at the time of this report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2004-05-14
40750 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2004-05-14 09:00 | 2004-05-14 17:07 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * 91-01 BULLETIN - LOSS OF CRITICALITY SAFETY CONTROLS "An Integrated Safety Analysis (ISA) review being performed for a system modification identified a previously unidentified failure mode for a piece of Safety Related Equipment (SRE). The SRE item (conductivity probe) is in place to detect and prevent the transfer of moderating materials to a fissile material storage column. The conductivity probe was subsequently tested and found to not meet the currently required performance criteria (i.e. the conductivity probe was not capable of detecting certain moderating materials that could be present in the fissile material). The operation was already in a shutdown state and all fissile material had been removed from the system when the test was performed on the probe. "Safety significance of the event: The safety significance is very low since the system was currently shutdown and the identified failure mode has not occurred since startup of the operation in 1999. "Brief scenario(s) of how criticality could occur: Failure of the piece of SRE could only result in a criticality if a subsequent unlikely event were to also occur resulting in a large spill of fissile material. "Controlled parameters: Moderation and Geometry "Estimated amount, enrichment, form of licensed material (include process limit and % worst case critical mass): Uranium compounds in the column would be 43 times minimum critical mass if spill of materials in full column occurred. Process limit is limited by geometry of equipment "Control(s) or control system(s) and the failure(s) or deficiencies: A fissile material transfer line is monitored (for moderation) such that the transfer of moderating materials into a column is prevented. The monitoring equipment was found to not be compatible for all moderating materials in the system preventing it from halting the transfer of moderating materials into the equipment under certain postulated upset conditions. "Corrective actions taken and when was each was implemented: The conductivity probe was tested in the newly identified failure mode and was found to not respond adequately. The system was already in a shutdown state and all fissile material had been removed from the system when the test was performed on the probe. Compensatory measures (both administrative and engineered) were drafted and reviewed by the plant safety review committee. The system remains shutdown until all compensatory measures are approved and in place." Licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/11/08 BY J KOZAL * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 0 | 2008-05-11
40749 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2004-05-14 09:17 | 2004-05-14 15:45 | 2004-05-14 | CHANGE IN THE METHODOLOGY USED BY GE/GNF TO DEMONSTRATE COMPLIANCE WITH ECCS PERFORMANCE REQUIREMENTS "Nine Mile Point has been informed of a change in its vendor's calculation of Peak Cladding Temperature (PCT) and local cladding oxidation that is based on a reanalysis of the oxygen available for injection into the reactor vessel that would then recombine with hydrogen produced during the postulated zinc-water reaction. Based on 10CFR50 Appendix K inputs and assumptions the additional heat released from this increased reaction rate would result in an estimated increase of 25 degrees F in PCT and 1.73% in maximum local oxidation during five reactor recirculation loop operation, with containment inerted. The increased oxidation results in the analysis of record being non-conservative to the 17% limit as specified in 10CFR50.46(b)(2). Maximum Average Planar-Linear Heat Generation Rate (MAPLHGR) limit adjustments will be applied to bring the oxidation limits below the 17% limit. "Notification is being made as a result of the 10CFR50.46(a)(3)(ii) requirement to report this issue in accordance with 10CFR50.72 and 10CFR50.73. Background "During a Loss of Coolant Accident (LOCA), oxygen is available in the fuel bundles due to evaporation of the Emergency Core Cooling System (ECCS) water and release of the dissolved oxygen. In addition, oxygen can also be drawn into the reactor vessel later in the LOCA when the vessel pressure has dropped to the Primary Containment (Drywell) pressure. Condensation of the steam in the reactor vessel upper plenum due to the injection of sub-cooled ECCS water causes a reduction in pressure that will result in drawing the non-condensable gases (including oxygen) from the Drywell. "Hydrogen is generated, within the fuel bundles during a LOCA due to Zirconium metal - water reaction caused by high cladding temperatures. It has been postulated that, at the pressure and temperature conditions in the reactor core during a LOCA, free hydrogen and oxygen could combine and release heat that will increase the steam temperature. Since steam is the heat sink when the core is uncovered, an increase in the steam temperature can result in an increase in the PCT for non-jet pump plants. The LOCA scenario for a BWR/2 designed plant is different since the core remains uncovered and there is no period of reflooding for large breaks. The cladding will still be heating up when the oxygen from the containment gets into the vessel. This phenomenon also results in an increase in local oxidation. "The change in the allowable MAPLGHR limit for five loop operation with the containment inerted results in the offsite dose for this scenario being still bounded by our current safety analysis. Therefore, this event is not significant with respect to the health and safety of the public. Corrective Action(s): "Reactor Engineering has implemented the 2% MAPLHGR Limit reduction through imposition of a .98 MAPRAT to restore compliance to the 10CFR50.46 limits. "Operations will place administrative controls/ procedure changes to preclude operating without containment inerted at or above 25% power to limit oxygen available for this postulated phenomenon. "In accordance with 10CFR50.73, a LER will be submitted with a more detailed discussion of the nature of this change in the ECCS evaluation model, its estimated effect of the limiting ECCS analysis, and a proposed schedule for providing a reanalysis or taking other action as may be needed to comply with this regulation." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-05-14
40748 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-05-14 08:13 | 2004-05-14 10:50 | 2004-05-14 | CHANGE IN THE METHODOLOGY USED BY GE/GNF TO DEMONSTRATE COMPLIANCE WITH ECCS PERFORMANCE REQUIREMENTS "Oyster Creek has been informed of a change in its vendor's calculation of Peak Cladding Temperature (PCT) and local cladding oxidation that is based on a reanalysis of the oxygen available for injection into the reactor vessel that would then recombine with hydrogen produced during the postulated zinc-water reaction. Based on 10CFR50 Appendix K inputs and assumptions the additional heat released from this increased reaction rate would result in an estimated increase of 25 degrees F in PCT and 1.73% in maximum local oxidation. Using these results, the increased oxidation results in the analysis of record being non-conservative to the 17% limit as specified in 10CFR50.46(b)(2) by 1.23%. Maximum Average Planar-Linear Heat Generation Rate (MAPLHGR) limit adjustments will be applied to bring the oxidation limits below the 17% limit. "However, sufficient margin exists under current operation to ensure the maximum local oxidation limit would not be exceeded. All other 10CFR50.46 ECCS criteria are not impacted. Additionally, based on a conservative evaluation using nominal inputs and assumptions significant margin to 10CFR50.48 ECCS criteria exists even under unlimited oxygen conditions. "This voluntary notification is being made as a result of the 10CFR50.46(a)(3)(ii) requirement to report this issue in accordance with 10CFR50.72 and 10CFR50.73. Background "During a Loss of Coolant Accident (LOCA), oxygen is available in the fuel bundles due to evaporation of the Emergency Core Cooling System (ECCS) water and release of the dissolved oxygen. In addition, oxygen can also be drawn into the reactor vessel later in the LOCA when the vessel pressure has dropped to the Primary Containment (Drywell) pressure. Condensation of the steam in the reactor vessel upper plenum due to the injection of sub-cooled ECCS water causes a reduction in pressure that will result in drawing the non-condensable gases (including oxygen) from the Drywell. "Hydrogen is generated, within the fuel bundles during a LOCA due to Zirconium metal - water reaction caused by high cladding temperatures. It has been postulated that, at the pressure and temperature conditions in the reactor core during a LOCA, free hydrogen and oxygen could combine and release heat that will increase the steam temperature. Since steam is the heat sink when the core is uncovered, an increase in the steam temperature can result in an increase in the PCT for non-jet pump plants including Oyster Creek (BWR/2). The LOCA scenario for a BWR/2 designed plant is different since the core remains uncovered and there is no period of reflooding for large breaks. The cladding will still be heating up when the oxygen from the containment gets into the vessel. This phenomenon also results in an increase in local oxidation. "Based on current core thermal power level and existing margin to limits on power operation there is sufficient margin for analyzed accident scenarios requiring ECCS operation including appropriate compensation to restore the analytical oxidation within 10CFR50.46 criteria and there is no impact on safe operation. This is further supported by the results of conservative evaluation using nominal inputs. As a result of this change in the ECCS model and the consequential adjustment to the allowable MAPLGHR limit, the offsite dose for this scenario is still bounded by our current safety analysis. Therefore, this event is not significant with respect to the health and safety of the public. Corrective Action(s): "An administrative adjustment to our allowable MAPLHGR limits will be imposed to compensate for the estimated change in cladding oxidation and thereby restore the previously analyzed margin on core thermal power limits to within the new ECCS model prediction. Additionally deinerting of the Primary Containment will be constrained to less than 25% rated power-level until more specific analyses are complete. "In accordance with 10CFR50.73, a voluntary LER will be submitted within 60 days with a more detailed discussion of the nature of this change in the ECCS evaluation model, its estimated effect of the limiting ECCS analysis, and a proposed schedule for providing a reanalysis or taking other action as may be needed to comply with this regulation. "The licensee will notify the NRC Resident Inspector." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2004-05-14
40747 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2004-05-11 | 2004-05-14 10:20 | 2004-05-14 | AGREEMENT STATE REPORT - TRITIUM EXIT SIGNS LOST IN SHIPMENT The following information was received via facsimile (North Carolina Incident report 04-19): "The shipment was picked up from SRB Technologies, Inc. in Winston Salem, NC. The shipment was to be delivered to Wild Sales Co. in Santa Fe Springs, CA by Pilot Air Freight (shipment #070743258). Pilot Air Freight picked up a shipment of 14 boxes of which 13 boxes contained 129 tritium exit signs from the licensee on April 23, 2004. The balance of 1 box contained sign accessories/hardware. The sign customer notified the licensee that a box was missing on April 28, 2004. Pilot freight was immediately informed and they began investigating. Final confirmation was given to the licensee on May 11, 2004 that the box could not be located. The missing box contained 10 exit signs each containing 9.9 curies of tritium. The serial numbers of the missing signs are 316493-316502." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2004-05-19
40746 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-05-13 19:15 | 2004-05-13 22:12 | 2004-05-13 | LOSS OF ENS AND COMMERCIAL PHONE LINES TO CONTROL ROOMS "At 1915 CST, Dresden personnel identified that the ENS phone was not operational, either with outgoing or incoming calls. The NRC Ops Center was contacted via the normal commercial phone system and informed of the situation. Call back from the NRC via the commercial phone line failed as Dresden is currently not receiving outside phone calls due to the failure. A call back method through BPO [Bulk Power Operations] has been established. The phone problem appears to be not at the Dresden Site, SBC [local phone provider] is initiating repairs. Current off-site communications are being augmented via personal cellular telephones." The licensee notified the NRC Resident Inspector. | 0 | 98 | 99 | 0 | 98 | 99 | 0 | -1 | -1 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-05-13
40745 | 0 | ENGINEERING CONSULTING SERVICES LTD |  |  |  |  | 2004-05-13 14:30 | 2004-05-13 18:26 | 2004-05-13 | DAMAGED CPN MOISTURE DENSITY GAUGE At approximately 1430 EDT on 05/13/04, an equipment operator backed a truck over a CPN moisture density gauge model MC1DRP, Serial No. MD30506972, containing an 10 milliCurie Cs-137 and a 50 milliCurie Am-241:Be source. The exterior cover of the gauge was damaged, the source rod was stuck in the shielded position at the time the incident occurred. The top shield was broken off. The technician removed personnel from the area and contacted the company headquarters who contacted the manufacturer. The technician placed the gauge in a five gallon bucket filled with gravel. The bucket and gauge are locked in a truck for transportation to the home office in Fredericksburg, VA. Radiation measurement before the gauge was placed in the bucket was 2 millirem per hour at five feet. Radiation measurement after the gauge was placed in the bucket was 0.6 millirem per hour at one meter. The ground where the accident occurred was also surveyed at a slow pace at a distance of 1 inch, and no reading was recorded other than background radiation. The licensee will conduct a leak test of the gauge when the gauge reaches Fredericksburg, VA. They plan to ship the gauge to the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2004-05-13
40744 | 0 | APPLIED TESTING INC |  |  |  |  | 2004-05-13 09:40 | 2004-05-13 16:00 | 2004-05-13 | DAMAGED TROXLER GAUGE At approximately 0940 EDT on 05/13/04, an employee set a Troxler Moisture Density Gauge (Model: 3411B, S/N: 9031, containing an 8 milliCurie Cs-137 (S/N: 750-3440) and a 40 milliCurie Am-241:Be (S/N: 47-5500) source) down to prepare for testing. Another contractor in a pick-up truck drove through and knocked over the gauge. The source was in the locked position when the gauge was knocked over. The employee cordoned off the area and checked the gauge for damage. The gauge had little damage but the source appears to be bent in the stowed position. The gauge will be sent to NorthEast Technical Services for repair or decommissioning. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2004-05-13
40743 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-05-13 10:29 | 2004-05-13 16:47 | 2004-05-13 | NON-ACTIVE LICENSED OPERATOR TESTED POSITIVE FOR ALCOHOL A non-active licensed employee was determined to be under the influence of alcohol during for cause testing. The employee's access has been suspended to the Point Beach Nuclear Plant and all other Nuclear Management Company, LLC (NMC) sites. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2004-05-13
40742 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-05-10 | 2004-05-13 09:17 | 2004-05-13 | MEDICAL MISADMINISTRATION On May 10, 2004 two patients were scheduled for administration of diagnostic dosages of radioiodine. Patient A was scheduled to have administered 2 millicuries I-131 Na - l for a thyroid cancer ("CA") workup to determine the appropriate I-131 Na - l therapeutic dosage for treatment of thyroid cancer. Patient B was scheduled to have administered 200 microcuries of I-123 Na - l for a thyroid uptake and scan to determine the appropriate therapeutic dosage of I-131 Na - l for hyperthyroidism. Both patients were small, elderly, Caucasian women and both had been previously treated at TUH Nuclear Medicine. Patient B (hard of hearing) was checked in as Patient A and responded affirmatively to being addressed as Patient A. The technologist believed he knew the patient, believed the correct patient responded so he administered the 2 millicuries of I-131 Na - I to Patient B. The error was discovered when an Administrative Assistant in the department addressed the patient as Patient A and the patient responded she was Patient B. The prescribing physician informed Patient B of the misadministration during her appointment on May 11, 2004. The prescribing physician informed the referring physician's office of the misadministration on May 11, 2004. This incident occurred because the technologist did not follow departmental, hospital, Radiation Control and Safety Program and QMP policies regarding proper identification of patients. All policies require technologists use two separate methods for verifying the identification of the patient. The technologist thought he knew the patient; however, he was incorrect with this assumption. In addition, the technologist did not use an accepted second method of identifying the patient. The second method of identification used by the technologist was estimating the patient's apparent age with the date of birth listed. No adverse effect is expected for the patient. Patient B was scheduled to receive a therapeutic dose of I-131 Na - I the day after the misadministration occurred. The prescribing physician indicated he would administer the calculated treatment dose minus the 2 millicuries administered from the misadministration. On May 11, 2004 the appropriate dosage for patient B's hyperthyroid treatment was determined to be 17 millicuries. Patient B was administered 15.56 millicuries (prescribed as 17 millicuries - 2 millicuries or 15 millicuries) on May 11, 2004. Technologists shall be expected to strictly follow hospital, departmental, Radiation Control and Safety Program and QMP policies requiring patient identification using a minimum of two identification methods. Identification of patients by a member of hospital staff, such as the technologist performing the procedure, should be eliminated as an approved mechanism for one of the two identification methods. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2004-05-18
40741 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2004-05-11 10:55 | 2004-05-11 18:07 | 2004-05-11 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY DUE TO LOSS OF NORMAL POWER TO TSC The following information was obtained from the licensee via facsimile: "A loss of emergency assessment capability occurred due to a loss of normal power to the Cooper Nuclear Station Technical Support Center [TSC]. At 1055 [CDT], power loss occurred due to a ground fault on the feeder to the motor control center [supplying] power to the TSC. Power was transferred to the alternate feeder for the TSC at 1214 [hrs]. Alternate power was available during the entire time, however due to the nature of the ground fault, transfer was not performed until source of ground was known: (during 'bump' checking of a chiller compressor, the compressor internally shorted causing the ground fault protection circuitry to activate for the feeder breaker [Electrical Panel designated OBFP].) The source of fault has been identified and has been isolated. "Normal power was restored to the TSC at 1443. "The emergency offsite facility and the main control room were unaffected by the ground fault. "The NRC Senior Resident Inspector has been notified of this event." No other safety systems were affected by the loss of the feeder circuit. Prior to finding the fault, the system was undergoing maintenance. The 'bump' check involves momentarily powering the chiller compressor to verify proper and free rotation. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-05-11
40740 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2004-05-07 13:30 | 2004-05-10 11:10 | 2004-05-10 | TROXLER GAUGE RUN OVER BY BULLDOZER AT CONSTRUCTION SITE A Troxler gauge model 3430 containing 10 millicuries Cs-137 and 40 millicuries AmBe-241 was run over by a bulldozer at a construction site in Montgomery County, MD. The device was completely destroyed, but the sources were not broken or leaking. The device was shipped to NE Technical Service in Westminster, MD and will be disposed of at a nuclear waste site in California.. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2004-05-13
40739 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-05-09 20:05 | 2004-05-10 00:11 | 2004-05-10 | BOTH UNIT 2 EMERGENCY DIESELS DECLARED INOPERABLE DUE TO SHIMS/SUPPORTS FOUND TO BE EITHER MISSING OR NOT PROPERLY FASTENED. "2-EE-EG-2H was out of service for scheduled maintenance. During an inspection, 4 shims on the exhaust stack seismic support on the south wall were found missing. The shims provide baseplate bearing on the concrete wall near each anchor bolt and had fallen to the floor. In addition, both lower anchor bolt nuts had worked loose and had fallen to the floor and one of the upper anchor bolt nuts had worked loose and was partially disengaged. "Following this discovery 2-EE-EG-2J was inspected and 3 of the 4 supports were not properly fastened. 2J EDG was declared inoperable based on this discovery. Due to both U-2 Emergency Diesel Generators being in operable the safety functions needed to maintain the reactor in a safe shutdown condition and remove residual heat would have been imparted in the event of a loss of off site power "2-EE-EG-2J was repaired and returned to operable at 2313 EST on May 09, 2004." The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-05-10
40738 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-05-09 01:30 | 2004-05-09 20:48 | 2004-05-09 | FAILURE OF THE HIGH VOLTAGE UF6 RELEASE DETECTION SYSTEM The following information was obtained by the regulatee via facsimile: "At 0130 [hrs. CDT] on 05-09-04, the Plant Shift Superintendent (PSS) was notified of a failure of the C-316 High Voltage UF6 Release Detection System. The High Voltage UF6 detection system was disabled by a computer malfunction. This High Voltage UF6 Release System is designed to activate alarms in the event of a UF6 release. The PSS declared the system inoperable and TSR [Technical Safety Requirement] LCO 2.3.4.4.A actions were implemented to post a continuous smoke watch in the affected area. The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(i); 'An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident.' The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. "The Senior NRC Resident Inspector has been notified of this event." The Automatic Data Processing (ADP) computer can be used to interface with the Process Gas Detection (PGD) system part of which is the High Voltage UF6 detection system. The PSS directed that the ADP be bypassed to isolate the fault from the system. The release detection system was tested satisfactorily and returned to service and the smoke watch was secured. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-05-09
40737 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2004-05-08 20:39 | 2004-05-09 02:56 | 2004-05-09 | MANUAL REACTOR TRIP DURING PHYSICS TESTING DUE TO CONTROL ELEMENT ASSEMBLY SLIPPING 6 INCHES. On May 8, 2004, at approximately 20:39 Mountain Standard Time (MST) Palo Verde Unit 1 operations manually tripped the reactor when a Control Element Assembly (CEA) slipped approximately 6 inches (CEA # 89) while conducting physics testing (at 10E-02 percent power) following Unit 1's eleventh refueling outage. Unit 1 was at normal operating temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core (Initial Conditions: Regulating groups 1, 2 & 5 were fully withdrawn, regulating group 3 was fully inserted, regulating group 4 was being inserted when CEA # 89 slipped approximately 6 inches. Shutdown groups were fully withdrawn). This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. No automatic ESF actuations occurred and none were required. Safety related buses remained energized during and following the reactor trip. No LCOs (Limiting Conditions of Operations) have been entered as a result of this event. No major equipment was inoperable prior to the event that contributed to the event. Unit 1 is stable at normal operating temperature and pressure in Mode 3 (Hot Standby). The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. The Senior Resident Inspector was informed of the Unit 1 reactor trip. | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-05-09
40736 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2004-05-08 13:25 | 2004-05-08 15:58 | 2004-05-08 | OFFSITE NOTIFICATION DUE TO INADVERTENT ACTIVATION OF EMERGENCY SIRENS The following information was obtained from the licensee via facsimile: "At 0912 [EDT] the Salem Township sirens, zone 14, sounded for 3 minutes. All ten sirens in zone 14 sounded. The reason for the siren sounding was unknown at that time. The Sheriff Dispatcher notified Emergency Preparedness of the sirens sounding. Emergency Preparedness called the vendor, Transco, to investigate the siren sounding. Transco went to the 500 [foot] siren tower and polled the siren system and found that the Zone 14 sirens had been activated by a signal from the Sheriff Dispatch office at 0912 [hrs.]. Transco then went to the Sheriff Dispatch office to look at the system and found no problems. At 1158 [hrs.], on 5/8/04, a quiet test, e.g. low noise level test, was conducted for siren 91, next to the Sheriff's office, to ensure the siren system was operating properly. "Discussions with the Sheriff Dispatchers indicated that they were not in the vicinity of the siren console and did not have the siren screen called up. Therefore, it was not possible for the Sheriff Dispatchers to inadvertently activate the sirens. The only other activity in the siren console area was an exterminator working. Therefore, at this time, the most likely cause of the sirens sounding is the exterminator inadvertently activating the Zone 14 sirens. "The Prompt Notification System (sirens) were verified capable of performing [their] intended function (operable), at no time was Emergency Notification capability impaired, it was also validated, that once activated by the inadvertent action, the system responded as expected. This spurious activation does not appear in any way to be related to Event #40734 regarding the test failure on May 7, 2004." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-05-08
40735 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-05-08 04:50 | 2004-05-08 07:07 | 2004-05-08 | REACTOR STARTUP CANCELLED DUE TO ERRATIC SOURCE RANGE MONITOR While performing a unit start-up, SRM 24 was declared inoperable due to erratic indications. SRM 22 was already inoperable which resulted in falling below the Technical Specification 3.3.1.2 mode 2 requirement of 3 operable SRMs. The cause of the erratic indications on SRM 24 is unknown at this time. All control rods were fully inserted at 0527 CDT. The license plans to go to a cold shutdown condition to investigate the erratic source range monitor. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Startup; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-05-08
40734 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2004-05-07 12:00 | 2004-05-07 17:20 | 2004-05-07 | LOSS OF EMERGENCY PREPAREDNESS CAPABILITY DUE TO INABILITY TO ACTIVATE SIRENS The following information was obtained by the licensee via facsimile: "During the May 7, 2004 monthly siren test, it was determined that the Ottawa County Sheriff dispatcher did not have the capability to activate the EPZ [Emergency Preparedness Zone] Sirens. Follow-up investigation determined that a time difference between the control station in the Emergency Operations Facility (EOF) and the sheriff's dispatch control station caused the sheriff's control station to be unable to activate the sirens. This condition was corrected within minutes of discovery, however it appears that the Sheriff's dispatcher had lost capability to activate the sirens when the EOF computer clock was reset due to daylight savings time (reset manually on April 5, 2004). "All 54 sirens were successfully tested using the vendors control station. The ability to [activate] the sirens from the Sheriff's control station was restored. The EOF control station retained the ability to activate the sirens throughout this time period. "Because the sirens could not be sounded from a 24-hour manned station, in accordance with station procedures, this event represents a Loss of Emergency Preparedness Capability. Therefore, this event is reportable within 8 hours of discovery in accordance with 10CFR50.72(b)(3)(xiii)." The Ottawa County Sheriff's Office was notified of this event. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-05-07
40733 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-21 12:32 | 2004-05-07 15:42 | 2004-05-07 | INVALID ACTUATION OF CONTAINMENT ISOLATION SIGNALS IN MORE THAN ONE SYSTEM The following information was obtained from the licensee via facsimile: "On 03/21/04 at 12:32 hours [EST], a JLG Manlift working on the Unit 1 Cooling Tower came into contact with a 230 KV transmission line, causing the loss of one of two off-site power supplies to the plant [Startup Transformer T-10 and its associated loads]. The other Startup Transformer [T-20] assumed the extra electrical load, as designed, and restored power to the station. At the time of this event, Unit 1 was in Mode 5 and Unit 2 was in Mode 1. Both Units continued in Modes 5 and 1, respectively. "As a result of the loss of the T-10 transformer, the following Unit 2 Primary Containment Isolation [Valves][PCIVs] closed on loss of logic power: Containment Atmosphere Control PCIVs HV-25740A, HV-25750A, HV-25776A, HV25780A, HV-25736A, and HV-25742A, HV-25752A, HV-25774A, HV-25782A, HV-25734A. Drywell Sump PCIVs HV-261108 A1 and A2 closed. Reactor Building Chilled Water PCIVs HV-28791 A1 and A2 and HV-28792 A1 and A2 closed. Recirculation Sample PCIV HV-243F019 closed. All isolation signals were successfully reset and the T-10 line was subsequently restored. "The Unit 2 electrical transient event resulted in general containment isolation signals affecting containment isolation valves in more than one system and is therefore being reported per 10 CFR 50.73(a)(1) and 10 CFR 50.73(a)(2)(iv)(A). A voluntary ENS Phone Notification to the NRC, related to this event, was previously made on 03/21/04, due to notification of the Pennsylvania Emergency Management Agency [PEMA], because an emergency vehicle entered plant property. "The above listed systems' Division 1 containment isolation valve actuations were completed and functioned successfully on loss of logic power." The licensee has informed the NRC Resident Inspector of this notification. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-05-07
40732 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-05-07 | 2004-05-07 15:21 | 2004-05-07 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was obtained from the Louisiana Department of Environmental Quality via facsimile: "There was a Medical Event reported on April 7, 2004 concerning an incident that occurred on March 31-April 1, 2004. In the process of constructing a computer generated treatment plan for prostate Brachytherapy, a default switch that changes the source position calculation orientation from 'Connector End' to 'Catheter tip' was not adjusted to the correct orientation (Catheter/Needle tip). This led to the sources stopping short of the target and the total prescribed dose was not delivered. The facility was using a Nucletron Micro Selectron with a 7.315 [Curie] source of Ir-192. There was a total of three fractions for the treatment. One on March 31, 2004 and two on April 1, 2004. The total dose that was delivered was 1800 centigray to the wrong location. The misadministration is being compensated by external beam therapy. [There] are two causes for this event. The design of the default switch automatically selects an orientation that is not used at this facility and cannot be adjusted to default to the correct position. The other cause is operator error in not assuring that the orientation had been changed to read correctly. The patient is self-[referred] from Guatemala. The patient was informed immediately of the misadministration and received further external beam treatment. According to the Radiation Oncologist, no detrimental effects are expected. Actions taken to prevent further recurrence will be the addition of a visible check and documentation that the treatment plan was done with the source positions calculated from the tip end of the catheter or needle. This will be added to the pretreatment checklist which is performed and signed by the Radiation Oncologist, the Physicist, and the Dosimetrist. This checklist will be performed prior to initial treatment and at plan changes and is part of the patient's permanent record. There will also be a written notification to Nucletron regarding the potential danger of misadministration due to inability to change the default on the orientation 'switch'. The design should be that if the connector end is selected, the [planner] should be warned that this will change the source placement." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-05-12
40731 | 0 | MALLINCKRODT |  |  |  |  | 2004-04-21 | 2004-05-06 16:45 | 2004-05-06 | MISSING DEPLETED URANIUM SHIPPING SHIELD The licensee reported that an empty 45.7 lb. depleted uranium shipping shield could not be located. The shield was last reported as being shipped back to St. Louis from Mallinckrodt's Beltsville, MD facility on 5/10/03. After an investigation as to the possible location of the shield conducted in early 2004, it was declared lost on 4/21/04. The licensee has contacted NRC Region 3. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-05-06
40730 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2004-05-06 12:52 | 2004-05-06 16:25 | 2004-05-06 | AUTOMATIC REACTOR TRIP AND ACTUATION OF AUXILIARY FEEDWATER SYSTEM The following information was received from the licensee via facsimile: "On May 6, 2004, with the reactor at 100 percent power in MODE 1, an unplanned actuation of the reactor protection system occurred. At 1252 [EDT] the reactor was automatically tripped from a power range negative flux rate trip signal. The auxiliary feedwater system actuated as expected to stabilize steam generator levels. All systems functioned as required and no other safety systems were actuated. All control rods inserted on the reactor trip. The operations staff responded to the event in accordance with applicable plant procedures. The plant stabilized at normal operating no-load reactor coolant system temperature and pressure following the reactor trip. Steam generator water levels are being maintained using normal main feedwater. All emergency core cooling system equipment is available. The plant electrical system is available and in a normal configuration. The cause of the plant trip is under investigation. "This condition is being reported as an unplanned reactor protection system actuation and specified system actuation in accordance with 10 CFR 50.72(b)(2)(iv)(B) and10 CFR 50.72(b)(3)(iv)(A) ." During the transient, a steam generator power-operated relief valve lifted momentarily and then re-seated. No reportable radiological release occurred during the event. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-05-06
40729 | 0 | VA NATIONAL HEALTH PHYSICS PROGRAM |  |  |  |  | 2004-05-06 | 2004-05-06 14:47 | 2004-05-06 | LOSS OF FOUR TRITIUM EXIT SIGNS The following information was obtained from the Master Materials License Holder via facsimile: "The loss occurred at a medical permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853 01 VA. The permittee is the Clement T. Zablocki VA Medical Center, Milwaukee, Wisconsin. "The loss occurred circa 2001 and was discovered on May 6, 2004. The basis for the report is under 10 CFR 31.5(c)(10) in that radioactive materials obtained under a general license were lost and the reporting requirements in 10 CFR 20.2201 must be followed. "Specifically, the permittee stated four tritium exit signs were apparently disposed or discarded during a facility construction project circa 2001. The signs were last seen in 2000. "The signs were either of two models. 'The first model is a 11.5 Curie sign from Shield Source Incorporated. The second model is a 20 Curie sign from SRB Technology. The signs were manufactured circa 1994. "The Department of Veterans Affairs will evaluate the circumstances related to the loss of radioactive materials and submit a written report to NRC, Region III, within 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | WI | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-05-06
40728 | 0 | POINT BEACH | 1 |  |  | [1] W-2-LP,[2] W-2-LP | 2004-05-06 10:46 | 2004-05-06 13:30 | 2004-05-06 | REACTOR VESSEL HEAD NOZZLE WELD AREA FLAW "During performance of NDE examinations of the Point Beach Nuclear Plant (PBNP) Unit 1 reactor pressure vessel (RPV) head required by the First Revised NRC Order (EA-03-009), flaw indications were identified on Nozzle 26. The ultrasonic examination (UT) signal for nozzle 26 identified flaw indications in the J-groove weld area that extend into the CRDM tube base material. "A dye-penetrant (PT) examination of the nozzle 26 CRDM J-groove material was also performed. The PT exams showed minor surface indications that required further evaluation. Following minor excavation of the weld surface, additional examinations of the J-groove surface were performed. The results of these exams indicated the existence of flaws in the weld that do not meet accepted flaw evaluation guidance. "Based upon preliminary analysis, it is expected that these indications would not be found acceptable under ASME standards. Therefore, this condition represents degradation of a principal safety barrier reportable under 10 CFR 50.72(b)(3)(ii)(A). "PBNP Unit 1 Nozzle 26 is planned to be repaired prior to placing the RPV Head back into service. "The condition was determined to be reportable at 1046 CDT on May 6, 2004. The licensee has notified the Resident Inspectors." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-05-06
40727 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-05-05 13:27 | 2004-05-05 15:29 | 2004-05-05 | UNUSUAL EVENT DUE TO LOSS OF OFFSITE POWER "Unit 3 scrammed as a result of a loss of offsite power. An unusual event was declared and the state was notified at 1352 [EST]. A Group I, II, and III [isolation] was received. The Isolation Condenser was manually initiated for reactor pressure control. HPCI [High Pressure Coolant Injection] was manually initiated to control reactor water level. All systems operated as expected. The Unit 3 and 2/3 emergency diesel generators automatically started and closed on to their respective busses. The reason for the loss of offsite power is not know at this time. Switchyard work was in progress at the time of the event." All control rods fully inserted into the core during the reactor scram. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 05/05/04 AT 1746 FROM D. GRONEK TO W. GOTT * * * "At 1601 Dresden Station Unit 3 terminated from an Unusual Event for a loss of offsite power. Bus 8 in the 345 KV switchyard was restored from circuit breaker 4-8. Transformer 32 was energized and supplied to Bus 33 and 33-1. Bus 34 remains energized from the Unit 3 SBO diesel generator. Bus 34-1 remains powered from the Unit 3 emergency diesel generator. Actions are being taken to restore those busses to the normal offsite power source. Plant cooldown is in progress and the unit is proceeding to Mode 4. Reactor water level is being maintained by HPCI and reactor pressure is being controlled with HPCI and the Isolation Condenser. LPCI is running in the torus cooling mode of operation. The LCO action requirement for secondary containment inoperability was exited at 1630." The licensee notified the State and the NRC Resident Inspector. Notified DHS (McIntire), FEMA (M. Eaches), DIRO (Nieh), R3DO (Lipa) and NRR EO (Lyons). | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | UNUSUAL EVENT | 3 | IL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-05-05
40725 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-05-04 15:00 | 2004-05-05 11:28 | 2004-05-05 | AGREEMENT STATE RADIOACTIVE CONTAMINATION DUE TO MELTED SOURCE State of Ohio reported that a Cs 137 source was destroyed in a furnace at the Timken Steel Company. The initial detection of a problem occurred with high radiation being detected in the bag house exhaust system. Dose rates are 660 micro R/hr in the bag house. It is not known at this time the origin of the radioactive material. The licensee is conducting surveys to determine if there is contamination anywhere else in the facility. The licensee is also conducting an inventory of their radioactive material to determine if it was their material. It is suspected that the radioactive material may have been in a load of scrap steel that was being melted for reprocessing. The licensee has contacted a contractor to perform decontamination activities. Licensee notified the NRC Agreement States representative (J. Lynch). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2004-05-10
40724 | 0 | OCONEE | 1 |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-05-04 16:55 | 2004-05-04 19:08 | 2004-05-04 | UNANALYZED CONDITION AND POTENTIAL LOSS OF CONTAINMENT SAFETY FUNCTION "NOTE: Oconee Unit 2 is DEFUELED (No Mode) in a refueling outage. "Oconee has discovered a new scenario where the double ended guillotine rupture addressed by IE Bulletin 80-04 is not the worst case with respect to containment pressure following a Main Steam Line Break (MSLB). Therefore this scenario is being reporting as an Unanalyzed Condition and a potential loss of the containment safety function. This new scenario involves a range of MSLB break sizes smaller than the double ended guillotine rupture addressed by IE Bulletin 80-04, with the break located inside containment, and with a concurrent Loss Of Offsite Power (LOOP). "This event scenario is still being evaluated but it appears to result in containment pressures in excess of the 59 psig limit discussed in the UFSAR. Preliminary results indicate that pressure would not exceed the containment 'ultimate capacity' of 144 psig. "Analysis has shown that the Steam Generator tube stresses remain within acceptable limits for this event scenario so that no additional RCS leakage would occur. As a result, the offsite dose for this scenario is bounded by previous scenarios for a MSLB outside containment. "Background The AFIS (Automatic Feedwater Isolation System) Circuitry required by Tech Specs 3.3.11, 3.3.12, and 3.3.13 is intended to isolate Feedwater from the steam generators in the event of a Main Steam Line Break (MSLB) by closing the Feedwater Control Valves and preventing operation of the Emergency Feedwater Pumps. Tech Spec 3.7.3 requires the Feedwater Control Valves to be operable and provides an 8 hour Allowed Outage Time (AOT) if they are not. If the AOT is exceeded, the affected unit must be in Mode 3 within an additional 12 hours. The Feedwater Control Valves are air operated and fail as-is on loss of Instrument Air. Low MS pressure causes AFIS to signal the valves to close. Emergency Feedwater Pumps are interlocked based on rate of MS pressure drop. "Scenario: ONS identified a new scenario involving a MSLB smaller than the double ended guillotine rupture addressed by IE Bulletin 80-04, located inside containment, and occurring concurrent with a LOOP. "In this scenario, the LOOP results in the loss of power to the permanently installed plant instrument air compressors, so that instrument air pressure would begin to decay. The smaller MSLB break size slows the rate of pressure loss from the affected MS line. Break sizes exist such that by the time the MS system pressure decays to the AFIS actuation setpoint, instrument air pressure might become inadequate to close the Feedwater Control Valves. Also, the low rate of change of MS pressure might not satisfy the AFIS rate based setpoint for actuating the EFW pump interlock. If the control valves remain open or if the EFW pumps are allowed to operate, additional inventory would reach the steam generators and flash to steam. Since the scenario requires the break to be located inside containment, this would result in increased containment pressures. "Initial Safety Significance: The Main Steam Line Break inside containment is a low probability event. Also, although the MSLB scenario includes the assumption of some primary to secondary leakage, the analysis shows that Steam Generator tube stresses remain within acceptable limits for these break sizes, so that no additional RCS leakage would occur. As a result, the offsite dose for this scenario is still bounded by the scenario for a break outside containment. Therefore this event is not significant with respect to the health and safety of the public. "Corrective Action(s): A diesel compressor connected to the Instrument Air header has been placed in operation to assure a source of instrument air in the event of a LOOP. Additional actions for permanent resolution are being evaluated." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 100 | 100 | 0 | 100 | -1 | 0 | -1 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | Power Operation |  | Power Operation | Power Operation |  | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-05-04
40723 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-05-03 16:00 | 2004-05-04 14:10 | 2004-05-04 | CRITICALITY CONTROL 24-HOUR (BULLETIN 91-01) REPORT "At 1600 on 5-03-04, the Plant Shift Superintendent was notified of a violation of SRI 5.4.1 of NCSE 052. The oil seals and bearing housing for the C-310 cell 6 stage 2B pump failed allowing significant quantities of oil to be accessible for entry to the cascade through a failed process seal in violation of SRI 5.4.1 in NCSE 052. Also, greater than 3.7 gallons (5.1 [measured]) of oil was found inside the pump casing in violation of the unlikely arguments which limit the amount of oil that will enter the process side of the pump. "The NRC Senior Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: While the moderation parameter of 3.7 gallons of oil was exceeded, NDA measurements showed the pump contained less than a safe mass of uranium and double contingency has been established under NCSA GEN-010. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to occur, greater than a critical mass of uranium would have to be in the pump and greater than 3.7 gallons of oil would have to enter the process side of the cell and moderate the uranium deposit in a critical configuration. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency is maintained by implementing two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The pump contains less than the [DELETED] 235U process limit at an enrichment of less than 5.5 wt %235U. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on the oil seals and bearing housing to limit the amount of oil that may be accessible for entry to a failed process seal to less than 3.7 gallons. This SRI failed; therefore double contingency was not maintained. "The second leg of double contingency relies on shutting down the affected equipment as soon as practical after discovery of a catastrophic process seal failure to make it unlikely to continue to operate for any appreciable length of time with wet air inleakage. Since the cell was shut down in accordance with control 3.2.2, but significant wet air inleakage continued for a period of time which allowed greater than 3.7 gallons of oil to enter the process side of the pump, the unlikely argument was violated. Since greater than 3.7 gallons of oil entered the process side of the cell, double contingency was not maintained. "Since double contingency is based on two controls on one parameter, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: NDA measurements showed the pump contained less than a safe mass of uranium and double contingency has been established under NCSA GEN-010. "NUCLEAR CRITICALITY SAFETY CONTROLS INVOLVED AND THEIR IMPACT ON DOUBLE CONTINGENCY: Double Contingency Double contingency is maintained by implementing two controls on moderation. "The first leg of double contingency relies on the oil seals and bearing housing to limit the amount of oil that may be accessible for entry to a failed process seal to less than 3.7 gallons. This SRI failed; therefore double contingency was not maintained. "The second leg of double contingency relies on shutting down the affected equipment as soon as practical after discovery of a catastrophic process seal failure to make it unlikely to continue to operate for any appreciable length of time with wet air inleakage. Since the cell was shut down in accordance with control 3.2.2 but significant wet air inleakage continued for a time period which allowed greater than 3.7 gallons of oil to enter the process side of the pump, the unlikely argument was violated. Since greater than 3.7 gallons of oil entered the process side of the cell, double contingency was not maintained. "Since double contingency is based on two controls on one parameter, double contingency was not maintained. The NCS parameter of moderation was not maintained. "Potential Critical Pathways: In order for a criticality to occur, greater than a critical mass of uranium would have to be in the pump and greater than 3.7 gallons of oil would have to enter the process side of the cell and moderate the uranium deposit in a critical configuration. "Safety Significance: While the moderation parameter of 3.7 gallons of oil was exceeded, NDA measurements showed the pump contained less than a safe mass of uranium and double contingency has been established under NCSA GEN-010. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-05-04
40722 | 0 | TES CONSULTANTS |  |  |  |  | 2004-05-04 08:00 | 2004-05-04 13:34 | 2004-05-07 | DAMAGED TROXLER MOISTURE DENSITY GAUGE At approximately 0800 EDT on 05/04/04, an equipment operator backed an excavator over a Troxler density gauge model 3430, Serial No. 29858, containing an 8 millicurie Cs-137 and a 40 millicurie Am-241:Be source. The exterior cover of the gauge was damaged, the source rod was bent and stuck in the exposed position at the time the incident occurred. The technician removed personnel from the area and contacted the local Hazmat fire department which placed the damaged gauge in a steel drum. The licensee is in possession of the steel drum containing the damaged gauge and has plans to return it to the manufacturer for disposal. The licensee believes that based on the structure of the damaged gauge, there was no source leakage and they are in process of performing personnel exposure calculations as warranted. The licensee contacted Region 3 and will submit a written report of this incident, as required. * * * UPDATE AT 0937 EDT ON 05/07/04 TO JOHN MACKINNON FROM NICK HUTCHINSON * * * Correct gauge serial number mentioned above should be 30162 instead of 29858. R3DO (Christine Lipa) & NMSS (Roberto Torres) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MI | MAT | [5 empty] | 0 | 2004-05-04
40721 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2004-04-30 14:38 | 2004-05-03 15:29 | 2004-05-03 | "On 4/30/2004, during Refueling Outage 1 R18, ultrasonic testing of the reactor vessel head identified two axial indications on Control Rod Drive Mechanism, nozzle 61. The indications were located on the outside diameter of the nozzle on the lower hillside. One of the flaws was at the toe of the fillet weld and extended below the fillet weld cap. The second flaw extended the full length of the weld and just below the toe of the fillet weld. "There were no indications that either of the flaws was through-wall or through-weld and both were typical of Primary Water Stress Corrosion Cracking. No formal evaluation of these flaws has been completed; however, based on past analysis it is expected that they would not be found acceptable under ASME standards and, therefore, represent degradation of a principal safety barrier reportable under the referenced criterion. This condition was determined to be reportable at 0839 CDT on 5/3/2004. "The nozzle will be repaired prior to startup from the current refueling outage. "The reactor vessel head inspection was subsequently completed with no additional flaws identified." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-05-03
40720 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-05-03 01:25 | 2004-05-03 09:42 | 2004-05-13 | NON-LICENSED EMPLOYEE TESTED POSITIVE FOR ALCOHOL A non-licensed employee was identified as under the influence during for cause testing. The employee's access to the plant has been placed on hold. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * * UPDATE FROM RON FRANTZ TO MIKE RIPLEY 5/13/04 AT 1132 EDT * * * Followup testing at the hospital confirmed the previous positive test results. The employee's plant access remains suspended. The employee has been referred to the Employee Assistance Program. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R3RDO (Stone) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2004-05-03
40719 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2004-05-02 02:17 | 2004-05-02 04:09 | 2004-05-02 | MANUAL SCRAM DUE TO RISING TORUS TEMPERATURE DUE TO STUCK OPEN ERV "Operators inserted a manual scram at 0217 (EDT) in anticipation of torus bulk temperature approaching 110 degrees F following an Electromatic Relief Valve (ERV) failing to close during ERV testing. Technical Specification 3.3.2.e requires the insertion of a manual scram prior to torus bulk temperature reaching 110 degrees F. The maximum average torus temperature was 104 degrees F. "Operators opened ERV 123 at 0209 for post maintenance testing from approximately 19% power. The ERV subsequently stuck open. Operators performed the off-normal procedure for a stuck open ERV, but this failed to shut the valve. This ported steam from the reactor vessel to the torus resulting in an uncontrolled torus temperature rise. Operators placed torus cooling in service but this did not stop the rising torus temperature. Following the manual scram, cooldown, and depressurization, shutdown cooling is being placed in service. "Immediately following the manual scram, a turbine trip signal actuated the logic for high pressure coolant injection. High pressure coolant injection actuated and operators controlled level above 53 inches. "With the ERV stuck open, the cooldown rate could not be controlled. The cooldown rate was approximately 190 degrees F during the first hour following the scram." All control rods fully inserted into the core. Decay heat is being removed by shutdown cooling (in service at the time of the report). The operators intend to cooldown to cold shutdown. The electrical buses are stable. Nine Mile Point Unit 2 was not affected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 19 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2004-05-02
40718 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-04-01 03:06 | 2004-04-30 17:20 | 2004-04-30 | INVALID AUTOMATIC START OF EMERGENCY DIESEL GENERATOR DURING SURVEILLANCE TEST "The purpose of this report is provide a telephone notification under 10 CFR 50.73 (a)(2)(iv)(A) in lieu of submitting a written LER for an invalid actuation from other than the Reactor Protection System (RPS) when the reactor is critical. "On April 1, 2004 at 0306, during a refueling outage the Division I Diesel Generator auto-started during the performance of a bus under-voltage surveillance test. The diesel generator successfully started with the Divisional Switchgear remaining energized from off-site power. The diesel was secured following verification of the start to be a result of an invalid signal. "Prior to the engine start, the diesel was removed from service to support planned maintenance activities. In conjunction with these activities surveillance testing was being performed which required the diesel generator to be unavailable. When the maintenance activities were completed the diesel was restored to available. The relay and control testing was recommenced without realizing the impact that restoring the tag out would have on the testing. The diesel started successfully, however it did not energize the switchgear, as the switchgear remained energized from its normal power supply." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-04-30
40717 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-04-29 17:17 | 2004-04-30 15:04 | 2004-04-30 | A STATE OF CALIFORNIA LICENSEE CADMIUM-109 SOURCES LOST IN BRAZIL At 1717 PDT on 04/29/04, the CA Licensee, Isotope Products Laboratory, Valencia, CA, Radiation Safety Officer notified a CA Radiation Control Program Officer by voicemail that a transport container containing several sealed sources totaling 50 millicuries of Cadmium-109 was shipped from Burbank, CA to Chile. The shipment was transported by air on Lan Chile Airlines from Los Angles International Airport to Chile. However, the aircraft landed in Brazil and the package was offloaded at the Brazilian airport. The Brazilian Customs Agents at the Brazilian Airport are on strike and the package is thought to be in a warehouse at the airport (location unknown). Lan Chile Airlines notified the International Air Transport Association. The transport container contains a sealed source comprised of several sealed sources in a ring configuration; the ring being only a holder for the sealed sources. The source is used for X-ray fluorescence. The RSO plans to provide information on the packaging and labeling, transport index, surface reading, shipper, date/time shipped from Isotope Products Laboratory, leak tests, contact name/phone number at Lan Chile Airlines, Brazil Airport location, number of sources and activity of each source, time/date when package was determined to be missing and by whom. There has been no press/media involvement. CA does not consider this event to be a threat to health and safety. The licensee was notified of this event at 1510 PDT on 04/29/04. CA received the voicemail at 1100 PDT on 04/30/04. CA plans to issue a written report to the NRC within 30 days. * * * UPDATE PROVIDED AT 1842 EDT ON 04/30/04 FROM KAUFMAN TO JOLLIFFE * * * The licensee reported to CA that the Brazilian Customs have the package in their possession. Notified R4DO Charles Marschall and NMSS EO Patricia Holahan. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-05-05
40716 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-29 15:57 | 2004-04-29 18:09 | 2004-04-29 | IDENTIFIED LEAKAGE LIMIT EXCEEDED FOR 5 MINUTE PERIOD DUE TO LIFTED LETDOWN LINE SAFETY VALVE "D.C. Cook Unit 2 was performing post-maintenance testing on a solenoid valve associated with a letdown orifice valve and realigning letdown flowpath when safety valve 2-SV-51 (Regenerative Heat Exchanger Letdown Outlet Safety Valve) lifted on 4/29/04 at 15:57 EDT, relieving 323 gallons of water to the Pressurizer Relief Tank over a five (5) minute period before letdown was isolated. Average leak rate was approximately 65 gallons per minute, greater than the 25 gallon per minute identified leak rate limit for an Unusual Event [10CFR50.72(a)(1)(i)]. This was a rapidly concluded event of a five (5) minute duration. Time of discovery for leakage quantity and reportability was 17:10 on 4/29/04. "Therefore, for a five (5) minute period, D.C. Cook Unit 2 met the conditions for an Unusual Event. However, this fact was discovered after leakage was stopped. Unit 2 is stable at approximately 100% reactor thermal power with the excess letdown system in service. "An Unusual Event was NOT declared, but the conditions for an Unusual Event were met between 15:57 and 16:02 on 4/29/04. This ENS notification is being made within one hour of the discovery of the undeclared event." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | MI | POW | [5 empty] | 0 | 2004-04-29
40715 | -1 | COGEMA MINING INC |  |  |  |  | 2004-04-28 15:00 | 2004-04-29 11:03 | 2004-04-30 | MINOR WASTE POND LEAKAGE AT COGEMA MINING The licensee reported the discovery of minor leaks detected in two of four surface evaporator waste ponds used as a portion of an uranium milling process. Each pond has a leak detection system which is checked once per week. The minor leaks were detected on 4/28/04 indicating some minor leakage through the pool liner. The licensee stated there was no release of liquid to the environment. Corrective actions planned are to pump down the two ponds and inspect and repair the liner as needed. This report was made pursuant to License Condition 11.4 which specifies to notify the NRC of any spills or leaks. The licensee also notified the Wyoming Department of Environmental Quality. *****RETRACTED ON 4/30/04 AT 1115 FROM Nicholson TO LAURA***** The licensee determined this event was not reportable because 10 CFR40.60 and 10 CFR20.2202 did not apply. The leakage was very minor and none was released to the environment. Notified NMSS (J. Hickey) and R4DO (C. Marschall). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | WY | MAT | [5 empty] | 0 | 2004-04-29
40714 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-28 22:30 | 2004-04-29 01:40 | 2004-05-28 | HPCI SYSTEM INOPERABLE FOLLOWING PLANNED MAINTENANCE "During post maintenance testing following a High Pressure Coolant Injection (HPCI) System outage, the HPCI System was not declared operable due to unstable operation - oscillations of turbine speed (300-400 RPM), pump flow (600 GPM) and discharge pressure (300-550 psig) were seen in both automatic and manual flow control during the System Operability Periodic Test. HPCI had been declared inoperable at 0410 on 4/28/04 and placed under clearance to support planned maintenance on the Flow Controller, Flow Transmitter, system valves and condensate pump. The cause of the unstable operation is currently being investigated." The licensee notified the NRC Resident Inspector. * * * * RETRACTION FROM S. TABOR TO M. RIPLEY AT 1423 ET ON 5/28/04 * * * * "On April 28, 2004, at 0410 hours, the High Pressure Coolant Injection (HPCI) system was declared inoperable to support scheduled maintenance on the HPCI system. To satisfy post maintenance test requirements and support restoring the HPCI system to an operable status, surveillance test, OPT-09.2, "HPCI System Operability Test," was performed. During this testing at 2230 hours, oscillations in pump flow, pressure, and turbine speed were observed in both the automatic and manual flow control modes of operation. Based on the test results, HPCI remained inoperable until the cause of the oscillations could be identified, corrective actions implemented, and the system satisfactorily tested. On April 29, 2004, at 0140 hours, the NRC was conservatively notified (Event Number 40714), in accordance with 10 CPR 50.72(b)(3)(v)(D), of a condition that at the time of discovery could have prevented the fulfillment of the HPCI safety function. "Troubleshooting determined that the HPCI flow controller to the 2-E41-C002-CNV Ramp Generator Signal Converter (RGSC) was subject to spurious deviations. The RGSC was removed from its installed position and bench tested. Circuit review and testing determined that electronic component degradation was the most likely cause of the RGSC output signal perturbations. A new RGSC was calibrated and installed. After installation, in place testing showed that the new ramp generator did not exhibit signal variations. A final HPCI system operability test was performed and verified that the HPCI system was responding normally. On May 1, 2004, at 1220 hours, the HPC1 system was restored to service. "Reportability Discussion: NUREG-1022, Rev. 2, Section 3.2.7 (page 56) lists types of events or conditions that are generally not reportable under 10 CFR 50.72(b)(3)(v) and 10 CFR 50.73(a)(2)(v) criteria. The list of not-reportable conditions includes: Removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function). "On April 28, 2004, the HPCI system was removed from service to support a planned maintenance system outage. In addition, surveillance testing was performed to support system restoration following the maintenance outage for testing in accordance with an approved surveillance procedure. Based on the post maintenance test results, the HPCI system was declared inoperable and since the HPCI system is a single train safety system, an ENS notification was made. However, further evaluation of the condition determined that no condition was discovered that could have prevented the HPCI system from performing its functions. The following information provides the basis for that determination: "Review of all applicable operating data collected during HPCI system testing performed from the time of discovery of the oscillation concern indicates that (1) the resulting HPCI speed spikes were in the positive direction and therefore no concern related to the inability of HPCI to provide adequate vessel level makeup existed, (2) the RGSC output perturbations followed a consistent pattern and the magnitude of the associated control problem would not have become more severe for a period longer than the assumed HPCI mission time, and (3) none of the excursions experienced were high enough to cause a system trip at the 5000 plus/minus 100 rpm overspeed trip setpoint. Even if a spurious speed spike resulted in a HPCI overspeed trip, the HPCI overspeed trip is designed to automatically reset and allow the system to ramp back up to operating speed. Given these facts, there was no observed performance that represented a loss of system function. Had HPCI been called upon to inject during the time that the condition resulting in HPCI flow oscillations existed, the system would have met all functional requirements. "Carolina Power & Light Company, doing business as Progress Energy Carolinas, Inc., has determined that this event does not meet the 10 CFR 50.72 or 10 CFR 50.73 reporting criteria and the notification for Event Number 40714, is retracted. The resident inspector has been notified." Notified R2 DO (R. Ayres). | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-04-29
40713 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-04-28 15:36 | 2004-04-28 18:50 | 2004-04-28 | MANUAL REACTOR SCRAM DUE TO SPURIOUS TRIP OF 2A REACTOR RECIRCULATION MG AND PUMP "On 4/28/04 at 1536 [CDT], Dresden Unit 2 experienced a trip of the 2A Recirc MG set and associated recirc pump. This placed the unit in the immediate scram region of the power to flow map. The Unit NSO manually scrammed the reactor in accordance with the immediate operator actions of DOA 202.01. "Troubleshooting is in progress to determine the cause of the 2A Recirc MG set trip. There were no Electromatic Relief or Safety Relief Valve actuations. There were no ECCS initiations. PCIS Group 2 and Group 3 Isolations occurred as expected due to normal reactor water level decrease following the scram. All systems responded as expected following the reactor scram. "This report is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(B) for an actuation of the RPS and 10 CFR 50.72(b)(3)(iv)(A) for Group 2 and 3 actuations." All control rods fully inserted, the electrical grid is stable, ECCS and the EDGs remain operable. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 66 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-04-28
40712 | 0 | DRESDEN |  | 2 | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-04-28 12:09 | 2004-04-28 18:50 | 2004-04-28 | CONTROL ROOM HVAC INOPERABLE "During routine alignment of the Control Room HVAC system it was determined the 2/3-5741-053B damper failed to close as required. The damper is required to close to isolate outside air to the control room for accident conditions. "Because of the damper failure the Control Room Emergency Ventilation System (CREVS) was declared inoperable at 1209 on 4/28/04. "The CREVS is a single train system utilized to mitigate the consequences of an accident and this event is reportable under 10 CFR 50.72(b)(3)(v)(D). (Exelon Reportability Manual Section - SAF 1.8)" The licensee notified the NRC Resident Inspector. | 0 | 52 | 100 | 0 | 52 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-04-28
40711 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-28 13:07 | 2004-04-28 13:55 | 2004-04-28 | UNUSUAL EVENT DECLEARED DUE TO AN ELECTRICAL FAILURE IN A NON-VITAL LOAD CENTER LOCATED IN THE UNIT 2 REACTOR BUILDING On 04/28/04 at 1325 EDT, Susquehanna declared an Unusual Event due to an electrical failure in a power distribution panel at a non-vital load center located in the Unit 2 Reactor Building. The affected load center supplies electrical power to the Main Condenser Vacuum system causing plant operations to be reduced to 80% reactor power. Unit 1 has not been affected by this incident and Unit 2 remains stable at 80% reactor power. The licensee terminated the Unusual Event at 1552 and is investigating the cause of the incident which appears to have been a phase-to-phase fault on the 13.8 KV load center feeder cable. Currently, load center 2B250 is being fed through an alternate feeder so that associated systems can be placed back in service. Unit 2 is making preparations to return to full power. There were no personnel injuries nor radioactive releases as a result of this event. The licensee notified the NRC Resident Inspector, Luzerne and Columbia county emergency management agencies, the Pennsylvania Emergency Management Agency and has issued a press release. Notified the following of the termination of the Unusual Event: R1DO(Barkley), DIRO (Frant), NRR (Marsh), DHS (E. McDonald) and FEMA (D. Barden). | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2004-04-28
40710 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-04-27 16:16 | 2004-04-28 12:48 | 2004-05-03 | PROCEDURAL ACCEPTANCE CRITERIA FOR DIESEL DRIVEN FIRE PUMP FUEL OIL VISCOSITY NOT MET "In the process of performing an assessment of the Hope Creek diesel driven fire pump fuel oil supply, a review of the most recently performed fuel oil analysis was performed. This review identified that a fuel oil sample analysis performed on February 11, 2004, to satisfy the 92-day surveillance requirement specified in procedure NC.FP-AP.ZZ-0005, 'Fire Protection Surveillance and Periodic Test Program,' showed that the fuel oil did not meet the procedural acceptance criteria for viscosity (was low out of specification). The diesel driven fire pump was not declared inoperable at this time and no compensatory measures were put in place. Upon discovery of the out of specification fuel sample, the diesel driven fire pump was declared inoperable on April 27, 2004 at 1616 hours and compensatory measures were established. Although the diesel driven fire pump is inoperable due to failure to meet this acceptance criteria, engineering judgment based upon vendor recommended viscosity requirements and satisfactory surveillance pump performance indicates that the diesel driven fire pump would continue to operate and perform its necessary functions with the lower viscosity fuel oil. "Failure to declare the diesel driven fire pump inoperable and establish appropriate compensatory measures is contrary to the provisions of Hope Creek Operating License Section 2.C.7, 'Fire Protection'. This event is being reported in accordance with Hope Creek Operating License Condition 2.F which requires a 24 hour notification for violation of the requirements of Section 2.C of the Operating License." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BRADY TO RIPLEY ON 05/03/04 AT 1749 EDT * * * "An investigation was performed regarding the out of specification fuel oil sample for the diesel driven fire pump that identified that the Chemistry procedure used to perform the fuel oil sample analysis contained testing criteria for viscosity that differed from the requirements of the testing criteria in procedure NC-FP-AP.22-0005, 'Fire Protection Surveillance and Periodic Test Program.' The Chemistry procedure required viscosity testing to be performed at 40 deg C and the Fire Protection surveillance procedure acceptance criteria requires testing for viscosity at 20 deg C. A fuel oil sample obtained on April 26, 2004 was re-analyzed using the required testing parameters of the Fire Protection surveillance procedure and was determined to be within acceptance criteria (satisfactory). A review of previous fuel oil sample analysis data back to August 2000 was performed and compared to the current testing results. The current test results were determined to bound the previous test data. Based on this information, the diesel driven fire pump fuel oil has been acceptable throughout this time period. The diesel driven fire pump was returned to an operable status and the impairment closed. Since the pump remained operable, there was no violation of the Fire Protection Program. The report for violation of License Condition 2.C.7 of the Operating License is being retracted." The licensee will be notifying the NRC Resident Inspector. Notified R1DO (A. Della Greca). | 74 | 0 | 0 | 74 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW | [5 empty] | 0 | 2004-04-28
40709 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2004-04-27 17:14 | 2004-04-27 18:50 | 2004-04-27 | LOSS OF COMMUNICATION CAPABILITY THROUGH ENS LINE The licensee was notified by the phone communications provider of a loss of all communications that affected the licensee's Emergency Notification System (ENS) line. The licensee has provided the NRC Operations Center with a back up cell phone. The ENS capability is expected to be restored by 23:00 tonight and after restoration of the phone lines, the licensee will verify ENS functionality. It is believed that the loss of communications was due to maintenance work being performed by the provider on the fiber optics lines. The NRC Resident Inspector was notified by the licensee via voice mail phone message. * * * UPDATE ON 04/27/04 AT 20:24 EDT FROM D. KENNEY TO A. COSTA * * * The ENS line has been restored at 19:33 on 04/27/04. Communications with the US NRC Operations Center was tested satisfactorily. The NRC Resident Inspector will be notified by the licensee via voice mail phone message. Notified the R1DO (Barkley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-04-27
40708 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-03-19 11:30 | 2004-04-27 16:06 | 2004-04-27 | A STATE OF CALIFORNIA LICENSEE HAS LOST A CESIUM 137 SEED The licensee reported that at approximately 1130 am, the physicist was involved in removal of cesium 137 seeds from an implant. The seeds were counted and accounted for in the patient's room after removal. They were then brought to the radiation oncology hot lab for placement into the safe. While removing them from the "Heyman Carrier" the physicist encountered some difficulty with one of the seeds which resulted in its being "flung" behind the counter in the hot lab and "lost." The Radiation Safety Office was notified and an initial search for the seed (activity 10 mg Ra equivalent - 25 millicuries) did not locate it. The same afternoon the RSO presumably located the seed lodged in the crack of the counter. Because of its location the counter was required to be taken apart. The State was informed by RSO on April 26, 2004 that final retrieval will be made in approximately two weeks when they receive their new counter table and safe so that the remaining seeds can be removed and present counter cut to retrieve the lost seed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-04-30
40707 | 0 | US DEPT OF VETERANS AFFAIRS |  |  |  |  | 2004-04-20 | 2004-04-27 13:20 | 2004-04-27 | DOSE TO AN EMBRYO/FETUS On April 20, 2004, a female patient was administered 6 microcuries of I-131 sodium iodide orally and on April 21, 2004, 12 millicuries of Tc-99m (Tc04). An investigation was undertaken after it was determined that the patient was pregnant. The duration of gestation was estimated as 10 weeks +/- 1 week. The dose to the embryo/fetus occurred on April 20-21, 2004, and it was discovered on April 26, 2004. Outside experts estimated that, if the thyroid were functioning, the fetus received a dose of 6.6 rem, and if the thyroid were not functioning, a dose of 0.5 to 1 rem. The permittee has implemented initial corrective actions to prevent a recurrence of the circumstances that resulted in the dose to the embryo/fetus. The permittee is aware of the requirements for notifying the patient and the referring physician. The Department of Veterans Affairs will evaluate the circumstances related to this incident and will submit a written report to NRC, Region III, within 15 days. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | EMBRYO/FETUS DOSE > 50 mSv | [9 empty] | NON EMERGENCY | 1 | AL | HOS |  | 35.3047(a) |  |  |  | 0 | 2004-04-27
40706 | -1 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-26 09:30 | 2004-04-27 09:21 | 2004-04-29 | NON-LICENSED EMPLOYEE TESTED POSITIVE FOR CONTROLLED SUBSTANCE A non-licensed employee was determined to be under the influence of an illegal drug during a random urinalysis. The employee's access to the plant has been terminated. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 4/27/0 JENKINS TO GOULD * * * Contact the Headquarters Operations Officer for details of update. Notified the Reg 2DO (Ernstes) of update. * * * RETRACTION ON 4/29/04 HEAFNER TO GOTT * * * Event retracted. Contact the Headquarters Operations Officer for details. The Licensee notified the NRC Resident Inspector. Notified R2DO (Ernstes) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2004-04-27
40705 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-04-26 17:11 | 2004-04-26 20:06 | 2004-04-26 | TECHNICAL SPECIFICATIONS REQUIRED REPORT OF STEAM GENERATOR DEFECTIVE TUBES "During Refueling Outage RF13, interim results of 'A' Steam Generator (S/G) tube inspections indicate 59 tubes out of 5341 tubes (i.e., > 1 %) have been determined to be defective. This S/G tube inspection result for the 'A' S/G is classified as category C-3 in accordance with Technical Specification 5.5.9, Table 5.5.9-2. Per NUREG 1022, Section 3.2.4 Discussion (A)(3), the present C-3 classification of the 'A' S/G tubes does not meet the listed criteria for serious S/G tube degradation and thus is not a degraded or unanalyzed condition. Since this report is required by Administrative Technical Specification 5.5.9, this notification is being listed as an 'Other Unspecified Requirement'. "All defective tubes will be removed from service before the S/G is returned to service. There were no adverse safety consequences or implications as a result of this event. This event did not adversely affect the safe operation of Callaway Plant or the health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MO | POW | [5 empty] | 0 | 2004-04-26
40704 | 0 | STERIGENICS/IBA (Former RTI) |  |  |  |  | 2004-04-22 13:30 | 2004-04-26 14:09 | 2004-04-26 | HIGH CONDUCTIVITY READINGS IN GAMMA POOL On 4/22/04, around 13:30 EDT, after the irradiator shielding pool had been vacuumed, pool water conductivity exceeded 100 microsiemens per centimeter. The licensee initiated a change of the resin beds and observed pool water conductivity to decrease, as expected. On 4/23/04, the licensee noticed that pool water conductivity had increased to 110 microsiemens per centimeter. New resin beds are being placed in service today (4/26/04) by 18:00 and its is expected that pool water conductivity will decrease from 201 microsiemens to levels of less than 20 microsiemens per centimeter within 24 to 48 hours at the current recirculation rate through the resin beds. There are no personnel safety issues involved with this incident. The licensee will contact the Operations Center if the expected water pool conductivity does not return to normal operating levels. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | POOL COND HIGH | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 36.83(a)(10) |  |  |  | 0 | 2004-04-26
40703 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-04-24 10:50 | 2004-04-24 15:30 | 2004-06-23 | ISOLATION CONDENSER DECLARED INOPERABLE "This report is being made in accordance with 10 CFR 50.72(b)(3)(v)(B). "On 04/24/2004 at 06:03 [CDT], Dresden Unit 2 was using the Isolation Condenser to control reactor pressure following a Unit Scram. The isolation condenser operated properly until 10:50 [CDT] when the Isolation Condenser 2-1301-3 valve could not be opened to the full open position. ISO Condenser was declared INOPERABLE and Technical Specification Limiting Condition of Operation 3.5.3. Condition 'A' was ENTERED. High Pressure Coolant Injection has been administratively verified OPERABLE. "Reactor Pressure is being maintained 550-1000 psig and being maintained with Reactor Water Clean Up Flow and Gland Seal System. "Investigation into the cause of the valve failure is in-progress." Unit 2 had been operating approximately 30 days prior to the scram reported previously in EN #40702. The licensee informed the NRC Resident Inspector. * * * RETRACTION ON 6/23/04 AT 2036 EDT FROM GLEN MORROW TO ARLON COSTA * * * "On April 24, 2004, Dresden made an ENS call due to the failure of Isolation Condenser valve 2-1301-3 to fully open and the subsequent determination that the Isolation Condenser was inoperable. The ENS call was made based on the decision that this was required by 10CFR50.72(b)(3)(v)(B), 'Any event or condition that at the time of discovery could have prevented fulfillment of the safety function of structures or systems that are needed to remove residual heat.' "Isolation Condenser System operation is not credited in Dresden's accident analyses. Transients and Events treated as transients are listed under section 15.0.2.1 of the UFSAR. Accidents are described and analyzed under section 15.0.2.2 of the UFSAR. The isolation condenser is not credited for fulfilling safety function of removal of residual heat of any accident as described in section 15.0.2.2, Accidents. In accordance with the guidance contained in NUREG 1022, 'Event Reporting Guidelines 10CFR50.72 and 10CFR50.73,' Section 3.2.7, 'Event or Condition That Could Have Prevented Fulfillment of a Safety Function,' a functional failure of the Isolation Condenser System is not reportable under 10CFR50.72(b)(3)(v)(B). Therefore, Dresden is retracting this ENS call. "This Isolation Condenser System event will be described in a Licensee Event Report in accordance with 10CFR50.73(a)(2)(i)(B), 'Any event or condition which was prohibited by the plant's Technical Specifications'" The licensee notified the NRC Resident Inspector. Notified R3DO (Kozak). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(B) |  |  |  | 0 | 2004-04-24
40702 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-04-24 06:03 | 2004-04-24 09:00 | 2004-04-24 | AUTOMATIC REACTOR SCRAM DUE TO MSIV CLOSURE "This report is being made in accordance with 10 CFR 50.72 (b)(2)(iv)(B) . "On 04/24/2004 at 06:03 [CDT], Dresden Unit 2 experienced an automatic Scram from 20% Reactor power due to Main Steam Isolation Valve closure, cause is under investigation. There were no Electromatic Relief or Safety Relief Valve actuations and the Isolation Condenser was initiated manually for pressure control. There were no ECCS initiations. PCIS Group 2 and Group 3 Isolations occurred as expected due to normal reactor water level decrease following the scram. All other systems responded as expected." All control rods fully inserted on the automatic scram. The electric plant is in a normal lineup and being supplied from offsite power. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-04-24
40701 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-04-24 04:04 | 2004-04-24 06:59 | 2004-04-24 | TRANSPORT OF POTENTIALLY CONTAMINATED INJURED PERSONNEL TO OFFSITE MEDICAL FACILITY The following information was obtained from the licensee via facsimile: "Individual transported to the hospital as potentially contaminated due to injury received in Unit 2 Reactor Containment Building. At 0430 on 4-24-04 EDT, individual left site by ambulance. "RP [Radiation Protection] technician escorted injured person to hospital. RP has notified site that the injured person was not contaminated. (0500 EDT on 4-24-04)" Injured person was transported to the Oconee Memorial Hospital using the hospital ambulance. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-04-24
40700 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-04-23 08:45 | 2004-04-24 04:46 | 2004-04-24 | CRITICALITY CONTROL 24-HOUR (BULLETIN 91-01) REPORT The following information was obtained from the regulatee via facsimile: "At 0845, on 04-23-04, the Plant Shift Superintendent was notified of a violation of Nuclear Criticality Safety (NCS) controls associated with storage of waste drums in the C-335 building. Two Spacing Exempt waste drums were identified to have been characterized utilizing erroneous results from the Q2 drum monitor in violation of Nuclear Criticality Safety Evaluation (NCSE) 091. The characterization is based on it being unlikely that the drum monitor will give an erroneous result. The purpose of the requirements is to ensure the mass in an NCS Spacing Exempt waste drum is below the [DELETED] 235U limit. "The waste drums have been independently sampled and demonstrated to be below the [DELETED] 235U limit. "The NRC Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: While the [DELETED] 235U limit was not exceeded for these two drums, both legs of double contingency were lost and the potential exists for waste drums to be non-conservatively characterized using the Q2 drum monitor. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S)) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to occur, two or more waste drums containing above the [DELETED] 235U limit would have to be accumulated to exceed a critical mass with no spacing and be moderated. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency is maintained by implementing two controls on mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): Each drum contains less than [DELETED] 235U at an enrichment of less than 1.5 wt% 235U. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency relies on it being unlikely for the Q2 drum monitor to provide an erroneous result. The drum monitor measurement gave a non-conservative erroneous result, which was used to characterize the drum. Therefore, the unlikely statement was violated. However, the drums were subsequently sampled with the result being below the [DELETED] 235U limit for each drum. Therefore, the parameter was maintained. "The second leg of double contingency relies on it being independently unlikely for the Q2 drum monitor to provide an erroneous result. The independent drum monitor measurement gave a non-conservative erroneous result, which was independently used to characterize the drum. Therefore, the independent unlikely statement was violated. However, the drums were subsequently independently sampled with the independent result being below the [DELETED] 235U limit for each drum. Therefore, the parameter was maintained. "Although the parameter was maintained, double contingency is based on two controls on one parameter. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Characterize waste drums (PF-04-7258 and PF-03-5051) using the independent sample results. Completed 04/23/04. 2. Complete the 'extent of condition' examination prior to making a determination for removal of the ropes and postings." The Q2 drum monitor requires a density of material input to properly characterize drum material. Sodium fluoride (NaF) density was used instead of uranyl fluoride (UO2F2) which resulted in a non-conservative characterization. The drum contained both materials. Plant personnel have imposed spacing requirements on all other drums in the immediate area that have questionable characterizations until they can be properly analyzed. To prevent re-occurrence, plant management has issued orders and mandates to verify drum contents utilizing two different and distinct sampling methods (i.e. monitoring and laboratory sampling). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-04-24
40699 | 0 | FAIRBANKS MORSE ENGINE |  |  |  |  | 2004-04-21 | 2004-04-23 12:41 | 2006-01-12 | FAIRBANKS MORSE ENGINE HAS DETERMINED A POTENTIAL SAFETY HAZARD WITH THE WOODWARD DIGITAL REFERENCE UNIT (DRU) On April 21, 2004, Fairbanks Morse Engine evaluation determined a potential safety hazard exists for Woodward DRU's. The FM P/N is 12998236 and the Woodward P/N is 9903-439. The defect exhibits erratic ramp up of speed and hence the inability to reach rated RPM and inability to apply load to the engine. The cause has been traced to a random contamination problem of an integrated circuit (IC) in DRU's manufactured by Woodward between November 2000, and January 2002. The rate of occurrence is less than 10 in the US and approx 20 worldwide. There are approx 38,000 Woodward units worldwide that use this IC. Only one US nuclear utility has experienced this failure and the failure occurred during testing prior to declaration of operability. In all cases, the failure occurs within a very few hours of operation. Therefore, if a DRU has been installed and has been operating for many hours/years, it is not at risk for this failure. The utilities that FM has supplied DRU's to in the timeframe identified that may be affected include the following: Utility Site Year Shipped FP&L Seabrook 2001 WCNOC Wolf Creek 2001 The above utilities are also being notified and affected DRU's will have IC's replaced as necessary. * * * UPDATE FROM STEVENSON TO KNOKE AT 17:52 ON 01/12/06 * * * "Fairbanks Morse Engine evaluation has determined a potential safety hazard exists for Woodward Digital Reference Units (DRUs). The FM P/N is 12998236, and the Woodward P/N is 9903-439. A list of specific affected S/N's is identified in the letter dated 01/12/06. "The defect exhibits erratic ramp up of speed and hence the inability to reach rated RPM and inability to apply load to the engine. The cause has been traced to a random interaction between solder flux and integrated circuit (IC) material causing chip delamination. This condition is further described in Woodward Service Bulletin 01363, dated December 2005. "This same problem had been previously reported on 4/23/04, and at that time was thought to only affect DRU's manufactured between November 2000 thru January 2002. The manufacturer thought they had purged their stock of the specific IC chips that manifested the problem, but additional chips have been found in their system that now extends the affected time period to December 2005. "DRU's that have had IC chips replaced per the earlier 10 CFR 21 notification are not affected due to the use of a different solder flux that does not introduce the problem. "The utility that FM has supplied DRU's to in the timeframe identified that are affected Include the following: Utility Site Detroit Edison Fermi First Energy BV-2 SCE&G VC Summer "The above utilities are also being notified and affected DRU's will have IC's replaced as necessary." Notified R1DO (Conte), R2DO (Munday), R3DO (O'Brien), NRR EO (Mayfield), and emailed and faxed to Part 21 Coordinator (Tabatabai) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2004-04-23
40698 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-04-22 10:45 | 2004-04-22 13:48 | 2004-04-22 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) DECLARED INOPERABLE "At 1045 hours on 04/22/04, the Safety Parameter Display System (SPDS) portion of the Emergency Response Facility Computer System (ERFCS) was noted to be inoperable due to all outputs being displayed in "magenta" color. Attempts were made to reboot the system, but were unsuccessful. At 1145 hours on 4/22/04, SPDS was returned to service. Therefore, the SPDS had been out of service for 1 hour, which is considered a major loss of emergency assessment capability. This report is being made in accordance with 10CFR50.72(b)(3)(xiii)." SPDS is not 100% operable, but it does meet the licensee's operability criteria to be declared operable. The licensee is analyzing the problem. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-04-22
40697 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2004-03-09 12:42 | 2004-04-22 10:58 | 2004-04-22 | INVALID SYSTEM ACTUATION DUE TO MOMENTARY POWER INTERRUPTION This report is being made under 10 CFR 50.73(a)(2)(iv)(A). Actuations occurred on the following systems (System-Actuation Status) -Primary Containment (Drywell and Suppression Chamber) Atmospheric Control Isolation Valves - Complete -Drywell Vent Monitor - Partial -Off-gas Treatment - Partial -Secondary Containment - Complete -Control Room Ventilation - Complete -Standby Gas Treatment - Complete System response indicated that the cause was a momentary power interruption to a portion of the Primary Containment Isolation System Division 2 logic. Print verification determined that the system functioned as designed on loss of power. The Licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-04-22
40696 | 0 | MISSOURI BAPTIST MEDICAL CENTER |  |  |  |  | 2004-03-01 | 2004-04-22 08:38 | 2004-04-22 | DOSE TO THE SKIN OTHER THAN THE INTENDED TREATMENT SITE A female patient received a potential dose to the skin on the inner thigh during a High Dose Rate Treatment. The treatment occurred in late February to early March. This was discovered on 4/21/04, when the patient returned for follow-up and markings on the inner thigh were noticed that were unusual for the intended treatment area. The licensee is determining the actual exposure to the skin. The patient has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE TO OTHER SITE > SPECIFIED LIMITS | [9 empty] | NON EMERGENCY | 3 | MO | HOS |  | 35.3045(a)(3) |  |  |  | 0 | 2004-04-22
40695 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-04-21 16:35 | 2004-04-21 18:06 | 2004-04-21 | MANUAL REACTOR SCRAM IN RESPONSE TO HIGH MAIN TURBINE VIBRATION DURING STARTUP "At 1635 on 04/21/2004, Susquehanna Unit 1 was returning to service from its 13th Refueling and Inspection Outage which included main turbine replacement. During start-up turbine testing with the generator off line, several main turbine bearings experienced high vibration. In response to these high vibrations, the reactor was manually scrammed from approximately 17% power. The main steam line isolation valves were manually closed and main condenser vacuum was broken in order to more rapidly slow the main turbine speed. "All control rods fully inserted on the SCRAM, a level 3 containment isolation signal was received as expected. RCIC was manually initiated to control reactor water level. Lowest reactor water level reached was approximately 3" narrow range. There were no radioactive releases. "This RPS actuation is reportable under 10CFR50.72(b)(2)(iv)(B) as an 'Unplanned RPS Actuation with the Reactor Critical.' The RPS Actuation and the RCIC injection are reportable per 10CFR50.72(b)(3)(iv)(A) 'Unplanned Actuations of Systems that Mitigate the Consequences of Significant Events.' "Investigation into the high main turbine bearing vibrations is ongoing." The main turbine was tripped prior to the manual scram and no SRVs have lifted due to low decay heat level. The electric plant is in a normal lineup. The licensee notified the NRC Resident Inspector and the PEMA representative. | 0 | 0 | 0 | 17 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-04-21
40694 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2004-04-21 17:50 | 2004-04-21 18:00 | 2004-04-21 | LICENSEE PLANS TO ISSUE NEWS RELEASE REGARDING AN ACCOUNTABILITY DISCREPANCY OF SNM The following is the text of the planned press release: "Entergy Vermont Yankee Press Release "Fuel Rod Segments at Vermont Yankee Unaccounted For "BRATTLEBORO, VT -- In response to a recent NRC inspection, Entergy Vermont Yankee has determined that two short spent fuel rod segments are not in their documented location in the spent fuel pool. Entergy engineers are reviewing storage records and performing a thorough inspection of the spent fuel pool to determine the location of the rod segments. "One of the segments is about the length and diameter of a pencil and the other is the same diameter and about 17 inches long. According to station documentation, in 1979, the highly radioactive rods were placed in a special stainless steel container in the spent fuel pool after a fuel inspection to address fuel cladding deficiencies. "Vermont Yankee has an extensive system of radiation monitors and, due to the radioactive nature of the material, the segments could not have been inadvertently removed from the pool in anything other than a container specifically designed and licensed to contain radioactive material. Therefore, public health and safety is not at risk as a result of this issue. Entergy Vermont Yankee will continue to keep the Nuclear Regulatory Commission and state authorities informed on the progress of the investigation. "The Vermont Yankee spent fuel pool is 40 feet in depth and contains 2,789 spent uranium fuel assemblies that were used in energy production since 1972. Vermont Yankee is presently shut down for its twenty fourth refueling and maintenance outage." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-21
40693 | 0 | BAXTER HEALTH CARE |  |  |  |  | 2004-04-21 12:00 | 2004-04-21 16:54 | 2004-04-27 | IRRADIATOR SOURCE RACK JAMMED IN THE UP POSITION At 1200 EDT operators were lowering a source rack when it jammed due to a maintenance ladder. The licensee entered their emergency procedure and contacted the manufacturer, i.e., MDS Nordion, for assistance. MDS Nordion is expected onsite at 1040 EDT tomorrow 4/22 to help the licensee develop a recovery plan. The stuck source rack contains approximately 2,030 curies of Co-60. The maze is closed restricting personnel access. There were no personnel exposures associated with this occurrence. A conference call with the Baxter Plant Manager and NRC staff was established to discuss the details of this report. * * * UPDATE ON 04/24/04 @ 1424 BY ANGEL ALICEA TO CHAUNCEY GOULD * * * The licensee reported that at 2000 on 04/23/04 the source was placed in the shielded position submerged in 25 ft of water in the pool. They are terminating this event. Notified Tom Decker, George Pangburn, Frank Costello, Cathy Modes, and Betsey Ullrich * * * UPDATE ON 4/27/04 @ 1129 EDT FROM A. ALICEA TO HOWIE CROUCH * * * The licensee reported that a re-enactment of the event indicates that two plant employees may have been over-exposed during the initial event. The licensee is conservatively reporting this update under 10 CFR 20.2202 (b)(1) since the exposure value is unknown but believed to be less than 5 rem. Personnel dosimetry is being analyzed and the calculations are being verified by the contractor at the site. The licensee will update this event when the exposure data is known. The licensee has informed the on site Regional Materials Inspector (Diaz). Notified NMSS (Fred Brown) and R1DO (Richard Barkley). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNSHIELD STUCK SOURCE | PERS OVEREXPOSURE/TEDE >= 5 REM | [8 empty] | NON EMERGENCY | 1 | PR | MAT |  | 36.83(a)(1) | 20.2202(b)(1) |  |  | 0 | 2004-04-21
40692 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2004-04-21 | 2004-04-21 13:45 | 2004-04-21 | AGREEMENT STATE REPORT INVOLVING LOST GENERAL LICENSE SOURCE MATERIAL "The licensee called to report that a Filtec FT-50 fill level gauge, serial number, 112082, containing 100 millicuries of Am-241 in sealed source, serial number 4473, could not be located during inventory. The unit was removed from a manufacturing line in June, 1995 and stored in a building along with other idle equipment. During a recent project to clean this building and dispose of old equipment, the licensee was unable to locate this unit. An extensive search was conducted throughout the facility and the gauge could not be located. Personnel who may have had knowledge of the unit were interviewed. The last documented time that the gauge was seen in storage was in January 1998. The licensee believes that the unit was discarded with other idle equipment. The manufacturer's records indicate the source was not returned to them. Inspectors [Tennessee Division of Radiological Health] are enroute to the facility to investigate." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2004-04-26
40691 | 0 | AREVA ELECTRICAL PRODUCTS |  |  |  |  | 2004-04-21 | 2004-04-21 13:07 | 2004-04-21 | PART 21 NOTIFICATION INVOLVING VOLTAGE MONITORING RELAYS "The following information is provided pursuant to the requirements of 10 CFR Part 21 to report a potential safety concern. A potential safety condition may exist with the Eaton Cutler-Hammer D65 Series B1 Voltage Monitoring Relay that can cause the unit to bypass the Manual Reset feature. This could result in the D65 relay being energized without an operator manually resetting it resulting in possible personal injury or death or property damage. This condition exists with Eaton Cutler-Hammer D65 Series B1 Voltage Monitoring Relays with a manufacturing date between May 12, 2002, and February 20, 2004. "On March 25, 2004, Framatome/AREVA Electrical Products received the attached Eaton Cutler Hammer Product Safety Warning for D65 Voltage Monitoring Relays, dated March 24, 2004. The Product Safety Warning states that Eaton's Cutler-Hammer D65 Series B1 Voltage Monitoring Relays with a manufacturing date identified above may power up without being manually reset even when a NC [Normally closed] switch is wired to activate manual reset mode. This condition is only present when used in applications operating in the manual reset mode. This condition is not present when the device is used in automatic reset mode. This condition may only result when the D65 Series B1 is used and will not result if the A1 Series is used (as the A1 series did not offer the potential for manual reset). "The supply of Safety Related D65 Voltage Monitoring Relays by Framatome/AREVA Electrical Products is isolated to only one Nuclear Customer (i.e. First Energy - Davis Besse Nuclear Power Plant). The First Energy Davis Besse Nuclear Power Plant was notified by Framatome/AREVA Electrical Products on April 2, 2004." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2004-04-21
40690 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2004-04-21 | 2004-04-21 12:15 | 2004-04-21 | RADIOACTIVE SURFACE CONTAMINATION GREATER THAN LIMITS A package that exceeded the limits for removable radioactive surface contamination was received April 21, 2004, by VA Chicago Health Care System , a permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. The basis for reporting the contamination is under 10 CFR 20.1906(d)(1) in that the package, an ammo box being used to deliver radioactive materials, had approximately 80.9 disintegrations per minute per square centimeter removable radioactive contamination on the outside. The contamination was identified as Tc 99M. The Cardinal Health Nuclear Pharmacy Services delivered the package. The status of whether the vendor delivery vehicle was exclusive use was not determined. The ammo box has been decontaminated. The permittee's Radiation Safety Officer notified the delivery vendor about the package. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | SURFACE CONTAM LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 3 | IL | HOS |  | 20.1906(d)(1) |  |  |  | 0 | 2004-04-21
40689 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-04-20 18:10 | 2004-04-20 23:26 | 2004-04-20 | DEGRADED CONDITION - GREATER THAN ONE PERCENT OF STEAM GENERATOR TUBES DEFECTIVE "On April 08, 2004, during the Unit 1 twelfth refueling outage (1R12), analysis of eddy current data on [Steam Generator] SG 1-4 indicated that greater than one percent of the total tubes inspected in SG 1-4 were defective. Ninety-two (92) defective tubes in SG 1-4 were detected and are being plugged. Most of the [pluggable] indications are due to circumferential primary water stress corrosion cracking in the Rows 5 to 8 U-bend region. Results of the SG tube inspection fall into Category C-3, which requires a four-hour non-emergency report in accordance with Technical Specification (TS) Table 5.5.9-2 and 10 CFR 50.72(b)(3)(ii) (an 8-hour requirement replacing the former (b)(2)(iii)(C), 4-hour requirement). [This was reported in EN#40659 dated 04/08/04.] "An NRC teleconference in accordance with TS 5.6.10.d to report the results of the voltage-based repair criteria implemented for the tube support plate intersections was conducted on Wednesday April 14, 2004, at 1300 EDT. "On April 20, 2004, following completion of SG eddy current testing, PG&E identified SG 1-1 had greater than one percent of the total tubes that were defective. Forty (40) defective tubes in SG 1-1 were detected and plugged. Most of the [pluggable] indications are due to outside diameter stress corrosion cracking at the SG tube to support plate intersections. SG 1-2 had twenty-six (26) and SG 1-3 had twenty-seven (27) defective tubes that required plugging. "A Special Report in accordance with TS 5.6.10.a and e will be submitted prior to returning Unit 1 to power operation. "A Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(v)(C) will be submitted within 60 days." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-04-20
40688 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-04-20 13:10 | 2004-04-20 13:56 | 2004-04-20 | OFFSITE NOTIFICATION - NON-WORK RELATED FATALITY On April 20, 2004, a non-work related fatality occurred at H. B. Robinson. At 0730 EDT, a Progress Energy employee assigned to the main turbine maintenance crew for the current maintenance outage that began on April 20, suffered a condition that required immediate medical attention. Medical assistance was provided by onsite plant employees trained as first responders. The employee was transported by ambulance to a nearby medical facility where additional medical treatment was rendered. At 1310, site personnel were notified that attempts to revive the employee were not successful and that the employee had died. The employee was working in a non-radiological controlled area of the plant and no radioactive material or contamination was involved. Notification of the South Carolina Occupational Safety and Health Agency is planned. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-20
40687 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2004-04-13 15:30 | 2004-04-20 11:55 | 2004-04-20 | AGREEMENT STATE REPORT - ACCIDENTAL SHIPMENT OF RADIOACTIVE MATERIAL On 4/13/04, at approximately 3:30 PM CDT, the Wisconsin Radiation Protection section received a telephone call from the New York State Labor Department, Radiological Health Department. New York State Radiological Health Dept. had just been informed by one of their licensees, Mick Radio-Nuclear Instruments, Inc., that a package had been received from St. Nicholas Hospital, Sheboygan, WI. The company had found 2 radioactive brachytherapy seeds within a Mick applicator which had been returned to their company for repairs. The radioactive seeds were stuck in the Mick applicator. Mick Radio-Nuclear Instruments contacted the shipper of the device, St. Nicholas Hospital, to obtain details identifying the radionuclide. The 2 seeds have been identified as containing I-125, 0.370 milli Curies each on 3/12/04. Mick Radio-Nuclear is not licensed to receive this radioactive material which was inadvertently sent by St. Nicholas Hospital. The package was shipped on 4/8/04 and received on 4/13/04. The Wisconsin Department of Health and Family Services (DHFS) is reporting this item as a "loss of control of radioactive material to an unlicensed entity" and "potential exposure to the general public." DHFS staff are being dispatched on 4/20/04 to investigate. The radioactive material is now in the possession of the Radiological Health Department for the state of New York. St. Nicholas Hospital is working on identifying a company in New York that can take possession of the radioactive brachytherapy seeds and return them to the manufacturer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2004-04-23
40686 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-03-20 15:59 | 2004-04-20 10:55 | 2004-04-26 | INVALID ACTUATION OF THE MOTOR DRIVEN EMERGENCY FEEDWATER PUMPS "By design, the Steam Generator (SG) Dry-out Protection Circuit actuates whenever two level indications (two of two actuation logic) in either SG are lower than the setpoint for more than 30 seconds. This start circuit is not credited in any ONS safety analysis, therefore this signal is considered an INVALID signal with respect to 50.73 (a)(2)(iv)(A). Upon actuation, the circuit starts both Motor Driven Emergency Feedwater Pumps (MDEFWPs) on the affected unit. It does not send a start signal to the Turbine Driven Emergency Feedwater Pump. "Shortly after entering Mode 4, a control operator stopped one of two operating Reactor Coolant Pumps per the Unit shutdown procedure. A second control operator was manually controlling Feedwater and reduced flow to control the system cooldown rate, without recognizing that the 2B SG had reached the low level setpoint for SG Dry-out Protection Circuit actuation. "In this event, the 2B SG level trains A and B indicated lower than the setpoint value (-21 inches) for more than 30 seconds, so the SG Dry-out Protection Circuit started the 2A and 2B MDEFWPs. The actuation was considered complete and the system started and functioned successfully. Both MDEFWPs started. The 2B SG control valve, 2FDW-316, opened and fed the 2B SG from the 2B MDEFWP for approximately one minute until the SG level reached the EFDW control setpoint (30 inches). The 2A pump did not feed the 2A SG because 2A SG level remained well above the EFDW control setpoint so there was no demand for the 2A SG control valve, 2FDW-315, to open." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 4/26/04 AT 16:23 FROM R. TODD TO A. COSTA * * * This update is to clarify a typographic misspelling on the first sentence of the last paragraph of this event notification which should read (~[approximately] 21 inches) instead of (-21 inches). Notified R2DO(Julian). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode2: Hot Shutdown; FMode2: Hot Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-04-20
40685 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-04-16 13:15 | 2004-04-19 20:23 | 2004-04-22 | CALIFORNIA AGREEMENT STATE REPORT - EXPOSURE INCIDENT (<1 REM WHOLE BODY) INDUSTRIAL RADIOGRAPHER At 2023 EDT, the following email was received from Decisive Testing: "On April 16, 2004, a radiographer was working on a schedule 40 stainless steel 4" pipe. The Ir-192 radiography operation was being conducted inside a shielded x-ray room, but was considered by the licensee to be a temporary jobsite for materials radiography. The camera, the cable and collimator were inside the room while the operator and crank were located approximately 8' from the closed x-ray door. At 1:15 PM, the radiographer finished the 6th shot and reentered the room to prepare for the 7th shot. After setting up the 7th shot, he picked up his survey meter as he left the room (the meter had been placed on top of the camera when he entered the room) and noticed the meter was off scale. He exited the room and checked the position of the radiography source by attempting to crank it out, only to discover that he had failed to crank the source in after the 6th shot. His 0-200 millirem dosimeter was off scale and he was not wearing his alarming ratemeter. His dosimeter was sent in for processing by overnight mail. The licensee did a re-enactment and estimated the radiographer's whole body dose to be under 1 rem. The radiographer's extremity dose is estimated to be under 10 rem. "Source: Industrial Nuclear, model 7, Ir-192 source assayed 10/16/03 and decayed to 17.9 Curies on 4-16-04). Camera: Amersham, model 660B, serial # B2928. Collimator: Industrial Radiography Maintenance & Supply, model - tungsten mini (side port) collimator (attenuation 1/16 for Ir-192). "RHB responded to the site on Saturday, April 17, 2004 to interview the radiographer and RSO. The investigation is ongoing, but it does appear that neither the whole body nor extremity regulatory dose limits for the radiographer were exceeded." * * * UPDATE 1500 EDT ON 4/22/04 FROM ROBERT GREGER TO S. SANDIN VIA FAX * * * "The dosimeter results were received from Landauer on 4/21/04 and showed a whole body dose of 95 mrem for the radiographer in this event, which is consistent with a reenactment conducted by the licensee. Based on this information, the whole body dose did not exceed regulatory limits. The extremity dose to the radiographer is still under investigation." Notified R4DO (Bywater) and NMSS (Torres). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-04-22
40684 | -1 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-04-18 18:30 | 2004-04-18 23:45 | 2004-06-01 | RESIDUAL HEAT REMOVAL SYSTEM ISOLATION DUE TO A RISE IN REACTOR PRESSURE "At 1830 hours on 18 April 2004, Nine Mile Point Unit 2 was restoring from reactor pressure vessel leakage test. "Reactor pressure was ~82 psi, temperature ~178 degrees, reactor level was solid with both reactor recirculation pumps running in slow speed per the leak test procedure. " 'B' residual heat removal system was being warmed up in preparation for going in to service. Reactor water cleanup reject from the vessel was secured to maintain RPV [Reactor Pressure Vessel] pressure stable in order to provide driving head for flow through the residual heat removal discharge line to radwaste. The line is warmed up from the reactor, back through the Shutdown cooling isolation valve, to radwaste prior to placing shutdown cooling in service. When warm-up criteria are met, the operating procedure directs securing flow. When flow was secured, this effectively isolated the solid reactor vessel, resulting in a rise in reactor pressure. Pressure peaked at ~146 psi before operators established reactor water cleanup reject flow. "When RPV pressure reached 128 psi, the residual heat removal system isolation was automatically initiated as designed. The shutdown cooling injection valve, which was open to support piping warm-up, closed as designed. All other shutdown cooling valves were closed prior to the event per the warm-up lineup." RPV is currently depressurized with shutdown cooling in service. All systems are functioning as expected. The licensee notified the NRC Resident Inspector. * * * Retraction on 06/01/04 at 1512 EDT from Chris Skinner to John MacKinnon * * * "The following is a retraction of ENS Notification #40684: On April 18, 2004, Nine Mile Point Unit 2 reported Residual Heat Removal Shutdown Cooling System isolated due to a pressure spike while warming up the piping. The shutdown cooling injection valve, which was open to support piping warm-up, closed as designed. All other shutdown cooling valves were closed prior to the event per the warm-up lineup. Accordingly, Control Room personnel conservatively initiated ENS reporting under 10CFR50.72(b)(3)(iv)(A) in response to the valid containment isolation signal. "Subsequent analysis has concluded that, although the isolation signal was valid, it was not a general containment isolation signal (i.e., the isolation signal only involved the shutdown cooling system) and the shutdown cooling function of the Residual Heat Removal System is not listed under 10CFR50.72(b)(3)(iv)(B) as a system that is required to be reportable. This system isolation does not meet the reporting requirements of 10CFR50.72(b)(3)(iv)(A). "Therefore, this notification made on April 18, 2004, is being retracted. The NRC Resident Inspector was notified." NRC R1DO (Ron Bellamy) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-04-19
40683 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2004-04-18 20:10 | 2004-04-18 22:33 | 2004-04-18 | COURTESY CALL INVOLVING SUSPENSION OF SECURITY PATROLS DUE TO ADVERSE WEATHER During a tornado and severe thunder storm watch, wind gusts on site exceeded 80 mph. At 2010 CDT the shift manager directed that the security supervisor suspend guard patrols within the Owner Controlled Area and access control point for personnel safety inside the Protected Area. Patrols were restored at 2044 CDT after the wind gusts subsided. The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW | [5 empty] | 0 | 2004-04-18
40682 | 0 | VOGTLE |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-18 12:38 | 2004-04-18 15:31 | 2004-04-18 | AUXILIARY FEEDWATER SYSTEM ACTUATION DUE TO MAIN FEED PUMP TRIPS "An Auxiliary Feedwater [AFW] actuation occurred with the plant in Mode 3, Main Feedwater out of service and a cooldown in progress. An AFW actuation was received when both main feed pumps tripped due to low condenser vacuum. AFW was already in service with both motor-driven pumps running and discharge valves throttled to maintain steam generator level. A surveillance to test AFW actuation on the trip of main feedwater pumps was in progress. The main feed pump trip signal was generated when condenser vacuum was broken prior to completing the test and blocking the actuation signal from the main feed pumps to AFW. Steam generator blowdown and sample valves isolated and MDAFW [Motor Driven AFW] discharge valves opened as expected. Operators took action to throttle AFW feed to the steam generators. No adverse affects on the plant occurred. The AFW actuation signal from the trip of main feed pumps has been blocked as allowed by plant conditions." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-04-18
40681 | 0 | CONSTRUCTION TESTING & ENGINEERING |  |  |  |  | 2004-04-17 12:00 | 2004-04-17 19:37 | 2004-04-17 | DAMAGED TROXLER MOISTURE DENSITY GAUGE The licensee RSO reported that at 1200 EDT, a Troxler Moisture Density Gauge, Model #3440 (Serial #32741 containing 40 millicuries Am-241/Be and 8 millicuries Cs-137) was run over by heavy equipment on a residential construction site in Vienna, VA. A 20 square foot area around the location of the incident was cordoned off, and the damaged equipment was transported to the company's laboratory in Manassas, VA. According to the RSO, the device was damaged, but the source remained intact. At 2020 EDT the Fairfax County, VA HazMat team was directed to the construction site, and conducted testing to see if any contamination occurred. At 2125 EDT, the HazMat responders reported that no radiation above normal background was found at the site, and they were following up with the operator of the device to check for personal contamination. At 2208 EDT, the team reported that no contamination was found on either the individual who operated and transported the device, or his clothing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | MAT | [5 empty] | 0 | 2004-04-17
40680 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2004-04-17 07:26 | 2004-04-17 13:57 | 2004-04-18 | OFFSITE NOTIFICATION - SMALL FIRE AT PALO VERDE 1: TWO EMPLOYEES INJURED, NO PLANT EQUIPMENT DAMAGE "On Saturday, April 17, 2004, at approximately 07:26 [MST], a fire in the Palo Verde Nuclear Generating Station Unit 1 turbine building resulted in two injuries due to burns. Both individuals were transported offsite for treatment. One of the two was airlifted with suspected second degree burns. Neither involved any radioactive contamination. "No press release is planned, but media attention has already been observed in response to media monitoring communications on local police/fire scanners. Calls have been received from several TV stations. One local station broadcast the fire and injuries at approximately 09:40 (MST). "Palo Verde Unit 1 is shutdown and defueled in its eleventh refueling outage. The fire was associated with pre-heating for welding in the turbine building. It is suspected that solvent vapor in the vicinity of the pre-heating activity may have flashed. The fire was extinguished in less than 15 minutes and no emergency plan classification was declared or required as a result of the fire. "The NRC Resident Inspector has been notified of the event and this ENS notification." The fire occurred near the Main Feed Pump Turbine Alpha, which was dismantled at the time. There appears to be no physical damage to any plant equipment, although some nearby cleaning rags were partially burned. * * * * UPDATE FROM D. DAILEY TO M. RIPLEY 1635 ET 04/18/04 * * * * "1) Both workers received facial burns. One was treated and released at approximately 11:00 MST on Saturday, April 17, 2004. The other was released during the morning of Sunday, April 18, 2004. "2) There was no equipment damage as a result of the fire. The apparent cause of the fire in the "A" main feed pump turbine lower shell was residual isopropyl alcohol in a drain hole. The alcohol is used to clean solvent residue to have the turbine shell oil-free for NDE (non-destructive examination) purposes. "The NRC Resident Inspector has been notified of this ENS update." Notified NRC Region 4 Duty Officer (D. Powers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-17
40679 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-04-15 16:15 | 2004-04-16 12:23 | 2004-04-16 | NEVADA AGREEMENT STATE REPORT - LOST PORTABLE NUCLEAR GAUGE The following information was received on 4/16/04 via facsimile: At approximately 4:15 p.m. on 4/15/04 the State received a telephone call from the RSO for Nortech - Reno. The RSO reported the loss of a Pacific Nuclear Model MC-1 portable moisture density gauge, S/N is M12044864, which contains 10 millicuries of Cs-137 and 50 millicuries of Am-241/Be. The operator had the device sitting on the tailgate of his pickup, out of the shipping box, while talking on the telephone. He got in the truck and proceeded to drive to a convenience store several miles away. Upon getting out of the truck at the convenience store he noticed that the gauge was missing. He retraced his route looking for the device but did not find it. It is not known if the device was locked or not. The individual had been conducting testing, so there is the possibility that it was not locked. The RSO has had four different individuals retracing the route looking for the device. They reportedly have been looking in alleys, dumpsters etc. but have not located the device. The licensee has notified the Reno Police and the Washoe County Sheriff. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-04-21
40678 | 0 | WESTINGHOUSE NUCLEAR SERVICES |  |  |  |  | 2004-04-16 | 2004-04-16 10:14 | 2004-04-16 | PART 21 NOTIFICATION DUE TO POTENTIAL CRACKING IN B4C HYDRID CONTROL RODS This issue concerns the potential for cracking in the tips of the Westinghouse designed B4C Hybrid Rod Cluster Control Assembly (RCCA) while in operation. Westinghouse supplied B4C Hybrid RCCAs are currently in use in the U.S. only at Tennessee Valley Authority's (TVA) Watts Bar Nuclear Plant. Cracks in the hybrid RCCAs could result in a potential loss of B4C [a neutron absorber] from the RCCA if left uncorrected. Westinghouse will review and revise its guidelines on the use and expected life of B4C Hybrid RCCAs to assure that this information is accurately reflected and communicated to its customers. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 0 |  | OTH | PAR | 21.21 |  |  |  | 0 | 2004-04-16
40677 | 0 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-04-16 01:05 | 2004-04-16 08:47 | 2004-04-16 | TRANSPORT OF POTENTIALLY CONTAMINATED PERSON TO OFFSITE MEDICAL FACILITY A vendor received a possible ankle fracture while working in the Unit 2 Reactor Building (RB). The injured person was descending a ladder and stepped on a roll of poly material and injured his ankle when the roll shifted. Onsite medical assistance team responded and removed the individual from the RB and prepared him for transport to Oconee Memorial Hospital using a hospital ambulance. Due to the nature of the injury, the individual was unable to stand in the whole body frisker and was transported to the hospital as potentially contaminated. A licensee Radiation Protection Technician (RPT) accompanied the injured person in the ambulance to the hospital where it was determined that the individual was not contaminated. At this time, there is no media/press interest and no press release is expected by the licensee. The NRC Resident Inspector was notified by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-04-16
40676 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-04-15 10:30 | 2004-04-15 12:37 | 2004-04-15 | HAZARDOUS MATERIAL SPILL "On 4/15/04 at approximately 0315 hours, an 18 inch expansion joint on a exterior overhead steam supply line ruptured during routine utilities valving operations. The asbestos insulating the expansion joint was released to the ground resulting in a hazardous material spill of approximately 1 - 2 pounds of friable asbestos. "At 1030 hours, The Plant Shift Superintendent notified the National Response Center that a Reportable Quantity (RQ) of hazardous material (friable asbestos) was released to the ground. No material left the immediate area and clean-up of the 1 to 2 pounds of asbestos is currently in [progress]. UE2-RA-RE1030, Appendix D, section P requires a 4 hour NRC event when other government agencies are notified." The licensee notified NRC Region II. The Ohio EPA and the local Department of Energy office were also notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2004-04-15
40674 | 0 | PENNSYLVANIA STATE UNIVERSITY |  |  |  |  | 2004-03-30 | 2004-04-14 15:25 | 2004-04-14 | MISSING GAS CHROMATOGRAPH "During a routine sealed source inventory and leak test in March 2004, a technician from the Pennsylvania State University's Office of Environmental Health and Safety (EHS) found that a 14 millicurie source of nickel-63 was missing. The source was from a Varian Associates, Inc. gas chromatograph (GC): Model number: 3400CX Serial number : 17561 Source serial number: A10017 NRC Device Key #: 478731 Penn State # 1993-1019 Source Description: Plated nickel-63 source Current activity: 14 millicuries "EHS contacted faculty and staff associated with the laboratory while trying to locate the instrument. After repeated inquiries, it was determined that the GC had been sent to University Salvage in September 2003, and from there it was sold as scrap. According to NUREG-1717, Systematic Radiological Assessment of Exemptions for Source and Byproduct Materials, the dose to any individual from a scrapped Ni-63 gas chromatograph source would be less than 0.01 mSv (1 millirem)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-04-14
40673 | 0 | YANKEE ROWE | 1 |  |  | [1] W-4-LP | 2004-04-14 12:25 | 2004-04-14 13:00 | 2004-04-14 | UNUSUAL EVENT - FIRE GREATER THAN 30 MINUTES While dismantling the vapor containment using a torch, slag fell down on some plastic below and started a fire. The fire was reported to the control room at 1155. The licensee declared an unusual event at 1225. The fire department responded. The fire was extinguished at 1303. This is a decommissioned facility and there is no fuel in the reactor. No one was injured. There was only very low levels of radioactivity in the building of less than 1000 disintegrations per minute per 100 centimeters squared. * * * UPDATE AT 1416 ON 4/14/04 DEBAY TO GOTT * * * At 1408, Yankee Rowe terminated from the Unusual Event. Initial sampling indicates that there was no radiological release. Notified R1(McDermott), NRR (Reis), NMSS (Holahan), DIRO (Wessman), DHS (MacKee), and FEMA (Sullivan). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | UNUSUAL EVENT | 1 | MA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-04-14
40672 | 0 | DEPARTMENT OF VETERANS AFFAIRS |  |  |  |  | 2004-03-15 | 2004-04-13 17:03 | 2004-04-13 | LOSS OF LICENSED MATERIAL "The Department of Veterans Affairs is reporting a loss of licensed material. The loss occurred at a medical broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs. The permittee is VA Boston Healthcare System, Boston, Massachusetts. "The loss was discovered by the permittee Radiation Safety Officer (RSO) on March 15, 2004. The RSO discovered a container of solid animal waste containing approximately 350 micro-Curies of I-125 solid was disposed by transfer to a biological waste vendor and incinerated by the vendor as non-radioactive animal waste. "The permittee does not anticipate any exposure to individuals based on the loss. The permittee has taken measures to prevent a recurrence of the loss. "The basis for reporting the loss is under 10 CFR 20.2201(a)(ii) in that the permittee disposed of licensed material in a quantity greater than 10 times the quantity specified in 10 CFR 20, Appendix C, and is still missing at this time. The licensed material cannot be recovered. "Per 10 CFR 20.2201(b), the Department of Veterans Affairs will evaluate the circumstances related to the loss and submit a written report to NRC, Region 3, within 30 days of this notification." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MI | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-04-13
40671 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-04-12 18:10 | 2004-04-13 00:46 | 2004-04-13 | HIGH PRESSURE COOLANT INJECTION SYSTEM (HPCI) DECLARED INOPERABLE "High Pressure Coolant Injection System Incapable of Performing its intended Safety Function. "This report is being made in accordance with 10 CFR 50.72(b)(3)(v) due the High Pressure Coolant Injection System being incapable of performing its intended safety function. "At 1810 hours (CDT) during performance of the functional test of the level instrumentation for the automatic realignment of the High Pressure Coolant Injection system (HPCI) suction sources, plant maintenance person identified that logic circuitry leads had been lifted. The leads not being connected would prevent the automatic realignment of the HPCI suction from its non-safety related source, the Condensate Storage Tank (CST), to its safety related source, the Suppression Pool. "Based on preliminary information, the leads were lifted during scheduled maintenance activities on the HPCI system in March. "The applicable Technical Specification specified that HPCI be declared inoperable within an hour. Actions were immediately taken to restore the automatic function. The leads were re-landed and the TS condition exited at 1853 hours. "The inability of the system to automatically realign due to a CST low level or a Suppression Pool high level is considered to be a condition that would prevent the fulfillment of the safety function of the HPCI system." The licensee is still investigating the cause. The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-04-13
40670 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-12 10:33 | 2004-04-12 15:43 | 2004-04-12 | ACCIDENT MITIGATION - COMMON CONTROL ROOM EMERGENCY AIR CONDITIONING SYSTEM "Salem Unit 2 was placed in a configuration that affected the ability to mitigate the consequences of an accident due to an inadvertent actuation of the common control room emergency air conditioning system (CREACS). CREACS was actuated as a result of an invalid safety injection signal initiated on April 12, 2004 at 1033 hours, during solid state protection system testing on Salem Unit-1. Salem Unit-1 is currently defueled. Salem Unit 2 is in Mode 1 at 100% power. Unit 2 has two shutdown LCOs in effect. The first is for the CREACS system, which is shared between Unit 1 & 2, being aligned for single train operation with the Unit 1 CREACS train out of service per LCO 3.7.6a. The second shutdown LCO is for two outside air intake dampers being inoperable for scheduled maintenance. "With Unit 1 having an invalid Safety Injection signal, the CREACS system actuates in accident pressurized mode. This mode of actuation starts the CREACS fans, isolates the Control Room Envelope from the normal control room ventilation system and aligns the two sets of CREACS outside air intake dampers. With a Unit 1 Sl signal, the Unit 1 CREACS intake dampers close and the Unit 2 CREACS intake dampers open. These damper positions are locked in until manually reset. With only one train of CREACS operable, the dose analysis indicates that the requirements of General Design Criterion (GDC) 19 can only be met during a the worst case design basis accident if the Unit 2 CREACS intake dampers are closed and the Unit 1 CREACS intake dampers open. Therefore, until the CREACS intake dampers were reset and realigned, Salem Unit 2 would not have been able to mitigate the consequences of an accident and is reportable in accordance with 10CFR50.72(b)(3)(v)(D). The CREACS system actuation was reset and the dampers were re-aligned to their pre-actuation alignment at 1232 hours, restoring Salem Unit 2 to within the assumptions of the dose analysis. "As a result of the Unit 1 Safety Injection signal, all available equipment started as designed. Since the SI signal has been determined to be invalid the start of this equipment is not reportable per 10CFR50.72(b)(3)(iv)(B). The Unit-1 Safety Injection signal has been cleared and an investigation of the cause is in progress. "The only piece of major equipment out of service on Salem Unit 2 is the 25 Service water pump which is out of service for scheduled maintenance." The Licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-04-12
40669 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-01-09 | 2004-04-12 15:38 | 2004-04-12 | AGREEMENT STATE REPORT OF OVEREXPOSURE The following facsimile was received from the Louisiana Radiation Protection Division: "Cooperheat reported an over exposure to the assistant radiographer, on January 20, 2004. The radiographer received a dose of 9,347 mR due [to] failure to properly survey the radiography camera on January 9, 2004. The other radiographer received a dose of 4,974 mR. Both employees are not allowed to perform radiographic operations until after January 1, 2005. The radiographer was suspended 5 days without pay and the other radiographer was suspended 7 days without pay. Both employees are required to perform the 40 hour radiation safety training again before resuming radiographic operations. The employees were utilizing an Amersham camera model 660B with serial number B4293. The source was a 37.2 curie source of Ir-192 model number 424-9 with serial number 12680B." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-04-15
40668 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-02-12 | 2004-04-12 09:17 | 2004-04-12 | AGREEMENT STATE REPORT INVOLVING SAFETY EQUIPMENT FAILURE On 2/12/04, a Niton XRF Portable Analyzer (model Xli 800 - S/N 5089) shutter failed to close when the device was placed in the off mode. The incident occurred at the Pearl Harbor Naval Shipyard in Honolulu, HI and did not involve any significant radiation exposures to personnel. The device was packaged with temporary shielding and returned to Niton for evaluation. Niton determined that the shutter malfunction was the result of a loose set screw which connects the shutter to the motor. A component change to the Xli 800 series models was made that involves upgrading to a nylock set screw. This was the first instance of this type of failure. Instruments returned to Niton for resourcing or software upgrade will be modified in this manner to prevent shutter failure. This particular device contains a 30 millicurie Americium-241 source and is used for rapid identification and chemistry of metal alloy composition. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-04-15
40667 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-04-12 03:47 | 2004-04-12 05:25 | 2004-04-12 | UNIT 2 EXPERIENCED A REACTOR TRIP DURING STARTUP DUE TO AN INVALID SR TRIP SIGNAL "Unit 2 reactor tripped during low power physics testing. Trip appeared to be from an invalid source range [SR] trip signal in one train of solid state protection system. All systems responded properly. The Unit is currently stable in mode 3." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-04-12
40666 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-04-11 11:05 | 2004-04-11 12:47 | 2004-04-11 | AUTOMATIC REACTOR TRIP FOR UNKNOWN REASONS DURING PLANT STARTUP At 1247 EDT on 04/11/04, the licensee reported that at 1105 CDT on 04/11/04, control room operators were performing low power physics testing in accordance with FNP-2-STP-101 during startup of Unit 2 following a refueling outage. With reactor power at 10E-8 amps in the intermediate range in Mode 2, the 'B' reactor trip breaker opened for unknown reasons. All control rods inserted completely. The licensee is investigating the cause. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-04-11
40665 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-04-11 00:23 | 2004-04-11 04:43 | 2004-05-30 | PLANT HAD A VALID ESF SIGNAL TO START 1C EMERGENCY DIESEL GENERATOR "THIS IS AN 8-HOUR NOTIFICATION TO REPORT A VALID ESF SIGNAL TO START 1C EMERGENCY DIESEL GENERATOR THAT OCCURRED ON 4/11/04 AT 0023. Salem Unit 1 is defueled. The spent fuel pool cooling system is providing decay heat removal. Spent fuel pool temperature is being maintained at 106 degrees. RCS temperature is 75 degrees. The RCS is vented to atmosphere. Reactor level is 97.5 feet. 1C emergency diesel generator is cleared and tagged for maintenance. 13 station power transformer was returned to service on 4/10/04 at 2347. The operating crew briefed expected response and abnormal procedures if the 4kv vital bus did not transfer during the retest of 13 station power transformer. Operations successfully retested 1A and 1B 4kv vital bus transfer from 14 station power transformer to 13 station power transformer and back to 14 station power transformer in accordance with station operating procedures. Operations attempted to retest the 1C 4kv vital bus transfer from 14 station power transformer to 13 station power transformer. When the operator attempted to close 13CSD in feed breaker, the 14CSD in feed breaker opened as designed, but 13CSD breaker failed to close. The 1C 4kv vital bus deenergized due to both offsite power source in feed breakers opening and 1C emergency diesel generator unavailable. An ESF signal to start the 1C emergency diesel generator was provided by the safeguards equipment cabinet {SEC}. Since the 1C emergency diesel was cleared and tagged for maintenance, it did not start. The cause of the failure to transfer is not known at this time. The operating crew implemented the appropriate abnormal operating procedures for the de-energized 1C 4kv vital bus. Operator and plant response was as expected. Decay heat continues to be removed by the spent fuel pool cooling system. Outage incident response team is evaluating and troubleshooting the cause of the loss of power to 1C 4kv vital bus. ORAM risk remains yellow. There were no personnel injured during the event." The licensee will inform Lower Alloway Creek (LAC) Township and the NRC Resident Inspector. * * * RETRACTED ON 5/30/04 AT 1103 EDT BY STEVE SAUER AND TAKEN BY GERRY WAIG * * * The licensee provided the following information via facsimile: "On April 11, 2004 at 0023 PSEG made an 8 hour notification to report a valid ESF actuation of the 1 'C' Emergency Diesel Generator (Event Number 40665). At the time of the event Salem Unit 1 was defueled. The spent: fuel pool cooling system was providing decay heat removal and spent fuel pool temperature was being maintained at 106 degrees. RCS temperature was 75 degrees and the RCS was vented to atmosphere. The 1 'C' EDG was cleared and tagged for maintenance. "The 13 Station Power Transformer (SPT) had been returned to service on 4/10/04 at 2347. The operating crew was briefed on the expected response and reviewed the abnormal procedures if the 4kv vital bus did not transfer during the retest of 13 SPT. Operations successfully retested 1 'A' and 1 "B" 4kv vital bus transfer from 14 SPT to 13 SPT and back to 14 SPT in accordance with station operating procedures. When Operations attempted to retest the 1 'C' 4kv vital bus transfer from 14 SPT to 13 SPT, the 14 SPT in feed breaker opened as designed, but 13 SPT breaker failed to close and the 1 'C' 4kv vital bus de-energized. A signal to start the 1 "C" EDG was provided by the safeguards equipment cabinet (SEC), because the 1 'C' EDG was cleared and tagged for maintenance it did not start. "Decay heat continued to be removed by the spent fuel pool cooling system. "Subsequent Investigation into this event and further review of NUREG 1022 has determined that the condition described above is not reportable under the requirements of 10CFR50.72(b)(3)(iv) or 50.73(a)(2)(iv). "NUREG-1022, section 3.2.6 states that valid signals are those signals that are initiated in response to actual plant conditions or parameters satisfying the requirements for initiation of the safety function of the system. In this case, plant conditions were such that it did not require the 1 'C' EDG to be capable of starting and loading automatically in response to an undervoltage signal. The reactor was defueled and spent fuel cooling system providing fuel cooling was unaffected by the event. "NUREG-1022 states that train level actuations are reportable. However, in this instance, the EDG did not actuate because it was removed from service and was not required to be operable. NUREG-1022 states that single component actuations are typically not reportable because single components of complex systems, by themselves, usually do not mitigate the consequences of significant events. With the 1 'C' EDG removed from service, the 1 'C' bus undervoltage signal is not sufficient to complete the full actuation logic to mitigate the event. "Therefore this event was not reportable under 10CFR50.72 or 50.73, as per the guidance provided in NUREG 1022." The licensee will notify the NRC Resident Inspector. Notified R1DO (Richard Conte) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-04-11
40664 | 0 | SAN ONOFRE |  | 2 |  | [1] W-3-LP,[2] CE,[3] CE | 2004-04-10 11:50 | 2004-04-10 16:54 | 2004-04-10 | MANUAL REACTOR TRIP DUE TO LOSS OF BOTH MAIN FEEDWATER PUMPS San Onofre Unit 2 was manually tripped from 97% power due to the loss of feed water pumps. After both feedwater pumps tripped, the operators manually tripped the reactor. Both trains of the emergency feed water system actuated as expected due to the initial power level. The plant is stable at NOP/NOT. The cause of the feed water pump trips is being evaluated. All control rods fully inserted and all safety systems worked properly. The steam generators are discharging steam to the main condenser using the turbine bypass valves. AFW pumps are running to maintain steam generator water levels. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-04-10
40663 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-04-09 16:45 | 2004-04-09 21:49 | 2004-04-09 | TEXAS AGREEMENT STATE EVENT - STOLEN TROXLER MOISTURE DENSITY GAUGE At 2149 EDT on 04/09/04, the Texas Department of Health, Bureau of Radiation Control reported that between 1645 CDT and 1910 CDT on 04/09/04, a Troxler Moisture Density Gauge, Model #3430, Serial #24711, belonging to PSI Construction Company, San Antonio, TX was stolen from a 2003 Ford Ranger company pickup truck in San Antonio, TX. The stolen gauge contained an 8 millicurie Cs-137 source and a 40 millicurie Am-241:Be source. The gauge case was locked to the back of the truck but the gauge was not locked in its case. The company truck driver was suspended pending investigation. The theft was reported to the San Antonio Police Department. An announcement about the theft will be made on the local AM radio and the local TV Station tonight at 2200 CDT offering a $500 reward for the return of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-04-14
40662 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2004-04-09 16:30 | 2004-04-09 17:33 | 2004-04-09 | LOSS OF POWER TO EOF At 1630 on 4/9/04, it was discovered the Emergency Operating Facility had lost power. It is still without power. The cause was the backup facility diesel generator started and attempted to power the facility while normal offsite power was still applied. The electrical transfer switch was damaged. The time to repair is unknown. A space normally used as a media center is used as an alternate EOF. The Licensee notified the NRC Resident Inspector. | 93 | 100 | 0 | 93 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-04-09
40661 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-04-09 12:30 | 2004-04-09 17:14 | 2004-04-09 | OFFSITE NOTIFICATION OF CHEMICAL SPILL "On 419/04 at 1230 hours, Energy Northwest contacted Washington State Emergency Management Division (1-800-258-5990) to report a spill of pHreeGuard-4500 (a water treatment scale inhibitor) at the Columbia Generating Station Circulating Water Pump House. Washington State Emergency Management Division assigned Incident No. 04-0721 to this report. It is estimated as much as 60 gallons of the water treatment chemical could have been released to the concrete tank pedestal, asphalt apron, and adjoining soil over a period of several hours from a leaking expansion joint at the tank outlet. The leak was detected at about 0830 hrs. The leaking material is captured and redirected to the Circulating water basin. Washington State Emergency Management Division is relaying the information to the on-call responder in the Washington State Department of Ecology's Central Region Office. "This event is being reported under 10 CFR 50.72 (b)(2)(xi), any event or situation, related to the health and safety of the pubic or on-site personnel, or protection if the environment, for which a news release is planned or notification to other government agencies has been or will be made." The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-09
40660 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-08 22:16 | 2004-04-09 01:47 | 2004-04-09 | AUTOMATIC REACTOR TRIP DUE TO A FEEDWATER FLOW TRANSIENT "On April 8, 2004, at about 2215, Cook Unit 2 experienced a feedwater flow transient resulting in oscillating flows to Nr. 22, 23, & 24 steam generators. At 2216, the high level turbine trip setpoint was reached in Nr. 24 steam generator resulting in [a] main turbine trip signal. The main turbine trip signal caused a turbine trip resulting in an RPS [Reactor Protection System] actuation (reactor trip). At the time of the RPS actuation, Cook Unit 2 was at about 50 percent power and lowering power to facilitate turbine control maintenance. The cause of [the] feedwater transient is unknown and under investigation at this time. "Following the RPS actuation, the Auxiliary Feedwater System automatically started on low-low Steam Generator levels. This constituted a valid unplanned actuation of the Engineered Safeguards Feature (ESF). Operators stabilized the Plant using Condenser Steam Dumps and Auxiliary Feedwater. Unit 2 is currently in Mode 3 with Reactor Coolant System conditions stable at normal operating temperature and pressure. No other ESF systems actuated. "During the response to the RPS actuation by the operating crew, it was noted that the Main generator output breaker remained closed requiring a manual trip signal to open the output breakers. Another condition identified was a leak from a crack in the side of the 'C' South condenser near the condensate booster pumps' recirculation line inlet. The operating crew removed the condensate booster pumps from service to stop condenser hotwell outleakage; the main condenser remains in service. The causes for the above items are unknown and [are] under investigation at this time." All control rods fully inserted into the core in response to the automatic reactor trip and heat sink is currently been maintained using Auxiliary Feedwater Pumps and the Main Steam Dumps. Except as noted, all other systems functioned as required. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 50 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-04-09
40659 | 0 | DIABLO CANYON | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-04-08 13:00 | 2004-04-08 17:02 | 2004-04-08 | DEGRADED CONDITION - GREATER THAN ONE PERCENT OF STEAM GENERATOR TUBES DEFECTIVE "On April 08, 2004, during the Unit 1 twelfth refueling outage (1R12), analysis of eddy current data on [Steam Generator] SG 1-4 indicated that greater than one percent of the total tubes inspected in SG 1-4 were defective. Approximately ninety (90) defective tubes in SG 1-4 were detected and are being plugged. Most of the pluggable indications are due to circumferential primary water stress corrosion cracking in the Rows 5 to 8 U-bend region. Results of the SG tube inspection fall into Category C-3, which requires a four-hour non-emergency report in accordance with Technical Specification (TS) Table 5.5.9-2 and 10 CFR 50.72(b)(3)(ii) (an 8-hour requirement replacing the former (b)(2)(iii)(C), 4-hour requirement). "An NRC teleconference in accordance with TS 5.6.10.d to report the results of the voltage-based repair criteria implemented for the tube support plate intersections is currently scheduled for Wednesday April 14, 2004, at 1300 EDT. "A Special Report in accordance with TS 5.6.10.a and e will be submitted prior to returning Unit 1 to power operation. "A Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(v)(C) will be submitted within 60 days." The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-04-08
40658 | 0 | ABB, Inc |  |  |  |  | 2004-04-08 15:00 | 2004-04-08 15:49 | 2004-04-08 | INFORMATION CALL - POTENTIAL 10CFR PART 21 At 1549 EDT on 04/08/04, the Quality Manager of ABB, Inc, Coral Springs, FL, reported that he has determined that a potential defect exists regarding the potential overheating of overcurrent instantaneous units in protective relays in high power transformers, generators, and circuit breakers in various electrical power systems. The Quality Manager plans to determine the list of equipment affected and power plants and customers affected by this potential defect, including Duke Power Corporation, and provide written notification to the NRC of this potential defect within the next 2 to 4 weeks. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | FL | OTH | PAR |  |  |  |  | 0 | 2004-04-08
40657 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-04-08 09:44 | 2004-04-08 14:06 | 2004-04-08 | OFFSITE NOTIFICATION OF A FATALITY "The purpose of this report is to notify the NRC of a fatality involving a contract worker at the South Texas Project. Specifically, at 0810 (CDT), the South Texas Project Unit 1 Control Room was notified that an individual located outside of Unit 2 in a non-radiological area had lost consciousness. The site emergency medical team responded and an ambulance was requested at 0812. At 0836, the worker left the site in an ambulance. At 0944, South Texas Project was notified that the individual passed away at Matagorda General Hospital. This fatality was the result of a medical emergency and was not occupationally related. South Texas Project has notified OSHA of the fatality. A press release is not planned." The individual was a contractor working in a temporary tool storage area outside Unit 2. The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-08
40656 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-04-08 12:55 | 2004-04-08 12:58 | 2004-04-08 | PRESS RELEASE REGARDING LAW SUITE SETTLEMENT "Oyster Creek station is making a press release regarding a settlement with the State of New Jersey related to and environmental event which occurred on September 23, 2002. The press release contains the following information: "'FORKED RIVER, NJ. - The Oyster Creek Generating Station and the State of New Jersey agreed today to settle and resolve all matters related to the Sept. 23, 2002, water permit violation at the station. Under the terms of the agreement reached with the New Jersey Department of Environmental Protection and the Attorney General's office, Oyster Creek will pay a total of $1 million that will be distributed to several state organizations and environmental causes. "'The settlement resolves the 2002 event that resulted in the loss of nearly 6,000 fish. The event occurred because the station equipment was out of service for planned maintenance which caused the discharge water temperatures to rise resulting in the fish kill.'" The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-08
40655 | 0 | SEQUOYAH | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-08 08:45 | 2004-04-08 12:16 | 2004-04-08 | OFF SITE NOTIFICATION "On 04/08/04 at 0845 EDT, 24-hour notification was made to the Tennessee Department of Environment and Conservation (Division of Water Pollution Control) to report a potential upset of the Sequoia (SQN) National Pollution Elimination Discharge System Permit. Additional follow up evaluation is underway. "On 04/07/04 at approximately 0830, a field report was received that a possible break or breach in one of the two 15 feet diameter out fall discharge diffuser pipes where the plant discharge returns to the Tennessee River. SQN inserted a 'stop log' gate in the suspected discharge path and confirmed that the #1 (South) diffuser pipe is breached. The breached portion of the pipe is underwater on the river bottom approximately 100 feet from shore. "Concurrently, SQN placed both cooling towers in service with six of the available seven cooling tower lift pumps in service to minimize the potential for, or any adverse impacts from, exceeding any of the site's discharge limits. Repair actions for the pipe including initial inspections are in progress with divers on site at this time. "The Site Environmental Group, in conjunction with the Tennessee Valley Authority Corporate Environmental Group, are evaluating any potential thermal non-compliance issues." The Licensee does not consider this to be a security issue. The Licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-08
40654 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-04-07 20:00 | 2004-04-07 21:45 | 2004-04-12 | LOUISIANA AGREEMENT STATE REPORT - LOST RADIOGRAPHY CAMERA IN THE GULF OF MEXICO While passing a SPEC 150 Industrial Radiography Camera from a boat to an Apache Corporation Petroleum platform in the Gulf of Mexico, the radiography camera fell into the water. The water depth is 60 to 70 feet and is located approximately 50 to 70 miles from the coast of LA. The lost camera was a SPEC 150 S/N 223 with a 24 Curie Ir-192 source S/N 12433B. The radiography camera was in a Type B shipping container. The licensee plans on using divers to retrieve the radiography camera. * * * UPDATE 0940 EDT ON 4/12/04 FROM MIKE CIULLA TO S. SANDIN * * * The LA licensee notified the State of Louisiana (Joe Noble) that the camera was recovered on 4/10/04 at approximately 0930 CDT and has been returned to the manufacturer for evaluation. Notified R4DO (Powers), NMSS (Essig) and TAS (Hahn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-04-12
40653 | 0 | PROFESSIONAL INSPECTION AND TESTING |  |  |  |  | 2004-04-07 | 2004-04-07 13:51 | 2004-04-15 | LOST OR STOLEN TROXLER GAUGE The licensee reported that on Friday 4/2/04 the driver and the company's truck which contained a Troxler Moisture Density Gauge Model: 03430, S/N: 023850 with a Cs-137 and Am-241:Be source, S/N: 75-5183 did not return to the company's Temple Hills, MD office. On the same day, the licensee reported this to the Prince George's County, MD Police Department and swore a warrant for the unauthorized use of the vehicle. The vehicle was found on 4/6/04 in the Prince George's County impound lot. The licensee asked the lot attendant to look inside the vehicle for the gauge. The gauge was not there. The licensee also conducted a search of all of its storage locations to verify that the gauge had not been turned in, but they did not find the gauge. The licensee continues to search for the employee. * * * * UPDATE FROM R. CURTIS TO M. RIPLEY 1930 ET 04/15/03 * * * * The licensee reported a call from the Prince George's County, MD police stating that the gauge carrying case had been located in Hyattsville, MD and that the Haz Mat Team was responding to perform a radiological survey. The details of the gauge's discovery were not provided. The licensee subsequently reported that the Haz Mat Team from the Glendale, MD fire department responded and determined that the gauge was found inside its case and that the gauge appeared to be intact. The licensee will pick up the gauge at the Glendale, MD fire department on 4/16/04. Notified R1 DO (McDermott) and NMSS EO (B. Pierson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-04-07
40652 | -1 | CLINTON | 1 |  |  | [1] GE-6 | 2004-04-06 14:00 | 2004-04-06 19:47 | 2004-06-03 | AIR VALVE MISALIGNMENT REDUCES STANDBY LIQUID CONTROL CAPABILITY "On April 6, 2004, at 1400 CDT, Clinton Power Station discovered an air valve open for the Standby Liquid Control tank sparger. The open air sparger valve caused both Standby Liquid Control pumps to be inoperable due to the potential of air binding the pumps. The valve was closed, and the Standby Liquid Control is now operable. A Prompt Investigation is being commenced to determine circumstances of this open air sparger. The condition existed for approximately five weeks." The system was restored at approximately 1500 on 4/6/04. The Licensee notified the NRC Resident Inspector. * * * UPDATE 1840 EDT ON 6/3/04 FROM ED TIEDEMANN TO S. SANDIN * * * This report is retracted based on the following: "During further investigation, a calculation was performed to detail the air entrainment into the SLC pumps and the results show that air entrainment from the air sparger would not reduce system flow below that required by Technical Specifications. Therefore, it was determined that the system design is such that whenever the air sparge valve to the Standby Liquid Control (SLC) tank is open, the pumps remain operable and capable of performing their safety function. Thus, this occurrence (EN #40652 dated 4/6/04) was not reportable under 10CFR50.72(B)(3)(V)(A) and 10CFR50.72(B)(3)(V)(D). "The Licensee notified the NRC Resident Inspector." Notified R3DO (Lanksbury). | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-04-06
40651 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-04-06 11:51 | 2004-04-06 12:58 | 2004-04-06 | UNUSUAL EVENT DECLARED DUE TO TORNADO WARNINGS "The South Texas Project has invoked 10 CFR 50.54(x). Due to weather conditions associated with Tornado Warning, security personnel have been pulled from outside areas into hardened buildings. This condition does not meet the requirements of 10 CFR 73.51 (d) (3). When conditions have improved normal security measures will be reestablished. "At 1151 06 April 2004 due to the above information South Texas Project has a "Security Alert as defined by the Safeguards Contingency Plan" and is therefore in an Unusual Event per plant procedure OERP01-ZV-IN01 Emergency Classification rev. 6, Initiating condition HU1, Emergency Action Level -1. Class 'UE.'" At 1319, NRC management determined that an NRC response was not required. The Licensee notified the NRC Resident Inspector. * * * UPDATE AT 1418 EST ON 04/06/04 DUNNY TO GOTT * * * South Texas Project reported that the security forces have been reposted and they have secured from the Unusual Event. Notified R4DO (Spitzberg), NRR (Reis), DIRO (Wessman), TAS (Perez), DHS (Griggs), and FEMA (Caldwell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | DEVIATION FROM T SPEC |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | UNUSUAL EVENT | 4 | TX | POW |  | 50.72(a) (1) (i) | 50.72(b)(1) |  |  | 0 | 2004-04-06
40650 | 0 | US ARMY |  |  |  |  | 2004-03-11 | 2004-04-06 12:15 | 2004-04-06 | LOST TRITIUM SEALED SOURCE The US Army Tank Automotive Armaments Command reported that, during routine maintenance following live fire exercises at the National Training Center, Fort Erwin, CA, the US Army determined that the beam splitter from the muzzle reference sensor was missing from the muzzle of one of the tanks. The beam splitter contains a 10 curie tritium sealed source. The range was searched with negative results. Device number: NR-155D-120-S. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-04-06
40649 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-06 00:10 | 2004-04-06 06:43 | 2004-04-09 | MOMENTARY LOSS OF NOAA WEATHER RADIO SYSTEM "The Plant Site detected a momentary loss of the NOAA Weather Radio System from 00:10 am on 04/06/04 to 00:14 am on 04/06/04. During this time interval of inoperability for this system, a major loss of off site notification capability is considered. Site Emergency Planning personnel were notified and will investigate this momentary loss of system capability. The NOAA Weather Radio System is currently in service and functioning properly." The licensee will notify the NRC Resident Inspector. * * * RETRACTION AT 1700 ON 4/9/04 RUSSELL TO GOTT * * * "After further investigation, a determination has been made that there was no major loss of offsite notification capability of the Hatch Prompt Notification System (NOAA Weather Radio System). The momentary losses reported were caused by testing of the primary audio feed line utilizing a tone generator while investigating the loss of this feed. The secondary audio feed from Jacksonville NWS remained operable during the time of testing." The Licensee notified the NRC Resident Inspector. Notified R2DO (Decker) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-04-06
40648 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-04-05 20:30 | 2004-04-06 02:17 | 2004-04-06 | OFFSITE ELECTRICAL POWER SOURCES AND 1E 4KV DISTRIBUTION BUSES INOPERABLE "On 04/05/04 at 2030 hours, Engineering personnel informed Operations personnel of an issue affecting the ability of the offsite power sources to provide adequate 1E bus voltage consistent with the design basis. Operating procedures currently contain non-conservative values for minimum voltage on 1E 4 kV buses. In addition, the transformer auto load tap changer (LTC) is currently set to regulate at approximately 4200 VAC, a value that is below the required 1E 4 kV bus lower voltage design limit. Adequate voltage from the offsite power sources is required IAW General Design Criteria 17 to ensure that vital buses remain connected to their preferred power source and adequate terminal voltage exists at the load end device during accident conditions. The ability of the Emergency Diesel Generators to perform their design function is not affected by this condition. This event is being reported in accordance with 10CFR50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function because it affects the ability of both offsite power sources to provide adequate voltage to all 1E buses to properly mitigate the consequences of an accident. "Both offsite electrical power sources and all four 4 kV distribution buses have been declared inoperable and the appropriate Technical Specification Actions have been entered. The current voltage readings for all 1E 4 kV buses are between 4204 and 4263 VAC. The plant will remain in Operational Condition 4 until this condition is corrected. Engineering and Operations personnel are evaluating this condition to determine required corrective actions. All other plant systems are available to support Operational Condition change and reactor startup." The licensee notified the NRC Resident Inspector and will notify the local township. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-04-06
40647 | -1 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-05 19:16 | 2004-04-05 20:46 | 2004-04-09 | BRIEF LOSS OF NOAA WEATHER RADIO CAPABILITY "Site experienced a momentary loss of the NOAA Weather Radio System from 1916 to 1918 EST. During the time that this system was out of service, a major loss of offsite communication capability is considered. Site emergency planning personnel were notified and will investigate this momentary loss. The system is in service and functioning properly." The licensee notified both state/local agencies and will inform the NRC Resident Inspector. * * * RETRACTION AT 1700 ON 4/9/04 RUSSELL TO GOTT * * * "After further investigation, a determination has been made that there was no major loss of offsite notification capability of the Hatch Prompt Notification System (NOAA Weather Radio System). The momentary losses reported were caused by testing of the primary audio feed line utilizing a tone generator while investigating the loss of this feed. The secondary audio feed from Jacksonville NWS remained operable during the time of testing." The Licensee notified the NRC Resident Inspector. Notified R2DO (Decker) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-04-05
40646 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-05 11:40 | 2004-04-05 18:19 | 2004-05-27 | LOSS OF SAFETY FUNCTION FOR EMERGENCY DIESEL GENERATORS DURING SURVEILLANCE TESTING "At 1040 hrs during setup for Unit 1 Division 1 LOCA/LOOP Surveillance testing, the controlling procedure required making the Loss of Power instrumentation for the 1A and 1C ESS buses inoperable. The specification has a 1 hour time limit for restoration, or the associated Diesel Generators must be declared inoperable. Due to delays during the setup of equipment the time requirements were not met, and the 'E' (Substituting for 'A') and 'C' Diesel Generators were declared inoperable at 1140 hrs. The Loss of Power instruments were restored, and the Diesel Generators declared operable at 1206 hrs. Unit 1 is in Mode 5 requiring only 2 diesel generators operable, therefore not impacted by the Loss of Power instrumentation inoperability. "Also during the surveillance, two pump start timers failed to meet the required acceptance criteria. The 'A' ESW Pump timer actuated at 47.86 seconds (criteria; 36 sec. to 44 sec) and the 'C' ESW Pump timer actuated at 50.38 seconds (criteria: 39.6 sec. to 48.4 sec). With failure of the timers, proper loading on the Diesel Generators is not assured, and they were declared inoperable until the associated pump control breakers were opened. The 'E' Diesel Generator was declared inoperable at 1448 hrs, when the data analysis identified that the 'A' ESW pump timer did not meet acceptance criteria. The 'E' Diesel Generator was returned to operable at 1453 hrs when the DC Knife switches for the 'A' ESW pump were open. The 'C' Diesel Generator was declared inoperable at 1524 hrs, when the data analysis identified that the 'C' ESW pump timer did not meet acceptance criteria. The 'C' Diesel Generator was restored to operable at 1706 hrs after supported systems were realigned to prevent further loss of safety function and the DC Knife switches for the 'C' ESW pump were open. "The Susquehanna safety analysis requires three operable Diesel Generators to safely shutdown the plant. Therefore with only two operable Diesel Generators, the condition requires an 8 hr ENS notification in accordance with 10CFR50.72(b)(3)(v)and (vi)." All times referenced above are EDT. The licensee informed the NRC Resident Inspector. * * * RETRACTION FROM R. FRY TO M. RIPLEY 1419 ET ON 05/27/04 * * * * "The following is a retraction of ENS Notification #40642 AND #40646: On April 5, 2004, PPL Susquehanna, LLC reported three events to the NRC associated with Unit 1 Division 1 LOCA/LOOP surveillance testing. In each case, the safety function of two (out of 4) emergency diesel generators was brought into question during the testing. In two of these events, the E (substituting for A) and C diesel generators were administratively declared inoperable per Technical Specifications. This was necessary because Loss of Power instrumentation for the 1A and 1C buses, rendered inoperable in support of the test procedure, was not restored within 1 hour. In the third event, the E (for A) and C emergency diesel generators were, again, declared inoperable when two ESW pump start timers failed to meet acceptance criteria thus bringing the proper start sequencing of emergency loads into question. Because the Susquehanna Safety Analysis requires three diesel generators to safely shutdown an operating unit, the potential compromise of the diesel generator safety function was a concern for Unit 2 in each instance. (NOTE: Unit 1 was in Refueling Mode 5 and was, therefore, not impacted by these events.) Accordingly, Control Room personnel conservatively initiated ENS reporting under 10CFR50.72(b)(3)(v) in response to the apparent loss of safety function for Unit 2. "Subsequent engineering analysis has concluded that, although the declaration of diesel generator inoperability was correct and in accordance with Technical Specifications, fulfillment of these administrative actions did not result in an actual loss of safety function during any of the above described events. Details of the analysis show that the diesel generators were available to supply emergency power to the ESS buses and/or that sufficient redundant equipment was available to fulfill the safety function needs of Unit 2. These analysis conclusions provide the basis for retraction of the ENS reports made on April 5, 2004." The licensee notified the NRC Resident Inspector. Notified R1DO (R. Conte) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2004-04-05
40645 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2004-04-05 13:30 | 2004-04-05 16:41 | 2004-05-28 | MS AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE At 1641 EDT on 04/05/04, a MS Division of Radiological Health representative reported that at 1330 CDT on 04/05/04, a representative of Lampkin Construction Company, Vicksburg, MS, reported that between 1700 CDT on 04/02/04 and 0800 CDT on 04/05/04 a Troxler Moisture Density Gauge, locked in its transport case was stolen from a storage building at their office in Vicksburg, MS. A window had been broken and a door was forced open at the storage building. The Troxler Gauge, Model #3430, Serial #22349 contains an 8 milliCurie Cs-137 source and a 40 milliCurie Am-241-Be source. The licensee notified the MS Emergency Management Agency and the Warren County Sheriff. The licensee is planning to issue a press release. * * * UPDATE VIA EMAIL FROM B. J. SMITH, MS DIVISION OF RADIOLOGICAL HEALTH ON 5/28/04 AT 0956 EDT TAKEN BY CROUCH * * * The following information was received via e-mail: "Troxler gauge recovered by Warren County Sheriff's department on 5-26-04 at approximately 3:30 PM. Gauge was located on the Mississippi River after water level had receded. Gauge was picked up by Division of Radiological Health and returned to our office for leak test. No damage was observed to the gauge however it was apparent it had been under water. The gauge was determined to be free of contamination. Licensee Lampkin Construction RSO was coming to pick up gauge at DRH office this morning. Licensee will be required to send gauge for repair and leak tests and furnish DRH with copy of results. This incident is closed as of 5-28-04." * * * UPDATE VIA EMAIL FROM B. J. SMITH, MS DIVISION OF RADIOLOGICAL HEALTH ON 5/28/04 AT 1225 EDT TAKEN BY RIPLEY * * * The following information was received via e-mail: The location of the gauge recovery was clarified to be near a road close to Delta, Louisiana. The balance of the information remains the same. Notified R1DO (Conte), NMSS (Torres), and TAS (Hahn). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MS | OTH | AGR |  |  |  |  | 0 | 2004-04-08
40644 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2004-03-31 | 2004-04-05 16:45 | 2004-04-05 | OFFSITE NOTIFICATION TO THE STATE OF MAINE CONCERNING AN UNSCHEDULED RAD RELEASE "Notification made to government agencies (State of Maine Dept. of Human Services and Maine Emergency Management Agency) for unscheduled release of radioactive materials. On Wednesday 3/31 Maine Yankee had a minor release of 0.0000000470 curies of particulate material, which resulted in an exposure value of about 0.00000426 millirem. The cause of the release resulted from a minor fire during thermal cutting of structural material during the demolition process." The licensee will inform their designated NRC Inspectors. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-05
40643 | 0 | ST. VINCENT HOSPITAL |  |  |  |  | 2004-04-05 11:00 | 2004-04-05 16:33 | 2004-04-05 | MEDICAL EVENT INVOLVING FRACTIONATED DOSE DELIVERY HIGHER THAN PRESCRIBED A patient was prescribed five (5) fractional treatments of 500 centigray each to the surface using a 6.7 curie Ir-192 brachytherapy source. On 3/15, 3/22 and 3/29/04 the patient received 500 centigray/fraction at a depth of 5 mm. This resulted in a delivered dose of 818 centigray/fraction at the surface. The error was discovered prior to delivering the fourth (4th) fraction and is attributed to a miscalculation. The prescribing physician has been informed and concluded that there would be no adverse effects to the patient. The licensee is implementing additional reviews to preclude this type of event from reoccurring. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-04-05
40642 | -1 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-04-05 01:30 | 2004-04-05 04:02 | 2004-05-27 | LOSS OF SAFETY FUNCTION FOR EMERGENCY DIESEL GENERATORS DURING SURVEILLANCE TESTING "At 0030 [ET] during setup for Unit 1 Division 1 LOCA/LOOP Surveillance testing, the controlling procedure required making the Loss of Power instrumentation for the 1A and 1C ESS buses inoperable. The specification has a 1 hour time limit for restoration, or the associated Diesel Generators must be declared inoperable. Due to delays during the setup of equipment the time requirements were not met, and the associated Diesel Generators were declared inoperable at 0130. The Susquehanna Safety Analysis requires three operable Diesel Generators to safely shutdown. Therefore, this condition is reportable for Unit 2 under 10CFR50.72(b)(3)(v). Unit 1 is in Mode 5 and therefore not impacted. The Loss of Power instruments were restored, and the Diesel Generators declared operable at 0223." The licensee notified the NRC Resident Inspector. * * * * RETRACTION FROM R. FRY TO M. RIPLEY 1419 ET ON 05/27/04 * * * * "The following is a retraction of ENS Notification #40642 AND #40646: On April 5, 2004, PPL Susquehanna, LLC reported three events to the NRC associated with Unit 1 Division 1 LOCA/LOOP surveillance testing. In each case, the safety function of two (out of 4) emergency diesel generators was brought into question during the testing. In two of these events, the E (substituting for A) and C diesel generators were administratively declared inoperable per Technical Specifications. This was necessary because Loss of Power instrumentation for the 1A and 1C buses, rendered inoperable in support of the test procedure, was not restored within 1 hour. In the third event, the E (for A) and C emergency diesel generators were, again, declared inoperable when two ESW pump start timers failed to meet acceptance criteria thus bringing the proper start sequencing of emergency loads into question. Because the Susquehanna Safety Analysis requires three diesel generators to safely shutdown an operating unit, the potential compromise of the diesel generator safety function was a concern for Unit 2 in each instance. (NOTE: Unit 1 was in Refueling Mode 5 and was, therefore, not impacted by these events.) Accordingly, Control Room personnel conservatively initiated ENS reporting under 10CFR50.72(b)(3)(v) in response to the apparent loss of safety function for Unit 2. "Subsequent engineering analysis has concluded that, although the declaration of diesel generator inoperability was correct and in accordance with Technical Specifications, fulfillment of these administrative actions did not result in an actual loss of safety function during any of the above described events. Details of the analysis show that the diesel generators were available to supply emergency power to the ESS buses and/or that sufficient redundant equipment was available to fulfill the safety function needs of Unit 2. These analysis conclusions provide the basis for retraction of the ENS reports made on April 5, 2004." The licensee notified the NRC Resident Inspector. Notified R1DO (R. Conte) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2004-04-05
40641 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-04-04 14:30 | 2004-04-05 01:40 | 2004-04-29 | 24-HOUR NRC BULLETIN 91-01 LOSS OF CRITICALITY CONTROL NOTIFICATION "At 1430, on 04-04-04 the Plant Shift Superintendent was notified of a violation of Nuclear Criticality Safety (NCS) control in the C-333 process building. While preparing for start up of the C-333 #1 High Speed Purge and Evacuation (P & E) pump, operations discovered that the delta pressure (DP) alarm instrument line to the RCW supply was unattached and the isolation valve was closed. With the RCW instrument line not attached, both DP alarms for this pump were not functional and therefore not able to perform their safety function, violating a safety related item (SRI) in NCSE 039. The SRI requires that both DP alarms be functional while the P & E is isolated from the cascade. The purpose of the SRI Is to alert the operator to take actions within a 28-hour timeframe to prevent wet R-114 from leaking into the process gas system. The DP alarms had been nonfunctional for more than 28 hours when discovered. Both DP alarms were put back in service and the R-114 sampled and found dry within 4 hours of discovery, therefore, re-establishing double contingency. "The Senior NRC Resident Inspector has been notified of this event." "PGDP Problem Report No, ATR-04-1342; PGDP Event Report No. PAD-2004-09; Event Worksheet #40641 Responsible Division: Operations "SAFETY SIGNIFICANCE OF EVENTS: While the R-114 was demonstrated to be dry, both DP alarms relied on for double contingency were disabled without the knowledge of the operators. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: In order for a criticality to occur, an unsafe mass uranium deposit would have to be present in the process gas system, an R-114 leak to the process gas system would have to occur, the R-114 would have to contain an unacceptable amount of moisture ( i.e., greater than 10 kg of water) and moderate the deposit. "CONTROLLED PARAMETERS (MASS, MODERATION, G5OMETRY, CONCENTRATION, ETC): Double contingency is maintained by implementing two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: No known mass of licensed material exists in the #1 High Speed Purge and Evacuation pump. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on the DP switch alarming to alert the operator to take action to either verify the R-114 is dry or to isolate the RCW and remove the R-114 from the system in order to prevent water from leaking into the process gas system. This DP alarm was not maintained as functional. The DP alarm was put back in service and the R-114 was sampled and found to be dry. The SRI was not maintained and the control was violated but the process condition was maintained. "The second leg of double contingency is based on the independent DP switch alarming to alert the operator to take action to either verify the R-114 is dry or to isolate the RCW and remove the R-114 from the system in order to prevent water from leaking into the process gas system. The independent DP alarm was not maintained as functional. The independent DP alarm was put back in service and the R-114 was sampled and found to be dry. The SRI was not maintained and the control was violated but the process condition was maintained. This re-established double contingency. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Both DP switches were returned to service and the R-114 was sampled and found to be dry on 04-04-04 at 1655." * * * UPDATE 4/29/04 AT 1025 BEASLEY TO GOTT * * * "Subsequent assay sample analysis of the Purge and Evacuation pump system indicates the system is non-fissile." The PGDP notified the NRC Resident Inspector. Notified NMSS (Torres) and R2DO (Ernstes) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-04-05
40640 | 0 | WESTERN SOIL |  |  |  |  | 2004-04-03 02:00 | 2004-04-03 15:55 | 2004-04-03 | STOLEN MOISTURE DENSITY GAUGE A truck containing a CPN moisture density gauge was stolen from an employee's home in Puerto Rico. The truck and gauge were stolen between 0200 - 0300 EST on 04/03/04. The truck was recovered without the gauge. A report was filed with the police, and the local media was informed. A reward for the gauge's return has been offered. The gauge contains 10 millicuries Cs-137 and 50 millicuries Am-241. The gauge's serial number is MD10606200. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | PR | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-04-03
40639 | -1 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-04-03 10:50 | 2004-04-03 14:10 | 2004-05-05 | VALID ACTUATION OF AUXILIARY FEEDWATER SYSTEM DURING MAINTENANCE "This is an 8-hour notification being made to report that a valid ESF Auxiliary Feed actuation occurred. Salem Unit 1 is in mode 5 with RHR providing shutdown cooling. '11' Aux Feed Pump was in service to fill '13' and '14' steam generators for wet lay-up conditions. Actual levels were low in both '13' and '14' steam generators but jumpers were installed on steam generator narrow range level channel III and IV to prevent an ESF actuation. On 4/03/04 at 1050 AM, a breaker effecting reactor protection system channel III was cleared and tagged as part of preparations to remove 1C 4KV vital bus from service. The actual low level in '13' and '14' steam generators along with the power loss to channel III caused 2 out of 3 logic to be satisfied and initiated an AFW actuation. '11' Auxiliary Feed Pump remained running. '12' Auxiliary Feed Pump auto started. '13' Auxiliary Feedwater Pump was removed from service prior to the actuation and did not start. The '13' and '14' steam generators continued to fill. '11' and '12" Auxiliary Feed Valves (11AF21 and 12AF21) were closed and no level rise was observed. The breaker was restored and reactor protection system channel III was placed back in service. All auto start signals cleared after power was restored and the '12' Aux Feed Pump was stopped at 1101. There were no unusual or unexpected plant response from the actuation. All safety systems and equipment performed as expected. Entry into mode 6 is expected this afternoon and progress of the refueling outage is expected to continue. There were no personnel injured." The licensee will inform the Lower Alloways Creek Township (LAC) and has informed the NRC Resident Inspector. * * * RETRACTION ON 05/05/04 AT 1252 EDT FROM S. SAUER TO A. COSTA * * * "On April 3, 2004 at 1410 PSEG made an 8 hour notification to report a valid ESF actuation of the auxiliary feedwater system (Event Number 40639). At the time of the report 11 Auxiliary feedwater pump was in service to fill the 13 and 14 steam generators for wet lay-up. The levels on those generators were low (as previous plant condition had demanded) and the jumpers had been installed in the level detectors to prevent the automatic start of the auxiliary feedwater pumps. 12 auxiliary feedwater pump was out of service. The steam driven auxiliary feedwater pump was tagged out of service. Core heat removal was being provided by the Residual Heat Removal System. On April 3, with the steam generator level being carried below the low level setpoint, in accordance with procedures, as a result of other activities associated with the refueling outage the installed jumpers were removed causing the auto start of the 12 pump. "Subsequent investigation Into this event and further review of NUREG 1022 has determined that the condition described above is not reportable under the requirements of 10CFR50.72(b)(3)(iv) or 50.73(a)(2)(iv). As stated In NUREG 1022 the intent of reporting under this paragraph is '..to report actuations of systems that mitigate the consequences of significant events .. The Staff does not consider this to include single component actuation because single components of complex systems, by themselves usually do not mitigate the consequences of significant events.' Furthermore valid signals are defined as ' those signals that are Initiated in response to actual plant conditions .. Satisfying the requirements for initiation of a safety function of the system.' (emphasis added on safety function). "In this particular event the required Safety Function to maintain the core cooled and decay heat removal was being accomplished by the Residual Heat Removal System and it remained unaffected throughout this event. The plant was in a condition where the steam generators in conjunction with the Auxiliary Feedwater System were not part of the ultimate heat sink or a principal means to remove decay heat. The Auxiliary Feedwater System was only functional and available to provide a means to place the steam generators in wet lay-up in support of outage activities. The 11 pump was already in service providing for this non-safety related function. Thus the auto start of the 12 pump was not as a result of a valid signal for a significant event that required initiation of a mitigating function; e.g. an ESF actuation. Therefore this event was not reportable under 10CFR50.72 or 50.73, as per the guidance provided in NUREG 1022." The licensee notified the NRC Resident Inspector. Notified R1DO(Della Greca). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-04-03
40638 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2004-04-03 | 2004-04-03 13:56 | 2004-04-05 | AGREEMENT STATE REPORT - NUCLEAR DENSITY GAUGE MISSING WITH EMPLOYEE Dressler Consulting reported to the Kansas Department of Health and Environment that a trusted employee failed to show up at his worksite at 634 Prospect, Kansas City, MO this morning. Dressler Consulting is located in Shawnee Mission, KS. The employee had in his possession a Humboldt Moisture Density Gauge, Model 5000, Serial Number 2655 which had a 10 millicuries Cs-137 and 40 millicuries Am-241source. Dressler Consulting also notified the local law enforcement, Raytown Police Department, and the MO Department of Health. The gauge is normally restrained with a 2000# tow strap and locks in the employee's truck. The employee was told to store the gauge inside his home overnight. A Dressler Consulting representative attempted to contact the employee on telephone and went to his apartment in Raytown, MO with negative results. The employee last contacted Dressler Consulting at 1700 CST on 4/2/04 when he finished a job at 6700 Agnes, Kansas City, MO. * * * UPDATE FROM DRESSLER TO GOTT AT 1527 EST ON 4/3/04 * * * Dressler Consulting reported that the driver was contacted by his sister on his personal cell phone. His truck is broken down between Saint Louis and Kansas City, MO. The gauge is not in the truck. The driver will be contacted again to determine the location of the gauge. Notified NMSS (Moore) and R4DO (Powers) *****UPDATE FROM DRESSLER TO LAURA AT 0930 EST ON 4/5/04***** Dressler Consulting reported that the gauge was found in the employees apartment and is no longer considered missing. The protocol for handling and storing gauges will be reviewed by the licensee. Notified NMSS (L. Psyk) and R4DO (B. Spitzberg). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2004-04-07
40637 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-04-03 13:14 | 2004-04-03 13:17 | 2004-04-03 | NOTIFICATION TO VIRGINIA DEQ CONCERNING A CHEMICAL SPILL "Notification made to State Department of Environmental Quality (DEQ) for a chemical spill of Calgon H-901-g going into onsite waters." Approximately 500 gallons of chemicals containing Bromine used to treat service water spilled onsite. A portion of the spill entered the drainage system and was released offsite. The licensee attributes the spill to a mechanical failure on their brominator system and is in the process of cleaning up the material onsite. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-03
40636 | -1 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-04-03 03:00 | 2004-04-03 05:49 | 2004-05-06 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "During plant startup from the Brunswick Unit 1 Refueling Outage, the High Pressure Coolant Injection (HPCI) System was declared inoperable due to pump data not meeting the acceptable value of OPT-09.2, HPCI System Operability Test. With pump flow established at the reference value of 4550 gallons per minute, the actual turbine speed was 2530 rpm, outside the acceptable range of 2485-2515 rpm. "Initial Safety Significance Evaluation: Minimal since the Automatic Depressurization System (ADS), the Low Pressure Coolant Injection System (LPCI), and the Core Spray System are Operable. In addition the Reactor Core Isolation Cooling System (RCIC) is Operable. "Corrective Actions: Engineering to evaluate the test results and determine corrective actions." The licensee will notify the NRC Resident Inspector. * * * RETRACTION TAKEN ON 5/6/04 @ 1534 EDT BY CROUCH FROM ELBERFELD * * * The following information was obtained from the licensee via facsimile: "The purpose of this call is to retract the notification (Event Number 40636) made by the Brunswick Steam Electric Plant, Unit No, 1, Docket No. 50-325 / License No. DPR-71, on April 3, 2004, at 0549 hours. "On April 2, 2004, at 2324 hours, the High Pressure Coolant Injection (HPCI) system was declared inoperable for scheduled testing performed in accordance with 0PT-09.2, 'HPCI System Operability Test.' 0PT-09.2 includes, in part, Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.7, to verify that, with reactor pressure < 1045 and > 945 psig, the HPCI pump unit could develop a flow rate > 4250 gpm against a system head corresponding to reactor pressure. The testing also includes in part, In-service Test (IST) program requirements for HPCI pump performance (to test for pump degradation). During this testing, water is circulated from the Condensate Storage Tank (CST) through the HPCI pump and back to the CST through a 'Bypass to CST' valve. Motive force for the pump is provided by reactor steam being routed through the HPCI turbine into the suppression pool. Due to the heat energy being deposited in the suppression pool, time for HPCI turbine/pump testing is limited. "When tested, the HPCI pump passed the TS SR 3.5.1.7 pump pressure and flow rate test requirements. However, when HPCI turbine speed was set to the IST-required value of 2,500 rpm, as indicated by the control room indicator 1-E41-C002-4 (the preferred indication), the IST required system flow of 4,550 gpm could not be attained. Turbine speed was then adjusted, using a portable speed indicator, to attain 4,550 gpm system flow. The portable speed indicator read 2530 rpm, high, outside the acceptable range of 2,485 to 2,515 rpm. The unsatisfactory test indicated potential pump degradation. The IST program requires the equipment to be declared inoperable until unsatisfactory test results are evaluated. On April 3, 2004, at 0436 hours, the HPCI system was declared inoperable due to the unsatisfactory test. At 0549 hours, the NRC was notified (Event Number 40636) in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. "During the testing with the portable speed indicator, it was noted that the control room indicator 1-E41-C002-4 was reading high (i.e., 1-E41-C002-4 was reading 2,600 rpm compared to 2,500 rpm on the portable speed indicator). Turbine speed indicator 1-E41-C002-4 was adjusted back to within required accuracy in accordance with Work Order 306977. "After the initial test, a thorough review of pump data, instrument calibration data, and IST program guidance was conducted. It was determined that there was no indication of pump degradation and no indication of a flow indicator problem. Having corrected a speed indicator problem, sections of 0PT-09.2 were performed on April 5, 2004, to test for pump degradation using the preferred speed indicator 1-E41-C002-4. Test results were satisfactory and demonstrated that the pump performance met the IST program requirements. The HPCI system was declared operable on April 5, 2004, at approximately 0521 hours. Investigation of this condition is documented in the corrective action program in Action Request (AR) 123551. "NUREG-1022, Rev. 2, Section 3.2.7 (page 56) lists types of events or conditions that are generally not reportable under 10 CFR 50.72(b)(3)(v) and 10 CFR 50.73 (a)(2)(v) criteria. The list of not-reportable conditions includes: "- Removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function) "On April 2, 2004, the HPCI system was removed from service for testing in accordance with an approved procedure 0PT-09.2. The system was declared inoperable due to the test results discussed above, and since the HPCI system is a single train safety system, an ENS notification was made. However, no condition was discovered that could have prevented the HPCI system from performing its functions. "Carolina Power & Light Company, doing business as Progress Energy Carolinas, Inc., has determined that this event does not meet the 10 CFR 50.72 or 10 CFR 50.73 reporting criteria and the notification for Event Number 40636 is retracted. The resident inspector has been notified." | 22 | 0 | 0 | 22 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-04-03
40635 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2004-04-02 13:30 | 2004-04-02 20:30 | 2004-04-02 | OFFSITE NOTIFICATION TO LOCAL GOVERNMENT AGENCY FOLLOWING SIREN ACTIVATION DURING TESTING "One emergency siren activated for approximately one minute during planned maintenance activities. The control room was notified later and the initial determination was that the event was not reportable. However, upon further review, it was determined to be reportable due to later media and local government notification." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-04-02
40634 | 0 | U.S. DEPT OF VA HP PROGRAM |  |  |  |  | 2004-03-31 12:00 | 2004-04-02 17:40 | 2004-04-02 | POSSIBLE MEDICAL EVENT The U.S. Department of Veteran's Affairs Health Physics Program (VA NHPP) notified the NRC of the following possible Medical Event at the VA Greater Los Angeles Healthcare System (GLAHCS), 11301 Wilshire Boulevard, Los Angeles, California 90073, a master material license permittee. "On March 31, 2004, a permanent-implant prostate brachytherapy procedure was performed. 109 Iodine-125 seeds were implanted in the patient. A number of seeds were mistakenly placed in the patient's bladder. The seeds placed in the bladder have been recovered. At this time, it appears that the dose to the prostate was more than 20 percent less than that prescribed. The VA GLAHCS has taken initial action to prevent a recurrence. The VA NHPP intends to conduct a reactive inspection next week." The VA NHPP is in the process of verifying that the licensee notified the patient of this occurrence. Initial action taken to prevent recurrence was to cease performing this procedure until an investigation and root cause determination are complete. The licensee has not yet determined whether any unintended damage was done to the bladder as a result of this procedure. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | CA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-04-02
40633 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2004-04-01 13:00 | 2004-04-02 10:35 | 2004-04-02 | OUTDOOR AREA CRITICALITY WARNING SYSTEM HORN INOPERATIVE "At approximately 1:00 p.m. on April 1, 2004 it was discovered a Criticality Warning System (CWS) horn had been rendered inoperative in an unoccupied remote outdoor area due to maintenance conducted on the system on March 31, 2004. Maintenance was conducted on the system to remove a tree that had fallen across the communication line to Data Acquisition Module (DAM) #25 which provides coverage for the outdoor process lagoon area. During maintenance activities to remove the tree, a temporary system was installed and the permanently installed system horn was disconnected. Following completion of the maintenance, the restoration effort failed to reinstall a local horn relay. "Throughout the maintenance, the DAM remained operable and indications of normal conditions were available. With the exception of the local horn at the remote outdoor area, all other system functions remained operable. "Upon discovery of the local horn being disabled, the horn relay was promptly restored and tested, confirming restoration of full system operability. This condition is reported pursuant to 10CFR70.50(B)(2) as an event in which equipment designed to mitigate the effects of an incident are disabled or fails to function as designed. Incident investigation and evaluation of additional corrective actions are continuing." "SAFETY SIGNIFICANCE OF EVENTS: Low safety significance - The potential for a criticality event in this area is highly unlikely because of the very low uranium concentration, low material density, and high levels of non-uranium materials. This is consistent with the Integrated Safety Analysis (ISA) for the area. "POTENTIAL CRITICALITY PATHWAYS INVOLVED: There is no known process upset that would change the highly unlikely potential for a criticality in this area. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION ETC.): Density and Mass (concentration) "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST BASE CRITICAL MASS): N/A. Affected area is final wastewater process lagoon. Uranium concentration in the affected area is approximately [deleted] parts per million (PPM) "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEMS AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: N/A "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: System was restored to normal operation at 1300 on 4/1/04 and subsequently tested. Investigation of event and evaluation of additional corrective actions pending." The licensee will notified the local County, the State of North Carolina, and NRC Region II. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | NC | FUE |  | 70.50(b)(2) |  |  |  | 0 | 2004-04-02
40632 | 0 | WATERFORD | 3 |  |  | [3] CE | 2004-03-31 19:19 | 2004-04-01 00:44 | 2004-04-01 | NEW WORST CASE SINGLE FAILURE MAY EXCEED 10 CFR 50.46 ACCEPTANCE CRITERION FOR SBLOCA "A new worst case single failure was identified on 03-31-04 for the small break LOCA analysis of record due to a postulated loss of a DC power bus. This condition may result in the analysis of record exceeding 10 CFR 50.46 acceptance criterion of 2200 F when a small break LOCA with this failure is postulated. "The current small break LOCA analysis of record assumes a single failure of one Emergency Diesel Generator (EDG) and credits flow from one charging pump. The peak cladding temperature for the analysis of record is 1929 F compared to the acceptance criteria of less than or equal to 2200 F. Half of the flow from a charging pump is assumed to go to the RCS and half is assumed to flow out the break. It was identified on 03-31-04 that a single failure of a DC power bus would be more limiting than the currently assumed single failure of an EDG. The DC bus failure will result in the EDG failure to start and also cause a charging loop isolation valve to the RCS to fail closed on loss of DC power. The other charging flow path to the RCS is on the assumed broken RCS leg so it is assumed to be spilled to the containment resulting in no charging flow to the RCS. Therefore, no charging flow would be delivered to the RCS as assumed in the current small break LOCA analysis of record. This condition has not been analyzed. "Engineering judgment indicates that in the event of a small break accident the 10 CFR 50.46 acceptance criterion of 2200 F may be exceeded if the charging flow is not credited in the analysis of record. Therefore, this condition is reportable pursuant to 10 CFR 50.46 and 10 CFR 50.72(b)(3)(ii)(B). "The current conservatism in the analysis of record and previous Westinghouse SBLOCA non-design basis scoping analyses using the NOTRUMP code provide assurance the plant is operating in a safe manner and is operable. The NOTRUMP analyses included cases with no changing flow. The peak clad temperature for these analyses were significantly below the acceptance criteria of 2200 F by more than 200 F. Thus, if an analysis were performed for Waterford 3 with the NOTRUMP code there is reasonable assurance due to the large margins that acceptable results would be achieved without any charging flow. "This report is based on conservative judgment and available information. This report may be retracted based on the results of further evaluation." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | OTHER UNSPEC REQMNT |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-04-01
40631 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2004-03-31 18:56 | 2004-03-31 19:28 | 2004-03-31 | UNUSUAL EVENT DECLARED DUE TO REACTOR COOLANT SYSTEM LEAKAGE GREATER THAN 10 GPM On 3/31/04, Saint Lucie Unit 1 was in a refueling outage when it experienced a leak-by which appeared to be at a Volume Control Tank to Hold Up Tank divert valve off the Shutdown Purification System. The Reactor Coolant System (RCS) leakage was greater than ten gallons per minute as indicated in the Control Room. The Facility declared an Unusual Event at 1856 EST since the RCS leakage was greater than ten but less fifty gallons per minute. Refueling activities were stopped as a result of the incident. The RCS leakage was isolated and the Unusual Event was terminated at 1915. The licensee has notified local, state and other government agencies through the ring down phone system. The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Refueling; FMode1: Refueling | UNUSUAL EVENT | 2 | FL | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-03-31
40630 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-03-31 07:57 | 2004-03-31 18:02 | 2004-03-31 | NON-LICENSED EMPLOYEE TESTED POSITIVE FOR ALCOHOL A non-licensed supervisor tested positive for alcohol during a "for cause" test. A review of the employee's work concluded that the individual had not been engaged in safety-related activities. The individual has been denied access to Point Beach Nuclear Plant and to all other Nuclear Management Company, LLC (NMC) sites. Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 92 | 100 | 0 | 92 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY | OTHER UNSPEC REQMNT |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2004-03-31
40629 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-03-30 17:00 | 2004-03-30 23:54 | 2004-04-02 | STATE LICENSEE REPORTED A CPN GAUGE WAS STOLEN FROM THEIR TECHNICIAN'S TRUCK Lor Geo Technical of Riverside, CA reported to the state of California that a CPN nuclear gauge model MC1DR serial # MD10506147 was stolen from the back of a technician's pickup truck when it was parked at a fast food restaurant in Victorville, CA. The gauge contained 10 millicuries of Cs-137 and 50 millicuries of Am-241. The local police department was notified and a reward is being offered. * * * UPDATE 1550 EST ON 4/2/04 FROM DONELLE KRAJEWSKI TO S. SANDIN VIA EMAIL * * * The State of California was notified on 3/31/04 that the gauge was recovered intact in a utility trench at a jobsite near the one the user had been working in on 3/30/04. The lock on the gauge handle was missing. The recovery of the gauge was also reported to the police by the user. Notified R4DO (Powers), NMSS (Essig) and Mexico (Gonzalez) via fax. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-04-02
40628 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2004-03-30 11:29 | 2004-03-30 17:38 | 2004-03-30 | AUTOMATIC REACTOR TRIP DUE TO LO-LO STEAM GENERATOR LEVEL "On March 30, 2004, while at power, VCSNS [V.C. Summer Nuclear Station] personnel were performing a reactor building inspection to identify the source of reactor coolant system unidentified leakage that was within Technical Specification (TS) limits. "At 1129 hours, a pressure boundary leak was identified at the seal injection line to reactor coolant pump 'C'. "Pursuant to TS 3.4.6.2, Action a., VCSNS commenced a controlled reactor shutdown at 1410 on March 30, 2004. "During the shutdown, the main turbine experienced higher than normal vibration. At 1516, the turbine was manually tripped at approximately 43% reactor power. Subsequent to the turbine trip, feedwater regulating valve IFV-498 failed in the closed position while in automatic with a full open demand signal. The cause of this failure is not known. The reactor automatically tripped at 1520 due to lo-lo level in the 'C' steam generator at 10% reactor power. "All control rods fully inserted and all safety systems responded normally. Both motor driven emergency feedwater pumps started as required. The plant stabilized in mode 3." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 10 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | PLANT S/D REQD BY TS | RPS ACTUATION - CRITICAL | DEGRADED CONDITION | VALID SPECIF SYS ACTUATION | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(iv)(A) | 0 | 2004-03-30
40627 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2004-03-17 | 2004-03-30 16:30 | 2004-03-30 | SOUTH CAROLINA - AGREEMENT STATE REPORT ON PERSONNEL EXTERNAL CONTAMINATION The following event description report (ID No. SC040001) was received at the Operations Center via facsimile: "The SC Department of Health and Environmental Control was notified on Tuesday, March 30, 2004, by the physicist/consultant for the facility that a pharmacist in training in the nuclear pharmacy had sustained external contamination on his hand and forearm. The pharmacist was in the process of compounding Iodine-131 from a vial when a spill apparently took place. His arm and forearm were contaminated. This vent took place on Wednesday, March 17, 2004. The pharmacist did not notify anyone that this event had taken place. He performed clean up of the area and decontamination of the skin. He continued work until March 19, 2004, at which, time he performed a bioassay prior to going on vacation. He returned to work on Monday, March 29, 2004, at which time the nuclear pharmacist in charge discovered the elevated readings on the person's arm and forearm. The appropriate hospital/nuclear medicine personnel were notified. The person involved has been suspended from any and all duties involving radioactive material. The consultant for this facility is in the process of assimilating additional data and the person involved has had two whole body scans performed to determine if there was any internal uptake of the radioiodine. These scans have produced no indication of internal uptake at this point. The event is still under investigation and updates will be made through the national NMED system as they become available." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2004-04-02
40626 | 0 | POINT BEACH |  | 2 |  | [1] W-2-LP,[2] W-2-LP | 2004-03-30 12:15 | 2004-03-30 15:26 | 2004-03-30 | SAFETY INJECTION ACCUMULATOR LEVEL GREATER THAN ALLOWED BY TECHNICAL SPECIFICATION "Unit 2 'A' Safety Injection Accumulator level was determined to be greater than level band allowed by technical specification 3.5.1 for Safety Injection Accumulators at 1127 [CST]. A power reduction in preparation for a normal reactor shutdown was commenced at 1215 in accordance with normal plant procedures. "The Safety Injection Accumulator level instruments were in question due to one indicator being within the normal range and the other being off-scale high. During troubleshooting efforts, an ultra-sonic detector was used to verify 'A' Safety Accumulator tank level. The ultra-sonic detector indicated that level was above the high scale indication, and the accumulator was declared OOS due to being above the maximum accumulator volume allowed by SR 3.5.1.2 (<1136 cubic feet). The Unit 2 'B' Safety Injection Accumulator was unaffected by the event and remains operable. "The Unit 2 'A' Safety Injection Accumulator level and pressure was returned to technical specification parameters at 1403. The Unit 2 shutdown was stopped with the unit at 82% power and actions are in progress to return to full power operation." The licensee notified the NRC Resident Inspector. | 0 | 82 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-03-30
40625 | 0 | QUAD CITIES |  | 2 |  | [1] GE-3,[2] GE-3 | 2004-03-30 07:40 | 2004-03-30 10:40 | 2004-03-30 | AUTOMATIC REACTOR SCRAM DURING TURBINE THRUST BEARING WEAR DETECTOR TESTING "At 0740 hours [CST] during testing of the turbine thrust bearing wear detector, a main turbine trip occurred. This resulted in an automatic reactor scram due to turbine stop valve closure. Following the scram all Group II (Primary Containment) and Group III (Reactor Water Cleanup) isolations occurred as expected. All essential equipment functioned as required. Unit 2 remains in Mode 3 with reactor water level in the normal level band. An investigation into the Unit 2 turbine trip is in progress. "Unit 1 was unaffected by the event and remains at 85% power." All control rods fully inserted. Decay heat is being removed via steam to the main condenser using the bypass valves. The Licensee notified the NRC Resident inspector. | 0 | 0 | 0 | 0 | 72 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-03-30
40624 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-03-29 17:22 | 2004-03-29 20:52 | 2004-03-30 | OFFSITE NOTIFICATION OF A FATALITY "The purpose of this report is to notify the NRC of a fatality involving a [contract] worker from Nine-Mile Point Unit 2, for which a news release is planned. Specifically, at 1541[EST], the Nine Mile Point Unit 2 Control Room was notified of an individual (located in a non-radiological area) experiencing dizziness and tightness in his chest. The Fire Brigade responded and requested an ambulance at 1558. At 1633, the worker left the site in an ambulance. At 1722, Nine Mile Point Unit 2 was notified that the individual passed away at Oswego Hospital." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 3/30/04 AT1433 EST FROM STEPHEN FREGEAU TO A. COSTA * * * "The purpose of the report is to update and clarify the description of the fatality involving a worker at Nine-Mile Point Unit 2. The initial notification occurred on March 29, 2004 at 2052. The utility wants to clarify that this fatality was the result of a medical emergency and was not occupationally related. The utility [did not issue a press release for the initial event notification] does not plan on issuing a press release concerning this incident [update]." The licensee notified the NRC Resident Inspector of this update. Notified R1DO (Jenison). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-29
40623 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-03-29 15:59 | 2004-03-29 16:26 | 2004-03-29 | THE LICENSEE NOTIFIED THE CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION OF AN OIL SPILL A hydraulic hose ruptured during demolition activities, resulting in a spill of approximately 2 gallons of oil to the soil and 6 gallons of oil to the concrete. The spill has been contained and cleaned up. The licensee notified the State DEP. There is no Resident Inspector at the site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-29
40622 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-03-29 14:04 | 2004-03-29 17:17 | 2004-03-29 | AUTOMATIC REACTOR TRIP DURING REACTOR TRIP BYPASS BREAKER MANIPULATION TEST "On March 29, 2004 at 1404 hours [EST], Unit 2 received an automatic actuation of the Reactor Protection (RPS). The RPS actuation occurred when the train B Reactor Trip Bypass Breaker was manipulated during the conduct of the Solid State Protection System (SSPS). Testing the Bypass Breaker had been racked in and closed, but correct indication was not received earlier during the test. The decision was made to restore from the testing and the Bypass Breaker was being racked out when the actuation occurred. The Unit was at full power with all system in normal alignment. "Initial indication is that the actuation signal was a Power Range Rate Trip. The RPS actuation is believed to be related to the manipulation of the Bypass Breaker. Cause is under investigation. Following the RPS actuation, the Auxiliary Feedwater System automatically started on low-low Steam Generator levels. This constituted a valid unplanned actuation of the Engineered Safeguards Feature (ESF). Operators stabilized the Plant using Condenser Steam Dumps and Auxiliary Feedwater. No other ESF systems actuated. All other Plant systems responded normally." All control rods fully inserted into the core. The Plant is currently stable in Mode 3, and Steam Generator levels are being maintained using the Auxiliary Feedwater System. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-29
40621 | 0 | VOGTLE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-03-29 10:30 | 2004-03-29 14:08 | 2004-03-29 | LICENSED OPERATOR TESTED POSITIVE FOR A CONTROLLED SUBSTANCE " Notification was received at 1030 EST on March 29, 2004 of a confirmed positive [random test] FFD result for a Controlled Substance for a Licensed Operator. This individual's unescorted access authorization has been suspended pending investigation." Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2004-03-29
40620 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-29 07:38 | 2004-03-29 09:57 | 2004-03-29 | LOSS OF POWER TO NOAA WEATHER RADIO SYSTEM Due to the loss of power to the Plant Entry Security Building, the NOAA Weather Radio System was rendered inoperable at 0738 EST on 3/29/04. At 0751 power was restored to the NOAA Weather Radio System. This loss of this system is considered a major loss of offsite notification capability. The power reduction was due to loss of power to one of the cooling towers which has also been restored. The Licensee notified the NRC Resident Inspector. | 91 | 91 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-03-29
40619 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2004-03-28 13:49 | 2004-03-28 21:25 | 2004-03-28 | OFFSITE NOTIFICATION AT SAN OFRE 2 AND 3 DUE TO INADVERTENT WEAPON DISCHARGE "At about 1349 (PST) on March 28, 2004, while a Security Offer was receiving his weapon in the armory, the weapon accidentally discharged as it was being holstered. The discharge grazed the officer's leg and the officer was treated for the resulting abrasion. At about 1425 PST, Southern California Edison notified the FBI (SONGS LLEA). SCE is reporting this occurrence in accordance with 10CFR50.72(b)(2)(xi)." The NRC Resident Inspector was notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-28
40618 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2004-03-28 13:03 | 2004-03-28 20:27 | 2004-03-28 | BOTH EMERGENCY DIESEL GENERATORS INOPERABLE DUE TO CLOSED FUEL OIL TRANSFER CROSS-TIE VALVE "CNS was operating at 100% power in Mode 1 with Emergency Diesel Generator (EDG) #1 inoperable due to increased levels of particulates in the EDG Fuel Oil Storage Tank and supply piping. EDG #2 was determined to be operable with compensatory measures in place, including maintaining the two diesel fuel oil storage tanks tied together. With the crosstie valves open and the storage tank levels equalized, evaluation has shown that flow rates between the #2 EDG Fuel Oil Storage Tanks is low enough during EDG #2 operation to preclude excessive contamination of the EDG #2 Fuel Oil Storage Tank. "At 13:03 hours CST one of the two valves that cross-tie the two Emergency Diesel Generator Fuel Oil Storage Tanks together was found in the closed position, which was in conflict with the Operability Evaluation such that EDG #2 was determined to be inoperable. The valve was opened immediately and EDG #2 was declared operable. The cause of the event is under investigation. The NRC Resident Inspector has been notified of this event." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-03-28
40617 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-03-28 10:26 | 2004-03-28 15:00 | 2004-03-28 | BOTH TRAINS OF HIGH PRESSURE SAFETY INJECTION INOPERABLE FOR 25 MINUTES "At approximately 1343 hours on March 27, 2004, during a routine hand - rotation check of the "C" high pressure safety injection pump (HPSI), it was discovered the pump shaft was exhibiting some binding. At the time, the "C" HPSI pump was in service as the "B" Train HPSI pump. The "C" HPSI pump was declared inoperable and Condition A of LCO 3.5.2 was entered. This LCO condition requires restoration of the inoperable safety injection train within 72 hours. At that time, the "B" HPSI pump was in service as the Train "A" HPSI pump. The "A" HPSI pump was out of service due to a previously discovered condition of minor leakage observed near two of the casing bolts. The H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, HPSI system has three safety injection pumps. The "A" HPSI pump is the normal Train "A" pump, the "C" pump is the normal Train "B" pump, and the "B" pump is capable of serving as either the Train "A" or the Train "B" pump in the place of the "A" or "C" HPSI pump. At the time of discovery of the binding in the "C" HPSI pump, the "B" HPSI pump was in service as the Train "A" HPSI pump. It was determined that the "A" pump could be restored to operable status and placed back in service to restore two Trains of HPSI. In order to do so, the "B" HPSI pump was removed from service as the Train "A" pump and placed in service as the Train "B" pump. Therefore, at 1026 hours on March 28, 2004, for approximately 25 minutes, during the process of placing the "B" HPSI pump in service on Train "B," which was necessary to allow the "A" HPSI pump to be returned to service, there was no HPSI pump automatically available to provide HPSI to the Reactor Coolant System, if an accident were to occur. Therefore, this condition is reportable in accordance with 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function of systems needed to mitigate the consequences of an accident. An additional 8-hour reporting criterion associated with the plant being in an unanalyzed condition that significantly degrades plant safety 10 CFR 50.72(b)(3)(ii) has also been identified due to the inoperability of the HPSI system. It was known prior to the switching the "B" HPSI pump to Train "B" that this would cause inoperability of both trains of HPSI. It was also known that LCO 3.0.3 would be entered due to this circumstance. This situation was not avoidable, based on the sequence of events. The time in this condition was minimized, the operators were fully aware of plant conditions, and no other system inoperabilities were known of that would have complicated the situation. Both trains of HPSI are operable, although the "C" HPSI pump remains inoperable and out-of-service, pending investigation and repair." The licensee notified the NRC Resident Inspector | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-03-28
40616 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-28 06:37 | 2004-03-28 08:25 | 2004-03-28 | OFFSITE NOTIFICATION DUE TO THREE CAR ACCIDENT "On 3/28/04 at 0637, Plant Security was notified of a three car accident at the entrance to the site involving 1) an employee leaving the site, 2) a south bound vehicle on US Route 11, and 3) an employee entering the site. There were no reported injuries. Local law enforcement (LLEA) was contacted and investigated the incident. Because of the involvement of a LLEA and potential media or general public interest in the event, the Pennsylvania Emergency Management Agency (PEMA) was notified of the incident at 0812 hours. "Based on the notification to a government agency and possible public interest, this event was determined to be reportable under 10CFR50.72(b)(2)(xi)." The Licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-28
40615 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-03-27 22:05 | 2004-03-28 00:30 | 2004-03-28 | MANUAL REACTOR TRIP DUE TO LOSS OF FEEDWATER PUMP SPEED CONTROL "On 3/27/2004, the Unit 1 Reactor was manually tripped when the 1B Main Feedwater Pump speed could not be controlled in automatic or manual. An unexpected increase in Main Feedwater Pump speed was observed which increased the Main Feedwater header pressure to higher than expected values. An attempt was made to manually control the speed of the 1B Main Feedwater Pump from the various controllers in the Main Control Room. Preparations to start the 1A Main Feedwater Pump were initiated. The speed of the 1B Main Feedwater Pump continued to increase to a point where level control of the Steam Generators and overspeed of the 1B Main Feedwater Pump became a concern. At this point the Reactor was manually tripped and the 1B Main Feedwater Pump was tripped. An Auxiliary Feedwater System automatic actuation occurred on the trip a the 1B Main Feedwater Pump as expected because the 1A Main Feedwater Pump was also tripped at the time due to being at a low power level. All systems responded as expected on the Reactor Trip. The plant is currently stable in Mode 3. An Event Review Team will be performing a review of the event and making recommendations related to restarting the Reactor." All control rods fully inserted. Decay heat is being removed using the steam dumps and auxiliary feedwater. Plant pressure is 2235 psig and temperature is 557 degrees F. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 35 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-28
40614 | 0 | CONNECTICUT DEPT. OF RAD. PROT. |  |  |  |  | 2004-03-27 20:00 | 2004-03-27 21:22 | 2004-05-07 | STATE OF CONNECTICUT REPORTED THE DISCOVERY OF A STRONTIUM-90 SOURCE The item was found adjacent to a house in a wooded area in East Lyme, CT. It was a cylinder measuring 6 inches in length and 2 inches in diameter. The bottom of the cylinder had the following serial number: M2477. It was a general licensed strontium-90 source. The source was contained inside a metal box with a radioactive material symbol on the outside. The State response personnel conducted a radiological survey. The source read 250 millirem per hour on contact for gamma. The source read 3.2 rem per hour on contact for beta. At 12 inches, the source measured 5 millirem per hour. At one meter the source measured less than 1 millirem per hour. The State took the source to a secure locked location for followup on Monday to try to determine the owner. * * * UPDATE 0900 ON 3/29/04 MOSS (NMSS) TO GOTT * * * The item was identified as a component to a helicopter In-flight Blade Inspection System. Notified Mark Evetts at the Homeland Security Operations Center. * * * UPDATE 1120 ON 05/07/04 USNA Capt. Dave Farrand TO John MacKinnon * * * U.S. NRC, Region I (Mr. Jim Schmidt) informed the U. S. Navy (NAVSEADET RASO) on March 31, 2004 that an IBIS device (serial number 2397) containing 500 microCi of Sr-90 was found on private property in East Lyme, Connecticut, on March 28, 2004. The NRC also informed the Navy that the IBIS device was confiscated by the State of Connecticut, and placed in safe and secure storage. Early results of NRC inquiries pointed to the U.S. Navy as the probable owner of the IBIS device. A preliminary investigation by the Navy has found that the these devices are routinely returned to the manufacturer (General Nucleonics) for refurbishing, where they may be resold, through the Defense Logistic Agency to the Navy, the Marine Corp, the Army, or the Coast Guard. The Navy's preliminary investigation also found that these devices are also used on some commercial aircraft. The Navy's preliminary investigation verified that the Navy possessed the device until at least 1989, but found no conclusive data or documentation to show that the device was returned to the manufacturer after that time. Therefore, the Navy has accepted responsibility for the device. The Navy's preliminary investigation was unable to determine how the IBIS device came to be located on private property. The Navy has contacted the State of Connecticut, and has initiated actions to retrieve the device for proper disposal or facilitate its return to the manufacturer. The Navy will follow-up with a 30 day report as required by 10 CFR 20.2201. United States Navy General Radioactive Material license number is 45-23645-01NA. R1DO (Della Greca) & NMSS (Roberto Torres) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | MAT | [5 empty] | 0 | 2004-03-27
40613 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-03-26 22:00 | 2004-03-27 19:00 | 2004-03-27 | STATE LICENSEE, GLOBAL GEO ENGINEERING, REPORTED A TROXLER GAUGE WAS STOLEN FROM A TECHNICIAN'S TRUCK. A Troxler moisture/density gauge, Model 3430, with nominal activity of 10 mCi Cs-137 and 30 mCi Am-241, was stolen from the back of a flat bed truck sometime after 10:00 pm on 3/26/04, and before 5:00 am 3/27/04. The truck was parked at the technician's residence in West Covina. The technician involved worked late last night, and took the gauge home and left it chained to the flat bed truck overnight. The licensee contacted the West Covina PD. The licensee will be offering a $500 reward for the return of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-03-31
40612 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-03-26 22:30 | 2004-03-27 02:08 | 2004-03-27 | UNANALYZED CONDITION REGARDING HHSI FLUSH LINE ISOLATION VALVE LEAKAGE - While performing a High Head Safety Injection (HHSI) Train-B inservice test, a Plant Operator noted leakage coming through HHSI Flush Line Isolation Valve #SI-0120B. This valve is located on a flush line coming from the discharge of the HHSI pump and directs water to the Safety Injection Pump room sump located within the Fuel Handling Building. The operator investigated and determined that the leakage was due to the valve not being fully seated. The Licensee has come to the conclusion that the estimated leakage through the valve exceeded the allowable value to remain in compliance with 10 CFR 50, Appendix A, GDC 19 limits for Control Room Envelope during the post LOCA Containment recirc phase of a large break LOCA. This condition resulted in an unanalyzed condition that significantly degraded plant safety requiring a notification to the NRC within eight hours per 10 CFR 50.72 (b) (3) ii. Subsequently, flush line valve #SI-0120B has been fully seated, and the leakage stopped. The licensee considers this valve to be operable. The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-03-27
40611 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2004-03-25 08:45 | 2004-03-26 14:53 | 2004-03-26 | AGREEMENT STATE REPORT INVOLVING A MISADMINSTRATION DURING EYE TREATMENT "Event description: A pterygium patient was scheduled to receive a 42.5 second treatment utilizing a 100 millicurie Srontium-90 sealed source manufactured by 3M Company, model number 6D1A. The dosimetrist programmed the manual timer for 4 minutes and 25 seconds. During the treatment, the physician questioned the treatment time and it was terminated after 2 minutes and 30 seconds. The prescribed dose was 20 Gy. The patient received 70.59 Gy. The patient and the physician were notified of the misadministration. The licensee notified the Division the same day of the event. The licensee will submit a written report within 15 days. This incident is reportable under 1200-2-5-.32 (79) (e) (4) of 'State Regulations for Protection Against Radiation.'" TN Event Report ID No.: TN-04-035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2004-03-31
40610 | 0 | FAIRBANKS MORSE ENGINE |  |  |  |  | 2004-03-25 | 2004-03-25 17:56 | 2004-03-25 | PART 21 NOTIFICATION INVOLVING POTENTIAL SAFETY HAZARD FOR BLOWERS ON OP ENGINES "Subject:Roots Blower on OP Engines "On March 23, 2004, Fairbanks Morse Engine evaluation determined a potential safety hazard exists for blowers (P/N 16609294) on OP engines. It is possible that the aluminum rotors can slip on the steel shaft and cause rotor-to-rotor or rotor-to-housing contact which could cause blower failure and inability of engine to perform its safety function. "The defect was caused by improper cleaning of the shaft prior to casting the rotor onto the shaft. This causes an inadequate bond and allows the aluminum rotor to move axially on the steel shaft. Sample testing of rotors has found this condition to exist to varying degrees on approximately 75% of rotors produced between 1998 and 2003. "(4) blowers were shipped to nuclear utilities that may be affected: "Utility Site Blower S/N "Exelon Limerick (RB813A, RB3871, RB816) "Entergy ANO-2 (RB814) "To date, no engine failures have been experienced as a result of this problem. However, the potential exists. All slipped rotors have been found during routine maintenance inspections. This condition has been found to manifest itself within a low number of hours of operation. Therefore, the longer the rotors run and maintain proper clearance, the less likely they are to be affected by this condition. "The affected utilities will be notified to evaluate inspection results and replace as necessary." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2004-03-25
40609 | 0 | THERMO ELECTRON CORPORATION |  |  |  |  | 2004-03-24 | 2004-03-24 19:45 | 2004-03-24 | THERMO WESTRONICS MODEL 3000C AND 3200C SERIES CHART RECORDER FAILURES It has been determined that Thermo Electron Corporation's Thermo Westronics model 3000C and 3200C chart recorders have had problems with overheating and are a possible fire hazard. These units have been supplied to Fermi and Indian Point. The manufacturer has made arrangements with the customers to provide replacements for the faulty circuit board assemblies upon customer request. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | TX | OTH | PAR | 21.21 |  |  |  | 0 | 2004-03-24
40608 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2004-03-24 03:31 | 2004-03-24 04:39 | 2004-03-24 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At approximately 0331 EST the reactor tripped due to reactor protection system actuation. The Emergency Feedwater System actuated. "It appears that a main feedwater perturbation [sensed low feedwater flow] occurred which actuated a main turbine trip. The main turbine trip actuated the reactor protection system which tripped the reactor." The reactor shutdown and all control rods fully inserted. Decay heat is being removed using the turbine bypass valves and emergency feedwater. The Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-24
40607 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-03-23 14:32 | 2004-03-23 16:49 | 2004-03-23 | OFFSITE NOTIFICATIONS MADE DUE TO AN ETHYLENE GLYCOL SPILL FROM UNDERGROUND PIPING Environmental state notification was made on 3/23/04 due to an ethylene glycol spill from the underground circulating water (CW) boiler piping. The spill is isolated and contained on site. Clean-up is in progress, and no discharge to the river occurred. Approximately 100 gallons of ethylene glycol has been cleaned up. The CW system is not effected by this spill. There were no injuries as a result of the spill. The NRC Resident Inspector will be notified. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-23
40606 | -1 | US ARMY |  |  |  |  | 2004-03-23 12:15 | 2004-03-23 15:15 | 2004-03-26 | THE US ARMY REPORTED A MISSING BEAM SPLITTER FOR A M1A1 TANK. On 03/03/04 the Texas National Guard discovered that one of their M1A1 tanks which was stored in a outside fenced area at their Army training facility in Wylie, Texas was missing a tritium beam splitter from its muzzle reference sensor. A thorough search was made of the entire area with negative results and a wipe of the tank also tested negative. The beam splitter contained a sealed 10 curie tritium source. All of the other tanks stored in the same fenced area with the one having the missing source were inspected and found to be intact. * * * RETRACTION AT 1030 ON 2/26/04 GIZICKI TO RIPLEY * * * Following reinspection, it was determined that the tritium beam splitter was not missing from the muzzle reference sensor. The individual who conducted the initial inspection could not see the illumination in the day light. When it was reinspected in a dark area, appropriate illumination was noted. Therefore the source was still in the beam splitter. Notified NMSS (Psyk), R3DO (Madera) and R4DO (Graves). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-03-23
40605 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-03-23 07:46 | 2004-03-23 11:00 | 2004-04-29 | INDICATION OF CRACK FAILURE ON RCS PRESSURE BOUNDARY PENETRATION "Unit 1 is currently in a refueling outage in Mode 5. During a routine inservice inspection of the reactor vessel, an indication was discovered on the N1B penetration. This is associated with the suction for B Loop of Reactor Recirculation. At 0746 on 3/23/2004, the Control Room was notified that the evaluation was completed and the indication was determined to be unacceptable under the ASME Section XI Code. Based on guidance provided in NUREG-1022, Rev. 2, this material defect in the primary coolant boundary constitutes a seriously degraded condition and is reportable under 10CFR50.72(b)(3)(ii)(A). A final evaluation of the flaw and a repair plan is being developed." The licensee informed the NRC Resident Inspector. *****RETRACTED ON 4/29/04 AT1018 FROM HUFFORD TO LAURA***** "On March 23, 2004, PPL Susquehanna, LLC reported a material defect discovered on the N1B penetration associated with the suction for the B Loop of Reactor Recirculation. The defect was discovered during routine inservice inspection of the reactor vessel. At the time of the report, the indication was believed to exceed the acceptability standards of ASME Section XI, IWB-3640. Accordingly, an ENS call was made pursuant to the reporting requirements of 10CFR50.72(b)(3)(ii)(A). Engineering analysis subsequently determined that the dimensional characteristics of the flaw were within the acceptability requirements of ASME Section Xl. This analysis conclusion provides the basis for retraction of the ENS report of March 23. "Although hypothetical flaw growth calculations demonstrated that the flaw size would remain within the allowable envelope of ASME Section Xl, IWB-3641-1 over the next operating cycle, and continued operation without repair of the observed flaw was justified, PPL Susquehanna, LLC performed a weld repair of the defect during the recently completed refueling outage." Notified the R1DO (R. Barkley) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-03-23
40604 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-03-22 19:31 | 2004-03-22 23:00 | 2004-03-22 | REACTOR SCRAM FROM 93% POWER DUE TO GENERATOR TRIP "The plant had a reactor SCRAM, cause is under investigation with initial indications of a Main Generator over voltage alarm and Generator lockout #2 were indicated on the Generator first hit panel. All plant systems responded as expected to the generator trip and Reactor SCRAM. All rods fully inserted and no ECCS actuations or relief valves lifted. The plant is stable in Mode 3 with the recovery plan being implemented." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-03-22
40603 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2003-11-26 | 2004-03-22 13:22 | 2004-03-22 | THE COLORADO STATE UNIVERSITY RADIATION CONTROL OFFICE (RCO) DISCOVERED A MALFUNCTION OF THE ALARM SYSTEMS IN THE MOLECULAR AND RADIOLOGICAL BIOSCIENCE BLD. ON THE UNIVERSITY'S MAIN CAMPUS. "On 26 November 2003, the fire alarm computer system for the University crashed. This system also carried the MRB Irradiator alarms. The Radiation Control Office was informed of this malfunction on 28 November 2003, whereby RCO Staff checked the irradiators for users and found no one scheduled for operations of either machine. The system was restored to campus the following week and it was assumed that the alarm system was back on-line. All pre-use checks of the irradiators found no problems with the daily operation of either irradiator after the incident. However, the annual inspection whereby the alarm system is checked with CSUPD revealed the problem last week. The malfunction of the alarm system was reported to the Radiation Safety Officer on 3 February 2004 after an annual inspection found the local alarms and interlocks working to the irradiator (automatic source retraction, audible and visual alarms), but not reporting an intrusion to the University Police Department. The alarms in question satisfy the requirements of CDPHE Regulation 19.8.2. The Radiation Safety Officer requested to the Principal User that all work with each irradiator be stopped until the alarms could be repaired. The Principal User complied, with the request on 3 February 2004. Reporting this incident to the CDPHE is pursuant to Regulation 19.29.15 for "inoperability of an access control system." The system is being worked on by University Facilities Management and is planned to be operational by 6 February 2004. The system will be tested fully before operations are permitted to resume." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-03-25
40602 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-21 12:32 | 2004-03-21 16:03 | 2004-03-21 | THREE INJURIED NONCONTAMINATED CONTRACTORS WERE TRANSPORTED TO THE HOSPITAL. "On 3/21/04 at 12:32 hrs a bucket truck working at the Unit 1 Cooling Tower came in contact with a 230KV transmission line causing the loss of one off site power supply to the plant. The 500 KV offsite circuit remained energized during the event. A contract employee at the base of the truck was thrown due to the electrical short. A contract employee in the bucket of the truck was able to lower the bucket to the ground. A first aid crew was dispatched to the location and an Ambulance was requested. The Ambulance entered the site at 12:50 and at 13:02 the individuals were transported to the local hospital. Due to the electrical transient in the plant, a contract employee performing grinding activities lost control of the grinder and injured his middle finger. This individual received first aid and was transported to the local hospital by his supervisor. The individual injured in the plant was surveyed by Health Physics prior to leaving the site and no contamination was found. The Local Law Enforcement Agency was notified of the Emergency vehicle being dispatched to the site. The State Emergency Operations Center will be notified of the Emergency vehicle entering the site." The NRC Resident Inspector and local agencies were notified and the state will be notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2004-03-21
40601 | 0 | CALVERT CLIFFS | 1 |  |  | [1] CE,[2] CE | 2004-03-20 13:40 | 2004-03-20 15:25 | 2004-03-20 | AUTOMATIC REACTOR TRIP AT CALVERT CLIFFS UNIT 1 DUE TO A LOSS OF FEEDWATER "At 1340 on 3/20/2004, Calvert Cliffs Unit 1 Reactor automatically shutdown due to low Steam Generator Water Level. The low water level was caused by a loss of at least one Steam Generator Feed Pump. The loss was initially caused by a short or ground from Chart Recorder maintenance in Panel 1C29. 1C29 is a control panel in the control room. The chart recorder was a 500KV Bus Voltage Monitor. "The post trip primary indications responded normally. The auto steam dump operation responded normally until the quick open signal was cleared at which time the Turbine Bypass Valves failed shut. It is unclear at this time why they failed shut. Steam dump continues through the use of the Atmospheric dump valves and feedwater is supplied via the Auxiliary Feedwater System with the use of 11 (Steam Driven Pump) & 13 AFW Pump (electric driven pump). Lowest Steam Generator Level was -210" in 11 S/G and -115" in 12 S/G level. "Current Conditions are RCS pressure is 2250 PSIA and temperature is 532°F." All control rods properly inserted into the reactor core. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-03-20
40600 | -1 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-03-19 14:08 | 2004-03-19 21:00 | 2004-04-14 | HPCI SYSTEM DECLARED INOPERABLE AT LIMERICK 1 DUE TO A BROKEN HAND SWITCH "On 3/19/04 at 14:08 PM EST, the Unit-1. HPCI system was declared inoperable due to a hand-switch failure, which prevented main control room operation of the HV-055-1F0O1 HPCI steam admission valve. The system had just successfully completed its functional surveillance test and the switch broke resulting in the operators using an, alternate means to shutdown the HPCI system. The steam admission valve is not a PCIV. The valve was open all the time; the system was shutdown using an alternate procedure. The system is now blocked for hand-switch replacement. This report is being made pursuant to 10CFR50.72(b)(3)(v) for failure of a single train accident mitigation system." The NRC Resident inspector was notified. Operators entered the unit into a 14 day LCO for declaring HPCI system inoperable. *****RETRACTED ON 4/14/04 AT 12:56 FROM GAMBLE TO LAURA***** "This is a retraction of the event notification made on 3/19/04 at 21:00 hours. This event (#40600) was initially reported as a safety system functional failure under the requirement of 10CFR50.72(b)(3)(v)(D). Unit 1 High Pressure Coolant Injection (HPCI) system was declared inoperable due to a handswitch failure that prevented operation of the HV-055-1F001 HPCI steam admission valve from the main control room. The handswitch failed while attempting to close the steam admission valve during system shutdown at the conclusion of surveillance testing. The operator then closed the outboard steam line isolation valve to complete the system shutdown. "HPCI is automatically initiated by low reactor level or high drywell pressure signals. Manual HPCI initiation for inventory makeup is performed by depressing the initiation pushbutton. Both automatic initiation and manual initiation using the pushbutton open the steam admission valve. The failed handswitch did not adversely affect the initiation of the HPCI system in the inventory makeup mode. The manual startup of the system in the test mode of operation is unavailable when the handswitch is failed. The test mode can be used to remove decay heat following an isolation of the main steam lines but it is not a credited safety function. "The steam admission valve handswitch would not be used to shutdown the system when an automatic initiation signal is present; the outboard steam line isolation valve would be closed to secure the system. This is the method that was used to secure the system during the surveillance test. The handswitch is mainly used to startup and secure the system during surveillance testing. The system was removed from service as part of a planned evolution to conduct surveillance testing in accordance with an approved procedure and the plant's Technical Specifications. The system was secured for the purpose of concluding the surveillance test and replacing the handswitch. The failed handswitch did not adversely affect the systems capability of performing its safety function. A condition did not exist at the time of discovery that could have prevented the fulfillment of the HPCI safety function." Notified R1DO (B. MCDERMOTT). | 15 | 0 | 0 | 15 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-03-19
40599 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-03-19 09:10 | 2004-03-19 17:45 | 2004-03-19 | SAFETY SYSTEM ACTUATION AT PORTSMOUTH GDP "On 03/19/04 at 0910 hours, Autoclave #5 in the X-343 Facility experienced a Steam Shutdown due to high condensate level alarms (A) and (B) actuating. The autoclave was in an applicable TSR mode (Mode II, Heating) at the time of the alarm actuations. The autoclave was placed in Mode VII (Shutdown) and declared INOPERABLE by the Plant Shift Superintendent (PSS). An investigation is underway to determine the cause of the actuations. No release of radioactive material occurred as a result of this incident. This event is being reported in accordance with UE2-RA-RE1030, Appendix D. J. 2. Safety System Actuations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 2 | OH | FUE | [5 empty] | 0 | 2004-03-19
40598 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2004-02-22 10:16 | 2004-03-19 16:17 | 2004-03-19 | PARTIAL RPS ACTUATION DURING TESTING AT PERRY "This report is being made in accordance with 10CFR50.73 (a)(1), which states, in part, "in the case of an, invalid actuation reported under 10 CFR50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER." These invalid actuations are being reported under 10CFR50.73(a)(2)(iv)(A). "On February 22, 2004, at 1016 hours, while operating at 100 percent power, the reactor protection system manual scram channel functional test was performed. When a division 1 manual scram pushbutton was depressed, in addition to the expected half scram, the reactor protection system (RPS) A motor-generator electrical protection assembly circuit breakers tripped open. Loss of power from the RPS A motor-generator caused the loss of electrical power to the RPS instrumentation. This resulted in the invalid actuation of the logic that is powered by RPS A. The actuations resulted in isolation signals that closed one or more valves in each of the following division 1 subsystems: main steam line drains, containment and drywell radiation monitors, reactor water cleanup, fuel pool cooling, suppression pool cleanup, containment and drywell radwaste sumps and containment chilled water. All systems and components responded as designed for the signals that resulted from the loss of RPS A buss. This is considered a partial actuation since only division 1 components were effected. Following restoration of power to the RIPS A buss, the actuation logic was reset, and the equipment/systems were returned to the status required by plant conditions. "Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in condition report 04-00901. The resident inspector has been notified." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-03-19
40597 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-03-18 10:42 | 2004-03-18 15:51 | 2004-03-18 | CONTRACTOR SUPERVISOR TESTED POSITIVE FOR A CONTROLLED SUBSTANCE "At 1042 CST Fitness for Duty (FFD) test results indicated a contractor supervisor had a positive test result for a controlled substance. It was determined the individual was not on site. The Medical Review Officer (MRO) contacted the individual by telephone and determined the result was a confirmed positive test. Unescorted access was removed effective 1128 CST." The licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 26.73 |  |  |  | 0 | 2004-03-18
40596 | -1 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2004-03-17 14:57 | 2004-03-17 21:25 | 2004-05-11 | SWITCHGEAR ROOMS FLOODING ANALYSIS CONCERNS "At 1457 on 3-17-2004, Wolf Creek Generating Station Fire Protection Engineering submitted information to the Control Room that there was a flooding analysis concern in the Engineered Safety Features Switchgear (NB) Rooms regarding the 2 ½ inch fire protection header that is located in the rooms. The capability of the floor drain system in the room is indeterminate in regards to draining all the water that could be expected to accumulate in the rooms if the fire main were to rupture during a seismic event. "Compensatory actions have been put in place in the form of additional fire suppression equipment and administrative isolation of the fire protection header that is located in the NB switchgear rooms. Investigation continues into the assumptions used in the flooding and seismic analysis. The Senior Resident Inspector has been notified. " * * * RETRACTION ON 05/11/04 AT 1555 EDT FROM C. SIBLEY TO A. COSTA * * * "On March 17, 2004, at 2125 EST, Wolf Creek Nuclear Operating Corporation (WCNOC) made an event notification regarding a flooding analysis concern related to a 2 1/2 Inch fire protection header located in the Engineered Safety Features Switchgear (NB) Rooms (EN40596). This notification identified that the analysis with regards to draining all the water from the room in the event that the fire protection header pipe were to rupture during a seismic event was indeterminate. "Subsequent evaluation has determined that the fire protection header piping located in the subject NB switchgear rooms is built to seismic Il/I requirements, and is therefore not subject to a pipe rupture in the event of a seismic event. Therefore, WCNOC is retracting the March 17, 2004 event notification. "The NRC Senior Resident Inspector has been notified." Notified R4DO (L. Smith). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2004-03-17
40595 | 0 | DRAXIMAGE, INC |  |  |  |  | 2004-03-17 | 2004-03-17 16:00 | 2004-03-17 | At 1600 EST on 03/17/04, Edward Bump, Radiation Safety Officer, Draximage, Inc, a radiopharmaceutical manufacturer, Kirkland, Quebec, Canada reported that on 02/18/04, Draximage shipped a Type A box (Transport Index 1.1 on 02/18/04) containing a Sodium Iodide I-131 solution by FedEx Air from Montreal Mirabel Airport to Cardinal Health Nuclear Pharmacy Services, Miami Lakes, FL. Cardinal Health (FL RAM License #3453-9); Manager, Health Physics is Kory Kodimer. The activity of the solution on 02/18/04 was 769 millicuries and on 03/17/04, the activity should be approximately 63 millicuries. On 02/19/04, the shipment arrived by FedEx Air at the FedEx Hub in Memphis, TN and cleared customs. However, the shipment has not reached its destination. Since 02/19/04, FedEx has conducted a thorough search of its holding facilities. The FedEx tracking number is 635162720540. Roy Parker is the FedEx Radiation Physicist. There is no known nor likely exposure to individuals. FedEx contacted all other Cardinal Health facilities in the United States and have not located the package. The package most probably remains in a storage facility associated with its transport. Representatives from FedEx, Draximage, and Cardinal Health concluded that this situation is extremely unlikely to be a security related event. Mr Bump plans to submit a written report to NRC Region I within 30 days of the determination that the medical product package was missing. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-03-17
40594 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-03-16 | 2004-03-17 16:37 | 2004-03-17 | AGREEMENT STATE REPORT - MISSING SR-90 EYE APPLICATOR SOURCE "Licensee reported to Radiologic Health Branch-Granada Hills (RHB-GH) that it had discovered one of its Sr-90 eye applicator sources (Model Manning #357, SIN pending) missing yesterday [03/16/04] from its sealed source storage C-container where it had been stored for the last ten years. The actual eye applicator was kept in its own box provided by the manufacturer. The discovery was made when the RSO was conducting a routine check for leak test/inventory purposes. This source was reportedly last accounted for about July 2003. The original assay date for the source was 8/22/79 at 31.7 millicuries (Reported to be about 17 millicuries now). "The source was stored in a locked and alarmed C-container used exclusively for radioactive material storage. A fence around it is also locked. There was no sign of a break-in. However, the licensee reported that in May 2002 there was a break-in to this storage container. The same source was at that time removed from the C-container by the intruder apparently and was later found in an outside barrel so it was recovered. Incidentally, some uranyl nitrate (or acetate?) in microcurie quantities was stolen then, too. "The licensee will continue searching to determine the likely disposition of the missing source. RHB-GH suggested they notify their security people. The licensee will be providing a written report." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-03-22
40593 | 0 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2004-03-17 12:35 | 2004-03-17 15:19 | 2004-03-17 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "This report is being made pursuant to 10CFR50.72(b)(3)(v). This report documents the failure of the Peach Bottom Unit 3 High Pressure Coolant Injection (HPCI) System to develop speed and discharge pressure during the performance of a scheduled Surveillance Test. The test was aborted and the cause of the inability of the HPCI system to develop speed and discharge pressure is under investigation. Unit 3 has entered a 14-day LCO Required Action statement due to the HPCI inoperability. Unit 3 remains operating at 100% power. The Peach Bottom NRC Resident Inspector was notified." | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-03-17
40592 | -1 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2004-03-16 10:42 | 2004-03-16 17:02 | 2004-03-18 | CABLE SEPARATION CRITERIA NOT MET "At 1042 hours on March 16, 2003, Operations determined that a field condition did not meet cable separation criteria. This condition represented an unanalyzed condition potentially reportable under 10 CFR 50.72(b)(3)(ii)(B) since the event might represent a significant degradation of plant safety. The cable separation discrepancy, identified during a walk down, was a misplaced portion of non-safety cables from one safety channel into another safety channel. The non-safety cables are assorted low energy instrumentation cables (generally associated with fire protection and radiation monitoring or retired) and an ac power supply cable to a charcoal filter fan plenum drain line pump. The drain line pump power cable created the potential for a significant degradation of plant safety due to a potential for damage to cables of safety related components in the channels. The safety related cables in the two channels included power cables for two of three Component Cooling Water pumps, two Containment Spray pumps, and power cables to four motor control centers. "Immediate corrective action was taken at 1044 hours to de-energize the power cable to the drain line pump and subsequent action was taken, at about 1100 hours, to re-establish separation by moving the cables back to a single channel. Electrical feeds to all required safeguard loads were maintained at all times. An evaluation is being performed to further identify the cables in the two channels, and to evaluate the significance of the cable separation discrepancy. The extent of condition will be evaluated as part of the corrective action process." The licensee notified the NRC Resident Inspector. * * * UPDATE 1329 EST ON 3/18/04 FROM BRIAN ROKES TO S. SANDIN * * * The licensee is retracting this report based on the following: "Indian Point Unit 2 is withdrawing the 8-hour non-emergency notification made on March 16, 2004, at 1702 hours (EN Log No. 40592). The notification on March 16, reported an unanalyzed condition that might represent a significant degradation of plant safety, as a result of discovery of a plant condition that did not meet cable separation criteria, and therefore reportable under 10 CFR 50.72(b)(3)(ii)(B). A walk-down discovered several cables that traversed two cable channels containing cables for redundant safeguards equipment. All but one of the misplaced cables were low energy instrumentation cables. One of misplaced cables was a power cable for the charcoal filter fan plenum drain line pump. The power cable for the drain line pump created the potential for a significant degradation of plant safety due to a potential for damage to cables of safety related components in the two separate safety channels. Immediate corrective action was taken at 1044 hours, to de-energize the power cable to the drain line pump. At approximately 1100 hours re-establishment of separation was completed by moving the cables back to a single channel. "Subsequently, Engineering evaluated the condition and determined the power cable for the charcoal filter fan plenum drain line pump is designed and protected such that faults originating on this cable or its associated load will be quickly interrupted prior to the onset of damage so that safety related cables in its proximity and along its route will be protected from such damage. The method of protection involving double safety related fuses has been shown to provide the necessary enhanced electrical isolation consistent with the Indian Point Unit 2 design criteria. Therefore, engineering concluded the as-found condition did not represent a significant degradation of plant safety." The licensee informed the NRC Resident Inspector. Notified R1DO (Gray) and NRR (Reis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-03-16
40591 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2004-03-15 20:20 | 2004-03-15 20:57 | 2004-03-15 | AUTOMATIC REACTOR TRIP AT MILLSTONE 2 DUE TO SPURIOUS LOSS OF ONE MAIN FEED PUMP The licensee reported that an automatic reactor trip occurred on 3/15/04 at 2020 EST due to the spurious trip of one main feed pump which caused a low steam generator water level trip signal. The plant has two main feed pumps. Operators reset the tripped main feed pump but steam generator levels didn't recover in time. The lowest level observed was in the "B" steam generator at 15% level as compared to the normal level of 65%. The trip setpoint is at 50% level. All control rods properly inserted into the core. The auxiliary feed water system automatically initiated as designed and expected. The plant remains stable in mode 3 while the licensee commenced the post trip review to determine the cause of the main feed pump trip. Decay heat removal was established using the AFW system to feed steam generators and bleed steam to the main condenser through the condenser dump valves. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-15
40590 | 0 | TURKEY POINT | 3 |  |  | [3] W-3-LP,[4] W-3-LP | 2004-03-15 13:30 | 2004-03-15 18:40 | 2004-03-15 | CONTRACT SUPERVISOR FITNESS FOR DUTY At 1330 ET on 3/15/04, it was determined that a contract supervisor had tested positive for drugs on an access reinstatement urinalysis test. Access has been denied. The individual had only been badged for one day. A work review was conducted and no safety-related activities had been performed. Contact HOO for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2004-03-15
40589 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-03-15 15:18 | 2004-03-15 17:13 | 2004-03-15 | AUTOMATIC REACTOR TRIP DUE TO MAIN GENERATOR ELECTRICAL FAULT SIGNAL "At 1518 on 3/15/04, Unit 1 Reactor tripped due to a Main Turbine trip. The Main Turbine tripped due to a Main Generator electrical fault, Auxiliary Feedwater (AFW) started when both Main Feedwater Pumps tripped on Low Tave Feedwater isolation. The AFW start was expected on the Reactor Trip. All safety systems performed as required. Investigation is in progress to determine and correct the cause of this trip." All control rods fully inserted; the electrical grid is stable; ECCS systems remain operable; decay heat is being removed via AFW and steam dumps. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-15
40588 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-03-15 10:30 | 2004-03-15 14:13 | 2004-03-15 | SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO INOPERABLE ISOLATION INSTRUMENTATION "During the planned shutdown for RFO9, the Reactor Water Clean Up (RWCU) Differential Flow Signals and the Reject Flow indicator did not receive a signal from the transmitters associated with the reject flow path from the reactor to the condenser in the RWCU system. Maintenance was contacted and the differential flow timers associated with these control loops were removed per operating procedure N2-OP-37 for the RWCU system and the Technical Specification Required Action for both required channels of Functions 4a and 4b in table 3.3.6.1-1 being inoperable was entered. This was required to allow venting of the transmitters and prevented an inadvertent isolation signal of the RWCU system. "These primary containment isolation instruments were declared inoperable at 0830 on 3/15/2004. CONDITION B of LCO 3.3.6.1 was entered, which requires isolation capability to be restored in 1 hour. At 0930 on 3/15/04, CONDITIONS C and F were entered which require system isolation in one hour. "At 1025, maintenance was completed; however, all post maintenance testing was not complete. At 1030, on 3/15/04 CONDITION F was not met and CONDITION H was entered. CONDITION H requires the unit be in MODE 3 in 12 hours and in MODE 4 in 36 hours. "Since the unit was in a planned shutdown, with negative reactivity being inserted, it was unclear whether the entry into CONDITION H of Technical Specification 3.3.6.1 would have required actual insertion of negative reactivity for this situation. Thus, as a conservative action, NMPNS is reporting this event pursuant to 50.72(b)(2)(i) 'The initiation of any nuclear plant shutdown required by Technical Specifications.' "The Differential flow timers were installed at 1129 on 3/15/04 with the plant in MODE 2. Operating procedures require a CHANNEL FUNCTION TEST prior to a declaration of operability, The CHANNEL FUNCTIONAL TEST is in progress." The licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 3 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-03-15
40587 | 0 | FEDERAL BUREAU OF INVESTIGATION |  |  |  |  | 2001-11-03 11:30 | 2004-03-12 09:50 | 2004-03-12 | STOLEN RADIOACTIVE SOURCE FROM HAZMAT VEHICLE A Federal Bureau of Investigation (FBI) Hazmat Response Vehicle was parked at a Holiday Inn Select in Trivose, PA when it was broken into. Among the stolen material was a 10 millicurie Ni-63 source, Model 2428800-20, Serial No.881 manufactured by Enviro Tech Group. The licensee notified the theft to the Bensalem Police Department who filed a report and to the Philadelphia FBI Field office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-03-12
40586 | 0 | NEW MEXICO RAD CONTROL PROGRAM |  |  |  |  | 2004-03-11 20:00 | 2004-03-12 10:19 | 2004-03-12 | AGREEMENT STATE REPORT FROM STATE OF NEW MEXICO At approximately 2000 hrs MST on 3/11/04, the licensee, Baker-Hughes Oil Field Operations, was rigging a well with a well logging source (2.5 Ci of Cs-137) on a 90 foot tool string when the well started spewing natural gas. The location of the source is 4-6 feet below the rigging platform, which is approximately 15 feet tall, and around 8-10 feet above ground level. The area around the well was immediately evacuated. Currently, a contractor team from the Cudd company is preparing to enter the well area to cap off the well. The contractor, local law enforcement and local fire department are aware of the source. The State of New Mexico will update this report when the event has concluded. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NM | OTH | AGR |  |  |  |  | 0 | 2004-03-17
40585 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-03-11 14:30 | 2004-03-11 21:22 | 2004-03-11 | VOLUNTARY REPORT INVOLVING POTENTIAL TSC UNAVAILABILITY DURING A DBA LOCA "Monticello Nuclear Generating plant is making a voluntary report with regard to the Technical Support Center (TSC) not meeting design criteria Subsection 8.2-1.f of Supplement 1 to NUREG-0737. This specifies that the TSC will be provided with radiological protection necessary to assure that the radiation exposure to any person working in the TSC would not exceed 5 REM whole body (or its equivalent part of the body) for the duration of the accident. "During review of the calculations associated with an on-going Alternative Source Term project, plant staff identified the potential for a radiation shine path to exist from the reactor building to the TSC during a DBA [Design Basis Accident] - Loss of Coolant Accident [LOCA], that could result in radiation levels reaching a point dictating evacuation of the TSC under existing emergency plan procedures. "As required by NUREG-0696 and confirmed by the plant staff, existing procedural guidance directs personnel to evacuate to the back-up TSC (located in the EOF) if the TSC cannot be occupied continuously. "The NRC resident has been informed of this discovery." The licensee is continuing their assessment and will determine the appropriate corrective actions. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW | [5 empty] | 0 | 2004-03-11
40584 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-01-30 | 2004-03-11 14:41 | 2004-03-11 | RADIOGRAPHER MAY HAVE EXCEEDED ANNUAL EXPOSURE LIMIT "XRI reported that [a radiographer] received an annual exposure of 6.120 R for the year of 2003. [The Radiographer] had a dose of 4.016 R prior to December of 2003. [The Radiographer] received a dose of 2.104 R for December 2003. Once the badge results were discussed with [the Radiographer] in January of 2004, he stated that his badge had dropped near a source. [The Radiographer] did not feel that it needed to be reported at that time because of the distance from the source. According to the facilities files [the Radiographer] received 0.315 R for the month of December 2003. As a result of this incident there have been some additional steps taken to prevent reoccurrence. All radiographers have been retrained. Also if a radiographer receives a dose of 4.0 R by December, that radiographer will not be allowed to perform radiograph operations until the next calendar year. If that limit is reached prior to that date, the radiographer may be granted specified permission to work on monitored low production jobs." LA Report ID No.: LA040003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-03-16
40583 | 0 | CARDINAL HEALTH |  |  |  |  | 2004-03-10 07:00 | 2004-03-10 20:22 | 2004-03-10 | TRANSPORT ACCIDENT INVOLVING RADIOACTIVE SPILL OF RADIOPHARMACEUTICAL At approximately 0700 EST on 3/10/04, a courier vehicle dispatched from the Cardinal Health (formerly Syncor International) office in Glastonbury, CT overturned at Exit 43 eastbound on I-84 in West Hartford, CT. One of the pigs containing an unused Tc-99M syringe return was ejected from the vehicle. The syringe was crushed releasing an estimated 1-10 microcuries roadside. The local Fire Department responded closing the ramp for cleanup. The CT Department of Environmental Protection (DEP) was informed and arrived at the scene to take possession and isolate the syringe and pig. CT DEP notified the NRC Region I office (Duncan White, Tom Thompson) of the incident. The licensee has prepared a press release to address any concerns. The local media is carrying the news story on their public website, i.e., www.WTNH.com. The licensee notified the National Response Center (DOT), case #715670. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | CT | TRA | [5 empty] | 0 | 2004-03-10
40582 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2004-03-09 | 2004-03-10 18:32 | 2004-03-10 | AGREEMENT STATE REPORT - REMOVABLE CONTAMINATION ON RECEIVED PACKAGE "Loyola University of Chicago, a broadscope academic licensee, notified the agency that a package containing two vials of Phosphorous-32 was found to contain levels of removable P-32 contamination in excess of the regulatory limits. The package was received on Friday, March 5, 2004 and surveyed on Tuesday, March 9. 315,000 dpm/100 square centimeters was measured using a pancake probe. A swipe of an area on the exterior surface of the package was found to contain 26,000 dpm/100 square centimeters. This exceeds the maximum allowable level of 22,000 dpm/100 sq centimeters removable contamination. Further examination of the package revealed that contamination was also found on a plastic bag containing an inner container and the vials of liquid P-32 (1 vial contained 500 microcuries, the other 250 microcuries) and on the exterior surface of the inner plastic container. The contamination measured on the items on the interior of the package ranged from a maximum of 4,700 dpm to 120 dpm/ 100 sq centimeters. However, the interior of the inner container and the exterior surfaces of the vials were not contaminated. The consultant performed surveys of the area where the package was opened and no additional contamination was noted. The shipper was Perkin-Elmer, Boston, MA. The carrier was Airborne Express. "The licensee notified the shipper, Perkin Elmer, and Airborne Express. The Hazmat representative for Airborne Express, contacted the Agency and stated that Airborne Express is currently trying to perform radiation surveys of all ground vehicles and the two planes involved in transport of this package. The package was transferred via Airborne Ground transportation from the Perkin Elmer Boston, MA, facility and transferred to a plane at Boston's airport. It was then flown to the Airborne facility in Wilmington, Ohio. The package was later flown to Chicago O'Hare then transported via Airborne Express Ground vehicle to the Illinois licensee's facility. "The MA radiation control program also contacted the Illinois radiation control program and discussed this matter. The licensee's consultant is currently conducting additional surveys of the Illinois facility to see if any additional P-32 contamination can be found. The Agency will also perform independent surveys and an investigation to try to determine the source of contamination." Illinois report number IL040012. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2004-03-15
40581 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2004-03-09 14:00 | 2004-03-10 15:10 | 2004-03-10 | AGREEMENT STATE REPORT - DAMAGED MOISTURE DENSITY GAUGE A dump truck ran over a Campbell Pacific Nuclear moisture density gauge at 1400 EST on 3/9/10 in Friendly, MD. The gauge had a 10 millicuries Cs-137 and 40 millicuries Am-241:Be source, serial number AM7147. The sources were intact and were packaged and shipped back to the licensee, Independent Consultants and Engineers of Upper Marlboro, MD. There was no detected leakage. The Gauge serial number is MD-30907147. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2004-03-15
40580 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-03-10 08:35 | 2004-03-10 15:00 | 2004-03-10 | OFFSITE NOTIFICATION DUE TO A FATALITY ONSITE "This notification is being made to report an onsite fatality due to a personal medical condition. During the incident, plant First Responder personnel responded to a Control Room notification of a man down. First Responder personnel initiated CPR and used an Automated External Defibrillator (AED) and continued until the Hanford Fire Department ambulance paramedics responded. The individual was taken via ambulance to Kadlec Medical Center in Richland, Washington where the individual was pronounced dead at 0835 PST." The fatality occurred in the Protected Area (PA) and was not associated with any work inside a Radiologically Controlled Area (RCA). The licensee informed the NRC Resident Inspector and will inform both state/local agencies. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-10
40579 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2004-03-06 | 2004-03-09 14:06 | 2004-03-09 | AGREEMENT STATE REPORT OF A STOLEN RADIOGRAPHER'S DARKROOM. NO RADIOACTIVE MATERIAL INVOLVED An industrial radiographer's 14 ft tandem axle trailer (darkroom) was stolen from the parking lot behind the home office sometime between 3/6/04 and 3/9/04. The trailer is red with white lettering, "Titan Atlantic." Neither the radiography source nor camera was in the trailer at the time of the theft. The following materials were in the trailer: overpack with "Caution Radioactive Materials" and "Radioactive Yellow II" labels, "Caution Radioactive Materials", "Caution Radiation Area", and "Caution High Radiation Area" signs, and yellow and magenta ropes and barricades. The Raleigh NC police were notified on 3/9/04. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2004-03-12
40578 | -1 | US DEPT OF VETERANS AFFAIRS |  |  |  |  | 2004-03-08 | 2004-03-09 13:06 | 2004-04-01 | LOSS OF LICENSED MATERIAL The Department of Veterans Affairs reported the following via facsimile: "I am calling to report a loss of licensed material. The loss occurred at a medical broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. The permittee is VA Boston Healthcare System, Boston, Massachusetts. "The loss was reported to the permittee Radiation Safety Officer on March 8, 2004. "The basis for reporting the loss is under 10 CFR 20.2201(a)(i) in that a waste vendor reported that a drum from the permittee triggered a radiation detector at a landfill. The activity involved although unknown at this time could potentially be greater than the reporting limit. "Specifically, the vendor (New York Environmental Services) indicated that a survey meter reading on contact with the drum was 4.8 millirem per hour. The drum is being returned to the permittee for radionuclide evaluation. "The Department of Veterans Affairs will evaluate the circumstances related to the loss and submit a written report to NRC, Region III, within 30 days." * * * RETRACTION ON 3/31/04 AT 1406 EST FROM J. WISSING TO A. COSTA * * * The following retraction was faxed to the NRC Operations Center on 3/31/04. Categorization of this information as a retraction was reviewed and approved by K. O'Brien, NRC Region 3. "The licensed material was recovered and returned to the VA Boston Healthcare System for evaluation on March 11, 2004. The medical center RSO evaluated the drum contents for radionuclidic identity and activity. The National Health Physics Program (NHPP) performed an inspection at the Medical Center on March 18, 2004. The NHPP inspection included a review of the Medical Center RSO's analysis of the recovered. Licensed material. "Analysis of the recovered drum indicated a total activity of less than 100 [microcuries] of I-125, (less than 1000 times Appendix C, 10 CFR 20) reportable quantity specified by 10 CFR 20.2201(a)(i). Since the material was recovered and is in the possession of permittee, a 30-day report specified by 10 CFR 20.2201(a)(ii) is not required." Notified NMSS EO (C. Miller), R1DO (K. Jenison), | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-03-09
40577 | 0 | MAINE YANKEE | 1 |  |  | [1] CE | 2004-03-09 09:55 | 2004-03-09 11:32 | 2004-03-09 | OFFSITE NOTIFICATIONS TO STATE AGENCIES DUE TO LIQUID RELEASE The licensee notified the Maine Emergency Management Agency and the Maine Department of Human Services of an unscheduled liquid release of containing 1.35e-6 Curies that occurred on 3/8/04. This release resulted in a minor exposure of 9e-11millirem. Site has no resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | ME | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-09
40576 | -1 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2004-03-08 11:30 | 2004-03-08 17:04 | 2004-04-20 | HPCI SYSTEM INOPERABLE DUE TO FAILURE OF TORUS SUCTION VALVE TO FULLY OPEN "U2 HPCI was declared inoperable to fulfill its safety function to mitigate the consequences of an accident. "U2 HPCI torus suction valve MO-2-23-058 failed to fully open, during performance of ST-O-023-301-2 'HPCI Pump, Valve, Flow, and Unit Cooler Functional and In-Service Test.' The valve stopped in a mid-position. HPCI flow path from Condensate Storage Tank remains available for HPCI injection. Investigation into cause is continuing." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED AT 1509 ET ON 4/20/04 BY D. FOSS TO J. ROTTON * * * "The purpose of this notification is to retract a previous report made on 3/8/04 at 1130 hours (EN# 40576). Notification of the event to the NRC was initially made as a result of declaring the Unit 2 High Pressure Coolant Injection (HPCI) system inoperable when unexpected conditions were found during performance of routine surveillance testing of HPCI. Specifically, it was noted that a motor-operated Suppression Pool suction valve for HPCI (MO-58) did not complete its stroke in the open direction during testing. The HPCI system was not operating at the time of the discovery. "Since the initial report, Engineering has determined that HPCI was capable of performing its safety function. The evaluation has determined that the MO-58 valve was operable for continued operations. The MO-58 stopped in the mid-stroke position due to motor operator torque switch operation. During design events, the torque switch is bypassed and would not have interrupted valve operation. The torque switch is only in the valve logic for remote manual valve operations (e.g. testing). The torque switch was adjusted and HPCI was returned to service on 3/10/04 by approximately 1500 hours [ET]. "During adjustments to the HPCI MO-58 motor operator, the suction source from the Suppression Pool was isolated in accordance with Technical Specifications since MO-58 is considered as a Primary Containment Isolation Valve. This occurred on 3/8/04 by approximately 1340 hours. This action was performed in accordance with station procedures and is considered planned maintenance. Throughout the time period of repairs to the MO-58, HPCI was available for operations with its suction source from the normally aligned Condensate Storage Tank. "The NRC resident has been informed of the retraction." Notified R1 DO (D. Silk). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-03-08
40575 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-03-04 16:00 | 2004-03-08 10:15 | 2004-03-08 | THE CLEVELAND CLINIC FOUNDATION ADMINISTERED AN UNDERDOSE DURING A THERAPEUTIC TREATMENT During a therapeutic procedure using I-125 Gliasite from 2/28 - 3/1, the state licensee administered an under dose of 24%. The therapist calculated a dwell time of only 97 hours when the prescribed dwell time was 120 hrs for treating a brain tumor. This resulted in the patient receiving 5,300 rads instead of the prescribed 7,000 rads. Both the patient and the referring physician were notified. The licensee will make up for the under dosage by using a linear accelerator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2004-03-11
40574 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-07 02:01 | 2004-03-07 09:01 | 2004-03-07 | START OF THE "A" EMERGENCY DIESEL GENERATOR DURING EMERGENCY SERVICE SUPPLY BUS OUTAGE At 0201 on 03/07/2004, with Susquehanna Unit 1 in its 13th Refueling and Inspection Outage, the 'A' Emergency Diesel Generator auto started during preparations for a scheduled 1A ESS(Emergency Service Supply) Bus outage. While performing the procedure for removal of the ESS Bus from service, two incorrect fuses were removed. This caused the normal supply breaker to open on sensed undervoltage deenergizing the 1'A' ESS Bus. The alternate breaker also attempted to close as designed, but tripped open immediately due to the sensed undervoltage. With all breakers open, the 'A' Emergency Diesel Generator auto started and loaded onto the bus. All leads had previously been removed from the bus per the procedure. The 'A' Emergency Diesel Generator is operating as designed and is available to supply Unit 2 'A' ESS Bus if required. The auto start of a Emergency Diesel Generator is reportable as an event that results in the valid actuation of a system designed to mitigate the consequences of significant events per 10CFR50.72(b)(3)(iv)(A). The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-03-07
40573 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-03-06 22:10 | 2004-03-07 04:06 | 2004-03-08 | SPDS WILL BE DE-ENERGIZED FOR MORE THAN 8 HOURS DUE TO REFUELING OUTAGE ACTIVITIES "At 22:10 on March 6, 2004 the Unit 1 Safety Parameter Display System (SPDS) was deenergized during planned refuel outage activities. It has been determined that it will not be restored within the required eight hours. Currently, restoration is scheduled for March 7, 2004 at 17:00. All required instrumentation is available in the control room. Since the Unit 1 SPDS computer system will be unavailable for greater than 8 hours, this is considered a Loss of Emergency Assessment Capability and therefore reportable under 10CFR50,72(b)(3)(xiii). Unit 1 is currently in Mode 5 for the planned 13th Refuel and Inspection Outage." The licensee notified the NRC Resident Inspector **** Update at 2219 EST on 03/07/04 by Gordon Robinson taken by MacKinnon **** SPDS is still out of service and it will be restored to service by 0600 EST on 03/08/04. R1DO (M. Shanbaky) notified. NRC Resident has be notified of the update by the licensee. * * * UPDATE ON 03/09/04 @ 1122 BY GRANT FERNSLER TO C. GOULD* * * As of 1117 the SPDS was energized and restored to service. The NRC Resident Inspector was notified. Reg 1 RDO(Cobey) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-03-07
40572 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2004-03-06 21:47 | 2004-03-07 00:14 | 2004-03-07 | PLANT HAD A LOSS OF POWER TO THE STARTUP TRANSFORMER AND THE "B" TRAIN 4.16KV ESFAS BUS. On 03/06/2004 at 2147 CDT Wolf Creek Generating Station experienced a loss of the west bus in the switchyard causing a loss of power to the Startup Transformer and the "B" Train 4.16 KV ESFAS bus, NB02. The "B" Emergency Diesel Generator started and loaded, as expected, upon the loss of power from the Startup Transformer. All systems and equipment operated as expected for a loss of power to NB02. Reactor power was lowered by the control room staff following the expected start of the steam driven aux. feedwater pump to maintain reactor thermal power below license limits. The cause of the loss of power appears to be the failure of one of the 13.8 KV output bushings on the Startup Transformer. System Operations has dispatched a line crew to the Wolf Creek switchyard to investigate and initiate repair activities. System Operations has reported that all three (3) lines to Wolf Creek are energized and have proper voltage. The plant also entered a 72 hour LCO action statement due to the loss of the power source. The licensee notified the NRC Resident Inspector. *** Update on 03/07/04 at 1820 EST by Steve Gifford taken by MacKinnon **** Licensee will have a contractor perform Doble Testing of Startup Transformer windings and also determine if the bushing has been damaged. Testing results should be known by midnight CST. Repair time will depend on test results. R4DO (Greg Peck) notified. NRC Resident Inspector was notified of the update by the licensee. | 98 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-03-07
40571 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-06 05:28 | 2004-03-06 08:20 | 2004-03-06 | OFFSITE NOTIFICATION AT SUSQUEHANNA INVOLVING A TRAFFIC ACCIDENT "On 3/06/04 at 0528 Plant Security was notified of an accident at the entrance to the site involving an employee leaving work and a south bound vehicle on PA Route 11. There were no reported injuries. Local law enforcement was contacted and investigated the incident. Because of the involvement of a LLEA and potential media or general public interest in the event, the Pennsylvania Emergency Management Agency (PEMA) was notified of the incident at 0812 hours. Based on the notification to a government agency and possible public interest, this event was determined to be reportable under 10CFR50.72(b)(2)(xi)." The NRC Resident Inspector was notified. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-06
40570 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2004-03-06 00:50 | 2004-03-06 02:02 | 2004-03-06 | MANUAL REACTOR TRIP AT MILLSTONE 2 DUE TO SPURIOUS TRIP OF THE "B" FEED PUMP The licensee reported that the "B" Steam Generator Feed Pump tripped unexpectedly and would not reset causing lowering steam generator water levels. Operators manually tripped the reactor and all control rods properly inserted. The auxiliary feed water (AFW) system automatically initiated to restore steam generator water levels. The lowest steam generator water level observed during the event was 55% level as opposed to the normal level of 70%. No primary relief valves lifted. Operators established decay heat removal capability using AFW system and the atmospheric steam dump valves. The licensee initiated a post trip review to determine the cause of the feed pump trip. The NRC Resident inspector has been notified by the licensee. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-06
40569 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-11-01 | 2004-03-05 12:39 | 2004-03-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS Menard's Lumber reported that following demolition and replacement of their old store building, it was determined that all 13 Tritium exit signs were missing and apparently removed along with the old building debris. The signs were SafetyLite/EvenLite Model 101 (7 Curies Tritium as of the manufacture date of October 1991). An investigation did not determine the final disposition of the signs and the State is closing the report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2004-03-10
40568 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2004-02-29 | 2004-03-05 12:39 | 2004-03-05 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The City of Holdrege, NE reported that in late February 2004 during an annual inventory, it was discovered that 25 of 40 Tritium exit signs were missing. The signs were installed in stairways in the city auditorium. The signs are SafetyLite Model 2088 (2.2 Curies Tritium each as of the shipment date of March 1990). An investigation did not determine what happened to the signs and the State is closing the report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2004-03-10
40567 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2004-03-04 15:00 | 2004-03-05 12:08 | 2004-03-09 | 24-HOUR NOTIFICATION - BULLETIN 91-01 CRITICALITY CONTROL "A review of incinerator data indicated higher than expected accumulations and concentrations of uranium bearing material in the incinerator off-gas system. Criticality was not possible because the mass corresponding to each concentration was below the minimum critical mass. "Controlled Parameters: The safety basis for the incinerator off gas-system states that criticality is not credible. This was based on minimal expected carryover and low concentrations of uranium from the incinerator to the off -gas system. The uranium concentrations in the off-gas system were expected to be well below the [deleted] concentration criticality limit for an infinite mass. "A criticality would be possible in the off-gas system only if a minimum critical mass for a corresponding uranium concentration accumulated in a critical configuration with sufficient moderator. "Because higher than expected accumulation and concentration of uranium bearing material was detected in the incinerator off gas system, this 24-hour notification is being made. "Summary of Activity: 1) Incinerator was shut down; 2) The off-gas system is being inspected; 3) Samples from the off-gas system are being obtained for analysis. "Conclusions: 1). The bounding assumptions for concentration and carryover were exceeded; 2). At no time was there any risk to the health or safety of any employee or member of the public. No exposure to hazardous material was involved & 3). The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A formal causal analysis will be performed. The licensee will be notifying NRC Region III. * * * UPDATE AT 1346 EST ON 3/9/04 SNYDER TO GOTT * * * The licensee sent the following addendum via facsimile: "Reason for Addendum: Higher than expected concentration of uranium bearing material detected in the incinerator ash. The ash from the lower chamber of the incinerator is lifted via a bucket elevator and dumped into a mill feed hopper and then into a fitzmill. "As Found Condition: A review of incinerator data indicated higher than expected concentrations of uranium in the incinerator ash. "Controlled Parameters: The safety basis for the ash handling system (elevator and fitzmill) states that criticality is not credible based on the ash remaining below 21.6 weight percent uranium. "Summary of Activity: -In addition to the previous activities, the formal root cause team has initiated their investigation. -The incinerator ash elevator and fitzmill safety basis is being re-evaluated. "Conclusions: -The bounding assumption for concentration was exceeded. -At no time was there any risk to the health or safety of any employee or member of the public. -No exposure to hazardous material was involved. -The ash handling aspect will be incorporated into the formal causal analysis." Notified NMSS (Psyk) and R2DO (Ayres). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2004-03-05
40566 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-03-04 05:20 | 2004-03-04 10:51 | 2004-04-15 | RCIC STEAM SUPPLY FAILED LLRT "Appendix J Local Leak Rate Testing [LLRT] of the RCIC Steam Supply failed the Combined Main Steam Isolation Valves leakage limit of 300 scfh. The Combined MSIV leakage limit includes MSIV'S, MSL Drains, HPCI Steam Supply and RCIC Steam Supply. The volume between RCIC Steam Supply valves could not be pressurized therefore, the Minimum Pathway leakage limit is considered to be exceeded. "This is also considered a failure of the Primary Containment Air Leakage Minimum Pathway leakage limit of 1.0 La. "The identified degraded condition is reportable as a condition of the nuclear power plant, including its principle safety barriers being seriously degraded per 10CFR50.72(b)(3)(ii) requiring an 8-hr ENS notification." The RCIC Steam Supply line was tested successfully approximately two years ago during the last refueling outage. The licensee will inform the NRC Resident Inspector. ******RETRACTED ON 4/14/2004 AT 1610 EST FROM FRY TO HEISSERER***** "At the time the original 8-hour ENS notification was made, it was declared that the Appendix J Local Leak Rate Test of the RCIC Steam Supply had failed the combined Main Steam Isolation Valves Minimum Pathway leakage limit of 300 scfh. The combined MSIV leakage limit includes MSIVs, MSL Drains, HPCI Steam Supply and the RCIC Steam Supply. The volume between the inboard and outboard RCIC Steam Supply valves could not be pressurized, therefore the Minimum Pathway leakage limit was considered to be exceeded. "Subsequent to this event, during performance of an additional Local Leak Rate Test of the RCIC Steam Supply Penetration, it was demonstrated that the as-found Appendix J and combined MSIV Minimum Pathway leakage and the Primary Containment Air Leakage Minimum Pathway of 1.0 La were not exceeded as previously reported. "The original Local Leak Rate Test was performed between the combination of two parallel inboard valves and the outboard valve. The subsequent test determined that the outboard isolation valve did not exceed Minimum Pathway criteria. The majority of the leakage was from the smaller inboard RCIC warm-up line isolation valve of the three RCIC Steam Supply valves. The post-maintenance test of the penetration measured leakage that was within acceptable limits. "As such, the condition of the nuclear power plant, including its principle barriers, was not significantly degraded." The NRC Resident Inspector has been notified. Notified R1DO (B. McDermott). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-03-04
40565 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-03-03 13:45 | 2004-03-03 17:01 | 2004-03-05 | SWING DIESEL GENERATOR AUTO STARTED FROM A BUS UNDERVOLTAGE VALID SIGNAL "At the time of this occurrence Unit 1 is in a scheduled Refueling Outage and Unit 2 is at 100% Maximum Operating Power. Also note, the 1 B Diesel Generator is a Swing Diesel Generator which is capable of supplying Unit 1 1F 4160 Volt bus and also when required 2F 4160 Volt bus. "At 13:45 EST on 03/03/04, the 1B Diesel Generator auto started due to a momentary Bus Undervoltage sensed on the 1F 4160 volt bus. "At the time of the occurrence the 1F 4160 Volt bus was energized with the Normal Supply Breaker racked out and the Alternate Supply Breaker closed in and supplying the 1F 4160 Volt bus. The Normal Supply Breaker was racked out for a scheduled breaker replacement. At the time of the occurrence 2 electricians were removing the Racked Out Normal Supply breaker from the cubicle. The breaker shutter mechanism (a component of the breaker) fell off of the breaker inside the cubicle causing the 1F 4160 Volt bus to sense a momentary bus undervoltage, the Alternate Supply breaker momentarily cycled open and re-closed causing the 1B Diesel Generator to auto start. Since the 1 B Diesel Generator auto started from a valid signal (Bus Undervoltage) an 8 hour report is being made. "At the time of this report the 1B Diesel Generator has been Shutdown and restored to a standby Lineup. The 1B Diesel Generator remains Operable." The licensee notified the NRC Resident Inspector. *****UPDATE FROM JOHNSON TO LAURA ON 3/5/04 AT 1050 EST***** "Subsequent investigation revealed the most probable cause of this event was the trip of the alternate supply breaker to the emergency bus, resulting in its momentary de-energization and an automatic start of the diesel generator on an actual bus undervoltage signal. The alternate supply breaker apparently tripped as a result of the shutter in the formal supply breaker cubicle falling against the fingers of the breaker when as the breaker was being removed from the breaker cubicle. The affected breaker was already n the racked out position. When the breaker was moved to allow its removal from the cubicle, the shutter was apparently forced upward by the movement of the breaker musing the shutter to move upward and the shutter actuating lever to pivot downward until the moc switch mechanism actuated the logic causing the alternate supply breaker to -rip and the diesel generator to start. The shutter actuating lever became separated from the shutter allowing the moc switch to return to its expected open position thereby allowing the alternate supply breaker to recluse and provide power to the bus before the swing diesel generator had sufficient permissives to tie to the bus. Even with the condition found in this breaker cubicle the breaker can be safely racked out. It is when the breaker is removed from the cubicle that there is an increased potential for the shutter and its connected lever arm to cause a logic actuation similar to that experienced in this event. The condition does not create an operability concern for the bus and at most could cause a logic actuation in the conservative direction and does not present any known operability issues for the associated 4160 volt buses. Additional inspections have been performed on 6 balance of plant 4160 volt breakers that are identical in design with acceptable clearances observed in the locations where problems were noted in the subject breaker cubicle. The normal supply breaker for the 1F 4160V bus has been inspected with no problems noted. The associated shutter and lever mechanisms for this breaker have been inspected, components replaced and the breaker returned to service. The alternate supply breaker on the safety related 4160 volt switchgear that was involved in this event was also checked and found to have acceptable clearances and no problems noted with the shutter mechanism. At this point this condition is limited to the breaker cubicle that is the subject of this notification based on extent of condition review performed up this point. There are currently no operability concerns for the affected 4160 volt switchgear or associated diesel generator." Notified R2DO (R. HAAG). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-03-03
40564 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-03-03 12:45 | 2004-03-03 14:03 | 2004-03-03 | OFFSITE NOTIFICATION OF INJURED INDIVIDUAL "At 12:45 PM EST, the Main Control Room was notified that an individual needed medical assistance at the South Building. The individual was light headed and nauseous. An ambulance was requested to the site, and arrived on site at 01:04 PM. The individual was not contaminated and was transported to a local hospital at 01:12 PM. Pennsylvania Emergency Management Agency (PEMA) was notified of the incident. "This requires a voluntary report due to the offsite notification on an emergency vehicle responding to the site." The licensee notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-03
40563 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2004-03-02 13:30 | 2004-03-02 18:18 | 2005-07-13 | NEVADA - AGREEMENT STATE NOTIFICATION OF STOLEN MOISTURE DENSITY GAUGE "Between 1:30 p.m. and 3:30 pm on March 2, 2004, at Vista & McCarran in Reno, Nevada, a Humboldt Scientific Model 5001 moisture density gauge containing 11 millicuries of Cs-137 and 44 millicuries of Am-241:Be, s/n 1854, was stolen from the transport vehicle. The employee indicated the chain securing the gauge to the pickup bed was cut. " The Reno, Nevada Police Department was notified." * * * UPDATE FROM STATE OF NEVADA TO ABRAMOVITZ ON 07/13/05 @ 14:41 EDT * * * The State provided the following information via facsimile: "The gauge was found in a remote canyon east of Reno Nevada on July 12, 2005. The Storey County, Nevada sheriff's office contacted the Nevada Radiological Health Section who took possession of the gauge on July 12, 2005, and placed it in locked storage pending fingerprinting by law enforcement and leak testing. The shipping case for the gauge was not found but radiation measurements indicated the source was intact and the gauge appeared to be undamaged. "Gauge serial number is actually 1859, the 1854 serial number listed above was a typographical error." Nevada event report number NV040001 Notified the R4DO (Spitzberg), NMSS EO (Miller) and TASDO (Whitney via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2004-03-05
40562 | 0 | YANKEE ROWE | 1 |  |  | [1] W-4-LP | 2004-03-02 12:25 | 2004-03-02 15:55 | 2004-03-02 | OFFSITE NOTIFICATION TO OTHER AGENCIES OF CONCRETE RUBBLE CONTAINER SPILL A container of concrete rubble was being transported from the Plant to Palmer, MA where it would eventually be transported via railroad to a waste repository. The intermodal container connection to the trailer broke off allowing the container to fall off spilling contents on the road. The location of the incident is approximately two miles from the Plant at Ford Hill Road, in Rowe, MA. The net weight of the container is 38,860 lbs and it contains low level radioactive concrete. Site Radiation Protection was sent by the licensee to the location of the incident. The spilled concrete rubble will be placed in a new container which will be taken back to the site. Clean up of the area is in progress, and area release is pending a post clean up survey. No one was injured during this incident. The licensee has notified the NRC Resident Inspector, the local Fire Department, State and Local government agencies and the Environmental Protection Agency (EPA). A Press Release is being planned to be issued by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-02
40561 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2004-03-01 16:49 | 2004-03-02 12:50 | 2004-03-02 | PRESS RELEASE REGARDING BORON RESIDUE The license provided the following via facsimile: "This ENS notification is to inform the agency of a news release that was issued 03/01/04 at 1649 Mountain Standard Time (MST) regarding the shutdown of Palo Verde Nuclear Generating Station Unit 3 and discovery of boron residue on a pressurizer heater sleeve which was reported to the Headquarters Operations Center in ENS ID 40556. "The unit has been cooled down to Mode 5 in preparation of maintenance to repair the pressurizer heater sleeve. Current plant conditions are approximately 125 degrees F and 35 psia." The unit was shutdown on 2/29/03 while troubleshooting a turbine-generator excitation problem. The residue was discovered by engineering personnel performing preplanned visual examinations of reactor coolant system (RCS) piping. "The NRC Resident Inspector has been notified of this ENS call." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Cold Shutdown; FMode3: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-03-02
40560 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2004-03-02 08:30 | 2004-03-02 09:48 | 2004-03-02 | PLANT RECEIVED A PACKAGE THAT EXCEEDED EXTERNAL SURFACE CONTAMINATION LIMITS The license received a 20 box shipment of fuel sipping equipment from Framatone ANP, Inc out of Richland, WA. One of the 20 boxes was determined to have an external surface contact reading >200 millirem (actual reading 202 millirem). The box was opened and contents surveyed resulting in a reading of 400 millirem/hr coming from a support stand that was in the package. A hot particle was captured from the stand and properly disposed of with their rad waste. After the particle had been removed, the stand, readings went from 400 millirem/hr to 20 millirem/hr. The licensee notified Framatone ANP about the incident. The Resident Inspector was notified | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | MS | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2004-03-02
40559 | 0 | BRAIDWOOD | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-03-01 16:00 | 2004-03-01 19:05 | 2004-03-01 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING POTENTIAL VIOLATION OF MAXIMUM POWER LEVEL "This 24-hour report is being made as required by Braidwood Unit 1 License Condition 2.G as a potential violation of the maximum power level 3586.6 MWt as stated in Unit 1 License Condition 2.C(1). "Braidwood is conservatively reporting an overpower condition on Unit 1 due to the implementation of an ultrasonic flow measurement system. Unit 1 was potentially overpowered a maximum of 1.07%. This value is based upon the maximum ultrasonic flow meter correction factor used for Unit 1 during the period between June 1999 and September 2003. "During post installation testing of the permanent ultrasonic flow measurement system, discrepancies in the ultrasonic flow measurement system were identified that could have resulted in an overpower condition of Unit 2 during the previous use of the ultrasonic system (i.e., during the period between June 1999 and September 2003). The ultrasonic flow measurement system was used to correct venturi feedwater flow measurements. The corrected feedwater flow measurements were then used is the calorimetric calculation for reactor power. "Currently Braidwood Unit 1 and Unit 2 are controlling power level based only on the venturi feedwater flow indication." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2004-03-01
40558 | 0 | FARLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2004-03-01 05:22 | 2004-03-01 07:23 | 2004-03-01 | UNIT 1 EXPERIENCED A REACTOR TRIP ON TURBINE TRIP DUE TO A FEEDWATER SYSTEM PROBLEM "Reactor trip Unit 1 as a result of Turbine Trip from Hi-Hi Steam Generator level '1C' Steam Generator. Steam Generator Feed pump suction pressure initially dropped, deviation alarms were received on 'A' and 'C' Steam Generator levels. Third condensate [pump] was started, increasing feed to S/Gs. '1C' S/G went high and caused turbine trip/reactor trip. Autostart of 'A' and 'B' motor driven feed pumps occurred following the trip." All rods fully inserted following the reactor trip. Both motor-driven auxiliary feedwater pumps are currently supplying the steam generators with the steam dump system in-service to remove decay heat via the main condenser. Offsite power is stable with the EDGs in standby, if needed. All systems functioned as required. The licensee is conducting an investigation to determine the root cause. The licensee will inform the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-03-01
40557 | -1 | OCONEE |  | 2 |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-02-29 20:11 | 2004-03-01 04:17 | 2004-03-23 | UNIT 2 AUTOMATIC FEEDWATER ISOLATION SYSTEM (AFIS) DECLARED INOPERABLE The licensee reported that both digital trains of the automatic feedwater isolation system were declared inoperable when one channel's input failed to zero and about the same time the second channel showed a shift in readouts which was fairly significant that they also declared it inoperable. These two channels have a shared neutral bus and it is believed that there may be a loose connection somewhere in the circuit. They are currently troubleshooting the problem. Plant will initiate a unit shutdown if the problem cannot be corrected by 0600 on 03/01/04 (12-hour LCO A/S). The NRC Resident Inspector will be notified. * * * * UPDATE ON 03/23/04 @ 1348 BY RANDY TODD TO C. GOULD * * * * RETRACTION Update- FNS 40557, dated 3-1-04, addressed an apparent loss of safety function on Oconee Unit 2. Specifically, the Automatic Feedwater Initiation System (AFIS) was considered inoperable, and therefore unable to perform its required safety functions. During that event, Operations shift personnel conservatively declared AFIS Channel 2 inoperable because it demonstrated an unexpected shift in readout concurrent with the failure of Channel 1. Subsequently Duke power concluded that Channel 2 remained capable of performing its safety function despite the shift in readout, which was in the conservative direction. Therefore, Duke Power has concluded that there was no reportable loss of safety function associated with this event and hereby retracts ENS notification 40557. Duke Power notes that, during the event, both channels were intentionally disabled for a brief period as a planned part of the repair activity. This was done to prevent the possibility of a spurious actuation during the repair. However, per guidance in NUREG 1022, removal of both trains of a safety function as part of a planned activity which results in entry into a Tech Spec action statement is not reportable. Initial Safety Significance: Operations declared TS 3.3.13 Condition B, which allowed 12 hours to come to Mode 3. Repairs were completed prior to initiation of shutdown. Corrective Action(s): A loose wiring connection was repaired. The NRC Resident Inspector was informed. | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-03-01
40556 | 0 | PALO VERDE |  |  | 3 | [1] CE,[2] CE,[3] CE | 2004-02-29 | 2004-02-29 11:46 | 2004-02-29 | BORIC ACID RESIDUE FOUND ON PRESSURIZER HEATER SLEEVE "The following event description is based on information currently available. If through subsequent reviews of this event, additional Information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 29, 2004, at approximately 05:21 Mountain Standard Time (MST) engineering personnel performing preplanned visual examinations of reactor coolant system (RCS) piping in accordance with procedure requirements discovered boric acid residue on the A03 pressurizer heater sleeve. The heater sleeve is an alloy 600 penetration. The visual observation was characterized as a small white buildup of boron residue around the heater sleeve as the sleeve enters the pressurizer bottom head. There does not appear to be residue running down the outside of the sleeve. There were no signs of dripping, spraying, puddles of liquid, or liquid running down the nozzle or pressurizer. The residue appeared dry. "Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.14 permits no reactor coolant system (RCS) pressure boundary leakage and therefore, the discovery of leakage (presumed boric acid residue) from the pressurizer heater sleeve was a degradation of a principal safety barrier. Therefore, the ENS notification of this event is in accordance with 10CFR50.72(b)(3)(ii). The control room personnel entered LCO 3.4.14 Condition B and are taking action to place the plant In Mode 5 within 36 hours. The Unit had been shutdown and was being maintained in Mode 3 while troubleshooting a turbine-generator excitation problem. At the time of discovery, the RCS was at approximately 565 degrees F and 2245 psia. "An investigation of this event will be conducted in accordance with the PVNGS corrective action program. "No ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode3: Hot Standby; FMode3: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2004-02-29
40555 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-02-03 | 2004-02-28 15:47 | 2004-03-04 | DEAD FISH FOUND AT CLINTON POWER STATION The licensee provided the following in accordance with their operating license Appendix B, Environmental Protection Plan. "At approximately 2100 hrs. on 2/27/04, the Illinois Department of Natural Resources (IDNR) contacted Exelon corporate environmental personnel and informed them there was a fish loss on Clinton Lake. Corporate personnel notified Clinton Power Station personnel at 2130 hrs. "An inspection on the lake shoreline on 2/28/04 occurred from 0800 to 1200 hrs by station personnel. "The inspection revealed a total of several hundred deceased fish over several locations. The species predominantly observed were gizzard shad. As followup, the final tally of fish affected will be determined after further communication by CPS environmental personnel working with IDNR. "The fish appeared have been deceased 3-5 weeks, based on observed decomposition. This 3-5 week time period closely coincides with Clinton Power Station's shutdown on 2/3/04 for refueling outage C1R09." The Licensee notified the NRC Resident Inspector. **** Update on 03/04/04 at 1648 EST from Leffel taken by MacKinnon ***** A press release of the dead fish found was issued today, 03/04/04, by the licensee. R3DO (Jim Creed) notified. NRC Resident Inspector was notified of this update by the licensee. | 25 | 0 | 0 | 25 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2004-02-28
40554 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-02-28 00:54 | 2004-02-28 02:02 | 2004-02-28 | OFFSITE NOTIFICATION TO STATE BASED ON MEDICAL TRANSPORT OF INJURED WORKER "At 00:54 AM EST, the Main Control Room was notified than an individual had fallen approx. 12 feet from scaffolding. An ambulance was requested to the site, and arrived on site at 01:20. The individual is not contaminated and was transported to a local hospital at 01:40. PEMA [Pennsylvania Emergency Management Agency] was notified of the incident." The licensee informed the NRC Resident Inspector. | 18 | 100 | 0 | 18 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-28
40553 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2004-02-26 15:00 | 2004-02-27 17:59 | 2004-02-27 | AGREEMENT STATE REPORTS SPILL AT NUCLEAR PHARMACY A syringe with 28 millicuries of Iodine-131 was stored inside a pig inside a hooded glove box. At 1500 CST on 2/26/04, the pig was knocked over, and the syringe broke. The contents of the syringe spilled into the hooded glove box. The spill was cleaned up. The glove box was ventilated and the ventilation system had a charcoal filter. It is estimated that 3 microcuries escaped to the atmosphere. Bioassays were performed on the 3 people involved in the spill and cleanup. No absorption was found. The charcoal filter and papers used in the glove box were placed in storage to allow the Iodine to decay. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2004-03-03
40552 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2004-01-23 01:15 | 2004-02-27 15:13 | 2004-02-27 | AGREEMENT STATE REPORT REGARDING A DAMAGED RADIOGRAPHY DEVICE The following facsimile was received from the Louisiana Department of Environmental Quality: "At 1:15 AM [CST] on January 23, 2004, a 90.1 Curie Iridium-192 AEA Model 969 sealed source with serial number 12449B could not be returned to the shielded position. The radiography camera was a SPEC Model 150 with serial number 82. The radiographers secured the area and contacted William Johnston, Radiation Safety Officer (RSO). The source was returned to the shielded position at approximately 1:55 AM on January 23. Apparently the drive cable connector pulled off of the worm. The connector appeared to be old. However, the cable itself is still very flexible/pliable. No overexposures were identified. The dosimeters for the radiographers read 125 millirem, 150 millirem, and 130 millirem. The TLD badges were sent off for emergency processing with readings of 0.715 R, 0.426 R, and 0.688 R." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-03-03
40551 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-02-26 | 2004-02-26 21:02 | 2004-02-26 | AGREEMENT STATE REPORT OF A LOST GAUGE "Del Monte Foods, a general licensee has been unable to locate a fixed gauge containing 100 milliCuries of Americium-241. The unit was one of 4 generally licensed gauges used as fill/level detectors at the Del Monte facility at Terminal Island. Del Monte had the 4 lines removed by contractors and after the completion of the project Del Monte realized one gauge remains unaccounted for. They have searched their facility and checked with all contractors and no information was obtained regarding the whereabouts of the gauge. The licensee has been requested to provide [the California Radiation Control Program Office] additional information regarding the dates/times involved, the names of the contractors who removed the lines, and the names of individuals who may have purchased the equipment." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-03-02
40550 | 0 | UNIVERSITY OF VIRGINIA |  |  |  |  | 2004-02-26 | 2004-02-26 15:49 | 2004-02-26 | LOST ELECTRON CAPTURE DETECTOR On December 16, 2003. the University of Virginia shipped the Electron Capture Detector section of a Gas Chromatograph to Varian Chromatograph Systems in Walnut Creek, California, using FEDEX. The Electron Capture Detector has a 5 millicurie Nickel-63 source. According to FEDEX, Mr. Cordero signed for receipt of the shipment at 0909 on December 17, 2003. Today, when UVA called Varian to follow up on the status of the detector, they were told that Varian never received the detector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-02-26
40549 | -1 | ST. MARY HOSPITAL |  |  |  |  | 2003-12-15 12:00 | 2004-02-26 15:43 | 2004-03-09 | MEDICAL EVENT During a Health Physics audit, while reviewing seed implantation cases, the auditor was reviewing a procedure performed on a patient on 2/13/04. The procedure involved an I-125 seed implantation that delivered 5000 Rad to the patient's prostate. The auditor saw a notation in the record that a previous implantation on 12/15/03 had also delivered 5000 Rad to the same patient's prostate. When the auditor pulled the record for the 12/15/03 implantation, he discovered that the intended dose from the procedure was 10,000 Rad. He proceeded to call Radiation Medicine Center, the licensee who performed both procedures (License # 2902023-06). Radiation Medicine Center stated that, when evaluating the patient in mid-January, they discovered, via CT scan and dosimetry, that the patient had only received 5000 Rad during the first procedure, and that is why the second procedure was performed on 2/13/04. The auditor is reporting the implantation from 12/15/03 as a Medical Event. * * * UPDATE ON 03/09/04 @ 0956 BY IRA GARELICK TO C GOULD * * * RETRACTION The licensee is retracting this event on the basis that further investigation along with consultation and a site visit with Reg 1 NRC personnel determined the implant went as planned. There was some tissue shrinkage resulting in cold spots which were adequately treated in the second implant on 02/13/04. Notified Reg 1 RDO(Cobey) and NMSS EO(Psyk) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-02-26
40548 | 0 | OCONEE |  |  | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-02-26 11:51 | 2004-02-26 13:59 | 2004-02-26 | RPS ACTUATION WHILE CRITICAL While operating at power, a main turbine trip caused a reactor trip. The cause of the trip is unknown but is being investigated. All control rods inserted on the reactor trip, no primary or secondary system relief valves operated, and reactor temperature is being maintained using the turbine bypass valve to the condenser. Steam generator water levels are being maintained using main feedwater. The station electrical system is available and in a normal configuration. Current RCS pressure is 2149 psig and temperature is 552 deg F. Units 1 and 2 were not affected. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-02-26
40547 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2004-02-26 01:05 | 2004-02-26 08:38 | 2004-02-26 | CONTROL POWER FUSE FAILURE IN HPCI SYSTEM "The High Pressure Coolant Injection (HPCI) system had been removed from service to perform planned maintenance and testing. During post-maintenance testing, the HPCI gland seal condensate pump tripped due to a blown control power fuse. The maintenance scope did not include the pump or its power supply. The fuse was replaced and the surveillance completed satisfactorily. Investigation into the cause of the failure is ongoing. HPCI remains inoperable in support of additional pre-planned testing." The licensee notified the State and the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2004-02-26
40545 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-02-25 11:15 | 2004-02-25 14:05 | 2004-02-25 | OFFSITE NOTIFICATION TO NEW JERSEY DEPARTMENT OF ENVIRONMENTAL PROTECTION "Made 2 hour notification to the New Jersey Department of Environmental Protection of a New Jersey pollutant discharge elimination system permit violation. The limit for petroleum hydrocarbons is a daily average of 10 ppm over a month period. Current projected amount is 40 ppm." The sample is taken at the oil water separator outfall for liquid going to the storm drains. The NRC Inspector was notified. | 100 | 99 | 0 | 100 | 99 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-25
40544 | -1 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-02-19 13:00 | 2004-02-24 14:51 | 2004-02-27 | AGREEMENT STATE REPORT A Campbell Pacific Nuclear (CPN) Density Gauge, Model MC2, serial number M21084026 was stolen from the backseat of a privately owned chevy suburban at approximately 1300 CST on 2/19/04. The gauge contains 10 millicuries of Cs-137, and 50 millicuries of Am-241/Be. The gauge case inside the truck was not locked, but was blocked to prevent movement. Several other items were also stolen from the truck including a cellphone, wallet, and briefcase. The licensee reported the theft to the Colorado Springs Police Department, Case No. 04-6892, shortly after the theft was discovered. Police are investigating credit card and cellphone usage to try and track down the perpetrators. * * * RETRACTION ON 02/27/04 AT 11:20 BY A. COSTA * * * This event notification is a duplication of event notification number 40532. The information contained herein will be shown as an update to EN#40532. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-02-27
40543 | 0 | NORTH DAKOTA DEPARTMENT OF HEALTH |  |  |  |  | 2004-01-28 12:00 | 2004-02-24 14:10 | 2004-02-24 | AGREEMENT STATE REPORT OF MEDICAL EVENT On 1/28/04, the patient was to receive a total dose of 50.4 Grays to the 'vaginal cuff' region using a 6 Curie Ir-192 sealed source. The dose was to be administered using a Microselectron Remote Afterloader HDR manufactured by Nucletron, serial number 31021. The plan was to administer 3 radiation treatments using a catheter that is 1500 millimeters (mm) long. The treatment planning software system uses a default value of 995 mm for the catheter length. When preparing the treatment plan for the first of the 3 planned radiation treatments, the medical physicist did not notice that the catheter length in the treatment plan was incorrect (995 mm instead of the actual 1500 mm catheter that would be used). When the radiation oncologist and the medical physicist were doing a pretreatment review and ensuring that the important parameters of the planned treatment were correct, they did not check the catheter length in the treatment plan to ensure that it was correct. The first radiation treatment was conducted, but instead of the radiation source traveling approximately 1500 mm in the catheter and providing radiation treatment to the 'vaginal cuff' region on the patient, it traveled only about 995 mm, and never entered the patient's body. When the medical physicist began to plan the second of the three radiation treatments, he noticed the error in the treatment plan for the first treatment. The radiation oncologist notified the patient on the same day the error was discovered. The records of all patients previously treated by this medical physicist and radiation oncologist were reviewed to determine if a similar error had occurred during any other high dose rate remote afterloader treatments, but no other errors of this type were found. To prevent future errors, both the medical physicist and the radiation oncologist have reviewed the treatment planning software and have agreed on a program of formal cross checking of the pretreatment printout that would include verifying that the catheter length specified in the treatment plan is correct. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | DOSE <> PRESCRIBED DOSAGE | [8 empty] | NON EMERGENCY | 4 | ND | OTH | AGR |  | 35.3045(a)(1) |  |  | 0 | 2004-02-27
40542 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2004-02-19 23:45 | 2004-02-23 17:23 | 2004-02-23 | AGREEMENT STATE REPORT "The Wisconsin Radiation Protection Section was notified of a fire involving radioactive materials on February 19, 2004 at 23:45. The item was a NDC Model 104P Portable Mass Gauge containing 25 millicuries of Am-241. "Members from the Wisconsin Radiation Protection Section responded to the location of the fire in Wisconsin Rapids on Friday, February 20, 2004. Wisconsin Rapids Police Department controlled access to the scene and allowed no one to enter until personnel arrived from the Radiation Protection Section. "A survey was performed at the location using sodium iodide detectors. The gauge was located under 3 to 4 inches of fire debris. The gauge was emitting 30 millirem/hour on contact with the source opening. Wipe test of the gauge and surveys of the surrounding area confirmed the source was intact. The gauge was damaged severely by the fire. "Initial investigation into the fire by the Wisconsin Rapids Police Department indicated that the fire was set by two to three individuals to cover up an apparent robbery at the residence. These individuals have been apprehended. "The licensee used the gauge at temporary job sites in Wisconsin to measure drainage profiles on paper lines at paper mills." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2004-02-26
40541 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-01-11 06:37 | 2004-02-23 15:36 | 2004-02-23 | INVALID SPECIFIED SYSTEM ACTUATION "This report is being made in accordance with 10CFR50.73 (a)(1), which states, in part, "in the case of an invalid actuation reported under 10 CFR50.73(a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event instead of submitting a written LER." These invalid actuations are being reported under 10CFR50.73(a)(2)(iv)(A). NUREG-1022, Rev. 2, states that the report should provide the following information: -The specific train(s) and system(s) that were actuated -Whether each train actuation was complete or partial -Whether or not the system started and functioned successfully. "On January 11, 2004, at 0637 hours, the Reactor Building Exhaust Radiation Monitor (i.e., 1-D12-RM-K609B) signal input spiked resulting in the invalid actuation of the logic associated with the instrument channel. The actuations included the Primary Containment Isolation System (PCIS) Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems) valves, the Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation) and the automatic start of both Standby Gas Treatment (SGT) System trains A and B. The actuations of PCIS Group 6 valves and Reactor Building Ventilation System isolation were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). Additionally, SGT System trains A and B started and functioned successfully. After verification of the expected equipment responses, 1-D12-RM-K609B was reset, the actuation logic was reset, and the equipment/systems were returned to the status required by plant conditions. A radiological survey of the monitored area was completed with no abnormal conditions noted. "Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in action request (i.e., AR) 115087. The resident inspector has been notified." | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-02-23
40540 | 0 | UNIVERSITY OF VIRGINIA HOSPITAL |  |  |  |  | 2004-02-21 09:00 | 2004-02-23 14:20 | 2004-03-10 | MISSING MEDICAL SOURCE FOR 2 HOURS AT UVA HOSPITAL The licensee at University of Virginia Hospital reported an event where a radioactive medical source was missing for approximately 2 hours. The patient was being treated for uterine cancer. At the end of the treatment, the licensee removed 8 catheters from the patient. Unknown at the time, one ribbon with 8 seeds of Ir-192, with an approximate activity of 5 millicuries, fell onto the floor. The licensee performed a search and radiological surveys, and the missing ribbon was located 2 hours later in a trash compactor. The licensee is performing an assessment of any unplanned exposures that resulted from this event. * * * UPDATE AT 1530 EST ON 2/24/04 FROM R. ALLEN TO E. THOMAS * * * The licensee has concluded their assessment of any unplanned exposures from this incident, along with determining its root cause. In the unlikely case that the patient was laying directly on top of the source (on contact) for the entire 30 minutes from the time the physicians removed the sources until the missing ribbon was discovered, her skin exposure would have been 662 rad. This exposure is less than her skin exposure from other treatments of the tumor thus far, and would result in minimal adverse effects. If the 30 minute exposure occurred at a distance of 1.5 millimeters from the patient, her exposure would have been 41 rad to the skin. It is highly unlikely that the patient received anywhere near these exposure levels, as the missing ribbon was most likely picked up with other trash shortly after the room was de-posted, and prior to the physicians discovering the loss. In the brief time (1-2 minutes) it took to transport the ribbon with other trash to the dumpster, and during the time the ribbon was in the dumpster, any exposures to additional personnel would have been negligible. The root cause of the lost ribbon is that the meter used to survey the room following the procedure was defective. Another meter was used to locate the ribbon in the trash compactor. Notified R1DO (Shanbaky) and NMSS (Essig) * * * UPDATE AT 1459 ON 3/10/04 FROM ALLEN TO GOTT * * * Due to skin reddening on the patient, the patient may have received an over exposure to the thigh. It is unknown how long the source was stuck to the patient's skin or the exposure. The licensee is continuing to investigate. This report is now being classified as a Medical Event reportable under 10 CFR 35.3045(a)(3). Notified R1DO (Cobey) and NMSS (Brown) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>1000X | DOSE TO OTHER SITE > SPECIFIED LIMITS | [8 empty] | NON EMERGENCY | 1 | VA | HOS |  | 20.2201(a)(1)(i) | 35.3045(a)(3) |  |  | 0 | 2004-02-23
40539 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-02-23 01:52 | 2004-02-23 07:32 | 2004-02-23 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN STARTED DUE TO GRASS INTRUSION "At 0152 on February 23rd the station service water system at Hope Creek experienced elevated differential pressure due to grass intrusion. At the time of the grass intrusion the `C' Service Water Traveling Screen was removed from service for an inspection. The grass intrusion resulted in the `A' Service Water strainer breaker tripping open de-energizing the strainer. Differential pressure on this strainer was pegged high and flow was reduced to 1900 gallons per minute [17,000 normal; 15,500 minimum]. The combination of these conditions resulted in inadequate cooling water flow to the `A' Station Auxiliaries Cooling Water system, and consequently inadequate cooling for the `A' Control Room Emergency Filtration [CREF] unit. With the `B' CREF fan already inoperable for a scheduled maintenance window, this resulted in entry into Technical Specification 3.0.3. "This report is to document starting a unit shutdown to comply with Technical Specifications 3.0.3. Power reduction for Unit shutdown was commenced at 0407 [ET]. Unit shutdown was terminated at 0424 when `C' Service water pump was returned to service restoring cooling water to `A' SACS loop, restoring it to an OPERABLE status. This event is reportable under 10CFR50.72(b)(2)(i) as a four hour report. "The Control Room Ventilation System provides heating, cooling, ventilation, and environmental control for the control room and adjacent areas. Under accident conditions, the Control Room Emergency Filtration Unit (CREF) ensures that the control room will remain habitable during and following all design basis accidents. Because the CREF system is required to automatically respond in the event of a design basis accident, having both trains of CREF inoperable at the same time impacted the ability to mitigate the consequences of an accident. Therefore, this event is also being reported in accordance with 10CFR50.72(b)(3)(v)(D) to comply with the requirements of an 8 hour report. "At the time of the event the following Tech Spec related equipment was inoperable. `C' Service Water for screen inspection and `B' CREF for chiller maintenance work. Currently all safety related equipment is operable with the exception of the `A' Service Water Loop." The licensee notified the NRC Resident Inspector. | 94 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-02-23
40538 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-02-22 17:30 | 2004-02-22 19:02 | 2004-02-22 | UNIT 1 MANUALLY TRIPPED AFTER THE "B" SG FEEDWATER ISOLATION VALVE FAILED CLOSED "The 1CF-42B (1B Steam Generator Feedwater Isolation Valve) failed closed with Unit 1 at 100% power. Operators performed a manual reactor trip as required by 'Loss of Normal Steam Generator Feedwater Supply', AP-06. Emergency procedures were utilized to respond and stabilize Unit 1 in mode 3. The plant is currently stable in mode 3 at normal operating pressure and temperature. Currently, steam generator levels are being maintained using the auxiliary feedwater system. Other than the failure of 1CF-42B (Initiating Event), all plant safety systems operated as required." No primary or secondary safeties or reliefs lifted during the transient. All control rods fully inserted. The main condenser is in-service to remove decay heat. The licensee had identified a problem with the hydraulic motor associated with 1CF-42B and was in the process of developing corrective actions before the failure. The licensee will inform both state/local agencies (courtesy notification) and has informed the NRC resident inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-02-22
40537 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2004-02-22 15:10 | 2004-02-22 18:42 | 2004-02-22 | MANUAL SCRAM AT PEACH BOTTOM 2 DUE TO DECREASING CONDENSER VACUUM "Peach Bottom Unit 2 reactor was manually scrammed due to degrading main condenser vacuum. The reactor was manually scrammed prior to reaching the automatic scram setpoint. All plant systems responded as expected with no significant issues noted. A Group II and Group III Primary Containment Isolation was received due to reactor water level passing through 1 inch. All isolation systems responded as required and repositioned to their expected positions." The licensee also indicated that all control rods properly inserted into the core. The method of decay heat removal was using the main condenser. The licensee initiated a post scram review to identify and correct the source of degrading vacuum. The licensee also indicated the manual scram was initiated at 25 inches and lowering of condenser vacuum. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-02-22
40536 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-02-21 08:41 | 2004-02-21 15:48 | 2004-02-21 | RCIC SYSTEM INOPERABLE DUE TO POSSIBLE UNDERVOLTAGE RELAY FAILURE "This ENS notification is made to report that on February 21, 2004 at 0841 PST Reactor Core Isolation Cooling was rendered inoperable due to RCIC-V-13 (RPV injection valve) motor operator losing power. Preliminary investigation indicates the undervoltage relay may have failed, resulting in a loss of control power for the valve and loss of valve position indication. "The event is considered reportable to the NRC under 10 CFR 50.72(b)(3)(v)(D) based on guidance contained in NUREG 1022, "Event Reporting Guidelines," and NRC Regulatory Issue Summary (RIS) 2001-14, 'Position on Reportability Requirements for Reactor Core Isolation Cooling System Failure.' A follow-up LER will be issued under 10 CFR 50.73(a)(2)(v)(D)." This event placed the plant in technical specifications LCO 3.5.3 which has a 14 day duration. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-02-21
40535 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-02-21 10:05 | 2004-02-21 12:06 | 2004-02-21 | OFFSITE NOTIFICATION OF MEDICAL EVENT AT SUSQUEHANNA "At 10:05 AM PST, the Susquehanna LLC Shift Manager was notified that a member of the general public required medical assistance. The individual was at a company owned public recreation area adjacent to the Susquehanna LLC River Intake access road. The recreation area is outside the protected area. An ambulance was called to the scene, arriving at 10:28 and leaving at 10:52. The individual was transported to a local hospital. The LLEA and PEMA were notified of the incident." The NRC Resident Inspector was notified. | 80 | 100 | 0 | 80 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-21
40534 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-02-20 23:20 | 2004-02-21 02:04 | 2004-02-21 | EMERGENCY RESPONSE FACILITY INFORMATION SYSTEM INOPERABLE "At 2220 hours EST, on February 20, 2004, the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, Emergency Response Facility Information System (ERFIS) computer system became inoperable. The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, FAX modems for Emergency Preparedness functions, and the Inadequate Core Cooling Monitor (ICCM). Actions were completed to restore the ERFIS computer system to an operable status at 0053 hours on February 21, 2004. The loss of ERFIS requires alternate methods, as described in plant procedures, to be used for the above described functions. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still have been made, if required, during the time that the ERFIS computer system was inoperable. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remained available to assess plant conditions, make notifications, and accomplish required communications, as necessary." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-02-21
40533 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2004-02-20 10:33 | 2004-02-20 13:00 | 2004-02-20 | OFFSITE NOTIFICATION DUE TO A PRESS RELEASE CONCERNING THE UNIT 2 SHUTDOWN "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the Information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "This ENS notification is to inform the agency of the shutdown of Palo Verde Nuclear Generating Station Unit 2, due to increasing primary to secondary leakage, for which a news release has been issued. "Unit 2 was shutdown to Mode 3 on February 19, 2004 at 18:28 Mountain Standard Time (MST) following detection of increased primary to secondary leakage at approximately 15:22 MST. The leakage was less than the Technical Specification 3.4.14(d) limit of 150 gallons per day through any one SG. Steam generator #1 was isolated at approximately 18:40 MST. The unit has been cooled down to Mode 5 in preparation of maintenance to repair the steam generator. Current plant conditions are approximately 160 degrees F and 350 psia. "The decision to issue a press release was made at approximately 09:00 MST on February 20, 2004. The press release was issued at approximately 10:33 MST. "The NRC Resident Inspector has been notified of this ENS call." This is the 1st cycle using these Steam Generators which were replaced in 2003. The licensee indicated that the change in in primary to secondary leakage was a step increase but was unable to accurately quantify the amount since it was less than 20 gallons per day. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-20
40532 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2004-02-19 15:50 | 2004-02-20 10:41 | 2004-03-24 | AGREEMENT STATE REPORT CONCERNING STOLEN GAUGE "At 3:50 PM [MST] on 19 Feb 04 - The Department received telephone notification of a stolen gauge by Larry W. Chisman, the RSO for Soil Testing and Engineering Inc. "The theft occurred between 11:30 AM and 2:00 PM [MST] on 19 Feb 04 in a parking lot at 314 W. Bijou, Colorado Springs, Colorado. The gauge was locked within its orange transport case which was locked within a Suburban. The windows were reported to be intact and it is unknown how entry to the vehicle was gained. "The stolen gauge is a CPN Model MC-2, serial number M21084026. The gauge contains 10 milliCi of Cs-137 and 50 milliCi of Am-241:Be. The incident was reported to local police on the day of the theft." * * * UPDATE ON 02/27/04 AT 11:20 BY A. COSTA * * * This text update was reported as EN#40544 on 02/24/04 at 14:51 EST. EN#40544 has been retracted because it was a duplicate of this event notification. "A Campbell Pacific Nuclear (CPN) Density Gauge, Model MC2, serial number M21084026 was stolen from the backseat of a privately owned Chevy suburban at approximately 1300 CST on 2/19/04. The gauge contains 10 millicuries of Cs-137, and 50 millicuries of Am-241/Be. The gauge case inside the truck was not locked, but was blocked to prevent movement. Several other items were also stolen from the truck including a cellphone, wallet, and briefcase. "The licensee reported the theft to the Colorado Springs Police Department, Case No. 04-6892, shortly after the theft was discovered. Police are investigating credit card and cellphone usage to try and track down the perpetrators." * * * UPDATE ON 02/27/04 FROM JAMES JARVIS TO A. COSTA * * * The Colorado Department of Health reported that Local Law Enforcement located the lost gauge, and it was returned to licensee, Soil Test and Engineering. The gauge source is intact and the licensee is leak testing the instrument as requested by the Agreement State. Notified R4DO (Sanborn) and NMSS (Brown). * * * UPDATE ON 03/24/04 @ 1652 BY TIM BONZER TO C. GOULD * * * The stolen gauge was found intact and not damaged between two storage units in its transport box in Colorado Springs, CO. on 2/26/04. Notified NMSS EO(Essig) and Reg 4 RDO(Graves) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-02-25
40531 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-02-18 | 2004-02-18 17:47 | 2004-02-18 | OFFSITE NOTIFICATION TO PEMA OF MISLABELED CONTAINER "At 1500 on 2/16/2004, a tractor trailer with two intermodals [sea land containers] arrived at SSES [Susquehanna Steam Electric Station] from Race, LLC placarded radioactive 'empty'. Upon inspection it was determined that one of the intermodals had equipment in it contrary to the bill of lading and DOT regulations. This equipment was surveyed and found to be non-contaminated and non-radioactive. There was no radioactive exposure to any individuals as a result. Operations personnel were made aware of this event at 1630 on 2/18/2004. It was determined that this event may be of public significance and is reportable under 10CFR 50.72 (b)(2)(xi). The Pennsylvania Emergency Management Agency (PEMA) is being notified of this incident." The licensee notified NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-18
40530 | 0 | US AIR FORCE |  |  |  |  | 2004-02-17 17:00 | 2004-02-18 15:33 | 2004-02-18 | UNPLANNED CONTAMINATION USAF personnel in the Johnston Atoll in the Pacific were attempting to remove the "batteries" from an exit sign they believed to be battery powered. During the attempt to open the case, they destroyed the sign only to discover that it was a tritium sign. All tritium modules were broken. Five personnel were in the room at the time and all were potentially exposed to the tritium. The Radiation Safety Officer (RSO) isolated the room and the personnel clothing, etc. Pre-cleanup surveys indicated greater than 6 times the normal background survey readings in the room. The RSO double-bagged the sign and tritium module debris. The room and work areas were decontaminated. Post-cleanup surveys indicated normal background readings. Personnel uptake and dose evaluations are currently being assessed. The tritium sign was an Isolite model 2040 with original activity of 15.0 Curies and was manufactured in March of 1993. Current activity was calculated to be 8.06 Curies. The RSO will follow up with Region 4 concerning personnel tritium uptake and contamination levels as well as equivalent dose calculations. The licensee will be notifying Region 4 Materials branch. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 0 |  | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2004-02-18
40529 | 0 | US ARMY TACOM |  |  |  |  | 2004-01-05 | 2004-02-18 12:47 | 2004-02-18 | LOST TELESCOPE COMPONENT TRITIUM SEALED SOURCE On December 16, 2003, the US Army shipped a telescope firing component containing a 2.65 curie tritium source via DHL air from Vicenza, Italy to St. Louis MO destined to Siler Instruments, a US Army contractor. The source was discovered missing on January 5, 2004. It was determined that the package did not arrive in Cincinnati, OH, the point of entrance through US Customs. The US Army received a final notice from DHL on January 26, 2004 that the box containing the missing source cannot be located. The Army Health Physicist has contacted NRC Region 3 and is in the process of finalizing the 30-day written report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-02-18
40528 | 0 | NATIONAL INSTITUTE ON DRUG ABUSE |  |  |  |  | 2004-01-19 09:00 | 2004-02-18 09:08 | 2004-02-18 | NIH, DHHS REPORTED THE LOSS OF SIX VIALS OF TRITIATED ACETIC ACID FROM ITS NATIONAL INSTITUTE ON DRUG ABUSE A vial box containing 10mCi tritiated acetic acid in each of six 1.5ml vials, held at -75°C for 22 months, was mistaken for a container of nonradioactive sample vials when its "Caution: Radioactive Materials" (CRAM) tape lost adhesion, separated from the vial box, and became obscured by accumulated frost. Although each of the 6 vials was labeled with a CRAM sticker noting the identity, activity, and inventory number assigned to its contents, these small stickers were not visible through the unopened box after prolonged storage. The container in question was mistakenly disposed of as biohazard waste, in a batch of approximately 50 boxes of identical size and appearance, all the rest of which contained nonradioactive samples. The container at issue was initially recognized as missing when the lab for which it was being stored requested that 2 of the 6 remaining vials be delivered from a repository maintained in a locked freezer under exclusive control of the licensee's Radiation Safety Officer (RSO). An extensive search of agency freezers was undertaken to rule out the possibility that the container in question had been inadvertently merged, after losing its label, with other sample collections. Once this possibility was eliminated, the RSO concluded that the item had entered the biohazard waste stream and had been incinerated at a medical waste incinerator. Upon notification, the incinerator operator indicated that its incinerator was equipped with a high efficiency acid emissions scrubber, which would be expected to retain tritiated acetic acid. Retained byproduct material was buried mixed with 5 tons of scrubber absorbent and 40 tons of incinerator ash, the daily amounts shipped by that facility. Among other steps taken to prevent recurrence, a large lockable multicompartment acrylic box was fabricated, with an internally mounted vinyl CRAM sign, for long-term ultracold storage of radioactive materials being held for future distribution. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-02-18
40527 | 0 | STATE OF WEST VIRGINIA |  |  |  |  | 2004-02-17 10:27 | 2004-02-17 16:32 | 2004-02-17 | RADIOACTIVE MATERIAL DISCOVERED AT LANDFILL West Virginia Bureau for Public Health (WVBPH) notified the NRC Operations Center that at 1022 hrs. EST on 2/17/04, they received a call from Northwest Landfill, Waste Management, Inc., located on Drybranch Road in Parkersburg, W.VA., stating that a truck full of household refuse alarmed a radiation monitor at the landfill. WVBPH responded to the landfill and took radiation measurements on the outside of the vehicle. The highest dose measured was 1.2 millirem/hr. The truck was dumped and the trash searched until the source of the radiation was discovered. The inspectors discovered a metallic object approximately 1 inch long by 1/2 inch wide that was the source. The object was odd-shaped and its use and origin is unknown. The material was bagged and isolated at the landfill where it will remain to decay away. Radiation readings at 1cm were 5 millirem/hr. Spectrum analysis indicates that the material is an iodine, possibly Iodine-131. Notified R1DO (Henderson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | WV | OTH | GEN |  |  |  |  | 0 | 2004-02-17
40526 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2004-02-04 | 2004-02-17 15:30 | 2004-02-17 | AGREEMENT STATE (NE) NOTIFICATION OF LOST TRITIUM SOURCES The licensee reported that upon an inventory check in early February 2004, two general licensed self-luminous exit signs were missing and are currently unaccounted for. The two units were purchased from SRB Technologies, Inc (serial #'s 18132 and 16138) containing 24 curies of activity each as assayed in May of 1985. These exit signs were purchased and installed in 1985 and were removed and held in storage since 1990. The licensee has concluded that the exit signs were unintentionally disposed of or misplaced and thrown away during a clean-up of inventory from their change of ownership to Newell Rubbermaid Inc. Efforts of locating and recovering these units have been unsuccessful. The remaining five signs were placed in a single container and stored in a locked fireproof cabinet for subsequent transfer to their respective manufacturers for proper disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2004-02-20
40525 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-02-17 13:30 | 2004-02-17 13:45 | 2004-02-17 | OFFSITE NOTIFICATION DUE TO POTENTIAL NEWSWORTHY OCCURRENCE "FPLE Seabrook station is issuing information to the media as a result of a potential newsworthy occurrence that took place today. An employee handling mail exhibited symptoms of a reaction. The station isolated and evacuated the area and contacted offsite law enforcement agencies per station guidelines. The area has been inspected by hazardous materials responders with no abnormalities noted and has been released for normal access." The licensee notified the NRC Resident Inspector, the state Emergency Preparedness Director, Local Law Enforcement and the FBI. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-17
40524 | 0 | FAIRBANKS MORSE ENGINE |  |  |  |  | 2004-02-16 | 2004-02-16 14:57 | 2004-02-16 | PART 21.21 NOTIFICATION OF POTENTIAL SAFETY HAZARD ASSOCIATED WITH USE OF TURBOCHARGER "On February 12, 2004, Fairbanks Morse Engine evaluation determined a potential safety hazard associated with the use of ABB turbocharger model VTC-304 on OP engines only. "Torsional resonance has been found in the rotating assembly which is excited by exhaust pulses. The resonance manifests itself as either a bent or broken shaft, slipped compressor wheel, cracked compressor wheel or complete rupture of the compressor set. Once failure occurs, engine power cannot be sustained. "This condition is corrected by machining the rotating assembly to tune the natural frequency away from operating conditions. "The only affected site is Crystal River 3. (6) turbos have been shipped to this site. None of the turbos have been installed and all are in storage. The FM parts department will arrange to have the turbos returned to the factory to have the necessary machining performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | WI | OTH | PAR | 21.21 |  |  |  | 0 | 2004-02-16
40523 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2004-02-16 02:25 | 2004-02-16 02:58 | 2004-02-16 | UNUSUAL EVENT DECLARED DUE TO SERVICE AIR COMPRESSOR CONTROLLER EXPLODING At 0225 EST on 02/16/04, the licensee declared an Unusual Event due to the instrument air/service air system service air compressor controller exploding due to an electrical fault. Instrument air compressor alarm #H-16 actuated. The backup 'A' and 'B' instrument air compressors auto started. The licensee immediately electrically isolated the service air compressor controller. The licensee declared the Unusual Event in accordance with EAL 8.3.2, an explosion or detection of explosion affecting plant equipment or structures within plant protected area boundaries. No other plant equipment or structures were affected. The plant is stable at 100% power. There is no indication of tampering or foreign objects inside the controller. The licensee is investigating the cause. The licensee notified the NRC Resident Inspector and State and Local Officials. The licensee does not plan to issue a press release. * * * Update at 0425 EST on 02/16/04 from John White to Jolliffe * * * At 0420 EST on 02/16/04, the licensee terminated the Unusual Event based on the service air compressor controller being electrically isolated and removed from service and the surrounding area secured. The licensee is continuing to investigate the cause of the electrical fault. Plant security personnel determined in accordance with their security tampering procedure that this event is clearly not security related. The licensee notified the NRC Resident Inspector and State and Local Officials of the termination of the Unusual Event. Notified R1DO James Trapp, NRR EO John Hannon, DIRO Susan Frant, TAS Hahn, FEMA Ken Sweetser, and DHS John Frost. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-02-16
40522 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-02-15 15:19 | 2004-02-15 20:18 | 2004-02-16 | AUTOMATIC REACTOR TRIP WITH AUXILIARY FEEDWATER ACTUATION The following information was received from the licensee via facsimile: "At 1519 [CDT] on 2-15-04, the plant was at 20 power, increasing load. During the transfer from the bypass feedwater regulating valves to the main feedwater regulating valves, the main turbine tripped due to a P-14 S/G Hi-Hi level signal. The P-14 signal also caused a Feedwater Isolation Signal (FWIS), which resulted in a Motor Driven Aux Feedwater Actuation (MDAFAS), and Steam Generator Blowdown Isolation Signal. "Steam Generator levels subsequently shrunk to low levels causing a Steam Generator low level reactor trip at 1524 [hrs]. Sometime after the turbine trip, the turbine driven aux feed pump [(TDAFP)] was manually started to help restore S/G levels. The pump was later manually secured, but then received a subsequent auto-start signal and tripped on overspeed. The TDAFP was declared inoperable at 1535 [hrs]. With the exception of the TDAFP, all safety systems operated properly. "The plant is currently stable in Mode 3, with the primary plant at 557 deg F and 2235 psig, and pressurizer level at 25%." The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0031 EST ON 2/16/04 HOPE BRADLEY TO GOTT * * * The following information was received from the licensee via facsimile as a "rewrite of above paragraph 2." "Sometime after the turbine trip, the Turbine Driven Aux Feedwater Pump (TDAFP) was manually started to help restore S/G levels. Due to decreasing reactor coolant system (RCS) temperature, it was decided to stop the TDAFP since it is a steam load. The steam supply valves were remote manually closed from the control room. At the same time the steam supply valves were closing, the steam generator levels shrunk to low levels causing a Steam Generator low level reactor trip and Turbine Driven Aux Feedwater Actuation (TDAFAS) at 1524. The steam supply valves immediately reopened due to the TDAFAS. It is postulated that this transient in the steam supply caused the pump to overspeed trip. The TDAFP was declared inoperable at 1535. With the exception of the TDAFP, all safety systems operated properly." The licensee notified the NRC Resident Inspector. Notified R4DO (Cain). | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-02-15
40521 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-02-15 08:22 | 2004-02-15 11:16 | 2004-02-15 | CONTAMINATED AND INJURED EMPLOYEE TRANSPORTED TO OFFSITE MEDICAL FACILITY No System or Plant affect. At 08:22 AM EST, an injured Contractor worke[r] who was potentially contaminated was transported by ambulance to an offsite medical facility. The Contract employee fell approximately 15 to 20 feet in the Unit 1 Circulation Water box which is located in the Condenser Bay area. Unit 1 is presently in Cold Shutdown and in Mode 4 for a scheduled Refueling Outage. The employee received cuts to the forehead and nose and an injury to the arm and also some back pain. In an effort to provide medical treatment as the first priority, decontamination efforts were not completed on site and the individual was transported as potentially contaminated. The injured cont[r]act employee was also accompanied by a Health Physics Technician. Upon arrival at the hospital and while receiving medial care, the Health Physics technicians did discover a 500 dpm/cm2 spot of contamination on the back of the head of the injured person. Decontamination efforts are underway while medical treatment is rendered. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2004-02-15
40520 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2004-02-14 13:00 | 2004-02-14 14:30 | 2004-02-15 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER MOISTURE DENSITY GAUGE At approximately 1300 hours on 2/14/04, the technician returned home for lunch in the company truck with a Troxler Model 3430, S/N 30167, gauge containing two sources, i.e., 8 millicuries Cs-137 and 40 millicuries Am-241/Be, locked in its case in the truck bed. The chain securing the case was cut and the Troxler stolen. The technician has the key which locks the source in the retracted position. The Miami Police Department and the Florida State Warning Point were notified. The company will issue a press release and reward for the return of the gauge. Florida Incident No. FL04-116. ***Update on 02/15/04 at 1549 EST by Mr. Jerry Eakins taken by MacKinnon*** The Troxler gauge was found next to a garbage dumpster located on a grocery store parking lot. The gauge was still in its case and had not been damaged. Miami HAZMAT came to the scene and took radiation readings of the gauge in its case. Radiation readings were 2 millirem/hr (expected value). The gauge has been returned to its assigned owner. R1DO ( Jim Trapp) & NMSS EO (Gary Janosko) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2004-02-18
40519 | -1 | WATERFORD | 3 |  |  | [3] CE | 2004-02-13 05:25 | 2004-02-13 20:32 | 2004-03-15 | 24 HOUR NOTIFICATION PER LICENSEE CONDITION 2.F "On February 13, 2004, Waterford 3 reactor power reached an estimated maximum reactor power level of 101.9% due to Atmospheric Dump Valve #2 (ADV#2) failing full open. ADV#2 failed open due to the control system setpoint failing low. Operations personnel promptly responded to the condition by reducing turbine load (5 megawatts per minute ) and manually closing ADV#2, to restore plant power. ADV#2 was open for less than a minute. Per the FSAR, this transient is an analyzed event and is bounded by the safety analyses. This event is being reported in accordance with Waterford 3 event notification and reporting procedure, UNT-006-010, which is more conservative than the guidance provided in NRC Inspection Procedure 61706. This event is being reported pursuant to Waterford 3 License Condition 2.F as a 24 hour notification." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM R. MURILLO TO M. RIPLEY 2100 ET ON 03/15/04 * * * "On February 13, 2004, Waterford 3 provided a 24 hour notification to the NRC (reference EN# 40519) stating that due to a failed open atmospheric dump valve, plant reactor power level momentarily reached a value of 101.9%. The event was reported conservatively based on the guidance provided in the plant's event notification and reporting procedure. The procedure has been revised to incorporate the guidance provided by NRC inspection Procedure 61706, 'Core Thermal Power Evaluation.' Based on this guidance, reporting of events such as stated above (transient power increases) are not required unless reactor power level exceeds 102%. Accordingly, this event is not reportable as power level only reached 101.9% momentarily. "Based on the above, the 24 hour notification made on 2/13/2004 is being retracted." The licensee has notified the NRC Resident Inspector. Notified R4 DO (J. Clark) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | LA | POW | [5 empty] | 0 | 2004-02-13
40518 | 0 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-02-13 07:30 | 2004-02-13 11:49 | 2004-02-13 | LOSS OF OFFSITE COMMUNICATIONS At 0730, Monticello Nuclear Generating Plant became aware of the loss of incoming phone call capability. Investigation determined loss of ENS, HPN (FTS) lines were inoperable as well as the State of MN dedicated line. Commercial incoming calls (inoperable) out calls were operable. By 0930 CST all phone system were restored and determined operable. NRC Operations Center was notified of inoperable ENS phone via backup commercial line. NRC Resident Inspector was notified of this by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-13
40517 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2004-02-13 08:10 | 2004-02-13 11:00 | 2004-02-13 | RPS ACTUATION DUE TO LOW STEAM GENERATOR LEVEL "At 0810 CST on 2-13-2004, all four Steam Generators alarmed with Steam Flow/Feed Flow Mismatch alarms, followed by indication of decreasing level in "D" Steam Generator. The reactor tripped approximately 20 seconds later on Lo-Lo level at 23.5% in "D" Steam Generator, as required. The cause of the loss of feedwater flow to "D" Steam Generator is under investigation. "All plant safety related systems operated as required. The Steam Dumps, which function to remove excess heat as the secondary systems shutdown, exhibited control problems resulting in operation of the Steam Generator Atmospheric Relief Valves (ARVs) until the steam dump controller setpoint was adjusted and the steam dumps began to operate normally. The steam dumps are currently operating in automatic. The Steam Generator ARVs closed when the steam dumps began to operate. "The auxiliary feedwater system actuated as designed, and a Feedwater Isolation signal was generated as designed on Lo-Lo Steam Generator Level. "The plant is currently stable in Mode 3 at NOP and NOT while plant personnel investigate the causes of the trip and formulate the repair/restart plan." Decay heat is currently being removed via the steam dumps. The plant electrical system responded normally and all emergency diesel generators remain in standby. There are no primary to secondary leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-02-13
40516 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-02-12 17:45 | 2004-02-12 21:14 | 2004-02-12 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) OUT OF SERVICE FOR MAINTENANCE. "The Safety Parameter Display System (SPDS) was removed from service on February 12, 2004, at 1745 CST, to support planned maintenance on uninterruptible power supply (UPS) 1B. SPDS will be out of service for greater than eight hours. The UPS 1B provides power to the Nuclear Steam Supply (NSS) Computer, which provides the computer points for SPDS. The UPS 1B outage is scheduled for approximately twenty-eight (28) hours. Operators are taking compensatory measures for monitoring parameters. "10CFR50.72(b)(3)(xiii) states 'the licensee shall notify the NRC as soon as practical and in all cases within 8 hours of the occurrence of any event that results in the major loss of emergency assessment capability.' "The loss of SPDS is considered a major loss of safety assessment capability. The site defines a 'major loss' of SPDS, 'when the SPDS function is not available in the control room for greater than eight hours.' This is consistent with NUREG-1022, EVENT REPORTING GUIDELINES 10CFR 50.72 and 50.73 section 3.2.13, Loss of Emergency Preparedness Capabilities. "SPDS is expected to be restored to service on February 13, 2004. The plant is in a refueling outage. All other plant conditions are normal in support of the refueling outage. The NRC Resident Inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-02-12
40515 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-02-11 22:58 | 2004-02-12 03:51 | 2004-02-12 | ECCS ACTUATION DURING RCS HEATUP "At 2258 (CST) on 02/11/04, Callaway Plant was performing a heat up of the Reactor Coolant System in Mode 3 using plant procedure, OTG-ZZ-00001. When performing Section 6.4 of OTG-ZZ-00001, a Steam Line Pressure Safety Injection was initiated due to the automatic resetting of permissive P-11 at 1970 psig Reactor Coolant System pressure with steam line press less than 615 psig. Actual steam pressure was approximately 600 psig, 15 psig below the Steam Line Pressure Safety Injection set point. As a result of the Safety Injection [signal], the following safety related systems actuated: Safety Injection, Residual Heat Removal, Auxiliary Feedwater, Essential Service Water, and both of the Emergency Diesel Generators. During the injection phase, Pressurizer water level increased to approximately 98 percent and pressurizer pressure increased above the Pressurizer Power Operated Relief Valve (PORV) set point causing the PORVs to operate. During the operation of the PORVs, an open alarm for a Pressurizer Safety Relief Valve actuated, however, there are no indications that this valve actually opened. Initial indications are that a valve position limit switch has malfunctioned. "All systems responded as expected during the event with the exception of the above mention Pressurizer Safety valve position indication problem and one Steam Generator Atmospheric Safety Valve that would not operate properly in Manual. At present, the plant is being stabilized using plant procedures. Both Emergency Diesel Generators are in standby and the primary system is at 500 degrees F and 1900 psig with Pressurizer level at 25%." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-02-12
40514 | 0 | TENNESSEE DIV OF RAD HEALTH |  |  |  |  | 2004-02-04 12:00 | 2004-02-11 15:25 | 2004-02-12 | AGREEMENT STATE REPORT INVOLVING A SPILL OF IODINE-131 (UNPLANNED CONTAMINATION EVENT) "TDRH was notified on 02/11/04 of a spill involving I-131 at the Cardinal Health pharmacy in Chattanooga, TN. This event occurred during the afternoon on 02/04/04. An employee was transferring a stock bottle containing 97 millicuries of I-131 from the glove box to the fume hood. The employee dropped the lead pig and the contents of the vial were spilled. Two employees cleaned the area for approximately 20 minutes. Air samples were collected and bioassays of the workers were performed. The room was immediately closed off and access by personnel limited to once a day to collect air sampling media. The initial bioassay results were above the licensee's action limits but below regulatory limits. As of 02/10/04, bioassays results were below the licensee's action limits. The initial air sample collected 18 hours after the spill indicated a stack concentration of 6.5E-08 microcuries/ml. The area will remain restricted, under negative pressure, with fume hoods running. TDRH was notified by the Senior Manager of Health Physics from the corporate office in California. A written report from the licensee will be submitted within 30 days. This incident is reportable under 1200-2-5-.141(c)1(i) of" State Regulations for Protection Against Radiation". Event Report ID No: TN-04-013 Media attention: None * * * UPDATE FROM SHULTS TO GOTT AT 0905 (EST) ON 2/12/04 * * * "The correct license number is R-33111. The correct reference in 'State Regulations for Protection Against Radiation' should be 1200-2-5-.141 (2) (c) 1. (i)." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | TN | OTH | AGR |  |  |  |  | 0 | 2004-02-16
40513 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2004-02-10 10:20 | 2004-02-10 15:09 | 2004-02-10 | MAJOR LOSS OF COMMUNICATIONS AT THE EOF At approximately 10:20 AM on 2/10104 it was reported to the St. Lucie plant site that there were problems with the phone lines at the St. Lucie Emergency Off-Site Facility (EOF). Site personnel went to the facility and determined that the primary methods for NRC (Emergency Notification System-ENS) and State (Hat Ring Down-HRD) notification and most of the commercial phone lines were not functioning. However, backup methods for NRC and State notification including 3 commercial phone lines remain functional at the Emergency Off-Site Facility. There was no effect on site communication capability. The event appears to be due to work by the local phone company which severed a fiber optic transmission cable in the vicinity of the Emergency Operating Facility. The telephone company is currently working to restore normal communications capability. This eight (8) hr. phone notification is being made pursuant to 10CFR50.72(b)(3)(xiii) due to significant loss of portions of the off-site notifications system. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 02/10/04 BY JOE HESSLING TO C GOULD * * * All phone lines restored as of 2230 EDT to the EOF. The NRC Resident Inspector will be notified. Informed the Reg 2 RDO (Lesser) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-02-10
40512 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-02-08 08:30 | 2004-02-10 13:08 | 2004-02-10 | LICENSEE MADE OFF SITE NOTIFICATIONS TO OTHER GOVERNMENT AGENCIES DUE TO A LIME SPILL. The licensee notified the Coast Guard, National Response, Connecticut Department of Environmental Protection and local and state emergency planning commissions that a lime spill into their discharge canal occurred during dredging operations. The licensee had no information on the quantity of the spill or the area it covered. Some went onto the soil on the bank of the canal, some went onto the ice on the surface of the canal and some went into the water in the canal. Cleanup is ongoing and should be completed in a couple of days. The licensee notified the lead NRC Inspector | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-10
40511 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-02-10 | 2004-02-10 11:12 | 2004-02-10 | LOAD OF WASTE ARRIVING AT A WASTE-TO-ENERGY FACILITY SET OFF RADIATION MONITORS A load of waste or recycle materials that had been transported to Covanta Haverhill, Inc (a waste-to-energy facility) in Haverhill, MA had a radiation measurement of 0.13 mrem/hr when it entered the facility. The driver of the truck was told to return the load back to its origin, BFI facilities, in Peabody, MA without any stops. Once at the origin of the shipment, the load is to be isolated until mitigation by a consultant. A report detailing material identification and disposition shall be submitted to the MA Radiation control Program. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-02-13
40510 | 0 | PMK GROUP |  |  |  |  | 2004-02-09 12:30 | 2004-02-10 11:02 | 2004-02-10 | DAMAGED/MISSING DENSITY GAUGE AT DEMOLITION SITE The licensee reported a damaged/missing Humboldt Density Gauge at a demolition site located in East Orange, New Jersey near the intersection of Gould Avenue and Steuben Street. The gauge was a model HS-5001 with a serial number of 2822. The source contains less than 11 millicuries of Cs-137 and less than 44 millicuries of Am-241:Be. Only the gauge faceplate was found and no other parts including the radioactive source. The licensee performed a radiological survey and did not detect any levels greater than background. The licensee started interviews to determine what happened and where the remaining parts are located. The licensee notified the NRC Region I office on 2/9/04 and two NRC inspectors were arriving onsite at the time of this report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | NJ | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-02-10
40509 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-02-09 19:00 | 2004-02-09 19:52 | 2004-02-09 | VOLUNTARY REPORT OF A PRESS RELEASE On 2/9/04 PPL issued a Press Release concerning the NRC decision to send an Inspection team to investigate the cause of the loose bolts found on one of the Emergency Diesel Generator and two other events involving Emergency Diesel Generators at the Susquehanna site. The NRC Resident Inspector was notified. | 85 | 100 | 0 | 85 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW | [5 empty] | 0 | 2004-02-09
40508 | 0 | ST LUKES HOSPITAL |  |  |  |  | 2004-02-04 | 2004-02-09 14:17 | 2004-02-09 | LICENSEE REPORTED A SEALED ACRYLIC ROD SOURCE CONTAINING AM-241 WAS UNACOUNTED FOR DURING AN INVENTORY MADE IN THE SPRING OF 2002. The licensee reported that in the Spring of 2002 a six microcurie Am-241 source was unaccounted for during an inventory check. The item was a New England Nuclear model NES-136T sealed acrylic rod source which was purchased in 1979. It was initially thought at the time it was unaccounted for to have a half life of 433 days, therefore, being exempt from being reportable. However, during a meeting attended by the RSO last week, a discussion of AM-241 half life informed him that it is 433 years not 433 days as he had assumed in 2002 of the unaccountable source. This change in half life value made the incident reportable. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-02-09
40507 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-02-05 17:01 | 2004-02-05 18:32 | 2004-02-05 | OFFSITE NOTIFICATION TO THE MISSOURI PUBLIC SERVICE COMMISSION "At 1701 [CST] on 02/05/2004, a report was made to the Missouri Public Service Commission (MPSC) to notify the MPSC of a forced outage at the Callaway Nuclear Plant. This notification is reportable under 4CSR240 20.080(3)(B) because the outage is expected to last longer than 72 hours. At 0439, 02/03/04, Callaway Plant experienced a reactor trip while operating transmission breakers located in the plant switchyard. It was determined on 02/05/2004 that the outage was expected to last longer than 72 hours." The Licensee will inform the NRC Resident Inspector of the MPSC notification. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-02-05
40506 | -1 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2004-02-05 13:40 | 2004-02-05 15:45 | 2004-03-04 | EMERGENCY DIESEL GENERATOR VENTILATION EXHAUST DAMPER COVERED WITH SNOW AND ICE "During performance of a weekly preventive maintenance activity, [it was] discovered that the discharge dampers of Emergency Diesel Generator 102 Exhaust Fans opened approximately one inch vice full open as expected. Technical Specification 3.6.3e 14 day shutdown LCO was entered at 13:40. At 1350, Technical Specification 3.6.3e(1) was entered due to as found condition of both ventilation exhaust dampers for Emergency Diesel Generators 102 and 103 covered with snow and ice preventing normal operation of dampers. This condition required an initiation of normal orderly shutdown in one hour and the Reactor in cold shutdown condition within ten hours. At 14:10, Emergency Diesel Generators 102 and 103 were declared operable based on snow/ice removal and satisfactory completion of testing on all fans and dampers." The Licensee notified the NRC Resident Inspector. ***** Event Retracted. From Hicks to Taylor on 3/4/04 at 1020 EST***** "This Event Notification is being made to rescind previous Event Notification made on 2/05/2004. The notification was made as an eight hour report per 10 CFR50.72 (b)(3)(v)(D) and an LER IAW 10CFR50.73(a)(2)(v)(D) and (vi). "Subsequent Engineering evaluation has concluded that the Emergency Diesel Generators (EDGs), and more specifically their Room Ventilation Fans (Support System) would have performed their design function. "The specific event described a snow and ice condition that impeded the Ventilation Fan Dampers from fully opening. The dampers did however, partially open. Engineering has concluded that although there was reduced ventilation flow through the dampers, the air flow rate through the reduced exhaust fan opening would have melted the snow and ice. The melting would have occurred at a progressively faster rate (as the exhaust flow rate and room air temperature both increased) and eventually provided adequate ventilation flow to maintain normal room temperature." Notified R1DO (Todd Jackson). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-02-05
40505 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-02-03 18:25 | 2004-02-03 19:24 | 2004-02-04 | SAFEGUARDS REPORT "Discovered vulnerability in a safeguard system that could allow unauthorized or undetected access to safeguards material for which compensatory measures have not been employed. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details." * * * * RETRACTION FROM D. RITTER TO M. RIPLEY 1748 ET 02/04/04 * * * * "Seabrook Station is retracting the one-hour notification made at 1924, 3 Feb 04 under EN # 40505. Upon further review of reporting criteria, the incident will be documented in the station's Security Event Log." The licensee will notify the NRC Resident Inspector and NRC Region 1 office. Notified R1 DO (J. Kinneman) and NSIR TAS (A. Danis). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 0 | 2004-02-03
40504 | 0 | SAN ONOFRE |  | 2 | 3 | [1] W-3-LP,[2] CE,[3] CE | 2004-02-03 11:30 | 2004-02-03 19:05 | 2004-02-03 | LICENSEE REPORTED A FISH KILL INVOLVING APPROXIMATELY 13,590 POUNDS OF SARDINES Section 4.1 of Appendix B of the Operating License for Units 2 and 3 requires Southern California Edison (SCE) to report to the NRC within 24 hours any unusual or important environmental events, which includes unusual fish kills. Between February 2 and February 3, 2004, SCE removed an unusually large number of sardines from the Units 2 and 3 intake structure. At approximately 1100 on February 3, 2004, SCE determined the quantity to be approximately 13,590 pounds (approximately 6940 pounds from Unit 2 and 6650 pounds from Unit 3). While the NRC has not specified a reporting limit for an unusual fish kill, SCE has internally defined this quantity as 4500 pounds. SCE believes the unusual influx of sardines may be related to current winter storm conditions. The NRC Resident Inspectors have been notified The licensee will also give a courtesy call to the San Diego Regional Water Quality Control Board | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation | NON EMERGENCY | 4 | CA | POW | [5 empty] | 0 | 2004-02-03
40503 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2004-02-03 15:35 | 2004-02-03 18:52 | 2004-02-03 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO RCS PRESSURE BOUNDARY LEAKAGE "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On February 3, 2004 at approximately 14:18 MST, Palo Verde Nuclear Generating Station (PVNGS) Unit 1 identified reactor coolant system (RCS) pressure boundary leakage. PVNGS Unit 1 was in Mode 1 (Power Operation) at 99% power with normal RCS temperature and pressure at the time of discovery. A normal reactor shutdown was commenced at 15:35. Technical Specification Limiting Condition for Operation 3.4.14 (RCS Operational Leakage) allows no pressure boundary leakage and requires the plant to be in Mode 3 (Hot Shutdown) within 6 hours and Mode 5 (Cold Shutdown) within 36 hours and TLCO 3.14.103 (Structural Integrity). "The leakage was discovered on a High Pressure Safety Injection Drain Valve (SIA-V056) with is connected to the RCS loop 1 hot leg and is non isolable. The location of the leak is at a weld on the valve socket weld and is estimated at 10 drops per second. "No automatic or manual reactor protection system or engineered safety features actuations occurred and none were required. There were no other component failures, testing or work in progress that contributed to the leak. The leak is located within the containment building, therefore there is no release of radioactivity to the environment and no impact to the health and safety of the public. There is no elevated RCS activity and heat removal is via normal steaming to the main turbine condenser, The electric grid is stable." The licensee has notified the NRC resident Inspector. | 45 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | DEGRADED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(A) |  |  | 0 | 2004-02-03
40502 | 0 | MERCY HEALTH SYSTEM |  |  |  |  | 2004-01-23 | 2004-02-03 14:05 | 2004-02-06 | HIGH BACKGROUND READINGS FOUND IN STERILIZATION WATER USED TO STERILIZE THE SEEDS AND CARTRIDGE PRIOR TO USAGE. The licensee reported that during the completion of a prostate implant a higher than background reading was measured in the sterilization water used to sterilize the seeds and the cartridge prior to the implant. The licensee had two extra seeds left over after the implant, so they returned them to the manufacturer along with a sample of the sterilization water to be analyzed. The manufacturer suspects that one of the seeds may have been a leaking, but that has not yet been verified. A bioassay was also performed on the staff involved with the implant and only the physicist had a higher than background reading. The patient was also given a bioassay, but since they have never done this to a patient, there was no data to compare with. * * * UPDATE AT 0930 EST ON 2/06/04 FROM J. BABU TO GOTT * * * The licensee reported that a second patient also had a higher thyroid bioassay but his urine sample tested negative. The licensee is continuing with their investigation. Notified NMSS (Psyk) and R1DO (Kinneman) * * * UPDATE AT 1431 EST ON 2/06/04 FROM J. BABU TO A. COSTA * * * Detectable contamination was found upon surveying the left over seeds (12 to 18) from the second patient. Two swipes were taken of all seeds together and the first swipe indicated 809 counts per minute and the second swipe indicated 1689 counts per minute. Background readings was 4 counts per minute. The contamination was localized to the cartridges and seeds. The appropriate areas of the Hospital were surveyed and no detectable contamination was found. The licensee intends to keep the leaking iodine seeds in storage for decay and future disposal. Notified NMSS (Hickey) and R1DO (Kinneman) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | HOS | [5 empty] | 0 | 2004-02-03
40501 | 0 | ST. JOSEPHS WAYNE HOSPITAL |  |  |  |  | 2004-01-13 | 2004-02-03 11:26 | 2004-02-03 | TWO I-125 SEEDS UNACCOUNTED FOR FOLLOWING SURGERY On 1/13/04 a male patient received I-125 implants. Following the operation, the physician did not properly inventory the residual I-125 seeds. Two (2) seeds were missing (0.36 millicuries/ea). St. Josephs Wayne Hospital was informed of the discrepancy by the physician performing the operation and conducted extensive surveys with negative results. Corrective action includes an administrative requirement to have either a dosimetrist or physicist present during all future implant operations to ensure adequate inventory control. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2004-02-03
40500 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-02-03 04:39 | 2004-02-03 09:24 | 2004-02-03 | AUTOMATIC REACTOR TRIP DUE TO MAIN GENERATOR OUTPUT BREAKERS OPENING. "AT 0439, 02/03/04, Callaway Plant experienced a reactor trip while operating transmission breakers located in the plant switchyard. Auxiliary feedwater actuated as expected to stabilize steam generator water levels. All other plant systems responded as expected. At present, the cause of the reactor trip is undetermined. Initial indications are that there were no voltage or frequency perturbations on the electrical grid. Plant staff is investigating potential areas in an effort to identify the cause of the trip." The main generator output breakers opened when one of the transmission breakers in the switchyard was opened per the scheduled maintenance test. When the incoming Transmission line breaker was opened it should not have caused the main generator output breakers to open. All rods fully inserted into the core. Both Motor Driven Auxiliary Feedwater pumps automatically started on a loss of both main feedwater pumps and the Turbine Driven Auxiliary Feedwater pump started on low low steam generator water level. The "C" Steam Generator atmospheric steam dump valve opened for about 17 seconds before it closed (no leaking steam generator tubes in the "C" Steam Generator). All Emergency Core Cooling systems are fully operable except for the "A" Safety Injection System. It was declared inoperable when it failed a valve test last night at 0205 CST. All Emergency Diesel Generators are fully operable. Turbine Driven Auxiliary Feedwater Pump discharge valves were closed after it had operator for about two hours. Approximately one hour after the valves were closed the Turbine Driven Auxiliary Feedwater pump tripped. This incident is being investigated. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-02-03
40499 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-02-02 04:15 | 2004-02-03 03:06 | 2004-02-03 | FAILURE OF C-360 #1 AUTOCLAVE HIGH PRESSURE ISOLATION SYSTEM. At 0415 on 02-02-04 the Plant Shift Superintendent (PSS) was notified of a failure of the C-130 # 1 Autoclave High Pressure Isolation System. Water was observed leaking from the autoclave head-to-shell interface near the six o'clock position shortly after initiating a cylinder heat cycle. At the time of discovery, the autoclave was in TSR Mode 5 (heating) and the High Pressure Isolation System was required to be operable while in this mode. This system is designed to provide containment of the autoclave and prevent an external release of UF6 during a system breach while heating a UF6 cylinder. The PSS declared the system inoperable and TSR LCO 2.1.3.1.C.1 actions were implemented to remove the autoclave from service and place it in Mode 2, "Out of Service". The event is reportable as a 24 hour event, as required by 10 CFR76.120(c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specific limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. The Senior NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-02-03
40498 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-02-02 09:01 | 2004-02-02 17:33 | 2004-02-02 | FITNESS FOR DUTY A contractor foreman/supervisor was determined to be under the influence of alcohol during a pre-access FFD test as part of processing for unescorted access. The supervisor was denied unescorted access to the protected area. Contact the HOO for additional details The licensee notified the NRC Resident Inspector. | 87 | 100 | 0 | 87 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2004-02-02
40497 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-02-02 08:35 | 2004-02-02 16:41 | 2004-02-02 | FITNESS FOR DUTY A licensed operator was determined to be under the influence of alcohol during a random test. However, it was below the 10CFR26 cut-off level but could have resulted in the individual being unfit for scheduled work activities. The employee's access to the plant has been put on fitness-for-duty hold pending resolution. Contact the HOO for additional details. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 26.73 |  |  |  | 0 | 2004-02-02
40496 | 0 | BRUNSWICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-12-21 22:04 | 2004-02-02 10:55 | 2004-02-02 | INVALID REACTOR BUILDING EXHAUST RADIATION MONITOR SIGNAL RESULTING IN PCIS ISOLATIONS "This report is being made in accordance with §50.73 (a)(1), which states, in part, 'In the case of an invalid actuation reported under §50.73 (a)(2)(iv), other than actuation of the reactor protection system (RPS) when the reactor is critical, the licensee may, at its option, provide a telephone notification to the NRC Operations Center within 60 days after discovery of the event Instead of submitting a written LER.' These invalid actuations are being reported under §50.73 (a)(2)(iv)(A). NUREG-1022, Rev. 2, states that the report should provide the following information: - The specific train(s) and system(s) that were actuated - Whether each train actuation was complete or partial - Whether or not the system started and functioned successfully. "On December 21, 2003, at 2204 hours, the Reactor Building Exhaust Radiation Monitor (i.e., 1-D12-RM-K609B) signal input spiked resulting in the invalid actuation of the logic associated with the instrument channel. The actuations included the Primary Containment Isolation System (PCIS) Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems) valves, the Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation) and the automatic start of both Standby Gas Treatment (SGT) System trains A and B. The actuations of PCIS Group 6 valves and Reactor Building Ventilation System isolation were complete and the affected equipment responded as designed to the invalid signal (i.e., the valves and dampers that were open, at the time of the event, closed). Additionally, SGT System trains A and B started and functioned successfully. After verification of the expected equipment responses, 1-D12-RM-K609B was reset, the actuation logic was reset, and the equipment/systems were returned to the status required by plant conditions. A radiological survey of the monitored area was completed with no abnormal conditions noted. "Discussion of the causes and corrective actions associated with this event are documented in the corrective action program in action request (i.e., AR) 114005. The resident inspector has been notified." | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-02-02
40495 | 0 | LASALLE |  | 2 |  | [1] GE-5,[2] GE-5 | 2004-02-01 22:34 | 2004-02-02 02:25 | 2004-02-02 | ONE HALF SCRAM SIGNAL DUE TO THE LOSS OF THE "B" REACTOR PROTECTION SYSTEM BUS. This report is being made pursuant to 10 CFR50.72(b)(3)(iv)(A), system actuation not including Reactor Protection System; due to a trip of the "D" Electric Power Monitoring Assembly on the "B" Reactor Protection System Motor Generator set resulting in a trip of the "B" Reactor Protection System bus. The loss of "B" Reactor Protection System bus caused the actuation of multiple Primary Containment Isolation Systems. Station abnormal procedures have been entered and the plant stabilized. The system actuations that occurred have been verified and restorations of these systems are in progress. Troubleshooting plans are being developed to determine cause of the trip and to correct the deficient condition. The NRC Resident Inspector was notified of this event by the Licensee. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-02-02
40494 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-02-01 04:00 | 2004-02-01 09:54 | 2004-02-01 | HIGH PRESSURE COOLANT INJECTION DECLARED INOPERABLE BUT REMAINS AVAILABLE. During the Unit 3 scram on 01/30/04 the response of the feedwater level control system caused the RPV (Reactor Pressure Vessel) level to increase higher than expected. RPV level rose above the HPCI steam line. Calculations showed approximately 60 gallons of water entered the steam line. This response could adversely affect the HPCI system should the same type of event occur and FWLC (Feedwater Level Control) respond the same way on Unit 2. Based on this information and no reasonable assurance that the same response will not occur, the Unit 2 HPCI system is conservatively being declared inoperable. HPCI remains available. Entering Tech Spec 3.5.1 Required Action F.1 (Isolation Condenser is OPERABLE) and F.2 (Restore HPCI to Operable status within 14 days). A modification is being prepared to change the response of FWLC to preclude this adverse response during a transient. The NRC Resident Inspector will be notified. | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-02-01
40493 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2004-01-30 18:45 | 2004-01-31 10:59 | 2004-01-31 | CONTRACTOR SUPERVISOR TESTED POSITIVE FOR ALCOHOL At 1845 hrs on 1/30/04 a contractor supervisor tested positive for alcohol during a for cause fitness-for-duty drug test. The test was administered prior to the individual entering the Protected Area (PA). Site access has been terminated and he was removed from plant access. There was no impact on the plant or plant systems due to this condition. The licensee informed the NRC Resident Inspector and the Illinois Department of Nuclear Safety (IDNS) representative. Contact the Headquarters Operations Center for additional details. | 78 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 26.73 |  |  |  | 0 | 2004-01-31
40492 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-01-30 09:41 | 2004-01-30 18:40 | 2004-01-30 | SAFETY EQUIPMENT FAILURE At 0941 CST on 1/30/04, the Plant Shift Superintendent (PSS) was notified that High Pressure Fire Water System, C-1, in C-333 building was discovered to be in a potential frozen condition on the system main supply header standpipe. Frozen water in the standpipe could result in the restricted flow or complete loss of water supply to the sprinkler heads. The PSS declared the system inoperable and TSR LCO 2.4.4.5 actions were initiated to remove the system from service. Freeze out of the system was due to extremely low outside ambient temperatures and a faulty filter room thermostat. The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. The faulty filter room thermostat was replaced, and the High Pressure Fire Water System was declared operable at 1500 CST. Operations personnel took compensatory measures by checking similar indicators in all process buildings. The Senior NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-01-30
40491 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-01-30 11:55 | 2004-01-30 14:35 | 2004-01-30 | RPS ACTUATION WHILE CRITICAL Unit 3 experienced an automatic reactor scram due to a main turbine trip. The main turbine tripped due to low oil pressure, the cause of which is under investigation. Primary Containment Isolation System Group 2 and 3 isolations occurred as expected due to the reactor water level decrease following the scram. After reactor water level was restored to normal (+30 inches), level continued to increase to the reactor feed pump high level trip setpoint. Reactor level was subsequently restored to normal and the reactor feed pumps were restarted and are currently supplying the reactor. Decay heat is being removed by the main steam system via auxiliary loads. All other systems responded as expected. Current reactor pressure is 850 psi, and level is stable at 30 inches. The NRC Senior Resident Inspector is in the control room. | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-01-30
40490 | 0 | US DEPT OF VETERANS AFFAIRS |  |  |  |  | 2004-01-30 11:51 | 2004-01-30 13:26 | 2004-01-30 | MEDICAL EVENT DUE TO ADMINISTERED DOSE EXCEEDING PRESCRIBED DOSAGE TO THE THYROID "The medical event occurred at a medical broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. The permittee is VA Boston Healthcare System, Boston, Massachusetts. "The medical event occurred on January 29, 2004, and was discovered the same day. "The basis for the medical event is under 10 CFR 35.3045(a)(1)(ii) in that an administered dosage differed from the prescribed dosage by more than 20% and resulted in a dose of more than 50 rem to an organ. "Specifically, the verbal order from the authorized user was for 5 microcuries Iodine 131 and the patient was given 500 microcuries Iodine 131. After the event was discovered, the patient was given a thyroid blocking solution. Based on the patient's resultant thyroid uptake, the permittee computed a dose to the thyroid of approximately 83 rem. "The authorized user does not anticipate any adverse medical effects to the patient. "The permittee has implemented initial corrective actions to prevent a recurrence of the circumstances that resulted in the medical event. "The Department of Veterans Affairs will evaluate the circumstances related to the medical event and submit a written report to NRC, Region III, within 15 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | MA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-01-30
40489 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-01-30 11:30 | 2004-01-30 13:26 | 2004-01-30 | UNUSUAL EVENT At 1151 CST, the licensee declared an Unusual Event per chart P. At approximately 1115 CST, while filling the CARDOX carbon dioxide (CO2) storage tank, the tank had reached the full mark and the operator requested the trucker to stop filling the tank. The operator verified tank filling had stopped and isolated the fill line at the tank. The operator then isolated the fill line at the truck bay. The fill line relief valve lifted, causing the vent line to bleed CO2 through a weep hole in the tank room. At 1140 CST, the shift manager was informed that CO2 levels in the tank room were at life threatening levels (40,000 ppm at floor level, 30,000 ppm at waist level). At 1155 CST, the shift manager was informed that CO2 concentration had decreased below life threatening levels. At 1215 CST, no further leakage of CO2 through the weep hole into the room was observed. At 1245 CST, CO2 levels in the CARDOX room and adjacent spaces had returned to at or near normal levels. At 1343 EST, the NRC decided not to enter Monitoring mode. The licensee notified the NRC senior resident inspector, along with state and local authorities. * * * UPDATE AT 1454 EST ON 1/30 2004 FROM J. RISTE TO E. THOMAS * * * At 1346 the Unusual Event was terminated by the licensee. CO2 levels in all areas of the plant have returned to normal working levels. The CO2 release was terminated at 1239 CST. Notified P. Louden, T. McGinty, T. Reis, FEMA, DHS (D. Lewis) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | UNUSUAL EVENT | 3 | WI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-01-30
40488 | 0 | WISCONSIN RADIATION PROTECTION |  |  |  |  | 2004-01-28 | 2004-01-29 14:45 | 2004-01-29 | MISSING NDR, INC. STATIC ELIMINATOR GUN DEVICE. On January 28, 2004 a letter was received by Wisconsin's Radioactive Materials Program, dated January 26, 2004 from state licensee J.K. Display, Inc., 8300 W. Parkland Court, Milwaukee, WI 53223. The letter informed the department that the company could not locate one of the two NDR, Inc., P-2021 Nuclecel-Ionizer air gun devices that it had in its possession.. The missing/loss P-2021 device, serial # A2CL456 was leased from NDR, November 2002 with an activity of 10.0 mCi of Po-210. The static eliminator gun was last used in July of 2003 because it was broken and unusable. Apparently, the connections between the air-hose and device leaked, reducing the gun's ability to produce ionized air. The device was placed in the shop on a shelf for return to NDR, Inc. at termination of the lease. Polonium-210 has a half-life of 138 days, therefore, if the assay date of November 2003 is accurate, the source has gone through approximately three (3) half-lives. The Po-210 source at this point should have an activity of approximately 1.275 mCi. The licensee has done an exhaustive search of the shop and offices for the device, but it cannot be located. The most likely possibility, according to the company, is an employee threw out the device. Corrective actions taken by the company are to instruct their six employees to identify the device(s) and their location at all times and to isolate and store unused device(s) in a secure location. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2004-02-03
40487 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2004-01-28 15:30 | 2004-01-29 13:50 | 2004-01-29 | 24-HOUR CONDITION OF LICENSE REPORT DUE TO INOPERABLE DIVISION II CONTROL ROOM SPECIAL FILTER TRAIN "While attempting to perform the Control Room Special Filter Train Functional Test for Division ll, the required train flow test conditions could not be established. Investigation revealed that the inlet backdraft damper 2HVC*DMPV93 was latched closed and would not open automatically on a Special Filter Train start. "The damper was found latched closed due to an improperly set spring-loaded 'stop.' As a result, the Division II Control Room Special Filter Train was declared inoperable as of 1530 on 1/28/04. Technical Specification 3.7.2, Condition A was entered which allows 7 days to restore the Division II Control Room Special Filter Train to an operable status. "A review of plant computer data and monthly surveillance tests for the Division II Special Filter Train determined that the backdraft damper has been latched closed since October 2003. As a result, the Division Il Control Room Special Filter exceeded Technical Specification 3.7.2 action to restore Control Room Special Filter Train Subsystem to operable within 7 days. This is reportable under 50.73(a)(2)(i)(B) 'Any operation or condition which was prohibited by the plant's Technical Specifications,' and Section 2.F of the Nine Mile Point Operating License. Per Nine Mile Point Operating license, initial notification that the facility is not operated in accordance with the Technical Specifications shall be made within 24 hours to the NRC Operations Center via the Emergency Notification System, with written follow up within 30 days in accordance with 10 CFR 50.73(b), (c), and (e). "A repair plan is being prepared with work to commence today (1/29). Following repairs, surveillance testing will be performed to confirm proper operation of the damper. "An inspection of the redundant Division I Control Room Special Filter Train damper and review of monthly surveillance tests demonstrated that the latching mechanism does not interfere with the ability of the damper to open as designed. Therefore, operability of the Division I Control Room Special Filter Train has been confirmed." The licensee informed the NRC Resident Inspector. | 0 | 97 | 0 | 0 | 97 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2004-01-29
40486 | 0 | SUSQUEHANNA |  | 2 |  | [1] GE-4,[2] GE-4 | 2004-01-28 20:33 | 2004-01-29 00:05 | 2004-01-29 | OFFSITE NOTIFICATION TO LOCAL LAW ENFORCEMENT DUE TO FIRE BRIGADE ACTIVATION "At 2018 hrs, the Control Room was notified of smoke coming from the Unit 2 Vital UPS room. The Field Unit Supervisor (FUS) was dispatched to the room to investigate. At 2026 hrs, the Fire Brigade was activated. When the FUS arrived at the Vital UPS Panel he reported that there was smoke coming from the panel. He opened the panel and observed smoke coming from the transformer in the panel. He did not observe any flames at any time while dealing with the event. At 2029 hrs, Security was notified and subsequently notified the State Police at 2033 hrs. At 2033 hrs, the transformer was deenergized and the smoke began to dissipate. Entry into the Emergency Plan was evaluated and it was determined that no entry conditions exists at this time. "Due to the notification of the Local Law Enforcement Agency, this event constitutes an Offsite Notification and therefore reportable under 10CFR50.72(b)(2)(xi) requiring a 4 hr ENS notification." When the transformer was deenergized, all loads were automatically transferred to the alternate power supply. The loss of this transformer did not affect any safety related equipment and does not require entry into any TS LCO Action Statements. The licensee notified state/local agencies and the NRC Resident Inspector. No press release is planned. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-01-29
40485 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2004-01-28 08:00 | 2004-01-28 10:29 | 2008-05-11 | * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * THE LICENSEE RECEIVED A PACKAGE CONTAINING Cs-137 WHICH EXCEEDED EXTERNAL RADIATION LIMITS BWXT received two type A packages packed inside a larger package from Baker Hughes in Houston, TX on 1/27/04. When they opened the larger package, they discovered that one of the type A packages containing a single 2.5 curie Cs-137 source exceeded the limits (200 mr/hr) for external radiation. The package was measuring 375 mr/hr, however the surface smears were within limits and the package was intact. The seal numbers on the package and manifest matched. The licensee notified both Baker Hughes and the transport company, Emery Worldwide, of the problem. The NRC Resident Inspector was notified. * * * UPDATE ON 05/11/08 BY H. Crouch * * * THIS IS NOT A NEW REPORT. This event report was originally withheld from public release under the NRC's policy for protecting sensitive unclassified information. The NRC has reevaluated this policy and is now making this event report available to the public with suitable redactions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EXTERNAL RAD LEVELS > LIMITS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 20.1906(d)(2) |  |  |  | 0 | 2008-05-11
40484 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-01-27 17:30 | 2004-01-27 22:15 | 2004-01-28 | AUTOMATIC REACTOR TRIP "At 1730, 1/27/04, Callaway Plant experienced a reactor trip. Auxiliary feedwater actuated as expected to stabilize steam generator levels. All other plant systems responded as expected. At present the cause of the reactor trip is undetermined. Initial indications are that there were no voltage or frequency perturbations on the electrical grid and that the trip signal originated from Callaway's switchyard breaker circuitry. Plant staff is currently engaged in a review of all indications that occurred at the time of the trip and systematically investigating potential problem areas in an effort to identify the cause of the trip." The licensee also reported that all control rods inserted on the reactor trip, no primary or secondary system relief valves operated, and that reactor temperature is being maintained using steam dump to the condenser. Steam generator water levels are being maintained using auxiliary feedwater. The station electrical system is available and in a normal configuration. The licensee notified the NRC Resident Inspector. * * * UPDATE 0250 EST ON 1/28/04 FROM EURMAN HENSON TO S. SANDIN * * * The licensee provided the following information as an update to their initial report: "The cause of the reactor trip has been identified as a failed electrical relay in the main generator protection circuitry. The relay is designed to sense a fault in the main electrical generator and trip the generator output breakers. The failed relay was designated as a 321/G relay and provides phase fault backup protection to prevent exceeding thermal limits of the stator windings. "After determining the cause of the reactor trip, preparations for a reactor startup are in progress." The licensee will inform the NRC Resident Inspector. Notified R4DO(Johnson). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-01-27
40483 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2004-01-27 12:00 | 2004-01-27 13:33 | 2004-01-29 | LOSS OF ENS TELEPHONE AND SIREN SYSTEM The licensee reported intermittent problems with the ENS telephone and Early Warning Siren System (EWSS) capability. EWSS capability is less than 75% and is currently 58%. The ENS phone system is repaired. Ice storms are the cause of the communication problems. The licensee notified the NRC Resident Inspector. * * * UPDATE 1138 EST ON 1/29/04 FROM ROBERT SWEET TO S. SANDIN * * * The licensee is updating this report to indicate that greater than 75% of the EWSS capability has been restored. The licensee informed the NRC Resident Inspector. Notified R2DO(Kuzo). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-01-27
40482 | 0 | SAINT LUCIE | 1 |  |  | [1] CE,[2] CE | 2004-01-27 08:05 | 2004-01-27 11:16 | 2004-01-27 | OFFSITE NOTIFICATION OF LOSS OF COMMUNICATIONS "On January 27, 2004, at 0805 hours, the Unit 1 Control Room Bell (Commercial) telephones, Unit 1 State Warning Point / Hot Ringdown phone, the Unit 1 NRC Emergency Notification System phone, and the Unit 1 ESATCOM phone communications capabilities were lost, due to inadvertent severing of cables. The Technical Support Center (adjacent to Unit 1 Control Room), and Unit 2, communications telephones, including the Bell (Commercial) phones, State Warning Point / Hot Ringdown phones, NRC Emergency Notification System phones, and ESATCOM phones, were verified operational and satisfactory. The Unit 1 Cellular Telephone and the Portable (Wireless) Telephone continued to remain operable. The licensee has restored all these temporarily disrupted communications capabilities as of 01/27/04 @ 1100 hours. State and Local Government Agencies, and the NRC Resident, have been notified. "This non-emergency notification is being made pursuant to 10 CFR 50.72 (b)(1)(xi), due to the 'Other Government Notifications' (State & Local Government Agencies), NUREG-1022 Section 3.2.12, and 10 CFR 50.72(b)(3)(xiii), due to the 'Loss of Emergency Assessment, Offsite Response, or Communications Capability,' NUREG-1022 Section 3.2.13." This event had no effect on Unit 2. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation |  | 2 | FL | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2004-01-27
40481 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2004-01-26 14:30 | 2004-01-26 20:20 | 2004-03-23 | RECIRCULATION FAN ALTERATION AFFECTS ACCIDENT MITIGATION "V-ERF-11 ('A' Emergency Filtration Train (EFT) recirculation fan) was found to have an improper alteration affecting the fan's shaft speed, and 'A' EFT was declared inoperable. Concurrently, the #12 Emergency Diesel Generator (EDG) was inoperable for planned maintenance, making 'B' EFT inoperable. This condition is a loss of safety function during a design basis accident, and impacts the ability of the plant to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 1/26/04 AT 2112 EST FROM RASK TO GOTT * * * At 1958 CST the licensee declared the #12 EDG operable and thus the #12 ("B") EFT was also operable. Additionally, at 2010 the licensee declared the #11 ("A") EFT operable. Notified R3DO (Burgess). * * * RETRACTION AT 1043 ON 3/23/04 BLAKESLEY TO GOTT * * * Based on further investigation V-ERF-11 ('A' Emergency Filtration Train (EFT) recirculation fan) would have been able to provide the required flow and would have fulfilled its required safety functions with the improper alterations. Therefore the event was not reportable. Notified R3DO ( O'Brien). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-01-26
40480 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-01-25 17:00 | 2004-01-26 17:11 | 2004-01-26 | HIGH DIFFERENTIAL PRESSURE IN AUXILIARY BUILDING "On January 25, 2004, during troubleshooting of high differential pressure in the Unit 1 Auxiliary Building, the 1ABF13 fire damper was found closed at approximately 1700 (EST) hours. The 1ABF13 fire damper was re-opened and system flows and differential pressure were verified to be normal at approximately 1950 hours." "On January 26, 2004, at 1500 hours, a determination was made that with the 1ABF13 fire damper closed, filtration of the effluents from the pipe chase and RHR areas could not be processed through the HEPA-Charcoal absorber. This condition did not meet the assumptions of the Salem dose analysis and is being reported under the requirement of 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-01-26
40479 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2004-01-23 17:30 | 2004-01-26 13:21 | 2004-01-26 | AGREEMENT STATE REPORT OF OVEREXPOSURE FROM RADIOGRAPHY SOURCE "On 1/26/04, about 8:00 am (CST), [Kansas Department of Health and Environment] KDHE staff retrieved a phone message from the Assistant Radiation Safety Officer (ARSO), of Taylor Forge Engineered Systems, Inc (TFES). The ARSO called on 1/23/04, Friday, about 10:20 pm, stating that one of their radiographers may have received an exposure greater than 5 Rem. This was the initial phone call stating that an unusual event may have occurred. Around 5:30 pm, on 1/23/04, a radiographer was performing radiographic operations in the middle bullpen cell, using a Co-60, 62.1 curie source. According to the radiographer, the gamma alarm malfunctioned, thereby the lights, bells and alarms weren't working. He entered the vault to try and determine the cause of the malfunction, but failed to retract the source, resulting in a possible overexposure to himself. The radiographer was in the area about 10 - 15 minutes. The radiographer contacted the ARSO later that evening and related the above events. "On 1/26/04, about 8:00 am, KDHE staff retrieved a phone message from the Radiation Safety Officer (RSO). The RSO called on 1/24/04, Saturday, about 7:00 am, stating that one of their radiographers had received an overexposure greater than the 5 Rem limit. This was the official 24 hour emergency notification. The radiographer's chirping alarm rate meter and pocket ion chambers (PICs 200 mrems / 500 mrems) were found to be off-scale. The radiographers film badge was overnighted to Landauer dosimetry services for processing. The radiographer has been relieved of his duties as they relate to IR. Preliminary dose calculation estimates, from the RSO, are that radiographer received between 15 - 30 rems whole body and up to 87 rems to the hand. TFES is currently investigating the incident and is trying to recreate the above mentioned conditions (using a dummy source) to determine what happened. KDHE is currently investigating the incident. We will provide updates when they occur." Source: Cobalt 60, 62.1 Curies Manufacturer: AEA Technologies Model Number: TECHOPS A-424-14 Serial Number: S/N 2899 Device: Manufacturer: AEA Technologies Model Number 660-B Serial Number: S/N B-234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2004-01-29
40478 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2004-01-26 09:41 | 2004-01-26 11:15 | 2004-01-26 | UNUSUAL EVENT (TRANSITORY) DUE TO LOW INTAKE BAY LEVEL CAUSED BY ICING "This is a notification of a transitory Notification of Unusual Event. Nine Mile Point Unit 1 experienced a transitory low intake bay level due to icing. This condition was resolved by shifting circulating water flow from reverse flow to normal flow. This met Emergency Action Level 8.4.3 for low fore bay level less than 238.8 feet. The duration of this event was from 0941 (EST) to 0943. "While returning reactor power to 100%, an unrelated problem [plant computer] halted power ascension at 92.4% [from a stable 90% reactor power]." The licensee notified the NRC Resident Inspector and the state and local government through their "warning point" emergency notification system. The Unusual Event was terminated at 0943. | 90 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-01-26
40477 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2004-01-25 22:36 | 2004-01-26 03:50 | 2004-01-26 | LOSS OF EMERGENCY RESPONSE COMMUNICATIONS DUE TO FAILED UNINTERRUPTIBLE POWER SUPPLY "At approximately 22:36 hours EST, on January 25, 2004, the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, Emergency Response Facility Information System (ERFIS) computer system became inoperable due to a loss of the uninterruptible power supply (UPS). The ERFIS computer system provides monitoring and communications capability for plant data systems including the Emergency Response Data System (ERDS), Safety Parameter Display System (SPDS), Meteorological Data link system, FAX modems for Emergency Preparedness functions, and the Inadequate Core Cooling Monitor (ICCM). The loss of ERFIS requires alternate methods as described in plant procedures to be used for these functions, as necessary. Therefore, it is expected that appropriate assessment of plant conditions, notifications, and communications could still have been made as necessary, if required, during the time that the ERFIS was inoperable. The ERFIS computer system was restored at approximately 01:47 hours EST on January 26, 2004, using a back-up power supply. The cause of the loss of the ERFIS UPS has not yet been determined. Plant personnel are continuing to investigate the loss of the power supply and are in the process of repairing the UPS. This report is being made in accordance with 10 CFR 50.72(b)(3)(xiii), which is any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability. As previously stated, alternate means remained available to assess plant conditions, make notifications, and accomplish required communications, as necessary." The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-01-26
40476 | -1 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2004-01-25 11:10 | 2004-01-25 15:26 | 2004-01-26 | INOPERABLE REFUELING INTERLOCK "This report is being made pursuant to 10CFR50.72(b)(3)(v)(A) and 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to Maintain Safe Shutdown and Mitigate the Consequences of an Accident. During Unit 1 refueling operations, it was discovered at 1110 hours 1/25/04 CST that the Refuel Position One-Rod-Out Interlock was inoperable. Because this interlock is credited for mitigating the 'Control Rod Removal Error During Refueling' event evaluated in the UFSAR, this is reportable as an 8 hour ENS notification. "With the Unit 1 Mode Switch in REFUEL, the one-rod-out interlock function was tested per LaSalle Operating Surveillance LOS-RD-SR4. Since the acceptance criterion of this surveillance was not met, the interlock was declared inoperable and the required actions of Technical Specification 3.9.2 entered. Currently all control rod withdrawals are suspended and all control rods are fully inserted in core cells containing fuel assemblies. The Unit 1 Mode Switch is in Shutdown. Actions are in progress to restore the One-Rod-Out Interlock to an operable status." The licensee notified the NRC Resident Inspector. * * * RETRACTION FROM BAILEY TO GOTT AT 1617 EST ON 1/26/04 * * * "During further investigation, it was determined that the system design is such that whenever the Mode Switch is placed in the REFUEL position with a rod withdrawn, no select block is received but a rod withdrawal block is generated. This design feature allows control rods to be inserted should the Mode Switch be placed in REFUEL with any rod out. The LaSalle Operating Surveillance (LOS-RD-SR4) used to demonstrate operability of the Refuel Position One-Rod-Out Block does not currently recognize this design feature and its acceptance criteria is based solely on receipt of the select block. The subject procedure will be revised to ensure all rods are fully inserted prior to performing the surveillance thereby ensuring the logic initial conditions are met to satisfactorily demonstrate the select block function. With these initial conditions satisfied, the Refuel Position One-Rod-Out Interlock was satisfactorily tested on 1/25/04 at 1935 hours CST. Therefore, the Refuel Position One-Rod-Out interlock performed as designed and was capable of performing its safety function. Thus, this occurrence was not reportable under 10CFR50.72(b)(3)(v)(A) and 10CFR50.72(b)(3)(v)(D)." The licensee notified the NRC Resident Inspector. Notified R3DO (Louden). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2004-01-25
40475 | -1 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-01-25 03:16 | 2004-01-25 10:10 | 2004-02-25 | UNPLANNED AUTO START OF TURBINE DRIVEN AUXILIARY FEEDWATER PUMP "At 0316, EST, on 25 January 2004, the Unit 2 turbine driven auxiliary feedwater pump (TDAFWP) was automatically started upon receipt of a valid start signal. The start of the pump was unplanned. At the time, the Unit 2 reactor was critical at [approximately] 0.001 % power as indicated on the Intermediate Range Nuclear Instruments (Unit 2 is emerging from a forced outage following main generator repairs). The steam generators were being supplied water by the motor-driven auxiliary feedwater pumps. "Shift operators were in the process of aligning the Unit 2 condensate system for cleanup and closed both (out of service) main feedwater pumps' suction isolation valves, as required by the procedure. Closure of a main feedwater pump's suction valve generates a main feedwater pump trip signal. Trip of both main feedwater pumps generates an automatic auxiliary feedwater system start signal. "The start of the TDAFWP had no adverse effect on the unit. Operators reset one of the main feedwater pumps and secured the TDAFWP." The Licensee will notify the NRC Resident Inspector. *****RETRACTION ON 2/25/04 AT 1215 EST FROM JONES TO LAURA***** "Background: On January 25, 2004, Unit 2 was being returned to operation following a maintenance outage. Unit 2 was critical (Mode 2) with auxiliary feedwater pumps 2A and 2B in service and both MFW pumps trip buses energized. Operations continued to align the condensate system, on long cycle for clean-up. This alignment requires the closure of the main feedwater pumps suction valves. The main feedwater pumps had already been aligned for service with the trip buses energized. The plant design results in an automatic start of the auxiliary feedwater pumps when both MFW pumps trip buses trip. On January 25, 2004 at approximately 0316 hours, the Unit-2 TDAFW pump automatically started when an operator inappropriately closed the suction valves to both MFW pumps. The closure of the pumps suction valves initiated an invalid AFW pump start signal, resulting in the start of the TDAFW pump and the steam generator level control valves went to automatic. The two motor driven AFW pumps received a start signal though they were already in service for plant startup. This actuation was not the result of actual plant conditions or parameters (there was no feedwater flow through the MFW pumps); rather it was the result of an inappropriate action in closure of the MFW pumps suction valves with both MFW pumps trip buses energized. "This event was originally reported on January 25, 2004 as a valid auxiliary feedwater system start signal. Further review has determined the signal to be invalid as described above. "REPORT: "This event was originally reported on January 25, 2004 as a valid auxiliary feedwater system start signal. Further review has determined the signal to be invalid as described above. The following information is provided in accordance with 10 CFR 50.73(a)(2)(iv)(A): "1. Both the Unit 2 Train A and B motor-driven auxiliary feedwater pumps were running, the turbine driven auxiliary feedwater pump started and the steam generator level control valves went to automatic. "2. Complete train actuation occurred. "3. The turbine-driven auxiliary feedwater pump start and the steam generator level control valves going to automatic were successful." Notified the R2DO (OGLE). The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2004-01-25
40474 | 0 | DRESDEN |  |  | 3 | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-01-24 00:37 | 2004-01-24 03:22 | 2004-01-24 | AUTO REACTOR SCRAM DUE TO AUTO MAIN TURBINE TRIP At 0322 EST on 01/24/03, Licensee reported that at 0037 CST on 01/24/03, the Unit 3 reactor auto scrammed from 96% power due to an auto main turbine trip while performing weekly main turbine testing. All control rods inserted completely. Steam is being dumped to the main condenser. PCIS Group 2 (Containment Ventilation System) and Group 3 (Shutdown Cooling System) isolated as expected due to reactor vessel level decrease following the scram. Reactor vessel level is being maintained at normal level (30 inches) with the reactor feedwater system. Reactor pressure is 900 psig and moderator temperature is 530 degrees F. All systems functioned as expected. Unit 3 is in Condition 3 (Hot Shutdown). The cause of the main turbine trip is under investigation. This event had no effect on Unit 2. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | -1 | N | N | A/R | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode3: Power Operation; FMode3: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-01-24
40473 | 0 | SOUTH TEXAS | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-01-23 16:16 | 2004-01-23 19:42 | 2004-01-23 | AUTOMATIC REACTOR TRIP DUE TO HIGH-HIGH STEAM GENERATOR LEVEL "We make the following report per 10CFR50.72(b)(2)(iv)(B). At 16:16 CST Unit 1 Reactor automatically tripped from full power due to [actual] high-high level in 1B Steam Generator. Prior to the trip, vital distribution panel 1201 lost power when it's normal power supply inverter failed. Steam Generators 1A and 1B levels were selected to instruments from this power supply [and therefore generating a false low level output]. Operators were in the process of taking manual control of 1A and 1B Main Feed regulating valves when the Main Turbine trip was actuated due to the high level in 1B Steam Generator. A reactor trip occurred due to the Turbine Trip above 50% power. The unit is stable at 567 degrees and 2235 pslg. "We also make the following report per 10CFR50.72(b)(3)(iv)(A). Following the reactor trip the Auxiliary Feed Water System automatically actuated on [actual] low steam generator level. This is normal for a trip in the Unit 1 from full power. "The following information is also provided: All control rods fully inserted. No primary reliefs lifted. Technical Specification 3.8.3.1 action b was entered due to the vital distribution panel not being energized from its normal source. (inverter). It is currently power from it's voltage regulator." Decay heat is currently being removed via the steam dumps. The plant electrical system responded normally and all emergency diesel generators remain in standby. All ECCS systems remain operable. There are no primary to secondary leaks. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-01-23
40472 | 0 | CALVERT CLIFFS |  | 2 |  | [1] CE,[2] CE | 2004-01-23 15:29 | 2004-01-23 17:45 | 2004-03-23 | MANUAL REACTOR TRIP WITH SAFETY INJECTION ACTUATION SIGNALS "At 1529 ET the reactor was manually tripped due to low steam generator level as a result of the loss of the 22 SGFP (Steam Generator Feed Pump). When the reactor was tripped, the turbine bypass and atmospheric dump valves went full open and did not shut. This lead to a SIAS (Safety Injection Actuation Signal) and SGIS (Steam Generator Isolation Signal). At 1718 ET, a second SIAS actuation occurred while reestablishing pressurizer level. The cause of the SGFP trip is unknown. The cause of the over steaming on turbine bypass valves and atmospheric dump valves is unknown." All control rods fully inserted. Auxiliary Feedwater initiated normally. The licensee stated that there was no actual ECCS injection to the RCS. The plant electrical system responded normally and all emergency diesel generators remain operable. All ECCS systems remain operable. There are no primary to secondary leaks. Decay heat is currently being removed via the steam-driven auxiliary feedwater pump and the atmospheric steam dumps. As of 1830 ET, primary pressure is approximately 2103 psi and pressurizer level is at 242 inches. Plant conditions are being stabilized at normal hot standby values . The licensee notified the NRC Resident Inspector who responded to the Control Room. * * * UPDATE FROM PACE TO GOTT ON 1/26/04 AT 1438 EST * * * The licensee reported that their post trip review determined that the reactor received an automatic trip about 2 seconds before the manual trip. The automatic trip was due to low steam generator water level. The licensee notified the NRC Resident Inspector. Notified NRR (Reis) and R1DO (Meyer) * * * UPDATE ON 03/23/04 @ 1604 BY DAVID FRYE TO C. GOULD * * * During post event review of the 1/23/04 Rx Trip event (40472), it was discovered that Unit 2 met the entry criteria for EOP-4, Excess Steam Demand event. This condition required declaration of an Unusual Event. No declaration was made at the time because of the transitory nature of the condition. Transitory conditions such as this, however, still require reporting per NUREG-1022, Rev. 2. Immediate notification to the NRC via the Emergency Notification System is required per 10 CFR 50.72(a)(1)(i). The NRC Resident Inspector will be notified. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-01-23
40471 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2004-01-22 17:20 | 2004-01-23 16:10 | 2004-01-23 | AGREEMENT STATE REPORT - STOLEN NUCLEAR GAUGE "The Radiation Safety Officer (RSO) who works for LFR Inc. of Braintree, MA reported his personal pick up truck stolen while on an errand at a gas station-mart in Providence, RI. His pick up truck contained a 4 x 2 foot case which contained his Niton XL series Xray florences gauge [Serial # U-472] which contains about 14 millicuries Cd-109 byproduct material. He left his pick up truck unlocked, and keys on seat, while he went into mart for purchase. "RI state police were notified of theft, and they reported theft to MA state police at approx 5:17 PM [ET] on 1/22/04. MA state police in turn notified a MA radiation control officer at home at approx. 5:30 PM who then notified his MA Radiation Control Supervisor. At 9:39 on 1/23/04 AM, the supervisor notified the RI Radiation Program by e mail that theft had occurred. "A MA radiation control officer, called the RSO at approx. 10:30 AM and 1:50 PM and was told vehicle had not been recovered yet. The RSO was asked to fax MA RCP a copy of police theft report and copy of RI radioactive license, and to call us if vehicle is recovered. The RSO lives in RI. The RSO said he would perform a leak test if tester is ever recovered. "MA sent email to RI Radioactive Materials Program at 2:45 PM with status. Immediate notification requirement means complete investigation is pending." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2004-01-28
40470 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2003-12-31 | 2004-01-23 14:36 | 2004-01-23 | RADIOGRAPHER EXCEEDED ANNUAL RADIATION DOSE LIMIT When film badge dosimetry for December 2003 was processed, it was determined that a radiographer, employed by an inspection firm in Utah but working in Colorado, received an annual radiation dose of 5.035 Rem for the year ending 12/31/03. The radiographer claimed, however, that his film badge had fell on the ground during radiography such that the dose was not actually received. No additional information has been provided at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2004-01-28
40469 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-11-29 15:26 | 2004-01-23 14:05 | 2004-01-23 | INVALID SYSTEM ACTUATION On November 29, 2003, at 1526 hours, the Perry Nuclear Power Plant experienced an actuation of several Division 2 Balance-of-Plant (BOP) inboard isolation valves as a result of the loss of the normal power supply to the Reactor Protection System (RPS) B. At the time of the event, the plant was in mode 1(Power Operations) at about 100% power. The isolation closed one or more valves in each of the following Division 2 subsystems: Main Steam line drains, Fuel Pool Cooling and Cleanup, Liquid Radwaste Sumps, Containment Vessel Chilled WATER, Reactor Water Sampling, Drywell and Containment Radiation Monitoring, and Control Room Ventilation. Instrumentation that receives electrical power from RPS B also lost power. Division 1 components and valves were not affected. The event is considered an invalid system actuation, and is reportable under 10 CFR 50.73(a)(2)(iv)(A). The isolation was not initiated in response to actual plant conditions or parameters, and was not a manual initiation. It meets the criteria specified in 10 CFR 50.73(a)(2)(iv)(B)(2) as a general containment isolation signal affecting containment isolation valves in more than one system. Therefore, notification is being provided via 60-day optional phone call in accordance with 10 CFR 50.73(a)(1). All systems functioned as expected for an inboard isolation. Repositioning of the valves did not present operational concerns; and the valves were re-opened per restoration procedures. The BOP isolation was attributed to the loss of power to RPS B as a result of a blown fuse. The blown fuse was the result of the failure of a GE CR105 contactor due to age related degradation (insulating varnish degradation resulting in a winding to winding short circuit). This event was documented in the corrective action program. Remedial actions included replacement of the failed fuse and the RPS A and B normal power supply contactors and the RPS A alternate power supply contactor. The RPS B alternate power supply contactor will also be replaced. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2004-01-23
40468 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2004-01-23 12:20 | 2004-01-23 13:53 | 2004-01-23 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "Dresden Unit 2 is performing a Technical Specification required shutdown due to the loss of the [120 VAC] Essential Service Bus normal electrical feed. This is reportable per 10CFR 50.72(b)(2)(i), SAF 1.2 "Plant Shutdown Required by Technical Specification". The loss of the feed occurred at 02:10 [CST] on 01/23/04 and power swapped to the backup feed. Technical Specification 3.8.7. A. was entered and repairs began on the uninterruptible power supply. Repairs were unsuccessful and Unit 2 shut down began at 12:20 [CST] with unit required to be hot shutdown by 22:10 [CST] 01/23/04 and cold shutdown by 22:10 [CST] 01/24/04. Repairs will continue in parallel will unit shutdown." The licensee notified the NRC Resident Inspector. ***UPDATE on 01/23/04 at 1742 EST by G. Morrow taken by John MacKinnon**** Unit 2 ESS BUS normal feed was restored to OPERABLE, unit shutdown was secured and preparations for load increase are in progress. Preliminary troubleshooting data taken on the ESS UPS show the most likely cause of the UPS power supply transfer was a static switch component that caused the UPS to swap to the emergency supply. The troubleshooting shows the malfunction that caused the initial power supply transfer to the ESS Emergency supply via the ABT at 0210 this morning originated in the static switch circuitry. The static switch is bypassed in the current configuration and therefore the power supply to the ESS bus is assured. The voltage sensing relays investigated during the troubleshooting on the output of the inverter show no indication that an inverter failure initiated the bus transfer. Operations will continue to monitor the output of the inverter. Troubleshooting of the UPS static switch will continue to determine the cause of the malfunction. R3DO (Roger Lanksbury) notified NRC Resident Inspector was notified of this update by the licensee. | 0 | 95 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-01-23
40467 | 0 | BEST MEDICAL INTERNATIONAL, INC. |  |  |  |  | 2004-01-22 | 2004-01-23 09:45 | 2004-01-23 | MISPLACED SHIPMENT OF I-125 SEEDS The licensee was notified by the Pomona Valley Hospital Medical Center that a package containing 85 I-125 brachytherapy seeds (total activity 40 millicuries) had not arrived as of 1/22/04. The licensee contacted Airborne Express who initiated an investigation. The following information was received earlier at 0245 EST on 1/23/04 from the National Response Center : Airborne Express reported to the National Response Center (Incident # 711334) that a package containing 2.48 GBq I-125 (solid metal form) shipped on 1/20/04 by Best Medical International, Inc located in Springfield, VA had not been received at the Pomona Valley Hospital Medical Center located in Pomona, CA. The Airborne Express Tracking Number 20270858952 shows an arrival scan on 1/21 at their Ontario, CA station. Information provided by their driver shows delivery to the US Post Office in Temecula, CA although Post Office officials assert that the package is not there. Airborne is continuing their investigation and will interview the driver involved. * * * * UPDATE FROM BEST MEDICAL (KRISHNAN SUTHANTHIRAN) TO M. RIPLEY 1238 ET 01/23/04 * * * * The licensee was notified by Post Office officials that the package was found in a post office in City of Industry, CA at approximately 1200 ET 01/23/04. There was no apparent tampering or damage to the package. The package will be retrieved by Airborne Express and either returned to Best Medical International or delivered to Pomona Valley Hospital Medical Center. Notified R1 DO (C. Anderson), R4 DO (L. Howell), and NMSS EO (L. Psyk) * * * UPDATE FROM BEST MEDICAL (KRISHNAN SUTHANTHIRAN) TO M. RIPLEY 1515 ET 01/23/04 * * * * The licensee was notified by Airborne Express that the package was retrieved by them at the post office and was found intact. The package will be delivered to Pomona Valley Hospital Medical Center this afternoon, 1/23/04. Notified R1 DO (C. Anderson), R4 DO (L. Howell), and NMSS EO (L. Psyk) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Transportation Event | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | VA | TRA | [5 empty] | 0 | 2004-01-23
40466 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2004-01-21 | 2004-01-22 17:29 | 2004-01-23 | MEDICAL SOURCES MISSING IN TRANSIT "The Director of Nuclear Regulatory Assurance of Amersham/Medi Physics (IL-01109-01) called late yesterday to report that a package of small activity sources intended for medical use had not arrived at its intended destination. The details are as follows: "On January 9, a package containing sixty-six sealed iodine-125 sources was sent from the Arlington Heights, IL facility intended for the St. John's Riverside Hospital in Yonkers, New York. The sources are stainless steel encapsulations of I-125, each originally 0.942 millicuries of activity. The total activity at the time of packaging was 62 millicuries. The sources are about the size of a grain of rice and designed for implantation in cancerous tumors of the prostate gland via a needle. The package was shipped in a standard 'Type A' box and had a surface dose rate of less than 0.5 millirem/hr. The package was due to arrive in Yonkers on the 12th of January for a treatment on the 14th. As part of Medi Physics customer service, a routine call to the client revealed that the package had not arrived as of the end of the day on the 12th. When the carrier, Federal Express, was queried by the licensee, Federal Express claimed that the package had been accidentally set aside at their Newark, New Jersey facility with some other packages and would be delivered the next day. Additional tracking by Medi Physics on subsequent days showed that the package never left the Federal Express sorting facility in Newark, New Jersey. To date, efforts by Medi Physics and those reported by Federal Express have not located the missing package. "As of this time, the activity of each source is 810 microcurie for a total package activity of 53.5 millicuries. Although in the past such packages have been located and recovered and returned to Medi Physics by the carrier, the extended length of time from the date of expected delivery to now is unusual. Both Medi Physics and Federal Express have indicated they will continue monitoring this situation. The U.S. NRC Region III Liaison Officer has been made aware of the situation and has indicated he will contact his U.S. NRC Region I counterpart to advise him of the situation. "Form of Radioactive Material: SEALED SOURCE Radionuclide: I-125; Source Use: BRACHYTHERAPY; Activity: 53.5E-3 Curies Manufacturer: MEDI+PHYSICS, Model Number: 6711; Serial Number: NA" * * * UPDATE ON 01/23/04 AT 10:27 FROM JOE KINGLER TO ARLON COSTA * * * Federal Express has located the package containing sixty-six sealed iodine-125 sources in Newark, NJ. Federal Express is in the process of returning the package back to Amersham/Medi. Notified R1DO (Anderson), R3DO (Lanksbury) and NMSS EO (Kokajko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2004-01-27
40465 | 0 | US DEPT OF VETERAN AFFAIRS |  |  |  |  | 2003-12-29 | 2004-01-22 15:19 | 2004-01-22 | POSSIBLE MEDICAL EVENT "The possible medical event occurred at a medical broad-scope permittee authorized under the master materials license issued to the Department of Veterans Affairs, NRC License 03-23853-01VA. The permittee is VA Medical Center, Ann Arbor, Michigan (Permit # 21-00159-01). "The possible medical event occurred on December 29, 2003. The possible medical event was discovered on January 21, 2004. "The basis for the possible medical event is under 10 CFR 35.3045(a)(2)(i) and involved administration of a wrong radiopharmaceutical drug. Specifically, the written directive for a patient therapy procedure incorrectly listed Strontium 90 when in fact Strontium 89 was administered to the patient. "Since the clinical intent was for the patient to receive Strontium 89, the possible medical event will not have any adverse impact on the patient. "The permittee has implemented corrective actions to prevent a recurrence of the circumstances that resulted in the possible medical event. The Department of Veterans Affairs will evaluate the circumstances related to the possible medical event and submit a written report to NRC, Region III, within 15 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2004-01-22
40464 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2004-01-16 16:10 | 2004-01-22 09:29 | 2004-01-22 | AGREEMENT STATE REPORT INVOLVING AN ABNORMAL OCCURRENCE (AO) On 11/20/03 a 19 year old female patient received 140.1 millicuries I-131 for thyroid carcinoma as prescribed. At the time she was unaware and had completed the required forms indicating she was not pregnant. On 12/5, 12/8 and 12/11/03 quantitative tests confirmed that she was pregnant. The results were provided to her endocrinologist who recommended that a fetal dose calculation be performed. The hospital was notified and their consultant informed the endocrinologist that the fetus would have received 19.6 rads. The Endocrinologist sent the results to the Center for Human Genetics at University Hospital in Cleveland where as assessment was performed that the pregnancy could safely continue. The Ohio Bureau of Radiation was informed on 1/16/04 and submitted the information to the NRC Region III office. NRC Region III (Lynch) recommended making a telephonic notification due to the incident meeting the criteria of an AO even though Ohio is not required to conform with the revised reporting requirements for a period of three years (October 2005) after the final rule is issued. Hillcrest Hospital has implemented pregnancy testing for child bearing age female patients receiving radiation therapy. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2004-01-27
40463 | 0 | CT DEPT OF ENVIRONMENTAL PROTECTION |  |  |  |  | 2003-12-21 | 2004-01-21 18:10 | 2004-01-21 | MISSING DOUGH DENSITY GAUGE The State of Connecticut Department of Environmental Protection reported that the Pepperidge Farm bakery facility in Norwalk, CT reported that a generally-licensed Kay-Ray (now Thermo Measure Tech, Inc) Model 7060BP density gauge used to measure bakery dough density is missing and presumed sent to a scrap recycler in South Norwalk, CT sometime within the last 4 weeks. Pepperidge Farm is in the process of relocating their facility and the gauge will no longer be used. The gauge contains a 50 millicurie (as of August 1983) Cs-137 source. The State plans on notifying recipients of processed scrap shipped by the scrap recycler. In addition, the State will be conducting a radiation survey of the Pepperidge Farm facility to help confirm that the gauge is no longer at the facility. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-01-21
40462 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2004-01-21 12:30 | 2004-01-21 17:03 | 2004-02-17 | EMERGENCY NOTIFICATION SIREN TEMPERATURE SENSITIVITY "On 1/14/04 a problem with emergency notification sirens was identified and traced to a manufacturing defect in components supplied by Federal Signal Corporation. "Investigations were initiated to determine if this situation was applicable to Callaway. At 1230, 1/21/04, Federal Signal Corporation notified Callaway Plant that there was a potential for siren inoperability due to a temperature sensitive piece of equipment. It was determined that 19 out of 29 emergency sirens were subject to this potential failure if ambient temperatures fall below approximately 20 degrees F. The model number of the questionable sirens is EOWS612. Callaway conducted a "quiet test" of the questionable sirens and 4 of the sirens indicated a problem. At present the ambient temperature is above 32 degree F and it is believed that the four questionable sirens are not experiencing the temperature related failure. A field test of the four sirens is being conducted this evening to determine their operability. Alternate methods of public notification have been established. "The failure mechanism has been identified by the vendor and temporary repairs will begin by 1/22/04." The licensee notified State and local agencies, FEMA, and the NRC Resident Inspector. ****Update on 01/23/04 at 1455 EST by E. Henson taken by MacKinnon**** "This event is an update to EN# 40462 in which Callaway reported that 19 of 29 emergency sirens were potentially susceptible to temperature sensitivity. A field test of four suspect sirens was completed by 1900, 01/21/04, and it was established that all four sirens were operable. All 19 of the emergency sirens using electronic circuits that were potentially susceptible to temperature sensitivity, had temporary heating elements installed on 01/23/04, thus eliminating the temperature sensitivity problem. Federal Signal Corporation expects to have a permanent solution identified and permanent repairs completed within 3 weeks." R4DO (Linda Howell) notified. The NRC Resident Inspector was notified of this update by the licensee. * * * UPDATE ON 02/17/04 AT 13:28 EST FROM R. BARTON TO A. COSTA * * * "This is an update to EN # 40462 in which Callaway reported that 19 of 29 emergency sirens were potentially susceptible to temperature sensitivity. Permanent repairs were completed 2/13/04 to eliminate the temperature sensitivity problem. All affected sirens have been successfully tested." The NRC Resident Inspector will be notified of this update by the licensee. Notified R4DO (Whitten). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-01-21
40461 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2004-01-16 | 2004-01-21 16:28 | 2004-01-21 | KENTUCKY AGREEMENT STATE REPORT ON LOSS OF RADIOACTIVE MATERIAL FOUND AT SCRAP YARD On 1/16/04, the radiation detectors alarmed at the North American Stainless scrap yard, located in Ghent, Kentucky, when a truck entered the scrap yard. The scrap yard radiation detectors indicated 42 microrem per hour. The truck was not accepted and sent back to its origin. The scrap material in the truck came from Industrial Services of America. Investigation determined that a piece of a fixed gauge caused the radiation alarms to set off. Apparently, the gauge went through a shredder. On-contact radiation readings were 35 millirem/hour with the shutter closed and 58 millirem/hour with the shutter open. This was considered a loss of radioactive material and further review will be performed to try to determine the owner of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2004-01-26
40460 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2004-01-19 | 2004-01-21 16:20 | 2004-01-21 | KENTUCKY AGREEMENT STATE REPORT ON A MEDICAL EVENT A medical event occurred on 1/19/04 at the Bowling Green Medical Center located in Bowling Green, Kentucky. Specifically, an inner vascular Brachytherapy treatment was planned. The catheter ran outside the body through an external valve which was inadvertently partially shut resulting in no dose to the target area. As a result, the doctor administering the treatment received .736 gray at his fingertips. Also, the patient received .736 gray to the thigh area. The source involved was 43.14 curies of strontium-90. There was no significant adverse health effects from this event. A review was initiated by the licensee to determine the cause and to initiate corrective actions. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2004-01-26
40459 | 0 | COMANCHE PEAK | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-01-19 14:16 | 2004-01-19 20:07 | 2004-01-19 | FITNESS FOR DUTY 24 HOUR REPORT FROM COMMANCHE PEAK A non-licensed contract supervisor refused to take a fitness-for-duty test resulting in the termination of his site access. Contact the HOO for additional details. The licensee indicated they will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 26.73 |  |  |  | 0 | 2004-01-19
40458 | 0 | DOE RUN COMPANY |  |  |  |  | 2004-01-19 10:30 | 2004-01-19 16:38 | 2004-01-19 | DAMAGED MOISTURE DENSITY GAUGE At approximately 10:30 CSTon 1/19/04, the Doe Run Company, located in Bunker, MO, reported that the source head of a moisture density gauge broke and fell to the floor. The gauge was being used in a slurry density line for mining and milling operations. The gauge is a Texas Nuclear, model SG-5191, gauge containing 500 millicuries of CS-137. The source serial number is B-1319. The licensee indicated that the area was isolated and the gauge manufacturer was contacted for corrective action. The source remained within the gauge head. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 3 | MO | MAT | [5 empty] | 0 | 2004-01-19
40457 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2004-01-19 11:20 | 2004-01-19 15:31 | 2004-02-20 | CERTAIN PLANT DOORS MAY NOT BE ABLE TO WITHSTAND PRESSURE CREATED BY MAIN STEAM LINE BREAK "On January 19, 2004, during on-going analysis of the effects of a Main Steam Line Break using new computer models, an issue was raised involving the capability of plant doors. Specifically, the preliminary analysis for a Main Steam Line Break in the Turbine Building determined that certain doors may not be able to withstand the initial pressure wave caused by a guillotine break of the main steam line. "The preliminary analysis indicates that a pressure wave of approximately 2.7 psi is generated from such a main steam line break, which is more than the capability of several doors isolating safety-related equipment from the Turbine Building. The forces generated from this pressure wave could cause failure of the doors leading to both trains of low voltage switchgear, and the resultant steam environment could potentially render all low voltage AC equipment as well the station batteries inoperable. One train of the high voltage switchgear equipment could also be affected due to failure of the door leading to this room. "Due to the potential loss of both trains of low voltage electrical distribution as a result of a steam line break, this issue is being reported as a non-emergency, 8-hour report in accordance with 10CFR50.72(b)(3)(ii)(B), a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. Current steam line pressures are low enough such that all doors are capable of withstanding any forces resulting from a steam line break. Engineering evaluation of the issue is continuing." The NRC Resident Inspector has been notified of this issue by the licensee. The licensee also plans to make a media/press release regarding this issue. *** UPDATE ON 02/20/04 AT 1022 EST FROM LARRY MYERS TO JEFF ROTTON *** "Further review and evaluation of this issue has determined that the pressure wave from a main steam line break in the Turbine Building results in pressures of less than 1.0 psi. Therefore, the affected doors would be able to withstand this pressure wave with one exception. The one exception is the door to a High Voltage Switchgear Room, which is different from the other doors in that it opens into the Switchgear Room and therefore has a very low capability to withstand a positive pressure in the Turbine Building. However, additional analysis determined that in the event of a main steam line break and possible failure of the door, the resultant environment in the room (i.e., temperature, pressure, and humidity) would be within the capability of the enclosed equipment, and equipment operability would not have been challenged. "Accordingly, this issue is no longer considered an unanalyzed condition that would have significantly degraded plant safety, and therefore the notification made per 10CFR50.72(b)(3)(ii)(B) is retracted." Notified R3O (Gardner) and NRR EO (Reis) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2004-01-19
40456 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2004-01-16 23:16 | 2004-01-16 23:29 | 2004-01-17 | NOUE DECLARED AT OYSTER CREEK DUE TO INTAKE LOW WATER LEVEL The licensee declared a NOUE due to intake water level less than or equal to minus 2.0 feet on the staff. The Oyster Creek EAL table classification used to classify this event is 02. There is no radioactive release in progress. The intake low water level condition is worsened by wind conditions (301 degrees at 26.1 MPH) and low tide. The licensee expects that after low tide (~2330 EST) the intake water level condition will improve. The licensee will notify the NRC Resident Inspector and the State of New Jersey. * * * UPDATE ON 01/17/04 BY R. BABEU TO C GOULD * * * The licensee has terminated the NOUE @ 0130 based on the level being less than -2ft (actual level is -1.5ft) The level is stable and the tide is incoming. The reactor is still at 100% power. The licensee has notified the state and will notify the NRC Resident Inspector. The HOO notified FEMA(David Barton), DHS(Justin Abold), Reg1 RDO(James Noggle), EO(David Matthews) and DIRO Manager(Ho Nieh) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NJ | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-01-17
40455 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-01-16 15:27 | 2004-01-16 21:42 | 2004-01-16 | 24 HOUR NOTIFICATION FOR BULLETIN 91-01 LOSS OF CRITICALITY SAFETY CONTROLS INVOLVING WASTE DRUM "At 1526 on 1-16-04, the Plant Shift Superintendent (PSS) was notified that a waste drum was not characterized and handled properly and handled as fissile waste. This is a continuation of PGDP Event Report No. PAD-2004-003, NRC Event Report 40447. "During the investigation of ATRC-03-4095, container RFD# 215759-20, which had been characterized as NCS [nuclear criticality safety] spacing exempt based on the drum being heterogeneous material, it was identified that this waste drum contained spent alumina material violating NCSA (nuclear criticality spacing analysis] WM0-001. The purpose of this NCSA requirement is to determine if the waste drum requires two independent characterization results. Two independent characterization methods were not utilized for characterization of this drum. "PGDP Assessment and Tracking Report No. ATR 04-0166; PGDP Event Report No. PAD-2004-004. NRC Event Worksheet 40455 Responsible Division: Production Support "SAFETY SIGNIFICANCE OF EVENTS: The control for performing two independent analysis for determining the U235 mass was violated but one drum monitor analysis determined that the drum did contain less than the safe mass for spacing exempt waste drums. Since the process condition was maintained, the safety significance is low but double contingency was not maintained. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIOS) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, two or more waste drums would have to contain greater than 120 grams U235 and not have the proper spacing maintained between the waste drum. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC The process condition relied upon for double contingency for this scenario is mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The drum has been characterized to show that Uranium mass is less than 120g U235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on the requirement that uranium waste material must be characterized to show that the U235 mass of the waste drum is less than 120 grams. This control was not violated and the process condition of mass was maintained. "The second leg of double contingency is based on the requirement that high density uranium homogeneous waste material be characterized using an independent analysis. Since the waste drum material was mistakenly identified as heterogeneous material, only one analysis was performed. Therefore, this control was violated. One drum monitor analysis determining that the waste drum contained less than 120 grams U235. Although the control was violated, the process condition was maintained. Since this scenario relies on two controls on one parameter and this control was violated, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Access to the area has been flagged off and access controlled until drums retagged and properly stored. "The NRC Senior Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-01-16
40454 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-01-16 11:37 | 2004-01-16 13:48 | 2004-01-16 | AUTOMATIC REACTOR TRIP DUE TO TURBINE TRIP "At 1137 hours EST on January 16, 2004, with Watts Bar Unit 1 in Mode 1 at 100 % power, a turbine trip and reactor trip occurred. This is reportable as a 4-hour notification under 10 CFR 50.72 (b)(2)(iv)(B) and an 8-hour notification under 10 CFR 50.72 (b)(3)(iv)(A). In addition, per design, there was auto start of the Auxiliary Feedwater system which is reportable as an 8-hour notification under 10 CFR 50.72 (b)(3)(iv)(A). Plant safety systems performed as designed and the reactor is currently stable in mode 3. "At the time of the trip, plant personnel were performing scheduled Solid State Protection System (SSPS) surveillance testing on the B Train Reactor Trip Breaker. Plant personnel are currently investigating the cause of the event." The licensee also reported that all control rods inserted on the reactor trip, no primary or secondary system relief valves operated, and that reactor temperature is being maintained using steam dump to the condenser. Steam generator water levels are being maintained using auxiliary feedwater. The station electrical system is available and in a normal configuration. All ECCS equipment is available. The reactor is currently stable at 2230 psig, 559 degrees Fahrenheit. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2004-01-16
40453 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-01-15 | 2004-01-16 08:06 | 2004-01-16 | PART 21 REPORT INVOLVING AN UNDERSIZED EMERGENCY FEEDWATER PUMP SHAFT FPL Energy Seabrook has determined that a Substantial Safety Hazard could exist regarding an undersized Emergency Feedwater Pump shaft in accordance with the requirements of 10CFR21. Therefore, FPL Energy Seabrook is reporting this deficiency to the NRC in accordance with 10CFR21. This Part 21 evaluation documents a deficiency in a rotating assembly for an Emergency Feedwater Pump refurbished at the Flowserve Charlotte Service Center - Charlotte, NC. The defect was an undersized shaft that was .001 inches smaller than the minimum diameter specified by the vendor. The shaft dimensions are considered to be proprietary by the vendor, so the undersized condition could not be identified by FPL Energy Seabrook personnel prior to installation. The undersized shaft was discovered during post-maintenance testing following shaft replacement. The NRC Resident Inspector will be informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 21.21 |  |  |  | 0 | 2004-01-16
40452 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2004-01-16 00:20 | 2004-01-16 02:01 | 2004-01-16 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO BOTH TRAINS OF SAFETY INJECTION DECLARED INOPERABLE The following information was obtained from the licensee via facsimile: "Inspections of the 'A' SI [Safety Injection] Pump lube oil cooler today per PMP [Plant Maintenance Procedure] 33-01 revealed silt and lake weed accumulation at tube pass inlets. Calculation C11423 Rev. 0, Addendum A was recently performed to determine service water flow and temperature requirements for the safety injection pump lube oil coolers. The calculation provides the required service water flow rate based on number of tubes blocked and SW [Service Water] temperature. At 1640 [hrs][CST], 1/15/04, it was reported that a visual inspection was performed on the 'A' SI Pump HX [Heat Exchanger] tube inlet and 17 of 20 tubes were found to be blocked. The flow for the 'A' HX was 3 - 3.8 gpm and after cleaning elevated to 5.95 - 6.05 gpm. This concern prompted an investigation into 'B' SI Pump HX and a flow test was performed at 1951 [hrs] on 1/15/04. The results from this test was no flow from 17 of the 20 tubes as seen from the outlet of the HX and a similar flow rate as seen in HX 'A'. The determination was made that this had potentially made both trains of SI Pump HX inoperable and that this needed to be reported under GNP 11.08.04 -'Reportability Determinations'. The Calculation (C11423) used data that was contradictory to current Surveillance Procedure acceptance criteria and used values that may not be indicative of post accident conditions. In a teleconference with Senior Plant Management, it was determined that future operability of the SI Pump lube oil HX cannot be verified and that both trains would be declared inoperable at time 0020 [hrs] [on] 1/16/04. This is in contradiction with the plant Technical Specification,3.3.b Emergency Core Cooling, and placed the plant in the standard shutdown sequence." The plant shutdown will commence at 0120 hrs CST. The NRC Resident Inspector has been notified by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION | ACCIDENT MITIGATION |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2004-01-16
40451 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2004-01-15 18:50 | 2004-01-15 23:39 | 2004-01-19 | POTENTIAL GAS BINDING OF CENTRIFUGAL CHARGING PUMP The following information was obtained from the licensee via facsimile: "During routine 31-day ECCS [Emergency Core Cooling System] venting per SR [Surveillance Requirement] 3.5.2.3 on January 7, 2004, a higher than normal amount of gas was vented from a location on a line off the common suction line for both charging pumps (NV pumps) for Unit 1. The amount of gas vented was not initially considered to be an operability concern. As a conservative measure the frequency of venting was increased from monthly to weekly. Follow-up venting on January 14 indicated the amount of gas vented from this location had increased. Gas was also collecting at a second location at a high point in the NV system. The second location was near the normally-closed valve 1ND-28A. 1ND-28A completes the lineup for 'piggy-back' flow from the Train 'A' decay heat removal system (ND) into the NV system. The type of gas from both locations was determined to be hydrogen. The increased presence of gas was considered a potential operability concern and an operability evaluation was initiated. Venting was increased to once per shift. The source of the hydrogen gas intrusion is unknown and is being investigated. On January 15 at 1850 [EST] it was determined that the amount of gas discovered on January 14 at both locations was greater than what is bounded by current analysis to ensure gas binding of both NV pumps would not have occurred. "Since January 14, subsequent venting at the first location (NV pump common suction line) has resulted in gas volumes within the analysis limits. The amount of gas at the second location (Train 'A' piggy-back tie in) initially decreased but increased again on January 15. As a result, the power was removed from 1ND-28A to prevent the transfer of gas into the NV pump suction line. This action results in Unit 1 Train 'A' of ECCS being inoperable and entry into TS [Technical Specification] 3.5.2 Action A1 on January 15 at 1857[hrs]. Train 'B' of ECCS is considered currently operable with 1ND-28A closed and continued increased venting. "Licensee notified the NRC Resident Inspector." This places Unit 1 in a 72-hr Limiting Condition for Operation [LCO]. Unit 2 is not affected. * * * UPDATE ON 1/19/04 @ 1123 BY S CHRISTOPHER TO C GOULD * * * UPDATE ON POTENTIAL FOR GAS BINDING CENTRIFUGAL CHARGING PUMPS "On January 15, 2004, Catawba reported potential for gas binding Unit 1 centrifugal charging pumps (Refer to Event Number 40451). "Normally-closed valve 1ND-28A completes the lineup for 'piggy-back' flow from the Train 'A' decay heat removal system (ND) for Train 'A' of ECCS. Gas accumulation near 1ND-28A became an operability concern on January 15 for both centrifugal charging pumps. On January 15, 1ND-28A was deenergized (power removed) to prevent the potential transfer of gas into ECCS suction piping. Deenergizing this valve placed Unit 1 into the 72 hour action statement of TS 3.5.2 (ECCS) and 3.6.6 (containment spray). Subsequent ultrasonic testing (UT) of several ECCS vent locations, including the one at 1ND-28A, revealed the piping to be essentially full of water. Based on the UT results, Catawba concluded the gas intrusion was a discrete event and that a current gas production mechanism did not exist. Based on the ECCS piping remaining essentially full of water over a period of approximately 60 hours, power was restored to 1ND28A and Catawba exited TS 3.5.2 and 3.6.6 at 1725 on January 18. Catawba continued with UT a several ECCS locations every six hours as a prudent measure. "At 0350 on January 19, UT revealed a void at the 1ND-28A location that was larger than the currently established acceptance criteria. The gas was vented and water solid conditions established at 0506. TS 3.0.3 was entered from 0350 until 0506 due to the discovery of the gas at 1ND-28A. The cause of the gas intrusion into the ECCS piping continues to be investigated. Frequent UT and venting (if necessary) continues while the root cause evaluation is in progress. Power was removed from 1ND-28A and the 72 hour action statements of TS 3.5.2 and 3.6.6 entered at 0715 on January 19." Licensee notified the NRC Resident inspector. The Reg 2 RDO(Haag) was informed | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-01-15
40450 | 0 | PA DEPARTMENT OF TRANSPORTATION |  |  |  |  | 2004-01-15 12:45 | 2004-01-15 13:13 | 2004-01-15 | DAMAGED TROXLER MOISTURE DENSITY GAUGE At 1313 EST on 01/15/04, Henry Schultz, PA Department of Transportation, reported that at 1245 EST on 01/15/04 a bulldozer ran over a Troxler Moisture Density Gauge (Model #3440, Serial #27356) at a construction site on Interstate-95 in North Eastern Philadelphia. The gauge is presently in the soil at the construction site with the handle broken off. The area around the gauge has been cordoned off. The Construction Nuclear Operator, who normally operates the gauge, is on the scene. The caller planned to contact the local Fire or Police Department to request that a local HAZMAT Team respond to the scene to perform a survey of the damaged instrument to determine if it is leaking and determine how to handle the damaged gauge and possibly the surrounding soil. The caller is also planning to notify the PA Emergency Management Agency and the U.S. National Response Center. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | [10 empty] | NON EMERGENCY | 1 | PA | MAT | [5 empty] | 0 | 2004-01-15
40449 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-01-14 19:50 | 2004-01-15 13:03 | 2004-01-15 | OFFSITE NOTIFICATION OF ACCIDENT INVOLVING 2 TRUCKS CARRYING EMPTY NEW FUEL SHIPPING CONTAINERS The following information was provided by the licensee via facsimile: "On 1/14/2004 at 19:56 hours, the Shift Manager was notified by the Clinton County, PA Emergency Management Agency of vehicle accident involving trucks that were carrying a shipment from Susquehanna. The trucks were carrying empty shipping boxes from a shipment of new fuel that had previously been delivered to Susquehanna. These empty boxes were being shipped in accordance with U.S. Department of Transportation regulations [49CFR173.428 Empty Class 7 (Rad Mat)]. "On 1/15/2004 at 10:20 hours, additional information was provided to the control room indicating that this accident could cause increased public interest due to the severity of the accident. The two tractor trailers involved in the shipment were amongst the vehicles in the accident. One of the truck drivers was seriously injured. The trucks were severely damaged. Clinton County, PA, Emergency Management Agency was called to the scene by initial responders as well as the Pennsylvania Department of Environmental Protection. Both surveyed the boxes and found no indication of radiation/contamination. The shipping boxes and vehicles are being held by the towing company until the shipping company can provide replacement vehicles." The licensee has notified the NRC Resident Inspector. | 94 | 100 | 0 | 94 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-01-15
40448 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2004-01-14 10:00 | 2004-01-14 15:00 | 2004-01-20 | EMERGENCY SIRENS INOPERABLE/DEGRADED DUE TO POTENTIAL AMPLIFIER PROBLEMS "At 1049 EST on January 14, 2004 the Control Room was notified that 78% (87 out of 112) Emergency Sirens failed a 'Quiet Test.' The Quiet test is a status check between the Emergency Offsite Facility and each individual siren. Further investigation revealed that 53 sirens would not operate as required and 34 were experiencing some degree of degradation. Indications point toward amplifier problems within each affected siren. "Efforts are ongoing to troubleshoot and repair the effected sirens. Contingency plans are in place for alternate notification. "The resident inspector has been notified." This condition was discovered during routine monthly testing. The sirens were upgraded about a year ago using equipment supplied by Federal Signal. * * * UPDATE ON 1/20/04 AT 1422 EST FROM RANDY HAISLET TO GERRY WAIG * * * The following was received via facsimile: "This is a follow up to event report 40448 concerning a loss of 53 sirens. As of this morning, 105 of the 112 sirens are considered operable. Six of the 7 inoperable sirens are due to rotational problems. The remaining siren is inoperable due to the impact of a vehicle on it's pole. Work is currently on going to restore these sirens. "The siren failures reported in event report are believed to be the result of a manufacturing defect which resulted in temperature sensitivity. A temporary means of heating the subject equipment has been put in place. Investigation is continuing." Notified R1DO (Clifford Anderson) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-01-14
40447 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-01-13 13:00 | 2004-01-14 13:53 | 2004-01-14 | 24 HOUR NOTIFICATION FOR BULLETIN 91-01 LOSS OF CRITICALITY SAFETY CONTROLS INVOLVING WASTE DRUM "At 1300 on 01/13/04, the Plant Shift Superintendent (PSS) was notified that a waste drum was not characterized and handled properly as fissile waste. During the investigation of ATRC-03-4095, container RFD# 213439-01, which had been characterized as NCS spacing exempt based on the drum being heterogeneous material, it was identified that this waste drum contained solid uranium deposit material violating NCSA WMO-001. The purpose of this NCSA requirement is to determine if the waste drum requires two independent characterization results. Two independent characterization methods were not utilized for the characterization of this drum. "SAFETY SIGNIFICANCE OF EVENTS: Safety significance of event Is low due to the fact that Nondestructive Assay characterization results of drum contents indicate a total U235 content of less than the safe mass limit for NCS Spacing Exempt waste. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: More than two drums, all exceeding the safe mass limit, spaced less than minimum spacing requirements. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): Double contingency is maintained by implementation of two controls on mass. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): The material in the drum is in a solid state. Uranium mass is less than 120g U235. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: Controls relied upon for maintaining double contingency are two Independent measurements to determine the U235 mass of the drum. Since there are two controls on one parameter, double contingency was not maintained since only one measurement was performed. Even though mass control was maintained, double contingency Is based on two controls on mass. Therefore, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Access to the area has been controlled and the drum has been spaced from other fissile material. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No. ATR 04-0111; PGDP Event Report No. PAD-2004-003, Responsible Division: Production Support" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2004-01-14
40446 | 0 | MGP INSTRUMENTS |  |  |  |  | 2004-01-14 | 2004-01-14 12:39 | 2004-01-14 | 10 CFR PART 21 NOTIFICATION FOR DEFECTIVE PARTICULATE RADIATION MONITORS Eight particulate radiation monitoring local processing units manufactured by MGP Instruments, Part # RMS 9040-S with software application 564J were supplied to SCE San Onofre Units 2 and 3. Manufacturer believes 4 units are installed in the following unit skid locations 3RE-7804, 3RE-7807, 2RE-7804, 2RE-7807 and 4 units were supplied as spares. The defect is a possible underestimation of volumetric activity following an auto filter paper advance. The manufacturer determined that you could have a potential underreporting measurement result if the unit program advanced the filter paper immediately following a step change or rapid release in particulate radiation. The manufacturer will revise the application software to handle both conditions simultaneously and advise SCE San Onofre Units 2 and 3 to manually advance the filter paper based on operating experience until the software application can be modified and installed. Manufacturer will notify SCE San Onofre Units 2 and 3 on 01/14/04. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | GA | OTH | PAR | 21.21 |  |  |  | 0 | 2004-01-14
40445 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-01-10 18:00 | 2004-01-13 23:10 | 2004-01-13 | AGREEMENT STATE REPORT INVOLVING PERSONNEL RADIATION EXPOSURE On 01/12/04, the State of California received a report from Schlumberger Technology of an incident that occurred about 1800 PST on 01/10/04. A 1.3 curie Cs-137 source fell off of its tool. A rig hand picked up the source with his fingertips thinking it was the base of a lightbulb. A Schlumberger crew member told the worker to leave it on the deck. The source was recovered with the source handling tool, and returned it to the shielded container. Touching exposure was estimated to be 20 mrem with calculations based on maximum touching time of 10 seconds. Whole body exposure was estimated to be 2.9 mrem with calculation exposure based on beginning at 6 feet from the source and closest distance at 2.5 feet for maximum of 2 minutes. The source has exposure characteristics of 2 mrem/hr at 200 inches (min) from shielded (dovetail) end, and 2 mrem/hr at 680 inches (max) from the non-shielded end. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-01-16
40444 | 0 | LIMERICK | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-01-13 19:21 | 2004-01-13 20:19 | 2004-01-14 | UNUSUAL EVENT DECLARED DUE TO EXPLOSION WITHIN PROTECTED AREA BOUNDARY Explosion occurred in a non-safety related transformer at 1908 EST 0n 01/13/04. The transformer became deenergized as a result of the explosion. Licensee declared an Unusual Event at 1921 EST on 01/13/04 due to an explosion resulting in visible damage to a non-safety related transformer in the Turbine Enclosure building. There was no fire or injured personnel, and the site did not require any off site assistance. The transformer explosion resulted in the loss of power to some 480 VAC non-safety related loads (most significant was a non-safeguard DC battery charger). The explosion has not severely impacted Unit 1 operations. The transformer has been inspected, and it appears that the explosion was internal to the transformer and due to an electrical malfunction. Security personnel conducted thorough walk downs of all areas and had no concerns. NRC Management determined that this event did not require entry into the Monitoring Phase of Normal Mode of Incident Response at 2040 on 01/13/04. The licensee notified the state and local emergency management agencies and notified the NRC Resident Inspector. * * * UPDATE FROM PETE ORPHANOS (VIA FACSIMILE) TO HOWIE CROUCH @ 0221 EST ON 1/14/04 * * * "Notification of reduction in classification status from Unusual Event. "Failure of non-safeguards electrical supply determined to be due to cable fault. Plant remains stable at 100% power. No additional equipment damage identified. Blocking and repair planning in progress." The unusual event was terminated by the licensee at 2151 hrs. EST on 1/13/04. The licensee has notified the NRC Resident Inspector and State and County authorities. A media press release will be issued in the morning. Notified DHS (Beal) and FEMA (Caldwell). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-01-13
40443 | 0 | FARLEY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2004-01-13 13:55 | 2004-01-13 17:42 | 2004-01-13 | LOSS OF COMMUNICATION AND EMERGENCY NOTIFICATION SYSTEM "General FTS Failure recognized by abnormal ring (long drawn out ring) coming from ENS. System operation verification performed after ring noted. At this time it was realized all lines had no dial tones and were inoperable. In addition to the ENS other FTS phones/lines inoperable noted were the MCL, HPN, PMCL, RSCL, and possibly the LAN line, ERDS 1 and 2. (ERDS, and LAN line not operability tested)." "ENS Failure- Discovered at 12:55 CST it was inoperable and reportable per FNP-0-EIP-8.0 (non emergency report) para. 12.6.2 at 13:55 CST. Plant Commercial lines not effected." The licensee notified the NRC Resident Inspector | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-01-13
40442 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-01-13 13:12 | 2004-01-13 14:25 | 2004-01-14 | LOSS OF COMMUNICATION AND EMERGENCY NOTIFICATION SYSTEM The ENS phones in the control room were discovered inoperable at 1312 EST on 01/13/04. Control room staff then notified EP personnel of a possible problem with the ENS phone lines. EP personnel investigated and determined that the ENS phone system as well as other Federal Telecommunication System lines were not operating on site. Information Resources (IR) is investigating. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 0530 hrs EST ON 1/14/03 FROM LICENSEE TO CROUCH * * * All FTS phone services have been restored to the plant and tested satisfactorily from the Operations Center to the ENS phone. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2004-01-13
40441 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2004-01-13 07:30 | 2004-01-13 14:27 | 2004-01-13 | CONTRACT EMPLOYEE FITNESS FOR DUTY A contract employee tested positive for illegal drugs during Pre-Access testing for unescorted access. The employee's access to the plant was denied. Contact the HOO for additional details. The licensee notified the NRC Resident Inspector. | 95 | 100 | 0 | 95 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2004-01-13
40440 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2004-01-12 15:45 | 2004-01-13 10:58 | 2004-01-13 | 24 HOUR NOTIFICATION BULLETIN 91-01 CRITICALITY CONTROL "Reason for Notification: Thirteen polypaks of uranium powder were dumped into a bulk container without a documented visual inspection of the bulk container. A visual inspection is performed prior to introducing SNM into a bulk container. "Upon recognizing that the documentation was missing, the operator confirmed that a visual inspection had been performed prior to introducing SNM, but had not been documented. The operator then re-inspected the bulk container and found no trace of moderator. The powder dumped into the container was previously documented to contain leas than 0.3 weight percent moisture. "Double Contingency Protection: Double contingency protection for the ADU Bulk Blending System is assured by preventing moderator from entering a bulk container. Empty bulk containers are inspected for the presence of moderator prior to introducing SNM. Failure to document the inspection left less than previously documented double contingency protection for the system. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5b), this event satisfies the criteria for a 24-hour notification. "Summary of Activity: Bulk blending operations were discontinued. Training was performed for each shift prior to resuming operations. "Conclusions: Less than previously documented double contingency protection remained. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) determined that this is a significant incident in accordance with governing procedures. A causal analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2004-01-13
40439 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2004-01-07 | 2004-01-13 06:03 | 2004-01-13 | AGREEMENT STATE REPORT - LACK OF POSTING AND ACCESS RESTRICTIONS TO RADIATION AREA "During an inspection of the licensee facility by RHB [State] on 1/7/04, a potential radiation problem was indicated by a high neutron radiation level above a shield assembly used to store Cf-252 neutron sources. Directly above the shield, the neutron dose rate was measured as approximately 5 rem/hr using a rem-ball. This area was not controlled as a high radiation area, nor were controls effective at the time of the inspection to preclude unrestricted access to the room. On the roof, directly above the shield assembly, the neutron dose rate was measured as approximately 25 mrem/hr, in an area of approximately 1 square foot. The roof area was not controlled as a restricted area. (Both neutron measurements were made by the licensee because of the lack of neutron survey instrumentation by the RHB inspector.) The licensee was directed to remeasure the neutron dose rate on the roof because it was inconsistent with the room dose rate, to add shielding to reduce the roof dose rates, and to provide high radiation area controls to the room containing the stored neutron sources. The second measurement of the roof dose rate found 250-260 mrem/hr in the highest area (approximately 1 square foot). The licensee representative reported he had incorrectly read the instrument scale during the previous measurement. Polyethylene sheets and a container of hydrogenous material were placed on the top of the shield assembly to act as temporary neutron shielding. This reduced the neutron dose rate directly above the shield assembly to 8-10 mrem/hr, and the roof dose rate to less than 2 mrem/hr. Locks were installed on the doors accessing the laboratory area where the Cf-252 sources are stored. "The licensee is in the process of constructing a permanent safe storage inside of this shield assembly, with additional shielding to conservatively ensure that individuals in unrestricted areas won't exceed 100 mrem/year dose (and unrestricted area dose rates will be less than 2 mrem in any hour). The shielding design will ensure that the shielding cannot be removed by an unauthorized person and accidentally recreate the high radiation area and unrestricted area dose rate problems. This construction is expected to be completed by 1/15/04. "The state (RHB) will continue to investigate this matter to evaluate the potential for exposures to personnel as a result of the elevated dose rates and lack of access controls. No personnel overexposures, worker or public, are known to have occurred at this time." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-01-15
40438 | -1 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-01-11 18:00 | 2004-01-12 14:17 | 2004-01-16 | SAFETY EQUIPMENT FAILS TO FUNCTION "At 1810 [CST] on 01-11-04 the Plant Shift Superintendent (PSS) was notified of a failure of the C-360 #4 Autoclave High Pressure Isolation System. Water was observed leaking from the autoclave head-to-shell interface near the six o'clock position shortly after initiating a cylinder heat cycle. At the time of discovery, the autoclave was in TSR mode 5 and the High Pressure Isolation System was required to be operable while in this mode. This system is designed to provide containment of the autoclave and prevent an external release of UF6 during a system breach while heating a UF6 cylinder. The PSS declared the system inoperable and TSR LCO 2.1.3.1 .C1 actions were implemented to remove the autoclave from service and place it in Mode 2, 'Out of Service.' The event is reportable as a 24 hour event, as required by 10 CFR 76.120 (c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function." "PGDP Problem Report No. ATR-04-0095; PGDP Event Report No. PAD-2004-02; Event Worksheet Responsible Division; Operations" Operations has notified the Senior NRC Resident Inspector. * * * UPDATE ON 1/16/04 AT 1536 EST FROM KEVIN BEASLEY TO GERRY WAIG * * * This event has been retracted and the following update information provided: "Subsequent to the report, plant engineers inspected the autoclave sealing surfaces and O-ring. The O-ring and autoclave sealing surfaces were found to be in good condition with no problems noted that would cause the water leak observed by the operators. The autoclave was subjected to a head-to-shell alignment (pinch) test. The test determined that the autoclave sealing surfaces were within acceptable alignment tolerances and no adjustments were made. To determine the autoclave's ability to perform its containment function, the TSR surveillance (pressure decay test) was performed with the autoclave In the as-found condition, i.e., without any maintenance or changes in the autoclave condition. The autoclave passed this test with approximately half the maximum allowable leak rate. The successful performance of the autoclave pressure decay test indicates that the autoclave HPIS [High Pressure Isolation System] would have been able to perform its designed containment function on January 11, 2004, had it been necessary. Thus, the 10CFR76.120 reporting criteria were not met. "The NRC Resident Inspector has been notified of this retraction." PGDP Problem Report No. ATR-04-0095; PGDP Event Report No. PAP-2004-02; Event Worksheet 40438 Responsible Division: Operations Notified R2DO (Robert Haag), NMSS (Tom Essig), DIRO (Richard Wessman). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-01-12
40437 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2004-01-12 10:48 | 2004-01-12 12:30 | 2004-01-12 | MANUAL SCRAM FOLLOWING INVALID CONTAINMENT ISOLATION SIGNAL "On 01/12/04 at 1048 hours, the Hope Creek Generating Station reactor was manually scrammed following an invalid containment isolation signal on Reactor Building High-High Radiation. The invalid signal was caused by the combination of a scheduled sensor calibration on channel 'C', coincident with an emergent failure on channel 'A.' This combination of trip signals made up the two out of three trip logic for the Reactor Building High-High Radiation containment isolation signal. While recovering from the spurious isolation signal, the operating crew observed two of the inboard MSIV's drifting closed from a loss of pneumatic pressure as a result of the isolation signal. In response to this condition, the operating crew manually scrammed the reactor. A low reactor water level scram signal was received at 12.5 inches as expected, and reactor level was subsequently returned to the normal band using the reactor feedpumps. At the time of this event, the 'A' Control Room Ventilation Train was inoperable but available pending emergent corrective maintenance. The 'C' channel Reactor Building Radiation monitor has been returned to service and is operable, and the 'A' channel remains failed in the tripped condition. All other systems functioned as expected, and a post-transient review team is being assembled to investigate the event." Decay heat is being removed via steam to the main condenser using the bypass valves. The condensate and feedwater system is in operation maintaining reactor vessel water level. No SRVs lifted during the transient and the electrical system is stable in a normal lineup. The licensee notified the NRC Resident Inspector and will be notifying the LAC Township. | 0 | 0 | 0 | 68 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2004-01-12
40436 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2004-01-10 13:00 | 2004-01-10 15:22 | 2004-01-10 | TS REQUIRED SHUTDOWN AT NMP1 DUE TO INOPERABLE MSIV "During the performance of a normal orderly planned shutdown for maintenance a packing leak was discovered on Main Steam Inboard Isolation Valve 01-02 (01-02). Drywall inspection results revealed MSIV 01-02 operator gear housing degraded allowing grease to be lost. Engineering assessment of the condition of the limitorque operator of MSIV 01-02 is not able to provide enough information to support operability of MSIV 01-02. Declaring MSIV 01-02 inoperable. Entering T.S. 3.2.7(b and c). Action required to close one valve in the line having an inoperable valve or initiate a normal orderly shutdown with in one hour and be in cold shutdown within ten hours. Entering T.S. 3.3.4(b and c). Action required to close one valve in the line having an inoperable valve within four hours or reduce reactor coolant temperature to a value less than 215 degrees F within ten hours. Most limiting action required in current condition is 10 hours to be in cold shutdown. 01-02 will be closed as soon as all rods are in." The NRC Resident Inspector was notified. | 1 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-01-10
40435 | -1 | COOPER | 1 |  |  | [1] GE-4 | 2004-01-10 05:00 | 2004-01-10 13:48 | 2004-01-15 | ACCIDENT MITIGATION - CREFS INOPERABLE This Notification is being made pursuant to 10 CFR 50.72 (b)(3)(v)(D). On January 8, 2004 at 17:35 CST with the Control Room Emergency Filtration System (CREFS) inoperable for planned maintenance, CREFS failed post work testing due to system flow being higher than that allowed by technical specifications. It was originally believed that the failure was connected with the planned maintenance because the system flow rate was initially within the specifications during surveillance testing the previous day. Following system troubleshooting, at 05:00 CST on January 10, 2004, it was determined that the cause of the high flow rates was indeterminate. Based on this evaluation, it could not be determined whether the CREFS failure was independent of planned maintenance or not. Additionally, it is not immediately clear if the high flow condition would result in a loss of safety function. It was therefore conservatively determined that the condition is reportable per 10 CFR 50.72 (b)(3)(v)(D) as a failure of a single train system which could have prevented the fulfillment of a safety function that is needed to mitigate the consequences of an accident. CREFS flow rates are currently within specifications, but the system will remain inoperable until the proper surveillances have been completed. The senior NRC Resident has been notified. * * * UPDATE ON 1/15/04 AT 1729 HOURS EST FROM JAMES DEDIC TO GERRY WAIG * * * The licensee retracted this event and provided the following information: "On January 10, 2004, Cooper Nuclear Station [CNS] made an eight hour event notification report to the NRC pursuant to 10CFR50.72.(b)(3)(v)(D), failure of a single train system which could have prevented the fulfillment of a safety function that is needed to mitigate the consequences of an accident. In particular, testing to restore the Control Room Emergency Filter System (CREFS) to operable status following planned maintenance indicated the flow rate was greater than that allowed by Technical Specifications. It was not known whether the high flow condition would result in a loss of safety function. Flow rate was restored to within Technical Specification Limits and CREFS was returned to operable status on January 11, 2004 at 1803 hours "Subsequent evaluation determined: "1. the high flow condition did not impact the system safety functions to maintain the Control Room at a positive pressure with respect to adjoining areas or to isolate the outside air intake on relevant Group isolation signals. "2. the CREFS safety function to limit the radiation exposure to Control Room personnel during any one of the postulated design basis events to within regulatory limits (10CFR50, Appendix A, GDC 19) was maintained during the high flow condition. "3. the design functions of CREFS for the CNS toxic hazards assessment and Fire Protection Program requirements were not affected by the CREFS high flow. "The evaluation concluded the safety function of the CREFS during the high flow condition was maintained. Therefore, CNS is retracting this 10CFR50.72 Event Notification." The licensee will notify the NRC Resident Inspector. Notified R4DO (Jeffery Clark) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2004-01-10
40434 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2004-01-10 01:27 | 2004-01-10 04:40 | 2004-01-10 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN INITIATED AND SUBSEQUENTLY TERMINATED "During a surveillance of the Beaver Valley Power Station Unit No. 1 Solid State Protection System (SSPS) train "B" on 01/09/2004, a master relay contact exhibited unacceptable high resistance and was declared inoperable at 2042 hours. Corrective action was initiated to replace the relay, which requires that the "B" train of the reactor trip system be transferred from the reactor trip breaker to the bypass reactor trip breaker and the "B" train of SSPS be de-energized. Action 40.b of Technical Specification 3.3.1.1, Table 3.3-1, Item 21 requires the Unit to be in at least Hot Standby within 6 hours with one reactor trip breaker inoperable as a result of something other than an inoperable diverse trip feature. Bypassing the reactor trip breaker in order to replace the SSPS master relay makes the reactor trip breaker inoperable as a result of something other than an inoperable diverse trip feature. "The 'B' train Reactor Trip System reactor trip breaker was bypassed at 00:28 hours on 01/10/2004. Beaver Valley Power Station Unit No. 1 initiated a plant shutdown at 01:27 hours on 01/10/2004 in response to entering Action 40.b of Technical Specification 3.3.1.1, Table 3.3-1, Item 21. "Action to replace the SSPS master relay was completed and the reactor trip breaker was returned to operability at 02:55 hours and the plant shutdown was terminated at 72% power. The Unit is scheduled to return to full power operation. "Source Range N-31 re-energized when source range high voltage switch was restored to "Normal" position. Investigation is currently underway to determine the cause of this." The licensee notified the NRC Resident Inspector. | 72 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-01-10
40433 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-01-08 15:02 | 2004-01-08 19:12 | 2004-01-08 | TS REQUIRED SHUTDOWN AT OCONEE 1 DUE TO UNIDENTIFIED RCS LEAKAGE "Event Description: Reactor Coolant System, (RCS) Leakage in excess of TS limits. RCS leakage calculations have shown a gradual increase in leakage following Unit l start-up from a refueling outage. On 1/7/2004 @ 1800 hours an RCS leakage calculation was performed with the calculated leak rate at 0.300 gpm. On 1/8/2004 @ 1225 hours, with Reactor power at approximately 26% Rated Thermal Power (RTP), leakage had increased to 0.778 gpm. Personnel have entered containment and have determined the source to be within the A steam generator cavity. At 1312 hours a power reduction to 17% RTP was initiated to reduce dose sufficiently to allow entry into the cavity in an attempt to identify the exact leak source. On 1/8/2004 @ 1502 hours, the leak rate was calculated to be one gpm which exceeds the allowed leakage for unidentified leakage. Units 2 and 3 are unaffected and remain at 100% RTP. "Initial Safety Significance: The measured leakage is well within the capacity of the normal RCS make-up system. The increase in leakage rate has been slow, and is not expected to increase significantly prior to completion of the TS required shutdown. The leakage is confined inside containment. At this time, there has been NO RADIOLOGICAL RELEASE associated with this event. "NOTE: Entry into the emergency plan is not required unless the leakage is => 10 gpm unidentified or => 25 gpm identified, the current leakage is significantly below those limits. "Corrective Action(s)= Unit shutdown per TS is in progress. Isolation or repair of the leak will be evaluated once the location of the leak source is determined. TS 3.4.13 allows 4 hours to reduce leakage within limits. If the source remains unidentified and leakage remains above limits, the TS requires shutdown to Mode 3 within 12 hours and to Mode 5 within 36 hours." The NRC resident inspector was notified. | 17 | 0 | 0 | 28 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2004-01-08
40432 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2004-01-08 17:58 | 2004-01-08 18:45 | 2004-01-09 | OFFSITE NOTIFICATION AT SEABROOK The licensee reported that the upper lights on the meteorological tower were not working. The licensee made an offsite notification to the FAA and will initiate corrective actions. The licensee notified the NRC resident inspector. * * * UPDATE ON 01/09/04 @ 0859 BY RITTER TO GOULD * * * RETRACTION The licensee is retracting this notification after a further review of the reporting requirements determined that the notification was unnecessary. The condition reported to other government agencies was not related to the radiological health and safety of the public or onsite personnel or the protection of the environment. The NRC Resident Inspector was informed. Notified Reg 1 RDO (Noggle) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2004-01-08
40431 | 0 | ASSOCIATES AND MEDICAL PHYSICS |  |  |  |  | 2001-03-22 13:30 | 2004-01-08 17:00 | 2004-01-08 | MEDICAL EVENT AT DOUGLAS CITY HOSPITAL IN MINNESOTA Associates and Medical Physics reported 6 related medical events that occurred between 3/22/01 thru 5/14/03 at Douglas City Hospital located in Alexandria, Minnesota. The licensee used Samarium 153 to treat patients for bone pain. The highest intended source strength was 115 milli-curies. The licensee discovered that the patients were actually under-dosed by 34% due to an incorrect dose calibrator setting. There was no significant adverse effects to the patients. Corrective actions were taken to calibrate the dose calibrator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MN | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2004-01-08
40430 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2004-01-05 08:16 | 2004-01-07 16:43 | 2004-01-07 | AGREEMENT STATE REPORT: NOVOSTE STRONTIUM-90 INTRAVASULAR BRACHYTHERAPY (IVB) SOURCE DISCOVERED MISSING. "Novoste Strontium-90 Intravascular brachytherapy (IVB) source (remote afterloader) was discovered missing on January 5, 2004. Source was last seen but not used on December 17, 2003. Reported by phone by RSO. Source is a small handlheld device - Manufacturer: Novoste, Model: BethCath, Serial No. 92607; Source train Serial No. ZB-520; Original Activity 55.62 millicuries; current activity (date of discovery) 54.64 millicuries; Calibration date: 04/11/2003; Last leak test 10/29/2003. Received at the hospital on November 4, 2003. Last used in a patient on December 5, 2003 (first and last use). Last seen on during a functional test on December 17, 2003 in the Fondren Building, Room F1099 (near cath lab) at the Licensee's main site 6565 Fannin Street, Houston, Texas. The source was not used that day. Two other sources of different activity and length remain in storage. The room and cath lab have been search 4 times by the Licensee's staff. Trash has been surveyed. Hospital staff has been notified of the missing equipment.." Texas Incident No.: I-8089. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2004-01-12
40429 | 0 | US AIR FORCE |  |  |  |  | 2003-12-31 | 2004-01-07 11:51 | 2004-01-07 | MISSING TRITIUM SIGN On 12/31/03 it was determined that a (1) tritium exit sign was missing from Bldg. 193 at Cannon Air Force Base in New Mexico. The sign was last observed the day before on 12/30/03. The missing sign is a Betalux-E, S/N 191736, containing a 20 curie tritium source. To date, three (3) exit signs have been reported missing during the on-going base renovation (see EN #40407). Efforts to locate the signs continue. * * * UPDATE1550 EST ON 1/7/04 FROM CRAIG REFOSCO TO S. SANDIN * * * The licensee is amending the original report to show that the last inventory of the exit sign was in May 2003 and not 12/30. The sign was discovered missing on 12/30 and reported to the USAF on 12/31/03. Notified R1DO(Noggle), R4DO(Runyan), and NMSS(Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | DC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2004-01-07
40428 | 0 | HATCH | 1 |  |  | [1] GE-4,[2] GE-4 | 2004-01-06 12:58 | 2004-01-06 13:32 | 2004-01-06 | UNUSUAL EVENT DECLARED DUE TO FIRE ON REFUEL FLOOR Fire reported to control room at 1240 EST 01/06/04. Fire was located inside a portable "Kelly" building on the Refueling Floor which lasted greater than 10 minutes. An Unusual Event was declared at 1258 on 01/06/04. Fire was extinguished at 1302. Fire did not spread beyond the boundary of the Kelly building. The Kelly building was in a contaminated area, but there was no radioactive release outside of the Kelly building. Unusual Event was terminated at 1321. Initial notification to NRC Headquarters of the Unusual Event was made by the NRC Senior Resident Inspector at 1254 EST. At 1303 EST 01/06/04 the decision was made not to enter the Monitoring Phase of Normal Mode of Incident Response for this event. Licensee notified NRC Resident Inspector, State, and Local emergency management authorities. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 2 | GA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(xi) |  |  | 0 | 2004-01-06
40427 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2003-12-02 | 2004-01-06 11:40 | 2004-01-06 | AGREEMENT STATE REPORT CONCERNING LOST GAUGE "A Kay-Ray Model 7063P gauge with serial number 12349 and a 500 milliCurie source of Cs-137 was not accounted for during the last Radiation Source Survey. The device has been stored in a locked warehouse with limited access since 1984. It was stored in a secured wooden crate with proper labeling. A search was conducted and interviews performed. As of December 2, 2003 the device has not been found. An email from Thermo Electron Corporation states that the source has decayed to 316.366 milliCurie. Vulcan also notified all of its scrap metal contractors to be on alert for the device." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2004-01-09
40426 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2004-01-05 08:00 | 2004-01-05 17:08 | 2004-01-05 | PLANT ACCESS TERMINATED DUE TO POSITIVE FITNESS FOR DUTY TEST A contractor employee was given an Administrative positive FFD test result due to not showing up for a random FFD test and leaving the site without completing the test. The employee's access to the plant has been terminated. Contact the HOO for additional details. The licensee notified the NRC Resident Inspector and Connecticut DEP. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 26.73 |  |  |  | 0 | 2004-01-05
40425 | 0 | MCGUIRE | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2004-01-05 09:30 | 2004-01-05 12:47 | 2004-01-05 | LICENSEE MANAGER TESTED POSITIVE FOR ALCOHOL ON A RANDOM TEST Contact HOO for additional information The NRC Resident Inspector will be informed. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 26.73 |  |  |  | 0 | 2004-01-05
40424 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2004-01-02 20:38 | 2004-01-02 21:30 | 2004-01-03 | UNIT 1 DECLARED AN UNUSUAL EVENT DUE TO 14 GPM UNIDENTIFIED RCS LEAKAGE At 2038EST Unit 1 Control Room Operators observed and quantified unidentified RCS leakage of approximately 14 gpm based on containment sump pump operation and a corresponding decrease in VCT level. Unit 1 was preparing for startup and there were no ongoing maintenance activities at the time. The licensee declared an Unusual Event entering their emergency procedures to isolate and identify the source of the leakage. As a result, a pressurizer sample line was isolated which terminated the leakage. The licensee will remain in the Unusual Event until an investigation is completed confirming that this was the source. There was no measured increase in radiation levels/humidity inside containment or radioactive release to the environment. At the time of the report, 3 of the 4 RCPs were operating for forced circulation with the 4th RCP secured earlier in the day during a test. All ECCS systems are available including the EDGs, if needed. Normal makeup is in service to maintain RCS inventory with MFW supplying the Generators for decay heat removal via the steam bypass to the Main Condenser. The licensee informed state/local agencies and will inform the NRC Resident Inspector. At 2158EST the NRC determined that this event did not require entry into the Monitoring Phase of Normal Mode. * * * UPDATE ON 01/03/04 AT 0006 EST FROM SLYVESTER MONTGOMERY TO GERRY WAIG * * * The licensee terminated the NOUE at 2353 hours EST on 01/02/04. The leak has been identified as coming from a relief valve flange on the pressurizer sample line. Maintenance activities are on-going to repair the leak and the reactor remains in mode 3. The licensee has notified state and local government of the NOUE termination and will be notifying the NRC Resident Inspector. Notified R2DO (David Ayres), FEMA (Dan Sullivan), DIRO (Tim McGinty), NRR (Pao-Tsin Kuo), NRC (Thomas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | UNUSUAL EVENT | 2 | SC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2004-01-02
40423 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2004-01-02 02:30 | 2004-01-02 10:03 | 2004-01-02 | FAILURE OF AUTOCLAVE ISOLATION SYSTEM "At 0230 on 01-02-04 the Plant Shift Superintendent (PSS) was notified of a failure of the C-360 #3 Autoclave High Pressure Isolation System. Steam was observed leaking from the autoclave head-to-shell interface between the eleven and one o'clock position shortly after initiating a cylinder heat cycle. At the time of discovery, the autoclave was in TSR [Technical Safety Requirements] mode 5 and the High Pressure Isolation System was required to be operable while in this mode. This system is designed to provide containment of the autoclave and prevent an external release of UF6 during a system breach while heating a UF6 cylinder. The PSS declared the system inoperable and TSR LCO 2.1.3.1.C1 actions were implemented to remove the autoclave from service and place it in Mode 2, "Out of Service". The event is reportable as a 24 hour event, as required by 10 CFR 76.120(c)(2)(i); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a pre-established safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function. "The Senior NRC Resident Inspector has been notified of this event." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | KY | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2004-01-02
40422 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2004-01-02 02:58 | 2004-01-02 06:50 | 2004-02-03 | SAFEGUARD SYSTEM VULNERABILITY Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will be notifying the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * * RETRACTION FROM F. SCHILL TO M. RIPLEY 1812 ET 02/03/2004 * * * "Further evaluation of the events associated with this report reveals that the reported event does not meet the criteria for reporting pursuant to 10 CFR 73.71(b)(1) and is hereby retracted." Contact the Headquarters Operations Officer for additional details. The licensee notified the NRC Resident Inspector. Notified R4 (A. Gody) and NSIR TAS (M. Hahn) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2004-01-02
40421 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-12-31 14:15 | 2003-12-31 16:19 | 2003-12-31 | CONTACTOR TESTED POSTIVE DURING A RANDOM DRUG TEST During a random drug test a Contractor tested positive. His access was revoked and he was escorted offsite. The contractor had full access to the Protected Area but he was working outside the Protected Area when he tested positive. A review of his past work will be performed. The NRC Resident Inspector will be notified of this event by the licensee. | 96 | 100 | 0 | 96 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 26.73 |  |  |  | 0 | 2003-12-31
40420 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-12-31 12:00 | 2003-12-31 15:50 | 2004-01-27 | AGREEMENT STATE REPORT: DAMAGED GAUGE "Licensee: Simpson Tacoma Kraft, LLC "City and State: Tacoma, Washington "License Number: WN-I014-1 "Type of License: Fixed Gauge "Date of Event: 31 December 2003 (when discovered by licensee "Location of Event: 801 Portland Avenue, Tacoma, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (department) on-site investigation; media attention): "The licensed Radiation Safety Officer reported to the Department, on 31 December, he noticed that process fluids had eroded a ½ inch by 4 inch hole through the ½ inch thick gauge body where it attached to process piping. The damage was apparently confined to the device's body and the event is not considered to present an emergency at this time. The device had been in service for about 12 years and had reached the end of its useful service life. It was being removed to prepare it for disposal. "The device is a Texas Nuclear Corp. Model 5176, Serial Number 2253, containing 7.4 gigabecquerels (200 millicuries) of Cesium 137. "The licensee informed the department they would bolt a ½ inch metal plate to the device's attachment point, over the damaged area, to temporarily return the device to its normal level of shielding and integrity. After removal and the temporary repair, the licensee placed the device into secured storage, along with several other similar devices, in preparation for source removal and disposal in January 2004, by a service provider. "The RSO, approved for device installation, relocation, removal from service, and surveys, reported that the device was reading 1.5 Mr/hr, contact at the damaged area, prior to the temporary repair. A similar, but undamaged, device read 1.2 Mr/hr at the same location. The RSO reported no activity from a wipe survey on the damaged device. "The Department will perform an on-site investigation on 6 January 2004. No media attention has been attracted, yet. "Notification Reporting Criteria: 10 CFR 31, General Domestic Licenses for Byproduct Material (damage to shielding) "Isotope and Activity involved: Cesium 137, 7.4 gigabecquerels (200 millicuries) "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): N/A "Lost, Stolen or Damaged? (mfg., model, serial number): damage confined to device body of a Texas Nuclear Corp, Model 5176 device, Serial Number 2253 "`Disposition/recovery: removed from service, temporarily repaired, secured for pending disposal "Leak test? Wipe survey indicated no contamination, last leak test was negative "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) N/A "Release of activity? None "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: See above "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided? Pending "Was referring physician notified? N/A "Consultant used? N/A for this event" * * * UPDATE ON 1/16/04 AT 1315 EST FROM ARDEN SCROGGS TO GERRY WAIG * * * The following information was received via email: "This is an updated notification of an event in Washington State, reported to and investigated by, the WA Department of Health, Office of Radiation Protection. "STATUS: update "Licensee: Simpson Tacoma Kraft, LLC "City and State: Tacoma, Washington "License Number: WN-I014-1 "Type of License: Fixed Gauge "Date of Event: 31 December 2003 (when discovered by licensee) "Location of Event: 801 Portland Avenue, Tacoma, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (department) on-site investigation; media attention): "The licensed Radiation Safety Officer reported to the Department, on 31 December, that he had discovered that process fluids (green liquor [sodium sulfite]) had eroded a 3-inch by 6-inch hole through a 1/8 inch thick aluminum gauge cover-plate on the gauge where the gauge attached to process piping. The damage was confined to the device's cover-plate and the event was not considered an emergency. The device had been in service for about 30 years and had reached the end of its useful service life. It was being removed in preparation for disposal. "The device is a Texas Nuclear Corp., Model 5176, Serial Number 2253, containing 7.4 gigabecquerels (200 millicuries) of Cesium 137. "The licensee informed the department they would bolt a ½ inch thick metal plate to the device's attachment point, over the damaged area, to cover the whole. After removal and temporary repair, the licensee placed the device into secured storage, along with several other similar devices, in preparation for source removal and disposal. A service provider, is scheduled to remove the devices from the licensee's facility in about April, 2004. "The RSO, approved for device installation, relocation, removal from service, and surveys, reported that the device was reading 1.5 Mr/hr, contact at the damaged area, prior to the temporary repair. A similar, but undamaged device, read 1.2 Mr/hr at the same point. A Ludlum Model 3, SN 104500, calibrated 19 November 2003, was used for stated measurements. The RSO took a leak test inside the opened area. The RSO sent the leak test sample for analysis and subsequently reported the test indicated less then detectable activity. "The Department performed an on-site investigation on 9 January 2004, resulting in this updated report. No media attention has been attracted, yet. "Initial Notification Reporting Criteria was: 10 CFR 31, General Domestic Licenses for Byproduct Material (damage to shielding) but now we understand that shielding was not compromised. "Isotope and Activity involved: Cesium 137, 7.4 gigabecquerels (200 millicuries) "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence): N/A "Lost, Stolen or Damaged? (mfg., model, serial number): damage confined to device cover-plate, of a Texas Nuclear Corp, Model 5176 device, Serial Number 2253 "Disposition/recovery: removed from service, temporarily repaired, secured for pending disposal "Leak test? Wipe survey indicated no contamination, leak test was negative "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) N/A "Release of activity? None "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: See above "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided? Pending "Was referring physician notified? N/A "Consultant used? N/A for this event" Notified R4DO (Jeffery Clark), NMSS (Thomas Essig) * * * UPDATE ON 1/27/04 AT 1433 EST LAWRENCE TO GOTT * * * "The changes include: 1. Update in status as complete, 2 Full description of the corrosive process fluids, 3. Additional information on the area of gauge that was damaged. "This incident is considered closed as of January 27, 2004. "This is an updated notification of an event in Washington State, reported to and investigated by, the WA Department of Health, Office of Radiation Protection. "STATUS: complete "Licensee: Simpson Tacoma Kraft, LLC City and State: Tacoma, Washington License Number: WN-I014-1 Type of License: Fixed Gauge "Date of Event: 31 December 2003 (when discovered by licensee) Location of Event: 801 Portland Avenue, Tacoma, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (department) on-site investigation; media attention): "The licensed Radiation Safety Officer reported to the Department, on 31 December, that he had discovered that process fluids (green liquor comprised of [sodium sulfide, sodium sulfate, and sodium carbonate]) had eroded a 3-inch by 6-inch hole through a 1/8 inch thick aluminum gauge cover-plate on the gauge where the gauge attached to process piping. The damage was confined to the device's cover-plate and the event was not considered an emergency. A service provider subsequently reported to the licensee, the plate is to prevent contaminants from fouling the shutter mechanism. The plate has little impact on shielding. The device had been in service for about 30 years and had reached the end of its useful service life. It was being removed in preparation for disposal. "The device is a Texas Nuclear Corp., Model 5176, Serial Number 2253, containing 7.4 gigabecquerels (200 millicuries) of Cesium 137. "The licensee informed the department they would bolt a ½ inch thick metal plate to the device's attachment point, over the damaged area, to cover the whole. After removal and the temporary repair, the licensee placed the device into secured storage, along with several other similar devices, in preparation for source removal and disposal. A service provider is scheduled to remove the devices from the licensee's facility in about April 2004. "The RSO, approved for device installation, relocation, removal from service, and surveys, reported that the device was reading 1.5 Mr/hr, contact at the damaged area, prior to the temporary repair. A similar, but undamaged, device read 1.2 Mr/hr at the same point. A Ludlum Model 3, SN 104500, calibrated 19 November 2003, was used for stated measurements. The RSO took a leak test, inside the opened area. The RSO sent the leak test sample for analysis and subsequently reported the test indicated less then detectable activity. "The Department performed an on-site investigation on 9 January 2004, resulting in this updated report. No media attention has been attracted, yet." Notified NMSS (Kokajko) and R4DO (William Johnson) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2004-01-05
40419 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-30 13:30 | 2003-12-30 15:01 | 2003-12-30 | REACTOR TRIPPED FROM 100% POWER DUE TO LOW STEAM GENERATOR Cook unit 2 automatically tripped from 100% power due to low steam generator level coincident with feed flow less than steam flow. The cause of this condition is under investigation, but it is suspected that unplanned closure of the steam generator 2 & 3 feedwater isolation valves led to the initiating signal. It is believed that the feedwater isolation valve closure originated from an abnormality in the Control Room Instrument Distribution(CRID) 120VAC power system. Technicians were landing leads on a Residual Heat Removal (RHR) System flow transmitter which was fed from the suspected CRID supply at the time of the event. An arc was observed during the lead landing procedure. The main generator also required a manual trip signal by control room operators due to sticking of the main stop valve which is also being investigated. All other systems responded as expected. All rods fully inserted, no ECCS actuation occurred, and no relief valves lifted. The unit is stable in mode 3 with aux feedwater providing heat sink supply. The NRC Resident Inspector has been informed. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-12-30
40418 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-12-30 08:30 | 2003-12-30 12:27 | 2003-12-30 | LICENSED EMPLOYEE FAILED A RANDOM FITNESS FOR DUTY ALCOHOL TEST Contact the HOO for additional details. The NRC Resident Inspector was notified | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2003-12-30
40417 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2003-12-29 11:29 | 2003-12-29 16:49 | 2003-12-29 | POSITIVE TEST DURING A RANDOM FITNESS FOR DUTY SCREENING Non - licensed, non-supervisory employee tested positive for presence of alcohol. The NRC Resident Inspector was notified. | 100 | 18 | 0 | 100 | 18 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 26.73 |  |  |  | 0 | 2003-12-29
40416 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-12-27 | 2003-12-29 16:43 | 2003-12-29 | A CALIFORNIA LICENSEE REPORTED A CPN NUCLEAR GAUGE WAS STOLEN FROM A JOBSITE GeoSoils, Inc., reported that a CPN nuclear gauge (Model MC3, S/N M390104771) was stolen on 12/27-28/03 from a locked jobsite trailer located at Cajalco Road and Wood Road in Riverside, CA. The gauge was in its transportation case, which was chained to the floor of the trailer. The chain was cut and the gauge and its transportation case stolen. The local Sheriffs Department was notified and a police report was taken (Police Report No. PCR03361015). A newspaper ad will be placed as soon as possible offering a reward for return of the gauge. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2004-01-01
40415 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2003-12-28 08:49 | 2003-12-28 11:42 | 2003-12-31 | FISH KILL AT CRYSTAL RIVER REPORTED TO FLORIDA FISH AND WILDLIFE CONSERVATION COMMISSION "At 0849 [EST] on December 28, 2003, Progress Energy determined that the Crystal River Energy Complex experienced a fish kill reportable to the state of Florida. This was based upon an unusual amount of dead fish within the discharge canal. It has not been determined if this event is casually related to power operations of the energy complex. The Florida Fish and Wildlife Conservation Commission has been notified of an unusual fish kill at 0900 [EST on December 28, 2003]. This report has been provided in accordance with 10CFR50.72(b)(2)(xi)." The Licensee notified the NRC Resident Inspector. * * * UPDATE ON 12/31/03 @ 1954 BY SWEENEY TO GOULD * * * The Florida Marine Research Institute has evaluated the fish and water samples taken from the discharge canal. This event has been evaluated as not being casually related to power operations of the energy complex. The NRC Resident will be notified Notified Reg 2 RDO (Bonser) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-12-28
40414 | 0 | BROWNS FERRY | 1 | 2 | 3 | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-12-24 09:51 | 2003-12-24 13:37 | 2003-12-24 | FITNESS FOR DUTY A contract employee was determined to be under the influence of alcohol during a random test. The employee's access to the plant has been terminated. Contact the HOO for additional details. The NRC Resident Inspector has been notified. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Cold Shutdown | Power Operation | Power Operation | Cold Shutdown | Power Operation | Power Operation | NON EMERGENCY | 2 | AL | POW |  | 26.73 |  |  |  | 0 | 2003-12-24
40413 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-12-22 13:00 | 2003-12-24 09:34 | 2003-12-24 | OHIO AGREEMENT STATE REPORT - RADIATION DOSE TO UNINTENDED SITE DURING BRACHYTHERAPHY TREATMENT On 12/23/2003 at 1600 hours EST the licensee notified the Ohio Department of Health, Bureau of Radiation Protection, of the following information regarding a patient undergoing intravascular brachytheraphy treatment: "On December 22, 2003 during a treatment with a Novoste Beta-Cath 3.5 French IVB System, the source did not travel the entire way to the treatment site and was 3 centimeters proximal to the treatment site. The immediate cause of the event was a small kink in the delivery catheter which kept the source train from traveling to the correct site, even though the kink was not substantial enough to affect the flow of sterile water used to send/retrieve the sources. The error was discovered the next day during medical physics quality checks and reported to Ohio Department of Health, Bureau of Radiation Protection. An investigation will be performed the week of December 29, 2003." The dose to the unintended site was identified as 1840 rad (18.4 Gy) from a 0.05378 curie, Sr-90, sealed source. The attending physician has been notified. The intravascular brachytheraphy unit is a Novoste, model TDA-1040, serial number 91828. The Ohio Department of Health, Bureau of Radiation Protection reference number for this event is 2003-126. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-12-29
40412 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-12-22 | 2003-12-23 16:58 | 2003-12-23 | LEAKING P-32 SOURCE WIRE The following information was received via facsimile: "Houston licensee received an IVB [Intravascular Brachytherapy] source wire back from a hospital. Source wire was determined to be leaking upon leak test. Leaking Source, P32 IVB, approximately 85 millicuries of P-32. Leaking IVB source returned by unknown hospital in Lafayette, Louisiana to the manufacturer." Texas Incident Report I-8086. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-12-26
40411 | 0 | PENNSYLVANIA STATE UNIVERSITY |  |  |  | 1000 KW TRIGA MARK III | 2003-12-23 13:49 | 2003-12-23 16:38 | 2003-12-23 | TECHNICAL SPECIFICATION VIOLATION "A violation of Tech Spec 6.1.3.a.1 occurred when the reactor operator left the control room without removing the key from the console key switch. Tech Spec 6.1.3.a.1 states: "The minimum staffing when the reactor is not secured shall be: A licensed operator present in the control room, in accordance with applicable regulations." Interviews of the Duty RO and the Duty SRO and console indications determined the condition was present for about 11 minutes. All other conditions for the reactor being secured were met with the exception of the console key switch. Investigation determined positively that the reactor was "secured" in all aspects except for the key switch during the period of time when a licensed operator was not present in the control room." The licensee has notified the NRC Project Manager. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Research Reactor | NON-POWER REACTOR EVENT | [9 empty] | NON EMERGENCY | 1 | PA | NPR | [5 empty] | 0 | 2003-12-23
40410 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-12-22 15:30 | 2003-12-22 16:43 | 2003-12-22 | OFFSITE NOTIFICATION "FPL Energy Seabrook notified the EPA and NHDES [New Hampshire Department of Environmental Services] this afternoon [12/22/03] at 3:30 pm of unusually high impingement of small fish during the last two weeks caused by a series of strong storms. This notification was made under FPL Energy's Seabrook NPDES permit Part 1.A.24.e. "Most of the fish were small and included silversides, winter flounder, windowpane flounder, cod, smelt, and several other species. "The biomass of the fish was relatively small." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-12-22
40409 | 0 | ARKANSAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-12-04 | 2003-12-22 13:49 | 2003-12-22 | AGREEMENT STATE EVENT "A medical misadministration resulting from an I-125 permanent prostate seed implant procedure was reported to Arkansas Department of Health, Radiation Control and Emergency Management on December 19, 2003. The licensee reported that the misadministration, resulting from a December 4, 2003 implant procedure, had been identified during the patient's post-implant CT study on December 18, 2003. "The brachytherapy misadministration involves an underdose to an intended treatment area as well as a radiation dose delivered to an unintended area. This event is still under investigation by the licensee and the Department." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AR | OTH | AGR |  |  |  |  | 0 | 2003-12-25
40408 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-22 11:22 | 2003-12-22 14:39 | 2003-12-23 | NOTIFICATION OF UNUSUAL EVENT - EARTHQUAKE At 1116 PST on 12/22/03, an earthquake was felt on-site measuring 0.04g on plant seismic instrumentation. The licensee declared an Unusual Event at 1122 PST per EAL 18 (greater than 0.01g) . Both Units 1 and 2 continue to operate at 100% power. The local electrical grid is stable and all Emergency Diesel Generators are fully operable. A number of plant tank level were momentarily alarmed. The Unit 2 Main Turbine Electro-Hydraulic Control (EHC) pump tripped and was successfully restarted. Plant walk-down inspections are in progress. The licensee notified the NRC Resident Inspector. The National Earthquake Information center reports that the earthquake measured 6.5 R and was centered approximately 5 miles Northeast of San Simeon, CA or approximately 35 miles Northwest of the Diablo Canyon site. * * * UPDATE ON 12/23/03 @ 1526 BY HENDERSON TO GOULD * * * The licensee terminated the NOUE at 1212 PST following a 24 hour period after the earthquake. It was determined that the probability of an earthquake at this point is no greater than it was prior to the earthquake that occurred on 12/22/03. The licensee notified the NRC Resident Inspector. Notified R4DO (Smith), NRR EO (Reis), DIRO Manager (Nieh), FEMA (Eaches) and DHS (Bozzo). | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-12-22
40407 | 0 | US AIR FORCE |  |  |  |  | 2003-12-18 16:00 | 2003-12-22 11:40 | 2003-12-22 | MISSING TRITIUM EXIT SIGNS On 12/18/03 it was determined that two (2) tritium exit signs were missing at Cannon Air Force Base in New Mexico. Contractors were in the process of replacing a number of the signs and two of the signs appearing on the inventory list could not be found. The signs are made by SRB Technology (Sealed Source & Device Registration NC585S103G). The signs were purchased in 1998 with a maximum tritium activity of 25 curies and the current maximum tritium activity is 18 curies. Efforts to locate the signs continue. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-12-22
40406 | 0 | COMANCHE PEAK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-22 08:27 | 2003-12-22 11:39 | 2003-12-22 | REACTOR TRIP DUE TO MAIN TURBINE TRIP "At 0827 on 12/22/2003, Comanche Peak Unit Two (2) tripped due to a turbine trip > 50%. The turbine trip was caused by ingestion of a small metallic cover plate into the main generator exciter housing, as witnessed by maintenance personnel. A small fire ensued, which self-extinguished in five (5) minutes. An Aux Feedwater auto start (ESF actuation) occurred due to normal post-trip steam generator shrink. The turbine-driven and both motor-driven aux feedwater pumps started as designed. "All control rods inserted into the core upon trip. The local electrical grid is stable. The number one (1) steam generator atmospheric relief valve cycled as designed upon the secondary pressure transient. "The number three (3) Reactor Coolant Pump tripped during the transfer of power sources post-trip. "Unit 1 was not affected by the trip. Unit 2 is stable in Mode 3. Damage assessment is in progress which will determine future (near-term) plant mode of operation." RCPs are in operation transferring decay heat to the steam generators. Decay heat removal is through the MSIVs to the main condenser using the turbine steam dump valves. Both motor-driven AFW pumps are running to maintain Steam Generator levels. The trip of the number (3) Reactor Coolant Pump is being investigated. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 99 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-12-22
40405 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2003-12-22 03:00 | 2003-12-22 05:00 | 2003-12-22 | SITE AREA EMERGENCY DECLARED DUE TO UF6 RELEASE At 0245 CST, a small release of UF6 occurred lasting approximately 45 minutes. At 0300 CST the licensee declared a Site Area Emergency. The release has been terminated at the time of the notification. All personnel were evacuated within a 1 mile radius. At the time of notification, the evacuated personnel were allowed to return to their homes. The local sheriff has responded to the scene. NRC HQ and Region 2 NRC personnel are responding and a NRC Inspector is in transit to the site. The NRC entered Monitoring phase of Normal Mode at 0515 EST. The Acting NRC Chairman (Commissioner Merrifield) has been informed. There is no indication at this time of any malevolent activity. Initial reports indicated that there were no injuries at the plant, but three individuals offsite were taken to the hospital. Two have been released, and the third is being evaluated further prior to release. About 25 people offsite were temporarily evacuated and some 75 persons remained sheltered for a time in their homes. The licensee is evaluating the amount of material released. Licensee notified State of Illinois. NRC Headquarters also notified DHS-DOE (Mike Wyatt) The licensee terminated the Site Area Emergency at 0650 CST on 12/22/03. The release is over, the plant is stable and the licensee is in the recovery mode. The NRC exited the Monitoring Phase of the Normal Mode for this event at 1230 ET. Notified DIRO (S. Frant), NMSS EO (F. Brown), R2DO (T. Decker), USDA (L. Jensen), HHS (J. Little), EPA (Rawls), DHS (Frost), FEMA (D. Barden) regarding exiting Monitoring Phase of the Normal Mode. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | SITE AREA EMERGENCY | 2 | IL | FUE |  | 40.35(f) |  |  |  | 0 | 2003-12-22
40404 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-12-21 20:21 | 2003-12-22 00:31 | 2003-12-22 | POTENTIAL IMPACT TO SAFE SHUTDOWN DUE TO CONTROL COMPLEX VENTILATION INOPERABILITY "On 12/21/03 at 2021, it was discovered that the temperature control valve for the Division 1 Emergency Closed Cooling system had two blown fuses. This results in the Division 1 Control Complex chiller becoming inoperable. Concurrent with this the Division 2 Control Complex chiller was inoperable for planned maintenance. With this configuration both trains of safety related ventilation have been declared inoperable. This results in a loss of safety function for AC and DC distribution systems. Additionally this results in all Emergency Core Cooling systems being inoperable. "This is reportable under 10 CFR 50.72 (b) (3) (ii) (b) and (b) (3) (v) (a, b & d) for unanalyzed condition and loss of a single train safety system." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT UNABLE TO SAFE SD | POT RHR INOP | ACCIDENT MITIGATION | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) | 0 | 2003-12-22
40403 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2003-12-20 09:49 | 2003-12-20 13:00 | 2004-01-08 | RPS ACTUATION DUE TO LOSS OF TURBINE GENERATOR EXCITATION On December 20, 2003, at 0949 hours, an automatic reactor trip occurred due to a loss of excitation of the turbine generator. All plant safety functions were maintained throughout the event. The plant was stabilized in Mode 3. All plant safety systems responded normally with the exception of the 2C Auxiliary Feedwater Pump (steam driven) which tripped on mechanical overspeed. The 2A and 2B Auxiliary Feedwater Pumps (electric driven) functioned normally to restore the 2A and 2B Steam Generator levels. Post trip system anomalies include RCS Letdown isolated, Steam Generator Blowdown isolation valves closed, Control Room ventilation system swapped to recirculation mode, and the Fuel Handling Building ventilation system swapped to the Shield Building. An Emergency Response Team has been formed to review these conditions prior to plant restart. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to the automatic RPS Reactor Trip. All controls inserted properly. Decay heat is being removed using the turbine bypass valves. The Licensee notified the NRC Resident Inspector. * * * UPDATE ON 1/08/04 @ 0625 B Y BRADY TO GOULD * * * This update is provided to include the 10CFR50.72(b)(3)(iv)(A) notification criterion for the auxiliary feedwater actuation. The NRC Resident Inspector was notified., Reg 2 RDO(Fredrickson) was informed. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-12-20
40402 | 0 | COOK |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-19 18:44 | 2003-12-19 19:12 | 2003-12-19 | UNUSUAL EVENT At 1844 on 12/19/2003, D.C. Cook Unit 2 received seal injection low flow alarms. Upon investigation, a leak of approximately 30 gpm was identified on the North Seal Injection Filter housing. The abnormal procedure for RCS leakage was entered. An Unusual Event was declared at 1853. A team was dispatched to place the South Seal Injection Filter in service and isolate the North Seal Injection Filter. At 1929, the leak was isolated. The licensee is reviewing UE termination criteria at this time. The Licensee notified the NRC Resident Inspector. * * * UPDATE AT 2020 ON 12/19/03 FROM KEPPLER TO THOMAS * * * At 2015 EST on 12/19/03 D.C. Cook terminated the Unusual Event. Notified DIRO (Wessman), R3DO (Kozak), NRREO (Black), NSIR (Weber), FEMA, and DHS. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Power Operation | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-12-19
40401 | 0 | SOUTHWESTERN VERMONT MEDICAL CENTER |  |  |  |  | 2003-12-18 07:40 | 2003-12-18 15:33 | 2003-12-18 | MEDICAL EVENT At 0740 EST on 12/18/03, a radioactive tracer consisting of 14.6 millicuries of Technetium-99m was administered to a patient for cardiac imaging. After the administration, the technicians called the physician to come complete the examination. The physician informed the technicians that he did not order the administration. This event occurred due to a secretarial error. The dose was properly administered, and there were no adverse effects on the patient. The patient was notified of the error, and an incident report was submitted by the secretary. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | VT | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-12-18
40400 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-12-18 | 2003-12-18 10:52 | 2003-12-18 | AGREEMENT STATE REPORT REGARDING LOST TRITIUM SIGNS The State of Nebraska reported that one of their licensees could not account for 17 missing tritium exit signs. After performing a store inventory in early December, the licensee notified the state of Nebraska on 12/09/03 of the missing tritium signs. The signs were manufactured in 07/84 and each sign contained 21 curies of tritium at the time of manufacture. Three major renovations have taken place in the store since that time and the licensee believes that is when the signs were lost. Store records indicate that 11 new signs were purchased in 1994. A search of the store did not find any of the missing signs. The State of Nebraska considers this issue closed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2003-12-23
40399 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-12-17 | 2003-12-17 19:03 | 2003-12-17 | AGREEMENT STATE - POTENTIAL LEAK ON P-32 SOURCE WIRE The following is taken from an email received from the State of Texas, Department of Health: "This is a Texas agreement state incident being forwarded based on a 5 day report requirement for a leaking source. (Incident 8083) The Licensee reporting the incident is Guidant located in Pearland, TX, L05178. More information is anticipated. This is a preliminary report. "Today a returned P-32 [Phosphorus-32] source wire was received at our Pearland facility. This facility is authorized for radioactive material use under license number L05178. The source wires we manufacture are registered with the TX-BRC as TX-1070-S-101-S. These source wires are sent to our user sites [hospitals] and returned to Pearland for decay and disposal. "The active portion of the source wire was wiped during the receipt survey. Approximately, 8.0 nCi [nanocuries] of activity was removed at that time. The source wire was stored for investigation at that time. "A later wipe showed removable activity of approximately 0.5 nCi [nanocuries]. We will continue to investigate the source wire to determine if the wire is leaking or if the contamination was from another source." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-12-22
40398 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-12-17 12:30 | 2003-12-17 15:17 | 2004-08-30 | AGREEMENT STATE REPORT - STOLEN TROXLER GAUGE On 12/16/03 at approximately 1230 MST, a soil moisture density gauge was stolen from the rear of a technician's pickup truck while he was stopped for lunch at 23rd Street and Indian School. The gauge was contained in a yellow transport case and is a Troxler Model 3430, Serial Number 33308. The gauge contains approximately 10 millicuries of Cesium-137, and 40 millicuries of Americium-241. The theft of the gauge was reported to the Arizona Radiation Regulatory Agency at approximately 1325 MST. The licensee issued a press release offering a $500.00 reward for the recovery of the gauge. The Arizona Radiation Regulatory Agency and the licensee will continue to investigate this occurrence and report further. The FBI, States of CA, NV, NM, CO, and the country of Mexico are being notified of this event. * * * UPDATE PROVIDED VIA FAX BY A. GODWIN TO JEFF ROTTON AT 1405 EDT ON 08/30/04 * * * "After working hours on 08/27/04, the [Arizona Radiation Regulatory] Agency was notified by the licensee, that a non-employee had contacted them and returned the missing Troxler Model 3430 gauge. "The FBI, States of CA, NV, NM, CO and the country of Mexico are being notified of the recovery. Notified R4DO (Jones), NMSS (Brach), and Mexico (V. Gonzalez). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-12-22
40397 | 0 | LASALLE | 1 | 2 |  | [1] GE-5,[2] GE-5 | 2003-12-17 11:30 | 2003-12-17 13:03 | 2003-12-17 | REFUELING EQUIPMENT RECEIVED AT LASALLE STATION EXCEEDING RADIATION LIMITS "This notification is being made in pursuant to Exelon Reportability manual RAD 1.11 and 10 CFR 20.1906(d)(2). At 11:30 CST on 12/17/03, Radiation Protection Technician notified the Shift Manager that a Radiation Shipment (03-1216-02) was received at LaSalle from Duratek (Memphis, TN) that exceeded 200 mrem/hr on the external surface of the package. In accordance with 10 CFR 71.47(b)(1) the package was not in a closed transport vehicle and thus did not meet the exclusion to allow the package to be greater than 200 mrem/hr and less than 1000 mrem/hr. The as found readings on the package were measured at 211 mrem/hr and verified with a second instrument at 207 mrem/hr. The package was also surveyed for contamination and found to be free of loose contamination. Pursuant to 10 CFR 20.1906(d)(2), the final delivery carrier (R&R Trucking Co) was also notified of this event." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EXTERNAL RAD LEVELS > LIMITS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 20.1906(d)(2) |  |  |  | 0 | 2003-12-17
40396 | 0 | SAN ONOFRE |  |  | 3 | [1] W-3-LP,[2] CE,[3] CE | 2003-12-17 03:15 | 2003-12-17 08:35 | 2003-12-17 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO LOSS OF BOTH TRAINS OF SAFETY INJECTION The following information was obtained from the licensee via facsimile: "1. SYSTEMS AFFECTED: High Pressure Safety Injection (HPSI), Low Pressure Safety Injection (LPSI), Recirculation Actuation [System] (RAS), Containment Spray (CS). "2. ACTUATIONS AND THEIR INITIATING SIGNALS: None "3. CAUSES: 400 [volt] Motor Control Center (MCC) 3BE deenergized due to an overcurrent condition on the 'A' train 1E bus. 'B' train equipment is cleared for maintenance causing Technical Specification 3.0.3 entry. "4. EFFECT OF EVENT ON PLANT: Both trains of Safety Injection equipment inoperable with no flow capability requiring plant shutdown. "5. ACTIONS TAKEN OR PLANNED: Shutdown commenced at 0410 [PST]. MCC 3BE is stripped and loads will be checked for faults while attempting to restore the bus. Train 'B' equipment will be restored as soon as possible. "Continuation Sheet: Power/Mode will be reduced per T.S. 3.0.3 action until MCC 3BE loads restored or Tr[ain] 'B' equipment returned to service. [Plant required to be in] Mode 3 [within] 7 hrs, Mode 4 [within] 13 hrs. [and] Mode 5 [within] 37 hrs. No abnormal electrical lineups. No effect on Unit 2. LPSI pump/valves will need to be restored to allow Mode 5 entry." Plant personnel suspect a problem with the 1E bus feeder breaker. A new breaker will be installed after testing is completed. Bus loads are in the process of being checked for problems. At the time of the initial call, plant power was at 80% and decreasing at approximately 10% per hour. At 0939 PST, plant power was at 71% and decreasing. The 1E bus have been meggered with no problems found. Battery chargers are currently not operating due to loss of the buses but not expected to be a problem since DC loads are very low during mode 1 operations. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 80 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 4 | CA | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-12-17
40395 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-12-15 | 2003-12-16 19:28 | 2003-12-22 | Xe-133 SOURCE LOST DURING SHIPMENT "On December 16, 2003, GE Vallecitos contacted RHB-Sacramento office to report that a shipment of 2.1 Ci [Curies] of Xe-133 to the University of Alabama has not arrived at its destination. On the same day, RHB-Berkeley office contacted the GE Vallecitos RSO, C.W. Bassett and the EHS leader, D.W. Turner and learned the following: On December 12, 2003, GE Vallecitos sent a shipment of 2.1 Ci of Xe-133 to the University of Alabama via Fedex. On December 15, 2003,one of the Vallecitos technicians noticed that the shipment had not arrived at its destination in Alabama. They contacted Fedex immediately [name deleted] and the tracking database indicated that the shipment supposedly left Oakland Friday. As of December 16, 2003, Fedex was unable to locate the final destination of the shipment. GE Vallecitos had contacted the University of Alabama and confirmed that they have not received the Xe-133 shipment. Per RSO, the current estimated activity (as of 12/16/03) of the Xe-133 shipment is 1.2 Ci [Curies]. * * * UPDATE 1115 ET 12/22/03 FROM R. GREGOR TO J. ROTTON * * * The following information was received via email: "This lost shipment was found Friday 12/19/03 at the Fed Ex warehouse facility in Memphis, TN. It has been shipped to it's original destination, the University of Alabama." Notified R1DO (R. Lorson), R2DO (T. Decker), R4DO (L. Smith), NMSS EO (F. Brown, Bill Reamer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-12-19
40394 | -1 | PEACH BOTTOM |  | 3 |  | [2] GE-4,[3] GE-4 | 2003-12-16 15:40 | 2003-12-16 19:11 | 2004-01-14 | HIGH PRESSURE COOLANT INJECTION SYSTEM INOPERABLE "During the performance of planned Unit 3 "High Pressure Coolant Injection (HPCI) Pump, Valve, Flow and Unit Cooler Functional and In-Service Testing" the HPCI turbine exhaust line drain valve remained open for longer than expected. The test was aborted and troubleshooting was initiated to determine the cause of this unexpected result. The HPCI system is being maintained in an available status but maintained Tech. Spec. inoperable pending additional evaluation." The licensee notified the NRC Resident Inspector. * * * UPDATE AT 1408 EST ON 1/14/04 FROM DAVE FOSS TO S. SANDIN * * * The licensee is retracting this report based on the following: "The purpose of this notification is to retract a previous report made on 12/16/03 at 1540 hours (EN# 40394). Notification of the event to the NRC was initially made as a result of declaring the Unit 3 High Pressure Coolant Injection (HPCI) system inoperable when unexpected conditions were found during performance of routine Inservice Testing of HPCI. Specifically, during an Inservice Test of a check valve associated with the leak off collection and transfer subsystem of HPCI, it was noted that additional leak-off inventory was being collected in the HPCI gland seal condenser than what had been noted during other tests. At the time, concern existed as to whether excessive condensate existed on the steam side of HPCI and therefore, HPCI may not be able to perform its safety function. HPCI was considered available, but Technical Specification inoperable. "Since the initial report, Engineering has determined that HPCI was fully capable of performing its safety function. The additional condensate inventory observed relative to other tests previously performed was due to the results of a revision to the test approved on 1/23/03. This revision re-ordered the sequence of stroking various HPCI related valves. Although this re-sequencing was an overall enhancement to the test quality, it resulted in the potential for additional condensate inventory existing in the leak-off collection and transfer subsystem depending on system conditions. Since the HPCI steam supply valve (MO-14) is now stroked earlier in the test, there resulted a condition where additional leak-off condensation could collect in the leak off collection and transfer subsystem. Appropriate testing and analysis was performed on this subsystem and it was verified that it was operating properly to remove condensate from the steam side of HPCI. The unexpected condition found during the test has been entered into the site-specific corrective action program for resolution (CR 191222). The NRC resident has been informed of the retraction." Notified R1DO(Holody). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-12-16
40393 | 0 | AUTOMATIC VALVE |  |  |  |  | 2003-10-16 | 2003-12-16 15:01 | 2003-12-16 | 10 CFR 21.21 POTENTIAL FAILURE OF SOLENOID OPERATED VALVE TO CLOSE AT ELEVATED AIR PRESSURE The following is taken from a facsimile from Automatic Valve: "Describe Problem (Initial Concern and Symptoms): On 10/16/2003 Paul Chenell of Dresden reported that a B7122-145, serial number 64065 shipped on 12/11/2002, valve failed to exhaust air with both solenoids de-energized causing the CRD valve to remain in the open position. "On 10/17/2003 the valve was delivered to Automatic Valve for analysis of the problem. Contain Symptom (Action): Re-inspect all existing 6910-001 plungers to verify the correct overall length (Done 10-17-03). Rebuild, retest, and return the B7122-145 valves to Dresden (Shipped 11-26-03). Notify customers potentially impacted, by Fax, to inspect plunger lengths (10/24/03). Inspect all units installed at Dresden station (completed 10-30-03, 15 of 274 plungers found out of specification) Inspect all units installed at Cooper station (completed 10-29-03, 0 of 64 plungers found out of specification) Hold shipment for all 6910-001 plungers from suspect lot. "Root Cause/s of Problem: 10 CFR Part 21 Report Required: Yes The valve was first functionally tested in the normal manner- that is at 35 psig low pressure & at 145 psig high pressure. The valve functioned without problems at low pressure but failed to return to its normally closed position at 145 psig when both solenoids were de-energized. Further functional testing revealed that at an inlet pressure of approximately 100 psig the valve would fail to return when de-energized. "When the valve was disassembled, the plunger in the number 2 solenoid, the left hand solenoid when facing the exhaust port, was found to be approximately .020 too long - 1.315" compared to the specified length of 1.290 +.005/-.003. Because the plunger only has a total stroke of less than .030, the natural expansion of the seal material in the plunger, due to a combination of heat and pressure, combined with the out of specification length created a situation where the plunger had no room to move and thus exhaust pilot air when the solenoid was deenergized. "The root cause of the failure is the out of spec plunger. Procedures require the lengths of all plungers to be inspected prior to use. "Analysis of the results of measurement testing revealed an unexpected degree of variation In recorded lengths. Variation was traced to the use of different types of equipment and the inherent difficulty in measuring compressible material with pressure sensitive measurement devices. This may have lead to some units being categorized as In specification initially and out of specification at subsequent inspection. (Refer to corrective action 5.1). "Notwithstanding measurement variation, the primary root cause of the observed plunger dimensions is changes to the length of the fluorocarbon insert after it is pressed into the plunger body. This variation is detectable and beyond measurement uncertainty. "Dissection of returned plungers revealed abnormal compression set among all plungers which were beyond specification limits and normal compression set among plungers which were within specification limits. "Chemical analysis and durometer testing did not show any significant differences In the chemical properties or material hardness of the lot or in previous lots of identical insert material. "However, the following results were obtained when plunger insert samples were compressed by 23 for 24 hours at 230 degrees F: "Scenario [Average Set %, # tested] Unused insert, suspect lot, visible set, as received [92%, 3] Unused insert, suspect lot, visible set, post cured at 260 F [11%, 2] Unused insert, previous lot no visible set, as received [10%, 3] Unused insert, suspect lot no visible set, as received [9%,, 2] Field return Insert, suspect lot, visible set [36%, 4] Field return Insert, suspect lot, no visible set [10%, 2] "From this we concluded that there is a cure problem with a portion of the suspect lot and that post cure takes place when the solenoid is continuously energized. Based on the test results, we believe that a portion of the lot was not properly post cured. "The degree of growth of the plunger insert due to compression set is observed to be variable. This depends on exact dimensions of the molded insert when installed, the ID of the plunger retaining the insert and the exact cure duration variation of the bad plunger inserts. "The degree of growth also seems to be terminal. Returned plungers (field failure) and other samples from the suspect lot on hand) at Automatic Valve have not changed dimensions during the period of study. Five plungers tested at 200 degrees F for five days exhibited thermal expansion and did not detectably change size when cooled down. Ten plungers subjected to 230 degrees F for ten days exhibited thermal expansion and did not detectably change size when cooled down. (Refer to corrective action 5.2, 5.3) 5. Corrective Action: 5.1) Specific individual measurement equipment is specified for plunger measurement. 5.2) Specific lot definition based on curing process (as opposed to pre-vulcanized rubber lot) to define lot homogeneity for all plunger inserts 5.3) A sample of each homogeneous processed sample to be tested for compression set as part of dedication process. Test Conducted to Verify It: Test samples to be placed under worst case temperature and pressure characteristics for a period of 10 months. "6. Implementation (Describe: Include Applicable CN Numbers): CN 8897 defines lot and compression set and measurement characteristics for 6910-001 plungers.. "7. Corrective Action to System to Prevent Recurrence: To be determined. "The following plants have components containing the suspected lots as follows: Nebraska Public Power - Cooper Station Exelon - Limerick, Peach Bottom, Quad Cities, Dresden" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 3 | MI | OTH | PAR | 21.21 |  |  |  | 0 | 2003-12-16
40392 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-12-10 | 2003-12-15 12:07 | 2003-12-15 | AGREEMENT STATE REPORT - LOST TRITIUM EXIT SIGNS The State of Nebraska was notified by letter dated December 10, 2003 of 4 (four) unaccounted for exit signs during an inventory conducted by the licensee, Novartis Consumer Health Inc., 10401 Highway 6, Lincoln, NE 68517. The signs, identified by the licensee as item numbers 4, 5, 8, & 10, are believed to have been lost during various renovations to licensee facility buildings occurring over a period of years. The licensee is unable to confirm the exact time or disposition of the signs but does not suspect theft. The make, shipping date, model number, serial number, and activity level of the exit signs are as follows: Item numbers 4 and 5: NRD, shipped last quarter 1984, model T4002, serial number 6988/6989 respectively, each containing 19.9 curies tritium. Item number 8: SRB, shipped 02/10/88, model B100, serial number 64174, containing 17.2 curies tritium. Item number 10: SRB, shipped 02/08/88, model B100, serial number not identified, 15.5 curies tritium. The State of Nebraska will not assign this event an incident number and considers this event to be closed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2003-12-18
40391 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-12-12 12:24 | 2003-12-12 14:39 | 2003-12-12 | BOTH TRAINS OF COMPONENT COOLING SYSTEM INOPERABLE. "On 12/12/2003 , at 1224 both trains of Component Cooling System were declared inoperable. The governance by the KNPP Technical Specification (3.3.d) requires that actions commence within an hour to place the plant in Hot Standby within 6 hours, Hot Shutdown within the following 6 hours, and to achieve the RCS Tavg less than 350 degrees F by use of alternate heat removal methods within an additional 36 hours. The issue stemmed from the discovery of liquid on R-17 (Component Cooling Radiation Detector) detector housing at the location of a air port. Liquid from this port was chemically tested to contain chemicals (molybdates and sulfites) currently found in the Component Cooling system. It was determined that this leak violated guidance in Generic Letter 90-05 and thus rendered both trains of component cooling inoperable due to this being in a common header. A Technical Specifications guided background has commenced at 1315 on 12/12/2003." At the time of the call, reactor power was 84% and decreasing. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if need. The electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | UNANALYZED CONDITION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(ii)(B) |  |  | 0 | 2003-12-12
40390 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2003-12-12 11:00 | 2003-12-12 14:36 | 2003-12-12 | GEORGIA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE On 12/12/03 at 1100 ET, a licensee's pickup truck was stolen with a moisture density gauge locked in the bed of the truck. The truck was parked at a construction site on Northside Drive in downtown Atlanta, GA. The gauge is a CPN Model MC Porta-Probe, Serial Number MD60703301. The gauge contained two sources: 50 milliCuries Am241/Be and 10 milliCuries Cs-137. The licensee has reported the theft to the Atlanta Police Dept. and the Atlanta Field Office of the FBI. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2003-12-17
40389 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-12-12 11:19 | 2003-12-12 14:33 | 2003-12-12 | BOTH TRAINS OF AUXILIARY FEEWATER WERE DECLARED INOPERABLE FOR ONE HOUR AND 22 MINUTES. Surry Power Station has determined that an unanalyzed condition related to Auxiliary Feedwater (AFW) isolation during a steam generator tube rupture (SGTR) event exists. The existing accident analysis for a SGTR requires that AFW to the ruptured steam generator (SG) be isolated prior to the water level in that SG rising into the main steam pipe. Failing to take these actions could result in a radioactive release or failure of equipment important to safety, which has not been previously analyzed. The current configuration of the AFW system has six motor operated valves (MOVs), two for each SG, which are used to control flow from one of two AFW headers. Three MOVs are powered from "H" emergency bus and three MOVs are powered from "J" emergency bus. The MOVs are maintained normally open. With a loss of emergency power to either train of AFW MOVs, the control room operators are not able to close the three MOVs from the de-energized emergency bus without manual action inside containment. A review of the plant safety analysis design basis indicates that with this AFW configuration, isolation of AFW to a ruptured SG would not be possible within the time frame specified in the analysis. Unit One and Unit Two entered a TS 3.0.1 clock at 1119 hours on December 12, 2003 due to the AFW systems being declared inoperable. The station took immediate actions to address the configuration control issue in order to meet the assumptions made in the SGTR accident analysis and both Unit One and Unit Two exited the TS 3.0.1 clock at 13:41 hours on December 12, 2003. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-12-12
40388 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-12-11 23:35 | 2003-12-12 01:25 | 2003-12-12 | MANUAL SCRAM DUE TO UNEXPECTED STATOR WATER COOLING RUNBACK Manual scram was inserted during a Stator Cooling Runback that was not expected. Cause of the Stator Cooling Runback is under investigation. Group 2 & 3 Primary Containment Isolation System (PCIS) isolations occurred as expected due to reactor level drop during the scram. All other systems operated as expected. All controls rods were fully inserted during the manual scram. The MSIVs are open with decay heat being removed via steam to the main condenser using the turbine bypass valves. The condensate and feedwater system is in operation maintaining reactor vessel water level. Current Reactor Pressure is 880 psig and Reactor Level +30 inches. The electrical plant lineup is stable and in a normal lineup for this condition. The manual scram of this unit had no affect on the other unit onsite which is in a refueling outage. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-12-12
40387 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2003-11-24 | 2003-12-11 14:06 | 2003-12-11 | KENTUCKY AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION On 11/24/03 a patient was administered a thyroid uptake dose of 0.98 millicuries. The prescribed dose was 0.015 millicuries. The misadministration apparently occurred due to the prescription order being made incorrectly with no subsequent verification. The patient and the patient's physician were notified on 11/26/03. No adverse effect to the patient occurred as a result of the misadministration. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | KY | OTH | AGR |  |  |  |  | 0 | 2003-12-16
40386 | 0 | THOMAS JEFFERSON UNIV. HOSP. |  |  |  |  | 2003-11-12 05:00 | 2003-12-11 13:46 | 2003-12-11 | VIAL CONTAINING 1.07 MILLICURIES OF SULFUR-35 WAS ACCIDENTALLY PLACED IN TRASH. On 11/10/03 a package containing two vials of P-32 and one vial of S-35 was delivered to Thomas Jefferson University Hospital Radiation Safety Office. The package was surveyed. The two vials of P-32 were picked up. The person who was to pick up the S-35 vial was not around. The trained Radiological Lab Tech obliterated the package radiation material markings thinking that the person picking up the S-35 was going to pick it up. The person to pick up the S-35 did not show up . A Lab person saw the open package without any radioactive material markings on the outside of the package and, not knowing that the S-35 vial was inside the package, placed the package in the trash, the afternoon of 11/10/03. The trash was removed by the custodian and placed in the dumpster the morning of 11/11/03. Later the trash was picked up by the trash collection company and eventually placed in a landfill. Corrective action has been taken by the licensee to prevent this type incident from occurring in the future. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-12-11
40385 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-12-09 | 2003-12-11 11:30 | 2004-01-22 | TEXAS AGREEMENT STATE REPORT INVOLVING FIRE WITH RADIOACTIVE MATERIAL "On December 10, 2003, [the licensee's RSO at] Waste Control Specialist reported a fire involving radioactive material that occurred on December 9, 2003. There was no excessive exposure to individuals nor was there any off-site airborne release. "The waste processing company believes reactive metals (lithium, sodium, potassium) oxidized in water to start the fire. Packing materials were placed in a shredder that feeds into a hopper containing mixed waste. The system is closed with HEPA filters in place. Vibrations from the hopper may have resulted in the ignition. The material burned for about 20 seconds and was extinguished. When more materials were poured into a mix pan, the fire reignited and again was quickly extinguished. "According to the Licensee's preliminary calculations, the affected or burned radioactive material exceeded the reportable quantity of five times an ALI [annual limit on intake]. The total radioactive material in the mix pan was under 50 microcuries. The shredder contained about 2.4 microcuries. There were 12 to 14 radionuclides involved. The Licensee will send a detailed written report within 30 days to include specifics on radionuclides and activities. "The most serious consequence was the unplanned fire. The building is pressurized and the smoke from the fire was pulled through HEPA filters and a monitored exhaust system. The workers wear PPE [personal protective equipment) and airlines with protection factors of 1000." Texas Incident # I-8024. * * * * UPDATE ON 1/21/4 AT 1651 EST TO M. RIPLEY FROM HELEN WATKINS VIA FACSIMILE * * * * The following information was provided in a letter dated 1/6/2004 from Waste Control Specialists (WCS) to the Texas Department of Health: "On December 9, 2003 at approximately 1400 hrs a small fire occurred in the Permacon building at our facility located 30 miles West of Andrews, Texas. This fire occurred in the hopper beneath the waste shredder. There was a small quantity of untreated water reactive radioactive waste (WP-019224) that caught fire after passing through the shredder above. Two employees at the scene quickly extinguished the fire within the hopper using hand-held halon fire extinguishers. The hopper was pulled from underneath the shredder and then the waste was put into the mix pan where it re-ignited. It was extinguished by dropping water on the materials using the prentice arm. "The personnel who were in the immediate area were wearing anti-contamination clothing and respiratory protection equipment in accordance with the Radiation Work Permit. The air sample that was being collected at the time of the incident indicated approximately 85% of the DAC for Th-228. The respiratory protection equipment used has a protection factor of 1000. There was no significant internal or external radiological exposure to personnel." "The radioactive distribution of the material involved is enclosed." Additionally, the licensee provided the following information to the State in response to a question about any action the licensee may have taken to prevent a reoccurrence of a fire. The licensee stated the following in an email to the State: "WCS issued a Stop Work Order on December 9, 2003. The Stop Order included a corrective action of 'Evaluate the treatment methodology for reactive metals prior to receipt of new shipments of reactive metals for processing.' WCS will not receive any new shipments of reactive metals for processing until such time that a different treatment methodology is developed to process these wastes without subsequent ignition of waste materials." Notified R4DO (L. Howell) and NMSS EO (L. Kokajko) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-12-16
40384 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2003-12-10 18:00 | 2003-12-10 23:49 | 2003-12-11 | REDUCTION IN ACCIDENT MITIGATION DUE TO IMPROPER HPCI SUCTION TRANSFER "During the performance of planned Unit 2 High Pressure Coolant Injection (HPCI) Logic System Functional Surveillance testing an unexpected condition occurred. It was observed during the HPCI suction swap from the Condensate Storage Tank (CST) to the Torus, that the CST level lowered and the Torus level rose unexpectedly. At that time, the test was aborted and the system was restored to an available status but maintained Tech. Spec. inoperable pending additional evaluation. Following the evaluation, it was determined that the HPCI system Torus suction check valve permitted reverse flow. The HPCI system could not be restored to an operable status and requires additional troubleshooting and maintenance to return to an operable status." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-12-11
40383 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-12-08 | 2003-12-10 22:02 | 2003-12-10 | AGREEMENT STATE REPORT - SEALED SOURCES DAMAGED IN FIRE "Licensee reported that several months ago, four (4) 'sensor units' on fixed GL [General License] gauges it manufactures were involved in a fire at one of their customer sites in Painesville, Ohio. The RSO did not know the exact date of the fire. The sealed source used in these units is the AEA, AMC, P1, 150 milliCurie Am-241. Two of the units appeared burned and the other two appeared undamaged. The licensee had the customer do wipes on these which were negative. Then the units were shipped back to the licensee where they are now. On 12-08-03 the RSO was disassembling the worst-looking one in preparation for shipment back to the source manufacturer, AEA Technology. Wipes were done. The RSO detected elevated readings up to 200 cpm (background is 2-3 cpm) from the burned area of source S/N 4382LX mounted on probe sensor S/N 2851 using a Ludlum Model 12 alpha meter. "Per the RSO, sources have been secured and contained pending further instructions. RSO indicated surveys were done of work area and personnel and no contamination was detected. The State is initiating an investigation and will send an inspector to the licensee for surveys." The State reported that the gauge is a model # 103. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-12-15
40382 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-12-10 19:19 | 2003-12-10 21:12 | 2003-12-11 | SAFEGUARDS REPORT Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures have not been employed. The licensee will notify the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE from R. Lowery to R. Jolliffe at 1100 EST on 12/11/03 * * * The licensee provided additional information about this event. Contact the Headquarters Operations Officer for additional details. Notified R4DO (D. Graves) and TAS (J. Whitney) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-12-10
40381 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-12-09 19:00 | 2003-12-10 16:19 | 2003-12-10 | OFFSITE NOTIFICATION FOLLOWING COMMUNICATION ERROR DURING EMERGENCY PLAN DRILL "On December 9, 2003, at 1900 hours, an unannounced emergency planning staff augmentation drill was initiated via a staff augmentation vendor. An incorrect message was inadvertently sent out. The message described a chemical spill and advised people to take shelter. The message did not indicate that there was an emergency at Palisades. It named a chemical plant in another town. An attempt to send the correct message was made, and the same erroneous message was sent. The erroneous message was only sent to plant personnel, however, several responders who received the message called local agencies to find out more about the emergency described in the message. (Note there was NO actual emergency at Palisades or at a chemical plant.) Various agencies then called the plant to request information. Courtesy calls were made later to state and local agencies that might be affected to explain the error in the message. Information was also FAXed to the agencies so they could make further courtesy calls. The error was also discussed with local media, although no press release had been issued. "There was no impact on plant operations. "This report is not being made within the required time period. The original review for reportability was made before the outside agencies were notified, and the error was believed to be an internal communication error. The Senior Resident Inspector was notified of the communication error. Plant staff had not planned on discussing it with outside agencies. However, once subsequent discussions were initiated, it was not immediately recognized that the NRC should be notified." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-12-10
40380 | 0 | SOUTH TEXAS | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-09 15:38 | 2003-12-09 17:32 | 2003-12-09 | UNABLE TO ACHIEVE COLD SHUTDOWN USING NATURAL CIRCULATION AT A COOLDOWN RATE OF 50 DEGREES PER HOUR "At 1538 on 12/09/03, it was determined that the plant could not achieve cold shutdown using Natural Circulation with the available volume of the Auxiliary Feed Water Storage Tank [AFWST] and at an allowed plant cooldown rate of 50 degrees F/hour. The plant has a functional objective to achieve Plant Shutdown from Operating Condition to Cold Shutdown Condition with the Natural Circulation Cooldown process with the volume of water available in the AFWST. Natural Circulation cooldown is required during Loss of Offsite Power (LOOP), long term cooling, Safety Grade Cold Shutdown and Appendix R type fire with LOOP. This condition also applies to Unit 2. "STP [South Texas Project] changed from a Reactor Vessel Head (RVH) T-Hot Plant to a RVH T-Cold Plant after replacement of the plant's steam generators. As a result, the plant cooldown rate under natural circulation conditions was changed from 25 degrees F/hour to 50 degrees F/hour based on a Westinghouse evaluation. "While performing confirmatory calculations to address a fire safe shutdown issue, it was determined that the plant can be cooled down with two steam generators using natural circulation. However, at a cooldown rate of 50 degrees F/hour, the two steam generators not being used for cooldown would stagnate with hot water in the primary side tubes. During the depressurization process, the hot water flashes to steam such that depressurization below approximately 1000 psig is significantly challenged. This results in filling the pressurizer and a loss of RCS pressure control. The fluid in the RCS [Reactor Coolant System] loops not receiving AFW will remain at saturated conditions until cooling is achieved by other means. "Cooldown and depressurization of the RCS in this configuration will take substantially longer than assumed in the current analyses. Although there is adequate core cooling, the plant will be in a condition that is outside the existing design basis and not specifically addressed by the Emergency Operating Procedures. Therefore, this condition resulted in the plant being in an unanalyzed condition that significantly degraded plant safety. "Thermal Hydraulic Analyses at a cooldown rate of 25 degrees F/hr demonstrated that natural circulation will occur in the two steam generators that are not being used for cooldown such that the stagnated hot water conditions would not occur in these steam generators. This would allow for depressurization of the reactor coolant system and successfully meet the functional objective. A compensatory action is in place to limit natural circulation cooldown rate to no greater than 25 degrees F/hr." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 4 | TX | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-12-09
40379 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-12-09 15:59 | 2003-12-09 17:12 | 2003-12-09 | INFORMATION ONLY - SEISMIC ACTIVITY FELT AT NORTH ANNA POWER STATION At 1559 EST on 12/09/03, Seismic activity was felt at North Anna Power Station (NAPS). Both units continue to operate at 100 percent power with no problems. Seismic monitoring systems did not pick up the event. The earthquake was centered 15 miles Southeast of Colombia, VA (29 miles from NAPS) and registered 4.5 on the Richter Scale. Initial plant walk downs have identified no issues. Operations and engineering are continuing to walk down the units to identify problems that are undetectable from the control room. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INFORMATION ONLY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2003-12-09
40378 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-12-05 23:49 | 2003-12-06 04:44 | 2004-01-09 | A LEVEL 3 LOW REACTOR WATER LEVEL WAS REACHED DURING A REACTOR WATER LEVEL TRANSIENT The reactor was being shutdown as part of a planned evolution to allow repairs on the Reactor Water Cleanup flange leak. After the Reactor Protection System Mode Select Switch had been placed in shutdown, the resulting reactor level transient caused the Level 3 low reactor level set point to be reached. The Reactor Protection System had already been de-energized and the lowest level reached during the transient was +2 inches. This level transient is a normal occurrence on a reactor shutdown, and level was restored to the normal operating band. There was no effect on the plant due to reaching the low level set point. No other abnormal plant response was noted. The licensee will notify the NRC Resident Inspector * * * RETRACTION ON 1/9/04 AT 1310 FROM CLYDE BAUER TO E. THOMAS * * * "Upon further review of this event, the resulting Level 3 low reactor water level signal following the manual scram is considered part of the pre-planned sequence in accordance with the guidance of NUREG-1022. Therefore, this event is not reportable under 10 CFR50.72(b)(3)(iv)(A) and is being retracted." Notified R1DO (J. Noggle) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-12-06
40377 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-12-03 | 2003-12-05 18:52 | 2003-12-05 | Cs-137 SOURCE CONTAINED WITHIN A LIQUID SCINTILLATION COUNTER WAS FOUND TO BE LEAKING The following is taken from a facsimile received from Texas Department of Health [TDH], Bureau of Radiation Control: "Event Description: A 30 microcurie cesium-137 source located in a scintillation counter was found with 430,000 cpm counts on a swab leak test conducted by a serviceman. No contamination was found outside the source assembly. "Texas Incident No. I-8024 The Licensee's report to TDH was also faxed to the NRC and is identified, in part, below: "On December 3, 2003, the Radiological Safety Officer at Texas A&M University (TAMU) was notified by a service representative of Beckman Coulter that a Cs-137 source contained within a liquid scintillation counter was leaking. After obtaining information from the service representative, the RSO then made a telephone notification to the Texas Department of Health-Bureau of Radiation Control, informing Ms. Helen Watkins of the situation. "This letter is a written notification of the leaking sealed source, in accordance with TAC 289.202 (ddd). The following information identifies the liquid scintillation counter and specifies of the source: Location: Chemistry Bldg., Room 2516 Manufacturer: Beckman Model: LS 6000 SE S/N: 7060437 Source: Cs-137 Activity: 30 uCi [microcuries] "The device user, a professor at TAMU, noticed that the device was not operating properly and contacted Beckman for service. The service representatives performed diagnostics on the device including a smear (cotton swab) of the plastic sphere source. The swab was counted with a result of approximately 430,000 cpm [counts per minute]. No parts have been removed from the device, but the intention is to replace the source, source housing, and source elevator. These components will then be returned to Beckman. Repair parts have been ordered. The device has been removed from service with signage indicating 'No Usage' and 'Contact Radiological Safety.' In addition, Environmental Health and Safety Department (EHSD) personnel performed contamination surveys on the device, the service representatives, and within the room. No contamination was detected." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-12-10
40376 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2003-12-04 | 2003-12-05 11:54 | 2008-08-26 | AGREEMENT STATE REPORT- FLORIDA - LOST OR STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was received via facsimile and telephone conversation: "Loss of Control - Lost, Abandoned, or Stolen Materials "Incident Location: Suspected Florida Department of Transportation (FDOT) job site at US1 just north of North Bridge Road, St. Lucie, Florida in unrestricted area. "Incident Description: POC [Point of Contact] reported he looked for gauge in the bed of transport truck this AM. Gauge was not in carrying case. He believes he left the gauge at the job site on 4 Dec. He has the locks for the transportation case and the box attached to the truck bed and they were intact. The gauge handle was locked and he has the keys. He had a crew in Ft. Pierce make a futile search for the gauge at the work site. He called the Ft. Pierce PD [Police Department] and they had no reports of a gauge being found. This office requested a press release and reward for the return of the gauge be issued and the gauge be reported lost or stolen to the Ft. Pierce PD. Further investigation of this incident will be by the Radioactive Materials section." The subject gauge is a Troxler model 3440, serial number 20515, 40 milliCuries Am-241:Be, 8 milliCuries Cs-137 moisture density gauge licensed to the FDOT. Florida incident number FL03-217. * * * UPDATE FROM THE STATE OF FLORIDA (FURNACE) TO HUFFMAN AT 1031 EDT ON 8/26/08 VIA FACSIMILE * * * "[On August 13, 2008,] a scrap truck tripped portal alarm [at a metal recycling facility - Trade Mark Metals]. [The scrap metal container] was rejected and returned to owner. [Redacted information] [The scrap metal] owner found what appear[ed] to be a bus door opener handle [as the] source [of the radioactivity]. An investigator [from the State] was dispatched to survey the source. The remaining load was accepted by Trade Mark Metals. "[The] 'Handle' [was determined to be] a part of a soil moisture density gauge [containing the CS-137 source and] originally belonging to Florida DOT, and reported stolen 05-Dec-03. Incident number FL03-217, original NRC Event number 40376 [see above]. Other parts of the load were surveyed for the Am-241/Be source, [however] no radiation [was] found emitting neutrons [and no other parts of the gauge found]. [The original gauge] owner [DOT] will take control of item and properly dispose of. No further action will be taken on this incident [by the State]." The State indicated that the CS-137 source was undamaged and the source serial number used to trace the original owner. Followup State Report is FL08-121 Notified R1DO (Powell); FSME (Burgess); and ILTAB (Whitney via e-mail). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2003-12-10
40375 | 0 | SAINT LUCIE |  | 2 |  | [1] CE,[2] CE | 2003-12-04 16:32 | 2003-12-04 20:14 | 2003-12-04 | ST. LUCIE UNIT 2 MANUAL REACTOR TRIP DUE TO LOSS OF CONDENSATE PUMP "On December 4, 2003, at 1605 hours, a down power was initiated due to a failing bearing on the 2A Condensate Pump. The pump bearing was hot and smoking. The plant fire team was deployed as a precautionary action. Due to continued degradation of the Pump bearing, a Manual Reactor Trip was initiated at approximately 60% power. Feed to the 2A and 2B Steam Generators was maintained via the 2B Main Feedwater Pump. All plant safety systems responded normally and plant safety functions were maintained throughout the event. The Plant was stabilized In Mode 3. Plant post trip anomalies include Steam Generator Blowdown isolation valves closed, Control Room ventilation system swapped to recirculation mode, the Fuel Handling Building ventilation system swapped to the Shield Building, and it was necessary to take Steam Bypass Control System to manual. An Emergency Response Team was formed to review these conditions prior to plant restart. This non-emergency notification is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to the manual initiation of the RPS Reactor Trip." All control rods fully inserted into the reactor on the trip. The emergency diesel generators are available and the offsite electrical grid is in a normal configuration. No safety relief valves or power operated relief valves were known to have actuated during this event. St. Lucie Unit 1 was not affected and continues to operate in mode 1 at 100% rated thermal power. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-12-04
40374 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2003-12-03 17:00 | 2003-12-04 16:03 | 2003-12-11 | LOUISIANA AGREEMENT STATE REPORT - LOST Ir-192 RADIOGRAPHY CAMERA An IR-100 industrial radiography camera, serial number 4470, Spec model G40F, with a 33 curie Ir-192 source, serial number KG2801, was reported lost while being transported by the licensee from a work-site to the licensee's office. On December 3, 2003 at approximately 1700 CST the licensee, Bayou Inspection Service, 318 Degravelle Road, Amelia, LA was transporting the radiography camera from a work-site located at 1081 Highway 70, Pierre Port, LA to the Amelia, LA address, a distance of approximately 20 miles. Upon arrival at the office, the camera was noticed missing from the pickup truck being used to transport it from the worksite. The route of travel was from the work-site on Highway 70, through Morgan City, and to the Amelia exit on Highway 90 . The licensee notified the State of Louisiana of the event on 12/04/03 at 0940 CST and has notified local law enforcement along the route of travel. * * * * UPDATE FROM J. NOBLE TO M. RIPLEY 1710 12/11/03 * * * * The Louisiana Radiation Protection Division reported that, at approximately 1500 CST on 12/11/03, the radiography camera was turned in to the licensee at his facility in Amelia, LA by a private citizen. The citizen found the camera along the side of Highway 70 in Belle River, LA on 12/03/03. The licensee performed a leak check of the source and no leakage was found. Notified R4DO (D. Graves), NMSS EO (T. Essig), and DHS Ops Center (E. McDonald) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-12-09
40373 | -1 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-12-03 12:30 | 2003-12-03 17:24 | 2004-02-02 | EMERGENCY PROCEDURE DEFICIENCY CAUSES UNANALYZED CONDITION "While reviewing operator emergency response times contained in Callaway Plant's Final Safety Analysis Report (FSAR), it was determined that emergency procedure E-0 did not contain specific guidance for actions to be taken when one train of Control Room Emergency Ventilation System (CREVS) failed to properly operate. In FSAR Chapter 15A, the limiting single failure analyzed for the CREVS is the failure of a filtration fan within one train of CREVS. In this accident analysis scenario, a Control Room Filtration Unit fan fails and the train must be secured to prevent inadequately filtered Control Building air from being introduced into the Control Room. If the train is not isolated within 30 minutes, postulated dose to Control Room staff could potentially exceed GDC 19 limits. "While procedure E-0 addressed identifying faulted CREVS equipment and an attempted restoration of the faulted equipment, it did not contain sufficient guidance to ensure the Control Room staff would isolate the faulted train of CREVS if the equipment restoration attempt failed. "A revision to procedure E-0 has been issued to correct this procedural deficiency." The licensee has notified the NRC Resident Inspector. * * * * RETRACTION FROM E. HENSON TO M. RIPLEY 1425 ET 2/2/04 * * * * "This notification is being retracted. Further evaluations concluded that a local area radiation monitor would have alerted the Control Room staff to a developing adverse condition in sufficient time for operators to have identified and isolated the faulted CREVS train prior to exceeding regulatory dose limits. This event does not represent an unanalyzed condition reportable per 10CFR50.72(b)(3)(ii)(B)." The NRC Resident Inspector was notified of this retraction by the licensee. Notified R4 DO (A. Gody) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-12-03
40372 | -1 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-03 15:00 | 2003-12-03 15:38 | 2004-01-13 | BACKWARD INSTALLATION OF CONTAINMENT LOOP SEAL PENETRATION VACUUM BREAKERS "Vacuum breakers 1WL980 and 2WL980 are installed backwards. In their current orientation, the valves will not lift from their seats to break a siphon into the corresponding unit's Ventilation Unit Condensate Drain Tank (VUCDT). "The VUCDT input line is a 6-Inch pipe. There is a loop seal between the outboard containment isolation valve and the VUCDT. Since the VUCDT is vented to the auxiliary building environment, the purpose of the loop seal is to provide a barrier between the containment atmosphere and the auxiliary building atmosphere during normal unit operations. The purpose of the vacuum breaker is to prevent siphoning water out of the loop seal. In its current configuration, the vacuum breaker will not open. The loop seal is not needed to provide a barrier between the containment atmosphere and the auxiliary building atmosphere during a large break Loss of Coolant Accident (LOCA) because valves 1(2)WL867A and 1(2)WL869B will close on a Phase B containment isolation signal on high-high containment pressure (3.2 psig in containment, accounting for instrument error). During certain small break LOCAs, however, a high-high containment isolation signal may not occur, since pressure might not reach the setpoint. In this scenario, the loop seal is needed to isolate the containment atmosphere from the auxiliary building atmosphere. "Given the size of the VUCDT inlet piping, the only mechanism that could form a siphon out of the loop seal is a large flow of water that would push the air out of the top of the loop seal. In this instance, a siphon could form and pull water out of the low point of the loop seal. If this were to occur, a vent path from the containment atmosphere to the auxiliary building atmosphere would be open. However, during normal operation, there is not sufficient flow into the tank to make this a plausible scenario. "For a large break LOCA, containment pressure would rise quickly to the high-high setpoint; then the inoperable VUCDT loop seal would be isolated by its containment isolation valves. For smaller LOCAs, particularly, for a rod ejection accident resulting in a LOCA, containment pressure would rise slowly- from 2.81 psig (the pressure at which the loop seal isolation function would fail), until 3.2 psig (the maximum high-high containment pressure setpoint, accounting for instrument error), the inoperable loop seal would represent a containment leak path. The rod ejection accident does result in a high level of fuel clad failure; therefore, the unisolated containment leak path represents a source of release to the environment until such time as the high-high containment pressure setpoint is reached (if it is reached). The dose consequences associated with this potential leak path have not been evaluated. "Upon discovery of the incorrectly installed vacuum breakers, the containment isolation valves associated with this penetration flow path were closed to isolate the path. The Unit 2 loop seal configuration has since been modified to correct this situation. The Unit 1 loop seal configuration will be modified prior to the completion of the current end of cycle 14 refueling outage." The incorrect installation of the vacuum breakers was identified on 11/03/03, and it is being investigated on how long this condition has existed. It is possible that it has existed since construction. The licensee will notify the NRC Resident Inspector, state and local regulatory agencies. *****RETRACTED ON 1/8/03 AT 1615 FROM COY TO LAURA***** "The subject EN was made on 12/3/03. Following additional review by the licensee, this event was determined to not meet the reportability requirements of 10 CFR 50.72. The event was determined to not result in a degraded or unanalyzed condition, as the consequences of the event were determined to be bounded by transients currently analyzed and described in the Updated Final Safety Analysis Report (UFSAR). In addition, the event did not represent a failure of structures, systems, or components utilized to control the release of radiological material or to mitigate the consequences of an accident. The licensee is therefore retracting the subject EN." The licensee notified the NRC Resident Inspector. Notified R2DO (P. Fredrickson) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION | UNANALYZED CONDITION | POT UNCNTRL RAD REL | ACCIDENT MITIGATION | Refueling | Power Operation |  | Refueling | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(C) | 50.72(b)(3)(v)(D) | 0 | 2003-12-03
40371 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2003-10-31 | 2003-12-03 14:38 | 2003-12-03 | INVALID GROUP III PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION "This notification is being made in accordance with 10CFR50.73(a)(2)(iv)(A) to provide the NRC with information pertaining to the Primary Containment Isolation System (PCIS) Group III invalid actuation signals that affected containment isolation valves in more than one system on two separate occasions. "On October 31, 2003 and November 9, 2003, with the reactor at full power, an invalid actuation of the 'B' Reactor Building Ventilation Monitor caused Group III isolations of PCIS. A spike that was caused by electronic noise within the detector invoked a spurious High Level Trip to this monitor (RM 17-452B), that resulted in a trip to PCIS logic Channel B1. "The PCIS functioned successfully providing a complete Group III isolation. The train actuation was complete. Both trains of the Standby Gas Treatment System started as designed. The PCIS Group III isolation occurred which involves isolation of valves in the following systems: Drywell Air Purge and Vent, Drywell and Suppression Chamber Main Exhaust, Suppression Chamber Purge and Vent, Containment Air Compressor Suction Valve, Exhaust to Standby Gas Treatment, Containment Purge Supply and Makeup, Containment Air Sampling, Air dilution Subsystem Valves, Vent Subsystem Valves, and Containment Air Dilution Vent System MOV VG-22 A/B. "It was determined that both of these Group III isolations were invalid, due to the Reactor Building Vent Monitor Radiation Level Trip occurring at 25 millirem/hr on 10/31/03 and 15 millirem/hr on 11/09/03. General area radiation levels in these areas at the time of the event were approximately 2.5 millirem/hr to 6 millirem/hr." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-12-03
40370 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-12-03 03:36 | 2003-12-03 07:05 | 2003-12-03 | PLANT HAD AN AUTO REACTOR TRIP FROM 100% POWER DUE TO STEAM GENERATOR LOW LEVEL The "2 D" steam generator Lo-2 level was caused by the loss of the "2C" feedwater pump while performing the "2 BWOS" feedwater weekly surveillance of the HP stop valve. Both trains of the aux feed actuated as expected on the "2D" Lo-2 s/g level signal. The plant is currently in mode 3 with all rods fully inserted. No ECCS or safety relief valves actuated. Licensee notified the NRC Resident Inspector | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-12-03
40369 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-09-01 | 2003-12-02 23:15 | 2003-12-02 | AGREEMENT STATE REPORT OF LOST TRITIUM EXIT SIGNS During major construction, five out of eight exit signs were discovered missing in September 2003. Each exit sign contained 20 Curies Tritium as of 12 years ago. As of today each sign contains about 10 Curies Tritium. These exit signs are Generally Licensed devices and were manufactured by Fisher. The owner investigated and interviewed several employees within the last 30 days and advised them that if they find the signs they should bring them to him. As of today, the signs have not been recovered. The owner also reported that the facility brought about 100 dumpsters to the facility for inspection of debris and that the exit signs were not picked-up with the debris. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-12-05
40368 | 0 | CLINTON | 1 |  |  | [1] GE-6 | 2003-12-02 16:58 | 2003-12-02 19:37 | 2003-12-02 | MANUAL SCRAM DUE TO LOW REACTOR WATER FEED PUMP SUCTION PRESSURE "On December 2, 2003, at 1658, a manual scram was inserted from 88% power, which is the maximum power due to the plant being in coastdown. The manual scram was inserted due to feedwater suction pressure being below the trip set point for the operation of the Turbine Driven Reactor Feed Pumps and Reactor Pressure Vessel water level trending down. The initiating event was the loss of the 480V Unit Sub 1I. All plant systems operated normally on the scram with the exception of those systems that lost power due to the tripping of 480V Unit Sub 1I. "The plant is shutdown at 0% power in Mode 3, maintaining pressure between 800 and 1065 psig, and reactor water level between level 3 and 8. Troubleshooting is in progress on the cause of the loss of the 480V Unit Sub 1I." Plant is identifying the loads lost during the loss of the 480V Unit Sub 1I and the cause of the low feedwater suction pressure. No additional specified system actuations occurred. No SRVs lifted and the electrical plant lineup is stable and in a normal lineup for plant conditions with the exception of the lost 480V bus. The licensee has notified the NRC Resident Inspector. * * * UPDATE AT 2245 ON 12/02/03 FROM CARSKY TO ROTTON * * * "As a consequence of the manual reactor scram inserted at 1658 CST, reactor water lowered to Level 3. This level is a valid RPS actuation and containment isolation signal [Groups 2, 3 and 20]. These actuations are being reported consistent with 10CFR50.72(b)(3)(iv)(A). The Level 3 RPS actuation is expected during a high power reactor scram. "Additionally, on December 2, 2003, at 1935 CST, a Level 3 RPS actuation reoccurred while transferring reactor coolant makeup from the Motor Driven Reactor Feed (MDRFP) to a Condensate/Condensate Booster Pump pair. Reactor pressure was being lowered to the discharge pressure of the Condensate/Condensate Booster pumps. This Level 3 is a valid RPS actuation and containment isolation signal. These actuations are being reported consistent with 10CFR50.72(b)(3)(iv)(A). "The plant is shutdown at 0% power in Mode 3, maintaining pressure between 550 and 750 psig, and reactor water level between level 3 and 8. Troubleshooting is in progress on the cause of the loss of the 480V Unit Sub 1I. "Both of these events will be reported as a single Licensee Event Report (LER)." The plant continues to remove decay heat via the turbine bypass valves to the main condenser. The licensee will notify the NRC Resident Inspector. Notified R3DO Bruce Burgess. | 0 | 0 | 0 | 88 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-12-02
40367 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-12-02 14:15 | 2003-12-02 15:55 | 2003-12-02 | OFFSITE NOTIFICATION DUE TO ONSITE FATALITY "At 1230 hrs, with both units at 100% power the Control Room was notified of a Medical Emergency at the Access Processing Facility on the Owner Controlled Area outside of the Protected Area. The affected individual was a contract employee working for Site Access Services. An ambulance and paramedics arrived on site at 1242 hrs. First Aid and CPR were initiated at the scene. The individual was transported offsite at 1257 hrs to the local Hospital. At 1415 hrs the control room was notified that the individual had passed away. This constitutes an event of public significance and therefore reportable under 10CFR50.72(b)(2)(XI) as a 4 hour ENS notification." The licensee notified the NRC Resident Inspector and Pennsylvania Emergency Management Agency. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-12-02
40366 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-12-01 20:00 | 2003-12-01 22:27 | 2003-12-01 | CONTAMINATED INDIVIDUAL TRANSPORTED TO LOCAL HOSPITAL Polar crane operator experienced a medical condition that required immediate transport to the local hospital. The individual's Anti-contamination clothing were removed in a contaminated area of the Containment building by medical responders and the individual with the medical condition was identified as being contaminated. No specific contamination level was available at the time of the initial report other than he was frisked and the level was above background. It was also not known what the general level of contamination in the immediate vicinity of the individual was at the time of the initial report. A licensee Radiation Protection Technician escorted the individual to a local hospital in an ambulance. After arrival at the hospital, the individual's modesty garments were removed and the individual was no longer contaminated. Modesty garments were disposed of and the ambulance was surveyed and determined to by uncontaminated. The transported individual is in stable condition. The licensee notified the NRC Resident Inspector. No media or press release is expected to be made at this time. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2003-12-01
40365 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-11-30 | 2003-12-01 16:42 | 2003-12-01 | AGREEMENT STATE REPORT REGARDING WELL LOGGING SOURCE ABANDONMENT "Texas Incident No.: I-8079 "Event Report ID No.: 40365 "Event location: Newfield Exploration Company "Well: Cotton Whitehead 2501 "Valverde County, Texas "Notifications: Texas Department of Health, Bureau of Radiation Control; Texas Railroad Commission, NRC Operations Center; NMED; NRC Region IV "Event description: Late Friday evening, November 28, 2003, a logging source string became stuck in the customer's well. After several fishing attempts without success, it was decided to abandon the sources downhole. The sources will be cemented in place with the top most point covered by a minimum of 100 feet of red dyed cement. A deflection device will be place above the source string. A plaque has been ordered for installation on the wellhead. The source string held three sources: one Am-241/Be source manufactured by NSSI, Model DA-5, Serial No 27942, with an activity of 4.5 curies; one Cs-137 source manufactured by AEA, Model CDC.CY4, Serial No. 2907GW, with an activity of 2 curies; and a second Cs-137 source, manufactured by Gammatron, Model GT-GHP, Serial No. Z-194, with an activity of 0.8 curie." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-12-04
40364 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-10-03 | 2003-12-01 14:37 | 2003-12-01 | NONCOMFORMANCE NOTIFICATION FOR SOLID STATE PROTECTION MASTER RELAY Failure of Master Relay K507 (MidTex Part Number 15614D200) in the Solid State Protection System (SSPS) was attributed to corrosion caused by off-gassing of chlorine contamination from paper used to wrap the relay coil, or the adhesive used to attach the paper wrap to the coil. Master Relays must change state, upon energization, to actuate various safety related equipment in the plant. The failure of Master Relay K507 is considered to be a manufacturing defect in a basic component that could cause a loss of safety function. The majority of MidTex relays investigated had cloth wrapped coils and these relays showed no evidence of corrosion. The number of affected relays and installed locations was not available at the time of the initial notification. The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 21.21 |  |  |  | 0 | 2003-12-01
40363 | 0 | NEVADA RADIOLOGICAL HEALTH |  |  |  |  | 2003-11-15 | 2003-12-01 10:45 | 2003-12-01 | AGREEMENT STATE REPORT - TROXLER MOISTURE DENSITY GAUGE STOLEN AND RECOVERED The State of Nevada provided the following information via facsimile: "Date notified of event by licensee or non-licensee: November 17, 2003 "Radionuclide, activity Cesium 137.8 millicuries "Any exposures (indicate short and long-term effects): Unknown "Sealed source, device, etc. (make, model #, serial #): Troxler 46408, S/N 2361 "Leak test information, if applicable: Unknown "Persons involved, consequences: Unknown "Cause and contributing factors: Gauge was secured, according to procedures, in the licensee's field lab trailer. Thief defeated locks and barriers to break into storage closet and remove gauge. Gauge case and source rod were padlocked at the time of gauge theft. "Licensee corrective actions: None, source was properly secured at the time of theft "Provide status through resolution (update record when found): Gauge recovered on November 26, 2003 by a person wanting to remain anonymous. Gauge delivered to State regulatory agency and will be returned to licensee. "Notifications, local police, FBI and other States; as needed: Henderson, NV Police Dept., Nevada Highway Patrol, Nevada Division of Emergency Management, and lastly, Nevada Radiological Health Section "Identify any possible generic safety concerns: None "Potential for others to experience the same event: Slight" Note: This EN is actually an update to EN 40334. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | GEN |  |  |  |  | 0 | 2003-12-04
40362 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-11-28 22:02 | 2003-11-29 02:47 | 2003-11-29 | AUTOMATIC SCRAM DUE TO LOW REACTOR WATER LEVEL "At 2202 CST, a low Reactor Water Level Scram (Level 3) occurred due to lowering feedwater flow. All control rods inserted on the Scram. The Scram resulted in actuation of HPCI and RCIC on low Reactor Water level (Level 2), and the low level ATWS Recirculation Pump Trip (RPT). HPCI and RCIC initiated and both Reactor Recirculation pumps tripped. It is estimated that RCIC injected approximately 500 to 600 gallons, and HPCI injected less than 100 gallons. HPCI was secured early in the transient, and RCIC operated for approximately 2 minutes. Reactor Water level was recovered and maintained with the operating feedwater pump. "The Reactor Water low level (Level 3) also resulted in Group 2 (Primary Containment), Group 3 (Reactor Water Cleanup), and Group 6 isolations (Secondary Containment Isolation and Control Room Ventilation system start). All isolations functioned as designed. "Initial indications are that Feedwater Pump B speed lowered unexpectedly, causing Reactor Water level to lower. Reactor Water level reached -44 inches (wide range instruments) [120 inches above top of active fuel]. The setpoints for HPCI, RCIC, and ATWS-RPT are -33 inches. "Plans are to take the unit to Mode 4." The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | ECCS INJECTION | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(2)(iv)(A) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-11-29
40361 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2003-11-28 22:05 | 2003-11-28 22:57 | 2003-11-28 | MANUAL REACTOR TRIP FROM 11% POWER DUE TO TURBINE VIBRATION At 2205 EST on 11/28/03 while at 11% power, Millstone Unit 2 performed a required manual reactor trip when main turbine vibration reached a turbine trip set point of 12 MILS. The turbine vibration did not reduce when the turbine was tripped which required breaking condenser vacuum and ultimately a manual reactor trip. The main turbine vibrations were anticipated during power ascension due to a newly installed low pressure "Mono-Block" rotor. All control rods fully inserted during the reactor trip and no ECCS injection occurred or primary relief valves lifted. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 11 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-11-28
40360 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2003-11-27 23:30 | 2003-11-28 08:18 | 2003-12-08 | PLANT HAD AN INADVERTENT SIREN ACTIVATION "At 2330 11/27/2003 RG&E Energy Operations Center Notified the Control Room that an Emergency Notification Siren on Arbor Road was going off. The Siren System Controller was checked and verified that the siren had inadvertently activated. The Siren System Controller was used to reset and then check that the siren was operable. The siren was reset by 2345 11/27/2003. The 4 hour notification was inadvertently missed by the midnight shift." The licensee will be investigating the cause of this inadvertent siren activation. The licensee notified the NRC Resident Inspector. * * * EVENT RETRACTED ON 12/08/03 AT 1232 BY ROBIN NYE TO GERRY WAIG "At 2330 on November 27, 2003, RG&E was notified that an Emergency Notification Siren on Arbor Road appeared to have inadvertently activated. However, since that time, RG&E has performed an extensive evaluation and determined that there is no indication that the siren in the vicinity had been activated. This event has been discussed with the resident inspector and he has been informed that the event will be retracted." Notified R1DO (Aniello Della Greca) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-28
40359 | -1 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-11-27 22:55 | 2003-11-28 01:55 | 2004-01-26 | COMPONENT COOLING SYSTEM SURGE TANK SUPPORTS MAY FAIL DURING A SEISMIC EVENT During an ISI inspection of the component cooling system, it was discovered that several of the surge tank support stiffener plates were missing due to a design change that was never fully implemented. This condition creates a question as to the adequacy of the tanks to withstand a seismic event. This deficiency affects both trains of component cooling on Units 1 and 2. The problem will be corrected on Unit 1 while it is in its refueling outage. Work on the Unit 2 "A" train is currently ongoing, making that train of the component cooling system inoperable, therefore, putting the plant in a 72 hour LCO. When work on the "A" train is completed, they will exit the LCO, but re-enter it when work begins on the "B" train. Licensee will notify the NRC Resident Inspector, the State and local agencies. * * * RETRACTION AT 1025 EST ON 01/26/04 BY MIKE HEAVNER TO JOLLIFFE * * * "The subject EN #40359 was made on 11/28/03. Following additional review by the licensee, this event was determined to not meet the reportability requirements of 10 CFR 50.72. The event was determined to not result in a condition that could have prevented fulfillment of a safety function, as the tank supports were analyzed to withstand a seismic event. In addition, the event did not result in the plant being in an unanalyzed condition. The condition did not prevent the fulfillment of a safety function or system that is needed to remove residual heat or mitigate the consequences of an accident." The licensee plans to notify the NRC Resident Inspector. Notified R2DO Caudle Julian. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | POT RHR INOP | ACCIDENT MITIGATION |  | Refueling Shutdown | Power Operation |  | Refueling Shutdown | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  | 0 | 2003-11-28
40358 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2003-11-27 06:29 | 2003-11-27 06:51 | 2003-11-28 | PLANT HAD A MANUAL REACTOR TRIP FROM 23% POWER DUE TO TURBINE VIBRATION While rolling the turbine when at 20% power they experienced an over speed turbine trip. During a second attempt when at 23% power, the turbine had high vibration so they manually tripped the reactor. Cause for the vibration is being investigated since a new rotor had just been installed in the turbine. All rods fully inserted during the reactor trip and no ECCS injection occurred or primary relief valves lifted. The licensee notified the NRC Resident, the State of Connecticut and Local agencies * * * UPDATE AT 1423 EST ON 11/28/03 FROM FRANKS TO GOTT * * * The following clarifying information was provided by the licensee. "While at 23% power of a scheduled power ascension following a refueling outage, Millstone Unit 2 performed a required manual reactor trip when main turbine vibration reached a trip set point of 12 MILS. The main turbine vibrations were anticipated during the power ascension due to a newly installed low pressure "Mono-Block" rotor. All control rods fully inserted during the reactor trip and no ECCS injection occurred or primary relief valves lifted." The overspeed trip discussed in the original report was a test conducted prior to placing the main turbine on the grid. Notified R1DO (Dimitriadis). The licensee will notify the NRC Residence Inspector. | 0 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-11-27
40357 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2003-11-27 00:52 | 2003-11-27 03:24 | 2003-11-27 | REACTOR MANUALLY SCRAMMED FROM 23% DUE TO DECREASING REACTOR VESSEL WATER LEVEL A manual reactor scram was initiated due to a decreasing reactor vessel water level. The decreasing water level occurred during a feedwater transient while performing a power reduction in preparation for taking the main generator off line for maintenance. The licensee is investigating the cause of the feedwater transient, but it occurred while one turbine driven reactor feed pump was being taken off line. All rods fully inserted following the scram and no ECCS or safety relief valves actuated. Residual heat is being rejected to the condenser. The licensee notified NRC Resident Inspector. | 0 | 0 | 0 | 23 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-11-27
40356 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-11-25 03:45 | 2003-11-25 21:13 | 2003-11-25 | 24 HOUR NRC BULLETIN 91-01 NOTIFICATION REGARDING LOSS OF DOUBLE CONTINGENCY PROTECTION "At 0420 on 11/25/03, the PSS (Plant Shift Superintendent) was notified that contrary to NCSA (Nuclear Criticality Safety Assessment) CAS-011, 'Shutdown of the Cascade With or Without Inventory', M&TE (Measuring & Testing Equipment) pressure gauges, installed on the RCW( Recirculating Cooling Water) return side of the C-331 U/3 C/2 condenser, were removed prior to the RCW supply spool piece being removed. NCSA CAS-011 requires independent verification that the supply spool piece has been removed prior to removing the M&TE gauges. The purpose of these gauges is to monitor the condenser pressure to insure RCW pressure in the condenser does not exceed 17 psig in the event the RCW supply valve leaks with the return valve completely closed. As long as the 17 psig limit is not exceeded, RCW pressure can not over come the coolant pressure and leak into the coolant. "Evolutions that occurred during the spool piece removal found that the RCW return valve to the condenser could not be completely closed. This provided an open flow path to pressure gauges installed on the RCW return header allowing for pressure readings to be taken that provides an indication of the pressure at the condenser. Pressure readings on the RCW return header indicate that the RCW return did not exceed the 17 psig as required in the NCSA. "The NRC Senior Resident Inspector has been notified of this event. "PGDP Assessment and Tracking Report No, ATRC-03-4076, PGDP Event Report No. PAD-2003-021, NRC Event Worksheet # 40356 "Responsible Division: Maintenance "SAFETY SIGNIFICANCE OF EVENTS: Double contingency was not maintained because independent verification that the supply spool piece had been removed before removing the M&TE pressure gauges was not performed. However, since the RCW return header did not exceed 17 psig, the process condition was maintained. This event was of low safety significance due to moderation control being maintained. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIOS) OF HOW CRITICALITY COULD OCCUR: Once the fluorinating environment is removed from the process cell, moisture that may leak into the process gas side could potentially moderate a uranium deposit that may be present. RCW pressures below 17 psig will prevent water from leaking into the coolant that could then leak into the process gas side. Sufficient water would have to leak into the process gas side from the coolant and moderate a critical mass of uranium. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC): Double contingency is maintained by implementing two controls on moderation. "ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDES PROCESS LIMIT AND % WORST CASE CRITICAL MASS): This system has a process limit of [DELETED]. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on ensuring that a condenser tube leak will not introduce RCW (moderator) into the process gas side through the coolant. This is accomplished through monitoring the RCW return pressure to be 17 psig or less. Once the return RCW valve is closed the M&TE gauges, installed on the RCW return side of the condenser, provide indication that the condenser does not exceed 17 psig. The purpose of these gauges is to monitor the condenser pressure in the event the supply valve leaks with the return valve completely closed. Under these conditions, actions are required if the condenser pressure exceeds 17 psig. As long as the 17 psig limit is not exceeded, RCW can not over come the coolant pressure and leak into the coolant. Since the pressure gauges were removed prior to the spool piece being removed, this control was violated. However, due to the return valve leaking at the condenser, an open flow pathway is available to peak reading pressure gauges installed on the RCW return header that would provide an indication of the pressure at the condenser. Pressure readings from the RCW return header do not indicate the return pressure exceeded 17 psig. Therefore, the process parameter, moderation, was maintained. "The second leg of double contingency is based on an independent verification that the supply spool piece has been removed prior to removing the M&TE pressure gauges. Since the gauges had been removed before the supply spool piece was removed, the independent verification requirement was violated. Though this control was violated, the process parameter was maintained due to the RCW return header pressure not exceeding 17 psig. Since double contingency is based on two controls on one parameter, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: The M&TE pressure gauges were re-installed at approximately 0620 on 11-25-03." The licensee will notify the DOE Site Representative. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | KY | FUE | [5 empty] | 0 | 2003-11-25
40355 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-11-25 14:00 | 2003-11-25 20:18 | 2003-11-25 | FITNESS FOR DUTY NOTIFICATION DURING RANDOM DRUG TESTING A contract employee tested positive during a random test. The employee's access to the protected area has been terminated. Contact the HOO for additional details. The licensee has informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2003-11-25
40354 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-11-25 17:30 | 2003-11-25 20:10 | 2003-11-25 | OFFSITE NOTIFICATION DUE TO ETHYLENE GLYCOL LEAK "On November 25, 2003 at 1730, offsite notification was made regarding a 692 pound leak of ethylene glycol from the north cooling tower de-ice system. The de-ice system was shutdown after the event. "The National Spill Response Center, EPA Regional Response Center, the Michigan Stale Police Operations Center, State of Michigan Department of Environmental Quality, and US Coast Guard were notified." Site permit requires state notification of any leak above 500 pounds. The material leaked into the cooling pond associated with the cooling tower and the cooling pond water will be slowly decanted into Lake Erie per normal procedure. The cause of the leak is being investigated. There is currently no affect to the plant due to loss of the de-icing system. The Licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-25
40353 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-11-25 15:22 | 2003-11-25 17:43 | 2003-11-25 | MANUAL SCRAM DUE TO DEGRADING CONDENSER VACUUM DURING POWER ASCENSION Unit was in process of returning to operation following repair of condenser expansion joint. During power ascension, a manual reactor scram was inserted due to degrading condenser vacuum. During the reactor water level transient after the scram, reactor water level dropped below 170 inches and caused the isolation of PCIS groups 2, 3, and 4. All isolations went to completion. This reactor water level drop is normal following a scram from 20% power due to void collapse in the reactor vessel. Reactor water level was restored to normal using the feedwater system and the PCIS group isolations are being reset. Current plan is to remain in Mode 3 during condenser vacuum troubleshooting and repair. All rods were fully inserted during the scram, no SRVs lifted, and the electric distribution system is in a normal lineup for plant condition. The MSIVs are open with decay heat being removed to the main condenser using the bypass valves. No additional specified system actuations occurred. Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 20 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-11-25
40352 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2003-11-24 14:15 | 2003-11-25 11:32 | 2003-11-25 | AGREEMENT STATE REPORT - DOSE TO PATIENT OUTSIDE INTENDED TREATMENT SITE "[Radiation Safety Officer (RSO)] for Advocate Lutheran General Hospital called Illinois Emergency Management Agency on 11/24/03 at approximately 1415 to report an event involving a Novoste Intravascular Brachytherapy [IVB] procedure. Hospital RSO stated that at approximately 1100 on 11/24/2003 during an IVB procedure with a prescribed dose of 18.4 gray, the end of the 40mm source train was not visible at the anticipated location at the end of the catheter. The sources were stuck in an apparent kink in the catheter. The source train was immediately retracted into the safe shielded position in the unit. A second attempt was then made but the sources became stuck in the same area and were again immediately retracted. " The procedure was then terminated and an analysis of the event and dose estimates were performed. An unintended area of the heart was exposed to radiation from the source train for approximately 47 seconds in the first attempt and 10 seconds in the second. The estimated radiation dose calculated to the wrong area of the heart was estimated to be approximately 5 gray. Essentially none of the prescribed dose of 18.4 gray was delivered to the intended area of the heart as the source train was retracted before reaching the intended area. "The patient has been notified that there was a problem encountered during the procedure and the physician will notify the patient shortly of the particulars involved with the unintended dose delivered. The physicians do not expect any adverse medical effects from this event. Hospital RSO stated that they will carefully review this event and enhance training for this procedure. Hospital RSO added that he will notify Novoste regarding this event and submit the required written report within 15 days." Illinois Event Report ID: IL030078, License Number: IL -01152-01 Source Information: NOVOSTE Model #A1767, Serial # 91834, Radionuclide: Sr 90, Activity: .0484 Curies | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-11-28
40351 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-11-24 03:22 | 2003-11-24 12:21 | 2003-11-24 | INABILITY TO INITIATE EMERGENCY SIRENS FROM EMERGENCY OPERATIONS FACILITY "At 0322 CST, on 11/24/2003, an alarm was received on the Alert Notification System. The system alarm is not necessarily indicative of a system fault. Normal procedure is to check the system at the start of the normal work day. When the system was tested at 0615 CST it was discovered that the emergency sirens could not be sounded from the Emergency Operations Facility (EOF). "Troubleshooting efforts were begun. The repair crew discovered that the sirens are able to be sounded by their normal stations (the counties). The sirens were also able to be sounded by a remote unmanned alternate location [owned by the utility located in downtown Omaha]. However, the EOF could not have verified which sirens had sounded. Verification of siren actuation was possible from the unmanned alternate location. Troubleshooting continues." The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-11-24
40350 | 0 | SALEM |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-11-23 05:19 | 2003-11-23 06:48 | 2003-11-23 | REACTOR WAS MANUALLY TRIPPED AFTER A CONTROL ROD DROPPED DURING LOW POWER PHYSICS "During performance of low power physics testing for dynamic rod worth measurements, control rod bank D was being withdrawn. At control bank D position of 209 steps, control rod 1D4 dropped into the reactor core. The control room crew entered the abnormal operating procedure for a dropped [control] rod at 0507. Based upon the dropped control rod causing the reactor to go subcritical, the abnormal operating procedure directs that all [control] rods to be inserted. Based upon the control bank D not being fully withdrawn and not in the proper bank overlap due to low power physics testing, the Control Room Supervisor directed the reactor to be [manually] tripped. The crew entered the emergency operating procedure at 0519. All equipment functioned as designed and all major equipment is available. [The crew] exited the emergency operating procedures at 0538. The plant is currently stable in mode 3 at normal operating temperature and pressure. "The cause of the drop rod is reported to be a blown fuse on the stationary coil. All reactor coolant pumps are in service and decay heat removal is through the steam dumps to the condenser." All control rods fully inserted when the reactor was manually tripped. Feedwater to the steam generators is being supplied by the auxiliary feedwater system. The licensee has notified the NRC Resident Inspector and will be notifying the LAC (Lower Alloways Creek) Township. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode2: Startup; FMode2: Hot Standby | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-11-23
40349 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2003-11-21 22:53 | 2003-11-22 04:30 | 2003-11-22 | VALID ACTUATION OF THE "A" EMERGENCY DIESEL GENERATOR DURING TESTING "The following event description is based on information currently available. If through subsequent reviews of this event, additional information is identified that is pertinent to this event or alters the information being provided at this time, a follow-up notification will be made via the ENS or under the reporting requirements of 10CFR50.73. "On November 21, 2003, at approximately 22:53 Mountain Standard Time, Palo Verde Nuclear Generating Station Unit 2 experienced a valid actuation (start) of the 'A' Emergency Diesel Generator (EDG). Unit 2 had been performing testing of the capability to parallel the EDG 'A' with the Gas Turbine Generator #1 (alternate AC Power source for station blackout.) The Train 'A' 4.16 Kv bus had been successfully transferred to the EDG and loads carried by the EDG for approximately 5 minutes. When the EDG speed control was taken from 'droop' mode (load sharing) to 'isochronous' mode (fixed frequency,) the EDG output breaker tripped opened, resulting in a valid Loss of Power (LOP) signal based on undervoltage on the Train 'A' bus. The EDG resupplied the bus in the LOP mode. "Offsite power remained available to both safety buses throughout the event. The other (Train 'B') safety bus is being supplied by offsite power and its EDG is operable. The offsite electrical grid is stable. "Palo Verde Unit 2 is shutdown and defueled in its 11th refueling outage. No other ESF actuations occurred and none were required. There were no structures, systems, or components that were inoperable at the time of discovery that contributed to this condition. There were no failures that rendered a train of a safety system inoperable and no failures of components with multiple functions were involved. The event did not result in the release of radioactivity to the environment and did not adversely affect the safe operation of the plant or health and safety of the public. "Troubleshooting will be conducted to determine the cause of the EDG output breaker opening." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-22
40348 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-11-21 09:10 | 2003-11-21 15:46 | 2003-11-21 | CONTROL BANK "C" RODS TRIPPED DUE TO INCORRECT DIGITAL ROD POSITION INDICATION (DRPI) "On Friday November 21, 2003, the V.C. Summer Nuclear Station was performing rod position testing in preparation for plant start-up, following refueling outage-14. The testing is in accordance with STP-106.002 Rod Position Indication Operational Test. Control Bank 'C' was being withdrawn. Per STP-106.002, RCS boron concentration was verified adequate to ensure Keff less than or equal to 0.95. When Control Bank 'C' reached 36 steps Digital Rod Position Indication system (DRPI) indication for rod M-4 went to 18 steps. At 0835, Control Rod motion was stopped and Abnormal Operating Procedure (AOP)-403.5, Stuck or Misaligned Control Rod, was entered after reviewing the AOP applicability versus current plant condition. At 0910 while taking action per the AOP, it was determined that both channels of DRPI were not functioning properly and per Tech Spec 3.10.5 the Rx Trip Breakers were immediately opened (manual actuation of the Reactor Protection System - reactor scram). Emergency Operating Procedure (EOP)-1.0, Reactor Trip, was entered. At 0915 EOP-1.0, was exited with the plant stable in Mode 3 (Hot Standby). "At this time it appears there was failure in the DRPI system. "This event is being reported in accordance with 10 CFR 50.72(b)(3)(IV)(A), a valid actuation of the Reactor Protection System (RPS)." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-21
40347 | 0 | U. S. AIR FORCE |  |  |  |  | 2003-11-14 | 2003-11-21 14:32 | 2003-11-21 | LOST RADIOACTIVE CHEMICAL DETECTOR On 11/14/2003, an APD-2000 chemical detector with a 10 millicurie Ni-63 source was discovered to be missing from its storage location. The detector was stored with the Fire Department for Westover Air Reserve Base in Massachusetts. It is not known when the detector was last accounted for through inventory and the ongoing search for the last 7 days has provided no results. The search is continuing and an investigation will be conducted to determine the cause of the loss and potential corrective actions to prevent reoccurrence. Licensee is going to contact NRC Region 4 to report loss. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | DC | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-11-21
40346 | 0 | ALBERT EINSTEIN MEDICAL CENTER |  |  |  |  | 2003-11-20 17:00 | 2003-11-21 13:48 | 2003-11-21 | TOTAL DOSE DELIVERED DIFFERS FROM PRESCRIBED DOSE BY MORE THAN 20 PERCENT On 10/16/2003, patient underwent surgery to implant 89 I-125 seeds for treatment of prostate cancer. X-rays taken after surgery appeared to be normal. On 11/17/2003, a routine follow up CT scan was performed and the results were made available to Radiation Oncology on 11/20/2003. Review of the CT scan showed that approximately 80% of the implanted seeds were in adjacent tissue and not in the intended location. The original prescribed dose to the prostate was 145 Gray. The estimated dose to the prostate with the existing seed location is 18.6 Gray. On 11/21/2003, the medical center left multiple messages with the patient providing applicable contact numbers. The treating physician has been notified. The hospital will be conducting an investigation into the cause of the error and determining appropriate treatment for the patient. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | PA | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-11-21
40345 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-11-20 17:00 | 2003-11-20 18:43 | 2003-11-21 | LOSS OF SPDS FOR GREATER THAN 8 HOURS "During the performance of the control room logs CKL ZL-003 the updating of the SPDS [Safety Parameter Display System] program on the Nuclear Plant Information System (NPIS) computer system was noted to have not changed state. With the recent restoration of the condenser off gas monitor GE RE-092 the computer log had not updated and indicated that the computer was not updating. A review of the computer services backlogs indicates the program has not updated since 11/14/2003 @ 10:29 [CST]. "This condition is being reported as a Loss of Emergency Preparedness under 10CFR50.72(b)(3)(xiii). The loss of NPIS affects Safety Parameter Display System (SPDS). SPDS is considered a significant portion of the WCGS emergency assessment capability. Because SPDS has been lost for longer than a short period of time, Wolf Creek Nuclear Operating Corporation is making this notification pursuant to 10CFR50.72(b)(3)(xiii). There is no other loss of normal procedures and are taking local readings of equipment normally monitored by the NPIS computer. Current plant status is still Mode 5, 0%." The licensee notified the NRC resident inspector. * * * UPDATE PROVIDED TO JEFF ROTTON FROM DAVE DEES ON 11/21/2003 AT 1255 * * * SPDS function was restored at time of initial notification and no other compensatory measures are required. The licensee notified the NRC resident inspector. Notified Kriss Kennedy - Region 4 Duty Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-11-20
40344 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-11-20 10:20 | 2003-11-20 12:11 | 2003-11-20 | LOW VOLTAGE CIRCUIT BREAKER DEFECT AND NONCOMPLIANCE REPORT Deviation related to upper stud assemblies for General Electric Nuclear AKR-30 low voltage circuit breakers. The deviation is specific to upper stud assemblies supplied under part number Q139C4632G1 and consist of an incorrect angle between the stud and pivot. Of the fifteen assemblies supplied with possible deviations to AmerenUE, five were returned and ten had been installed in Callaway Plant. The deviation will not prevent the circuit breakers from performing their design basis function at the Callaway Plant, however, the capability of the assemblies is indeterminate for severe faulted conditions. A circuit breaker could fail if an upper stud assembly with identified deviation was installed and the circuit breaker was called upon to interrupt a severe fault. "Callaway has concluded that this deviation does not constitute a "defect" as defined in 10CFR Part 21 because the breakers would still perform their design basis requirements and would not create a substantial safety hazard. However, Callaway can not determine if the potential for a significant safety hazard or exceeding of a technical specification safety limit could exist at another nuclear power plant." Received written documentation that the licensee has notified the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 21.21 |  |  |  | 0 | 2003-11-20
40343 | -1 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2003-11-20 09:25 | 2003-11-20 11:19 | 2004-01-15 | HIGH PRESSURE COOLANT INJECTION (HPCI) SYSTEM DECLARED INOPERABLE At 0925, while performing the HPCI time to rated flow surveillance, operators discovered the HPCI flow controller to be operating sluggishly in the automatic mode. The surveillance was stopped and HPCI was declared inoperable. The licensee entered a 24-hour LCO per Technical Specification 3.5.5.2 due to Torus Cooling being in service on RHR loop "A". The licensee is now in a 14-day LCO as a result of securing Torus Cooling and restoring RHR LPCI loop "A". Troubleshooting was performed with I&C prior to securing HPCI. I&C is pursuing controller restoration to operability. The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 01/15/04 @ 1035 BY DAVID HALLONQUIST TO C GOULD * * * RETRACTION BASIS FOR RETRACTION: NRC Notification 40343 was conservatively made to ensure that the Eight-Hour Non-Emergency reporting requirements of 10CFR50.73 were met pending the evaluation of an atypical condition observed with the High Pressure Coolant Injection (HPCI) Flow Controller while performing scheduled preventative maintenance testing for the HPCI System. After the off-site vendor lab completed testing the circuit board, the HPCI Flow Controller performed sluggishly, and it was determined that the initial NRC Notification was not required. During surveillance testing on 11/20/03, the HPCI System was started and met or exceeded the Technical Specification minimum requirements designed to demonstrate HPCI System Operability. While testing the specific components of the system, the HPCI Flow Controller was observed to be behaving erratically. Although the HPCI System was still capable of performing its required design safety function, the Shift Manager declared the system inoperable with a concern that further degradation of the flow controller "could have" prevented the HPCI System from performing its design safety function. Troubleshooting determined that the amplifier circuit board for the controller was not performing as expected. This board was subsequently replaced with one from stock and tested satisfactorily before declaring HPCI fully operational. The faulty amplifier circuit board was sent to an off-site vendor lab for testing and analysis. The vendor determined that the problem was due a capacitor failure on the board. The capacitor was removed, and the board was re-tested to determine the extent of the effect that this condition would have on the HPCI System performance. This testing revealed the same indications and system response that was initially observed by Vermont Yankee personnel during testing and troubleshooting. Therefore, it has been concluded that with the preventative maintenance system's surveillance as-found condition, the HPCI System was capable of performing its design safety function, and the flow controller's performance would not have degraded any further as a result of this condition. Therefore ENS Event Number 40343, made on 11/20/03, is being retracted. The NRC Resident Inspector was notified. Reg 1 RDO( Holody) was informed. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-11-20
40342 | 0 | CROW BUTTE RESOURCES, INC |  |  |  |  | 2003-11-19 14:00 | 2003-11-20 10:16 | 2003-11-20 | MEDICAL TREATMENT INVOLVING CONTAMINATION On 11/19/03, a contract worker at the licensee's facility fell from a ladder breaking his shoulder while working in a contaminated area. The worker was transported to the hospital with the licensee's RSO while wearing his protective clothing. The protective clothing had removable contamination measured at 1380 dpm/100 cm2 (disintegrations per minute per 100 square-centimeters). The employee was released from the hospital and the contaminated clothing was recovered by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | MED TREAT INVOLVING CONTAM | [9 empty] | NON EMERGENCY | 4 | NE | MAT |  | 40.60(b)(3) |  |  |  | 0 | 2003-11-20
40341 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-11-18 13:00 | 2003-11-19 16:50 | 2003-12-17 | STOLEN MOISTURE-DENSITY GAUGE The Arizona Agency was informed on 11/19/03 @ 1230 of a stolen moisture density gauge which was taken when the pickup truck it was in was stolen. The gauge was a CPN Model MC3, S/N M390404988 containing 10 millicuries of Cs-137 and 40 millicuries of Am:Be-241. Avondale, AZ police are investigating (report # 0327274) the incident. A press release will be issued and the licensee will notify the FBI, States of CA, NV, NM, CO and the Country of Mexico. * * * UPDATE ON 12/17/03 AT 1501 EST FROM A. GODWIN TO E. THOMAS * * * The Phoenix Police Department recovered the truck on 12/16/03. The driver door indicated a forced entry and the ignition switch key area was damaged. As of 12/17/03, the licensee reported the only item missing is the CPN moisture/density gauge. Other equipment, including cement testing equipment, was not removed from the truck. The Licensee issued a press release offering a reward for the recovery of the gauge. The release was not carried by the media. The Agency has an active investigation into the circumstances surrounding the loss of this device. The FBI, States of California, Nevada, New Mexico, Colorado, and the country of Mexico are being notified of this event. Notified R4DO (P. Harrell), and NMSS EO (J. Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-11-24
40340 | 0 | ROBINSON | 2 |  |  | [2] W-3-LP | 2003-11-19 13:30 | 2003-11-19 14:23 | 2003-11-19 | TWO FAILURE MODES NOT PREVIOUSLY POSTULATED COULD BE INTRODUCED BY A FIRE IN EITHER FIRE ZONE 19 OR FIRE ZONE 20. "At approximately 1330 hours (EDT) on November 19, 2003, during reviews being conducted on H. B. Robinson Steam Electric Plant (HBRSEP), Unit 2 No. 2, Appendix R fire scenario safe shutdown circuit analysis, it was concluded that two failure modes not previously postulated could be introduced by a fire in either Fire Zone 19, Cable Spreading Room, or Fire Zone 20, Emergency Switchgear Room. The suction source to the charging pump could spuriously close during a fire in one of these zones, which could cause a loss of Reactor Coolant System (RCS) make-up capability of the "A" Charging Pump were operating at the time if the event. The other failure mode involves spurious operation of both pressurizer power operated relief valves (PORVs), which could cause a loss of RCS inventory. Each of these failure modes could result in loss of safe shutdown capability. Therefore, this condition is being reported in accordance with 10 CFR 50.72(b)(3)(v)(A), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are required to shut down the reactor and maintain it in safe shutdown condition. "Short term corrective actions for this situation include procedure changes to establish preemptive actions that will provide reasonable assurance that safe shutdown can be achieved and maintained. The procedure changes will include rapid verification at the onset of a fire scenario that the "A" Charging Pump is not operating, and will direct closure of the pressurizer PORV block valves. Additionally, the Fire Protection Program (FPP) requirements for loss of detection or suppression in these zones were reviewed. The FPP requires establishment of a continuous fire watch in these areas for loss of detection or suppression capability. Additional administrative controls will be implemented or transient combustibles to further reduce the probability of these failure modes occurring. "Long term corrective actions are being developed via the Corrective Action Program and will be implemented to further reduce the likelihood of these failure modes" The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-11-19
40339 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2003-11-18 16:00 | 2003-11-19 13:37 | 2003-11-19 | PORTABLE TROXLER GAUGE RUN OVER BY BULLDOZER A portable Troxler Model 3411B S/N 6581, was run over by a bulldozer on 11/18/03. The probe was intact and was returned to inside of the gauge housing and moved to a secure location to be leak tested and transported back to the office awaiting recommendations from Troxler. The gauge contained 40 millicuries Am-241 and 8 millicuries Cs-137. A second licensee, Englehard #Ga178-1, was also involved. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | GA | OTH | AGR |  |  |  |  | 0 | 2003-11-24
40338 | 0 | MALLINCKRODT |  |  |  |  | 2003-10-31 | 2003-11-19 08:15 | 2003-11-19 | MISSING CESIUM-137 CHECK SOURCE During an inventory on 10/31/03, it was discovered that a sealed Cs-137 instrument check source was missing from its storage location. The source strength is 232.5 microcuries as of 11/18/03. The source was last seen during the previous inventory on 05/08/03. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-11-19
40337 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-11-17 | 2003-11-18 17:59 | 2003-11-18 | PATIENT RECEIVED AN OVERDOSE DURING A BRACHYTHERAPY PROCEDURE The licensee's RSO reported on 18 November 2003, that a patient, at Swedish Medical Center, Providence Campus, was scheduled to receive an intravascular Brachytherapy procedure that involved the use of a NOVOSTE Beta-Cath device. The device, Serial Number ZB638, employed a total activity of 2907 Megabecquerels (78.56 millicuries) of Strontium 90/Yttrium 90, in a sealed source-train, Serial Number 91837. The cardiologist was unable to insert the source-train for the treatment because, as reported by the RSO, it was into a small artery and the routing did not follow a direct path. This resulted in a 143 second, 13.78 Gray (1378 Rad), exposure to healthy patient tissue. The source-train was partially inserted into the patient when the cardiologist experienced difficulty. A 143 second exposure time elapsed before the cardiologist withdrew the source-train even though medical center procedure requires the sources to immediately be withdrawn once a problem is understood. The delay apparently occurred as the cardiologist first worked to fully insert the source-train and then discussed correcting the problem with the oncologist. The cause of the exposure was failure to follow established procedures. The cardiologist has been suspended from further licensed activities until the details of the event are fully understood. It is anticipated that no health affects to the patient will be realized as a result of the exposure. A DOH staff health physicist will pursue additional details of the event. There is no media attention at this time. Patient and referring physician were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-11-21
40336 | 0 | GLOBAL NUCLEAR FUEL - AMERICAS |  |  |  | URANIUM FUEL FABRICATION | 2003-11-18 15:55 | 2003-11-18 18:52 | 2003-11-18 | 24 HR NRC BULLETIN 91-01 DUE TO CRITICALITY CONTROLS DEGRADATION At approximately 3:55 p.m. on November 18, 2003, the storage of miscellaneous items was noted in a hood in the chemical area. The items included valves, small diameter pipes, and other objects wrapped in plastic. The criticality safety basis for the hood is based upon not exceeding the UO2 limit and the geometry of the objects in the hood. Since the geometry control is based upon only a single type of process component in the hood (e.g.: a limited number of 1" valves, or a maximum length of 1" pipe), the as found condition was not consistent with the documented analysis (only one type of component can be processed at a time). An assay confirmed less than 4 killograms uranium was contained in the components. Therefore, the mass limit was not exceeded. The mass control was not violated and no unsafe condition existed. The situation was corrected in less than four hours. This condition is reported within 24 hours pursuant to NRC bulletin 91-01 due to a degradation of criticality controls. Activities in the affected area have been suspended and the equipment tagged out until an investigation to determine the root cause and necessary corrective actions has been completed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | NC | FUE | [5 empty] | 0 | 2003-11-18
40335 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-11-18 17:14 | 2003-11-18 18:01 | 2003-11-18 | LICENSEE MADE A NOTIFICATION TO THE STATE OF CONNECTICUT Approximately 1 quart of transmission oil spilled from a privately owned vehicle onto the soil at the lower parking area which is about 200 yds from the industrial area(old PA). No oil went into the water and cleanup is in progress. The licensee made an off site notification to the state of Connecticut Licensee notified Reg 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-18
40334 | 0 | NV DIV OF RAD HEALTH |  |  |  |  | 2003-11-15 | 2003-11-18 14:13 | 2003-11-18 | NEVADA STATE LICENSEE REPORTED A STOLEN TROXLER GAUGE The Nevada Department of Transportation notified the Nevada Division of Rad Health on 11/17/03 that on 11/15/03 a Troxler 4640B, s/n 2361 was stolen out of a field lab trailer. The gauge was secured in the trailer, but the thief was able to defeat the locks and barriers. The gauge contained 8 millicuries of Cs-137. Notifications were made to the local police, the FBI and other states of the stolen gauge. Note: This gauge was recovered. See EN 40363. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NV | OTH | AGR |  |  |  |  | 0 | 2003-11-21
40333 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-11-18 11:07 | 2003-11-18 14:11 | 2003-11-18 | LICENSEE MADE OFFSITE NOTIFICATION DUE TO AN OIL SPILL A notification was made to the Pollution Emergency Alert System (PEAS) and Department of Environmental Quality (DEQ) due to an oil spill. This occurred during activities associated with replacing a transformer that is located in the owner controlled area, when oil within the transformer spilled to the ground. The quantity of oil was approximately 75 gallons. The spill was contained to the soil and never reached the surface water. Cleanup is in progress. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-18
40332 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-10-08 02:16 | 2003-11-18 14:02 | 2003-11-18 | INVALID SAFETY INJECTION SIGNAL DURING SURVEILLANCE TESTING AT GINNA "On October 8, 2003, at 0216 hours Eastern Daylight Savings Time, while in a refueling outage, R.E. Ginna Nuclear Station experienced an invalid "B" train Safety Injection (SI) signal. The invalid signal was the result of an error made while establishing pretest requirements during a 24 month surveillance. The invalid SI signal caused the "B" train Diesel Generator (DG) to actuate. The "B" DG started and functioned as designed, and all support systems functioned properly." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-11-18
40331 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-09-27 15:44 | 2003-11-18 13:58 | 2003-11-18 | INVALID PARTIAL SAFETY INJECTION SIGNAL DURING SURVEILLANCE TESTING AT GINNA "On September 27, 2003, at 1544 hours Eastern Daylight Savings Time, while In a refueling outage, R.E. Ginna Nuclear Station experienced a momentary invalid partial Safety Injection (SI) signal to the "A" train. The invalid signal was the result of an error made while placing a jumper across a relay during a 24 month surveillance. The invalid partial SI signal caused the following systems to actuate: "A " train Containment Ventilation Isolation (CVI), "A" train Diesel Generator (DG), trip of MCC G1, full opening of Service Water (SW) AOV-4561 to the containment recirculation fans, and the opening of Residual Heat Removal (RHR) core deluge valve MOV-852A. Each individual actuation was complete, the "A" DG started and functioned as designed, and all support systems functioned properly. The individual slave timers fed from the SI relay did not actuate. The most probable cause of this was the momentary nature of the partial SI signal." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NY | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-11-18
40330 | 0 | OCONEE | 1 | 2 | 3 | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-11-17 16:04 | 2003-11-18 11:05 | 2003-11-18 | FITNESS FOR DUTY A vendor supervisor was determined to be under the influence of illegal drugs during a random fitness for duty screening. The vendor supervisor's access to the plant has been terminated. Contact the HOO for additional details. The NRC Resident Inspector was notified of this event. | 0 | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Refueling | Power Operation | Power Operation | Refueling | Power Operation | Power Operation | NON EMERGENCY | 2 | SC | POW |  | 26.73 |  |  |  | 0 | 2003-11-18
40329 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-11-18 04:35 | 2003-11-18 10:47 | 2003-11-18 | LOSS OF COMMUNICATIONS CAPABILITY "On 11/18/03 at 0435 EST, it way discovered that the ENS phone system was inoperable when the NRC was unable to contact the Limerick Generating Station Control Room for a routine plant status update. The NRC was able to contact the Limerick Control Room via a normal station telephone. The cause of the communication loss was investigated and determined to be an ENS phone in TSC that was "off the hook". The TSC ENS phone had a headset connected that was inadvertently turned on and resulted in the busy signal when the NRC attempted to call. The TSC ENS phone headset was turned off restoring the communication line. Communications were verified with the NRC at 0459 via the ENS phone. This condition is being reported as an 8 hour notification per the requirements of 10 CFR 50.72(b)(3)(xiii) for loss of offsite communications capability." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-11-18
40328 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-11-17 11:50 | 2003-11-18 10:03 | 2003-11-18 | SIGNIFICANT LEAK IN FIRE PROTECTION HEADER "This is notification of a Special Report in accordance with Technical Requirement 7.1.1 of the North Anna Technical Requirements Manual. "On November 17, 2003, at 1150 hours, the Main Control Room observed the start of all fire pumps and receipt of associated alarms. An investigation determined that a significant leak in the fire protection header occurred outside the protected area. The cause for the fire protection header leak has not been determined. In an effort to isolate the leak, two of the three fire pumps had to be shut down and the third pump was isolated. The leaking portion of the fire protection header was isolated by 1313 hours. The running fire pump was then used to refill and pressurize the fire protection header. By 1420 hours, the fire protection system had been returned to normal." The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW | [5 empty] | 0 | 2003-11-18
40327 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-11-17 09:00 | 2003-11-17 16:08 | 2003-11-17 | REACTOR COOLANT SYSTEM LEAKAGE DUE TO A CRACKED SOCKET WELD During routine operations activities a leak was identified in the area of EPV0109 (combined SI/RHR to Accumulator "D" outlet line vent). At 0900 it was determined that the leak was due to a cracked weld on the socket upstream of EPV0109. The leak rate is 25-30 drops per minute. This condition is being reported as a degraded condition in the primary coolant system under 10CFR50.72(b)(3)(ii)(A). The plant is currently in Mode 5 with RCS pressure at approximately 345 psig and temperature at approximately 125F. Shutdown cooling is being supplied by the "A" train Residual Heat Removal System. The Resident Inspector has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-11-17
40326 | -1 | PERRY | 1 |  |  | [1] GE-6 | 2003-11-17 12:10 | 2003-11-17 15:26 | 2003-12-02 | DIVISION 1 AND 2 DIESEL GENERATORS AND ALL ECCS SYSTEMS WERE DECLARED INOPERABLE While aligning the Emergency Service Water (ESW) to the swale, the sluice gates were opened without the ESW being aligned to the swale. This condition made both Div 1&2 Diesel Generators and all ECCS systems inoperable. The probable cause of this event is that the wrong procedure was used in this evolution. Procedure SOI-P45/49 sec 7.3.1 "ESW Pumphouse Forebay Emergency Supply Initiation" was used instead of the correct procedure SOI-P45/49 section 7.3.3. "Alignment of ESW to Pumphouse Forebay Emergency Supply". The condition was discovered at 1215 and corrected at 1220 after section 7.3.1 was exited and section 7.3.3 was used to complete the lineup to the swale. The NRC Resident Inspector was notified. * * * RETRACTED AT 1457 ON 12/02/03 BY LAUSBERG TO ROTTON * * * "Further engineering analysis documented [that] the safety function of the Emergency Service Water (ESW) system was not lost while the system was inappropriately aligned. Also, plant design accounts for operator action to restore proper alignment and ensure continued functionality. Since the safety function of ESW was, and would continue to be maintained, the ECCS systems did not and would not lose the ability to perform their safety functions. Therefore, this condition is not reportable under 10CFR50.72(b)(3)(v)(B) and (D) as an event or condition that could have prevented fulfillment of a safety function and ENF 40326 is retracted." The licensee notified the NRC Resident Inspector. Notified R3DO Bruce Burgess. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT RHR INOP | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(v)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-11-17
40325 | 0 | LASALLE | 1 |  |  | [1] GE-5,[2] GE-5 | 2003-11-17 01:10 | 2003-11-17 09:35 | 2003-11-17 | EVENT OR CONDITION THAT COULD HAVE PREVENTED FULFILLMENT OF A SAFETY FUNCTION "This report is being made pursuant to 10CFR50.72(b)(3)(v)(D), Event or Condition that could have prevented fulfillment of a Safety Function needed to mitigate the consequences of an Accident. During performance of scheduled surveillance test LIS-HP-310, Reactor Vessel High Water Level 8 [High Pressure Core Spray] HPCS Injection Valve Closure Instrument Channels A and B Functional Test, Instrument Maintenance personnel discovered one end of fuse 1B21A-F8 not fully seated. The other end of the fuse was fully seated, and was maintaining the un-clipped end in sufficient contact with the fuse holder to complete the circuit. Had the circuit been deenergized, a Control Room annunciator (1H13-P601 A404) would have alarmed, and High Pressure Core Spray (HPCS) automatic low level initiation circuits would have been disabled. The fuse was fully seated without incident. "Upon discovery of the unseated fuse, the initial operability determination concluded that adequate contact was maintained to keep the circuit OPERABLE. After followup evaluation by Engineering, it was determined that continued OPERABILITY could not be assured during a seismic event. Failure of this fuse would prevent automatic actuation of HPCS on reactor vessel level low 2; and would prevent automatic closure of the HPCS discharge valve 1E22-F004 on reactor vessel level high 8. This would prevent the HPCS system, a single train safety system, from performing its design function during a Loss of Coolant Accident subsequent to a seismic event. This is reportable as an 8 hour ENS notification." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-11-17
40324 | 0 | QUEENS MEDICAL CENTER |  |  |  |  | 2003-11-04 | 2003-11-14 14:41 | 2003-11-14 | REPORTED LOSS OF NINE IMPLANTED I-125 SEEDS The licensee reported that 9 out of 156 I-125 seeds are unaccounted for following an autopsy performed on the recipient of an implant. The implant recipient was a dolphin which received the seeds on 08/16/03 and it died 11/02/03 and an autopsy was performed 11/04/03. The seeds probably came out of the dolphin where it was kept in a tank and washed into the harbor. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 4 | HI | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-11-14
40323 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 2003-11-14 | 2003-11-14 13:12 | 2003-11-14 | LOST TRITIUM EXIT SIGNS The State of Nebraska reported that one of their licensees could not account for 12 tritium exit signs during their annual inventory check. The signs were manufactured in 05/87 and 11 contained 25 curries each of tritium and 1 contained 50 curies. All activities were measured at date of manufacture. Remodeling of the store occurred during the period between the previous inventory check and the current inventory. The licensee has contacted the general contractor, but the location of the exit lights is still unknown. They may have ended up in the landfill. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2003-11-19
40322 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-11-13 21:49 | 2003-11-13 23:39 | 2003-11-13 | LOSS OF 115 KV LINE RESULTS IN EMERGENCY DIESEL GENERATOR AUTO-START "Auto initiation of Emergency Diesel Generator (EDG) 103 and re-energizing of PB 103 from EDG due to loss of off-site 115 KV line #4. Line #4 was momentarily lost, then re-energized. The loss of power also resulted in a trip of Reactor Recirculating Pump 13. Power reduced to approximately 80% rated. Recovery operations are in progress." All systems functioned as required and there was not anything unusual or not understood. The NRC Resident Inspector was notified. | 80 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-13
40321 | 0 | MILLSTONE |  |  | 3 | [1] GE-3,[2] CE,[3] W-4-LP | 2003-11-13 17:15 | 2003-11-13 19:25 | 2003-11-13 | LICENSEE CALLED THE WATERFORD, CT. FIRE DEPARTMENT TO ASSIST IN EXTINGUSHING A FIRE OUTSIDE THE PROTECTED AREA The licensee notified the Waterford, CT Fire Department to assist in extinguishing a fire affecting their offsite domestic water supply in the owner controlled area outside of the protected area. The fire caused damage to the offsite domestic water system limited to the heat tracing circuit for piping, an influent water filter and a trailer that provided shelter for the equipment. The fire, which was approximately 75-100 yards outside the protected area fence, was extinguished within 11 mins. The domestic water influent filter has been bypassed to allow normal domestic water supply capacity to the plant. The cause is being investigated. The NRC Resident Inspector was notified. | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode3: Power Operation; FMode3: Power Operation | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-13
40320 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-11-13 11:35 | 2003-11-13 13:48 | 2003-11-13 | AUTOMATIC REACTOR TRIP FROM 100% POWER WITH CAUSE BEING INVESTIGATED "Unit 1 was at 100% power when an automatic reactor trip occurred. The Auxiliary Feedwater systems automatically started due to low post trip steam generator levels. This includes the steam driven Auxiliary feedwater pump. The steam discharge of this pump is considered to [be] a gaseous release due to trace amounts of tritium in the secondary system. These trace amounts are well below limits. The pump was shutdown after 31 minutes of operation, terminating the discharge. The Rad Waste & Effluents Section will assess the impact during the event response review. The plant is currently stable in mode 3 with steam generator levels restored to post shutdown values. The steam dumps and main unit condenser are available for heat removal. All normal and emergency busses are energized from offsite power." All rods fully inserted, no ECCS actuation and no primary or secondary relief valves lifted. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-11-13
40319 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-11-13 09:54 | 2003-11-13 12:37 | 2003-11-13 | AUTO START AND LOADING OF THE "B" EMERGENCY DIESEL GENERATOR While the plant was in "ER-SC.1", Adverse Weather Plan, due to high winds and offsite power in a 50/50 alternate lineup, a momentary loss of offsite power circuit "751" occurred. This resulted in an undervoltage condition on safeguard busses "16" and "17". The "B" emergency diesel Generator automatically started and energized buses "16" and "17" . Entry was made into AP.Elec.1, Loss of 12A and/or 12B busses. The offsite electrical lineup was changed to 100/0 on circuit "767". Safeguard busses were re-energized from offsite power and the "B" diesel generator was secured and returned to automatic. This sequence of events took 22 minutes. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-13
40318 | -1 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-11-12 22:22 | 2003-11-13 05:27 | 2003-12-04 | HIGH PRESSURE COOLANT INJECTION SYSTEM ISOLATION DURING TESTING "During quarterly surveillance testing of the High Pressure Coolant Injection (HPCI) System the HPCI system isolated. The cause of the isolation is believed to be high turbine exhaust diaphragm pressure. HPCI is currently inoperable. The outboard steam line isolation valve closed automatically and the inboard steam line isolation valve was manually closed. The HPCI room carbon dioxide fire protection system actuated due to the high temperature spike. No fire was present. The Reactor Core Isolation Cooling (RCIC) System, Auto Depressurization System (ADS), Low Pressure Core Spray System and Low Pressure Coolant Injection System are operable. "Initial Safety Evaluation - Low initial safety significance due to availability of alternate high and low pressure injection systems. "Corrective Actions - HPCI will remain inoperable pending investigation. Determine and correct the cause of HPCI isolation. Determine if the inboard steam isolation valve should have automatically closed." The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 12/04/03 @ 0945 BY STEVE TABOR TO C GOULD * * * Upon further investigation of this event, it has been determined that the malfunction of the HPCI system was due to a condition which was introduced by the maintenance/testing activities while the system was declared inoperable. During the valve restoration/clearance cancellation process performed in support of HPCI system return to service, the 2-E41-F021, HPCI Exhaust Line Check Valve was inadvertently left in the locked closed position. In this configuration turbine exhaust over pressurization occurred resulting in actuation of the turbine exhaust diaphragm high pressure trip, subsequent generation of a Primary Containment Isolation system Division 1 Group 4 isolation signal, closure of the HPCI system outboard steam isolation valve 2-E41-F003, and rupture of the HPCI turbine exhaust rupture disc assembly. An evaluation of the impact of this event was performed and the necessary corrective actions and additional post-maintenance testing completed satisfactorily prior to declaring the HPCI system operable on November 16, 2003, at 2015 EST. After further review of the event and event reporting guidance, this event is not reportable in accordance with 10 CFR 50.72 or 50.73. NUREG-1022, Revision 2 provides clarification of the reporting requirements contained within 10 CFR 50.72 and 50.73. Specifically, in discussions associated with events that could prevent fulfillment of a safety function, NUREG-1022, Revision 2, Section 3.2.7, provides the following example of a condition that is not reportable under these criteria: removal of a system or part of a system from service as part of a planned evolution for maintenance or surveillance testing when done in accordance with an approved procedure and the plant's TS (unless a condition is discovered that could have prevented the system from performing its function) In this case, HPCI was properly removed from service for planned maintenance/testing under TS Limiting Condition for Operation, A2-03-1190, and was not returned to service until HPCI system operability was restored. The intent of the qualifying statement in NUREC-1022 (i.e., unless a condition is discovered that could have prevented the system from performing its function) is to ensure that pre-existing operability concerns that are discovered during maintenance activities are reported. It is not intended to require reporting of conditions, introduced by the maintenance/testing activity that are identified and corrected prior to returning the system to service. In this case, post-maintenance testing performed prior to declaring the HPCI system operable, identified a problem that had been introduced by activities implemented in support of the maintenance activity prior to returning the HPCI system to service and which did not exist at any time when the HPCI system had been relied upon to fulfill its intended safety function. Therefore the licensee is retracting this event. The licensee notified the Resident Inspector The Reg 2 RDO(Brian Bonser) was notified | 0 | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-11-13
40317 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-11-12 14:21 | 2003-11-12 21:01 | 2003-11-12 | INADVERTENT ACTUATION OF ESSENTIAL SERVICE WATER SYSTEM "On 11/12/03, Callaway Plant was restoring normal electrical power to electrical bus PB122 in the Circulating and Service Water Pumphouse. While attempting to restore the normal electrical power source to bus PB122, a Reactor Operator operated an incorrect switch. As a result of the incorrect switch operation, two other electrical feeder breakers opened and de-energized electrical busses PB121 and PB122. This resulted in a loss of the normal service water system which supplies cooling water to both safety related and non-safety related loads during normal operation. At 1421, operators manually initiated operation of the Essential Service Water system to restore cooling water to safety related loads. As a result of the loss of normal cooling water to non-safety related loads, a turbine runback occurred and power was stabilized at 68% reactor power. Initial plans are to perform inspections of affected electrical breakers plus circulating water and service water pumps. These inspections will not prevent a return to normal power. "Essential Service Water is an alternate source of emergency feedwater but in this instance, it was actuated to supply cooling water to safety related loads, not to supply emergency feedwater. This event is voluntarily being reported as an 8-hour ENS call for a valid actuation of an emergency feedwater system." The licensee notified the NRC Resident Inspector. | 67 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-12
40316 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2003-11-12 18:15 | 2003-11-12 20:11 | 2003-11-12 | OFFSITE NOTIFICATION OF EMERGENCY SIREN ACTIVATION Calvert County, Maryland was notified that, while "silent" testing the new St. Mary's County sirens (not yet in service), the Calvert County sirens were inadvertently activated. The sirens sounded for approximately 15 seconds. The licensee will notify the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-12
40315 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-11-12 10:03 | 2003-11-12 14:03 | 2003-11-12 | EMERGENCY SIREN TEST FAILURE "On November 12, 2003, at approximately 1003 hours, during an annual emergency preparedness siren test, the five sirens from New Hanover County, NC, did not respond to the signal sent by the New Hanover County Emergency Operations Center (EOC). The sirens were subsequently tested from the Brunswick Nuclear Plant (BNP) Emergency Offsite Facility (EOF) and responded as required. Maintenance activities are in progress to restore New Hanover County EOC siren initiation capability. Initiation capability will be maintained at the BNP EOF until the capability is restored to New Hanover County. Of the remaining 31 sirens tested, 30 successfully passed the annual test and are considered to be operable. The additional failed siren blew a control power fuse during the test and has since been repaired, tested, and returned to operable status. The resident inspector has been notified. "The safety significance of this event is considered to be minimal. Both Units 1 and 2 are operating in Mode 1 under normal parameters. Compensatory measures are in place to ensure the affected sirens will initiate if required. "Activities to restore siren initiation capability are in progress." * * * * UPDATE FROM DANIEL HARDIN TO MIKE RIPLEY 1706 ET 11/12/03 * * * * Repairs and retesting have been completed and, as of 1530 ET 11/12/03, New Hanover County EOC siren initiation capability has been restored. Notified R2DO (J. Pelchat) | 93 | 96 | 0 | 93 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-11-12
40314 | -1 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-11-10 17:40 | 2003-11-11 17:11 | 2003-12-01 | FITNESS FOR DUTY PROGRAM CONDITION "On November 10, 2003, at 1740 hours it was determined that a Fitness-For-Duty program condition existed which required a 24-hour report to the NRC. "Personnel with unescorted access are placed into different groups within the Fitness-For-Duty program. One of these groups, the Immune group, is for personnel not eligible for random test selection at our site, such as the NRC. The remaining groups become part of the random eligible population. "During a review of the Fitness-For-Duty program it was discovered that the total number of personnel in the Immune population group was higher than normally expected (133 vs. 24). Some personnel required to be in the random eligible population were discovered to be in the Immune group, which rendered them ineligible for selection. (This primarily affected personnel transferring from an approved program within 30 days.). This resulted in non-compliance with 10 CFR 26.24. "Security personnel are manually correcting the group listings, identifying the affected individuals, scheduling individuals still on site for testing, and notifying the plants where individuals potentially affected may have gone. "A root cause investigation is presently being conducted to identify the extent, time frame, and cause of this event. If relevant information is uncovered as a part of the root cause investigation that affects the reportability determination, the NRC will be notified. "This condition is being reported in accordance with 10CFR26.73." The licensee has notified the NRC Resident Inspector * * * RETRACTION AT 1553 ON 12/01/03 FROM SWEET TO GOTT * * * Based on subsequent research, the licensee determined that the above event is not reportable as a significant event under 10 CFR 26.73. The licensee will notify the NRC Resident Inspector. Notified R2DO (Bonser) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 26.73 |  |  |  | 0 | 2003-11-11
40313 | 0 | LAKELAND MEDICAL CENTER |  |  |  |  | 2003-11-10 12:15 | 2003-11-11 10:14 | 2003-11-11 | LESS THAN PRESCRIBED DOSE TO PATIENT The licensee received from the pharmacy a dose of Samarium-153 isotope (93.5 millicuries) scheduled to be administered to a patient for bone pain treatment. The dose calibrator at the hospital indicated that the assayed activity of the Samarium-153 was 9.39 millicuries. The licensee called the pharmacy and questioned about the discrepancy that the assayed activity needed to be multiplied by a factor of 10 which made the calculated value equal to 93.9 millicuries. The dose was then administered to the patient. About one hour later the pharmacy called and stated that the dose the patient received was in fact 9.39 millicuries of Samarium-153, realizing that the mistake was made due to the assumption that Samarium-153 is not just a pure beta emitter but actually gives off gamma radiation. The dose calibrator was accurate and the procedure was improperly followed by multiplying the assayed dose by a factor of 10. The physician, the Radiation Safety Officer and the patient were notified of the mistake. The physician will administer the rest of the dose to the patient. The licensee will make policy and procedural changes to reflect the fact that Quadramet Samarium-153 emits gamma radiation and can be properly measured by the hospital's calibrator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 3 | MI | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-11-11
40312 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-11-10 | 2003-11-10 17:51 | 2003-11-10 | AGREEMENT STATE REPORT - STOLEN AND RECOVERED TROXLER MOISTURE DENSITY GAUGE The State of California was informed at 1900, November 9, 2003 that Construction Testing & Engineering had reported the theft of one of their Troxler gauges (Model 3440, S/N 24168). The theft occurred on Friday November 7, 2003, and was reported to Sacramento County Sheriff. The sheriff detectives indicated that they would be questioning the operator who had possession of the gauge at the time it was stolen. An onsite inspection/investigation will be conducted. The licensee RSO indicated that the theft had been on the local television news Monday morning along with photographs of the stolen device, and a reward for its recovery. Subsequent to the initial report, the gauge was reported by an unknown party to be in a ditch in an area north of Sacramento. Sheriffs, Hazmat, and other agencies responded and the gauge was recovered without incident. California Incident Report # 111003. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-11-13
40311 | -1 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-11-10 07:20 | 2003-11-10 16:04 | 2003-12-31 | BYPASSING THE PRESSURE SUPPRESSION FUNCTION OF THE TORUS "On 11/10/2003 at 07:20 CST it was discovered, during a control room panel walk-down, that Dresden U2 had primary containment valves 2-1601-56 Torus Purge valve and 2-1601-21 DW (drywell) Purge valve open simultaneously. This valve alignment created a flow path from the Drywell to the Torus, effectively bypassing the pressure suppression function of the torus water volume during a LOCA (Loss of Coolant Accident) condition. This condition placed U2 containment in an unanalyzed condition, not capable of performing the intended design function, which is to mitigate the consequences of a LOCA. The proper valve alignment was restored at 07:26 CST which restored U2 primary containment to operable status per TS (Tech. Spec) 3.6.1.1. "A review of plant data identified that this valve arrangement, which bypassed primary containment, had been in effect when U2 entered Mode 2 (Startup) from Mode 4 (Cold Shutdown) at 12:01 on Nov 9, 2003. In addition, this valve line-up existed for a duration greater than that allowed by TS 3.6.1.1 A.1 and B.1 (1 hour)." The NRC Resident Inspector was notified of this event by the licensee. **** Retraction on 12/31/03 at 1430 EST by J. Welch taken by MacKinnon **** "Dresden has performed an engineering evaluation that bounds the plant conditions that existed while the two valves were simultaneously open. The evaluation concluded that the valves would have automatically closed in sufficient time to prevent exceeding the design limits of the primary containment during a postulated Design Basis Accident. "Therefore, Dresden retract the ENS call associated with this event. This event will be the subject of an Licensee Event Report in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), 'Any event or condition which was prohibited by the plant's Technical Specifications.'" R3DO (Ken Riemer) notified. The NRC Resident Inspector was notified of the above retraction by the Licensee. | 0 | 5 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION | ACCIDENT MITIGATION |  |  | IMode2: Startup; FMode2: Startup | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(ii)(B) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-11-10
40310 | 0 | EASTERN ISOTOPES INC |  |  |  |  | 2003-11-10 07:00 | 2003-11-10 13:52 | 2003-11-10 | TRANSPORTATION EVENT - SYRINGES LOST FROM COURIER VEHICLE The licensee reported that at 0700 ET on 11/10/03, a courier was transporting syringes containing Technetium-99M and Flourine-18 when, while driving over the Key Bridge in Georgetown, District of Columbia, the trunk of the vehicle popped open and 2 boxes were released just past the bridge in Georgetown. Everything was recovered except for 1 syringe containing 15 millicuries of Flourine-18 calibrated at 1145 ET with a 2-hr half life and 1 pig containing a syringe with 2 millicuries Technetium-99M calibrated at 1300 ET with a 6-hr half life. Pieces of the syringe containing the Flourine-18 were recovered and it was believed that the syringe had been run over by a truck. A radiation survey was performed and only very low readings were found where the syringe had been broken. The pig containing the syringe with Technetium-99M was not recovered and it is believed to have rolled into a storm drain near the intersection of Reservoir Road and M Street in Georgetown. The licensee and the local Hazmat Team determined that there was no need to attempt a recovery of the material from the storm drain. The licensee had initially notified the VA Dept. of Health, DC Department of Health, and US DOT (NRC) of the released Flourine-18 prior to realizing that the syringe containing Technetium-99M was also missing. The licensee will be updating these agencies. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | VA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-11-10
40309 | 0 | FARLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-11-10 10:36 | 2003-11-10 12:41 | 2003-11-10 | AUTOMATIC REACTOR TRIP DUE TO FALSE RCP BREAKER OPEN SIGNAL "Reactor Protection System actuation in response to an indicated (not an actual) 2A RCP [Reactor Coolant Pump] breaker open position signal. All reactor protection and support systems operated as expected. The Aux Feedwater System started as required in response to the tripping of both Steam Generator Feed Pumps. All 3 RCPs are running; none have tripped. "Not understood is the indication of the 2A RCP breaker open when the breaker has remained closed." The licensee reported that all control rods fully inserted; decay heat is being rejected to the condenser via the steam dumps; a steam generator atmospheric relief may have momentarily lifted during the transient; and that the electrical grid is stable. The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-11-10
40308 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-11-10 09:08 | 2003-11-10 09:45 | 2003-11-10 | UNUSUAL EVENT DECLARATION DUE TO RELEASE OF FLAMMABLE GAS THAT MAY IMPACT NORMAL STATION OPERATIONS A 1/8 inch sealant injection plug for the Main Generator was discovered out of it's location. This allowed the leakage of hydrogen gas into the Turbine Building. Fire Brigade leader responded and observed a flammable concentration of hydrogen. All available ventilation was initiated, and non-essential personnel were evacuated from the 75 foot level of the Turbine Building. Maintenance personnel responded and were able to reinstall the plug. Hydrogen levels were reduced to less than flammable. No radiological release occurred or is expected. An Unusual Event was declared at 0908 on 11/10/2003 and terminated at 0908. Unusual Event was declared based on EAL 18a.3 - Release of toxic or flammable gas from anywhere near site or on site that may adversely impact normal station operations. The licensee notified the NRC Resident Inspector and New Hampshire. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 1 | NH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-11-10
40307 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-11-10 | 2003-11-10 09:32 | 2003-11-10 | AGREEMENT STATE REPORT FOR LOST/STOLEN SOURCE "On October 30, 2003, during a routine inventory of sources, it was discovered that a Nickel-63 electron capture source that had been in storage since January 23, 1996, was missing. An exhaustive search of source storage areas did not locate the source. However, upon questioning employees that had access to the source storage area, one employee recalled that the source in question had been picked up by a Health Physics Technician from the manufacturer, it was believed during the year 1998. The manufacturer denies having the source picked. A search of paperwork is ongoing to locate a transfer document, if one exists." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-11-13
40306 | -1 | WATERFORD | 3 |  |  | [3] CE | 2003-11-10 05:00 | 2003-11-10 06:41 | 2003-11-13 | SAFEGUARD VULNERABILITY - PHYSICAL SECURITY Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures were not employed. The licensee notified the NRC Resident Inspector. TAS notified Region IAT member who will followup for NRC. Contact the Headquarters Operations Officer for additional details. * * * UPDATE ON 11/13/03 @ 1340 BY T. MANZELLA/ R. MURILLO TO GOULD * * * RETRACTION After further review it was determined that there was no vulnerability that would allow access to a controlled access area, therefore the licensee is retracting this event. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-11-10
40305 | -1 | SEQUOYAH |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-11-09 23:15 | 2003-11-10 00:39 | 2004-01-05 | SEQUOYAH UNIT 2 AUXILIARY FEEDWATER ACTUATION DURING OUTAGE "On 11/9/03 at 2315 [EST], with Unit 2 in Mode 3 in preparation for a Refueling Outage, an unanticipated ESF actuation occurred. With one Main Feedwater Pump (MFP) reset and one MFP tripped per the General Operating Procedures, Main Condenser Vacuum was being broken. Low Condenser vacuum caused the trip of the reset MFP. The signal for trip of two MFPs caused an Aux Feedwater (AFW) start. AFW was in service in manual control per procedure when the start signal was received; however, the start signal caused the Level Control Valves (LCVs) to reposition to their accident position." The licensee notified the NRC Resident Inspector. * * * RETRACTION PROVIDED BY B HARRIS TO JEFF ROTTON AT 1442 EST ON 01/05/04 * * * "On November 9, 2003, after the planned Unit 2 reactor shutdown for refueling outage number 12, an auxiliary feedwater system start signal was initiated. During the shutdown, the auxiliary feedwater pumps (AFW) were started and both main feedwater pumps (MFP) had been tripped. Following transition from emergency operating procedure to the normal plant shutdown procedure, the feedwater isolation signal and one MFP trip were reset to allow shutdown of the turbine-driven pump, in accordance with plant procedures. As a result of the reactor coolant temperature decreasing below 540 degrees Fahrenheit, emergency boration was performed, and subsequently, control room personnel closed the main steam isolation valves (MSIVs) to limit cooldown of the RCS. After closure of the MSIVs, Operations personnel broke main condenser vacuum in accordance with plant procedures. The operators knew by their procedure that this would result in a low-condenser vacuum trip signal to the reset MFP trip bus and, with both MFPs trip bus tripped, the logic would be completed for initiation of an AFW start signal. The procedure states 'Breaking main condenser vacuum will cause loss of main feed pump turbine condenser vacuum to both MFPs resulting in an ESF actuation.' "On November 10, 2003, at 0039 Eastern standard time, NRC was notified in accordance with 10 CFR 50.72 (b)(3)(iv)(A) of the ESF actuation (event notification No. 40305). "10 CFR 50.72 and 50.73 requires reporting of any event or condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation. NUREG 1022 states that the intent is to require reporting of actuations of systems that mitigate the consequences of significant events. The breaking of the condenser vacuum was driven by plant conditions. However, the start signal to the AFW system was not to mitigate an event for the condition the plant was in (i.e., both MFPs had been secured and decay heat was being controlled by AFW in accordance with normal operating procedures) and is therefore considered a preplanned event. "Based on the above information, the initiation of the AFW start signal is not reportable and the notification is being withdrawn." The licensee has notified the NRC Resident Inspector. Notified R2DO(Ayres) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Hot Standby; FMode2: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-10
40304 | 0 | KANSAS DEPT OF HEALTH & ENVIRONMENT |  |  |  |  | 2003-10-28 | 2003-11-07 17:44 | 2003-11-07 | AGREEMENT STATE - PERSONNEL OVEREXPOSURE "Licensee reported via phone call of potential overexposure of two employees to carbon-14. The licensee indicated initial calculations showed approximately 2.5 Rem exposure. "Licensee followed up the phone call on November 7, 2003, after receiving urinalysis results. The initial calculations indicated internal whole body exposure to carbon-14 of 7976 milli Rem and 8976 milli Rem for two employees. "The 252 milliCuries carbon-14 was in a mixture of 221 micro liter benzene in a flame sealed glass ampoule which was being readied for shipment to a customer. The ampoule was wiped for contamination and placed on a counter outside of the fume hood for approximately 2 hours. Initially the ampoule was thought to be in the fume hood. "The ampoule was found to be leaking and 59 milliCuries of carbon-14 remained in the ampoule. The resultant loss into the lab was 193 milliCuries of carbon-14." This is a preliminary report to be updated as information is received. Person 1 received 7.976 Rem internal (CEDE) occupational. Person 2 received 8.976 Rem internal (CEDE) occupational. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | KS | OTH | AGR |  |  |  |  | 0 | 2003-11-12
40303 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-11-07 07:45 | 2003-11-07 16:09 | 2003-11-07 | FFD REPORT A non-licensed supervisory individual was found to have failed a fitness for duty test because he exceeded the site's blood-alcohol level limits. The individual's access has been blocked. Contact the HOO for additional details. The NRC Resident Inspector has been notified. | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2003-11-07
40302 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-11-07 08:30 | 2003-11-07 14:57 | 2003-11-07 | RELEASE OF CHEMICALS INTO STATE WATERS "At 0830 hours on 11/07/03, a phosphoric acid/sodium hydroxide/potassium hydroxide diluted chemical mix overflowed from a holding tank, which resulted in a discharge of the chemicals into state waters through the plants storm drain system. This discharge was a result of two un-isolated filter vents that allowed the chemical mixture to overflow to the ground. It is estimated that approximately 70 gallons of the chemical mixture entered the plants discharge canal, which enters state waters, before it was isolated. The chemical mixture is considered non-hazardous. There were no radiological consequences associated with the discharge of the chemical mixture. Cleanup efforts are in progress. "This event is being reported in accordance with 10CFR50.72(b)(2)(xi) due to the fact that the Virginia Department of Environmental Quality was notified at 1330 hours EDT of the discharge into state waters. The NRC resident was notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-11-07
40301 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-11-07 01:34 | 2003-11-07 04:15 | 2003-11-07 | MANUAL SCRAM AT DUANE ARNOLD DUE TO HI COOLANT CONDUCTIVITY "Inserted a Manual Reactor Scram due to high reactor coolant conductivity. Source of high reactor coolant conductivity is not certain at this time. "In addition, this report is being made under 50.72(b)(3)(iv)(A), 'Any event or condition that results in valid actuation of any systems listed in paragraph (b)(3)(iv)(B) of this section' due to PCIS groups 2, 3, and 4 being received when reactor water level dropped below 170". All isolations went to completion. The reactor water level drop is normal following a scram from 45% power due to void collapse in the reactor vessel. Reactor water level was restored to normal and the PCIS group isolations were reset. "The current plan is to cool down the plant and enter Mode 4, plant cool down is being achieved using the RCIC system until the source of the conductivity transient is identified and isolated." The licensee indicated shortly prior to the scram a coolant chemistry transient was in progress. The limit for reactor coolant conductivity is 5 micro mhos per centimeter and the highest conductivity reading reached was 8 micro mhos per centimeter. The licensee speculates the most likely source of the high conductivity is related to an off service condensate demineralizer. There were no automatic ECCS initiations. No SRVs lifted. All control rods properly inserted. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 45 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-11-07
40300 | 0 | COLORADO DEPT OF HEALTH |  |  |  |  | 2003-11-05 17:30 | 2003-11-06 12:37 | 2003-11-06 | LOST OR STOLEN MOISTURE/DENSITY GAUGE At approximately 1700 MST on 11/5/03, a technician using a CPN model MC-3 moisture density gauge was told to relocate her vehicle on the jobsite at 8247 Shaffer Place in Littleton, CO. The gauge contains 10 millicuries of Cs-137 and 50 millicuries of Am-241, with serial number M380804502. The technician placed the gauge inside its orange transport box in the back of her truck, but she left the tailgate open, and did not chain the box to the bed of the truck. The technician left the jobsite at approximately 1730 MST to return to the main office 25 miles away. Shortly before arriving at the main office, the technician realized that the truck bed was open and the transport box (and gauge) were not in the truck. The technician turned around and re-traced her route back to the jobsite, but was unable locate the gauge. The technician reported the missing gauge to the Radiation Safety Officer (RSO) at 1830 MST. The RSO, along with other supervisors, retraced the route to the jobsite and searched for the gauge, which was not found. The licensee notified the Colorado Department of Public Health and Environment (CDPHE) at 0530 MST on 11/6/03. The CDPHE informed the licensee that a written report is required within 30 days. The licensee notified local law enforcement officials regarding the lost gauge, and issued a press release offering a reward for information leading to its recovery. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CO | OTH | AGR |  |  |  |  | 0 | 2003-11-11
40299 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2003-11-05 17:34 | 2003-11-05 19:31 | 2003-11-05 | AUTOMATIC REACTOR TRIP DUE TO HIGH REACTOR COOLANT SYSTEM PRESSURE "Crystal River Unit 3 was at 37 percent power starting up from a refueling outage. During troubleshooting of control problems with the B Main Feedwater Pump, a feedwater transient occurred which underfed the steam generators. This resulted in a reactor trip on high Reactor Coolant System pressure and Emergency Feedwater Actuation on low steam generator levels. This event is reportable as a 4-Hour Non-Emergency Notification per 10CFR50.72 (b)(2)(iv)(B) for Reactor Protection System Actuation and as an 8-Hour Non Emergency Notification per 10CFR50.72 (b)(3)(iv)(A) for Emergency Feedwater Actuation." The licensee reported that all control rods fully inserted on the trip and that steam generator safety valves lifted and reseated as expected. The primary system is currently at 2155 psi, 549 degrees F with steam generator feedwater being supplied by auxiliary feedwater. The main condenser is available and is being used for primary system heat removal via steam dump. The station electrical grid is stable and in normal configuration; the emergency diesel generators are operable and in standby. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 37 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-11-05
40298 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-11-04 21:32 | 2003-11-05 03:45 | 2003-11-05 | BRAIDWOOD 2 AFW SUPPORT SYSTEM ACTUATION DURING OUTAGE "Unit 2 auxiliary feedwater support systems actuated during scheduled ATWS testing when an unrelated clearance order placement de-energized two 6.9 kv busses (256 and 258). The 2 of 4 6.9 kv bus undervoltage coincidence initiated a valid auto-start signal causing lube oil pumps 2AF01PA-A, 2AF01PB-A and 2AF01PB-C to start. Auxiliary Feedwater Pump AOV discharge valves 2AF004A and 2AF004B auto opened. 2AF01PA 4kv breaker, which was in the equipment test position. Neither auxiliary feedwater pump started and no water transferred to the steam generators." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-11-05
40297 | 0 | BRUNSWICK |  | 2 |  | [1] GE-4,[2] GE-4 | 2003-11-04 17:32 | 2003-11-04 21:20 | 2003-11-04 | BRUNSWICK UNIT 2 SCRAM DUE TO GENERATOR/TURBINE TRIP "On November 4, 2003, at approximately 1732 hours, Unit 2 received a generator/turbine trip due to loss of excitation, which resulted in a Reactor Protection System (RPS) trip. Plant response to the reactor shutdown resulted in High Pressure Coolant Injection and Reactor Core Isolation Cooling [RCIC] system actuations on low reactor coolant level. Additionally, primary containment isolation system actuation signals for valve groups 1, 2, 3 , 6, 8, and 10 were received and the valves closed as required. All four emergency diesel generators automatically started, but did not load because power was never lost to the emergency buses. The loss of power from the generator trip resulted in reactor building ventilation isolation and automatic start of both trains of the Standby Gas Treatment (SBGT) system. SBGT Train A immediately tripped, but was successfully placed in service. All control rods fully inserted into the core. At approximately 1857 hours, another RPS trip was received due to low reactor coolant level while cycling Safety Relief Valves; however, all control rods were already inserted. "The safety significance of this event is considered to be minimal. The plant responded as designed to the transient with the exception of the SBGT Train A initial starting issue. "An event investigation team has been assembled to determine the cause of the event. Plant response to the event is being evaluated and identified issues will be addressed prior to plant restart." The licensee reported that the station electrical grid is normal and the emergency diesel generators have been shutdown and returned to standby status. The current plant conditions are 550 psi, 496 degrees F with RCIC operating to maintain reactor water level. The main condenser is available and being used to dump steam from the reactor. Two safety relief valves opened during the transient and reclosed as expected. The reactor water level decreased to minimum of approximately 90 inches during the transient. The cause of main steam isolation valve (MSIV) closure is under investigation. The licensee also reported that this event caused a Group 6 Isolation, reactor building ventilation isolation, and standby gas treatment actuation signal on Brunswick Unit 1. These Unit 1 systems have been returned to a normal configuration. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | A/R | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | [7 empty] | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-11-04
40296 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2003-11-04 14:30 | 2003-11-04 15:50 | 2003-11-24 | PRESSURIZER HEATER BUNDLE DIAPHRAGM PLATE DEGRADED CONDITION "On November 4, 2003, during the TMI Unit 1 15th (T1R15) refueling outage, an inspection of the Pressurizer Heater Bundle (PHB) Diaphragm Plate was completed. This Inspection identified a leak path emanating from the lower Pressurizer Heater Bundle. "The initial indication of a potential Reactor Coolant System (RCS) leak was boric acid residue located between the PHB Diaphragm Plate and the PHB Cover Plate. Initially the leak was believed to be from a seal weld, which is considered comparable to a gasket leak. Following disassembly of the PHB Cover Plate and performance of NDE, it was determined that the pathway was through the edge of the PHB Diaphragm Plate. This degraded condition of the PHB Diaphragm Plate is indicative of a RCS pressure boundary leak. This notification is being made in accordance with 10 CFR 50.72(b)(3)(ii)(A)." The licensee provided the following pre-refuel outage information: RCS Leak Rate = less than 0.1 gallons per minute Activity = 0.45 microcuries/milliliter TS [Technical Specifications] Limits: No leakage (3.1.6.4) Secondary System Activity = less than 1E-10 microcuries/milliliter The licensee has notified the NRC Resident Inspector. * * * UPDATE ON 11/24/03 AT 0114 EST FROM JOHN SCHORK TO HOWIE CROUCH * * * "Subsequent to the initial report made on 11/4/03, the Pressurizer Heater Bundle (PHB) Diaphragm Plate was repaired. On November 23, 2003 during performance of post-maintenance testing inspections with the plant in Hot Shutdown, steam was observed emanating from either the seal weld or the PHB diaphragm plate. "This update is being made to EN 40296 because the observed leak is being conservatively classified as a leak from the Primary System Pressure Boundary and is being addressed in a manner consistent with TMI Technical Specifications 3.1.6.4 and 3.1.6.6. An evaluation of the safety implications of the leak has been initiated. A condition report has been generated to capture all of the actions that have been and will be taken in response to the leak. "The plant is being taken to cold shutdown in order to perform an inspection and repair of the leak. The plant continues to be subcritical with all control rods fully inserted and the Reactor Coolant System boron concentration is at the refueling boron concentration. The plant continues to remain in the T1R15 refueling outage. "The NRC TMI-1 Sr. Resident Inspector has been notified of the leak. No other notifications were made to the State, Local or other governmental agencies. No press release has been issued regarding the event. The cause and corrective action to repair the leak will be addressed in the licensee event report being submitted in response to EN 40296. "The location of the leak observed on November 23, 2003 is in the immediate vicinity of the lower Pressurizer Heater Bundle. There has been no determination of the volumetric leak rate. The leak consists [of] steam wisping from the location. The start date of the leak is November 23, 2003 and the leak was initially observed during hot shutdown checks at 1930 hours on November 23, 2003. There has been no radiological release to the environment as a result of this leak." The licensee has notified the NRC Senior Resident Inspector. Notified R1DO (John Rogge) and NRR (William Ruland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-11-04
40295 | 0 | WATERFORD | 3 |  |  | [3] CE | 2003-11-04 | 2003-11-04 12:08 | 2003-11-04 | NUMBER OF STEAM GENERATOR TUBES REQUIRING REPAIR EXCEEDS 1 PERCENT "At 0400 CDT on November 4, 2003 with Waterford 3 refueled, steam generator inspection was being performed in accordance with Technical Specification (TS) 4.4.4.2, Steam Generator Tube Sample Selection and Inspection. The results of the on-going inspection performed on Steam Generator 31 indicated that greater than 1% of the inspected tubes require repair. The number of inspected tubes for SG 31 is 8906 and to date 98 tubes require repair. Based on TS 4.4.4.2.C, this determination results in the Category C-3. The current inspection results do not meet the criteria specified for steam generator tube degradation in NUREG 1022, Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73. However, for Category C-3, TS Table 4.4-2, Steam Generator Tube Inspection, requires that the results of the inspection be reported under 10 CFR 50.72(b)(2), which was superceded by an 8 hr notification in accordance with 50.72(b)(3)(ii). "Per TS 4.4.4.5, the final results of the SG tube inspection, which fall into Category C-3, shall be reported in a special report within 30 days and prior to resumption of plant operation." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-11-04
40294 | 0 | COOPER HEALTH SYSTEM |  |  |  |  | 2003-11-03 13:00 | 2003-11-04 11:30 | 2003-11-04 | A PATIENT RECEIVED AN UNDERDOSAGE DURING THERAPUTIC TREATMENT OF THE CERVEX A patient who was receiving her second of six treatments for cervix cancer on 10/31/03 was given a 200 Rad dose when a 600 Rad dose was prescribed. This was due to personnel error and both the patient and physician were notified. Since the treatment was an under dose and only the second treatment of six, the physician will make up for the discrepancy during the other treatments. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-11-04
40293 | 0 | OR DEPT OF HEALTH RAD PROTECTION |  |  |  |  | 2003-11-03 12:00 | 2003-11-03 19:15 | 2003-11-18 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE A Troxler Model 3440 Moisture Density Gauge, S/N 34418 (8 millicurie Cs-137; 40 millicurie Am-241/Be) was stolen from the back of a pickup truck sometime between 2000 PST 11/02/03 and 1200 PST 11/03/03 at an employee's apartment complex in Tualatin, OR. The gauge was locked in its case and the case was chained to the truck at the time of the theft. The licensee notified the Tualatin, OR police department. The State Dept. of Radiation Protection will be issuing a press release. * * * UPDATE FROM WRIGHT TO GOTT AT 1025 EST ON 11/18/03 * * * The Troxler Gauge was found behind a discount store and reported to the Tualatin, OR police on 11/17/03 at 1800 PST. The gauge was retrieved by the Oregon State Department of Radiation Protection. The gauge is intact. Notified R4DO (Kennedy) and NMSS (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OR | OTH | AGR |  |  |  |  | 0 | 2003-11-06
40292 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-11-03 17:20 | 2003-11-03 17:36 | 2003-11-03 | NON-CONSERVATISM IN DESIGN METHODOLOGY FOR LOSS OF RCP (REACTOR COOLANT PUMP) SEAL COOLING "The design data used to support Dominion's methodology to cope with a loss of [RCP] seal cooling (which was based on Westinghouse WCAP-10541 Rev. 2) may be non-conservative. The NRC issued an SER on Westinghouse report WCAP-15603 that indicates data from this new model must consider a 20% probability that the hot RCP seals may result in up to 182 gpm leakage per pump if seal cooling is lost for more than 13 minutes. Assuming this higher leak rate, the requirements of Appendix R, Section III.L, cannot be met since Pressurizer level could not be maintained. Current methodology indicates Surry will lose charging and seal cooling for greater than 13 minutes from a fire in the Emergency Switchgear Room. This report is being made pursuant to 10 CFR 50.72 (b)(3)(ii)(B). "The NRC resident [inspector] was notified of this condition." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | Power Operation | Cold Shutdown |  | Power Operation | Cold Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-11-03
40291 | 0 | NE DIV OF RADIOACTIVE MATERIALS |  |  |  |  | 1993-01-01 | 2003-11-03 12:13 | 2003-11-03 | AGREEMENT STATE - LOST OR STOLEN TRITIUM ILLUMINATED SIGN The following was received from the State of Nebraska via facsimile: "Four signs with 8.5 curies of tritium were installed at Big Red Keno Lottery in 1991 during a remodeling project. The main entrance to the building was moved in about 1993. The original main entrance doorway was closed except for a small door which was not a fire exit. They believe the sign to the original entrance was removed at that time. No one knows where the sign went. After doing an inventory requested by this Agency, the facility discovered the sign missing and we were notified. "The lost sign is a sealed source, manufactured by Safety Light Corporation, Model Number 880-12-5-12, Serial Number C17089. The probable disposition of the sign is the city landfill. "Nebraska event report ID number NE-03-0005" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | NE | OTH | AGR |  |  |  |  | 0 | 2003-11-06
40290 | 0 | CTI CONSULTANTS |  |  |  |  | 2003-11-03 07:30 | 2003-11-03 10:33 | 2003-11-03 | LOST HUMBOLDT NUCLEAR GAUGE The licensee reported that a technician left their office in Chesapeake, VA for a jobsite with the Humboldt gauge in the back of his truck and at approximately 0730 he noticed the gauge was missing. He notified his office of the incident and managers left the office in search of the gauge. They located the gauge intact and undamaged in the street not too far from the office at 0745. The gauge contained 11 millicuries of Cs - 137 and 40 millicuries of Am - 241. It was a Humboldt model 5000 serial # 4403. The gauge was taken to another jobsite. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | VA | OTH | GEN | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-11-03
40289 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-11-02 18:30 | 2003-11-02 20:47 | 2003-11-02 | EMERGENCY NOTIFICATION TONE ALERT RADIOS OUT OF SERVICE/RESTORED TO SERVICE "The Tone Alert System (Radio/EAS) has been out of service for greater than 1 hour. "The Tone Alert Radio/EAS was returned to service." The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-11-02
40288 | 0 | NINE MILE POINT | 1 | 2 |  | [1] GE-2,[2] GE-5 | 2003-11-02 18:30 | 2003-11-02 20:40 | 2003-11-02 | EMERGENCY NOTIFICATION TONE ALERT RADIOS OUT OF SERVICE/RESTORED TO SERVICE The National Weather Service was unable to activate the Tone Alert Radios. The allowable out of service time was exceeded. The Tone Alert Radios were out of service for greater than one hour. In accordance with site procedures, this is a major loss of notification capability. Oswego County reported that the Tone Alert Radios were returned to service. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-11-02
40287 | -1 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-11-01 17:00 | 2003-11-02 02:44 | 2003-12-26 | AN EVENT THAT COULD HAVE PREVENTED FULFILLMENT OF THE SAFETY FUNCTION TO MITIGATE THE CONSEQUENCES OF AN ACCIDENT, On November 1, 2003, the plant was performing testing on the Control Room Envelope for Unfiltered In-Leakage Tracer gas Test. During this test the control room ventilation is set up to simulate system line up following an F [high drywell pressure initiation signal], A [low reactor pressure vessel level], or Z [high containment building radiation] signal. This dual pressurization line up consists of both control room emergency filtration (CREF) fans running with the normal and one of two remote air intakes isolated. This line up caused a low-flow condition to occur on both trains of CREF, rendering both trains of CREF to become inoperable. The inoperability of the CREF is due to losing the permissive to allow the heaters located in each of the fresh air ducts to the emergency filters to energize. These heaters reduce the relative humidity of air entering the emergency filters to 70%. Without the heaters the 30-day dose limits to control room personnel of GDC 19 of 10CFR50, Appendix A could be exceeded during a Design Basis Accident. The isolation of a single remote air intake is a condition allowed under technical specification 3.3.7.1 and is also required for certain radiological and HAZMAT conditions. During an FAZ with an isolated remote air intake both trains of CREF will become inoperable until one train is shutdown. Once both trains of CREF were inoperable the plant entered LCO 3.0.3. per technical specification 3.7.3. At 1728 the plant opened the isolation valves for the second remote air intake and the low-flow condition cleared for one train of CREF and LCO 3.0.3 was exited. The plant is currently in a 7 day LCO to shutdown for having one train of CREF inoperable per 3.7.3. The NRC Resident Inspector was notified. * * * UPDATE (RETRACTION) AT 1439 EST ON 12/26/03 BY FRED SCHILL TO JOLLIFFE * * * On 11/1/2003 at 2344 [PST], Columbia Generating Station (CGS) reported (EN# 40287) both trains of Control Room Emergency Filtration (CREF) were made inoperable during performance of tracer gas testing. This condition was reported to NRC headquarters pursuant to 10 CFR § 50.72(b)(3)(v)(D) as a condition that at the time of discovery, could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. After further evaluation, the 8-hour report is being retracted based on the following: At 1646 (PST) on 11/1/2003, with the plant in mode 1, testing was being performed to measure control room in-leakage using (ASTM 741) tracer gas methodology. In accordance with the test procedure, the CREF system was configured in a non-standard manner that would create the most limiting in-leakage conditions. Specifically, the configuration was a dual-pressurization mode with both trains of CREF running and the normal, and one of the two remote intakes closed. This line-up caused a low-flow condition to occur in both CREF trains, and prevented electric heaters from energizing in each of the CREF air ducts containing the emergency filters. Differential pressure switches monitor the differential pressure across HEPA filters in each of the CREF trains. These switches provide a high/low alarm in the main control room to alert operators of either low airflow, fan failure, or dirt loading. Additionally, a low differential pressure setpoint provides an interlock permissive for automatic operation of an upstream duct heater. This design feature ensures the 5 KW heater has adequate airflow to prevent damage to the heater elements. When this low flow permissive is satisfied, the associated heater will cycle on and off to maintain the relative humidity of the air entering the CREF unit to 70% or lower. When the low-flow condition occurred on 11/1/2003, plant operators declared both trains of CREF inoperable and entered Technical Specifications Limiting Condition for Operation (LCO) 3.0.3 as directed by Technical Specifications LCO 3.7.3 condition D.1. This condition existed for approximately 45 minutes until 1728 (PST) when operators opened the second remote intake and the low-flow condition cleared. During the time the heaters were inoperable, meteorological conditions were recorded as: Relative Humidity (RH) between 31.5 to 34.0% RH, temperature between 39.2 to 40.3 degrees F, wind speed between 5.3 to 9.8 mph, and wind direction from the southeast. A postulated Main Steam or Feedwater line break outside of primary containment provides a potential for the RH conditions at the remote intake that was open during this event to exceed the measured ambient 34% RH. However, each of the remote intake lines are routed underground, then up through the interior of the building containing the control room, the intake ducts traverse the full length of the Control Room, and continue up to the 525 foot elevation where they join into a common line. Because the pipe is buried and routed through relatively warm internal building areas, the temperature of this fresh air makeup increases during this time of year. Test data collected in the same CREF alignment (i.e. dual train, single remote intake) showed a significant temperature increase (preliminary information indicates greater than 40 degrees F). Considering a worst-case postulated accident condition that results in remote intake inlet air containing 100% RH, only a minor temperature increase (i.e. approximately 2 degrees F) of the ambient fresh air makeup would be required to ensure that the resulting relative humidity of the air entering the CREF units was less than 95% RH. Therefore, taking into consideration the meteorological conditions, distance of the intake from CREF unit, and applying engineering judgment, it is reasonable to conclude that at all times during the approximately 45-minute event, the CREF inlet air relative humidity remained at or less than the design basis 95% RH and most likely less than the heater-controlled limit of 70% RH. As discussed in NRC Generic Letter 99-02 "Laboratory Testing of Nuclear-Grade Activated Charcoal," if ESF filtration systems have humidity control (i.e. heaters), then carbon lab testing should be in accordance with ASTM D3803-89 "Standard Test Method for Nuclear-Grade Activated Carbon" at 30 degrees C (86 degrees F) and 70% RH. For systems without humidity control the laboratory test conditions are 30 degrees C (86 degrees F) and 95% RH. Columbia's Technical Specification 5.5.7.c requires testing to demonstrate methyl iodide penetration for a sample of the CREF system charcoal adsorber is less than 2.5% when tested in accordance with ASTM D3803-89 at a temperature of (30 degrees C) 86 degrees F and 70% RH. The lower than normal flow conditions during the tracer gas test effectively resulted in a CREF system without humidity control, which per GL 99-02 would require lab testing at 30 degrees C (86 degrees F) and 95% RH. Figure A 5.1 of ASTM D3803-89 illustrates the impact of CREF unit operation with no humidity control. This figure provides the relative effect of carbon methyl iodide penetration versus % RH on new carbon. As shown by this figure, the methyl iodide penetration at 95% RH is 670% (which includes standard deviation) of penetration value at 70% RH. The most recent laboratory carbon test data for Columbia's filters provided methyl iodine penetration test results of 0.31% for train A and 0.13% for train B. Applying a multiplier of 6.7 (for the no-humidity control test 95% RH value) to these test results yields penetration values of 2.08% for train A and 0,87% for train B when no credit is taken for humidity control. A teleconference was conducted with an industry recognized charcoal testing laboratory to corroborate this carbon efficiency impact analysis. The laboratory stated they had observed an increase in penetration for used carbon of 300 to 500% (or 3 to 5 times) when varying RH from 70 to 95%. This analysis demonstrates that without reliance on the CREF heaters, the allowable methyl iodide penetration of 2.5% as specified in TS 5.5.7.c would not be exceeded and the penetration remains well below the more conservative analytical design limit of 5% (CGS accident analysis assumes 95% iodine removal efficiency for the CREF system). Therefore, the condition experienced at Columbia, on 11/1/2003 at 2344 (PST) where the CREF heaters did not energize during the low-flow condition, would not have prevented the CREF system from performing its design safety function and does not meet the criterion for reporting under 10 CFR § 50.72(b)(3)(v)(D) as "a condition that at the time of discovery, could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident." The licensee notified the NRC Resident Inspector. Notified R4DO Linda Smith. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-11-02
40286 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-10-31 19:48 | 2003-10-31 21:15 | 2003-10-31 | REACTOR TRIP ON LOW STEAM GENERATOR WATER LEVEL "Automatic Reactor Trip due to low Steam Generator levels. All systems responded normally. Plant is stable at NOT/NOP [normal operating temperature and pressure] in Mode 3. Emergency Feedwater system actuated as designed due to reactor trip." Lowest Steam Generator level reached was just below the trip setpoint of 25%. Low level caused by trip of one of two Main Feed Pumps. All control rods fully inserted. No primary or secondary relief valves lifted. The electrical system is stable and the EDG's remain in standby. Decay heat is being removed via steam dumps. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-10-31
40285 | 0 | ESMER & ASSOCIATES |  |  |  |  | 2003-10-31 07:00 | 2003-10-31 14:31 | 2003-11-03 | STOLEN TROXLER MOISTURE DENSITY GAUGE A Troxler moisture density gauge Model # 3411B, Serial # 9905 containing 8.1 millicuries Cs-137 and 40 millicuries Am-241:Be was stolen from a company field technician's SUV while parked at a motel in Kanawha City, WV sometime between 10:00 pm 10/30/03 and 7:00 am 10/31/03. The gauge was locked inside its case at the time of the theft. The licensee notified the Kanawha City police department and will be notifying NRC Region 1. * * * UPDATE ON 11/03/03 @ 0957 BY DOD PHILLIPS TO GOULD * * * Missing Troxler gauge was found along some railroad tracks near where it was stolen, undamaged and intact. It was taken to a volunteer fire department in Boone, Cty. WV. The licensee was notified by the fire department on 11/03/03 and they have sent someone to get it. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-10-31
40284 | 0 | PENNSYLVANIA DOT |  |  |  |  | 2003-10-30 11:00 | 2003-10-30 11:40 | 2003-10-30 | POTENTIAL DAMAGE TO TROXLER DENSITY GAUGE AT A CONSTRUCTION SITE At approximately 1100 EST on 10/30/03, the Penn DOT representative reported that a Troxler Density gauge at a construction site located at Route 201 in Connellsville (Fayette county), was run over. The extent of damage is unknown at this time although the case was reported as cracked. The contractor who possesses the device, TRIAD out of Morgantown, WV, has dispatched a technician to the site to assess the damage. The recovery will be overseen by a Penn DOT construction inspector on the scene. Penn DOT will inform the U.S. DOT (National Response Center) and their Pennsylvania Emergency Management Agency (PEMA). * * * * UPDATE FROM R. SIMAR TO M. RIPLEY 1345 ET 10/30/03 * * * * The RSO for Triad Engineering, owner of the gauge, reported that he and a representative from the County HAZMAT Team have performed radiation surveys and have determined that the gauge is not leaking. The RSO stated that a representative from the State Department of Environmental Protection (DEP) will also be arriving to perform a survey. Following this survey the RSO will package the gauge and transport it to Triad's facility. Notified R1DO (D. Silk) and NMSS EO (L. Psyk). * * * * UPDATE FROM R. SIMAR TO M. RIPLEY 1519 ET 10/30/03 * * * * The RSO for Triad Engineering reported that the State DEP has completed their radiation survey and that the gauge has been packaged for transport to Triad's facility. Notified R1DO (D. Silk) and NMSS EO (L. Psyk). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PA | OTH | GEN |  |  |  |  | 0 | 2003-10-30
40283 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-10-29 | 2003-10-29 10:05 | 2003-10-29 | 10 CFR 21 NOTIFICATION FOR GE MAGNE-BLAST BREAKER TUBE AND PISTON ASSEMBLIES "This notice is being sent within the two day period to inform you of a safety concern related to tube and piston assemblies for GE Magne-Blast breakers (model AM-4.16-350-2h medium voltage circuit breaker). "The concern is specific to tube and piston assemblies supplied under part number Q0213X0343R094. All five assemblies supplied to AmerenUE contain a dimensional design error which would cause the assembly to interfere and bind with the circuit breaker movable contact assembly, which would render the breaker inoperative." "All basic components with the defect at Callaway were returned to GENE . . .." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 21.21 |  |  |  | 0 | 2003-10-29
40282 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-10-28 20:30 | 2003-10-28 21:30 | 2003-10-28 | SAFEGUARDS REPORT AT VC SUMMER PLANT The licensee discovered vulnerability in a safeguard system that could allow access to a controlled area for which compensatory measures have not been employed. The licensee notified the NRC Resident Inspector. Contact the Headquarters Operations Officer (HOO) for additional details. *****RETRACTED ON 10/29/03 AT 1445 FROM McKINNEY TO LAURA****** Licensee review determined this event was not reportable under 10 CFR Part 73 but is considered a 24 hour safeguards loggable event. Contact the HOO for additional details. Notified TAS (L. English) and R2 IAT (A. Boland). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-28
40281 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-10-28 02:00 | 2003-10-28 06:30 | 2003-10-28 | THIS REPORT IS BEING MADE IN ACCORDANCE WITH 10CFR50.72, SECTIONS 50.72(b)(2)(iv)(B) AND 50.72(b)(3)(iv)(A) "At 0130, a fire was reported in the 345 KV switchyard. The fire was on a 345 KV wooden cross-arm on the plant's output line from the main power transformer to the 345KV switch yard. "At 0147, the operating crew entered Procedure 2.1.5, Emergency Shutdown from Power. Reactor power was lowered to [approximately] 75% with Reactor Recirculation. At 0200 a manual SCRAM was initiated. All control rods inserted and Containment Group Isolations 2, 3 and 6 initiated as expected. Reactor vessel level lowered to [about] - 25 inches wide range indication. Feed water recovered reactor water level, which swelled and tripped the running reactor feed pump. During restoration of the feed pump, level lowered to [about] 13 inches narrow range. A manual SCRAM was initiated in anticipation of a low level SCRAM. Level was recovered to 15 to 40 inches. The actual low level SCRAM signal and Group Isolation set points were not reached. "The plant is currently stable and a cooldown has been initiated. The Start-up and Emergency Transformers remained operable throughout the event. "No. 2 Diesel Generator remains out of service per the pre-planned maintenance." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 75 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-10-28
40280 | 0 | CENTRAL INDUSTRIAL SERVICES |  |  |  |  | 2003-10-27 15:00 | 2003-10-27 16:53 | 2003-10-27 | CPM MOISTURE DENSITY GAUGE DAMAGED ON CONSTRUCTION SITE A CPM brand moisture density gauge Serial # MD91005338 with a 50 millicurie Am-241 and 10 millicurie Cs-137 source was damaged when accidentally run over by construction equipment. The gauge was being used at a gas station construction site located at the end of Highway 26 known as the Carolina Construction Site. Both sources were reported to be intact and wipes taken on both sources were within limits with no detectable activity. The damaged gauge has been placed in its original shipping case and meets the normal transportation index. The licensee plans to transport the damaged gauge from the construction site to the Central Industrial Services office located in Barceloneta, PR. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 1 | PR | OTH | GEN |  |  |  |  | 0 | 2003-10-27
40279 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-10-18 | 2003-10-27 11:59 | 2003-10-27 | TEXAS AGREEMENT STATE REPORT ON LOST/FOUND RADIOGRAPHY CAMERA "Radiographic exposure device (Camera) was left unsecure on the tailgate of a company pickup truck before departing Licensee's local site enroute to the work site at: Huntsman Polymers, 2400 South Grandview Avenue, Odessa, Texas 79766. The Radiographer Trainer, (deleted), and his Trainee enter into conversation with another company employee and failed to block and brace the device or to secure the device to their truck. They drove out of the shop area and onto the street in front of the office. Approximately 100 yards from the office, the device fell off the tailgate and onto the service road. Approximately 10 minutes later, an NDT customer enroute to the Licensee's facility came by and noticed the camera in the road. He recovered the device and transported it to the Licensee's Odessa office. The crew was notified by cell phone and returned to the shop. The camera is an Industrial Nuclear Company, Model IR-100 exposure device, Serial No. 4318, containing 80 curies of iridium 192. The camera was surveyed for external damage and radiation at the shop. No external damage was noted and the results of the radiation survey revealed radiation levels that were the same as when the device had initially been surveyed that day. The exposure device was taken to a safe location, attached to associated equipment and operated to determine if the device had suffered internal damage. No damage was noted as the device operated perfectly. The device was leak tested. Results of this test have not been returned to the company as of October 27, 2003. As corrective action both the Radiographer Trainer and the Trainee have received a written warning under the Licensee's disciplinary policy. Both individuals will be required to participate in several radiation safety programs and be re-tested. The Trainee will be require to attend another 40-hour radiation safety class in December 2003. The Licensee is being cited for: failure to physically secure radioactive material; and failure to make an immediate (24-hour) notice to this Agency. In addition, the Radiographer Trainer will also be cited for failure to secure the device. Escalated Enforcement actions have been recommended which will include assessment of an Administrative penalty for the Licensee." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-30
40278 | 0 | WATERFORD | 3 |  |  | [3] CE | 2003-10-26 19:00 | 2003-10-27 00:21 | 2003-10-27 | INDICATION OF LEAKAGE "Inspection of the pressurizer bottom nozzles in accordance with the Alloy 600 Program during Refuel 12 identified a wet stain on heater sleeve C1, and a nozzle with a white substance extruding from a portion of the penetration on heater sleeve C3. The substance could not be verified at the time, and further investigation is required to determine if the substance is boron on heater sleeve C3. This condition constitutes a degradation of the RCS Pressure Boundary and is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(A)." The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-27
40277 | 0 | WATERFORD | 3 |  |  | [3] CE | 2003-10-24 23:00 | 2003-10-25 07:53 | 2003-10-25 | DEGRADATION OF THE REACTOR COOLANT SYSTEM (RCS) PRESSURE BOUNDARY "During inspection of the hot leg nozzles on RCP loop #2 in accordance with the Alloy 600 Program Plan during Refuel 12, evidence of leakage was identified on nozzle RC-IPT-0106B. This constitutes degradation of the RCS pressure boundary. Corrective action is being evaluated." RC-IPT-0106B is a pressure transmitter that taps off of reactor coolant system hot leg (loop) # 2 . The location of the Pressure transmitter is found in Waterford Unit 3, FSAR Chapter 5.1, Flow Diagram Reactor Coolant System, Figure 5.1-3. The license said that the picture indicates a small amount of boric acid crystals in the area of the leakage. Licensee did not know if the leakage is from a weld, pin hole leak, etc. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-25
40276 | -1 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2003-10-24 17:55 | 2003-10-24 19:34 | 2003-10-28 | DEGRADED SAFEGUARDS ACCESS Discovered vulnerability in a safeguard system that could allow access to a controlled access area for which compensatory measures were secured prematurely. The licensee notified the NRC Resident Inspector, the CT State Police and local law enforcement. Contact the Headquarters Operations Officer for additional details. The NRC Resident Inspector was notified of this event by the licensee. *****RETRACTED ON 10/28/03 AT 1315 FROM OCONNOR TO LAURA***** "Subsequent investigation has determined that the event was properly compensated within 10 minutes of discovery, and therefore it is not a reportable event but does require a security log entry per the guidance in GL 91-03." Notified TAS (L. English) and R1DO (D. Silk). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 1 | CT | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-24
40275 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-10-23 07:30 | 2003-10-24 17:19 | 2003-10-24 | AGREEMENT STATE NOTIFICATION REGARDING STOLEN GAUGE A Troxler gauge, Model 3241C, serial # 2547 with a 100 millicurie Am-241/Be source serial # 558906 was stolen from the back of gauge operator's pickup truck. The truck was parked at the gauge operator's residence overnight. The lock, chains, and broken handles from the gauge case remained on the back of the truck. Only the gauge and case were taken. TX Bureau of Radiation Control, Local police, states surrounding TX, and Mexico have been notified. Texas Incident # I-8067. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-29
40274 | 0 | U.S. GEOLOGICAL SURVEY |  |  |  |  | 2003-10-01 | 2003-10-24 12:32 | 2003-10-24 | RADIOACTIVE SOURCE DISCOVERED IN SURPLUS VEHICLE On 10/01/03, the U.S. Geological Survey (USGS) office in Oklahoma City, OK obtained a van from government surplus. When they received the vehicle, they discovered a Shimadzu series GC-14A gas chromatograph in the back of the van. The chromatograph contains a 10 milliCurie nickel-63 source. USGS contacted the van's previous owner but was not able to return the chromatograph. The chromatograph is presently secured in locked storage. USGS will leak test the source and return the chromatograph to the manufacturer for proper disposal. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | OK | MAT | [5 empty] | 0 | 2003-10-24
40273 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-10-23 17:43 | 2003-10-23 21:39 | 2003-10-23 | DEGRADED SAFEGUARDS CONDITION Discovered vulnerability in a safeguard system that could allow unauthorized or undetected access to safeguards material. Compensatory measures have been employed. The licensee notified the NRC Resident Inspector. Contact Headquarters Operations Officer for additional details. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-23
40272 | -1 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-10-23 16:40 | 2003-10-23 21:30 | 2003-12-12 | NONEMERGENCY NOTIFICATION DUE TO FAILURE TO MAINTAIN CONTROL STRUCTURE HABITABILITY ENVELOPE "During routine monitoring, Control Room personnel noted control structure pressure differential was below the 1/8" [inches of water pressure] required to maintain the Control Structure Habitability Envelope. A walkdown of the Control Structure and initial investigation has revealed no obvious problems that would cause the low positive pressure condition. Due to the inability of the Control Structure HVAC to maintain a positive pressure, both trains of Control Room Emergency Outside Air Supply system were declared inoperable. This is considered a Loss of Safety Function in accordance with 10 CFR 50.72(b)(3)(v)(D)." The licensee has notified the NRC Resident Inspector. * * * * RETRACTION FROM A. FITCH TO M. RIPLEY 1343 ET 12/12/03 * * * * "At the time of the original 8-hour ENS notification was made, both trains of the Control Room Emergency Outside Air Supply (CREOAS) system were declared inoperable due to the failure of the Control Structure HVAC system to maintain the control structure habitability envelope at a pressure greater than + 1/8" w.g. [water gauge] with respect to outside atmosphere. "Subsequent to this event, an evaluation was performed which determined that the requirement to maintain the control structure habitability envelope at a pressure greater than + 1/8" w.g. is only applicable during emergency operating conditions. Under emergency conditions, the CREOAS system, in conjunction with the Control Structure HVAC system, is required to maintain control structure pressure greater than + 1/8" w.g. in accordance with Technical Specification 3.7.3. However, during normal plant operation, the design function of the Control Structure HVAC system is to maintain the habitability envelope at a positive pressure above atmospheric. No specific value is required. Differential pressure readings for the control structure indicated that pressure was maintained above atmospheric at the time of this event. "On October 24, 2003, surveillance testing successfully demonstrated that the Control Structure HVAC and CREOAS systems were capable of maintaining the control structure habitability envelope at a pressure greater than + 1/8" w.g. As such, there was no loss of safety function." The licensee has notified the NRC Resident Inspector. Notified R1DO (A. Della Greca) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-10-23
40271 | 0 | U.S. ARMY TACOM |  |  |  |  | 2003-10-09 12:00 | 2003-10-23 12:45 | 2003-10-23 | UNPLANNED CONTAMINATION DUE TO DAMAGED M1A1 COLLIMATOR The following information was received from the licensee via facsimile: "Army personnel discovered a broken M1A1 collimator at the MATES [Maneuver Area Training Equipment Site] VAARNG [Virginia Army National Guard], Ft. Pickett, Blackstone, VA on 9 October 2003. The item was leak tested, double bagged and placed into a foot locker in an outdoor location. [Tritium] contamination levels on the collimator [were] 2.68 [micro Curies] and in the footlocker where the collimator sat, .087 [micro Curies]. The state RSO [Radiation Safety Officer] will retrieve this item and place it in a low level radioactive waste storage site for future disposal." The State of Virginia has been notified of the incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2003-10-23
40270 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-10-22 16:23 | 2003-10-22 18:58 | 2003-10-22 | OFFSITE NOTIFICATION CONCERNING ONSITE FATALITY "Today at 1623, a report was received in the Control Room of a medical emergency involving a plant employee at the power plant. Onsite personnel responded and paramedics/ambulance arrived onsite. "We have been informed that the individual died from an apparent heart attack. "The NRC Resident Inspector has been notified. This report is being made pursuant to 10 CPR 50.72(b)(2)(xi)." The local news media has broadcasted the event and the licensee does not intend to issue a press release at this time. The employee was not working in a radioactive contaminated area at the time of the event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-10-22
40269 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-10-22 14:30 | 2003-10-22 17:07 | 2003-10-22 | AGREEMENT STATE REPORT INVOLVING A LOST SOURCE "Event location: RLM Building Vault Room 2.306, J.J. Pickel Research Campus, The University of Texas at Austin, Austin, TX. "Event description: While performing an exhaustive inventory of sources for possible recovery in the DOE Source Recovery Program it was determined by visual survey a 5 millicurie, Am-241, sealed-source was missing. The source was probably procured in the 1960's and has been indicated as in storage since the late 1980's. The last leak test that was currently available was dated 04/19/88. The source is suspected of being manufactured by the Monsanto Company and is listed as Serial No. M-376. No information on Model is available. The source is indicated as being sealed in 1-inch pipe. The RSO reports that the source has evidently been confused for years with another source that is indicated on storage records as CNS-1. However, he feels relatively sure that it is not the same source. Records indicated that the source was transferred to storage 11/27/84 and may have last been seen on 04/19/88. A visual and instrument survey of the last known storage facility did not locate the source. The RSO believes that the source may have been disposed of with Radium sources but there is no indication on shipment manifests. The previous RSO has been contacted and reportedly cannot recall details about the specific source. "Transport vehicle description: Not applicable "Media attention: None "Texas Incident No.: I-8066" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-27
40268 | 0 | VOGTLE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-10-22 01:03 | 2003-10-22 02:56 | 2003-10-22 | HIGH PRESSURE HOSE CONNECTION FAILED RESULTING IN A TRAIN "A" MANUAL STEAM LINE ISOLATION "Manually initiated a steam line isolation signal upon report of a failed connection on a high pressure hose being used to vent a main steam isolation valve bonnet cavity (to open pressure locked valves). The manual isolation resulted in closure of the four open main steam isolation valves (Train "A"). The isolation was conducted as a preventative measure for personnel protection (three people were in the South Main Steam Valve Room when the fitting failed). No personnel were injured. Plant conditions remained stable." The NRC Resident Inspector was notified of this event by the licensee. | 2 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Startup; FMode1: Startup | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-10-22
40267 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-10-21 08:10 | 2003-10-21 12:22 | 2003-10-21 | AGREEMENT STATE REPORT INVOLVING A STOLEN RADIOGRAPHY CAMERA "Texas Incident No.: I-8065 "Event date and time: 10/21/03, discovered approx. 8:10 cst "Event location: Humble, TX storage shed "Event type: Stolen radiography camera "Notifications: The licensee notified the local police, BRC, and other radiography companies in the area. "Event description: SPEC Model 150 exposure device, sn #0336, 32 Ci [Curies], Ir-192 source, model G-20, sn #KF1204 "The licensee arrived at work this morning, found the security gate wide open, the lock cut on the storage shed, the lock cut on the vault and the camera missing. The only thing taken was the camera, all other equipment was still in place and the darkroom was still locked. The licensee had only one camera. The camera was used on a job yesterday and secured after use. "There are about 60 other storage sheds located within the fence. The only one broken into was the licensee's storage shed. Other radiography companies in the area were contacted by the licensee, also the local police were notified. "The incident has not received any media attention. The Agency [BRC] is investigating the incident. "Transport vehicle description: None reported "Media attention: None reported." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-24
40266 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-09-27 01:18 | 2003-10-21 12:14 | 2003-10-21 | INVALID HIGH PRESSURE CORE SPRAY (HPCS) ACTUATION DURING SURVEILLANCE TESTING "This report is being made under 10CFR50.73 (a) (2) (iv) (A). "On September 27, 2003, at 0118 hours Central Time, while operating at 100 percent power, Grand Gulf Nuclear Station experienced an invalid actuation of the High Pressure Core Spray (HPCS) System. The invalid signal was the result of an error made while performing a continuity check during a quarterly surveillance. "The invalid HPCS initiation caused the following systems to actuate: HPCS Pump, Division III Diesel Generator (DG) and Standby Service Water (SSW) 'C' (as designed to support DG operation). "Each train actuation was complete, HPCS started and functioned as designed and all support systems functioned properly. "There was an unexpected HPCS pump suction valve transfer to Suppression Pool. The most probable cause of this valve transfer was minor oscillation in Suppression Pool level." The licensee informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-10-21
40265 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-10-17 10:00 | 2003-10-21 10:27 | 2003-10-22 | LOSS OF CURRENT KNOWLEDGE OF LOCATION OF FUEL ROD Westinghouse provided the following information via facsimile pending resolution as to whether material has been lost: "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched < 5.0 wt.% U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107. "Reason for Notification: The Westinghouse Columbia Site Fundamental Nuclear Material Control Plan requires NRC notification of unresolved indications of missing uranium. Current knowledge of the location of Fuel Rod Id #18768319, has been lost. The fuel rod in question contains 85 grams U-235. "Description of Event: Columbia Site Rod Manufacturing employees could not locate fuel rod ID # 18768319 when verifying locations of items that showed up on a listing of items that had not moved through any process stages on the item control tracking system within the previous 7 days of when the report was generated. "The last transaction recorded for the item was on 8:31 am on October 2, 2003 indicating that the fuel rod was seal welded in the Chemical area after having been loaded with fuel pellets. No additional transactions were recorded for the fuel rod after this time. The next step in the process would have been an over check of the weld by the production line operator who would record the status of the weld via a transaction in the tracking system. The operator would apply a defect code to the rod in the system if a problem were noted with the weld. If the weld passed the overcheck inspection, it would have been transferred to the mechanical manufacturing area of the facility and be weighed and undergo a series of quality assurance inspections. No evidence was found to indicate that the fuel rod was transferred out of the chemical area of the facility. It is believed at this time that the rod most likely was scrapped [fuel removed and reused] and the necessary transactions were inadvertently not performed. "The manager of EH&S and the safeguards co-ordinator were notified of the on-going situation at approximately 10:00 am on October 17, 2003 and the investigation and search activities were intensified and are on-going. "Summary of Investigation/Search Activity - Rod area manufacturing employees searched for the fuel rod in the rod scrap areas of the facility and examined every fuel rod in the area. - Fuel rods in the storage areas of the facility were examined. - Containers of Low Level Radioactive Waste that may contain traceable portions of the fuel rod have been searched and continue to be searched. - Areas previously checked were re-checked and those areas not checked are in the process of being examined." * * * UPDATE AT 1009 EDT ON 10/22/03 FROM R. LIKES TO E. THOMAS * * * "Current knowledge of the location of Fuel Rod ID #18768319 was re-established on October 21, 2003 at approximately 19:30 hours, when a fuel rod manufacturing employee located the item. The fuel rod was found under a fuel rod handling conveyer in a position that was not readily visible to individuals performing search activities. The cause of how the fuel rod came to be in the location it was found is currently being investigated. "Because the fuel rod remained in controlled areas of the facility, this event is not considered safety significant and health and safety has not been compromised." Notified R2DO (J. Munday), NMSS EO (D. Broaddus), DIRO (D. Weaver), TAS (M. Kormann), DHS (R. Dasilva) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-10-23
40264 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2003-10-20 | 2003-10-21 08:20 | 2003-10-21 | AGREEMENT STATE REPORT - MISSING INTRAVASCULAR BRACHYTHERAPY SEEDS "Noveste Beta-Cath System [Model A1767 30mm S/N 86853] was used in a procedure on September 18, 2003. It has not been seen since. This office was notified October 20. This model contains 12 Sr-90 seeds, total activity up to 60 mCi [milliCuries]. Florida is investigating." Florida Incident # FL03-192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2003-10-24
40263 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-10-21 01:00 | 2003-10-21 05:20 | 2003-10-21 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS "Due to failure of an instrument power inverter (NN11) which supplies vital 120Vac bus NN01, Callaway Plant entered L.C.O. 3.8.7, Electrical Power Systems, Inverters - Operating, Condition A at 0721 on October 20, 2003. The inverter supplying the bus is required to meet the LCO. Since the initiation of the inverter failure, the vital instrument bus has been energized from alternate power supply transformers in accordance with plant design and procedures. It is not an acceptable alternative to meet the LCO OPERABILITY requirement. "Details of the impact on the plant due to this failure are detailed in Corrective Actions Program Report (C.A.R.) 200307636. In summary, the bus voltage was lost momentarily, then restored by operation of the inverter static transfer switch. The failure and subsequent restoration of power to AC Vital Bus caused some control systems responses that were corrected by the control room staff. After the event was stabilized, power remained at 100%. "The LCO Action is to restore the inverter to OPERABLE status within twenty four (24) hours, otherwise be in MODE 3 in 6 hours AND be in Mode 5 in thirty six (36) hours. The twenty four hour period ends at 0721 October 21, 2003. In advance of the action time, a controlled plant shutdown to Mode Three (3) was commenced at 0100 on October 21, 2003 at a rate of ten (10) percent per hour. At the time of this report, maintenance efforts have determined that the problem is internal to the inverter Static Transfer Switch, therefore the reduction of power will continue." No safety system actuations resulted from the control power transfer. The licensee has notified the NRC Resident Inspector. | 70 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-10-21
40262 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-10-20 15:26 | 2003-10-20 18:39 | 2003-10-20 | OFFSITE NOTIFICATION TO NEBRASKA DEPARTMENT OF ENVIRONMENTAL QUALITY "At 1526 on 10/20/2003 the Nebraska Department of Environmental Quality was contacted due to exceeding oil and grease release rates to the Missouri River from the Floor Drain System at the Headwall discharge point. A routine sample taken on 10/16/2003 of the Floor Drain System Headwall discharge point indicated 19.2mg/liter, this is above the maximum daily limit of 10 mg/liter. A follow up sample taken on 10/20/2003 indicated 18.3 mg/liter. Investigation of the source is ongoing, and the discharge lines have been flushed. The licensee believes this is a deminimus release of little or no significance. "NRC SRI has been informed." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-10-20
40261 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-10-20 07:00 | 2003-10-20 13:21 | 2003-10-20 | RCS THROUGH-WALL LEAKAGE FOUND ON SEAL INJECTION PIPING "On October 19, 2003, during performance of surveillance test procedure, STP 250.001B, Boric Acid Inspection Program, boron was observed around the seal injection piping and on the pump case housing of reactor coolant pump (RCP) 'C.' Inspection personnel contacted the Control Room and Outage Management at 1350 hours. Evaluation of the condition was initiated and a dye penetrant examination (PT) was scheduled for the morning of October 20. Evaluation of the PT results determined at 0700 hours on October 20 that the seal injection piping at the RCP pump case housing had through-wall leakage. This condition is being reported in accordance with 10CFR50.72(b)(3)(ii)(A)(2)." The licensee performed a similar inspection in April 2002 and found no indication of leakage at that time. Inspections of RCPs 'A' and 'B' have been completed during this outage with no indication of leakage observed. The licensee has corrective actions under review which will include additional UT inspections. The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-20
40260 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-10-06 08:30 | 2003-10-20 10:33 | 2003-10-20 | CONCURRENT GOVERNMENT NOTIFICATION INVOLVING SMALL OIL SPILL AT BWXT BWXT notified the Virginia Department of Environmental Quality of the onsite release of approximately 20 gallons of Macron Cutting Oil at the chemical storage tank farm. A larger amount of oil (approximately 1,800 gallons) was retained within a lined containment berm. The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 1 | 2003-10-20
40259 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-10-18 17:20 | 2003-10-19 01:13 | 2003-10-19 | LOSS OF EMERGENCY ASSESSMENT CAPABILITY The Wolf Creek Nuclear Plant Information System (NPIS) became unavailable for unknown reasons. Loss of the NPIS affects the Safety Parameter Display System (SPDS). The SPDS forms a significant portion of the Wolf Creek emergency assessment capability. There is no other loss of emergency assessment capability concurrent with this continuing loss of the SPDS. Plant personnel have entered applicable procedures and are taking local readings of equipment normally monitored by the NPIS. The licensee has notified the NRC Resident Inspector. * * * * UPDATE FROM DAVE DEES TO MIKE RIPLEY 0842 ET 10/19/03 * * * * "The SPDS was restored to service at 0621 CDT 10/19/03." Notified R4DO (G. Sanborn) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-10-19
40258 | 0 | DIABLO CANYON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-10-18 00:52 | 2003-10-18 04:04 | 2003-10-18 | EARTHQUAKE FELT ON SITE. ENTERED EMERGENCY ACTION LEVEL (EAL) 18 "Earthquake felt on plant site measured at 0.02g. Both Units remain at 100%" State and Local County notified by the licensee. Unusual Event declared per EAL 18, (greater than 0.01g) . Two jolts several minutes apart were felt in the Control Room. The electrical grid is stable, all Emergency Core Cooling Systems and all Emergency Diesel Generators are fully operable if needed. Licensee will perform walkdowns of the plant to check for any damage. Turbine supervisor system indicated high main turbine bearing vibration on both main turbines (cleared right away) and one of the Unit 1 Accumulator levels alarmed (also cleared right away). Following information from Earthquake Center located in Colorado: Two earthquakes both magnitude 3.4, located 10 miles Southwest of San Luis Obispo. First earthquake occurred at 0027 PDT and the other earthquake occurred at 0039 PDT. The NRC Resident Inspector will be notified. **** Update at 0635EDT on October 18 by Chitwood taken by MacKinnon **** EAL 18 exited and Unusual Event Classification terminated at 0330 PDT. Walkdown of plant completed with no damage to plant observed. R4D0 (G. Sanborn), HQPAO (Gagner), FEMA (Austin), DHS (V. Cates), DIRO (S. Frant), & (G. Holahan) notified. NRC Resident Inspector informed by licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 4 | CA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-10-18
40257 | 0 | NUCLEAR FUEL SERVICES INC. |  |  |  | URANIUM FUEL FABRICATION | 2003-10-17 16:00 | 2003-10-17 21:24 | 2003-10-17 | 24 HOUR BULLETIN 91-01 REPORT FROM NUCLEAR FUEL SERVICES IN ERWIN, TN "Provide a description of the event: On 10/17/2003; it was suspected that NFS storage area H/X limits were potentially exceeded for materials received from an off-site facility. A subsequent review of stored materials identified that the H/X values for two (2) containers exceeded the H/X limits for a storage area. "Sequence of events leading to the event: On 10/17/2003 and as a result of communications with personnel from an off-site facility, NFS determined that possible H/X issues existed with materials received from the off-site facility. The communications with the off-site facility involved details regarding the location of hydrogenous materials (e.g., plastic), with respect to the fissile material, when performing the H/X calculation. Based on these communications, NFS determined that the H/X values reported from the off-site facility might not satisfy NFS storage requirements. A subsequent review of stored materials indicated that the H/X values for two (2) containers exceeded NFS storage limits. "Remaining activities of personnel relied on to prevent potential accidents: The current storage of these materials does not pose a threat of an accident. Prior to receipt of materials from the off-site facility, NFS will confirm that the H/X values satisfy NFS storage requirements. "Safety significance: The safety significance associated with the handling and storage of the containers (received from off-site) is minor. "Brief scenario(s) of how criticality could occur: During storage of material, exceeding the H/X limits could only result in a criticality if the mass of U-235 was also exceeded concurrently in a significant number of containers. "What is the control(s) or control system(s) and the failure(s) or deficiencies? The control, control system, and failures/deficiencies are currently under investigation. "What are the corrective actions: The event is currently under investigation. Prior to receipt of materials from the off-site facility, NFS will confirm that the H/X values satisfy NFS storage requirements." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | TN | FUE | [5 empty] | 1 | 2003-10-17
40256 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2003-10-17 09:00 | 2003-10-17 11:54 | 2003-10-17 | STEAM AND FEEDWATER RUPTURE CONTROL SYSTEM UNANALYZED CONDITION AT DAVIS BESSE "System Affected : Steam and Feedwater Rupture Control System (SFRCS) "Actuation / Initiator Affected: Main Steam Line Rupture on Steam Generator "Effect of event on plant in current Mode - None "Actions Taken or planned: Declared SFRCS Actuation Channels 1 and 2 inoperable. Will track as a Mode 3 restraint against T.S. 3.3.2.2 (SFRCS Instrumentation). Will resolve, correct and retest prior to entry into Mode 3. "Discovered SFRCS Logic Channel 1 block upon restoration and repowering after maintenance activities on 10/16/03. After discussions with Engineering Department representatives it has been determined that a design issue exists with the SFRCS system where it would be possible that SFRCS Channels 1 and 2 low pressure trips could be blocked during a scenario where a Main Steam Line Rupture would be followed by a loss of off-site power. This would result in the potential that the OTSG [once through steam generators] with the main steam line rupture would be fed by the AFW system. This requires an 8 hour notification to the NRC per 10CFR50.72(b)(3)(ii)(B)." The licensee notified the NRC resident inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-10-17
40255 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-10-16 15:30 | 2003-10-16 17:53 | 2003-10-16 | 24 HOUR BULLETIN 91-01 NOTIFICATION FROM WESTINGHOUSE COLUMBIA FUEL FACILITY "Double Contingency Protection: Double contingency protection for the ADU Bulk Blending System is assured by (1) preventing moderator from becoming available to a bulk container, and (2) preventing moderator from entering a bulk container. The first contingency did not occur because the moderator was never available to a bulk container. Moderator is prevented from entering a bulk container by preventing high moisture polypaks from being dumped into the bulk container. The polypaks are processed through a scan and dump interlock, which prevents unacceptable polypaks from being dumped. The software malfunction left less than previously documented double contingency protection for the system. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5a), this event satisfies the criteria for a 24-hour notification. "As Found Condition: See Reason for Notification above. "Summary of Activity: Immediately after all packs were dumped into the bulk container to complete the blend of material, Operations noticed that the packs had not been denoted as "consumed" by the data base, and notified the computer system administrator and Nuclear Criticality Safety. The computer system administrator stopped all dumping operations. The computer system administrator immediately checked all packs that had been dumped into the blend. All moisture values were acceptable. All operations that use the same PLC interface program for criticality controls were stopped. "Conclusions: Less than previously documented double contingency protection remained. All moisture values for the material involved were acceptable, and the total amount of moderator in the blend was very low, far less than criticality limits. At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. A causal analysis will be performed." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-10-16
40254 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-10-16 12:30 | 2003-10-16 13:47 | 2003-10-16 | UNUSUAL EVENT AT COOPER DUE TO SMALL FIRE AT A TURBINE BEARING The licensee declared an Unusual Event at 12:30 CDT pertaining to a small fire, located at the high pressure turbine number 1 bearing, which was burning greater than 10 minutes. There were no injuries and the turbine continues to operate at full power while the fire brigade attempts to extinguish the fire. Subsequently, the licensee extinguished the fire; however, several minutes later, the fire restarted. The licensee decided to lower power to approximately 65% power to lower general area radiation levels for the fire brigade personnel. The fire was extinguished and reflashed a few times. The fire brigade used water, dry chemicals and foam when fighting the fire. The source of the fire at the bearing is under investigation by the licensee. *****UPDATE ON 10/16/03 AT 1700 FROM FISCHER TO LAURA***** The licensee reports that the fire is out and the investigation determined that the most likely source of the fire was oil pooled under the bearing pedestal. No current oil leakage was found. The licensee planned on contacting the turbine vendor prior to returning the plant to full power. The Unusual Event was terminated at 1541 CDT. Notified R4DO (G. Sanborn), DIRO (D. Weaver), NRR EO (T. Reis), DHS (J. Clardy) and FEMA (J. Dunker). | 65 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Power Operation | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-10-16
40253 | 0 | EXELON POWER LABORATORY |  |  |  |  | 2003-10-16 09:00 | 2003-10-16 10:03 | 2003-10-16 | CALIBRATOR SAFETY INTERLOCK FAILED TO FUNCTION DURING OPERATIONAL TEST The licensee RSO reported that the electrical interlock between the access door and the source position on a J. L. Shepherd Model 89-400 calibrator failed to function during the daily pre-operational test. With the door open, the interlock should have prevented raising the source, but did not. The source (400 Curie Cs-137) was lowered and the door re-closed without further incident. Radiation levels were normal and no personnel exposure occurred. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2003-10-16
40252 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-10-15 23:02 | 2003-10-16 00:28 | 2003-10-16 | PROMPT NOTIFICATION SYSTEM (PNS) SIRENS EXCEEDED ALLOWABLE OUT OF SERVICE TIME. More than 4 Prompt Notification System sirens were simultaneously out of service for greater than 12 hours. In accordance with site procedures, this is a major loss of notification capability. These sirens are out of service due to a loss of power caused by elevated wind conditions in the region. Oswego County is currently working to restore power to the sirens. State and Local counties were notified. The NRC Resident Inspector will be notified of this event by the licensee. *****UPDATE ON 10/16/03 AT 1524 FROM PAGE TO LAURA***** "On October 15, 2003, the James A. FitzPatrick nuclear power plant notified the NRC that more than 4 prompt notification system sirens were simultaneously out of service for greater than 12 hours due to loss of power caused by elevated wind conditions in the region (reference EN # 40252). On October 16, 2003 at approximately 0107, the county notified FitzPatrick that only 3 sirens remained out of service. As of October 16, 2003, at approximately 1200, only 2 of the sirens remain out of service. Efforts are continuing to restore electrical power to the remaining 2 sirens. As a result, the conditions under which the initial notification was made no longer exist (10CFR50.72(b)(3)(xiii) major loss of offsite response capability - due to loss of 4 or more sirens for greater than 12 hours). This informational notification is provided to update the NRC as to the current conditions." Notified R1DO (Brian MCDERMOTT) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-10-16
40251 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-10-15 23:02 | 2003-10-16 00:16 | 2003-10-16 | PROMPT NOTIFICATION SYSTEM (PNS) SIRENS EXCEEDED ALLOWABLE OUT OF SERVICE TIME. More than 4 Prompt Notification System sirens were simultaneously out of service for greater than 12 hours. In accordance with site procedures, this is a major loss of notification capability. These sirens are out of service due to a loss of power caused by elevated wind conditions in the region. Oswego County is currently working to restore power to the sirens. State and Local counties were notified. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-10-16
40250 | 0 | SALEM | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-10-15 16:03 | 2003-10-15 19:30 | 2003-10-15 | FEEDWATER REGULATING VALVE ISSUE FORCES INITIATION OF TECHNICAL SPECIFICATION SHUTDOWN "At 1603 Salem Unit 1 commenced a down power to comply with Technical Specifications. Tech. Spec. 3.0.3. was entered at 1505 when it was determined that the feed regulation valve for the 14 Steam generator (14BF19) was bound at approximately 71% open. This valve is required to close on a feedwater isolation signal. Currently the reactor is at 40% power and lowering with plans to stabilize at 25% prior to taking the unit off line (mode 3) by 2205 tonight. "Unit 1 has no other tech spec equipment out of service. Unit 1 is in two additional shutdown Technical Specifications, both are related to the control room ventilation system which is shared with Unit 2. Unit 2 is in a scheduled refueling outage and one of the Unit 2 emergency intake dampers is disabled (T.S. 3.7.6.1.a). This is a 7 day LCO that expires on 10/22/03. Additionally Unit 2's emergency filtration system is out of service for planned maintenance (T.S 3.7.6.1.a). This is a 30 day LCO that expires on 11/13/03. All other systems on Unit 1 are operating as expected for current plant conditions." The licensee notified the NRC Resident Inspector. | 40 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-10-15
40249 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-10-15 13:12 | 2003-10-15 14:07 | 2003-10-15 | UNSECORTED ACCESS GRANTED INAPPROPRIATELY Compensatory measures taken upon discovery. The NRC Resident Inspector was notified. Refer to the HOO for additional details | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-15
40248 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-10-15 10:24 | 2003-10-15 13:25 | 2003-10-15 | A MANUAL REACTOR TRIP FROM 1% POWER AS PER ABNORMAL OPERATING PROCEDURES OCCURRED The plant was in mode 2 (1% power) making preparations to place the unit on-line per procedures. At 0921, the plant had entered ER-SC.1, Adverse Weather Plan, due to sustained winds greater than 55 mph. At 1024, offsite power circuit "751" was lost due to offsite storm damage(tree down on powerline). The loss of circuit "751" led to the loss of the "B" reactor coolant pump on undervotltage. Procedure AP-RCS.2, loss of Reactor Coolant flow was entered. At 1026 a manual Reactor Trip was initiated as directed by procedures. All rods fully inserted, no ECCS injection or safety valves lifted and all ESF systems functioned as designed. Due to the partial loss of offsite power, the "B" emergency diesel auto started and loaded to supply safeguards equipment. The "A" and "B" aux feedwater pumps also auto started. Offsite power was restored to safeguards equipment being supplied power by the "B" emergency diesel within 15 minutes from the second offsite power line. The NRC Resident inspector was notified. | 0 | 0 | 0 | 1 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Startup; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-10-15
40247 | 0 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-10-14 23:55 | 2003-10-15 01:56 | 2003-10-15 | AUTOMATIC REACTOR TRIP DUE TO LOW "B" STEAM GENERATOR WATER LEVEL. "Automatic Trip due to low (21%) B Steam Generator Level (all rods fully inserted into the core). "While decreasing power for heater drain pump repairs, the B main feedwater regulating valve did not respond properly. Manual attempts to restore level were not effective. Steam generator level decreased to the low level trip setpoint. "Auxiliary feedwater systems automatically started due to low post trip steam generator levels. This includes the Steam Driven Auxiliary Feedwater Pump. The steam discharge of this pump is considered to a gaseous release due to trace amounts of tritium in the secondary system. These trace amounts are well below limits. The pump was shutdown after 16 minutes of operation, terminating the discharge. The Rad Waste & Effluents Section will assess the impact during the event response review. "Plant is currently stable in Mode 3 with steam generator levels restored to post shutdown values. The steam dumps and main unit condenser are available for heat removal. All normal and emergency busses are energized from offsite power." The NRC Resident Inspector was notified of the event by the licensee. | 0 | 0 | 0 | 0 | 39 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-10-15
40246 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-10-14 07:30 | 2003-10-14 13:07 | 2003-10-14 | 24-HOUR NRC 91-01 BULLETIN REPORT INVOLVING IMPROPER MASS CONTROL Improper Filling of Dry Combustible Trash Drum "Facility: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched less then or equal 5.0 wt.% U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107. Time and Date of Event: October 14, 2003 Reason for Notification: Dry combustible trash was placed into a single 55-gallon drum without proper mass control. Dry combustible trash drums are positioned on scales for filling. An operator removed a single drum from a scale and then filled the drum with dry combustible trash. The filling of drums on scales prevents exceeding the critical mass limit of [DELETED]. The scales actuate a visual alarm at 66 lbs.; and visual and audible alarm at 90 lbs. If the 66 lbs. limit is reached, operators are required to remove trash from a drum. If the 90 lbs. Limit is reached, operators are required to remove trash and write a Redbook. Double Contingency Protection: Double contingency protection for dry combustible trash is assured by preventing [DELETED] of UO2 from becoming available to a single combustible trash drum, and preventing the total weight of a drum from exceeding the [DELETED]. Criticality limit. The removal of the drum from the scale and subsequent filling left less than previously documented double contingency protection for the system. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5a), this event satisfies the criteria for a 24-hour notification. As Found Condition: During a routine checking of drums for spacing (i.e., U-235 gram counts), a second operator noticed that a dry combustible trash drum had a net weight of 95 tbs. The operator recognized that a drum weight of 95 lbs. Exceeded the scale limit of 90 lbs. and generated the required Redbook. The drum indicated an assay value of 5.285 grams of U-235. Summary of Activity: - When the second operator found the drum, it was placed on hold. Both process engineering and EH&S were notified. - The drum contents were examined and no improper material types were found in the drum. It was also determined that the material was not compacted. - The drum was weighed and assayed and found to match the values on the drum label. Conclusions: - Less than previously documented double contingency protection remained. - Less than a critical mass was involved. - At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. - The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. - A causal analysis will be performed." The licensee will inform the Region 2 Office. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-10-14
40245 | 0 | MILLSTONE |  | 2 |  | [1] GE-3,[2] CE,[3] W-4-LP | 2003-10-14 04:04 | 2003-10-14 05:12 | 2003-10-14 | UNUSUAL EVENT DECLARED - LOSS OF SHUTDOWN COOLING At 0404 EDT on 10/14/03, Millstone 2 lost shutdown cooling due to the loss of power to vital power bus VA10. Power and shutdown cooling were restored at 0414. Millstone declared an Unusual Event at 0423 due to a greater than 10 degree increase in reactor coolant system temperature. Reactor coolant system temperature increased from 101 degrees to 113 degrees. Power was lost to VA10 while attempting to swap power supplies from inverter 1 to inverter 5. Inverter 1 is now supplying power to VA10. The licensee notified the NRC Resident Inspector. * * * UPDATE FROM STRICKLAND TO GOTT ON 10/14/03 AT 0740 * * * Millstone 2 exited their Unusual Event at 0532, after completing the abnormal operating procedure and stabilizing plant conditions. Notified R1DO (Bellamy), NRR (Reis), DIRO (McGinty), DHS (Rick DaSilva), and FEMA (David Barden).. * * * UPDATE 10/14/03 @ 12:02 BY WILL CHESNUTT TO JEFF ROTTON * * * An update to event notification 40245 is being made to reflect that the loss of shutdown cooling is also considered reportable under 10CFR50.72(b)(3)(v). Additionally, further review of plant response following the loss of VA10, indicates that due to an equipment performance issue (failed relay) the containment isolation valves did not respond as expected and were manually closed per procedure. This issue will be investigated and addressed as needed in the LER. The NRC Resident Inspector will be notified Reg1 RDO(McDermott) was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED | POT RHR INOP |  |  | IMode2: Cold Shutdown; FMode2: Cold Shutdown | UNUSUAL EVENT | 1 | CT | POW |  | 50.72(a) (1) (i) | 50.72(b)(3)(v)(B) |  |  | 0 | 2003-10-14
40244 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2003-10-13 11:20 | 2003-10-13 19:30 | 2003-10-13 | OFFSITE NOTIFICATION TO OSHA AT THREE MILE ISLAND REGARDING A FATALITY "A contract delivery employee apparently suffered a heart attack while making a delivery at TMI. The contract employee was treated by the site EMTs and transported to the Hershey Medical Center by off site medical assistance. AmerGen was notified at approximately 1315 that the contract employee was declared dead at the Hershey Medical Center. AmerGen notified OSHA as required for a fatality at the facility. " The NRC resident was notified." | 96 | 0 | 0 | 96 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-10-13
40243 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2003-10-13 17:00 | 2003-10-13 17:53 | 2003-10-13 | INJURED CROCODILE FOUND ON PLANT ACCESS ROAD The control room was notified by Land Utilization at 1700 EDT that they had contacted the Florida Fish and Wildlife for information on where to take the injured crocodile found on the plant access road. The crocodile was taken to the Miami Zoo. The NRC Resident Inspector was notified along with the State | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-10-13
40242 | 0 | CATAWBA | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-10-13 08:00 | 2003-10-13 12:59 | 2003-10-13 | 1-HOUR SECURITY REPORT INVOLVING INADEQUATE SECURITY SEARCH A visual inspection of the contents of three (3) food containers brought into the protected area by a food vendor was not performed due to personnel error. Compensatory measures were taken upon discovery. The licensee will inform both state/local authorities and the NRC Resident Inspector. Contact the Headquarters Operations Center for additional details. * * * UPDATE 1500 EDT ON 10/13/03 FROM DON BRADLEY TO S. SANDIN * * * The licensee provided additional information to include the sizes of the three (3) containers and corrective actions taken. The licensee informed the NRC Resident Inspector. Notified R2IAT (Anne Boland). Contact the Headquarters Operations Center for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | SC | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-13
40241 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2003-10-10 15:30 | 2003-10-13 10:48 | 2003-10-13 | AGREEMENT STATE REPORT - LOST/STOLEN GAUGE "The South Carolina Department of Health and Environmental Control was notified on October 10, 2003, at 7:45 pm [EDT] by Coastal Engineering and Testing, Co. that a Troxler Model 3430 gauge, s/n 33695 was stolen from the back of a company pickup truck while at a temporary jobsite in Charleston, SC. The gauge contained an Am: Be [Americium: Beryllium] source with an activity of 44 mCi [millicuries] and a Cs-137 [Cesium-137] source with an activity of 9 mCi [millicuries]. The licensee has called the local police department to file a report. The licensee in its official report will provide further information to the Department." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | SC | OTH | AGR |  |  |  |  | 0 | 2003-10-16
40240 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-10-10 08:00 | 2003-10-13 10:16 | 2003-10-13 | AGREEMENT STATE REPORT - CONTAMINATION AT FORMER KELLY AIR FORCE BASE "A hangar formerly used by the U.S. Air Force was under re-construction for transformation to a corrosion control facility. The unlicensed facility had been contaminated by radium during use as a paint shop during 1922-1929, and as a paint removal facility during later years. Supposedly this facility has been deed recorded as a site of contamination with Ra-226 [Radium-226]. The facility is not Licensed by the State of Texas. At this time it is unclear if this facility was released for unrestricted use when turned over to the Greater Kelly Development Authority. This Agency can find no record of the site contamination. Contractors from the Boeing Corporation were working on the facility to be remodeled to a corrosion control facility. Digging around the foundation (slab) they hit a 2-inch galvanized pipe that was contaminated with radium-226. Background levels at the facility were measured at 10,000 counts per minute and after the incident at 10 times that level. An Agency inspector will be on site for soil sampling. It is estimated that 10-20 Boeing employees may have come in contact with the material. Urine analysis has been ordered by the contractor for personnel suspect of working in the contamination. Initial reports from both Greater Kelly Development Authority and the Boeing Corporation have been received - but are inconclusive." The Texas Commission on Environmental Quality, the EPA, and the U.S. Air Force have been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-16
40239 | 0 | NC DIV OF RADIATION PROTECTION |  |  |  |  | 2003-10-10 | 2003-10-10 12:30 | 2003-10-10 | AGREEMENT STATE REPORT INVOLVING DISCOVERY OF NUCLEAR GAUGE IN SCRAPYARD "This is to inform you that North Carolina Radiation Protection Section has discovered a fixed nuclear gauge that was scrapped and is now being held by a North Carolina scrap dealer from Gastonia, NC. "Radioactive Materials Branch Incident 03-13 has been open pending further investigation of a device, originally described as an X-Ray head, having been found in a returned scrap load sent to a South Carolina scrap steel processor and returned under a CRCPD exemption. "A Section representative performed a field inspection on October 9, 2003 on the undetermined item being held in secure isolation at the scrap-yard since its discovery in March 2003. "At present our investigation has determined that: "- Device is a Fixed Nuclear Gauge. K-Ray model 7107-6. This device is inactive per the SS&D registry sheet and is considered for both GL [General Licensing] and Specific Licensing. "- Contains isotope Cs-137 in the amount of 50 millicuries. Reference year from gauge label is March 1983. "- Highest general area (about 1[meter]) dose rate is approx 0.1 [millirem per] hr with 200 [millirem per] hr on contact. It is unknown whether the shutter is open or closed but dose rates when compared to SS&D [Sealed Source & Device] information for the general model indicate it may be open. "- Labeling has been painted over and also appears as if a deliberate attempt had been made to destroy the device identification labeling & serial number(s). "Corrective Actions So Far: "Surveys and leak tests have been performed. Analysis on wipes is pending but source does not appear to be leaking. "Device has been re-secured. Verbal direction has been given to the State Line Manager on its necessary security and continued isolation from the scrap yard workers and other members of the public. "Additional steps are being taken to determine if any significant exposures could have been received by anyone at State Line who spent time nearby or who may have handled the device since its return to them. "If/when significant additional information becomes available it will be passed along to you." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | NC | OTH | AGR |  |  |  |  | 0 | 2003-10-15
40238 | 0 | WISCONSON DEPT HEALTH & FAM SERVICE |  |  |  |  | 2003-10-09 | 2003-10-10 10:35 | 2003-10-13 | GENERAL LICENSED DEVICE PLACED IN PUBLIC DOMAIN The Wisconsin Department of Health and Family Services reported that on 10/9/03 it was discovered that a general licensed gauge used on the coal conveyor at the Wisconsin Public Services Corporation Pulliam coal-fired power plant in Green Bay, WI was removed without properly closing the shutter and left in a public area on 9/25/03. The gauge contains a 50 milliCuries Cs-137 source. The device was subsequently recovered and properly shuttered on 10/09/03. Wisconsin Public Services Corporation issued on 10/09/03. Fixed Gauge Manufacturer: Texas Nuclear Source S/N: B2920 The RSO [Radiation Safety Officer] took readings in the direction of the open shutter; at 8 feet (4 to 5 Mr/hr) and at 3 feet (10 Mr/hr). Wisconsin Department of Health and Family Services, Radiation Protection Section staff will perform an investigation the week of 10/13/03. * * * UPDATE 1706 EDT ON 10/13/03 FROM JASON HUNT (WISCONSIN ) TO S. SANDIN VIA EMAIL * * * The Wisconsin licensee notified the State of Wisconsin that there was an error in the original report related to gauge make, model, serial number and source strength. The new detailed information is as follows: ThermoMeasureTech Model # 5200, Ser. # B2011, Source Activity 20 mCi [milliCuries]. Notified R3DO (Madera) and NMSS (Holonich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | WI | OTH | AGR |  |  |  |  | 0 | 2003-10-15
40237 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-10-09 15:00 | 2003-10-09 18:08 | 2003-10-17 | AGREEMENT STATE REPORT INVOLVING MOISTURE DENSITY GAUGE VEHICLE ACCIDENT "At approximately 2:15 PM [MST] October 9, 2003 the Agency was informed by the Licensee that a truck carrying a moisture-density gauge had been involved in a single vehicle accident and the driver is dead. The reporting individual indicated that they were informed of the accident by the Department of Public Safety. The accident occurred on AZ Highway 260 between Bridgeport and Camp Verde. The moisture-density gauge is a Troxler Model 3440, SN 27494. The device contained 40 mCi Be:Am-241 and 8 mCi Cs-137 [mCi=millicuries]. The device remained in the transporting box inside a locked steel box in bed of pick up. The Licensee is trying to retrieve [it] from law enforcement for storage and leak test. [It is] Currently in an impound yard in Mayer, AZ. "Agency continues to receive information regarding this fatality. The Agency is unaware of any press coverage regarding radioactive materials. "The U.S. NRC is being notified of this event." AZ First Notice: 03-19 *****UPDATE ON 10/17/03 AT 13:30 FROM GODWIN TO LAURA***** "The leak test was negative. It appears the driver was not wearing his seat belt." Notified NMSS (D. Broaddus) and R4DO (G. SANBORN) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-10-14
40236 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-10-08 | 2003-10-09 14:32 | 2003-10-09 | AGREEMENT STATE REPORT INVOLVING POTENTIAL LEAKING SOURCE "This is notification of an event in Washington state as reported to the WA Department of Health, Division of Radiation Protection. "STATUS: "New (this is an preliminary notification due to the lack of required information at this point in time). "Licensee: Sacred Heart Medical Center "City and state: Spokane, Washington "License number: WN-M031-1 "Type of license: Medical "Date of event: 8 October 2003 "Location of Event: on campus (OR) "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) "The licensee was implanting a source train of I-125 seeds for a lung cancer treatment and during that implant decided the source train in use was longer than necessary. They decided to clip the unwanted part of the train but snipped a source rather than the space between the sources. "What is the notification or reporting criteria involved? Leaking source, possibly. If not, no notification is required, if so, then a possible overexposure to the patient (thyroid). "Activity and Isotope(s) involved: Iodine-125 therapy seed(s). "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) None, with the possible exception of the patient. "Lost, Stolen or Damaged? (mfg., model, serial number): This was an Iodine-125 seed, part of a source train of such seeds which was damaged when the licensee attempted to shorten the train but cut through a seed instead of the interstice desired. "Disposition/recovery: No loss of seeds. "Leak test? Licensee is performing one ASAP but as of this writing there are no results. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number): N/A "Release of activity? Unknown at this time, if the seed is not leaking, then 'no'. If the seed is in fact leaking then the potential exists for release of material inside the patient. "Activity and pharmaceutical compound intended: N/A, the proper nuclide and activity was delivered to the intended treatment site. "Misadministered activity and/or compound received: N/A, this was not a misadministration. Device (HDR, etc.) Mfg., Model; computer program: N/A, no device involved. Exposure (intended/actual); consequences: No unplanned exposure, unless the source turns out to be leaking. Was patient or responsible relative notified? Unknown at this time. "Was written report provided? Not yet, but it will be. "Was referring physician notified? Yes, referring MD notified by oncologist. "Consultant used? No." This is WA Event Report # WA-03-043. * * * UPDATE 1830 EDT ON 10/9/03 FROM ARDEN C. SCROGGS VIA EMAIL * * * "New (this is an updated notification). "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) "The licensee was implanting a source train of 31 [Iodine-125] seeds for a lung cancer treatment along the lining of the pleura and during that implant decided the source train in use was longer than necessary. They decided to clip the unwanted part of the train but snipped two source(s) rather than the space between the sources. "The licensee administered large quantities of SSKI within one hour of breaching the seeds. The current plan is to continue administration of SSKI in amounts of at least 0.5ml daily for at least the next two weeks. "What is the notification or reporting criteria involved? MISADMINISTRATION via leaking source. "Activity and Isotope(s) involved: Iodine-125 therapy seed(s). A total of two seeds with an activity of 0.729mCi each according to the licensee. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) None, with the possible exception of the patient. The primary handler has received thyroid bioassay with negative results. The licensee is expecting results of the pleural fluid sample taken from the patient soon, and will attempt thyroid bioassay of the patient at the 72-hour exposure interval. "Lost, Stolen or Damaged? (mfg., model, serial number): These are Iodine-125 seeds, part of a source train of such seeds which were damaged when the licensee attempted to shorten the train but cut through two seeds instead of the interstice desired. The manufacturer is MPI, the model is the 'Oncoseed' 'Rapid Strand'. The licensee will include an enlarged version of the product insert with their written report. "Disposition/recovery: No loss of seeds although remains of the two leaking sources are properly stored awaiting decay/disposal. "Leak test? Leak test results from the soak test (four hours in plain water) showed 'significant leakage' according to the licensee, and they are assuming a worst-case scenario basis of one entire seed leaking and one-half the second seed leaking. "Release of activity? Yes, it is assumed on a worst-case basis that the entire contents of one seed and fifty percent of the second seed has or will leak. "Misadministered activity and/or compound received: This was a misadministration by definition because the sources are determined to have leaked. "Exposure (intended/actual); consequences: Exposure is limited to the patient only. The licensee will attempt to quantify through both calculation and bioassay the extent of patient/thyroid exposure. Physicians involved expect little or no adverse effects at this point, assuming the SSKI works as expected. "Was patient or responsible relative notified? Yes. "Rev 1. 1530 hrs, 9 October 2003" Notified R4DO(Bill Johnson) and NMSS(Holonich). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-10-14
40235 | 0 | OHIO BUREAU OF RADIATION PROTECTION |  |  |  |  | 2003-10-09 | 2003-10-09 13:52 | 2003-10-09 | AGREEMENT STATE REPORT INVOLVING A STOLEN MOISTURE DENSITY GAUGE The Ohio Bureau of Radiation Protection was notified on 10/9/03 that a CPN Model MC portable moisture density gauge, S/N MD20606630, was stolen from an employee's vehicle parked overnight at his residence. The gauge contains two (2) sources; 9.7 millicuries Cs-137 and 49.8 millicuries Americium-241/Beryllium. The theft was discovered earlier this morning and reported to the State at 1259 EDT. The State is dispatching a field investigator for followup. The licensee informed the local Police Department of this incident. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | OH | OTH | AGR |  |  |  |  | 0 | 2003-10-14
40234 | 0 | FRAMATOME ANP |  |  |  |  | 2003-10-09 | 2003-10-09 11:22 | 2003-10-09 | PART 21 REPORT A potential safety condition was reported which may exist with the Eaton Cutler-Hammer Type W Vintage Unit plug in stabs. On July 3, 2003, Framatome ANP, Inc - Electrical Products received from Eaton Cutler-Hammer an Eaton Cutler-Hammer Type W Vintage Unit Product Advisory, dated June 27, 2003. The advisory warns that the condition exists when a unit of a particular Manufacturing Date Code range is withdrawn from a Motor Control Center structure. Under this condition, the clip holding the stab finger in place may dislodge. As a result, the stab finger remains plugged onto the vertical bus until the breaker cable connection forces the stab finger off the bus. The potential of a unit being extracted from live bus may cause arcing or single phasing or risk of personal injury, death or property damage. On July 3, 2003, Framatome ANP, Inc. - Electrical Products determined that the defective Eaton Cutler-Hammer Type W Vintage Unit Plug in Stabs were supplied as a Safety Related component installed in Safety Related Type W MCC Buckets to only one Nuclear Customer. On July 3, 2003, Framatome ANP, Inc. - Electrical Products notified the Point Beach Nuclear Plant (Nuclear Management Company). Corrective actions implemented by Framatome ANP, Inc. - Electrical Products included the replacement of thirteen (13) Type W Stab Assemblies, with new Type W Stab Assemblies manufactured by Eaton Cutler-Hammer with "updated clips" (clips with wings) at the Point Beach Nuclear Plant Site on July 11, 2003. Affected Plant: Point Beach | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-10-09
40233 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-10-08 13:25 | 2003-10-08 14:21 | 2003-10-08 | OFFSITE NOTIFICATION DUE TO HYDRAULIC OIL SPILL Offsite notification was due to a failure on a 100-ton mobile crane that resulted in a approximately 150 gallon hydraulic oil spill to the ground. The spill did not involve a pathway to surrounding bodies of water. Efforts are underway to remediate the affected area. The State of Connecticut Department of Environmental Protection as well as the National Response Center was notified. The licensee will be notifying the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-10-08
40232 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-10-08 10:30 | 2003-10-08 13:45 | 2003-10-08 | TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO PRIMARY COOLANT BOUNDARY LEAKAGE "Nine Mile Point Unit 1 entered a Technical Specification (TS) required shutdown due to suspected unsatisfactory allowable leakage past Primary Coolant System Pressure Isolation Valves. At 10:30 EST, The Condition Monitoring group notified the Control Room that leakage past the Core Spray keep-fill check valves 40-22 and 40-23 exceeded the TS allowable leak rate. Preliminarily, leakage was quantified at 1.1 gpm (uncorrected). With these two valves declared inoperable, Technical Specification 3.2.7.1b required an orderly shutdown be initiated within 1 hour and the reactor in cold shutdown condition within 10 hours. The shutdown was initiated at 11:27 [hrs]. A surveillance test was performed to quantify leakage rate under test conditions. At 13:10 [hrs], it was determined that the leakage rate was 0.156 gpm (corrected to 1080 psid) and that the previous data received was not valid. The TS required shutdown was suspended and power recovery is planned." The licensee has informed the NRC Resident Inspector. | 96 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-10-08
40231 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-10-08 11:24 | 2003-10-08 12:20 | 2003-10-10 | SECURITY WEAPON AND HOLSTER LEFT UNATTENDED Security weapon and holster left unattended. Immediate compensatory actions taken upon discovery. Contact the HOO for details. The licensee will be notifying the NRC Resident Inspector and has notified the R1TAS (Greg Smith). * * * UPDATE AT 1300 EDT ON 10/10/03 FROM STEVE MORRISSEY TO DICK JOLLIFFE * * * The licensee is retracting this report based upon further review. Contact the HOO for details. The licensee will inform the NRC Resident Inspector. Notified R1DO (Ron Bellamy). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | NH | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-10-08
40230 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-10-07 07:00 | 2003-10-08 10:53 | 2003-10-08 | CONCURRENT FEDERAL NOTIFICATION INVOLVING SMALL CHEMICAL RELEASE AT BWXT BWXT notified EPA Region 3 of the onsite release of hazardous material (2 to 3 gallons of nitric acid) as a result of a leaky valve on the outside wall of the Recovery Building. The licensee will notify the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 1 | 2003-10-08
40229 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-10-07 12:31 | 2003-10-07 19:54 | 2003-10-07 | HIGH PRESSURE CORE SPRAY DECLARED INOPERABLE (HPCS) At 1231 hours on October 7, 2003, the High Pressure Core Spray (HPCS) system at Columbia Generating Station was declared inoperable due to a failure to maintain system pressure while the system was being operated with the keep-fill piping isolated for maintenance on the system waterleg pump. This action rendered the HPCS system unable to perform its safety function to mitigate the consequences of an accident. Upon discovery of the inoperable condition, the Reactor Core Isolation Cooling system was verified to be operable and HPCS was restored to operable status at 1538 in accordance with the Required Action of plant Technical Specifications Limiting Condition for Operability 3.5.1, Conditions B.1 and B.2. All other Emergency Core Cooling System (ECCS) were operable during the time the HPCS system was inoperable. This event is being reported pursuant to the guidance for reporting under 50.72(b)(3)(v)(D) contained in NUREG 1022, which states for single train systems that perform a safety function, loss of a single train would prevent the fulfillment of the safety function and therefore is reportable. The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-10-07
40228 | -1 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-10-07 11:00 | 2003-10-07 18:13 | 2003-10-14 | REACTOR COOLANT SYSTEM PRESSURE BOUNDARY LEAKAGE At 1100 EDT on October 7, 2003, Seabrook Station concluded that the source of small boron deposits on the Reactor Vessel Head was a leaking conoseal weld on a CRDM housing. The defect in primary coolant is not acceptable per ASME XI. This condition is reportable pursuant to 10 CFR 50.72 (b)(3)(ii). The caller stated that through testing it is indicated that the leak had occurred in the last 2 months. A small amount of boric acid crystals was found. The NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 10/14/03 @ 1709 BY BEMIS TO GOULD * * * This report supplements and retracts the 8 hour notification (Event Number 40228) made on October 7, 2003 pursuant to 10CFR50.72(b)(3)(ii)(A) documenting reactor coolant system pressure boundary leakage. FPL Energy Seabrook has determined that the initial report, although conservative, inappropriately interpreted canopy seal degradation to be pressure boundary leakage. The canopy seal weld is neither a structural weld nor a pressure retaining weld comprising the reactor coolant system pressure boundary. Therefore, the initial report is being retracted. A permanent plant design is being developed to repair the canopy seal using a standard canopy seal clamp and will be installed prior to startup from the current refueling outage. The NRC Resident Inspector was notified. Notified Reg 1 RDO (MCDERMOTT) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-14
40227 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-10-06 22:15 | 2003-10-07 06:20 | 2003-10-07 | HPCI SYSTEM INOPERABILITY DUE TO FAILED SUPPRESSION POOL LEVEL SWITCH AT DRESDEN UNIT 2 "The Unit 2 HPCI system has been declared INOPERABLE due to the failure of a pressure suppression pool high-level switch during surveillance and being unable to maintain the HPCI pump suction lined up to the pressure suppression pool in standby lineup. "Per technical specification 3.3.5.1. required action D.2.2. with the high level switch INOPERABLE the HPCI system must have the pump suction aligned to the suppression pool with in 24 hours or declare the HPCI system INOPERABLE when the required action completion time can not be met. The function of the suppression pool high-level switch causes the HPCI pump suction to automatically realign to the suppression pool when the suppression pool reaches the high level set point during an accident. "When the pump suction swap to the suppression pool was performed the HPCI gland seal leak off pump began to run automatically. Further investigation determined that there was an unknown input into the HPCI gland seal leak off condenser (GSLO). Normally the GSLO does not have an input while in standby lineup and therefore does not normally operate while the pump suction is aligned to the Pressure Suppression Pool. The GSLO pump would have a discharge flow path with the HPCI system running and therefore would have the ability to maintain its design function. However in the standby line [-up] with the pump suction aligned to the suppression pool the GSLO pump did not have a discharge flow path. This inability to pump the GSLO condenser required the suction be realigned to the condensate storage tank and with the combination of a failed suppression pool high-level switch requires declaration of INOPERABITY of the HPCI system. This is a 14 day LCO. This is a single train system and reportable under SAF 1.8 Event or Condition That Could Have Prevented Fulfillment of a Safety Function. The INOPERABLE HPCI system function can be manually initiated from the main control room. Investigation and troubleshooting into the unknown HPCI GSLO input has been initiated in parallel with the repairs to the failed suppression high level switch." The licensee intended on notifying the NRC Resident Inspector. | 0 | 86 | 0 | 0 | 86 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-10-07
40226 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-10-05 11:00 | 2003-10-05 12:54 | 2003-10-05 | OSCILLATION POWER RANGE MONITORS (OPRM) DECLARED INOPERABLE See event # 40223, Part 21 reported on 10/04/03 by GE Nuclear Energy for background information. "On October 5, 2003, Progress Energy Carolinas, Inc. received notification from General Electric of a Part 21 involving the potential for numerous, unexpected confirmation count (CC) resets in the event of an instability condition. These CC resets may result in the inoperability of TS Table 3.3.1.1-1,'Reactor Protection System Instrumentation, Function 2. f, OPRM Upscale.' "All Unit 1 and Unit 2 OPRM channels have been declared inoperable. Technical Specification 3.3.1.1, Action I requires an alternate method of detecting and suppressing thermal hydraulic instabilities to be implemented within 12 hours. The alternate methods of detection and suppression are currently in place. "Due to the implementation of Technical Specification required compensatory actions, there is minimal safety significance." The NRC Resident Inspector was notified of this event by the licensee. Also see similar events reported by NMP Unit 2 (event # 40217) and Fermi Unit 2 (event # 40215) | 94 | 97 | 0 | 94 | 97 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-10-05
40225 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-10-05 03:00 | 2003-10-05 06:26 | 2003-11-19 | INOPERABLE TRAINS OF CONTROL ROOM EMERGENCY FILTRATION AT HOPE CREEK "While performing common mode failure testing of the Emergency Diesel Generators (EDG), the 'C' EDG was declared INOPERABLE for planned installation of required test equipment. Concurrent with the inoperability of the 'C' EDG, the 'B' Control Room Emergency Filtration (CREF) System has been INOPERABLE for emergent corrective maintenance since 10/2/03 at 0502. Because the 'C' EDG is the emergency power supply for the 'A' CREF train, 'A' CREF was also declared INOPERABLE and Technical Specification 3.0.3 was entered as of 0300 hrs on 10/05/03. At 0430 hrs on 10/05/03, the test equipment was removed from 'C' EDG, thereby restoring it and 'A' CREF to an operable status, and Technical Specification 3.0.3 was exited. Testing did verify the absence of a common mode failure and all EDG's are operable. The Control Room Ventilation System provides heating, cooling, ventilation, and environmental control for the control room and adjacent areas. Under accident conditions, CREF ensures that the control room will remain habitable during and following all design basis accidents. Because the CREF system is required to automatically respond in the event of a design basis accident, having both trains of CREF inoperable at the same time impacted the ability to mitigate the consequences of an accident. Therefore, this event is being reported in accordance with 10CFR50.72(b)(3)(v)(D). The plant is currently in HOT SHUTDOWN for repair of an emergent turbine hydraulic fluid leak, with decay heat removal to the main condenser via turbine bypass valves." The NRC resident inspector was notified by the licensee. * * * * UPDATE ON 11/19/03 @ 1640 BY RITA BRADDICK TO C. GOULD * * * * "At the time of the original notification, both trains of Control Room Emergency Filtration (CREF) were declared inoperable impacting the ability of CREF to mitigate the consequences of an accident. The "B" train was inoperable for emergent corrective maintenance and the "A" train was declared inoperable when test equipment was connected to the "C" emergency diesel generator (EDG). The "C" EDG provides emergency power to the "A" train of CREF. Subsequent to this event, an evaluation of the test equipment impact to the "C" EDG was performed and determined that the "C" EDG would still be capable of providing emergency power to the "A" CREF train in the event offsite power is lost. Therefore, the "A" CREF train remained available to respond to a design basis accident. Thus, the safety function would have been fulfilled." R1DO (Brain McDermott) notified. The NRC Resident Inspector will be notified of this retraction by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-10-05
40224 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-10-04 17:13 | 2003-10-04 20:04 | 2003-10-05 | RPS ACTUATION WHILE CRITICAL "Hope Creek Generating Unit was manually scrammed at 1713 hours [EDT] on 10/04/03 due to an Electro Hydraulic Control (EHC) System oil leak. Prior to the event the unit was at 100% power. The plant responded as designed for the scram, with lowest reactor level reaching -8 inches. Reactor level is currently being maintained between +12.5 inches and +54 inches with secondary condensate pumps. The unit is currently in Mode 3 - Hot Shutdown with reactor pressure being maintained between 500-600 psig with the main turbine bypass valves utilizing the main condenser as a heat sink. The EHC leak was validated to be associated with the #4 Combined Intermediate Control Valve (CIV) and has since been isolated. This report is being generated Law Event Classification Guide section 11.3.2 - Actuation of Reactor Protection System (RPS) when critical except preplanned. Current safety system status is normal with the exception that the `B' Emergency Diesel Generator (EDG) is inoperable as the result of a relay failure and the 'B' Control Room chiller is inoperable as the result of a failed economizer float. The 'B' EDG has been retested and validation of test results are currently underway to determine operability. Common mode failure testing is in progress for the remaining three EDG's." All control rods inserted fully during the reactor scram. No relief valves lifted during the transient and there were no ECCS actuations or Primary Containment Isolation System actuations. The electrical grid remained stable during the event. NRC Resident was notified by Licensee. * * *UPDATE PROVIDED BY CLYDE BAUER TAKEN BY JEFF ROTTON AT 1728 EDT ON 10/05/03 * * * During reactor level recovery following the scram, a second level 3 (+12.5 inches) RPS scram signal was received. The RPS system was still actuated upon receipt of this second level 3 signal. R1DO (Cobey ) notified of update. NRC Resident will be notified by licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-10-04
40223 | 0 | GE NUCLEAR ENERGY |  |  |  |  | 2003-10-04 | 2003-10-04 18:27 | 2003-10-04 | DEFECTS AND NONCOMPLIANCE REPORT GE Nuclear Energy provided information concerning a reportable condition on the stability Option III Period Based Detection Algorithm (PBDA) for the Oscillation Power Range Monitor (OPRM) installed at the affected Licensee plants listed below. The basic component with the defect is specification of the allowable values for the adjustable period confirmation variables in the PBDA used in Stability Option III. The defect is that certain values of period tolerance and conditioning filter cutoff frequency within the previously specified acceptable range could produce sufficient successive confirmation count resets such that Safety Limit Minimum Critical Power Ratio (SLMCPR) protection might not be provided for all anticipated reactor instabilities. This condition does not produce a substantial safety hazard and there is no threat of fuel failure. However, because the condition could contribute to exceeding the SLMCPR, it is a reportable condition. List of Affected Plants: Clinton Brunswick 1 & 2 Nine Mile Point 2 Fermi 2 Columbia Dresden 2 & 3 LaSalle 1 & 2 Limerick 1 & 2 Peach Bottom 2 & 3 Quad Cities 1 & 2 Perry 1 Susquehanna 1 & 2 Hope Creek Hatch 1 & 2 Browns Ferry 2 & 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | CA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-10-04
40222 | 0 | CRYSTAL RIVER | 3 |  |  | [3] B&W-L-LP | 2003-10-04 10:32 | 2003-10-04 16:11 | 2003-10-04 | DEGRADED CONDITION DUE TO RCS PRESSURE BOUNDARY LEAKAGE "At 1032 [EDT] on October 4, 2003 while in mode 4 conducting a planned refueling outage reactor coolant system inspection, Crystal River Unit 3 identified two potential RCS Pressure Boundary Leaks located in Pressurizer penetrations associated with upper level sensing lines. Upon closer inspection of the first one inch penetration, indications confirmed a Pressure Boundary Leak. A closer inspection of the second penetration is planned after obtaining access to the location. The last unidentified leak rate that was completed prior to the plant shutdown was 0.15 gpm. This defect in the primary coolant system is not acceptable per ASME XI. This condition is REPORTABLE per 10CFR 50.72 (b)(3)(ii)(A)." Licensee reported that a small amount of boric acid residue and residual rust was identified during inspection in the vicinity of the upper level Pressurizer tap near the Pressurizer shell and the nozzle. A closer inspection is planned of the other two upper Pressurizer level taps. The NRC resident has been notified by the Licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-04
40221 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-10-03 15:16 | 2003-10-03 20:14 | 2003-10-03 | ACCIDENT MITIGATION SYSTEM DEGRADED DUE TO BOTH TRAINS OF AUXILIARY BUILDING GAS TREATMENT SYSTEM INOPERABLE The following information was obtained from the licensee via facsimile: "On 10/03/2003, Watts Bar Nuclear Plant Unit 1 was in Mode 6 during a refueling outage with core re-load in progress. At 1516 [hrs EDT], the control room became aware that an activity in preparing for an upcoming test had placed the B Auxiliary Building Gas Treatment System (ABGTS) 480v Breaker in the off position. An operator was immediately dispatched to close the ABGTS breaker and the breaker was closed at 1521 [hrs], restoring the train to OPERABLE status. The opening of this breaker at about 1324 [hrs] caused the B ABGTS train to be INOPERABLE at a time when the A ABGTS train was available to start but technically INOPERABLE due to the emergency power supply ( A Train Diesel Generator) and a room cooler being out of service. "The ABGTS system is required for the mitigation of a postulated fuel handling accident. Site emergency procedures require the operator to promptly confirm ABGTS is in operation, indication is provided in the control room on ABGTS status and breaker restoration can be quickly performed. In addition, with off site power available, the A ABGTS train would have immediately responded to an event and begun to perform the filtration function while the otherwise operable B train was manually restored. However, at the time of discovery, the system could not have performed its function in the event of a postulated accident coincident with a loss of off site power. Accordingly, TVA has determined this event is reportable in accordance with 10 CFR 50.72 (b)(3)(v)(D)." The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-10-03
40220 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-10-03 17:00 | 2003-10-03 19:09 | 2003-10-03 | TEXAS AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE The following information was received from Texas Department of Health, Bureau of Radiation Control via facsimile: "Troxler model 3440, serial # 31623 "8 [millicuries] Cs-137 source, sn [serial number] 7506418 "40 [millicuries] Am-241/Be, sn 4728354 "A technician removed the gauge from the back of the pick up truck to wash the truck. The gauge was placed outside the wash bay. The gauge was stolen while the technician was busy washing the truck. The gauge was locked inside the storage container. Some tools were inside. No other items were stolen or left unattended. The licensee notified the local police. The incident was reported to the Agency by the Beaumont site RSO. "The Agency is investigating the incident." Texas Incident Number I-8060. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-08
40219 | 0 | FLORIDA BUREAU OF RADIATION CONTROL |  |  |  |  | 2003-10-02 | 2003-10-03 15:29 | 2003-10-08 | FLORIDA AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE Troxler moisture density gauge, model #3430, serial #32804 was stolen from the rear of licensee employee's truck parked at residence in Tampa, FL between the hours of 11 PM EDT 10/02/03 and 11 AM 10/03/03. The locked chain securing gauge box was broken. The gauge contained 40 [milliCuries] of Am-241/Be and 8 [milliCuries] of Cs-137. Tampa Police, Florida Department of Emergency Management and the NRC Region 2 have been informed. The licensee posted a notice offering a reward in the Tampa newspaper. Florida Incident # FL 03-181 * * * UPDATE VIA E-MAIL FROM ADAMS TO CROUCH @ 1550 HRS ON 10/8/03 * * * Troxler was notified by a pawn shop owner in Tampa on 8 October that they had bought the gauge. Troxler notified the State of Florida. The owner and police were notified and the gauge was retrieved. It was undamaged. The police have a good lead on the thieves. Licensee will be forwarding a copy of the police report to the State of Florida. Notified R1DO (Bellamy) and NMSS EO (Hickey). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | FL | OTH | AGR |  |  |  |  | 0 | 2003-10-08
40218 | 0 | MARYLAND DEPT OF THE ENVIRONMENT |  |  |  |  | 2003-10-02 | 2003-10-03 13:45 | 2003-10-03 | MARYLAND AGREEMENT STATE REPORT - MEDICAL MISADMINISTRATION On 10/02/03, a patient with suspected hyperthyroidism was undergoing treatment at Sinai Hospital in Baltimore, MD. During administration of an uptake diagnostic test, the patient was given a dose of 80 microcuries of I-131 versus the prescribed dose of 8 microcuries. Preliminary investigation indicates that hospital policy is to have technician dose measurement verified by another technician and approved by supervision until the technician shows proficiency at this task. It is unclear at this time whether the technician followed this protocol. The prescribing physician has been notified and has notified the patient. Follow-up tests will be performed on the patient, but no increase in physiological effect on the patient is expected.. Maryland Department of Radiation Health is planning to contact the Hospital Radiation Safety Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MD | OTH | AGR |  |  |  |  | 0 | 2003-10-08
40217 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2003-10-02 21:00 | 2003-10-03 02:05 | 2003-10-03 | LOSS OF SAFE SHUTDOWN CAPABILITY DUE TO ALL OPRM CHANNELS BEING DECLARED INOPERABLE. "According to information provided by Nuclear Fuels, Reactor Engineering and G. E. Nuclear Energy, a condition exists in the Oscillation Power Range Monitors (OPRM's) that could contribute to exceeding a Safety Limit. This condition involves excessive confirmation count resets attributed to both the conditioning filter cutoff frequency and period tolerance values. G.E. Nuclear Energy can not confirm that performance of the OPRM's with the conditioning filter cutoff frequency and period tolerance settings currently in use would prevent a condition whereby a Safety Limit MCPR could be violated during an anticipated instability event. The OPRM conditioning filter cutoff frequency and period tolerance are currently set as allowed by licensing documentation, and are calculated as specified in NEDO-32465-A, Reactor Stability Detect and Suppress Solutions Licensing Basis Methodology for Reload Applications. As a result, all OPRM's at Nine-Mile Point Unit 2 are considered inoperable. This INOPERABILITY determination is based on information received from G.E. Nuclear Energy which evaluated the Nine Mile Point OPRM performance on July 24, 2003." The licensee has taken action to address this condition in accordance with Technical Specification 3.3.1.1, Reactor Protection System Instrumentation. The licensee has a procedure providing guidance for alternate methods to detect and suppress thermal hydraulic instability. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-10-03
40216 | -1 | ARKANSAS NUCLEAR |  | 2 |  | [1] B&W-L-LP,[2] CE | 2003-10-02 17:15 | 2003-10-02 20:32 | 2003-12-01 | RCS BOUNDARY LEAKAGE DUE TO SMALL CRACK ON DRAIN LINE WELDED CAP "Safety injection tank (SIT) isolation valve (2CV-5043-2) has a drain pipe under the valve body with a welded cap. The welded cap has a small crack with boric acid residue. The welded cap does not have any threads and is considered RCS boundary leakage. There is a check valve between the reactor coolant system (RCS) and the SIT Outlet valve. The crack will be repair welded prior to coming out of the 2R16 outage." The Licensee has notified the NRC Resident Inspector. * * * RETRACTED EVENT AT 1432 EST ON 12/01/03 FROM SCHEIDE TO ROTTON * * * "This report is being made to retract a notification made at 1715 CDT on 10/02/03 (EN# 40216.) "The notification documented the identification of a small amount of boric acid residue on a drain line attached to a Safety Injection Tank isolation valve (2CV-5034-2). The report stated that the indication was within the Reactor Coolant System boundary. However, subsequent review of the condition determined that the indication was not within the Reactor Coolant System boundary since it was isolated from the Reactor Coolant System by an operable check valve. Therefore, the condition did not represent a serious degradation of a principal safety barrier. "Note; The drain line is 3/4 inch diameter stainless steel." The licensee notified the NRC Resident Inspector. Notified Claude Johnson - R4DO. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode2: Refueling; FMode2: Refueling | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-02
40215 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-10-02 15:00 | 2003-10-02 16:48 | 2003-10-02 | LOSS OF SAFE SHUTDOWN CAPABILITY DUE TO ALL OPRM CHANNELS BEING DECLARED INOPERABLE. "On October 2, 2003, Detroit Edison received verbal confirmation from General Electric of a potential Non-Conservative Analysis of OPRM Period Tolerance and Corner Frequency. "All OPRM channels have been declared inoperable. Technical Specifications 3.3.1.1 Action J requires an alternate method of detecting and suppressing thermal-hydraulic instabilities to be implemented within 12 hours. Alternate methods have been established to monitor for instability when operating in the Stability Awareness region, thus we are in compliance with the Technical Specifications. "This report is being made in accordance with 10CFR50.72(b)(3)(v), Any event or condition that could have prevented the fulfillment of the safety function of a system needed to shut down the reactor and maintain it in a safe shutdown condition." The Licensee will inform the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(v)(A) |  |  |  | 0 | 2003-10-02
40214 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-10-02 09:10 | 2003-10-02 11:45 | 2003-10-02 | OFFSITE NOTIFICATION TO U.S. FISH AND WILDLIFE SERVICE AND NEBRASKA GAME AND PARKS COMMISSION The following information was received from the licensee via facsimile: "At 0910 [CDT] on 10/02/2003, the US Fish and Wildlife Service and the Nebraska Game and Parks Commission were contacted to inform them of an injured Raptor (owl). The owl is caught in the razor wire located along the top of the fence surrounding the Elevated Release Point. Current plan is to remove the owl and turn it over to Nebraska Game and Parks Commission." The Licensee has informed the NRC Resident Inspector. | 90 | 0 | 0 | 90 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-10-02
40213 | 0 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-10-01 07:00 | 2003-10-01 20:42 | 2003-10-01 | FFD 26.73 REPORT "On 10/01/03 at approximately 07:00 CDT, an access authorization (AA) group employee detected the possible odor of alcohol on a contract supervisor while speaking with the individual in the Point Beach Nuclear Plant (PBNP) Training building (outside of the protected area). AA supervision was immediately notified so corroboration of the condition would be made. The AA employee and AA supervisor were unsuccessful in locating the contractor supervisor. Security was then contacted and directed to place a hold on the individual's badge in order to prevent entry to the PBNP protected area (PA). "The contract supervisor entered the PA at 07:12:56. The SAS operator placed the person's badge on hold at 07:13:30. The individual attempted to enter the plant's north service building at 07:17:00. Security personnel responded and escorted the individual to the gatehouse, at which time the contract supervisor was instructed to return to the AA group. At approximately 07:35, the FFD Manager met with the individual whereupon the odor of alcohol was corroborated. The individual was escorted to Medical and given a "for cause" test. Results of the test were positive for alcohol. A confirmatory blood draw was offered to the individual, which was accepted. Results of confirmatory testing are pending. The individual was denied access to PBNP and all other Nuclear Management Company (NMC) sites. "A review of the individual's work was performed. This review concluded the individual had not been engaged in safety-related work activities. "The NRC Region III safeguards inspector assigned to PBNP was informed of this event at approximately 14:35." | 100 | 77 | 0 | 100 | 77 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 26.73 |  |  |  | 0 | 2003-10-01
40212 | 0 | U.S. ARMY WHITE SANDS MISSILE RANGE |  |  |  |  | 2003-10-01 08:00 | 2003-10-01 17:20 | 2003-10-01 | LEAKING CO-60 IRRADIATOR SOURCE On 10/1/03, during a bi-annual wipe test on the delivery head of a Co-60 irradiator, the licensee found evidence of leakage from the source. The level of removable contamination on the wipe was .02 microcuries, which is 4 times the limit of .005 microcuries. At the time of the wipe test, the Co-60 source was in the stored position. The source has been in the irradiator since 1999, and had an original activity of 4000 Curies in 1996. The source is currently in a storage pig, which is stored behind a locked solenoid valve. The licensee intends to remove the source from the system and place it in floor storage for later disposal. The licensee will then decontaminate the system and install a new source. There were no personnel exposures as a result of this leakage. The Licensee informed the Region IV inspector (Robert Brown). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 4 | NM | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2003-10-01
40211 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-10-01 04:30 | 2003-10-01 11:12 | 2003-10-01 | REACTOR PRESSURE VESSEL BOUNDRY LEAKAGE FOUND DURING INSPECTION "At approximately 0430 on October 1, 2003 with the reactor Mode Switch in Refuel, reactor water level 210" above Top of Active Fuel, and reactor water temperature less than 110F, investigations and walkdowns were being performed to identify potential sources of drywell leakage. Drywell leakage was well within Technical Specification limits. During these walkdowns a small leak in a cap of a nozzle of the reactor pressure vessel boundary, nozzle N10, located at reactor vessel height 440" was identified. This location is 84" above Top of Active Fuel. This is a cut and capped 4" Control Rod Drive return line. The leak appears to be on the cap weld. This notification is being made per 10 CFR 50.72(b)3(ii)(A). All required ECCS systems are presently operable. "Investigation is continuing. The [NRC] resident inspector has been notified." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | DEGRADED CONDITION |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(ii)(A) |  |  |  | 0 | 2003-10-01
40210 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-09-30 20:50 | 2003-10-01 00:43 | 2003-10-20 | PLANT SHUTDOWN REQUIRED BY TECHNICAL SPECIFICATIONS DUE TO INOPERABLE CONTROL CENTER HVAC "With the plant in Mode 1 and 100% reactor power at 2043 [EDT] on September 30, 2003, while shifting divisions of Control Center HVAC (CCHVAC), the Division 1 chiller failed to start and Division 1 CCHVAC was declared INOPERABLE. At 2050, a restart of Division 2 CCHVAC was attempted and the Division 2 chiller failed to start. Division 2 CCHVAC was declared INOPERABLE, and the plant entered LCO 3.0.3 as required by LCO 3.7.4 Condition D. Plant shutdown was initiated at 2146. Division 1 CCHVAC was declared OPERABLE at 2315, and LCO 3.0.3 was exited. Plant shutdown was terminated at 2315 with the reactor at 84% power. Division 2 CCHVAC remains INOPERABLE and under investigation, with plant operating under LCO 3.7.4 Condition A. Plans are to return to 100% reactor power. All ECCS systems remained OPERABLE during this event. "The NRC Resident Inspector has been notified. This report is being made pursuant to 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(v)(D)." * * * UPDATE 1428 EDT ON 10/20/03 FROM JEFF YEAGER TO S. SANDIN * * * The licensee is retracting the notification required per 10 CFR 50.72(b)(3)(v) based on the following: "At 2050 hours on September 30,2003 with the plant operating at 100 percent reactor power air conditioning chillers for both divisions of the Control Center Air Conditioning System failed to start. Technical Specification (TS) LCO 3.0.3 was entered as directed by LCO 3.7.4, Control Center Air Conditioning System, Condition D.1 and a plant shutdown initiated at 2146 hours. Notification was made in accordance with 10 CFR 50.72(b)(2)(i), a Plant Shutdown Required by Technical Specifications. The chiller for Division 1 Control Center Air Conditioning System was started after approximately one hour and subsequently declared operable at 2315 hours. TS 3.0.3 was exited and power reduction was terminated at 84 percent reactor power. "Notification was also made in accordance with 10 CFR 50.72(b)(3)(v), Event or Condition that Could Have Prevented Fulfillment of a Safety Function. Investigation revealed an oil pressure permissive was not met for start of the chiller due to a small amount of air leaking into a pressure switch while shutdown. This delayed meeting the oil pressure permissive for starting the chiller. Subsequent start attempts removed the air, allowing the pressure permissive to be met and the chiller to be restarted. This restart of the chiller was accomplished from the main control room in accordance with plant procedures. Therefore, Division 1 Control Center Air Conditioning was capable of performing its intended function. This condition is therefore not reportable under 10 CFR 50.72(b)(3)(v). The original notification, Event Number 40210, is retracted." The licensee informed the NRC Resident Inspector. Notified R3DO (Jim Creed). | 84 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-10-01
40209 | 0 | DRESDEN |  | 2 |  | [1] GE-1,[2] GE-3,[3] GE-3 | 2003-09-30 20:14 | 2003-09-30 23:11 | 2003-09-30 | AUTOMATIC REACTOR SCRAM ON LOW REACTOR VESSEL WATER LEVEL. Dresden Unit 2 automatically scrammed on low reactor vessel water level after "2C" reactor feed pump tripped (1 of 2 running). All systems responded as required (all rods fully inserted). Investigation into reactor feed pump trip cause has begun. The NRC Resident Inspector will be notified of this event by the licensee. | 0 | 0 | 0 | 0 | 85 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-09-30
40208 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2003-09-30 21:34 | 2003-09-30 22:52 | 2003-09-30 | VALID SPECIFIED SYSTEM ACTUATION At 2134 EDT on 9/30/03, a reactor trip occurred on RPS (Reactor Protection System) shutdown high pressure. The plant was in Mode 3 performing a cooldown to Mode 4. RCS (Reactor Coolant System) pressure was 1788 psig on the cooldown pressure indicator. Group 1 safety rods were withdrawn prior to the trip. All other safety and regulating rods were already fully inserted. All systems performed as required, and the plant is stable in Mode 3. RCS pressure is 1755 psig, and RCS temperature is 526 degrees F. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | A/R | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Standby; FMode1: Hot Standby | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-09-30
40207 | 0 | U.S. ARMY ROCK ISLAND, IL |  |  |  |  | 2003-09-19 12:00 | 2003-09-30 17:47 | 2003-10-02 | PART 76.83 - TRANSFER OF RADIOACTIVE MATERIAL On 9/19/03, the U.S. Army Base at Fort Wainwright, AK sent a shipment of five M-119 Howitzers to the National Forest Service in California to be used for avalanche control. Prior to shipment, the Tritium fire control devices were removed from the Howitzers and placed in boxes. The boxes containing the fire control devices were inadvertently shipped along with the Howitzers. Two boxes, containing a total of 19.4 curies of tritium, ended up at the Alpine Meadows ski resort in Tahoe City, CA. Another 3 boxes, containing a total of 28.2 curies of tritium, ended up at the Mammoth Mountain ski resort in Mammoth Lake, CA. The National Forest Service will keep the tritium fire control devices in a secure storage location overnight, and they will be picked up by the Radiation Safety Officer from Hawthorne Army Depot on the morning of 10/1/03. * * * UPDATED VIA FAX ON 10/02/03 @ 1523 EDT* * * "Fort Wainwright, Alaska was given authority to ship 5 ea M119 howitzers to the National Forest Service in California as part of the avalanche control program. Three of the M119's were to be shipped to Mammoth Lakes, CA and two to Alpine Meadows ski area in Tahoe City, CA. The howitzers were in storage and therefore had their tritium fire control devices removed and placed in their associated BII boxes. "All of the fire control devices were properly stored in their BII boxes prior to shipment from Alaska. When the shipment was processed the shippers failed to remove the tritium devices from the Bll boxes (a grand total of 47.6 curies). Therefore the tritium devices were inadvertently shipped with the howitzers on 19 Sept 2003. On 29 Sept 2003, two howitzers, with BII boxes, were received at Alpine Meadows ski area, Tahoe City, CA and three howitzers, with BII boxes, were received at Mammoth Mt. ski area, Mammoth Lake, CA. Upon discovering radioactive commodities had been received, the National Forest Service called the U.S. Army Tank Automotive Command [TACOM]. "The TACOM RSO [Radiation Safety Officer] contacted the RSO at Hawthorne Army Depot, Hawthorne, CA on 30 Sept 2003 and requested their aid in capturing the radioactive components. On October 1st, 2003 the Hawthorne Army Depot RSO took possession of all the tritium fire control devices. Wipe surveys are being evaluated and disposition of the components will be determined upon receipt of the results." Notified R3DO (Lara), R4DO (Cain) and NMSS EO (Janosko). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 4 | NV | MAT | [5 empty] | 0 | 2003-09-30
40206 | 0 | FRAMATOME ANP |  |  |  |  | 2003-08-19 | 2003-09-30 14:39 | 2003-09-30 | PART 21 REPORT A potential safety concern was reported regarding failure of the Eaton Cutler-Hammer Freedom Series Heater Pack due to a possible defect in the weld which joins the screw terminal to the heater coil. The following conditions could potentially occur: - Open circuit resulting in loss of current to a pole in the overload relay. If the load was not running at the time of failure, it would draw excessive current during its next attempted start, and either trip the overload or damage the load. If the load was running at the time of failure, it would slow to a stop while drawing excessive current, which would either trip the overload or damage the load. - If two heaters failed in the same load, a shock hazard could develop due to voltage to ground on the remaining phase. The affected Heater Packs are H2009B-3 through H2011B-3, and H2012B-3 through H2017B-3. The following NRC Licensees are affected: DC Cook, Vogtle, and Beaver Valley, Framatome-ANP Inc. in Lynchburg, VA. Corrective actions by the supplier include daily inspection/replacement of weld electrodes, and destructive sample testing. Corrective actions by Framatome include dedication activities that address weld integrity acceptance. Framatome recommends licensees replace all affected Heater Packs. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-09-30
40205 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-09-28 23:45 | 2003-09-29 15:22 | 2003-09-29 | 50.72 NON-EMERGENCY - ACCIDENT MITIGATION "This report is being made in accordance with 10CFR50.72 section (b)(3)(v)(D). "At 2345 [CDT] on 9/28/03, while performing Turbine Trip Testing, the required sequence of events failed to occur, and it was determined that a turbine trip would not occur when required by Technical Specification 3.3.2.2, Feedwater and Main Turbine High Water Level Trip. Condition B of Specification 3.3.2.2 was entered, requiring restoration [of] highwater level trip capability in two hours, and Condition C requiring that thermal power be reduced to less than 25% in four hours. "The feedwater and main turbine high water level trip instrumentation is assumed to be capable of providing a turbine trip in the design basis transient analysis for a feedwater controller failure, maximum demand event. The Level 8 trip indirectly initiates a reactor scram from the main turbine trip (above 30% RTP) and trips the feedwater pumps, thereby terminating the event. The reactor scram mitigates the reduction in MCPR [Minimum Critical Power Ratio]. "Since the Turbine trip would not have occurred, the reactor scram would not have occurred. At 0530 on 9/29/03 reactor power was lowered to below 25%. "This event was determined to be reportable on 9/29/2003 at 1230 [CDT]." The licensee notified the NRC Resident Inspector. | 22 | 0 | 0 | 65 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-09-29
40204 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2003-09-28 00:13 | 2003-09-28 03:02 | 2003-09-28 | OFFSITE NOTIFICATION DUE TO REPORT OF EMERGENCY SIREN ACTUATION "At 00:13 on 9/28/03, the Unit 1 Control Room received an offsite call from the Pope County 911 office stating that two local individuals had reported the actuation of emergency sirens in the Russellville area. The Arkansas Department of Health, who controls the actuation of the sirens, was contacted; but they had no indication of the sirens alarming at the time that they were notified. The actuation of the sirens has not been confirmed. "This report is being made in accordance with SAF 4.1 'News Release or Government Agency Notification' and 10CFR50.72(b)(2)(xi) since there was a notification of state/county agencies of inadvertent actuation of part of the public notification system." The licensee will inform the state and has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-09-28
40203 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2003-09-27 15:08 | 2003-09-27 16:08 | 2003-09-27 | SAFETY PARAMETER DISPLAY SYSTEM (SPDS) "Unit 2 will be down powering inverter 2Y-26 for pre-planned maintenance during the Unit 2 refueling outage. This will result in the loss of power to the Safety Parameter Display System (SPDS). This constitutes a major loss of emergency assessment capability for both Unit 1 and Unit 2. The expected SPDS outage duration is 2 hours." State and the NRC Resident Inspector will be notified of this event by the Licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-27
40202 | 0 | VERMONT YANKEE | 1 |  |  | [1] GE-4 | 2003-09-27 07:40 | 2003-09-27 10:52 | 2003-09-27 | TECH SPEC REQUIRED SHUTDOWN DUE TO RCS LEAKAGE INCREASE GREATER THAN 2 GPM "Initiated Plant shutdown required by the Technical Specifications. TS 3.6.C.1.b limits unidentified primary containment leakage to a 2 gpm increase in any 24 hour period. Leakage increased by approximately 3.6 gpm." The licensee will inform the NRC Resident inspector. | 15 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | VT | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-09-27
40201 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-09-26 12:00 | 2003-09-26 18:40 | 2003-09-26 | LEAKING SEALED SOURCE FOUND: 5 CURIE AMERICIUM-241/BERYLLIUM "A 5 curie AM-241/Be sealed source was found leaking during a routine leak test on September 26, 2003. The removable contamination was 0.081 microcuries. The source is a Gulf Nuclear model 71-1 serial # 71-1448B. The source was transported during September 2003 from the Licensee's Edinburg, TX site to the Ft. Worth site. The contamination was confined to the inside of the transport container and the source housing. A second source that had been stored as a companion in the same down hole storage in Edinburg also had a small amount of contamination on it (399 dpm found, below the 11,000 dpm limit). Therefore, the Edinburg downhole site will be checked by the Licensee for contamination. The storage facility in Edinburg has been taken out of service and off limits until proper surveys are made. "An update will be provided when more information is available "Transport vehicle description: Computalog company vehicle" Texas Incident No: I-8059. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-10-01
40200 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-09-26 08:50 | 2003-09-26 16:31 | 2003-09-29 | GREATER THAN 1 PERCENT OF STEAM GENERATORS 1,2 & 4 TUBES INSPECTED INDICATE THAT THE INSPECTED TUBES REQUIRE PLUGGING. "At 0850 EST on September 26, 2003, with Watts Bar Nuclear Plant Unit 1 defueled, steam generator inspections were being performed in accordance with Technical Specification (TS) 5.7.2.12, 'Steam Generator Tube Surveillance Program.' The results of the inspections performed on Steam Generator Numbers 1, 2, and 4 indicated that greater than 1% of the inspected tubes require repair. Based on TS 5.7.2.12, this determination results in the classification of C-3. The current inspection results do not meet the criteria specified for steam generator tube degradation in Revision 2 of NUREG 1022, Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73. However, for classification C-3, WBN TS Table 5.7.2.12-1, 'SG Tube Inspection Supplemental Sampling Requirements, 'requires that the results of the inspection be reported under 10 CFR 50.72. At this time, the submittal of the Licensee Event Report in accordance with 10 CFR 50.73 is not planned." The NRC Resident Inspector was notified of this event by the licensee. **** Update on 09/29/03 at 1439 EDT by John Roden taken by MacKinnon **** "In addition, at 0800 on September 29, 2003 Steam Generator Number 3 has been determined to be in the classification of C-3 (48 tubes). The current inspection results do not meet the criteria specified for steam generator tube degradation in Revision 2 of NUREG 1022, Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73. However, for classification C-3, WBN TS Table 5.7.2.12-1, 'SG Tube Inspection Supplemental Sampling Requirements,' requires that the results of the inspection be reported under 10 CFR 50.72. At this time, the submittal of a Licensee Event Report in accordance with 10 CFR 50.73 is not planned." R2DO (Mark Lesser) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Refueling; FMode1: Refueling | NON EMERGENCY | 2 | TN | POW | [5 empty] | 0 | 2003-09-26
40198 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-09-25 | 2003-09-26 01:25 | 2003-11-10 | INITIATION OF A TECHNICAL SPECIFICATION REQUIRED SHUTDOWN AT PEACH BOTTOM 2 "On 09/25/03 @ 2210, while restoring reactor vessel instrumentation to service on Unit 3, an invalid ECCS actuation, (reactor vessel lo-lo-lo) occurred which caused all four (4) EDG to automatically start. All eight (8) 4 KV buses remained supplied from offsite sources. The Unit 3 ECCS pump auto starts were previously defeated per plant procedure and were not required to be operable per Tech Specs. The invalid ECCS initiation signal caused the offsite power Loss-of-Power instrumentation setpoints to transfer to the degraded voltage LOCA setpoints. With the degraded voltage LOCA setpoints initiated, the 4 KV E-bus fast transfer capability on a degraded voltage-NON-LOCA condition is defeated. With the inability to fast transfer the 4 KV E-buses on a degraded voltage NON-LOCA condition, both offsite sources are inoperable. Prior to restoring the reactor vessel level instrumentation, the E-2 diesel generator was inoperable. With both offsite source.; and one EDG inoperable, LCO 3.8.1 Required Action H.1 requires an entry into LCO 3.0.3 for Unit 2. With Unit 3 in MODE 5, LCO 3.0.3 is not applicable. "After one (1) hour, actions were taken to initiate a plant shutdown per LCO 3.0.3. No negative reactivity was added as the preparations were administrative in nature. At 09/26/03 @ 0006, the invalid ECCS initiation was removed. And all offsite Loss-of-Power instrumentation has been returned to OPERABLE status. "Following the automatic start of all four (4) EDGs, E-1, E-3, and E-4 were successfully shutdown per plant procedures. E-2 could not be shutdown per plant procedures and was shutdown locally. The cause of the inability to shutdown E-2 per plant procedures is under investigation. E-2 EDG remains inoperable." The NRC Resident Inspector was notified by the licensee. * * * UPDATE PROVIDED BY DAVE FOSS TO JEFF ROTTON AT 0932 ON 11/10/2003 * * * "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of a specified system, specifically the Units 2 and 3 Emergency Diesel Generators (EDGs).' 'On 9/25/03 at 2210 while restoring reactor vessel instrumentation to service on Unit 3, an invalid EDG start actuation signal on Reactor Vessel Lo-Lo-Lo level occurred which caused all four Emergency Diesel Generators to automatically start. Investigation into the cause of the event identified that the sequence of operating instrument valves associated with the instrument rack for level transmitters LT 72A and LT 72C resulted in the invalid reactor vessel lo-lo-lo reactor water level signal and subsequent EDG logic actuation. The EDGs initiated as expected for the given conditions. Off-site power was not affected and continued to supply power to the emergency busses. Once the reason for the EDG initiation was determined, the E-1, E-3, and E-4 EDGs were shut down per plant procedures from the Main Control Room by approximately 2255 hours. The E-2 EDG could not be shut down normally from the Main Control Room control switch. It was later shut down at the local control panel in the E-2 EDG bay at about 0030 hours on 9/26/03. Repairs to the E-2 EDG control switch were completed in accordance with the Corrective Action Program (CR 177605).' 'Notification of the event to the NRC was initially made at 0125 on 9/26/03 (EN # 40198). Since the initial report, it was determined that a Technical Specification LCO 3.0.3 condition did not exist since the off-site sources were operable. This event has been entered into the site-specific corrective action program for resolution (CR 1776 10)." The licensee has informed the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS | VALID SPECIF SYS ACTUATION | INVALID SPECIF SYSTEM ACTUATION |  | Power Operation | Refueling |  | Power Operation | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(i) | 50.72(b)(3)(iv)(A) | 50.73(a)(1) |  | 0 | 2003-09-26
40197 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-09-24 14:55 | 2003-09-24 16:52 | 2003-09-24 | OFFSITE NOTIFICATION DUE TO RECOVERY OF LIVE SEA TURTLE Notifications will be made to the National Marine Fisheries Service and the Brigintine Marine Mammal Stranding Center due to a live sea turtle retrieved from the Oyster Creek dilution plant. This notification and report is required by the Oyster Creek Environmental Technical Specifications. The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-09-24
40196 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-09-24 00:53 | 2003-09-24 03:20 | 2003-09-24 | AUTOMATIC SCRAM AT SUSQUEHANNA ON LOW WATER LEVEL "At 0053 hours on September 24, 2003 with Susquehanna Unit 1 operating at 100% power an automatic reactor scram occurred due to low water level. At the time of the scram, reactor feed pump testing was in progress and the 'C' reactor feed pump tripped. The reactor recirc pumps runback initiated as expected when water level reached 30" with the feed pump tripped. Level continued to drop and reached the Level 3 auto scram setpoint. Level continued to drop and reached a low level of approximately -48" wide range. Reactor Core Isolation Cooling and High Pressure Coolant Injection auto started at their initiation setpoints and injected to the vessel to recover level. All level 2 and 3 containment isolations occurred as expected. The reactor recirc pumps tripped as expected when level 2 was reached. Reactor Pressure was controlled with bypass valves, there were no Safety Relief Valve lifts. There are no challenges to containment. "Unit 1 is currently stable in Mode 3 with both reactor recirc pumps restarted. A human performance error was the cause of the reactor feed pump trip. Investigation is continuing into the plant response to the reactor feed pump trip." The NRC Resident Inspector was notified of this event. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | ECCS INJECTION | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(iv)(A) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-09-24
40195 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-09-23 12:27 | 2003-09-23 15:15 | 2003-09-23 | SAFEGUARD SYSTEM VULNERABILITY DISCOVERED BY FT CALHOUN The licensee discovered a vulnerability in a safeguard system that could have allowed access to a controlled area for which compensatory measures had not been employed. The licensee has notified the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-09-23
40194 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-09-23 13:20 | 2003-09-23 15:04 | 2003-09-24 | UNUSUAL EVENT "While in Mode 5, refueling Shutdown with Core offload in progress a fuel assembly in the Spent Fuel Pool became ungrappled. The assembly is currently sitting on the top of the Spent Fuel pool racks resting against the Pool wall at approximately 15 degrees. There is no damage to the Fuel Assembly, evident by no change in area radiation dose rates. EAL 1.14, Plant Conditions Warrant Increased Awareness By Plant Staff or Government Authorities. An investigation has begun to determine the cause of the event and a team is being assembled to plan the fuel bundle recovery." The licensee notified the NRC Resident Inspector. * * * UPDATE ON 9/23/03 AT 1857 EDT FROM RANDY CABE TO GERRY WAIG * * * The licensee remains in a NOUE (Notice of Unusual Event) due to the ungrappled spent fuel assembly. The position of the spent fuel assembly remains the same as previously reported. No damage to the fuel assembly nor the spent fuel rack has been detected. No abnormal radiation readings have been observed. As a precaution, the licensee has suspended all fuel movement operations and evacuated the auxiliary and containment buildings. The licensee plans to stabilize the fuel assembly, attach a lifting tool, and place it into a permanent storage position in the spent fuel pool. Notified R4DO (Greg Pick) * * * UPDATE ON 09/24/03 @ 1414 BY CADE TO GOULD * * * At 12:42 CDT the fabricated stabilization device installation was completed and it is currently secured to two walls of the spent fuel pool. The plant will remain in a NOUE until the fuel assembly is lowered into a safe location in the spent fuel pool. A tool has been fabricated to grapple the fuel assembly and it will be moved with the Spent Fuel Pool Refueling Machine. The tool is currently being tested and weighed. All unnecessary personnel were moved from the Protected Area to the Administration and Training Buildings during the placement of the stabilization device. The NRC Resident Inspector was notified. Reg 4 RDO (Greg Pick) was notified * * * UPDATE ON 09/24/03 @ 1800 EDT BY RANDY CADE TO GERRY WAIG * * * The licensee reported that the ungrappled spent fuel assembly was placed in a permanent storage position in the spent fuel pool at 1654 CDT. As a result of this action, the licensee terminated the Notice of Unusual Event (NOUE) condition at this time. Normal access to the facility protected area and radiation control area has been restored. Fuel movement operations remain suspended and a root cause investigation of this event is being conducted. The licensee notified the NRC Resident Inspector. NRC R4DO (Greg Pick), DIRO (Richard Wessman), NRR EO (Gene Imbro), FEMA (Ken Sweetser), DOE (Joe Stanbaugh), DHS (Sam Neglia) were notified by the Headquarters Operations Officer. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-09-23
40193 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-09-23 10:00 | 2003-09-23 13:00 | 2003-09-23 | ARIZONA AGREEMENT STATE REPORT FOR DAMAGED GAUGE "On 23 September 2003, the licensee notified the Agency that a Humboldt Scientific moisture/density gauge, serial number 1136, had been run over by a roller at a construction site in the vicinity of interstate 8 and Avenue 3E in Yuma. The source was in the backscatter position at the time; however, the licensee was able to retract the source into its shielded position. A leak test is being performed. The Agency will continue to investigate. The gauge contains approximately 10 millicuries of cesium 137 and 40 millicuries of americium-beryllium. The NRC and Governor's office are being notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-09-26
40192 | 0 | OCONEE | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP,[3] B&W-L-LP | 2003-09-23 04:00 | 2003-09-23 11:15 | 2003-09-23 | UNANALYZED CONDITION DUE TO POTENTIAL RCS LEAKAGE AT OCONEE 1 "During a scheduled bare metal visual inspection of the Unit 1 reactor vessel head prior to RV head retirement, evidence of possible through wall leakage was observed on two control rod drive mechanism (CRDM) and one thermocouple (T/C) penetrations (nozzles 6 and 16 and T/C nozzle 7). Of these locations, only the T/C had been previously repaired (plugged) in December 2000. "Initial Safety Significance: Any RCS leakage from these penetrations would have been below the threshold of measurability by the reactor coolant system leakage measurement process. Total measured RCS leakage prior to unit shutdown was varying between 0.15 gallons per minute and .24 gallons per minute. "Corrective Action: The reactor vessel head is scheduled for replacement during the present refueling outage. Therefore, there are no plans at this time to perform additional inspections or repairs on the current head." The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-09-23
40191 | 0 | RIVER BEND | 1 |  |  | [1] GE-6 | 2003-09-22 22:43 | 2003-09-23 02:44 | 2003-09-23 | AUTOMATIC REACTOR SCRAM RECEIVED DURING MAIN TURBINE CONTROL VALVE TESTING "At 2243 on 9/22/2003 a Reactor scram occurred while performing Main Turbine control valve testing. Preliminary investigations indicate that high Reactor pressure was the signal that caused the scram. As a result of the scram, a Reactor low level 3 (9.7 inch) signal was received as expected from a high power scram due to the rapid coolant shrinkage. All expected actions for the low reactor level 3 (9.7 inch) signal occurred as expected. The plant is stable in Mode 3 (hot shutdown) with level being controlled with the Feedwater System and Reactor pressure being controlled with the Main Turbine Bypass valves." All control rods fully inserted, no ECCS actuations were received, and the electrical grid is stable. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 78 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 4 | LA | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-09-23
40190 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-09-22 03:00 | 2003-09-22 22:11 | 2003-09-22 | AGREEMENT STATE REPORT "The RSO reported by phone to Radiologic Health Branch (RHB), Granada Hills, that one of its portable nuclear gauges had been stolen the night of 9/21/03, between 2330 and 0630 [PDT], from the RSO's vehicle which was parked in a back parking lot at his apartment complex in Glendale, CA. The gauge is a CPN, Model MC-2, S/N M21073950, containing Cs-137 and Am-241 sealed sources, special form, 10 [millicuries] and 50 [millicuries], respectively. "Apparently, the RSO took two gauges home on 9/21/03 to drop one off at a job site for another operator and one for his use at another job site the next day. The RSO stated he stored the two gauges in the bed of his vehicle, locked down and concealed with a tarp. The morning of 9/22/03, the RSO found that one of the two gauges (his) was missing. The second gauge was not taken but had its case damaged. It seems that a 'hammer-like' tool also kept in the vehicle was possibly used to break in. "Note that this is the 2nd reported theft of a nuclear gauge for this licensee this year. The last one was reported stolen on 6/19/03 and then recovered on 7/7/03. "The RSO had already notified the Glendale Police Department and his company management. The RSO will be providing a written report shortly." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-09-25
40189 | 0 | TURKEY POINT | 3 | 4 |  | [3] W-3-LP,[4] W-3-LP | 2003-09-22 00:35 | 2003-09-22 15:07 | 2003-09-22 | TURKET POINT UNITS 3 & 4 FITNESS FOR DUTY REPORT A licensed employee was determined to be under the influence of alcohol upon entry into the plant access control point. Access to the facility was denied and the employee's access to the facility has been suspended. Contact the Headquarters Operations Officer for additional details. The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 26.73 |  |  |  | 0 | 2003-09-22
40188 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-09-22 | 2003-09-22 14:08 | 2003-09-22 | AGREEMENT STATE REPORT- ABANDONMENT OF WELL LOGGING SOURCES "[The] Company [Schlumberger Technology Corporation] has decided to abandon two sources downhole. Recovery operations have failed and sources will be cemented in place today. Two sources consist of: One (1) AEA Technology, Cs-137, 1.7 curie sealed source, Model GSJ, Serial No 180; and (1) Schlumberger Am-241/1Be, 16 curie sealed source, Model NSR-F, Serial No. 2355. Sources are stuck in the well, Recovery has not been possible. Source will be cemented in place at 11,755 feet and 11,742 feet respectively by 200 feet of red dyed cement with whipstock place as a deterrent to future drilling. Schlumberger is in the process of ordering a wellhead placard for placement on the wellhead." Texas Incident No.: I-8056. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-09-25
40187 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-09-20 10:45 | 2003-09-20 11:56 | 2003-09-20 | BOTH HOPE CREEK AND SALEM LOST ALL METEOROLOGICAL CAPABILITY This notification is for both Hope Creek and Salem stations pursuant to 10CFR50.72(b)(3)(xiii) as a major loss of emergency assessment capability, offsite response capability, or offsite communication capability; specifically, the loss of all meteorological data for Hope Creek and Salem stations. Meteorological data is supplied to both stations via a common communications lank. Data is transmitted to Hope Creek then relayed to Salem. The problem in the communication link has been isolated to a faulty computer, which supplies Hope Creek with data. Troubleshooting and repairs are in progress; a projected availability time is not yet available. The NRC Resident Inspector was notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-20
40186 | 0 | GEOTEST |  |  |  |  | 2003-09-18 | 2003-09-20 08:16 | 2003-09-22 | MISSING TROXLER GAUGE The licensee has not been able to locate their technician who has had a Troxler gauge in his possession since the evening of 09/18/03. The missing gauge is a Troxler 3440 serial #24340 containing 8 millicuries Cs-137 and 40 millicuries Am-241/Be. The licensee has been unsuccessful in contacting the technician at his various addresses. A police report was made with the Brentwood, MO Police Dept. * * * UPDATE ON 09/22/03 @ 06:57 BY EVANS TO GOULD * * * The gauge was found at one of the technician's residences on 09/20/03. It was intact and not damaged. The technician is still missing. Notified Reg 3 RDO(Lanksbury) and NMSS(Reamer) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-09-20
40185 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-09-19 20:41 | 2003-09-20 00:18 | 2003-09-20 | PLANT HAD AUTO REACTOR SCRAM FROM 100% POWER DUE TO LOW REACTOR WATER LEVEL AS RESULT OF A PARTIAL LOSS OF OFFSITE POWER "At 2041 hrs on 09/19/03, an electrical fault on 500 KV Bus Section 2 caused a Group A Transformer lockout. The Alpha and Charlie 4.16 KV vital busses did not transfer to their respective alternate infeeds from Group B Transformers, the associated Emergency Diesel Generators auto-started to supply their respective busses, and the associated Loss of Power sequencers initiated. This automatic electrical transfer caused a loss of the Alpha and Charlie Reactor Feedpumps due to a low hydraulic oil pressure signal, and Reactor level decreased to the low level RPS scram setpoint of 12.5 inches. All rods fully inserted in response to the RPS scram signal. Reactor water level dropped to approx. minus 25 inches and was subsequently returned to a normal level of 34 inches post-scram by the Bravo Reactor Feedpump. In addition, 7.2 KV Bus 10A110 failed to transfer to its alternate infeed breaker, and de-energized causing a loss of the Alpha and Delta Turbine Building Chillers, 00K107 Station Air Compressor, Alpha Primary Condensate Pump, Alpha Secondary Condensate Pump, and the Alpha Reactor Recirc Pump. The Alpha Fuel Pool Cooling and Cleanup Pump tripped during the electrical transient, and was subsequently restarted. The Alpha and Bravo Reactor Water Cleanup Pumps tripped during the electrical transient, and preparations are being made to restart the system. Core circulation is being supplied by the Bravo Reactor Recirc Pump. Reactor Pressure is being controlled by Turbine Bypass valves to the Main Condenser, and Reactor Pressure is 762 PSIG. Electrical Distribution personnel are inspecting Switchyard electrical components and relaying to determine the exact location and nature of the fault. Hope Creek-Salem 500 KV 5037 500 KV line has been isolated as a result of visual reports of arcing/tracking, and is considered a potential cause of the electrical transient. Forced outage team personnel have been assembled to review the event and develop a recovery plan. This event is being reported IAW 10CFR50.72(b)(2)(iv)(B) for the actuation of RPS on a low reactor water level signal and 10CFR50.72(b)(3)(iv)(A) due to the Emergency Diesel Generators start and sequencer initiation," Two (A&C) of four Emergency Diesels started and loaded to their busses. The B&D Emergency Diesels are available. The plant has two offsite power sources available, but only one is feeding the B&D vital busses. The NRC Resident Inspector was notified. * * * UPDATE ON 9/20/03 AT 1948 FROM A. BREADY TO E. THOMAS * * * "Salem Unit 1, Unit 2, and Hope Creek Shut Down. "After riding out Hurricane Isabel and supplying power to the PJM grid, Salem Units 1 and 2, and Hope Creek were shut down over the weekend due to salting in the switchyard. "High winds and rough surf in the Delaware River resulted in salt deposits in the 500 KV switchyards at Salem and Hope Creek. These deposits caused electrical faults and arcing in both switchyards. Hope Creek automatically shut down on Friday at 8:41 p.m. due to problems initiated by the switchyard. Salem Unit 1 and Unit 2 were manually taken off line Saturday morning at 3:44 a.m. and 4:37 a.m. respectively. "A team has been assembled to investigate the cause of the events. All three units will remain shutdown while the switchyards are cleaned and any necessary repairs are made. The cleaning of the salt from the switchyards has already begun." Notified R1DO (H. Gray), NRR EO (J. Calvo), and DIRO (T. McGinty) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-09-20
40184 | -1 | GINNA | 1 |  |  | [1] W-2-LP | 2003-09-19 18:00 | 2003-09-19 20:49 | 2003-11-18 | UNANALYZED CONDITION While shutdown in Mode 5, containment recirculation sump 'B' was inspected for sump screen bypass flow paths in accordance with the requirements of NRC Bulletin 2003-01. Inspection results showed that approximately 25 square inches of space is available for recirculation flow to bypass the sump screens. This condition has the possibility of affecting the containment spray, safety injection and residual heat removal systems. The plant is stable in a refueling outage at approximately 95 degrees F, with normal residual heat removal in service and loop levels at 72 inches. The licensee notified the NRC Resident Inspector. * * * UPDATE ON 11/18/03 @ 1356 BY RICHARD KAPP TO GOULD * * * RETRACTION The licensee is retracting this event after performing an extensive evaluation had determined that equipment required to mitigate the event, though found to be in a degraded condition, would have performed their functions. This event has been discussed with the NRC Resident Inspector and he was informed of the event retraction. Notified Reg 1 RDO(Rogge) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-09-19
40183 | 0 | DUANE ARNOLD | 1 |  |  | [1] GE-4 | 2003-09-19 | 2003-09-19 20:11 | 2003-09-19 | OFFSITE NOTIFICATION The licensee notified the Iowa Department of Natural Resources, Linn County Sheriff, and the U.S. Coast Guard National Response Center of a reportable spill of fuel oil into the Cedar River per applicable reporting procedures. Dredging operations were underway, and while refueling dredging equipment located on a barge in the Cedar River, approximately one gallon of fuel oil was spilled into the Cedar river. The licensee notified the NRC Resident Inspector, and will notify the state and local authorities. | 93 | 0 | 0 | 93 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | IA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-09-19
40182 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-09-19 16:00 | 2003-09-19 17:54 | 2003-09-19 | LOSS OF EMERGENCY SIRENS DUE TO STORM "At approximately 1535 [ET] on 9/19/03 the Susquehanna Control Room was notified that the 7.2 Kv supply line to the Tank Mountain repeater for activation of all emergency sirens was unavailable [approximately 121 sirens in Lucerne and Columbia Counties]. The backup batteries for the repeater were reported to be supplying power for repeater activation. Following further discussion with Emergency Planning personnel, Susquehanna LLC could not determine how long the battery supply would be available. At 1600 the ability to activate the emergency sirens was declared inoperable due to the inability to determine the status of the power source. Loss of ability to activate the emergency sirens is reportable under 10CFR50.72(b)(3)(xiii), Loss of Emergency Preparedness Capabilities, as an eight hour notification. The Susquehanna LLC Emergency Plan incorporates alternate means, i.e. Route Alert Teams, to notify the public during an emergency situation." The licensee notified the NRC Resident Inspector and will be notifying State and local agencies. * * * * UPDATE FROM R. FRY TO M. RIPLEY 2105 ET 09/19/03 * * * * "As of 2010 hours [ET] on 9/19/2003, power was restored to the repeater that is used for emergency siren activation and the emergency sirens are considered operable. The NRC resident inspector has been updated." The licensee will be notifying State and local agencies. Informed R1DO (H. Gray) | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40181 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-09-19 11:30 | 2003-09-19 15:45 | 2003-09-29 | LOSS OF SIRENS "A poll of the Surry EWS sirens was conducted to determine operability of the siren system (Reference Hurricane Response Plan - Nuclear, Section 5.6). The poll was conducted from the back-up status logger at Innsbrook due to the unavailability of the primary status logger in the Surry LEOF (see Plant Issue - S-2003-4152). "45 of the 67 sirens expected to respond to the siren polling are considered inoperable at this time due to power failure as a result of Hurricane Isabel (the status of 2 of these was indeterminate). 22 of the 67 sirens responded satisfactorily and are considered operational. "This is a reportable event per VPAP - 2802 Attachment 3 d. Early Warning System second bullet "More than 25 percent of all sirens are unavailable" and the third bullet "The capability to alert a large segment of the population does not exist." This discrepancy was discovered at 1130 EDT on 9/19/03. The licensee notified the NRC Resident Inspector, as well as state and local government officials. **** Update on 09/29/03 at 1524 EDT by Larry Wheeler taken by MacKinnon **** Currently Surry Unit 1 is at 100% power and Unit 2 is in Cold Shutdown. "Surry EWS sirens have been returned to operable status on September 29, 2003 following repairs due to weather related effects of a Hurricane Isabel. Presently 63 of 67 sirens have been returned to service (94%). All sirens located within the 5 miles portion of the EPZ are operable. The current availability of the EWS no longer constitutes a major loss of emergency assessment capability, offsite response capability, or offsite communication capability pursuant to 10 CFR50.72(b)(3)(xiii). "Information related to the return to service of these sirens is being transmitted to the State of Virginia and FEMA. This is the final report that will be issued relative to siren system restoration efforts following Hurricane Isabel. Normal siren system status monitoring practices will remain in effect going forward." R2DO (Mark Lesser) notified. The NRC Resident Inspector was notified of this update by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Shutdown | Hot Shutdown |  | Hot Shutdown | Hot Shutdown |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40180 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-09-17 13:00 | 2003-09-19 13:00 | 2003-09-19 | AGREEMENT STATE REPORT - MEDICAL EVENT "At approximately 1:00 PM September 17, 2003 the Agency was informed of a medical event. The reporting individual indicated that in the course of treating a breast cancer, a saline filled balloon was used to aid in positioning the HDR source, Iridium 192, approximately 9.589 curies. Starting September 15, 2003, a series of 10 fractional treatments was prescribed. Between each, an ultra sound image was made to assure the continued proper placement of the source. The ultra sound technician indicated all was ok for all treatments. After the series was completed, the balloon was deflated for removal and the physician then noted that the balloon had ruptured. A review of the retained ultra sound images indicated [that] starting with treatment 7 the balloon was deflated. The doses were recalculated and the tissue dose was 40 [percent] higher than prescribed. The adjacent skin dose was calculated to be 266 cGy [centigray] rather than the 175 cGy [centigray] as originally calculated. The licensee has proposed corrective measures to prevent a recurrence of this event. The balloon manufacturer has been informed of this event. "The patient has been informed of the event. The medical review indicates some additional fat necrosis and possible inflammation may occur. It will be reviewed as a part of the patient follow up." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-09-24
40179 | 0 | NORTH ANNA | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-09-19 09:30 | 2003-09-19 11:25 | 2003-09-24 | LOSS OF EMERGENCY SIREN CAPABILITY TO THE ADVERSE WEATHER CONDITIONS "At 0930 on September 19, 2003 it was identified that there was a major loss of offsite response capability. 43 out of 63 early warning sirens were determined inoperable due to loss of power as a result of Hurricane Isabel. "The State and NRC Resident Inspector will be notified of this event." *****UPDATE ON 9/24/03 AT 0715 FROM JOHNSTONE TO LAURA***** "On September 24, 2003, at 0715 hours, a siren poll test was conducted to verify availability of the early warning sirens (EWS). The test identified that 57 of 63 (90%) sirens were available. The current availability of the EWS no longer constitutes a major loss of emergency assessment capability, offsite response capability, or offsite communication capability pursuant to 10CFR50.72(b)(3)(xiii)" The NRC Resident Inspector was informed. Notified R2DO (C. Julian) | 100 | 62 | 0 | 100 | 62 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | VA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40178 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2003-09-19 02:24 | 2003-09-19 05:23 | 2003-09-19 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER CONDITIONS "TMI is notifying the NRC Operations Center in accordance with 10 CFR 50.72 (b)(2)(xi), Notification of Other Government Agency and 10 CFR 50.72 (b)(3)(xiii) Major Loss of Emergency Preparedness Capabilities. At 0224 AM on Friday, September 19 it was determined that 25 of 79 of the public emergency sirens for Three Mile Island Unit 1 were inoperable due to loss of power due to Tropical Storm Isabel. Subsequently, it has been determined that 32 of 79 of the sirens are inoperable. The inoperable sirens are located throughout the five risk counties around TMI. The inoperability of the sirens around TMI impacts a large segment of the population. "Contingency actions have been established for the deficient sirens. Automatic route alerting, that is the coordinated use of vehicles that will make loudspeaker announcements throughout affected areas will be utilized if the need should arise prior to restoration of power to the inoperable sirens. Local power company line crews have been notified of the loss of power to the sirens and are working to restore power on a priority basis to the sirens." The licensee informed the affected counties/PEMA and the NRC Resident Inspector. | 10 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION | LOSS COMM/ASMT/RESPONSE |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) | 50.72(b)(3)(xiii) |  |  | 0 | 2003-09-19
40177 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-09-19 01:45 | 2003-09-19 04:55 | 2003-09-19 | LOSS OF POWER TO THE TECHNICAL SUPPORT CENTER "Peach Bottom lost power to the TSC from 0145 to 0255 this morning due to a temporary loss of the Station Blackout Line (SBO). The SBO line, and subsequently power to the TSC, has been restored. The station meteorological data was lost due to the initial power loss with the SBO at 0145. The meteorological data remains out of service at this time. "Contingency plans exist for the use of an alternate TSC, if required. Use of data from local and national weather services is available in place of the station meteorological data. "Additionally, Peach Bottom has notified the FAA that power has been lost to the flashing lights at the top of high voltage towers in the river." The licensee informed the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Refueling |  | Cold Shutdown | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40176 | 0 | LIMERICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-09-19 04:00 | 2003-09-19 04:16 | 2003-09-19 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER CONDITIONS "32 of 165 offsite sirens not functioning due to loss of power/equipment failure because of ongoing storm." The licensee will inform the affected counties/PEMA and the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40175 | 0 | CALVERT CLIFFS | 1 | 2 |  | [1] CE,[2] CE | 2003-09-18 21:05 | 2003-09-19 01:41 | 2003-09-19 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER CONDITIONS A significant portion of emergency sirens (43 of 72) located in Calvert, St. Mary's and Dorchester county are unavailable due to a loss of power. Restoration is not expected until dayshift when the effects of Tropical Storm Isabel have abated. The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | MD | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40174 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-09-19 01:20 | 2003-09-19 01:22 | 2003-09-19 | SECURITY REPORT INVOLVING LIMITED SUSPENSION OF ICMS The licensee is implementing a limited suspension of Interim Compensatory Measures (ICMs) due to high sustained winds. The licensee will inform the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. * * * UPDATE 0455 EDT ON 9/19/03 FROM JIM WILSON TO S. SANDIN * * * The licensee has reimplemented all ICMs due to abatement of the adverse weather conditions. The licensee will inform the NRC Resident Inspector. Notified R1DO(Gray). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Cold Shutdown | Refueling |  | Cold Shutdown | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-09-19
40173 | 0 | SUSQUEHANNA | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-08-29 10:25 | 2003-09-19 01:07 | 2003-09-19 | INVALID ACTUATION OF CONTAINMENT ISOLATION VALVES "On August 29th, 2003 at approximately 1025 EDT, an electrical perturbation affecting both Unit 1 & 2 at PPL Susquehanna LLC resulted in a partial isolation of Primary Containment Isolation valves on Division 1, specifically A & B Containment Radiation Monitors and the Containment Instrument Gas Purge supply valve. "This event is being reported as an invalid system actuation and is reportable under 10CFR 50.73(a)(2)(iv)(A). The condition meets the criteria of 10CFR 50.73(a)(2)(iv)(B)(2) due to a general containment isolation signal that affected containment isolation valves in more than one system. This notification is being provided via 60 day optional phone call as permitted under 10CFR 50.73(a)(1) in lieu of a written LER. "The event was initiated when Operators were returning a Unit 1 13.8 KV Non-ESS breaker back in service following routine maintenance. When the breaker was restored to its closed position, a fault downstream of the breaker caused it to immediately re-open. The 13.8 Kv system supplies power to both unit's Division 14kV ESS busses. The perturbation was sufficient to cause several 'fail closed' containment isolation valves to actuate and close. The transient caused other non-safety related plant equipment to trip/auto-start, no other safety-related equipment or functions were lost. There also were no challenges to the reactor systems or containments. All plant equipment and/or systems were capable of being restored to their original alignment. The fault that caused the electrical perturbation originated at a non-ESS transformer and is currently being replaced." The licensee will inform the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-09-19
40172 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-09-18 21:11 | 2003-09-19 00:37 | 2003-09-20 | LOSS OF EMERGENCY SIREN CAPABILITY DUE TO ADVERSE WEATHER CONDITIONS "Due to the effects of severe weather related to Hurricane Isabel, local power outages have resulted in an excessive number of sirens within the Salem/Hope Creek 10-mile Emergency Protection Zone (EPZ) being unavailable. At 21:11 on September 18, 2003, 29 offsite sirens were unavailable (22 in Delaware and 7 located in New Jersey). As of 22:11, some sirens have been restored, but there are still 14 unavailable in Delaware and 7 unavailable in New Jersey. It is likely that the functionality of the EPZ sirens will continue to change due to the ongoing severe weather. Sirens will be recovered when power is restored. "This notification is being for both Salem Generating Station and Hope Creek Generating Station pursuant to 10CFR50.72(b)(3)(xiii) as a major loss of emergency assessment, offsite response, or communication capability. Salem Units 1 and 2 are operating at 100% power with all safety related equipment operable. "Hope Creek is operating at 94% power with all safety related equipment operable. Power is reduced due to the degraded performance of the non-safety related ventilation system that cools the Reactor Recirculation Pump Motor-Generator Sets." The licensee informed the NRC Resident Inspector. * * * UPDATEON 09/20/03 @ 1000 BY KOPCHICK TO GOULD * * * "There are currently 11 unavailable sirens within the Salem/Hope Creek 10-mile Emergency Preparedness Zone (EPZ) (6 in New Jersey and 5 in Delaware). The current availability of sirens no longer constitutes a major loss of emergency assessment capability, offsite response capability, or offsite communication capability pursuant to 10C'FR50.72(b)(3)(xiii). It is anticipated that all sirens will be rendered available as power is restored and storm recovery actions are completed. No further updates to this event report will be provided." The NRC Resident Inspector was informed. | 94 | 0 | 0 | 94 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-19
40171 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-09-18 20:00 | 2003-09-18 22:08 | 2003-09-19 | LOSS OF 27 OF 97 EMERGENCY SIRENS DUE TO STORM "Peach Bottom has been notified that 27 of 97 emergency sirens are out of service as a result of storm conditions. 15 of the sirens are located in southern Lancaster County. The other 12 sirens are located throughout York, Harford, and Cecil Counties. "The individual counties have been notified of the out of service conditions." The licensee has notified the NRC Resident Inspector and will be notifying State agencies. * * * UPDATE 0303 EDT ON 9/19/03 FROM BOB FRANSSEN TO S. SANDIN * * * Due to adverse weather conditions, the number of emergency sirens out of service has risen to 80. The affected counties and PEMA have been notified. The licensee will inform the NRC Resident Inspector. Notified R1DO(Gray). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Cold Shutdown | Refueling |  | Cold Shutdown | Refueling |  | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-18
40170 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-09-18 14:33 | 2003-09-18 15:43 | 2003-09-19 | LOSS OF MORE THAN 20% OF OFFSITE EMERGENCY SIRENS The following was received via fax from the licensee: "As of 2:33 PM EDT, more than 20% of the offsite emergency sirens were inoperable for greater than one hour due to loss of power caused by Hurricane Isabel. Currently 27 of 81 sirens are out of service. The State of North Carolina and all four counties within the 10-mile emergency planning zone were notified and are in stand-by to implement mobile route alerting if needed. At this time, Harris cannot estimate the time of siren recovery. This requires an 8-hour non-emergency notification per 10CFR 50.72(b)(3)(xiii) due to the loss of a significant portion of the offsite notification system. The NRC Senior Resident Inspector was informed." * * * UPDATE 0910 EDT ON 9/19/03 FROM JOHN CAVES TO S. SANDIN * * * The licensee is updating this report to include that less than 20% of the emergency sirens are inoperable as of 2000 hours 9/18/03. The licensee informed the NRC Resident Inspector. Notified R2DO(Boland). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-09-18
40169 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2003-09-16 | 2003-09-18 12:33 | 2003-09-18 | AGREEMENT STATE REPORT -- MISSING IODINE-125 SEEDS The following was received via email from the State of Illinois: "On 9/16/2003, the agency was contacted by [DELETED] RSO at the Chicago Prostate Cancer Center in Westmont, IL (IL-02015-01). He indicated that on 9/11/2003, a package of unused radioactive seeds was being prepared to be returned to Amersham Health/Medi Physics in Arlington Heights, IL. At that time they noted that the package contained only 6 'strands' of sources whereas the paperwork for receipt on 9/4/2003 indicated 7 'strands' of sources to be present. "The I-125 seeds are contained in a special rigid plastic carrier. This carrier has a marketing name of 'rapid strand'. Each 'strand' contains ten I-125 seeds in a rigid plastic holder which is then placed in a stainless steel holder with an opening at one end. When the seeds are in the holder, radiation readings are at or very near background levels of radiation. This holder has been sterilized at Medi Physics and as a result it is placed in a sealed pouch until it is ready to be used in the operating room. A full description with some diagrams can be found at http://www.hsrd.ornl.gov/sources/pdf/01360338.pdf. "The package containing the six strands of seeds was picked up by Federal Express and returned to Medi Physics on 9/17/2003. [DELETED], RSO of Medi Physics participated in the inspection of the package to be sure that the problem was not just an administrative error. His inspection did not turn up the missing 7th strand. An inspection of previously used shipping containers from this site that had been returned to Medi Physics did not result in the recovery of the missing strand either. [DELETED] also had production perform an accounting check as well to see if perhaps only 6 strands had been originally shipped as a mistake. The check showed no outstanding seeds or strands from that lot that could not be accounted for, or shipped to another client as a result of a substitution. "An agency inspector also visited the Chicago Prostate Cancer Center in Westmont on 9/17/2003 and attempted to locate the strand through radiation monitoring. He was not successful in recovering the strand. As a result, one strand containing a total activity of 5.94 [milliCuries] mCi (10 seeds with 594 micro Curie each) is missing. The licensee will continue its attempts to locate the missing seeds and will keep the agency updated with its efforts. The licensee was also advised that a written report is due to the Agency in 30 days." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-09-23
40168 | 0 | SURRY | 1 | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-09-18 09:00 | 2003-09-18 09:16 | 2003-09-18 | UNUSUAL EVENT DECLARED DUE TO EXPECTED SEVERE WEATHER At 0900 EDT the licensee declared an Unusual Event as a precautionary measure due to expected severe weather from hurricane Isabel. Current wind speed and direction is 10-15 mph sustained with gusting to 20 mph from the NNE direction. No additional staff other than those for the planned outage have been brought onsite. The licensee informed state/local agencies and the NRC Resident Inspector. * * * * UPDATE 1608 ET FROM T. HUFF TO M. RIPLEY * * * * As of 1600 ET, Surry Unit 1 commenced a power reduction of 200 mwe (100% to approximately 75% power) in anticipation of grid instabilities due to heavy weather. One of eight circ water screens is degraded due to river debris and its associated circulating water pump has been secured. On-site meteorological panels are out of service. Additionally, the Emergency Operating Facility (EOF) is out of service due to a loss of power. Notified R2DO (A. Boland). * * * UPDATE 2101 EDT FROM DUANE SHEPHEARD TO NATHAN SANFILIPPO * * * The following was received via fax from the licensee: "With Surry Power Station Unit 1 at approximately 75% reactor power and Unit 2 at 100% reactor power, a manual reactor trip was initiated on Unit 1 at 1728 and on Unit 2 at 1732, due to the loss of the '1G' and `2G' buses which supply power to all eight circulating water pumps for both units. The loss of the buses occurred during high winds and rain associated with Hurricane Isabel, although no hurricane force winds were onsite prior to or at the time of the event. A discretionary Notification of Unusual Event had been declared earlier at 0900 due to the severe weather. "On Unit 1, the 'B' inadequate core cooling monitor (ICCM) failed. The 'A' ICCM remained operable throughout. All control rods fully inserted and the shutdown margin for Unit 1 was determined to be satisfactory. On Unit 2, eight rod position indicators showed greater than 10 steps but less than 20 steps following the reactor trip. Emergency boration was initiated. All Unit 2 IRPIs [Individual Rod Position Indications] are currently indicating less than five steps and the shutdown margin was satisfactory. "Auxiliary feedwater automatically initiated as designed for both units on low low steam generator level following the trip. Primary RCS temperature decreased to approximately 543 and 538 degrees on Unit 1 and 2 respectively and was stabilized at 547 degrees. "No primary safety or relief valves were actuated during the event on either unit. As a result of the loss of the circulating water pumps, the emergency service water pumps were started to conserve intake canal level. After start, 2 out of the 3 emergency service water pumps tripped on high water temperature. The pumps were checked and restarted 14 minutes later. Also due to the need to conserve intake canal level, the main steam trip valves on both units were closed and primary temperature is being maintained by use of the secondary power operated relief valves. No indication of primary to secondary leakage exists on either unit, therefore no adverse radiological consequences resulted from this event. "Both units are currently stable at hot shutdown. At 1845, the 2G bus was energized and circulating water pumps were started. The emergency service water pumps were secured and are in standby. "This 4 hour and 8 hour report is being made for Surry Units 1 and 2 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A)." Notified R2DO (A. Boland), NRR EO (J. Calvo), DIRO (R. Wessman), FEMA (Chuck Bagwell), DHS (Colleen Wilson). * * *UPDATE AT 1948 EDT ON 9/19/03 FROM BILL SUMMERS TO E. THOMAS* * * The licensee terminated their unusual event due to the following conditions: - severe weather has left the area - both units are stable at hot shutdown on offsite power - 2 of 3 ESW pumps are operable, and the third ESW pump is being prepared for an operational test - 45 of 67 sirens remain inoperable, but the sirens will be restored when power to the grid is restored The licensee will notify the NRC Senior Resident Inspector, as well as state and local officials Notified R2DO (Boland), NRR EO (Calvo), DIRO (McGinty), FEMA (M. Eaches), DHS (D. Licastro) | 0 | 0 | 0 | 75 | 100 | 0 | -1 | -1 | 0 | M/R | M/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | Power Operation | Power Operation |  | Hot Shutdown | Hot Shutdown |  | UNUSUAL EVENT | 2 | VA | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-09-18
40167 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-09-17 17:00 | 2003-09-17 17:35 | 2003-09-17 | SAFEGUARDS EVENT The licensee discovered a vulnerability in a safeguard system that could allow unauthorized access to a controlled area. Compensatory actions have been taken. The licensee contacted the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFEGUARDS REPORTS | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | 73.71(b)(1) |  |  |  | 1 | 2003-09-18
40166 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2003-09-17 17:35 | 2003-09-17 17:44 | 2003-09-17 | HURRICANE FORCE WINDS WITHIN 500 NAUTICAL MILES OF PLANT The Indian Point Unit 2 Technical Specification 3.14.A requires prompt notification of the NRC when hurricane force winds are within 500 nautical miles of the plant. Indian Point will continue to monitor the situation and update as necessary. The licensee has notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2003-09-17
40165 | -1 | FT CALHOUN | 1 |  |  | [1] CE | 2003-09-17 08:43 | 2003-09-17 10:29 | 2003-09-19 | POST ALERT EMERGENCY DECLARATION BASED ON CALCULATED RCS INVENTORY LOSS "The plant is currently in Mode 5 for a Refueling outage. Reactor Coolant System (RCS) level was being maintained just below the Reactor Vessel flange, 1012.33 feet, with Shutdown Cooling in service and Shutdown Cooling Purification in service. RCS temperature was 100F. At 0821 a lowering level was noted on the Control Room level indications LI-119 and LI-197. At 0824 Shutdown Cooling Purification was secured and the lowering level was stopped with an indicated RCS level 1010.33 feet. At 0843 it was determined that approximately 1350 gallons of RCS water was lost over the 3 minutes that the event lasted. It was determined that during that time conditions existed to enter EAL 1.4, RCS leak greater than 40 gpm. At no time was Shutdown Cooling lost and RCS temperature remained at 100F. At 0825 Abnormal Operating Procedure (AOP-19) was entered. Makeup to the RCS was initiated immediately and level was completely restored at 0842 with charging pumps secured. It has not been determined at this time where the inventory went. A walkdown of the Containment and Auxiliary Building has been completed. "At this time the plant is stable with an RCS level on 1012.5 feet." The licensee is conducting an investigation and will provide an update to this report. The licensee informed both the State of NE and IA and the NRC Resident Inspector. * * * UPDATE AT 1109 EDTR ON 09/19/03 FROM ERICK MATZKE TO S. SANDIN * * * The licensee is retracting this report based on the following: "On September 17, 2003, the Fort Calhoun Station notified the NRC that conditions had existed, for about 3 minutes, to make an alert notification. No alert was declared as the time the station was in the condition was such, a limited time. The condition that required the notification was a reactor coolant system (RCS) leak of >40 GPM. The event occurred as follows: "At approximately 0821 on September 17, 2003, Operations noted decreasing level in the reactor vessel. This was indicated on both of the shutdown RCS level indicators. Due to the uncontrolled (indicated) reduction in RCS level, AOP-19 was entered. Within minutes, the indicated level had dropped from 1012' 6" to 1010' 3". Shutdown cooling purification was isolated. The two (2) charging pumps running for shutdown purification were left in operation. After a few minutes, the charging pump's 80 gpm flow caused the RCS level to stop dropping and RCS level began to rise. During and immediately following this event, numerous walkdowns of containment and the auxiliary building were performed that ensured there was no loss of water from the RCS. No coolant leakage was noted during the walkdowns. "The cause of the level change was small pressure in the head making the indication read higher than actual. Disconnecting the HJTC clamp allowed a positive vent which caused indicated level to fall. When interviewing the craft performing the work on the HJTC, it was noted that when removing the clamp front a HJTC, the craft noticed a small amount of water bubbling on the HJTC and when an attempt was made to lift the HJTC hub, air was heard in the vicinity of the HJTC. Additionally the craft stated there was some resistance felt from the HTJC when attempting removal. The craft then contacted radiation protection to determine what personnel protection was required. On the second attempt to lift the hub, the craft heard air flow in the vicinity again. When the clamp was finally lifted there was little resistance. It is suspected that the air at the HJTC was due to a pressure differential between the vessel and the containment atmosphere. The higher pressure in the reactor vessel caused level indications to read higher than actual level by approximately 2 feet. When the HJTC flange opened, the change in pressure caused a redistribution of water levels in the RCS. This caused the indicated RCS level change. "There was never a leak of RCS coolant outside of the RCS. Therefore, this event notification is being retracted." The licensee informed the NRC Resident Inspector. Notified R4DO(Gody). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | ALERT | 4 | NE | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-09-17
40164 | 0 | BRUNSWICK | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-09-16 22:40 | 2003-09-16 23:17 | 2003-09-18 | UNUSUAL EVENT AT BRUNSWICK DUE TO HURRICANE WARNING "Hurricane warning issued. There is no significant impact to the safety of the plant at this time. The plant area is not currently experiencing any unusual winds. Unit 1 is at 94% and Unit 2 is at 96% power." The wind speed at the site is 14 miles per hour at the time of this report. The NRC Resident Inspector was notified by the licensee. * * * UPDATE ON 09/18/03 AT 1753 EDT FROM FRANK RAMPERSAD TO NATHAN SANFILIPPO * * * Brunswick has terminated the Unusual Event at 1740 EDT. This is based upon the hurricane warning being lifted. The licensee has notified the NRC Resident Inspector. Notified Wessman (DIRO), Boland (R2DO), FEMA (C. Bagwell), DHS (C. Wilson), Calvo (NRR EO). | 94 | 96 | 0 | 94 | 96 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | UNUSUAL EVENT | 2 | NC | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-09-16
40163 | 0 | U.S. ARMY TACOM |  |  |  |  | 2003-07-19 | 2003-09-16 16:14 | 2003-09-16 | UNCONTROLLED RELEASE OF TRITIUM FROM M109 HOWITZER U.S. Army Tank-automotive and Armaments Command (TACOM) was notified by U.S. Army Communications-Electronics Command (CECOM) on September 16, 2003 of an accident at Fort McCoy, WI on July 19, 2003. On July 19th, a M109 howitzer was being transported by a HumV when the HumV rolled over. Responders to the scene of the accident observed no physical damage to the M14 quadrant of the howitzer, which contains 2.2 Curies of tritium. Since no physical damage was observed, no wipe test was performed. On or near September 10, 2003, the howitzer was sent to a combined support maintenance shop (CSMS) for repair. At the CSMS site, a wipe test was performed on the quadrant (per procedure: prior to any repair on tritium fire control devices, a wipe test is performed). The quadrant was wipe tested on September 15, 2003 at a location inside the dial cavity and showed removable tritium contamination at 300,000 decades per minute. CECOM reported the incident to TACOM on September 16, 2003. Direction was given by TACOM to remove the device from the M109 howitzer, double bag it, and transfer to waste disposal. The area on the howitzer where the M14 quadrant was mounted is to be decontaminated and retested. Leak test results will be forthcoming from the CECOM lab to TACOM. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | UNPLANNED CONTAMINATION | [9 empty] | NON EMERGENCY | 3 | IL | MAT |  | 30.50(b)(1) |  |  |  | 0 | 2003-09-16
40162 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-09-16 09:18 | 2003-09-16 12:35 | 2003-09-16 | OFFSITE NOTIFICATION TO OSHA AT SEABROOK REGARDING A FATALITY "A contract employee, apparently suffered a heart attack, while in processing for Refueling Outage 09. The employee was treated by the site EMTs and transported to the hospital. It was subsequently reported that the employee passed away. Notification that the employee expired was at 11:03 EST." The licensee notified OSHA as required for a heart attack fatality. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-09-16
40161 | -1 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2003-09-16 00:30 | 2003-09-16 08:16 | 2003-11-11 | REACTOR COOLANT SYSTEM PRESSURE INCREASE CAUSED A VALID SIGNAL "At 1150 hours on 9/15/03 during Reactor Coolant System (RCS) pressure increase to approximately 700 psig, the Core Flood (CF) Tank 1 outlet motor-operated valve (CF1B) opened when the breaker for the valve was closed. Because RCS pressure was not high enough to actuate the pressure switch setpoint of 770 psig to open this valve, it was believed this was an invalid signal, and therefore the valve opening was not reportable under the criteria of 10 CFR50.72 "After further review, at 0030 hours on 9/16/03 it was determined the sensed pressure was within the setpoint range of the switch, making this a valid signal to open the valve. The CF Tank pressure at the time (approximately 600 psig) was less than the RCS pressure of approximately 700 psig, therefore no discharge into the RCS occurred, and this event is not reportable per 10 CFR50.72(b)(2)(iv). "The CF System is a passive system, but is used in conjunction with other Emergency Core Cooling Systems to mitigate significant events. Therefore, this event involving the opening of the CF Tank discharge valve CF1B is being conservatively reported in accordance with 10 CFR50.72(b(3)(2)(iv)(A) as a valid actuation of a train of the Emergency Core Cooling System. "Upon opening of this valve, CF Tank 1 level and pressure were observed lowering with a corresponding rise in the Reactor Coolant Drain Tank, most likely due to leakage past a check valve. CF1B was closed according to procedures and the source breaker for the valve opened." The NRC Resident Inspector was notified by the licensee. *** RETRACTION on 11/11/03 at 1643 EST by R. Walleman to MacKinnon **** "The actuation of the interlock for the Core Flood Tank 1 Outlet Isolation Valve did not constitute an actuation of the Core Flood System. The valve opened automatically as designed to ensure the Core Flood System was capable of performing its safety prior to being manually opened by the Operators. As part of the Emergency Core Cooling Systems, the primary function of the Core Flood System is to deliver cooling water to the reactor core in the event of a Loss of Cooling Accident per the Updated Safety Analysis Report. However, plant conditions (namely, Reactor Coolant System pressure lowering below Core Flood Tank pressure) did not exist that would have required the Core Flood System to perform its safety function. Therefore, the automatic opening of this valve does not constitute the actuation of the Emergency Core Cooling System, so this event is not reportable per 10CFR50.72(b)(3)(iv)(A). Therefore, NRC Event Number 40161 is retracted." R3DO (Anne Marie Stone) & NRR EO (Herb Berkow) notified. The NRC Resident Inspector will be informed of this retraction by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Hot Shutdown; FMode1: Hot Shutdown | NON EMERGENCY | 3 | OH | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-09-16
40160 | 0 | UTAH DIVISION OF RADIATION CONTROL |  |  |  |  | 2003-09-15 15:52 | 2003-09-15 18:25 | 2003-09-15 | UTAH AGREEMENT STATE REPORT ON MEDICAL EVENT "A patient was administered 15 millicuries of I-131 sodium iodide rather than 4 millicuries for a post-ablation scan. The administrative dosage differed from the prescribed dosage by more than 20% of the prescribed dosage." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | UT | OTH | AGR |  |  |  |  | 0 | 2003-09-18
40159 | 0 | SEABROOK | 1 |  |  | [1] W-4-LP | 2003-09-15 | 2003-09-15 16:40 | 2003-09-15 | PART 21 ISSUE AT SEABROOK ON SPENT FUEL POOL TEST COUPONS The licensee reported an apparent abnormality involving Boral spent fuel pool test coupons. Westinghouse built the spent fuel pool racks using Boral material manufactured by ARR Inc. Specifically, inspection of test coupons revealed bulging or blistering of the aluminum cladding. The information provided by the licensee does not include any other affected plants. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNSPECIFIED PARAGRAPH |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NH | POW |  | 21.21 |  |  |  | 0 | 2003-09-15
40158 | 0 | PEACH BOTTOM | 2 | 3 |  | [2] GE-4,[3] GE-4 | 2003-09-15 02:39 | 2003-09-15 03:06 | 2003-09-15 | DUAL UNIT REACTOR SCRAM. DISCRETIONAY UNUSUAL EVENT DECLARED "A discretionary UE has been declared for PB (Peach Bottom) U/2 (Unit 2) and U/3 (Unit 3) due to a dual unit transient that has resulted in both unit's scramming with a Group 1 (Main Steam Isolation Valve closure) PCIS isolation. "An electrical transient caused all 4KV emergency buses to be powered by the diesel generators. One diesel generator (E2) subsequently tripped leaving 6 of 8 (3 per unit) buses energized. "Off-site power is available. Preparations for transfer back to off-site power is in progress. The U/3 (Unit 3) "D" SRV (Safety relief valve) opened and did not close until electrically deenergized. The SRV is closed at this time.' Both reactors scrammed at 0132 EDT. NRC Resident Inspectors, State and Local were notified by the licensee. * * * Update 09/15/03 at 1055 EDT by McClellan to MacKinnon * * * Unusual Event for Peach Bottom Nuclear Power Station Units 2 & 3 was terminated at 1046 EDT. Unusual Event was terminated because plant conditions have been stabilized, offsite electrical power has been restored to the plant and both plants being in cold shutdown in Mode 4. An investigation is in progress. State and Local will be notified by the licensee. R1DO (M. Shanbaky), NRR EO (C. Holden), DIRO Manager (Doug Weaver), FEMA (Jim Dunker), DHS (Mark Babb) & R4DO (T. Gody) notified. The NRC Resident Inspectors are onsite and have been informed of the termination of the unusual event by the licensee. | 0 | 0 | 0 | 100 | 91 | 0 | -1 | -1 | 0 | A/R | A/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | Power Operation | Power Operation |  | Hot Shutdown | Hot Shutdown |  | UNUSUAL EVENT | 1 | PA | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-09-15
40157 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-09-14 05:49 | 2003-09-14 09:04 | 2003-09-14 | SLIGHTLY CONTAMINATED WORKER TRANSFERRED TO THE HOSPITAL FOR HEAT STRESS At about 0549, Sunday, September 14, 2003 a slightly contaminated worker who was exhibiting heat stress symptoms was transported to an off-site medical facility for treatment. The worker was very slightly contaminated on both the forearms and elbows. The worker has been treated and is being observed prior to being released. No contamination was spread off-site. Licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2003-09-14
40156 | 0 | FT CALHOUN | 1 |  |  | [1] CE | 2003-09-12 20:55 | 2003-09-13 01:10 | 2003-09-13 | MANUAL REACTOR TRIP DUE TO UNANTICIPATED NEGATIVE AXIAL SHAPE INDEX (ASI). "This report is being made pursuant to 10 CFR 50.72(b)(2)(iv)(B) due to manual initiation of the RPS, although briefed, was not part of any written pre-planned sequence. The unanticipated negative ASI response that began to approach RPS APD trip settings drove the decision to manually initiate an RPS trip. "Fort Calhoun Station Unit 1 was being shutdown for a planned refueling outage. During scheduled power shutdown at 3% per hour, ASI was trending more negative (power shifting to top of core) than expected. Reactor Engineering was contacted about the trend at 67% reactor power on September 11, 2003. New guidance was issued, however negative ASI trend continued. RPS Axial Power Distribution (APD) pretrip/trip setpoints were -0.55/-0.58 ASI Units. Below 15% power APD trips are bypassed. Operations briefed the continued power descension with manual trip criteria being the receipt of any 1 of 4 APD pretrip setpoints. "At 15.8% delta T power it became apparent that with ASI approaching APD pretrips (-0.5305 ASIU recorded), an Automatic Trip could be initiated if the downpower continued. At 2055 on September 12, 2003, with power at 15.8% delta T, a briefing was conducted and an manual reactor trip was initiated by tripping the Primary RPS Trip pushbutton on Control Board-4. "Operations entered EOP-00, "Standard Post Trip Actions" and transitioned to EOP-01, "Reactor Trip Recovery" with all safety functions verified. EOP-01 was exited at 2200 hours and the plant entered OP-3A, "Plant Trip". The plant is currently stable in Mode 3 with RCS Tave at 535 degrees F. "The only abnormal plant response noted was a feedwater side relief valve lifted and failed to fully reseat on FW-16A, High Pressure Feedwater Heater. The relief valve was cycled by maintenance and was reseated approximately 10 minutes after opening." The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 16 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | NE | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-09-13
40155 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-07-30 | 2003-09-12 16:44 | 2003-09-12 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE A Troxler Model 3411, Serial No 10540, containing two sealed sources: 1.48 GBq/40mCi (+/- 10%), Am-241:139, Serial No. 46-1962 and 0.30 GBq/8 mCi (+1-10%), Cs-137, Serial No. 40-7974, was stolen from an employee's truck at his residence. The cable securing the case had been cut and the case pried open with the gauge, calibration (standard) block and gauge paperwork removed. A police report was submitted to the San Antonio Police Department. Texas Incident No.: I-8051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-09-17
40154 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-09-09 | 2003-09-12 12:39 | 2003-09-12 | AGREEMENT STATE REPORT INVOLVING A RECOVERED SOURCE "At 4:30 pm on 9/9/03 the radiation alarm pegged at off scale at the Keller Canyon Land fill from a load of trash from the Contra Costa Transfer Station. The facility's Bicron probe indicated (off scale) on the drivers side of the truck. The passenger side probe was fluctuating above normal but not off scale. [DELETED], the Operations Manager informed RHB Berkeley of the radiation alarms and that Contra County Environmental Health had also been notified. Based upon this conversation it was determined that the truck will be secured in a restricted area and access will be restricted and warning tape and signs will be used. Arrangements were made to visit the facility on 9/10/03 to determine the cause of the radiation alarms. "The facility was visited on 9/10/03 and after surveys it was determined the source of the radiation alarms was cesium 137. The maximum reading on side of the dump truck was 2.5 milliRem/hr and 0.7 mRem at one meter using an Eberline RO 20 Calibrated 4/03. A Bicron Fieldspec was also used and it was determined that radiation was from cesium 137 based upon the 662 kev gamma photon. The truck was moved to an isolated area and the driver using hydraulics pushed the load out as while surveys were conducted to indicate when the source of radiation had left the truck. Based upon the identification of cesium 137 a sealed source was suspected. After the surveys indicated the source of the radiation was on the ground, rakes and wood were used to move the trash to identify the location of the source. Following surveys and raking, a small one inch cylinder or rod was identified as the source of the radiation readings. The source resembled the end of a moisture density gauge source rod. Based upon surveys it was calculated that the source contained about 8-10 milliCuries of cesium 137. Using tools the rod was placed in a lead pig and transported to CPN for further investigation. The investigation will try to determine if the rod was cut or broken off the source rod and if the serial number on the source can be used to locate it's previous owner. Surveys of the load and truck using a Ludlum Survey meter with a pancake G-m model 44-9 probe indicated their was no contamination from the source. CPN will also perform a leak on the source. "Troxler and Pacific Nuclear were also contacted to see if there were any unusual requests for a new source rod in the last six months. Both companies indicated they were not aware of any such requests. Further information will be provided following this investigation. "The engraved source capsule serial number is CDCW 556, 9290. This information has been reported to Troxler, Rancho Cordova, who will report it to the RSO, Troxler, North Carolina, where source/gauge/customer files are kept." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-09-17
40153 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2003-09-12 05:31 | 2003-09-12 07:04 | 2003-09-12 | ALERT DECLARED DUE TO RELEASE OF ANTIMONY PENTAFLOURIDE Ken O'Brien, NRC R3 Chief of the Fuels Cycle Branch, called at 0704 EDT to inform us that Honeywell had a chemical release and they had declared an Alert at 0531 CDT. There was no radiological release associated with this event. The event occurred when a plant employee attempted to obtain a sample from a tank of antimony pentaflouride. During the sampling process, the tank was inadvertently over pressurized and was vented outside of the building to atmosphere. The winds in the area during the release directed the chemical away from town. The building was isolated and the tank reduced to sub-atmospheric pressure by the plant response personnel. Their were no injuries as a result of the incident. An all-clear was given at 0655 CDT and the Alert was terminated at 1114 CDT. The Paducah Gaseous Diffusion Plant NRC Resident Inspector was notified by Honeywell. Notified the following federal agencies: FEMA(Caldwell), HHS-CDC(Davidson), DHS-DOE Desk(Yates), DOE(Turner), USDA(Thomas), NRC-EPA(Baumgarner). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | EMERGENCY DECLARED | [9 empty] | ALERT | 3 | IL | FUE |  | 40.35(f) |  |  |  | 0 | 2003-09-12
40152 | 0 | WESTINGHOUSE ELECTRIC CORPORATION |  |  |  | URANIUM FUEL FABRICATION | 2003-09-12 10:32 | 2003-09-12 10:32 | 2003-09-12 | IMPROPER SCANNING OF LEAD RODS FOR THE PRODUCT ENGINEERING LABORATORY NRC BULLETIN 91-01 24 HOUR NOTIFICATION FACILITY: Westinghouse Electric Company, Commercial Fuel Fabrication Facility, Columbia SC, low enriched (<5.0 wt,% U-235) PWR fuel fabricator for commercial light water reactors. License: SNM-1107. TIME AND DATE OF EVENT: April 4, 2001 - -- September 5, 2003 REASON FOR NOTIFICATION: Lead-filled rods in a small number of replica fuel assemblies were scanned using an improper instrument. The rods were to be verified as free of uranium prior to delivery to the Product Engineering Lab. The verification is accomplished by either scanning each individual rod with a hand-held instrument or scanning an assembly with a combination of a thimble tube probe and an external hand-held instrument. A few of the hand-held scans were performed with a marginal instrument. DOUBLE CONTINGENCY PROTECTION: Double contingency protection for the VIPER test loop vessel is assured by preventing uranium with greater than 1.0 weight percent uranium-235 from entering the Product Engineering (PE) Lab and preventing that uranium from entering the VIPER test loop vessel. Although lead-filled rods are not tested in the VIPER test loop, the improper scans left less than previously documented double contingency protection for the system. In accordance with Westinghouse Operating License (SNM-1107), paragraph 3.7.3 (c.5), this event satisfies the criteria for a 24-hour notification. AS FOUND CONDITION: See "Reason for Notification" above. NCS detected the absence of a procedure number listing during a normal special routing review. Inquiries led to the discovery that the incorrect instrument was being used to scan lead-filled rods. It was subsequently determined that the response of the instrument used was inadequate to reliably detect a single uranium rod mixed with lead-tilled rods. The initial investigation revealed a weakness in the procedure structure for scanning lead-filled rods. The procedure steps for scanning lead-filled rods are contained in a procedure for transfer and release of potentially contaminated equipment or materials and not addressed in the instrument procedures. SUMMARY OF ACTIVITY: 1). An improved procedure is now in place requiring that all lead-filled rods be individually scanned with the appropriate instrument. 2). All health physics personnel have been trained on the new procedure and proper instrument. CONCLUSIONS: 1). Loss of double contingency protection occurred. 2). At no time was the health or safety to any employee or member of the public in jeopardy. No exposure to hazardous material was involved. 3). The Incident Review Committee (IRC) determined that this is a safety significant incident in accordance with governing procedures. 4). Notification was the result of a weakness in the procedure structure, not a deficient NCS analysis. 5). A causal analysis will be performed. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 2 | SC | FUE | [5 empty] | 0 | 2003-09-12
40151 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-09-11 08:45 | 2003-09-12 02:36 | 2003-09-12 | DOUBLE CONTINGENCY WAS NOT MAINTAINED FOR NON-FISSILE NAMs. NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 0845 on 9/11/03, it was discovered that non-fissile negative air machines (NAMs) were not verified by two individuals to contain approved and properly installed filters, as specified in NCSA GEN-09, "Operation and Maintenance of Negative Air Machines". Procedure CP4-GP-BG2108, "Negative Air Machine and in-place HEPA System Internal Inspection and Filter Replacement", did not adequately flowdown requirements specified in NCSA GEN-09 was revised to make non-fissile portable negative air machines (NAMs) readily available for fissile use in emergency situations. Contrary to requirements specific in NCSA GEN-09, procedure CP4-GP-BG2108 did not include requirements for two individuals to perform independent verification that approved filters are selected and properly installed. This control prevents mass loadings of fissile material that are outside the scope of that analyzed in NCSE KY/S-249. SAFETY SIGNIFICANCE OF EVENTS: Double contingency was not maintained for non-fissile NAMs because the second verification was not performed. However, the non-fissile NAMs were not used for fissile material releases. The non-fissile NAMs have been subsequently verified to contain approved and properly installed filters. POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO(S) OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, a non-fissile NAM would have to be used in a fissile material release and greater than a safe mass of uranium would have to accumulate within the NAM in a configuration favorable for criticality. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.): Double contingency for the accumulation of an unsafe fissile mass is maintained by implementing two controls on mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL (INCLUDE PROCESS LIMIT AND % WORST CASE CRITICAL MASS): This system has a process limit of (xx) wt% U235. NUCLEAR CRITICLITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on one individual verifying and documenting that approved filters are selected and properly installed. This control prevents loadings of fissile material that are outside the scope of that analyzed in NCSE KY/S-249. This verification was performed, therefore, this control was maintained. The second leg of double contingency is based on a different individual verifying and documenting that approved filters are selected and properly installed. This control prevents loadings of fissile material that are outside the scope of the analyzed in NCSE KY/S-249. Because this verification was not performed, this control was lost. No events have occurred to introduce fissile material into any non-fissile NAMs. Therefore, though the control was violated, the parameter was maintained. Since double contingency is based on two controls on one parameter, and one control was violated, double contingency was not maintained. CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: 1. Non-fissile Nams verified to contain the correct filters and installed in the correct orientation. Completed 9/11/2003. 2. Procedure CP4-GP-BG2108 placed on hold pending revision to include independent verification requirements specific in NCSA GEN-09. Completed 9/11/2003. The NRC Senior Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-09-12
40150 | 0 | U.S. INSPECTION SERVICES |  |  |  |  | 2003-09-09 19:30 | 2003-09-11 16:46 | 2003-09-11 | PERSONNEL OVEREXPOSURE The RSO reported that on 9/9/03 an employee radiographer received a radiation exposure of 14.15 Rem whole body and 13.445 Rem shallow dose (by film badge data received 9/11/03) during pipe weld radiography for a piping fabricator's job site in Charleston, WV. A second employee received a dose of 627 millirem whole body and 613 millirem shallow dose (by film badge). No health-related symptoms have been noted by either employee. Following a radiography shot of a pipe weld, and after the source was thought to have been retracted, the equipment was being setup for a shot of the next weld. When the source was to be exposed for the second shot, it was discovered that the source had actually been exposed (probably fully) during the estimated 7-minute setup time. Both employees were wearing dosimeters which were found off scale and were wearing rad alarm devices set at 500 millirem/hr which they stated did not alarm. Additionally, the employees stated that a radiation survey was performed during the setup with no excessive radiation levels detected. The local RSO checked the survey meter and the radiography equipment and found nothing wrong. The radiography camera is an AEA Sentinal Model 660B (20.6 Curies Ir-192). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | PERS OVEREXPOSURE/TEDE >= 5 REM | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 20.2202(b)(1) |  |  |  | 0 | 2003-09-11
40149 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-09-11 12:00 | 2003-09-11 16:11 | 2003-09-11 | STOLEN SOIL DENSITY MOISTURE GAUGE The following information was provided via facsimile: "On September 11, 2003, and prior to 6:00 AM, a soil density moisture gauge was stolen from the back of a pickup truck located at (Deleted), Mesa, AZ. The gauge is a Troxler Model 4640, Serial Number 2443 and was contained in a yellow shipping container. It was reported that the gauge was originally chained and locked in the rear of the pickup bed and the chain and lock were missing. This Agency was notified and the Mesa Police are investigating. The company is offering a $500.00 for information leading to the recovery and return of the gauge. "The initial investigation indicates that several violations may have occurred. "The Agency and licensee's will continue to investigate this occurrence and report further. The U.S. NRC, FBI, Mexico, and the states of Colorado, Nevada, Utah, New Mexico and California are being informed of the incident." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-09-16
40148 | 0 | HUNTINGTON TESTING CO. |  |  |  |  | 2003-09-10 11:45 | 2003-09-11 12:40 | 2003-09-11 | RADIOGRAPHIC EXPOSURE DEVICE FAILURE On 9/10/03 at approximately 12:45 CDT, the slide bar associated with the posi-lock interlock device on an AEA Technology Model 660B (S/N B1215) radiography camera became stuck such that the source could not be repositioned following retrieval. The camera was being used at a Steel Forgings facility in Shreveport, LA. The source (40 Curie Ir-192) was in the secured position within the camera at the time. No personnel exposures occurred. The slide bar was subsequently freed up, however a replacement control device has been sent to the job site. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2003-09-11
40147 | 0 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-09-11 00:40 | 2003-09-11 02:40 | 2003-09-11 | OFFSITE NOTIFICATION MADE TO PENNSYLVANIA EMERGENCY MANAGEMENT AGENCY (PEMA) "At 2314 EDT on 9/10/03 a fire was reported at the Unit 1B Reactor Feed Pump. The Fire Brigade was activated and the fire was extinguished at 2322 (8 minutes after identification). To support removal of the feed pump from service reactor power was reduced to 63%. Due to notifying the Pennsylvania Emergency Management Agency (PEMA) and other outside agencies, this event is being reported under 10CFR50.72(b)(2)(xi)." The NRC Resident Inspector was notified by the Licensee. | 63 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-09-11
40146 | -1 | MONTICELLO | 1 |  |  | [1] GE-3 | 2003-09-10 17:46 | 2003-09-10 21:02 | 2003-11-07 | UNANALYZED CONDITION DUE TO A POTENTIAL BREAK IN FIRE PROTECTION WATER SYSTEM "Potential break of Fire Water Main in Admin Bldg could cause both divisions of Safe Shutdown equipment to be inoperable by flooding the battery rooms for #11 & 12 125VDC Batteries. Vulnerable section of piping has been isolated to eliminate the flooding concern. Fire Protection compensatory actions have been established in accordance with the site Fire Protection Program." The licensee informed the NRC resident inspector. * * * RETRACTION FROM PFEFFER TO GOTT AT 1242 ON 11/7/03 * * * "Monticello is retracting the event reported based on evaluations which indicate that the fire main is not considered a potential flooding source. Additional evaluations are ongoing, and issues will be entered into the station's corrective action program." The licensee has notified the NRC Resident Inspector. Notified R3DO (Hills) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MN | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-09-10
40145 | 0 | PRAIRIE ISLAND | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-09-10 17:40 | 2003-09-10 19:32 | 2003-09-10 | 1-HR SECURITY REPORT INVOLVING UNESCORTED ACCESS AUTHORIZATION Vital Area unescorted access inappropriately granted. Immediate compensatory measures taken upon discovery. The licensee informed the NRC Resident Inspector. Contact the Headquarters Operations Officer for additional details. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | MN | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-09-10
40144 | 0 | ILLINOIS EMERGENCY MGMT. AGENCY |  |  |  |  | 2003-09-10 13:15 | 2003-09-10 17:59 | 2003-09-10 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "Abstract: The agency received a call at 13:40 on September 10, 2003, from [DELETED] RSO of S.T.A.T.E. Testing, LLC (License Number IL-01015-01). He reported that, at approximately 13:15, this afternoon, a Troxler Model 3440 moisture density gauge, serial number 22737, (containing 8 mCi of Cesium-137 and 40 mCi of Americium-241/Beryllium), was stolen from the back of a locked truck (Ford F-150) parked on the street at 63rd and Racine in Chicago. According to the technician in charge of the gauge, [DELETED], the source rod was locked in the shielded position and the device itself was contained in a locked D.O.T. Type A transport container with Radioactive -Yellow II transport labels on it. The licensee stated that he would notify the police next. We suggested that he provide the police with photographs of such a type A container and the device itself. We also recommended that he consider a press release or other means to get the word out to the public, in case it is abandoned and later found. "In addition to the written report required by our regs, we instructed [DELETED] to keep us informed of any developments in this case. We also provided him with the number to our Dispatch Center, if it happens to be recovered during off-hours. This event was reported to the NRC Operations Center at 1759 hrs e.s.t. and assigned NRC Event No. 40144." Illinois Item Number: IL030067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-09-15
40143 | 0 | EDERER, LLC |  |  |  |  | 2003-09-10 | 2003-09-10 12:13 | 2003-09-10 | POTENTIAL SAFETY HAZARD INVOLVING CRANE EMERGENCY DRUM BRAKE "Subject: 10 CFR, Part 21 notification of potential safety related nonconforming condition. "This letter serves to notify the Commission of a potential safety related noncompliance in a delivered component as defined in 10 CFR, Part 21. "Condition: "On Friday, Aug. 15, 2003 the Duane Arnold Energy Center (DAEC) notified Ederer that during routine testing of the X-SAM® Single Failure Proof Safety System on Ederer crane S/N F1475, the emergency drum brake would not set consistently. DAEC said the condition was being evaluated in accordance with their 10 CFR, Part 21 reporting procedure. DAEC also said they had re-adjusted the system so it was functioning correctly for use. Ederer reviewed the information provided by DAEC and sent a letter to them on Wednesday, Aug. 20, 2003, which recommended the crane not be used for any safety-related or critical lifts until the X-SAM® Safety System has been thoroughly examined and verified to be in satisfactory operating condition. "Evaluation: "The crane had been in service since 1983 and this was the first instance where the system did not function correctly. Ederer's Design Engineer for the system traveled to DAEC Saturday Aug. 23, 2003 and examined and tested the system. It was determined that accumulated wear over the life of the assembly resulted in increased friction such that the cable would not slide freely and brake reaction setting force could no longer overcome the resistance of the cable. This resulted in the inconsistent operation of the emergency drum brake noted by DAEC. "Ederer has requested DAEC send the old cable assembly back to us for a more complete examination. If that examination provides any different results, a supplemental report will be submitted. "If allowed to remain uncorrected, this condition constitutes a 'safety hazard' because, in the event of the failure of another component, the loss of the safety function could result in a significant reduction in the degree of protection provided by the crane safety system. "Corrective Action: "1.) Ederer notified the other affected user (Point Beach) with the same type of system and advised them not to use their crane for any safety-related or critical lifts until the condition had been evaluated. "2.) Ederer replaced the cable assembly and retested the system at DAEC on Sunday, Aug 24, 2003. "3.) Even though the Point Beach system was functioning normally, Ederer went to site and replaced the cable assembly and retested the system on Monday, Sept. 1, 2003. "4.) Ederer has set a recommended replacement life for this component of 10 years. This is based on 50% of the shortest known useful life of 20 years. "Conclusion: "Ederer considers this condition to be reportable in accordance with 10 CFR, Part 21, Section 21.3(m). Nuclear plants using this equipment were identified and notified, and the components replaced. There have been no previous similar conditions reported. There was no adverse effect on plant safety or on the health and safety of the public as a result of this condition. "In summary, Ederer has notified affected users, notified the NRC and taken appropriate corrective action. "Any questions regarding this report or other Ederer cranes should be directed to: Jim Nelson, Account Manager for Cranes, at jnelson@ederer.par.com. Please provide the following information; customer name, contact person, email address, telephone number, facility, and crane serial number." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 4 | WA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-09-10
40142 | 0 | SUMMER | 1 |  |  | [1] W-3-LP | 2003-09-09 09:15 | 2003-09-09 11:28 | 2003-09-09 | ACCIDENT MITIGATION - CONTROL ROOM VENTILATION SYSTEM "At 1530 EDT on September 8, 2003, maintenance personnel opened the 'A' train Control Room charcoal filter plenum (XAA-0029A-AH) to replace the charcoal. At 0730 EDT on September 9, 2003, a question was raised about the work being performed on the 'A' train Control Room ventilation Charcoal Filter Plenum. The Operating shift asked Engineering if the Control Room was capable of maintaining the Technical Specification required pressure under the current conditions, should the ventilation system go into the emergency mode of operation. "Prior to getting the answer, the conservative decision was made to cease work on the charcoal filter plenum and restore the integrity of the 'A' train ventilation system. This was accomplished at 0805 EDT on September 9, 2003. At 0915 EDT on September 9, 2003, Engineering determined that with the isolation dampers for the 'A' train charcoal filter plenum open, due to the associated fan being tagged de-energized, the 'A' and 'B' trains of the control room ventilation system were effectively crossed. Breaching the charcoal filter plenum would have prevented the control room ventilation system from maintaining a greater than 1/8th inch positive pressure during the emergency mode of operation. "Replacement of the charcoal has been placed on hold until a methodology can be formulated to allow the ventilation system to maintain the design pressure." The licensee informed the NRC resident inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-09-09
40141 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-09-08 09:30 | 2003-09-08 19:01 | 2003-09-08 | AGREEMENT STATE REPORT - IRIDIUM 192 SOURCE FAILED TO RETRACT The following was received via fax from the California Radiation Control office: "At about 9:30 a.m. on 09-08-03, an Ir-192 source (4.6 Ci [Curie]) failed to retract following a patient treatment. The source became stuck in the transfer tube. The physicist started his stopwatch, entered the room and attempted to manually retract the source. Manual retract failed. The physicist called the physician, who was waiting outside the room. The physician entered the room and disconnected the apparatus from the patient and dropped the transfer tube into a lead pig. The physicist and physician moved the patient out of the room. The physicist stopped the watch and it showed that 2 minutes had elapsed. The physicist surveyed the patient and obtained no measurement above background. The physicist re-entered the room and performed a radiation survey, and found the hot spot along the transfer tube to be in the pig. The pig measured 10 mR [millirem] /hr at 3 feet. The room was locked and posted until arrival of the manufacturer's representative, who also was unable to make the source retract. The manufacturer's representative placed the transfer tube into a shipping container and shipped it back to the manufacturer for further investigation. Doses to the patient, physicist and physician were estimated as follows: patient skin dose (10cm from source for 2 minutes) = 9 rem; physicist for 2 minutes = 45 mrem [millirem]; physician 125 mrem [millirem] whole body and 15 rem extremity." The device used was a Nucleotron MicroSelectron HDR [High Dose Rate] model number 31324 (Serial Number D36A4476). The malfunction of the device is under investigation. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-09-11
40140 | 0 | BWX TECHNOLOGIES |  |  |  | URANIUM FUEL FABRICATION | 2003-09-07 13:30 | 2003-09-08 13:34 | 2003-09-08 | CONCURRENT EVENT INVOLVING SMALL CHEMICAL RELEASE AT BWXT "On Sunday, September 7, at approximately 1:30 p.m. an operator identified a low caustic gauge on a small local scrubber that serves the CRF Vertical Tube Furnace. When this was investigated, it was immediately determined that a pressure relief valve had opened allowing Hydrogen Chloride to be discharged directly into the glovebox bypassing the small local scrubber. The discharge of this glovebox goes through a set of HEPA filters and is subsequently discharged from a stack on the roof of the Uranium Recovery facility. "The system ran for approximately 5 hours in this mode, with a maximum possible Hydrogen Chloride release of 1.32 pounds per hour. "This was reported verbally to the Virginia Department of Environmental Quality (DEQ) at 10:40 a.m. on September 8 and will be followed with a written report within 14 days. This report is required by the DEQ Vertical Tube Furnace Permit to be made within four business daytime hours for any malfunction of the facility or related air pollution control equipment that may cause excess emissions for more than one hour. The cause of the malfunction is under investigation. "Radiological releases for the period have been reviewed and indicate no increase in radiological effluent. Additionally, calculations demonstrate that the quantity of Hydrogen Chloride released is relatively small and would not have resulted in detectable offsite concentrations." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OFFSITE NOTIFICATION/NEWS REL | [9 empty] | NON EMERGENCY | 2 | VA | FUE |  | PART 70 APP A (c) |  |  |  | 1 | 2003-09-08
40139 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-09-07 07:50 | 2003-09-07 18:15 | 2003-09-07 | 24 HOUR REPORT ON CRITICALITY CONTROLS DEGRADATION AT PADUCAH "At 0750 on 9/7/03, it was discovered that the Recirculating Cooling Water (RCW) Supply valve for C333 Unit 6 Cell 2 was not positioned correctly for the current condition of the cell, in violation of NCSA CAS-011. On 9/3/03, the cell was in a fluorinating environment with the Odd R-114 system drained and evacuated for leak repairs, Odd RCW valves closed, the Even R-114 system was not drained with the Even RCW valves open satisfying the conditions of CAS-002. It was determined that the cell needed to have a UF6 negative obtained for maintenance work. The UF6 negative was initiated without closing the Even RCW Supply valve, tagging both the Supply and Return valve, and without performing the independent checks for valve position, which violates NCSA CAS-002. Once the UF6 negative was obtained, the cell transitioned to NCSA CAS-011 without satisfying the RCW isolation controls of that NCSA. Both RCW isolation controls require that the RCW Supply valve be tagged closed and that the RCW Return valve be tagged open and both valves independently verified to be positioned correctly. The NRC Senior Resident Inspector has been notified of this event. "SAFETY SIGNIFICANCE OF EVENTS: Since the process condition (lack of moisture in the coolant, and therefore in the process gas system) was maintained, the safety significance of this incident is low. "POTENTIAL CRITICALITY PATHWAYS INVOLVED (BRIEF SCENARIO OF NOW CRITICALITY OF HOW CRITICALITY COULD OCCUR): Once the fluorinating environment is removed from a process cell, moisture that may leak into the process gas system could potentially moderate any uranium that may be present. Sufficient water would have to leak into the process gas system and moderate a critical mass of uranium. "CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC Double contingency is maintained by implementing two controls on mass. "NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OR DEFICIENCIES: The first leg of double contingency is based on ensuring that a coolant condenser leak will not introduce RCW (moderator) into the process gas side of a cell through the coolant. This is accomplished by either maintaining a fluorinating environment in the cell or by restricting /isolating the RCW supply prior to removing the fluorinating environment. This restriction/isolation is accomplished by either removing a supply spool piece or closing and tagging the manual supply valve and tagging open the return valve. Neither of these two RCW alignments was maintained. The second leg of double contingency is based on an independent verification of the RCW alignment relied upon for the first leg of double contingency. The independent verification was not performed. Therefore, this control was lost, Since double contingency is based on two controls on one parameter, double contingency was not maintained. "CORRECTIVE ACTIONS TO RESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMPNTED: At 1010 on 9-7-03, the Even RCW Supply valve was tagged closed, the Odd RCW Return valve was tagged open, and both valves were independently verified. The coolant moisture content was checked and was less than minimum detectible moisture. These actions have placed the system back in compliance with NCSA CAS-011." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-09-07
40138 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-09-06 11:51 | 2003-09-06 17:11 | 2003-09-06 | HPCI DECLARED INOPERABLE DUE TO LOSS OF THE 480V BUS. While operating at 100% power, the plant sustained a loss of the 480 bus "B1". As a result of the loss of power, HPCI has been isolated due to the inability to auto isolate on a primary containment isolation signal. The SBGT was initiated to restore building ventilation. The Reactor Water Clean Up System was manually isolated due to the loss of power. The "A" recirculation pump tripped as a result of the loss of power. The loss of the 480V bus is being investigated at this time. The NRC Resident Inspector was notified. *****UPDATE ON 9/6/03 AT 1805 FROM McDONNELL TO LAURA***** "Due to the loss of power to the RCIC quadrant coolers, the RCIC system is inoperable but available." The NRC Resident Inspector was notified. | 33 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-09-06
40137 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-09-04 | 2003-09-05 18:47 | 2003-09-05 | TEXAS AGREEMENT STATE REPORT ON STOLEN GAUGE "A nuclear gauge was stolen during the night from a pickup truck parked at a residence. The chain and lock were cut and the gauge was taken. We are unaware of whether other items were taken. The technician became aware the gauge was missing when he arrived at a jobsite at about 5:30 am on 09/05/2003. The field service manager looked around the neighborhood and at local pawn shops but did not locate the gauge. The Licensee is considering a public announcement and the offering of a reward. The Agency is investigating the incident." The gauge is a Troxler 3430, serial # 17272, with 39.2 milliCuries of Am-241 (serial # 47-12694) and 6 milliCuries of Cs-137 (serial # 50-6643). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-09-10
40136 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-09-04 08:00 | 2003-09-05 14:44 | 2003-09-05 | CALIFORNIA AGREEMENT STATE REPORT ON MEDICAL EVENT "On September 4, 2003, two patients were scheduled for prostate brachytherapy implants. The first was suppose to be implanted with Iodine 125 and the second with Palladium 103. In anticipation of these procedures both the Palladium 103 and Iodine 125 were brought to the surgical suite. "The first implant procedure was started and after two strands of Palladium 103 had been implanted it was discovered that an error had been made because the patient was scheduled to be implanted with Iodine 125. The treatment plan had been performed for Iodine 125. The decision was made to continue with the implanting of the Palladium 103 after a new treatment plan was performed. Based on the new plan the appropriate number of Palladium 103 seeds were implanted delivering the prescribed dose. Initial report from (DELETED) was that the patient was scheduled for 7:30 AM, so the event most likely occurred around 8:00 AM. Specific details will be included in his full report to follow. Because the treatment planning equipment was already in the surgical suits, the new plan could be developed with little delay. Specific time frame delays to follow in the full report. "The second patient, scheduled for Palladium 103 was in the same day surgery suite and had not been prepped nor given an IV. He was rescheduled for another day, as they did not have enough Palladium 103 for both patients." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | CA | OTH | AGR |  |  |  |  | 0 | 2003-09-10
40135 | 0 | MCGUIRE | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-09-05 10:30 | 2003-09-05 12:10 | 2003-09-05 | OFFSITE MEDICAL EVENT AT McGUIRE "Transport of a potentially radioactively contaminated person to Carolinas Medical Center due to head and neck injury. This is a conservative classification. Initial frisks of the injured individual did not reveal any contamination. His back could not be frisked because he was on a stretcher with potential head and neck injuries." The licensee notified the NRC Resident Inspector. *****UPDATE ON 9/5/03 AT 13:00 FROM REAMER TO LAURA***** Further radiological surveys determined the individual was not contaminated. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE MEDICAL |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(3)(xii) |  |  |  | 0 | 2003-09-05
40134 | -1 | SUSQUEHANNA | 1 |  |  | [1] GE-4,[2] GE-4 | 2003-09-05 09:33 | 2003-09-05 11:22 | 2003-10-02 | HIGH PRESSURE COOLANT INJECTION (HPCI) DECLARED INOPERABLE. "At 09:30 EDT, Unit 1 was performing the HPCI Quarterly Flow verification surveillance. Shortly after the initiation of the system an abnormally loud bang was heard. System flow of approximately 5200 gpm and discharge pressure of approximately 1300 psi was achieved at approximately 09:33. Approximately 4 seconds after reaching rated system flow HPCI discharge pressure increased to approximately 1675 psi and system flow dropped to approximately 2700 gpm. HPCI had been declared inoperable at 08:35 EDT to perform the surveillance and will remain inoperable until the cause of the loss of system flow is corrected. Because HPCI is a single train ECCS [Emergency Core Cooling System] safety system, this event results in the loss of an entire safety function which requires an 8 hour ENS notification in accordance with 10CFR50.72(b)(3)(v) and the guidance provided under NUREG-1022, rev. 2. "There are no other ECCS systems presently out of service." Reactor Core Isolation Cooling (RCIC) is fully operable and HPCI entered Tech Spec 3.5.1 (14 day Limiting Condition of Operation). All other ECCS systems are fully operable. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION FROM WALSH TO CROUCH ON 10/02/03 @ 1548 EDT* * * "On 09/05/2003, PPL Susquehanna LLC made an ENS notification per 10CFR50.72(b)(3)(v) in response to an apparent loss of the HPCI [High Pressure Coolant Injection] safety function. In the event, results of HPCI Quarterly Flow Surveillance testing did not meet acceptance criteria established for the system. "Investigation into the cause of the failed HPCI surveillance revealed a 360-degree weld crack on the HPCI Test Line to Condensate Storage Tank [CST] Valve, HV155F008. HV155F008 is not in the reactor vessel injection flowpath. The impact of this crack, which was located between the valve seat cage assembly and the valve body, was that the HPCI Test Line to CST valve was not capable of throttling over the full range of HPCI system flows. Valve performance became erratic at higher flows because the valve seat cage was lifted out of the valve body into the flow path, increasing system resistance, and preventing attainment of design flow in the HPCI test loop. "While the ability to effectively test the HPCI system using the test return path to the CST was compromised, the HPCI injection flowpath to the reactor vessel was not adversely affected by the damaged valve. Accordingly, the HPCI system maintained full capability for providing sufficient coolant to the reactor vessel in the event of a small break loss-of-coolant accident. Because the HPCI safety function was not compromised by the identified test path obstruction, this ENS notification is being retracted." The Licensee has notified the NRC Resident Inspector. Notified R1DO (Cobey). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | POT UNABLE TO SAFE SD | ACCIDENT MITIGATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(v)(A) | 50.72(b)(3)(v)(D) |  |  | 0 | 2003-09-05
40133 | 0 | WESTINGHOUSE ELECTRIC COMPANY |  |  |  |  | 2003-09-04 | 2003-09-04 09:57 | 2003-09-04 | POTENTIAL DEFECT IN CUTTLER HAMMER CIRCUIT BREAKERS "DHP-VR350, 1200A, circuit breakers were manufactured by Cutler-Hammer Inc., commercially dedicated for Class 1E applications by Westinghouse and shipped to the Columbia Generating Station. During installation acceptance testing, one breaker charging motor failed to charge. Columbia Generating personal performed, a 100% inspection on all 16 breakers with safety-related functions. There was a loose screw associated with this position switch found in seven of these breakers. "Westinghouse will be issuing a Nuclear Safety Advisory Letter (NSAL) to all PWR and BWR plants informing them of this issue so they can determine applicability to their plant." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | UNSPECIFIED PARAGRAPH | [9 empty] | NON EMERGENCY | 1 | PA | OTH | PAR | 21.21 |  |  |  | 0 | 2003-09-04
40132 | 0 | MISSISSIPPI DIV OF RAD HEALTH |  |  |  |  | 2003-09-04 06:00 | 2003-09-04 09:48 | 2003-09-05 | AGREEMENT STATE REPORT - STOLEN MOISTURE DENSITY GAUGE At approximately 0600 CDT on 9/4/2003, a 1999 Nissan Altima belonging to an employee of Professional Services Industries (PSI) was stolen while parked at his residence in Pass Christian, MS. The vehicle had a Troxler Moisture/Density gauge Model 3411B, serial number 18549, locked in the trunk. The gauge contained the following isotopes: Cs-137, 8 millicuries, serial number 50899, and Am-241/Be, 40 millicuries, serial number 4714005. The local PSI office is located in Gulfport, MS. Local Law Enforcement was notified of the stolen vehicle and gauge. *****UPDATE ON 9/5/03 AT 1710 FROM LANGSTON TO LAURA***** The stolen vehicle was located in downtown Gulfport, MS. The gauge was found intact and was transported back to the office for a leak test. It appeared that the gauge was not touched. Notified R2DO (P. Fredrickson). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | MS | OTH | AGR |  |  |  |  | 0 | 2003-09-09
40131 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-09-03 20:05 | 2003-09-03 23:18 | 2003-09-03 | OFFSITE NOTIFICATION DUE TO DEATH OF EMPLOYEE The following was received via fax from the licensee: "Radiation protection technician passed away due to what appears to be a heart attack. On-site emergency medical attention was given and the individual was transported to a local hospital where he was pronounced dead. Although this event occurred on-site, the individual was not within the Controlled Access Area (CAA) and was not contaminated." The licensee made an offsite notification to the Occupational Safety & Health Administration (OSHA) and notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-09-03
40130 | 0 | BRAIDWOOD | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-09-03 07:30 | 2003-09-03 16:57 | 2003-09-03 | 24-HOUR REPORT REQUIRED BY LICENSE CONDITION -- POTENTIAL VIOLATION OF MAXIMUM POWER LEVEL The following report was submitted by the licensee via fax: "This 24-hour report is being made as required by Braidwood Unit 1 License Condition 2.G and Braidwood Unit ~ License Condition 2.G as a potential violation of the maximum power level (3586.6 MWt) as stated in Unit 1 and Unit 2 License Condition 2.C(1). "Braidwood received Nuclear Safety Advisory Letter (NSAL) 03-6 from Westinghouse Electric Company. This NSAL documented that errors were found in calculations that may result in the use of a non conservatively high net heat input value to the plant calorimetric calculation. The net heat input is the difference between the reactor core power and the nuclear steam supply system power. "The values used in the NSAL were based on generic values for certain operational parameters. The NSAL documented that an increase in actual reactor power could be as much as 0.4 MWt. This equates to an error in reactor power of approximately 0.011%. Braidwood reviewed the power history and 8-hour average calorimetric values on Unit 1 and Unit 2 since full power uprate was applied on each Unit. Several time periods were identified on each Unit where the 8-hour calorimetric value exceeded the license thermal power limit when the 0.011% error was added to the 8-hour calorimetric value. Therefore, the licensed power limit of 3586.6 MWt was slightly exceeded on both Unit 1 and Unit 2. "The power level on both Units was reduced to less than 100% to account for the 0.4 MWt error. The calorimetric program was then updated to account for this error. This issue was identified at 0730 on September 3, 2003, and has been entered into the Corrective Action Program. Additional information will be contained in the 30-day licensee event report." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2003-09-03
40129 | 0 | UNIV OF MEDICINE & DENTISTRY OF NJ |  |  |  |  | 2003-08-26 | 2003-09-03 16:00 | 2003-09-03 | P-32 SOURCE INADVERTANTLY DISCARDED TO RECYCLING Late on the afternoon of 8/26 a 607 microcurie P-32 source was delivered to the Towers Building at the University of Medicine & Dentistry, Robert Wood Johnson Medical School located in Piscataway, NJ. Due to a missed communication, the packaging was discarded with the source vial to the cardboard recycling dumpster. The dumpster was picked up on 8/28 and delivered to the cardboard recycling facility located in Port Newark, NJ for bailing and shipment to China. The recycling facility produces about 550 bails/day. A rad survey at the recycling facility found no detectable radiation. The transit time to China is estimated between 4-6 weeks where the material will either enter the pulping process or municipal waste. The licensee has corrective actions under review. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | NJ | HOS |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-09-03
40128 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2003-08-27 11:30 | 2003-09-03 15:11 | 2003-09-03 | MASSACHUSETTS AGREEMENT STATE REPORT -- CONTAMINATED DELIVERY Upon receiving a package (small gray suitcase) of bulk Techneticum-99m (75 millicuries), a technician at Tobey Hospital detected high surface contamination readings on the case. The case was not open and showed no damage. Hospital staff isolated the case until the shipper could arrive. The shipper, Mallinckrodt, arrived at the hospital and performed their own tests on the package. There were two "hot spots" detected: one 3.5 to 4.0 millirem/hr on contact on the plastic auxiliary pouch, and one 0.3 to 0.4 millirem/hr on the side of the suitcase. Upon opening the package, a survey of the Tc-99m pig and inside foam showed almost no contamination. The driver of the delivery truck and the vehicle were immediately surveyed and showed no detectable activity. Surveys of the hospital lab and the lab where the suitcase was packed both showed no evidence of contamination. At this time, it is uncertain as to where the contamination originated. The package has been isolated and will be allowed to decay to background before the case is returned to service. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2003-09-08
40127 | 0 | U.S. ARMY |  |  |  |  | 2003-09-02 | 2003-09-02 14:11 | 2003-09-02 | LOSS OF CHEMICAL AGENT ALARM CONTAINING AMERICIUM-241 A U.S. Army Chemical Agent Alarm (SN #Z03-D-17464, Source # Z03-C-17468) has been reported missing from its unit, normally stationed in Fort Lee, Virginia. This device was sited before it was deployed overseas with the 319th Engineer Company in Kuwait. Upon its unit's return, the alarm could not be located. The device contains an Americium-241 source (300 microcuries). This alarm is used for perimeter warning of chemical attack. The U.S. Army is investigating as to the whereabouts of this device. Any findings made will be reported as updates to this event report. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 1 | MD | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-09-02
40126 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-08-01 21:18 | 2003-09-02 11:43 | 2003-09-02 | INVALID ACTUATION OF DIVISION 2 BALANCE-OF-POWER INBOARD ISOLATION VALVES "On August 1, 2003, at 2118 hours, the Perry Nuclear Power Plant experienced an actuation of several Division 2 Balance-of-Plant (BOP) inboard isolation valves. At the time of the event, the plant was in Mode 1 (Power Operation). The isolation closed one or more valves in each of the following Division 2 subsystems: Liquid Radwaste Sumps, Containment Vessel Chilled Water, Reactor Water Sampling, Drywell and Containment Radiation Monitoring, and Control Room Ventilation. "The event is considered an invalid system actuation, and is reportable under 10 CFR 50.73(a)(2)(iv)(A). The isolation was not initiated in response to actual plant conditions or parameters, and was not a manual initiation. It meets the criteria specified in 10 CFR 50.73(a)(2)(iv)(B)(2) as a general containment isolation signal affecting containment isolation valves in more than one system. Therefore, notification is being provided via 60-day optional phone call in accordance with 10 CFR 50.73(a)(1). All systems functioned as expected for a partial BOP (inboard) isolation. "Repositioning of the valves did not present operational concerns; they were re-opened per restoration procedures. The BOP isolation was attributed to an electrical transient on 120 volt AC electrical bus EK-1-B1 as a result of a failed capacitor. The capacitor had been previously replaced during Refuel Outage 9. "This event was documented in the Corrective Action Program. Remedial actions include replacement of the defective capacitor. The capacitor will be sent out for failure analysis." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | OH | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-09-02
40125 | 0 | FROEHING AND ROBERTSON |  |  |  |  | 2003-08-30 | 2003-09-02 09:59 | 2003-09-22 | STOLEN TROXLER MOISTURE DENSITY GAUGE A Troxler moisture density gauge Model # 3411, Serial # 14338 containing 5.5 millicuries of Cs-137 (serial #50-2959) and 39 millicuries Am-241:Be (serial # 478830) was stolen from the back of a technician's pickup truck while parked at his residence in Roanoke, VA. The Technician called the vendor (Troxler) 24 hour number and local City of Roanoke authorities. Upon notification of the theft on 9/1/03, the licensee called the Vendor (Troxler) and was told that the gauge had been recovered. The licensee was later informed by the vendor that only the case had been recovered in a lake (Smith Mountain Lake) east of Roanoke and south of Bedford, Va. The licensee plans to contact the vendor for possible detection methods to locate the gauge if in the lake. No press release has been issued at this time. The licensee has been in contact with NRC Region 2 (Jeff Griffis). * * * UPDATE ON 09/22/03 @ 1030 BY BRIODY TO GOULD * * * The gauge was found intact in the Roanoke river on 09/21/03 @ 13:00. They are making a complete check of the device. Notified Reg 2 (Boland) and NMSS(Brown) were notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-09-02
40124 | -1 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-09-01 21:45 | 2003-09-02 08:21 | 2003-09-15 | MANUAL ACTUATION OF SAFETY EQUIPMENT FOR AUTOCLAVE CONTAINMENT "On 09/01/03 Operations Personnel were preparing to disconnect a UF6 cylinder from Autoclave #1 in the X-344 facility. The UF6 cylinder as in the 9 O' Clock position and was being prepared to roll to the 12 O' Clock position to complete disconnecting the cylinder safety valve and pigtail from the cylinder. At approximately 2135 hours UF6 was observed smoking from the mechanical connection for the cylinder safety valve and process manifold. The Operator seeing the smoke, alerted personnel in the area, actuated the "Emergency Autoclave Shell Closure" and the building "Gas Release Alarm" that placed the Autoclave and other operational autoclaves into containment. Emergency Response Personnel Responded and performed Air Samples for HF and Uranium in the affected area. All samples were less than Minimum Detectable. "The actuation of the 'Emergency Autoclave Shell Closure' and the building 'Gas Release Alarm' is considered to be the manual actuation of Safety Equipment used to mitigate (prevent) a release of UF6. Reportable to the NRC as a 24 hour report." The certificate holder notified the NRC Resident Inspector and on-site DOE Inspector. * * * RETRACTED ON 9/15/03 AT 1159 EDT BY STEVE MAY TO GERRY WAIG * * * "Investigation of the incident has revealed that prior to the safety system actuation the cylinder valve had been fully closed, the sampling operation had concluded and that the leak point was between the cylinder valve and the cylinder safety valve. At this point, the safety function of isolating the UF6 leak had been performed prior to the actuation of the safety system. In addition it should be noted that based on leak location, the Pigtail Line Isolation system was not designed to protect against this plant condition. SAR Section 6.9, Table 6.9-1, criteria J.2.B (2) addresses that the J.2 reporting criteria excludes the reporting of actuations that are invalid and occur after the safety function has been completed. As noted above the actuation is invalid because the Pigtail Line Isolation system would not have mitigated this UF6 release and the safety functions that in fact did mitigate the release were taken. "It should also be noted that the 'Emergency Autoclave Shell Closure' is not a credited safety system and therefore is not applicable to the stated reporting criteria" The Certificate Holder has notified the NRC Resident Inspector (Bruce Bartlett) and DOE (Russ Vranicar). Notified R3DO (Roger Lanksbury) and NMSS (Doug Broaddus) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 3 | OH | FUE | [5 empty] | 0 | 2003-09-02
40123 | 0 | BRAIDWOOD |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-08-31 01:32 | 2003-08-31 14:43 | 2003-09-02 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING POTENTIAL VIOLATION OF MAXIMUM POWER LEVEL "This 24-hour report is being made as required by Braidwood Unit 2 License Condition 2.G as a potential violation of the maximum power level (3586.6 Mwt) as stated in Unit 2 License Condition 2.C(1). "As a result of issues at Byron Unit 1 and Unit 2 concerning potential discrepancies in the ultrasonic flow measurements for the main feedwater system, Braidwood investigated both Unit 1 and Unit 2 to determine if similar issues existed. These flow measurements are used in the calorimetric calculation for reactor power. Ultrasonic flow measurements were taken on the four individual main feedwater lines on Braidwood Unit 2. These measurements identified the presence of flow signal noise in the data signals for two of the four ultrasonic flow measurement devices installed on the individual feedwater lines, which may adversely affect the integrity of these measurements. In response to identifying this flow signal noise, Braidwood removed corrections based on ultrasonic flow measurement from these two loops. Based on removing credit for these ultrasonic flow measurements, it was determined at 0132 on August 31, 2003, that Braidwood Unit 2 could have potentially exceeded its licensed thermal power limit by up to 0.8%. "Ultrasonic flow measurements were taken on the main feedwater system piping header on Braidwood Unit 1 and were compared to the results from the ultrasonic flow measurement devices on the four individual feedwater lines. Based on the results of the data analysis, Unit 1 was determined to be acceptable. "The power level on Unit 2 was reduced to less than 100% power consistent with the feedwater flow as measured directly by the venturis without using the correction factor on two of the four ultrasonic flow meters. "Additional actions regarding the investigation of the condition, determination of the root cause and corrective actions, and the determination of the potential actual overpower will be included in the 30-day license event report." The licensee informed the NRC Resident Inspector. HOO NOTE: See Byron Event Notification #40117. * * * UPDATE ON 09/02/03 AT 1312 EDT MIKE DEBOARD TO GOTT * * * The following information was provided by the licensee: "The venturis were installed during initial construction of both Units. They are the original design for the Units. "AMAG is a method of calibrating our Feedwater Venturi flow instruments. These devices were installed by the Advanced Measurement and Analysis Group (AMAG). AMAG first applied: Unit 1 - 6/11/1999 and Unit 2 - 6/11/1999 "Rated MWt [Mega Watt Thermal] 3411 to 3586.6: Unit 1 - 5/14/2001 [and] Unit 2 -5/24/2001 "Of the above 5% uprate to 3586.6 MWt, we initially increased power only 1 % of the above. This 1 % increase was known as our mini-uprate. We did not increase the full 5% since our turbines had not yet been modified to withstand the higher flow rates. During the A_R09 outages, we modified the turbines and achieved full uprate as follows: Full Uprate to 3586.6 MWt: Unit 1 - 10/16/2001 [and] Unit 2 - 5/15/2002." Notified NRR (Reis) and R3DO (Gardner) | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2003-08-31
40122 | 0 | ARKANSAS NUCLEAR | 1 | 2 |  | [1] B&W-L-LP,[2] CE | 2003-08-29 17:50 | 2003-08-29 23:00 | 2003-08-29 | LOSS OF OFFSITE EMERGENCY SIREN ACTUATION CAPABILITY "At 1750 today (8/29/03), the Duty Emergency Planner was notified by the Arkansas Department of Health's Nuclear Planning and Response Program (NP&RP) staff that, due to the loss of the ANO microwave system, the capability to sound the offsite Siren Warning System was lost. The NP&RP staff discovered the loss of the Siren Warning System at 1730. The Siren Warning System is used to notify the public in ANO's 10-mile Emergency Planning Zone (EPZ) of an emergency at ANO. This system covers approximately 85% of the 10-mile EPZ population. "The Siren Warning System was restored at 1930 CDT on 8/29/03. The backup means for alerting the population in the EPZ remained available." The cause for the siren failure is unknown and under investigation. The licensee informed both the State of Arkansas and the NRC Resident Inspector. | 0 | 77 | 0 | 0 | 77 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Power Operation |  | Hot Standby | Power Operation |  | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-08-29
40121 | 0 | THREE MILE ISLAND | 1 |  |  | [1] B&W-L-LP,[2] B&W-L-LP | 2003-08-29 15:05 | 2003-08-29 18:37 | 2003-08-30 | DEGRADATION OF EMERGENCY PREPAREDNESS RESPONSE CAPABILITIES "At 1505 hrs. on Friday August 29, 2003, TMI Unit 1 determined that there had been a degradation of the emergency preparedness response capabilities when there was a loss of the Emergency Notification System (ENS), the Health Physics Network (HPN) and the Emergency Response Data System (ERDS). In addition most site telephone lines were inoperable. The loss of these communications systems was most probably caused by a lightning strike. Limited telephonic communications remains with the TMI 1 control room, i.e., one commercial phone exchange, a satellite phone and the emergency management phone circuit remain operable. "TMI 1 has verified operability of the ERO notification system (pagers), and the communication circuit used to notify the state and local counties. The siren system for local counties was unaffected by loss of site telephone systems. Plant page and radio systems remain operable. Adequate communications capabilities are operable at this time to implement the emergency plan. "Repairs to restore the inoperable telephone systems are in progress at this time. A return to service time for all systems is to be determined. However, at the time of this report, the ENS line has been restored to an operable status. "TMI 1 has determined that this event is reportable to the NRC as an 8-hour non-emergency report in accordance with 10 CFR 50.72 (b)(3)(xiii)." The NRC Resident Inspector, the State of Pennsylvania, and local authorities have been notified by the licensee. * * * UPDATE ON 8/30/03 AT 0448 BY DAVID WILSON TO GERRY WAIG * * * The licensee reported that the Emergency Notification System (ENS) was restored to service on 8/29/03 at approximately 2100 hours EDT and the Emergency Response Data System (ERDS) was returned to service on 8/29/03 at 2212 hours EDT. Notified R1DO (James Trapp). | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-08-29
40120 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-08-27 | 2003-08-29 17:52 | 2003-08-29 | AGREEMENT STATE REPORT INVOLVING A STOLEN TROXLER GAUGE "Subject: Event Report # WA-03-034 "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, Dept. of Health (DOH) on-site investigation; media attention) The license's representative, [...], reported that sometime between the evening of 27 August and the morning of 28 August that a Troxler, Model 3411B, moisture density gauge, Serial Number 13050, was stolen out of the trunk of the operator's transport vehicle parked outside the operator's residence in Everett, Washington. A police report was filed on 29 August and a reward posted. "The operator violated several DOH requirements that contributed to the theft to the device. DOH requires that portable gauge licensees prohibit operators from taking gauges to residences if the work site is within 50 miles of the primary storage location. The gauges must be returned to that location. This didn't happen. Also DOH requires two independent layers of protection to keep the transport box, with secured gauge inside, secured to the vehicle. The licensee had not been using the two-layer method. And, gauges are not allowed to remain in the transport vehicle overnight as did happen. The licensee will be cited for at least 3 violations as a result of the event. "A full report provided by the licensee, should be in the office, by the week of 1 September. This report will be updated after that. No media attention noted at present. Corrective actions will be discussed with the licensee. "What is the notification or reporting criteria involved? 24-hour "Activity and Isotope(s) involved: 370 megaBq (10 millicuries) Cesium 137 and 1850 megaBq (50 millicuries) Americium 241/Beryllium. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) N/A "Lost, Stolen or Damaged? STOLEN (mfg., model, serial number) noted above "Disposition/recovery: pending "Leak test? Unknown "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) Unknown "Release of activity? N/A "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided? Pending "Was referring physician notified? N/A "Consultant used? N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-09-03
40119 | 0 | ARKANSAS NUCLEAR | 1 |  |  | [1] B&W-L-LP,[2] CE | 2003-08-29 14:28 | 2003-08-29 16:59 | 2003-08-30 | AUTOMATIC REACTOR TRIP ON HIGH RCS PRESSURE "Unit 1 experienced an automatic reactor trip at approximately 14:28 CDT as a result of a turbine trip. Initial indications are that the trip was associated with a lightning strike on site. Plant is stable in Mode 3. All control rods fully inserted and there are no offsite radiation releases. Anomalies noted are 'C' Main Phase Transformer Sudden Pressure Trip Alarm, Main Generator Output Breakers failed to automatically open and were subsequently manually opened, and 'B' Once Through Steam Generator (OTSG) main feedwater block valve failed to indicate closed which resulted in a low level condition on 'B' OTSG and subsequent automatic actuation of Emergency Feedwater (EFW). EFW is controlling both OTSG levels at low level limits." A normal fast transfer to the Startup Transformer occurred following the trip and offsite power remains available. All EDGs are in standby, if needed. There is no safety related equipment out of service at this time. Decay heat is currently being removed via the steam dumps to the main condenser. The licensee will conduct an investigation into the equipment failures and determine if any plant equipment was damaged by the lightning strike. The licensee informed the NRC Resident Inspector. * * * UPDATE AT 0144 EDT FROM HOGUE TO CROUCH * * * "This message is intended to provide clarifying information for Event Notification #40119. Unit 1 experienced an automatic reactor trip at approximately 14:28 CDT as a result of a turbine trip. Initial indications are that the trip was associated with a lightning strike on site. Plant is stable in Mode 3. All control rods fully inserted and there are no offsite radiation releases. The following anomalies were noted in conjunction with plant trip. A 'C' Main Phase Transformer Sudden Pressure Trip Alarm occurred as a result of an indication problem only. The Main Generator Output Breakers failed to automatically open and were subsequently manually opened. The 'B' Once Through Steam Generator (OTSG) main feedwater (MFW) block valve failed to fully close. Complications associated with manual control of feedwater flow when the MFW block valve failed to fully close resulted in a momentary low level in the 'B' OTSG and Emergency Feedwater (EFW) automatic actuation. EFW flow quickly restored the 'B' OTSG level to normal. Both MFW pumps remained operating throughout the transient, and MFW flow was never lost. The EFW System was allowed to recirc for approximately 2 hours. After the MFW block valve was manually closed, the auxiliary feedwater pump was placed in service and EFW and the MFW pumps were secured." The licensee will be notifying the NRC Resident Inspector. * * * UPDATE 2017 EDT ON 8/30/03 FROM RICHARD SCHEIDE TO S. SANDIN * * * The following information was provided as an update: "This message is intended to update the information provided in previous notifications concerning Event Notification #40119. Based on subsequent investigation the automatic reactor trip which occurred at approximately 14:28 CDT on August 29, 2003, was a result of high reactor coolant system (RCS) pressure. The high RCS pressure resulted from the inadvertent closure of the main turbine governor valves. Although not conclusively determined, the closure of these valves is most likely due to a lightning strike on site. This automatic reactor trip also resulted in a main turbine trip. Anomalies associated with this event remain as previously reported." The primary PORV (2450 psia) and Safeties (2500 psia) did not lift during the pressure excursion. The High RCS Pressure setpoint for RPS actuation is 2355 psia. The licensee informed the NRC Resident Inspector. Notified R4DO(Runyan). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | AR | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-29
40118 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-08-29 13:50 | 2003-08-29 16:08 | 2003-08-29 | HIGH PRESSURE COOLANT INJECTION SYSTEM DECLARED INOPERABLE "During performance of routine operability testing, the High Pressure Coolant Injection System [HPCI] tripped and restarted due to an as yet undetermined cause. The trip and restart sequence occurred twice in close succession approximately 20 minutes into a normal run before the operator took action to manually trip the turbine. Investigation into the cause of the malfunction is on-going. The HPCI system has been declared inoperable in accordance with Technical Specifications." The operability of all other Emergency Core Cooling System components has been verified. There was never any actual coolant injection by the HPCI system during this event. The NRC Resident Inspector has been notified by the licensee. The State of Massachusetts will also be notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-08-29
40117 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-08-28 17:43 | 2003-08-29 14:55 | 2003-08-29 | 24-HOUR CONDITION OF LICENSE REPORT INVOLVING POTENTIAL VIOLATION OF MAXIMUM POWER LEVEL "This 24-hour report is being made as required by Byron Unit 1 License Condition 2.F and Byron Unit 2 License Condition 2.G as a potential violation of the maximum power level (3586.6 MWt) as stated in Unit 1 and Unit 2 License Condition 2.C(1). "On August 28, 2003 at 17:43 CST Byron Station was notified by the ultrasonic flow measurement vendor via letter that there were discrepancies in the ultrasonic flow measurements used in the calorimetric calculation for reactor power. As part of an ongoing testing plan, ultrasonic flow measurements were being taken on the main feedwater system piping header on Byron Unit 1 and were compared to the results from the ultrasonic flow measurement devices on the four individual feedwater lines. Based on the results of the data analysis, and noted signal abnormalities, it was determined that Byron Unit 1 has potentially exceeded its licensed thermal power limit by approximately 1.5%. "Based on the results of the testing on Unit 1, the ultrasonic flow measurements on Byron Unit 2 were also investigated. Similar signal abnormalities were identified on one of the four ultrasonic flow measurement devices installed on the individual feedwater lines on Unit 2. Subsequent evaluation indicates that Byron Unit 2 also has potentially exceeded its licensed thermal power limit by approximately 0.6%. "The power level on both units was reduced to less than 100% power consistent with feedwater flow as measured directly by the venturis without using the correction factors from the ultrasonic flowmeters. "Additional actions regarding investigation of the condition, determination of root cause and corrective action, and determination of the potential actual overpower will be included in the 30-day license event report." The licensee informed the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW | [5 empty] | 0 | 2003-08-29
40116 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2003-08-27 09:15 | 2003-08-29 14:00 | 2003-08-29 | AGREEMENT STATE REPORT INVOLVING A STOLEN/RECOVERED TROXLER GAUGE "At approximately 9:15 A.M. [on 08/27/03], [ ] the Area Manager of Ashland, KY called and advised [ ], RSO, that [ ] had his truck stolen with a Troxler 3440 gauge (s/n 14782) in it. He also indicated that the Ashland Police Department had been notified along with all other local police departments. Mountain Enterprises offered a $1000 reward for the return of the gauge, and also provided two employees to assist in the search for the gauge. At 1:30 P.M. the Ashland Police Department called and said that they found the truck in a yard at 2513 Newman St. The gauge was still locked in the bed of the truck and the case was still locked with the source locked in place. A survey was performed that showed the source to still be inside. The police said that another vehicle was stolen a block away so the indication is that the truck and gauge were stolen for the transportation and not for the gauge. The gauge will no longer be stored overnight anywhere but at the plant." KY Item Number: KY030003. This event is closed by the State. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | KY | OTH | AGR |  |  |  |  | 0 | 2003-09-03
40115 | 0 | SALEM | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-08-29 07:20 | 2003-08-29 10:22 | 2003-08-29 | OFFSITE NOTIFICATION DUE TO DISCHARGE OF WASTE WATER CONTAINING HYDRAZINE "A 2-hour notification was made to the New Jersey Department of Environmental Protection due to a discharge of 100,000 gallons of industrial waste water to the Delaware River. The water contained a concentration of 300 ppb [parts per billion] hydrazine. The discharge was immediately terminated upon discovery. This is a common water treatment system for both Salem Units, however, there is no impact on plant operations." The licensee has notified the NRC Resident Inspector and the LAC (Lower Alloways Creek) Township. The New Jersey Bureau of Nuclear Engineering will also be notified by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-08-29
40114 | 0 | CATAWBA | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-08-29 02:03 | 2003-08-29 05:27 | 2003-08-29 | CATAWBA UNIT 1 AUTOMATIC REACTOR TRIP DUE TO REACTOR PROTECTION SYSTEM ACTUATION Unit 1 tripped on Over Temperature - Delta Temperature (OTDT) protection. Channel 1 OTDT was in a trip condition due to a reactor coolant hot leg temperature problem. Per Technical Specifications, this required Channel 1 OTDT to be placed in the tripped condition. Channel 2 Pressurizer pressure failed low at 0203 EDT. This input (Channel 2 Pressurizer Low Pressure) caused Channel 2 OTDT to enter a trip condition. With 2 of 4 OTDT Channels in the trip condition, a reactor trip signal was generated by the reactor protection system resulting in an automatic reactor trip. After the reactor trip occurred, RCS (Reactor Coolant System) letdown was lost on the chemical and volume control system due to low Pressurizer level. 1NV-1A (Reactor Coolant Letdown Isolation Valve) did not close as required. This necessitated the alignment of the excess letdown flowpath to maintain the desired Pressurizer level. ESF (Engineered Safety Features) operated as designed. Auxiliary feedwater automatically started and main feedwater isolated as designed. All control rods fully inserted on the reactor trip. Station service electrical systems, emergency diesel generators, and ESF equipment are available. Catawba Unit 2 was unaffected by the trip of Unit 1. The licensee has notified the NRC Resident Inspector and will be notifying state and local officials. | 0 | 0 | 0 | 95 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-29
40113 | 0 | SEQUOYAH | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-08-28 16:04 | 2003-08-28 17:01 | 2003-08-28 | ALERT DECLARED DUE TO REACTOR PROTECTION SYSTEM FAILURE At 1618 EDT on 08/28/03, an Alert was declared at Sequoyah Unit 1 due to a failure of the Reactor Protection System (RPS) to auto-trip the reactor following a turbine trip. Turbine oil trip testing was in progress when at 1604, the main turbine tripped. The reactor trip breakers were opened by manual operator action approximately 20 seconds after the valid reactor trip signal. Following the trip, all systems operated as required. The main steam isolation valves were manually closed based on indication of steam flow and a throttled steam dump valve. No primary system or steam generator safety valves opened. The unit is currently stable with temperature controlled using atmospheric relief valves. The Auxiliary Feedwater System received an auto-start signal and successfully operated. All control rods were fully inserted into the core. There was no release of radioactive material. The licensee has initiated an investigation into the cause of the incident. The NRC Resident Inspector and the State of Tennessee were notified by the licensee. The NRC notified FEMA (Steiner), DOE (Morroni), USDA (Beers-Block), HHS (Williams), DHS (Glick), and DOT/EPA/NRC (Threatt). The NRC entered monitoring phase of normal mode with Region 2 in the lead at 1735 EDT. * * * UPDATE ON 08/28/03 AT 2044 EDT, KEVIN WILKES TO NATHAN SANFILIPPO * * * At 2030 EDT on 08/28/03, the licensee terminated the Alert at Sequoyah Unit 1. The reactor is stable and in Mode 3, Hot Standby. This termination is based upon containment integrity, Emergency Core Cooling System and Engineered Safety Features operability, availability of heat sink, onsite and offsite electrical system and Emergency Diesel Generator operability, radiation monitor operability, availability of technical support personnel, and activation of a forced outage recovery team. Reactor coolant samples were taken, which showed no increase in activity. The NRC notified FEMA (Austin), DOE (Morroni), USDA (Beers-Block), HHS (Hogan), DHS (Van Buskirk), and DOT/EPA/NRC (White). The NRC exited monitoring phase of normal mode at 2045 EDT. * * * UPDATE 1420 EDT FROM ZACHARY KITTS TO S. SANDIN * * * The following information was provided as an update: "This provides a follow-up report regarding the prior notification of an Alert on 8/28/03 that included a possible reactor protection system (RPS) failure on Unit 1. The main control room staff responded to a loss of generator load by initiating a manual reactor trip. The Alert was declared at 1618 under EN # 40113. The operators suspected a failure of the automatic RPS because they believed that, based on direct observation of plant conditions at the time, a valid automatic reactor trip signal should have occurred. A subsequent engineering review of plant parameters prior to and after the manual reactor trip determined that no automatic reactor trip signal was required. "TVA has determined that there was no failure of the turbine protection or reactor protection system. The apparent failure of a pressure switch from the turbine trip oil system in conjunction with the thrust bearing trip components being tested caused the actuation of the Unit 1 generator trip circuitry and the opening of the generator output breakers. The electrical unloading of the generator was followed by rapid closure of the turbine governor valves to control generator speed. "By design, the generator trip signal does not result in an automatic turbine trip under the conditions experienced. The turbine responded to the generator trip as a loss of load transient. The turbine overspeed protection circuitry (OPC) operated as expected to close the turbine governor valves to prevent an overspeed condition. The turbine protection system contains overspeed trip functions which function independently based on either mechanical or electrical inputs. While the mechanical overspeed protection function was inoperable due to the test in progress, the electrical overspeed trip was available to trip the turbine. The operation of the OPC limited the turbine overspeed transient such that the electrical overspeed trip setpoint was not required. "For a loss of electric load and/or turbine trip event, the reactor protection system is expected to initiate a reactor trip when either the high reactor coolant system pressure or over temperature differential temperature (OTDT) setpoint is reached. In this event, however the reactor was manually tripped by operator action in response to the generator trip. Subsequent review of the primary system transient response data confirmed that none of the reactor protection system setpoints were exceeded prior to the operator action. The reactor trip breakers opened as expected following the manual trip. The reactor protection system functioned as designed. "Event investigation will continue with resolution of adverse conditions prior to Unit 1 startup. TVA is providing this follow-up report to update you as to the subsequent information resulting from the investigation." The licensee informed the NRC Resident Inspector. Notified R2DO(Evans) and NRR EO(Reis). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | ALERT | 2 | TN | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-08-28
40112 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-08-25 17:30 | 2003-08-28 13:29 | 2003-08-28 | AGREEMENT STATE REPORT - IRIDIUM-192 SOURCE UNINTENTIONALLY DISCONNECTED FROM DRIVE CABLE The following report was received via fax from the Arizona Radiation Regulatory Agency: "On August 25, 2003, at approximately 5:30 PM, while making an exposure at valve #14 (Iverton Rd. and Contractors Way in Tucson, Arizona) the source assembly unintentionally disconnected from the drive cable in the end of the six foot collimating guide tube. The exposure device being used was an INC - IR100, SN-4015, containing a 61 Curie IR-192 source, Model #87703, capsule #08809B. A 35 foot set of NDT [Non Destructive Testing] drive cables and a NDT guide tube were being used. The source was removed from the guide tube and collimator, reattached to the drive cable and cranked back into the exposure device, plugged, locked, and the drive cables removed. Pocket dosimeters indicated that whole body exposures were approximately 30 mR [millirem] and a hand exposure to the individual recovering the source was calculated to be 200 mR. The exposure device and drive cables are being sent back to AEA in Baton Rouge, LA to determine the cause of the disconnect." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-09-02
40111 | 0 | COOPER | 1 |  |  | [1] GE-4 | 2003-08-28 07:00 | 2003-08-28 12:08 | 2003-08-28 | FITNESS FOR DUTY "At 0700 a non-licensed contract supervisor failed a for cause fitness-for-duty test. The individual tested positive for alcohol, and the results of the drug portion of the test have not yet been received. "Immediate Corrective Action: The individual's unescorted site access was denied at 0717 CST on August 28, 2003, and appropriate notifications have been completed in accordance with the station's Fitness-For-Duty Program. "Safety Significance: None. There is no reason to believe there have been any adverse consequences from this event. The employee had been cleared for unescorted access; however, had never obtained his badge for access to the protected area of the site. This event is not considered to have impacted operation of the plant in any way. "The licensee informed the NRC Resident Inspector. "Contact the Headquarters Operations Officer for additional details." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | NE | POW |  | 26.73 |  |  |  | 0 | 2003-08-28
40110 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-08-28 07:50 | 2003-08-28 11:27 | 2003-09-02 | LOSS OF POWER TO EMERGENCY OPERATIONS FACILITY "The Emergency Operations Facility (EOF) for Grand Gulf was lost when power was removed from the facility and the EOF diesel generator failed to start. Power had to be removed due to the loss of one phase of the local power supply. Actual plant operations are not affected. The power phase problem and failure of the EOF diesel generator to start are being investigated at this time. The Backup EOF is available if needed." The licensee notified the NRC Resident Inspector. * * * UPDATED ON 09/02/03 AT 1841 EDT FROM CARL EHRHARDT TO NATHAN SANFILIPPO * * * As of 09/02/03, power to the Grand Gulf Emergency Operations Facility (EOF) has been restored. The NRC Resident Inspector will be notified. Notified R4DO Charles Marschall. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-08-28
40109 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-08-27 09:00 | 2003-08-27 22:53 | 2003-08-27 | PROCEDURAL DEFICIENCY OMISSION NRC BULLETIN 91-01 24 HOUR NOTIFICATION At 0900 on 8/27/03, it was discovered that the procedure for operation of the C-409 Uranium Precipitation System did not adequately address flowdown requirements specified in NCSA 409-001. NCSA 409-001 control 3.2.39 prevents introduction of organic material to the precipitation system by requiring verification that the solution originated from either the C-710 Laboratory, the C-409 Cylinder Wash, or the C-409 Uranium Precipitation System and that the solution does not contain organic material, as indicated by sampling. The control had been flowed down for solutions originating from the C-710 Laboratory and the C-409 Cylinder Wash, however was not flowed down for solutions originating from the C-409 Uranium Precipitating System. PGDP Assessment and Tracking Report No. ATR 03-2767, PGDP Event Report No. PAD-2003-017. SAFETY SIGNIFICANCE OF EVENTS: Double contingency was not maintained because the independent verification of the origination of solutions from the C-409 Uranium Precipitation System and the independent verification that the solution did not contain organic material had not been performed. However, no oil has been introduced to the operation. POTENTIAL CRITICALITY PATHWAYS INVOLVED OF HOW CRITICALITY COULD OCCUR: In order for a criticality to be possible, greater than a safe mass of uranium must be accumulated within the Uranium Precipitation System, facilitated by the presence of organic material and accumulate in the rotary drum filter. CONTROLLED PARAMETERS (MASS, MODERATION, GEOMETRY, CONCENTRATION, ETC.) Double contingency is maintained by implementing two controls on mass. ESTIMATED AMOUNT, ENRICHMENT, FORM OF LICENSED MATERIAL: This system has a process limit of (xx) wt.% U235. NUCLEAR CRITICALITY SAFETY CONTROL(S) OR CONTROL SYSTEM(S) AND DESCRIPTION OF THE FAILURES OF DEFICIENCIES: The first leg of double contingency is based on controlling the mass of uranium in the tanks. NCSA 409-001 requires that prior to placing solution in the Uranium Precipitation Operation the solution must be verified to be uranium salvage from C-710 laboratory, C-409 cylinder wash, or the C-409 Uranium Precipitation System and that the solution does not contain organic material. This control prevents the build-up of organic material at the top of the Uranium Precipitation System tanks. If organic material were to get in the tanks it would create a floating uranium/oil layer and result in non-representative sampling of the concentration, since sampling is conducted near the bottom of the tank. This may lead to an unsafe mass reaching the rotary drum filter. The C-710 solution currently in the system was independently verified to be free of organic material prior to initial introduction. However, since no verification was documented for the C-409 Uranium Precipitation system solution, this control was lost. Chemical Operations personnel have subsequently verified that no events have occurred to introduce organic material into the solution from the C-409 Uranium Precipitation System. The control was violated; however the parameter was maintained. The second leg of double contingency is based on mass. NCSA 409-001 requires that prior to placing solution in the Uranium Precipitation Operation, the solution be independently verified to be uranium salvage from C-710 Laboratory, C-409 Cylinder Wash or the C-409 Uranium Precipitation System and that the solution does not contain organic material. However, since no independent verification was documented for the C-409 Uranium Precipitation system solution, this control was lost. Chemical Operations personnel have subsequently independently verified that no events have occurred to introduce organic material into the solution from the C-409 Uranium Precipitation System. Therefore, this control was violated. Since there are two controls on one parameter, double contingency was not maintained. Since double contingency is based on two controls on one parameter, and the controls were violated, double contingency was not maintained. CORRECTIVE ACTIONS TO REESTORE SAFETY SYSTEMS AND WHEN EACH WAS IMPLEMENTED: Chemical Operations revise procedure CP4-CU-CH2137 to include verification requirements specified in NCSA 409-001. Procedure change was initiated on 8-27-03. The NRC Senior Resident Inspector has been notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | RESPONSE-BULLETIN | [9 empty] | NON EMERGENCY | 3 | KY | FUE | [5 empty] | 0 | 2003-08-27
40108 | 0 | GRAND GULF | 1 |  |  | [1] GE-6 | 2003-08-22 02:01 | 2003-08-27 15:41 | 2003-08-27 | INVALID ACTUATION OF THE "A" STANDBY SERVICE WATER SYSTEM "On August 22,2003, at 0201 Central Time, while operating at 100 percent power, Grand Gulf Nuclear Station experienced an invalid actuation of the 'A' Standby Service Water (SSW) System. A failed DC/DC converter power supply in Panel 1H22P400 for the Division 1 Diesel Generator (DG) resulted in a faulty DG speed monitor signal indicating DG speed greater than 450 revolutions per minute (RPM). The DG was not running since it was already inoperable due to a planned outage. The event occurred during restoration activities to prepare the DG for retest. The invalid DG start signal caused the outside air fan and SSW 'A' to auto start as designed to support DG operation. SSW 'A' started and functioned as designed. No other actuations occurred and all support systems functioned properly." The licensee notified the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MS | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-08-27
40107 | -1 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-08-27 09:24 | 2003-08-27 15:22 | 2003-10-22 | CONTROL ROOM ACCESS DOOR LATCH WAS DETERMIEND TO BE NOT FULLY ENGAGING. At 09:24 am on 08/27/03, a Control Room access door latch was determined to be not fully engaging. The door and latch provide the following functions: maintain the integrity of the Control Room boundary which is a design feature to maintain Control Room habitability following a design bases accident, and provide a security barrier to restrict access into the Control Rom complex to only those personnel with preapproved security clearance. With the latch not engaged, the door was not capable of performing these functions. The appropriate security contingencies were implemented, requiring posting of a Security Force Member at the door controlling access to the Control Room Complex. Technical Specification (TS) 3.0.3 was entered due to the inability of either Control Room ventilation system to maintain Control Room habitability, as required by TS 3.7.2. At 10:20, the door latch was replaced to re-establish the integrity of the Control Room habitability boundary and TS 3.0.3 was exited. The ability of the latch to properly operate for access and egress was not established; access through the affected door remained restricted until repairs can be completed (there are additional doors to the Control Room that remain fully functional). At 14:00, the door was again impaired for repair of the door latch. Full functionality of the door was restored at 14:41. The NRC Resident Inspector was notified of this event by the licensee. * * * RETRACTION AT 1143 EDT ON 10/22/03 FROM A. BRAEDY TO E. THOMAS * * * "At the time of the original notification the ability to maintain Control Room habitability, as required by TS 3.7.2 was not assured. Subsequent evaluation has determined that if a postulated accident had occurred during the time that the door latch was impaired, control room dose would be less than the acceptance criteria specified in 10CFR50.67 and Regulatory Guide 1.183 and bounded by our current analysis. The site boundary doses were never affected. The dose impact of the condition as it existed would be bounded by the current analysis. Thus, the safety function would have been fulfilled." Notified R1DO (L. Doerflein) | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-08-27
40106 | 0 | US AIR FORCE |  |  |  |  | 2003-08-22 | 2003-08-27 11:10 | 2003-08-27 | MISSING EXIT SIGN CONTAINING TRITIUM On 08/22/03, while reviewing documentation following construction, personnel at Vance Air Force Base discovered that an exit sign containing 20 Curies of Tritium was misplaced. The sign was to be replaced with an electric sign. The construction occurred in late June 03. Personnel are conducting a search for the sign. It may have been disposed of in the regular trash. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 4 | OK | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-08-27
40105 | 0 | PUBLIC HEALTH LAB, SAN JUAN |  |  |  |  | 2003-08-19 12:00 | 2003-08-26 16:25 | 2003-08-26 | TWO GAS CHROMATOGRAPHS ACCIDENTALLY DISPOSED OF TO A LANDFILL On 08/19/03 The Public Health Lab in San Juan, Puerto Rico accidentally disposed of 2 Gas Chromatographs, Model 8500 manufactured by Perkin-Elmer. The Gas Chromatographs ended up in a San Juan landfill. The trash company said that it would nearly be impossible to find the 2 Gas Chromatographs because they were now under tons of dirt. This incident was reported to Commonwealth of Puerto Rico, San Juan Radiation Safety Officer on 08/25/03. The caller did not know what type of radioisotope or the strength of the radioisotope in each Gas Chromatographs. Search of former events revealed that Perkin-Elmer Gas Chromatographs normally contain a 15 millicurie Ni-63 source. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | PR | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-26
40104 | 0 | PEACH BOTTOM | 2 |  |  | [2] GE-4,[3] GE-4 | 2003-07-27 18:39 | 2003-08-26 13:36 | 2003-08-26 | 60 DAY OPTIONAL REPORT "This 60-day optional report, as allowed by 10 CFR 50.73(a)(1), is being made under the reporting requirement in 10CFR50.73(a)(2)(iv)(A) to describe an unplanned, invalid actuation of a specified system, specifically Primary Containment Isolation Valve (PCIV) Group II and III outboard valves. The inboard valves were unaffected by this event. "On July 27, 2003, at 1839 hours, a spurious operation of Primary Containment Isolation System (PCIS) logic relay occurred. This normally energized relay momentarily changed state resulting in an isolation of the outboard Secondary Containment Isolation Valves (SCIVs) and outboard Group 2 and 3 PCIV's. Additionally, the "B" Standby Gas Treatment (SBGT) subsystem started due to the isolation. "The affected systems responded as expected for the given conditions. The Group II/III PCIS isolation was reset by 1842 hours. The affected systems were promptly returned to a normal configuration. No other deficiencies or abnormalities were noted during the event. "This event has been entered into the site-specific corrective action program for resolution (CR 169219) "The NRC resident has been informed." | 77 | 0 | 0 | 77 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-08-26
40103 | 0 | STATE OF WEST VIRGINIA |  |  |  |  | 2003-08-25 15:00 | 2003-08-26 12:27 | 2003-09-05 | XENON-133 RELEASED TO COLD TRASH THE EVENT BELOW WAS REPORTED TO NRC REGION 2 BY DAN HILL OF THE STATE OF WEST VIRGINIA. Initial notification to NRC Region II by State of West Virginia. Source was recovered by the licensee and State of West Virginia on 08/25/03. Activity measured in the licensee's dose calibrator was 10.49 millicuries at approximately 3 PM on 08/25/03. Outer pig still had radioactive marking and listed 100 millicuries of activity. Pig originally contained 5 vials, 20 millicuries each (nominal). Only one vial remained in the improperly disposed pig. Trash was normal waste, not biomedical. Discovered when a landfill alarm was set off. * * * Update on 09/05/03 at 1130 EDT by Licensee Ashford Broadwater III to MacKinnon * * * Ashford Broadwater III of Camden Clark Memorial Hospital stated that on 08/26/03 at approximately 0845 EDT he was notified by the State of West Virginia Radiation Protection that a dumpster from their Hospital set off a radiation alarm at a local land fill. Mr. Broadwater III met a representative from the State of West Virginia at the landfill around 1130 EDT. The dumpster was dumped and an unused vial of Xenon-133 was found along with the lead pig that it came in. The total activity of the Xenon-133 on 08/20/03 at noon was 20 millicuries. Its half life is 5.3 days. The vial of Xenon-133 was taken back to the Hospital by 1230 EDT. The licensee has revised their procedures to prevent this incident from happening in the future. NRC R2DO (Paul Fredrickson) & NMSS EO (Tom Essig) notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | WV | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-26
40102 | 0 | ARIZONA RADIATION REGULATORY AGENCY |  |  |  |  | 2003-08-25 09:30 | 2003-08-25 18:22 | 2003-08-25 | 3 CURIE COBALT-60 SOURCE DISCOVERED DISCONNECTED "At approximately 9:30 AM MST August 25, 2003, the Agency was informed by the Licensee that they had discovered a source had disconnected from a rod in the Process Leaching Vessel. The source contains 3 Curies of Cobalt 60 as of October 2001. The licensee has made measurements and determined the radiation levels outside the vessel are not excessive. The device is a ThermoMeasure Tech Model 5031 L SN B43. Even though the source is disconnected, because it is trapped within a sealed source guide tube, it is still secure from inadvertent removal. The estimated date for full repair is October 21, 2003. Repair will be made by the device manufacturer. The Licensee has agreed not to drain the vessel without Agency notice and approval. "The Agency continues to investigate this incident." The Agency is: ARIZONA RADIATION REGULATORY AGENCY. First Notice: 03-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | AZ | OTH | AGR |  |  |  |  | 0 | 2003-08-28
40101 | 0 | COMMUNITY HOSPITAL OF ANDERSON |  |  |  |  | 2003-08-08 08:30 | 2003-08-25 16:20 | 2003-08-25 | FEMALE NOT KNOWING THAT SHE WAS PREGNANT WAS ADMINISTERED IODINE-131 A female doctor not knowing that she was pregnant was administered 29.8 millicuries of iodine-131 for a hyper thyroid condition. She was asked if she was pregnant and she stated that she was not pregnant and she chose not to take a pregnancy test before being administered the iodine-131. Today, Community Hospital of Anderson, IN was notified that the female patient was 15 weeks pregnant when she received the 29.8 millicuries of iodine-131. The patient has been informed by her doctor. Calculated total body dose to the fetus is 11.69 rads and the calculated dose to the fetal thyroid is 27,840 rads. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE > SPECIFIED EFF LIMITS | [9 empty] | NON EMERGENCY | 3 | IN | HOS |  | 35.3045(a)(2) |  |  |  | 0 | 2003-08-25
40100 | 0 | WATTS BAR | 1 |  |  | [1] W-4-LP,[2] W-4-LP | 2003-08-25 09:45 | 2003-08-25 13:03 | 2003-08-25 | AUTOMATIC TURBINE TRIP/REACTOR TRIP DUE TO A SUDDEN PRESSURE RELAY SIGNAL FROM MAIN TRANSFORMER BANK "1C" "On August 25, 2003, Watts Bar (WBN) Unit 1 was operating at 100 percent power when there was an operation of a "Sudden Pressure Relay" for Main Transformer Bank 1C. The actuation of the relay resulted in a turbine trip and a subsequent reactor trip at approximately 0945 EDT. The cause of the relay actuation is under investigation at this time. All control rods inserted as required and the safety systems actuated as designed including the motor and turbine driven pumps for the Auxiliary Feedwater (AFW) System. AFW pump 1B-B was inoperable at the time of the trip due to work on an area cooler. However, the pump was available for service and started as required. Unit 1 is currently stable in Mode 3 and will remain in this mode until the completion of the investigation into the cause of the trip." At the time of the Sudden Pressure Relay for Main Transformer Bank 1C, an oil sample was being taken of the Transformer. Fire Brigade was sent but there was no fire and no explosion to the Transformer. The electrical grid is stable, and Emergency Core Cooling systems and the Emergency Diesel Generators are fully operable if needed. At this time only the 1B-B Motor Driven Auxiliary Feedwater pump is still operating. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | TN | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-25
40099 | 0 | MALLINCKRODT INC |  |  |  |  | 2003-08-25 06:30 | 2003-08-25 08:18 | 2003-08-25 | LOST NUCLEAR MATERIAL DURING DELIVERY The licensee reported five I-123 capsules that were lost when they fell out of the back doors of a panel van during shipment by Associates Couriers International (ACI). This occurred in Bridgeton, MO at Lindberg Boulevard at Blake. The I-123 capsules each contained 600 microcuries during precalibration and were calibrated for noon at 8/26/03 for 100 microcuries. The capsules are used for diagnostic thyroid disorders. The licensee indicated there was no significant health aspect of this event due to the short half life (i.e., 13 hours) of I-123 and the relatively low activity level. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 3 | MO | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-25
40098 | 0 | COLUMBIA GENERATING STATION | 2 |  |  | [2] GE-5 | 2003-08-22 02:34 | 2003-08-22 13:23 | 2003-08-22 | REACTOR CORE ISOLATION COOLING SYSTEM INOPERABLE "This ENS notification is made to report that on August 22, 2003 at 02:34 PDT Reactor Core Isolation Cooling was isolated due to the discovery of a degraded pilot cell in the Division 1 250 VDC battery. Operators isolated the steam inlet valve to the RCIC turbine (RCIC-V-1) because the minimum flow bypass valve, RCIC-V-19, (a primary containment isolation valve) was declared inoperable and isolated to comply with the plant TS. Isolation of RCIC-V-1 effectively removed RCIC from service since it is the containment isolation valve. "The event is considered reportable to the NRC under 10 CFR 50.72(b)(3)(v)(D) based on guidance contained in NUREG 1022, "Event Reporting Guidelines," and NRC Regulatory Issue Summary (RIS) 2001-14, "Position on Reportability Requirements for Reactor Core Isolation Cooling System Failure." A follow-up LER will be issued under 10 CFR 50.73(a)(2)(v)(D)." The licensee will be notifying the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | ACCIDENT MITIGATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | WA | POW |  | 50.72(b)(3)(v)(D) |  |  |  | 0 | 2003-08-22
40096 | 0 | U.S. AIR FORCE |  |  |  |  | 2003-08-07 08:30 | 2003-08-22 10:33 | 2003-08-22 | SIX CHEMICAL AGENT MONITORS CONTAINING NI-63 REPORTED MISSING During a recent inventory check at MacDill Air Force Base in Florida, six Chemical Agent Monitors (15 milliCuries each) containing Ni-63 were found to be missing. In February 2002, these devices were scheduled to be shipped to Kimhae, Korea. The monitors were submitted to the shipping department at that time. During an inventory check in May 2003, it was determined that these sources could not be found in either Korea or MacDill AFB. The U.S. Air Force is unsure whether the materials were lost after the shipment commenced or whether the materials were even shipped at all. Searches at a MacDill AFB warehouse are scheduled for next week in an attempt to locate these devices. The licensee notified NRC Region IV. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 2 | FL | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-22
40095 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-08-22 02:59 | 2003-08-22 04:05 | 2003-08-22 | TURBINE TRIP CAUSES AUTOMATIC REACTOR SCRAM AT OYSTER CREEK The licensee reported that an automatic reactor scram occurred at 0259 due to a turbine generator trip from a hi-hi moisture separator water level. One control rod indicated position 02; however, the remainder of the control rods indicated full in. All other systems and components functioned as designed. The licensee is cooling the plant down to cold shutdown. The licensee notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-08-22
40094 | 0 | RADIATION SAFETY ASSOCIATES, INC. |  |  |  |  | 2003-07-31 | 2003-08-21 13:06 | 2003-08-21 | TWO NICKEL-63 SOURCES LOST Radiation Safety Associates, a consultant for the licensee, reported that two detector cells for gas chromatography units containing 15 millicuries of nickel-63 were determined to be missing. The two sources are a Perkin Elmer Model # 6000204 (Serial # 1140) and an HP/Agilant Technologies Model # G2379A (Serial U0169). Radiation Safety Associates, Inc. was performing decommissioning activities for the licensee at its Stamford, CT, facilities. In performing an inventory of material in one area of the facility, they were unable to locate a cardboard box which supposedly contained the sources. The box had been set aside and marked "save" for disposal as radioactive waste. The consultant believes that the box was inadvertently disposed of as normal trash. Trash is picked up by Waste Management, Inc. at P&G-Clairol on a daily basis. Trash is then taken to the Bridgeport, CT incinerator where it is incinerated daily. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | CT | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-21
40093 | 0 | OK DEQ RAD MANAGEMENT |  |  |  |  | 2003-08-09 | 2003-08-21 11:11 | 2003-08-21 | AGREEMENT STATE REPORT - STOLEN TROXLER MOISTURE DENSITY GAUGE The following information was reported to the Operations Center by Oklahoma Department of Environmental Quality: "On August 19, 2003, the licensee RSO [Radiation Safety Officer] conducted a biweekly inventory of his gauges and discovered that one of them was missing. Upon investigation he discovered that the gauge, a Troxler 3411B, S/N 6322, was last used on August 8, 2003. The next day, the technician who used the gauge took the gauge out to his truck and, preparing to go to a jobsite, loaded the gauge into the toolbox bolted to [the] bed of the truck. He left the tool box unlocked while he helped another worker unload, then discovered the gauge was missing when he returned. He had since decided not to work that day. He did not report this to anyone because he assumed that the other worker had taken the gauge out on the job with him. The licensee has contacted the police and has prepared a press release offering a reward for return of the gauge. According to the licensee, the gauge contained 281.2 Mega Becquerels of activity [7.6 milliCuries] as of 5/15/83. The gauge was not in its transport case and the gauge plunger was apparently unlocked when stolen." The Troxler contained an Am: Be source, S/N CAA-2493 and a CS-137 source, S/N CC-3452. Oklahoma Department of Environmental Quality is considering issuing a press release to its border states. The licensee will be offering a reward for the return of the gauge. The Oklahoma Department of Environmental Quality has notified NRC Region 4 (Linda McLean). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | OK | OTH | AGR |  |  |  |  | 0 | 2003-08-26
40092 | -1 | POINT BEACH | 1 | 2 |  | [1] W-2-LP,[2] W-2-LP | 2003-08-20 11:20 | 2003-08-20 13:19 | 2003-09-04 | UNAUTHORIZED ACCESS TO A VITAL AREA Actual individual had been granted unescorted access to a vital area. Compensatory measures immediately taken upon discovery. NRC Resident Inspector will be notified of this event by the licensee. * * *UPDATE ON 09/04/03 AT 1905 EDT FROM THOMAS JESSESSKY TO NATHAN SANFILIPPO * * * Based on subsequent review, the licensee has determined that there was no security violation. This event has been retracted. For additional information, contact the Headquarters Operations Officer. NRC Resident Inspector was notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-08-20
40091 | -1 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-08-20 10:45 | 2003-08-20 12:45 | 2003-09-05 | UNAUTHORIZED ACCESS Actual individual had been granted unescorted access to a vital area. Compensatory measures immediately taken upon discovery. NRC Senior Resident Inspector was notified of the event notification by the licensee. * * * RETRACTION ON 09/05/03 AT 1008 EDT FROM HARRINGTON TO JOHN MACKINNON * * * Based on subsequent review, the licensee has determined that there was no security violation. This event has been retracted. For additional information, contact the Headquarters Operation Officer. R3DO (R. Gardner) & IAT (A. Davis) notified. NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-08-20
40090 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-07-31 12:00 | 2003-08-20 12:05 | 2003-08-20 | MISSING FOIL SOURCE "STATUS: new & closed "Licensee: STL Seattle (STL) "City and state: Tacoma, Washington "License number: R-0158 (a General Licensee) "Type of license: N/A - receipt of generally licensed gas chromatography cells from manufacturer or equivalent. "Date of event: July 31, 2003 - date of licensee notification letter to DOH (date of actual event is unknown). "Location of Event: Severn Trent Laboratories Inc., dba STL Seattle. "5755 8th Street East, Tacoma, Washington 98424 "ABSTRACT: STL Seattle sent DOH notification dated July 31, 2003 of a lost GC detector cell, foil source. The letter was received August 4, 2003. In the letter STL Seattle reported a missing 555 megabecquerel (15 millicurie), Nickel 63, foil source, Serial Number A5447 that was assumed to have been in a Varian ECD cell. The cell had been sent to a DOH specific licensee that is licensed for GC repair work. A technician at the GC-repair licensee discovered the missing foil source. The GC-repair licensee notified STL of the missing source. STL performed a thorough search of the lab but could not find the missing foil. "DOH contacted both STL and our GC-repair licensee after receipt of the letter. The Operations Manager at STL, [DELETED], who was the event reporter, could not initially be contacted. DOH did reach him for discussion two weeks later. DOH contacted our GC-repair licensee shortly after receipt of the notification. The GC-repair RSO mentioned that the ECD cell received from STL was an older cell that looked like it had never been used. The cell showed severe corrosion, which indicated that this cell had been in storage for a long time. The cell came in a box and was broken. The GC-repair RSO stated that the foil in these cells could fall out or removed easily, if the cell had been opened or if the ceramic portion of the cell was broken. This cell had a broken connector when received by the GC-repair licensee. The GE-repair RSO said that the cells can become loose in the Varian device and can break at the ceramic connector, which may have happened when someone attempted to remove it from the GC device. A tool is needed to remove the source from a cell in normal condition. The GC-repair RSO said that the cell didn't look like it had been tampered with in a purposeful manner. The GC-Repair RSO contacted [DELETED] when it was determined that the source was missing. They discussed the event in detail and [DELETED] was reminded, per the terms of GL device receipt requirements that they were not allowed to perform activities involving removal of sources. [DELETED] had recently taken over the program at STL Seattle. [DELETED] was further reminded of his record keeping responsibilities and the other limitations of receipt of GL GC detector cells. "When DOH talked with [DELETED] he confirmed that he had spoken with the GC-repair RSO and had been made aware that the source was missing after the cell had been received. The cell had not been used for a few years. A person, no longer employed by STL Seattle, was thought to have worked on the cell. He had not worked for the company in over a year. [DELETED] thought that any work done on the cell would have been a year or two previous to this individual leaving. He did not know if this work had included removing the foil from the cell. [DELETED] stated that when he had been informed of the missing radioactive source, staff at STL performed a search of the lab. He stated that they have a Geiger counter, but were not able to find the source. DOH re-informed [DELETED] that they are not licensed to perform source work on cells, [DELETED] agreed. He stated that this won't happen again . [DELETED] stated that STL management oversight of lab activities had recently been improved. "DOH issued an item of noncompliance to STL that was categorized as a Violation, for their failure to keep licensed radioactive material secure. DOH did not perform an on site investigation and no media attention was noted. "What is the notification or reporting criteria involved? 10 CFR 20.2201(a)(1)(ii) 30 days. "Activity and Isotope(s) involved: 555 megabecquerel (15 millicurie), Nickel 63. "Overexposures? Likely N/A but was unable to be determined. "This is a lost source: Manufacturer Varian Associates Inc., Model- 02-001972-0, Serial Number 5447. "Disposition/recovery? STL was several times reminded of their responsibilities and limitations. "Leak test? N/A "Vehicle: N/A "Release of activity? Loss of 555 megabecquerel (15 millicurie), Nickel 63, foil source. "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Exposure (intended/actual); consequences: exposure, if any, is unknown; consequences are unlikely. "Was patient or responsible relative notified: N/A "Was written report provided? Yes "Was referring physician notified? N/A "Consultant used? No" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-08-25
40089 | 0 | HONEYWELL INTERNATIONAL, INC. |  |  |  | URANIUM HEXAFLUORIDE PRODUCTION | 2003-08-19 11:00 | 2003-08-20 11:02 | 2003-08-20 | PARTIAL LOSS OF FIRE PROTECTION SYSTEM DUE TO PIPE LEAK AT HONEYWELL METROPOLIS The fire protection system became inoperable to the Feeds Material and Fluorine Plant when an underground water leak on the fire suppression system was discovered and isolated. This caused the fire protection system water supply to be isolated to the Feeds Material and Fluorine Plant and thereby disabling a safety system. The fire system (water suppression system) to the Feeds Material and Fluorine Plant remains out of service pending repair of the failed pipe. No estimate of the time required to repair and return to service of the fire suppression system water supply is available at this time. Licensee compensatory measures include the establishment of a fire watch and staging of fire hose to stations normally supplied by the fire suppression water system The licensee has notified the NRC Resident Inspector and NRC Region 3 (Ken O'Brien) of this event. The licensee has reported similar events under EN #39899 and EN #40015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | IL | FUE |  | 40.60(b)(2) |  |  |  | 0 | 2003-08-20
40088 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2003-08-18 11:00 | 2003-08-19 18:44 | 2003-08-19 | PATIENT EXCEEDED PRESCRIBED DOSE. A patient was undergoing an intravascular brachytherapy procedure using a Novoste 40 mm. Sr-90 system with a prescribed dose of 23 gray. Due to difficulties retracting the source train to its shielded position, the exposure time was 5.09 minutes (one minute longer than the planned 4.09 minutes). Preliminary estimates indicate that the delivered dose exceeded the prescribed dose by approximately 25 percent. Novoste was notified and a Novoste representative went to the medical facility to investigate. The Novoste system will be sent to Novoste in Georgia for analysis. The licensee continues to investigate and refine the dose calculations and will submit the required written report as soon as possible. Illinois assigned event number: IL030064. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-08-22
40087 | 0 | LOUISIANA RADIATION PROTECTION DIV |  |  |  |  | 2003-08-05 12:00 | 2003-08-19 14:23 | 2003-08-19 | OVEREXPOSURE Louisiana Radiation Protection Division received the following information on August 6, 2003 from Source Production and Equipment Co., located in Saint Rose. On August 5, 2003 a Hot Cell operator discovered material on the floor that was reading a high radiation level. He believed the source was a form of contamination which he attempted to clean up with his hand and a swipe. It was later discovered the same day that the source was a iridium-192 wafer that had inadvertently been released from the Hot Cell (the caller said that it took them fours hours to find out how the wafer got out of the Hot Cell). The persons radiation badge was sent in for a reading on August 6, 2003. Whole Body dose to the person from the badge was 157 millirems. Hand exposure calculation is still being investigated but the exposure to his hand ranges from 20 Rem to 700 Rems. Two weeks after the incident the person hand does not show any clinical indication to exposure to a high dose of radiation (no reddening). This event is under investigation. The size of the iridium-192 wafer is approx. 0.1 inches in diameter, 0.01 inches in thickness with a total activity of 7.6 curies. NRC Region 4 was notified of this event by Louisiana Radiation Protection Division. Called did not have the licensee's license number or the State of Louisiana event number. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | LA | OTH | AGR |  |  |  |  | 0 | 2003-08-22
40086 | 0 | WOLF CREEK | 1 |  |  | [1] W-4-LP | 2003-08-18 15:54 | 2003-08-18 18:36 | 2003-08-18 | AUTOMATIC REACTOR TRIP DUE LOW LOW "B" STEAM GENERATOR WATER LEVEL "At 1554 CDT on 08/18/2003 all four Steam Generators alarmed with Steam Flow/Feed Flow Mismatch followed by indication that there was no feedwater flow to the "B" Steam Generator. The reactor tripped approximately 20 seconds later on Steam Generator Low-Low Level, 23.5% Narrow Range, as required. A review of the plant computer information shows that event-initiating cause may be the unexplained closure of the "B" Feedwater Isolation Valve. "All plant safety related systems operated as required. The Steam Dumps, which function to remove excess heat as the secondary systems shutdown, exhibited control problems when they were shifted from temperature control mode to steam pressure mode, as required by the emergency operating procedures. The Steam Dumps are currently operating and controlling in manual mode. When the reactor tripped all four Steam Generator Atmospheric Relief Valves opened, a normal response for a trip from full power. The "A" Steam Generator Atmospheric Relief Valve was slow to close in automatic. The valve was closed in manual and returned to automatic and is controlling properly. "The plant is currently stable in Mode 3 at NOP and NOT while plant personnel investigate the causes of the trip and formulate the repair/restart plan." All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable. The NRC Resident Inspector is in the Control Room. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 4 | KS | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-18
40085 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2000-06-19 12:00 | 2003-08-18 18:10 | 2003-08-18 | OVEREXPOSURE "Exposure (intended/actual): consequences: Actual exposure received was Licensee: Fred Hutchinson Cancer "Research Center "City and state: Seattle, Washington "License number: WN-L042-1 "Type of license: Medium Broad License "Date of event: Reported by licensee on 19 June 2000, (indicated overexposure for the wear period between 5 April to 4 "May 2000). "Location of Event: Seattle, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) On 19 June 2000, the licensed RSO reported that their dosimetry badge provider (Landauer Inc.) had notified them that one of the Fred Hutchinson employees had apparently received an exposure of 317,791 millirem of high energy gamma radiation. This employee performs animal studies involving irradiations using both a Linac and a Cobalt 60 irradiator (a J.L. Shepherd Model 285, Serial Numbers 625 & 626). "The RSO immediately started an investigation of the reported overexposure. The RSO discovered that the individual's dosimetry badge had been lost during the second week of April 2000 for a period of about one week. An unknown person, via the inter-office mail system, returned it to the individual the next week. The employee was unable to recall any situation that would have lead to an exposure of any amount greater then the usual for the work performed over that time period. "Several circumstantial events as well as actual occurrences seem to indicate that the exposure was probably only received by the dosimetry badge. These were: first, the employee indicated that the dosimetry badge had been lost during the second week of April 2000, for a period of about one week. Second, only the Cobalt 60 irradiator was in operation during that period; the Linac was out of service then. Third, since several groups share use of the irradiator, the badge conceivably was found, in the irradiator room, by one of those people and returned in the inter-office mail system. Lastly, the employee never experienced any radiation related illnesses. The reported exposure of 317,791 millirem was removed from the employee's exposure history and replaced with a 20 millirem exposure (average monthly exposure for previous 12 months). "No DOH on-site investigation was made or media attention was noted. "What is the notification or reporting criteria involved? 10 CFR 20.2202 (a)(1) significant . After reviewing our incident files and the Handbook on Nuclear Material Event Reporting in the Agreement States , we determined that an immediate notification should have been sent to NRC. This did not occur; consequently we are now submitting this completed report, although late. "Activity and Isotope(s) involved: 518 terabecquerels (1400 curies), cobalt 60. "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) The initial notification indicated that one worker (employee) had been overexposed. The event did not involve a member of the public. The Landauer report indicated that an employee had received a whole-body exposure of 317,719 millirem of high-energy gamma radiation. No consequences will be realized since the exposure was later determined to only involve the dosimetry badge. The employee's exposure history was revised to indicate a 20 millirem exposure for that period of wear. "Lost, Stolen or Damaged? (mfg., model, serial number) The employee's dosimetry badge was lost for a period of about one week. "Disposition/recovery: Badges were to be used by placing them into a pouch for individuals using the irradiator devices. "Leak test? N/A "Vehicle: N/A "Release of activity? None "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: J.L. Shepherd Model 285 irradiator. "Exposure (intended/actual): consequences: Actual exposure received was estimated to be the usual, average amount of 20 millirem for that wear period. "Was patient or responsible relative notified? N/A "Was written report provided? Yes, from licensed RSO dated 21 July 2000. "Was referring physician notified? N/A "Consultant used? No" Washington State Event Report # WA-00-023. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-08-21
40084 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-08-17 15:51 | 2003-08-17 19:40 | 2003-08-17 | MANUAL REACTOR TRIP DUE TO LOSS OF "A" CONDENSATE PUMP. "At 3:51 PM EDT, on August 17, 2003, with the reactor at 100% in Mode 1, the reactor was manually tripped in response to a trip of the A condensate pump and subsequent trip of the A main feed pump. Both motor-driven auxiliary feedwater pumps and the turbine driven auxiliary feedwater pump started automatically due to Lo-Lo steam generator level. The operations crew responded to the event in accordance with the applicable plant procedures. The plant was stabilized at a normal operating no-load Reactor Coolant System (RCS) temperature and pressure following the reactor trip. The condensate pump electrical supply breaker tripped due to instantaneous overcurrent, possibly related to a severe electrical storm in the area at the time. The feed pump tripped due to the loss of the condensate pump. Offsite power remained available throughout the transient. A local fire department responded to a downed power line in the vicinity of the Harris plant but the response was not related to any onsite activities. "This condition is being reported as actuation of the reactor protection system and AFW in accordance with 10CFR50.72(b)(2)(iv)(B), and 10CFR50.72(b)(3)(iv)(A). 10CFR50.72 requires an 8-hour report for "Any condition that results in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B) of this section except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation." In this case, the AFW pumps start signal was due to Lo-Lo Steam Generator Level. "A root cause team is being formed to identify the cause and corrective actions" Due to low decay heat in the core, the Main Steam Isolation Valves were closed and the Steam Generator PORVs are being used to maintain the plant in a Hot Standby condition. No known leaking steam generator tubes are known. Both motor-driven and the turbine driven auxiliary feedwater pumps were secured after main feedwater was returned to service. All Emergency Core Cooling Systems and the Emergency Diesel Generators are fully operable if needed. The electrical grid is stable. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | M/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 2 | NC | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-17
40083 | 0 | CALIFORNIA RADIATION CONTROL PRGM |  |  |  |  | 2003-08-16 13:30 | 2003-08-16 21:22 | 2003-08-16 | DAMAGED MOLYBDENUM GENERATOR YELLOW II TYPE A BOXES Four molybdenum 99 generators which were being shipped from the Naval Medical Center in San Diego, CA to Mallinckrodt Medical Center in Maryland Hts, MO had their packaging become wet while they were at the Roadway Express terminal in Bloomington, CA. Battery acid spilled out of a battery that fell on the floor came in contact with the bottoms of the four packages. The four 45lb packages were placed into two drums. The packages were only wet and not damaged. There was no contamination or rad releases. The trucking firm will contact Mallinckrodt as soon as possible to determine how the material should be handled. The following information on the shipment was noted: TI - 0.12 rem UN 2915 Activity 5.395 (?) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 4 | CA | MAT | [5 empty] | 0 | 2003-08-16
40082 | 0 | PADUCAH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-08-15 23:55 | 2003-08-16 13:10 | 2003-08-16 | FAILURE OF AUTOCLAVE HIGH PRESSURE ISOLATION SYSTEM "At 2355 CST, on 8-15-03 the Plant Shift Superintendent (PSS) was notified of a failure of the C-360 #3 Autoclave High Pressure Isolation System. Steam was observed leaking from the autoclave head-to-shell interface at the six o'clock position shortly after initiating a cylinder heat cycle. At the time of discovery, the autoclave was in TSR mode 5 and the High Pressure Isolation System is required to be operable while in this mode. This system is designed to provide containment of the autoclave and prevent external release of UF6 during a system breach while heating a UF6 cylinder. The PSS declared the system inoperable and TSR LCO 2.1.3.1 actions were Implemented to remove the autoclave from service and place it in Mode 2, "Out of Service". Initial investigation of the incident revealed damage to the autoclave head-to-shall interface sealing surface. The damage resulted from a previous obstruction within the interface while closing the autoclave. Investigation is ongoing to determine the root cause of failure. The event is reportable as a 24 hour event, as required by 10 CFR 76,120©(2)(I); An event in which equipment is disabled or fails to function as designed when the equipment is required by a TSR to prevent releases, prevent exposures to radiation and radioactive materials exceeding specified limits, mitigate the consequences of an accident, or restore this facility to a preestablished safe condition after an accident. The equipment was required by TSR to be available and operable and no redundant equipment was available to perform the required safety function." The Senior NRC Resident Inspector has been notified of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | KY | FUE |  | 30.50(b)(2) |  |  |  | 0 | 2003-08-16
40081 | 0 | CATAWBA |  | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-08-16 07:53 | 2003-08-16 09:22 | 2003-08-16 | UNIT 2 COMMENCED A SHUTDOWN AFTER ENTERING TECH SPEC 3.0.3 Both channels 1 and 3 of the FWST (Refueling Water Storage Tank) level instrumentation failed high due to an apparent lightning strike. This placed Unit 2 in Tech Spec 3.0.3 requiring Unit 2 to be in Mode 3 within 7 hours, Mode 4 within 13 hours, and Mode 5 within 37 hours. The licensee will inform the NRC resident inspector. * * * UPDATE ON 08/16/03 @ 1255 BY POETZSCH TO GOULD * * * The licensee had its NOED approved to continue operation for up to 48 hours to repair the level channels. At 1115 the licensee halted power reduction @ 82%. They are now repairing both channels 1&3 and they should be completed within the next 3 hrs. The NRC Resident Inspector was notified. Notified Reg2 RDO (Ayres) * * * UPDATE ON 089/16/03 @ 1432 BY POETZSCH TO GOULD * * * The licensee has completed repair of channel 1 of the level instrumentation and returned it to service @ 1357, so as of this time they have exited the action statement. Channel 3 should be returned to service within one hour. The NRC resident Inspector was informed. Notified Reg 2 RDO (Ayres) | 0 | 95 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | PLANT S/D REQD BY TS |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | SC | POW |  | 50.72(b)(2)(i) |  |  |  | 0 | 2003-08-16
40080 | 0 | BEAVER VALLEY | 1 |  |  | [1] W-3-LP,[2] W-3-LP | 2003-08-15 08:31 | 2003-08-15 19:28 | 2003-08-15 | LICENSED PERSON RANDOMLY TESTED FOR BLOOD ALCOHOL At 0831 hrs on 08/15/2003 at Beaver Valley Power Station, a person licensed under 10 CFR Part 55 was randomly tested for fitness for duty and found to have a blood alcohol content (BAC) level of 0.01. It was determined that this person's BAC did not exceed the limit of 0.04 BAC when it was back calculated for their time on site prior to the random test. Therefore, this was not a positive test for alcohol. However, it was the opinion of the medical review officer that the tested person was not fit to remain on scheduled duty and the person was provided transportation off site property. This is being reported pursuant to 10 CFR 26.73(a)(2)(iv). The individual's license was not in active status and therefore was not performing licensed duties on 08/15/2003. The NRC Resident Inspector was notified of this event by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | FITNESS FOR DUTY |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 26.73 |  |  |  | 0 | 2003-08-15
40079 | 0 | WA DIVISION OF RADIATION PROTECTION |  |  |  |  | 2003-06-30 09:45 | 2003-08-15 18:09 | 2003-08-15 | TROXLER MOISTURE DENSITY GAUGE RUN OVER "Licensee: WA State Dept. of Transportation (WA DOT), South Central Region "City and state: Yakima, Washington "License number: WN-L065-1 "Type of license: Portable Gauge "Date of event: 30 June 2003 "Location of Event: near Walla Walla, Washington "ABSTRACT: (where, when, how, why; cause, contributing factors, corrective actions, consequences, DOH on-site investigation; media attention) On 30 June 2003, at about 9:45 AM, an errant motorist entered a coned-off lane and ran over a Troxler, Model 3430, moisture/density gauge, Serial Number 24671. The gauge contained two sealed sources, one of about 8 millicuries of Cesium 137 and the second of about 40 millicuries of Americium 241/Beryllium. The accident happened just north of Myra Road on State Route 125 near Walla Walla, Washington. "An errant motorist drove past a WA DOT road flagger holding a stop sign. The motorist entered a lane that had been coned-off. The motorist proceeded to drive down the restricted lane and ran over the gauge while it was being used to test for compaction. The gauge operator saw the approaching vehicle and attempted to stop it by waving his hands and yelling as the vehicle approached. The motorist, a senior, was apparently oblivious to the lane restriction. After the gauge was hit, it wedged under the vehicle and was dragged for approximately 90 feet down the road until the motorist finally became aware of the problem and stopped. The cause was inattention or inability to understand that the road conditions had changed. It appears that age of the driver contributed to the cause of the event. "The need to make any corrective action was deemed to be unnecessary. The gauge operator was operating per procedure and was only feet away from the gauge as it performed the test. The lane was restricted from travel by flagger and cone. "The incident destroyed the gauge. Impact with the vehicle caused the Cesium 137 source to be drawn back into its shielded position. Although pieces of the gauge housing, electronics and mechanisms were scattered along the 90-foot section of road that the vehicle traveled after impact the gauge, the sources were still attached to their respective parts of the gauge. Subsequent leak tests were negative. "DOH was not able to do an on site investigation due to the excessive distance to the event site and excessive time it would have taken to get staff to the site and clear the incident. The licensed RSO, a person trained to respond to events of this nature and having experience with similar events, went to the scene to give direction. The RSO performed surveys and an evaluation that allowed trained WA DOT personnel to release the area. The gauge parts were placed into the Troxler transportation box, a gravel/dirt mix was used to lower dose-rate readings to below a usual reading for an intact gauge, and the box was transported by trained WA DOT personnel to the WA DOT Headquarters facility for further evaluation, leak testing and disposition. "WA DOH personnel performed an investigation of events and the gauge at WA DOT Headquarters after the gauge arrived. WA DOH staff inspected the gauge parts including the sources, evaluated the circumstances of the event, reviewed the report information, and consulted with WA DOT staff regarding procedure, equipment and their plan to return the gauge to Troxler. Once WA DOH staff determined that sources were not leaking and the material was safe to be returned to Troxler, it was sent to Troxler via normal method. "There was no media attention. "What is the notification or reporting criteria involved? 10 CFR 30.50(B)(2) and 20.2201 - After reviewing the incident file and the Handbook on Nuclear Material Event Reporting in the Agreement States , we determined that a 24 hour notification should have been sent to NRC. This did not occur; consequently we are now submitting this completed report, although late. "Activity and Isotope(s) involved: 8 millicuries of Cesium 137 and 40 millicuries of Americium 241/Beryllium "Overexposures? (number of workers/members of the public; dose estimate; body part receiving dose; consequence) No members of the public received exposure in any amount. Calculation, survey readings and previous experience with similar gauge events indicate that WA DOT radiation worker staff only received exposure that is associated with usual gauge operations. Dosimetry reports will be evaluated upon receipt from the dosimetry processor. "Lost, Stolen or Damaged? (mfg., model, serial number) Troxler, Model 3430, Serial Number 24671 was destroyed (damaged). "Disposition/recovery: The gauge was returned to Troxler for disposal. "Leak test? A leak test was performed on each source. They were found to be negative. "Vehicle: (description; placards; Shipper; package type; Pkg. ID number) The gauge transportation vehicle was not involved in the event. "Release of activity? There was no release of activity. "Activity and pharmaceutical compound intended: N/A "Misadministered activity and/or compound received: N/A "Device (HDR, etc.) Mfg., Model; computer program: N/A "Exposure (intended/actual); consequences: N/A "Was patient or responsible relative notified? N/A "Was written report provided? The licensee provided a written report, dated 7 July 2003. "Was referring physician notified? N/A "Consultant used? No" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | WA | OTH | AGR |  |  |  |  | 0 | 2003-08-20
40078 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-08-15 10:15 | 2003-08-15 13:25 | 2003-08-15 | POWER LOST TO EMERGENCY SIRENS. At approximately 1015 hours on August 15, 2003 a review of the county siren overviews maps revealed that Westchester County had experienced another major power loss to its service. This resulted in more than 60 sirens being without utility-supplied power. This situation rendered the system inoperable for Westchester County as the sirens were without substantial power by which to be sounded. Further information revealed that the utility had to shed load. Route alerting capability is available. New York State and County representatives were notified of this event. The NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Standby | Hot Standby |  | Hot Standby | Hot Standby |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-08-15
40077 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-08-15 11:20 | 2003-08-15 13:15 | 2003-08-15 | DISCOVERED BY SECURITY A VULNERABILITY THAT COULD ALLOW UNAUTHORIZED/UNDETECTED ACCESS TO A VITAL AREA. COMPENSATORY MEASURES HAVE BEEN TAKEN. THE NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS BY THE LICENSEE. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SAFEGUARDS REPORTS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 73.71(b)(1) |  |  |  | 0 | 2003-08-15
40076 | 0 | US NAVY |  |  |  |  | 2003-08-08 | 2003-08-15 10:27 | 2003-08-08 | LOST US NAVY SOURCE The US Navy reported a lost device involving an IBIS (in-flight blade inspection system) used on helicopters. The device uses 500 microcuries of strontium-90. The device sealed source and registry number is CA321D103G. The master materials license number is 4523645. The US Navy reported that the device most likely fell off during flight approximately 17 miles northwest of New River, NC. A search for the device was unsuccessful. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | NC | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-08-15
40075 | 0 | FERMI | 2 |  |  | [2] GE-4 | 2003-08-14 16:10 | 2003-08-14 20:08 | 2003-08-15 | PLANT ENTERED AN NOUE DUE TO THE LOSS OF OFF SITE POWER The reactor scrammed from 100% power due to fluctuations occurring on the main generator and a loss of off site power. All rods fully inserted and all MSIV's closed. Reactor level is being maintained in the normal band of 173 to 214 inches using RCIC. Reactor pressure is being controlled via SRV's in lo-lo set mode between 905 and 1017 psig. Isolations occurred as expected for level 2 and level 3. HPCI and RCIC started on level 2 signal. HPCI has been shutdown but is available. All 4 EDG's started and loaded. The NRC Resident Inspector was notified. * * * UPDATE ON 08/15/03 AT 1754EDT BY ERIC SORG TAKEN BY MACKINNON * * * Unusual Event terminated at 1348 EDT on 08/15/03. R3DO (Sonia Burgess), NRR EO (Stu Richards) & FEMA (Bob Caldwell) notified. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 3 | MI | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-08-14
40074 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-08-14 16:11 | 2003-08-14 20:07 | 2003-08-14 | REACTOR TRIP/AUXILIARY FEEDWATER ACTUATION Received grid disturbance that caused reactor trip at 1611. The trip occurred due to over temperature delta set point being reached from load swings experienced on the generator. Subsequently in the recovery process, the Auxiliary Feedwater Pumps auto started from a signal from the Main Feedwater Pumps being secured. As a result of grid problems it was noted that Ginna did not meet the required number of emergency sirens (greater than 25% of sirens without power). NRC Resident Inspector was notified of this event by the licensee. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-14
40073 | 0 | INDIAN POINT | 2 | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-08-14 16:25 | 2003-08-14 18:49 | 2003-08-14 | EMERGENCY SIRENS LOST IN FOUR COUNTIES Emergency sirens lost in four counties due to a loss of power. At approximately 1830 hours power starting to be returned to the sirens. NRC Resident Inspector notified of this event by the licensee. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Hot Shutdown | Hot Shutdown |  | Hot Shutdown | Hot Shutdown |  | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-08-14
40072 | 0 | FITZPATRICK | 1 |  |  | [1] GE-4 | 2003-08-14 16:26 | 2003-08-14 17:17 | 2003-08-15 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF OFFSITE POWER. Automatic reactor scram due to a loss of offsite power. All rods fully inserted into the core. All emergency core cooling systems and the emergency diesel generators are operating properly. NRC Resident Inspector was notified of this event by the licensee. *****UPDATE ON 8/15/03 AT 0035 FROM PAGE TO LAURA***** Reactor vessel pressure is 93 psig. Plant electrical loads have been shifted back to offsite power and the EDGs were secured. The licensee exited the Unusual Event at 0039. The licensee tentatively plans to remain shutdown for a brief period to do some maintenance work. Notified R1IRC and FEMA(Hyman). * * * UPDATE ON 08/15/03 @ 1539 BY HALLIDAY TO GOULD * * * This updated is being provided to note a correction to the previously submitted time information and provide additional clarification of information that did not get captured. The automatic reactor scram occurred due to a generator load rejection. All rods fully inserted into the core, all emergency core cooling systems and the emergency diesel generators operated properly. The incorrect "event time" was communicated to the NRC during the initial notification (at 1717 hours) and subsequent updates. The event time listed was "1611" hours EDT. This was the actual time of the loss of offsite power. The declaration of the Unusual Event was at "1626" hours EDT, based on EAL 6.1.1, Loss of power to transformers T2/T3 for greater than 15 minutes (loss of offsite power). In addition, the initial notification of the Unusual Event was also used to document two reporting requirements under 10CFR50.72. Specifically, 10CFR50.72(b)(2)(iv)(B) for actuation of the reactor protection system (RPS) when the reactor is critical, and 10CFR50.72(b)(3)(iv)(A) for valid actuation of systems listed in paragraph (b)(3)(iv)(B). Various system actuations occurred as a result of the loss of offsite power. The NRC Resident Inspector was notified along with state and local agencies. Notified Reg 1 RDO(Meyer) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-08-14
40071 | 0 | NINE MILE POINT | 1 |  |  | [1] GE-2,[2] GE-5 | 2003-08-14 16:35 | 2003-08-14 17:15 | 2003-08-15 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES. Automatic reactor scram due to a loss of offsite power. All rods fully inserted into the core. All emergency core cooling systems are operating properly and the emergency diesel generators are operating properly. NRC Resident Inspector was notified of this event by the licensee. *****UPDATE 8/15/03 AT 0145 TO LAURA***** Offsite electrical power was restored. The licensee exited the Unusual Event at 0123. Notified R1IRC and FEMA(Heyman). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-08-14
40070 | 0 | DAVIS BESSE | 1 |  |  | [1] B&W-R-LP | 2003-08-14 16:10 | 2003-08-14 16:54 | 2003-08-15 | UNUSUAL EVENT DECLARED DUE TO A LOSS OF OFFSITE POWER. All systems operated as expected. Decay Heat pumps are available if needed. NRC Resident Inspector was notified of this event by the licensee. * * * UPDATE ON 08/15/03 @ 1942 BY LEISURE TO GOULD * * * The plant exited the NOUE at 1940 on 08/15/03. The grid is stable, the plant is on off site power and the emergency diesels are in standby. Notified FEMA (Steindurf), Reg 3 RDO (S. Burgess) and EO (S. Richards) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Cold Shutdown; FMode1: Cold Shutdown | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-08-14
40069 | 0 | INDIAN POINT |  | 3 |  | [2] W-4-LP,[3] W-4-LP | 2003-08-14 16:23 | 2003-08-14 16:50 | 2003-08-15 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES. Automatic reactor scram due to a loss of offsite power. All rods fully inserted. Supplying power to vital buses via emergency diesel generators. All systems operating properly. NRC Resident Inspector was notified of the event by the licensee. * * * UPDATE 2340EDT ON 8/14/03 FROM ANDY MIHALIK TO S.SANDIN * * * The following information was provided as an update: "RPS Actuation (loss of flow) due to loss of offsite power. Auto actuation of AFW in response to the unit trips. Auto start & load of Emergency Diesel Generators in response to the loss of offsite power. Unit 3 also experienced a second AFW auto start during the event. Unit 3 also entered Tech Spec LCO 3.0.3 for loss of two offsite circuits and one EDG inoperable. #31 EDG was declared inoperable when its associated Fuel oil storage tank inventory decreased below required." The licensee informed the state/local authorities and the NRC resident inspector. Notified R1IRC. *****UPDATE ON 8/15/03 AT 0226 FROM CELENTANO TO GOTT***** The licensee exited the Unusual Event at 0210 upon confirmation of a stable off-site power. Notified R1 IRC and FEMA(Heyman). | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | PLANT S/D REQD BY TS | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(i) | 0 | 2003-08-14
40068 | 0 | GINNA | 1 |  |  | [1] W-2-LP | 2003-08-14 16:12 | 2003-08-14 16:46 | 2003-08-14 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES. Automatic reactor trip due to a loss of offsite power. All rods fully inserted into the core. All emergency systems operated as expected. NRC Resident Inspector was of this event by the licensee. * * * UPDATE 0510EDT ON 8/15/03 FROM McCOY TO S.SANDIN * * * Unit exited the UE at 2108EDT on 8/14/03 after restoration of offsite power. The licensee informed state.local agencies and the NRC resident inspector. Notified R1IRC and FEMA(Hyman). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-08-14
40067 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2003-08-14 16:25 | 2003-08-14 16:39 | 2003-08-15 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES. Automatic reactor scram due to a loss of offsite power. All rods fully inserted. Supplying power to vital buses via emergency diesel generators. All systems operating properly. NRC Resident Inspector was notified of the event by the licensee. * * * UPDATE 2340EDT ON 8/14/03 FROM ANDY MIHALIK TO S.SANDIN * * * The following information was provided as an update: "RPS Actuation (loss of flow) due to loss of offsite power. Auto actuation of AFW in response to the unit trips. Auto start & load of Emergency Diesel Generators in response to the loss of offsite power." The licensee informed the state/local authorities and the NRC resident inspector. Notified R1IRC. *****UPDATE ON 8/15/03 AT 0226 FROM CELENTANO TO GOTT***** The licensee exited the Unusual Event at 0210 upon confirmation of a stable off-site power. Notified R1 IRC and FEMA(Heyman). | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  | IMode1: Power Operation; FMode1: Hot Standby | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  | 0 | 2003-08-14
40066 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2003-08-14 17:00 | 2003-08-14 17:34 | 2003-08-15 | NOUE WAS DECLARED AT 1700 DUE TO LOSS OF OFFSITE POWER The plant lost offsite power due to grid disturbance which resulted in a reactor trip from 100% power. The NOUE was declared because of loss of offsite power was greater than 15 minutes. The NRC Resident Inspector was notified. *****UPDATE ON 8/15/03 AT 0805 FROM MORAN TO LAURA***** All offsite power lines are available. The electrical power grid is stable. The licensee terminated the Unusual Event at 0730. Notified R1 IRC, FEMA (D. Sullivan) and DHS (W. Hall) | 0 | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | A/R | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode2: Power Operation; FMode2: Hot Shutdown | UNUSUAL EVENT | 1 | NY | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-08-14
40065 | 0 | OYSTER CREEK | 1 |  |  | [1] GE-2 | 2003-08-14 16:11 | 2003-08-14 18:16 | 2003-08-14 | REACTOR SCRAM FROM 100% POWER DUE TO OFF SITE ELECTRICAL GRID INSTABILITY Reactor scram from 100% due to off site electrical grid instability, but did not lose off site power. Reactor conditions at 1730 are normal reactor water level, reactor pressure 850-1000psig, MSIV's closed and all recirc pumps are off and reactor is in hot shutdown with all rods inserted. The NRC Resident Inspector | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | NON EMERGENCY | 1 | NJ | POW |  | 50.72(b)(2)(iv)(B) |  |  |  | 0 | 2003-08-14
40064 | 0 | PALISADES | 1 |  |  | [1] CE | 2003-08-14 16:07 | 2003-08-14 17:10 | 2003-08-14 | POWER GRID DISTURBANCE OCCURRED RESULTING IN A MOMENTARY DROP IN VOLTAGE At 1607 EDT a significant electrical power grid disturbance occurred resulting in a momentary drop in voltage at the site, including both 2400 VAC safety busses 1C and 1D. The reduced voltage on the 2400VAC safety busses caused both emergency diesel generators to auto start, but not load. The plant is stable at pre-event conditions. The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | MI | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-08-14
40063 | 0 | PERRY | 1 |  |  | [1] GE-6 | 2003-08-14 16:10 | 2003-08-14 16:33 | 2003-08-15 | UNUSUAL EVENT DECLARED DUE TO LOSS OF OFFSITE POWER GREATER THAN 15 MINUTES. Automatic reactor scram due to a loss of offsite power. All rods fully inserted. Supplying power to vital buses via emergency diesel generators. All system operating properly. NRC Resident Inspector was notified of the event by the licensee. * * * UPDATE ON 08/15/03 @ 2007 BY STRACH TO GOULD * * * The NOUE was terminated at 1952. Off site power was restored and the emergency diesels secured. Notified FEMA (Austin), Reg 3 RDO (Burgess) and EO (Richards) | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | EMERGENCY DECLARED |  |  |  | IMode1: Power Operation; FMode1: Hot Shutdown | UNUSUAL EVENT | 3 | OH | POW |  | 50.72(a) (1) (i) |  |  |  | 0 | 2003-08-14
40062 | 0 | GEORGIA RADIOACTIVE MATERIAL PGM |  |  |  |  | 2003-08-12 | 2003-08-14 14:32 | 2003-08-14 | STOLEN NITON ANALYZER "Overnight, August 12, 2003, unknown persons entered the licensee's facility and stole various office equipment including copiers, computers and a Niton analyzer containing radioactive material." The Niton Analyzer is a model XLi or XLp series device which contains 30 millicuries of Am-241. The Licensee, Kewell, LLC, reported the theft to the local law enforcement. Media attention: None Georgia Event Report No: GA-2003-241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | GA | OTH | AGR |  |  |  |  | 0 | 2003-08-19
40061 | 0 | KEWAUNEE | 1 |  |  | [1] W-2-LP | 2003-08-14 09:10 | 2003-08-14 10:57 | 2003-08-14 | EP SIRENS OUT OF SERVICE IN KEWAUNEE COUNTY "At 0910 on August 14, It was reported to the Control Room that all thirteen Kewaunee County sirens had a communications problem that rendered them out of service. The percent siren coverage population lost is 68.52%. The State and County have been notified of the siren failures. The siren vendor has been contacted to begin troubleshooting the problem. "This is being reported under 10 CFR 50.72(b)(3)(xiii) as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability (loss of greater than 50% of emergency sirens). It is also being reported under 10 CFR 50.72(b)(2)(xi) as any event or situation, related to the health and safety of the public or onsite personnel, or protection of the environment, for which a news release is planned or notification to other government agencies has been or will be made." The NRC resident inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE | OFFSITE NOTIFICATION |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 3 | WI | POW |  | 50.72(b)(3)(xiii) | 50.72(b)(2)(xi) |  |  | 0 | 2003-08-14
40060 | 0 | UNIVERSITY OF PENNSYLVANIA |  |  |  |  | 2003-07-01 | 2003-08-14 09:00 | 2003-08-14 | MISSING SOURCE AT UNIVERSITY OF PENNSYLVANIA "During a routine sealed source inventory in July 2003, a technician from the University of Pennsylvania's Office of Environmental Health and Radiation Safety (EHRS) found that a Hewlett-Packard 6890 gas chromatograph (GC) containing a generally licensed 15 millicuries source of Ni-63 was missing from a laboratory undergoing renovations. EHRS contacted faculty and staff associated with the laboratory trying to locate the instrument. After an extensive search, it was determined that the GC was most likely sent to a scrap metal dealer. According to NUREG-1717, Systematic Radiological Assessment of Exemptions for Source and Byproduct Materials, the dose to any individual from a scrapped Ni-63 gas chromatograph source would be less than 0.01 millisievert (1 millirem)" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | PA | MAT |  | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-14
40059 | 0 | REYNOLDS ARMY COMMUNITY HOSPITAL |  |  |  |  | 2003-08-11 | 2003-08-13 19:11 | 2003-08-13 | PATIENT RECEIVES THERAPEUTIC DOSE INSTEAD OF DIAGNOSTIC DOSE OF I-131 On 8/13/03, the Chief Radiologist determined that a patient undergoing a diagnostic procedure had been given a dose of I-131 that far exceeds the customary diagnostic dose for a whole body scan. A patient at the hospital was incorrectly prescribed 5 milliCuries of I-131 and received 5.45 milliCuries of I-131 in preparation for a diagnostic scan evaluation for sub-sternal ectopic thyroid tissue. Additionally, the patient has a history of Grave's disease (a malady affecting the thyroid). According to the Chief Radiologist, the customary dose for this type of procedure is in the 1-2 milliCuries range. The patient has been notified by the hospital and will undergo further diagnostic imaging. The patient has undergone counseling at the hospital concerning the radiation effects of the I-131. Additionally, family members of the patient will be given bioassays to determine uptake, if any. The prescribing physician will be notified. The Medical Command Radiation Safety Officer has been notified. The hospital has placed procedural precautions in place to minimize the chances of a future occurrence of this event. Henceforth, all diagnostic uses of I-131 will be approved by the Chief Radiologist. The only allowed diagnostic uses will be for whole body scans for follow-up evaluations of the efficacy of thyroid cancer treatment or for the treatment of Grave's disease. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Hospital | DOSE <> PRESCRIBED DOSAGE | [9 empty] | NON EMERGENCY | 4 | OK | HOS |  | 35.3045(a)(1) |  |  |  | 0 | 2003-08-13
40058 | 0 | NINE MILE POINT |  | 2 |  | [1] GE-2,[2] GE-5 | 2003-08-12 19:01 | 2003-08-13 18:35 | 2003-08-13 | 24-HOUR CONDITION OF LICENSE REPORT DUE TO INOPERABLE INVERTER "On August 11, 2003 at 1901 [EDT], annunciator was received in the Nine Mile Point Unit 2 Control Room that 2VBA-UPS2B had transferred to its maintenance power source. With the inverter not powering the UPS loads, the inverter was declared inoperable as of 1901. This required entry into Technical Specification (TS) 3.8.7, Condition A with an action of restore inverter to operable within 24 hours or enter Condition B with actions to be in Mode 3 in 12 hours and Mode 4 in 36 hours. "On August 12 at 1958 hours, enforcement discretion was received from Region 1 & NRC headquarters to extend TS 3.8.7, Condition A an additional 18 hours to complete repairs to the equipment. Operability was restored to 2VBA-UPS2B on August 13 at 0508 hours. "This notification is being made in accordance with NMPNS, LLC Facility Operating License section 2.F that requires 24 hour notification, because discretionary enforcement was granted." The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2003-08-13
40057 | 0 | HOPE CREEK | 1 |  |  | [1] GE-4 | 2003-06-15 14:47 | 2003-08-12 16:11 | 2003-08-12 | 10 CFR 50.73 REPORT "The report is being made under 10 CFR 50.73(a)(2)(iv)(A) and is not considered a Licensee Event Report. "During performance of a Surveillance Order, a Reactor Building Ventilation System isolation was initiated at 14:47 on 6/15/03. The apparent cause of the isolation was human error due to the incorrect de-energizing and placement of test leads on the 'B' train component instead of the 'A' train component as required by procedure. After the 'B' Train Sorrento RM-80 (1SP-RY4856B) was de-energized, the 'A' train detector (1SP-RE-4857A) was disconnected in accordance with the procedure. When the opposite train detector was disconnected, the Reactor Building Ventilation System isolation was initiated. "Upon receipt of the Reactor Building Equipment (RBE) isolation, the following systems isolated: "Torus water cleanup, Drywell (DW) floor and equipment sumps, Drywell Leak Detection (DLD) sampling skid, Reactor Building Ventilation System (RBVS) isolated, Radwaste (RW) ventilation isolated, Filtration Recirculation Ventilation System (FRVS) auto started, B Station Service Water (SSW) pump and B Station Auxiliary Cooling System (SACS) pump auto started, Primary Containment Instrument (PCI) gas valves and compressors isolated. "The operating crew entered the procedure for Primary Containment abnormal condition B. When instrument technicians restored the 'B' RBE radiation monitor, the operating crew reset PCI Signal in accordance with the Operating Procedure and restored the systems to normal. "All safety systems responded to the isolation signal according to design." | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | INVALID SPECIF SYSTEM ACTUATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NJ | POW |  | 50.73(a)(1) |  |  |  | 0 | 2003-08-12
40056 | 0 | KENTUCKY DEPT OF RADIATION CONTROL |  |  |  |  | 2003-06-23 15:30 | 2003-08-12 14:10 | 2003-08-12 | AGREEMENT STATE REPORT "On June 23, 2003 at 3:30 PM the [University of Kentucky] radiation safety office received a call from an AU [Authorized User] in the Dept. of Biology, because a shipment of I-125, triiodothyronine, 100 microcuries, had not been received. Upon review of the records it was found that the package had arrived on June 18, 2003, and had measured 10 [millirem]/hr at the surface, 0.1 [millirem]/hr @ 1meter, and no external contamination. The Radiation Safety Office shipping paper record shows the I-125 package was included for delivery to room 109, Research Building 3, on June 19. The required signature of receipt for the package was not obtained. With the DOT shipping labels removed, the greatest likelihood is that the package was put into the ordinary trash. A thorough search of the Radiation Safety Office facilities and vehicles was conducted on June 23. On June 24, the authorized user's lab was searched, including use of a low energy NAI (Tl) detector, as well as all labs where deliveries were made on June 19. No trace of the package or contents has been found. It was concluded that the highest probability was that the package entered the normal waste stream and went to a landfill. Once in a landfill, the I-125 will be sequestered from any contact, and will be essentially non-radioactive in 1.65 years. Assuming worst case scenarios, the dose rate to the torso would be about 10 [millirem]/hr or less, and would have to be held against the body continuously by a single individual for 10 hours to produce a dose in excess of 100 [millirem]. Additionally there is no indication or likelihood of intentional or accidental ingestion of the contents since this is not intended for human use. However, if the entire 100 microcuries were ingested by a single individual, as sodium iodide, the thyroid dose would be 78 rem, and the effective dose would be 2.4 rem. While no thyroid dose information has been found for the triiodothyronine form, the effective dose from ingestion of 100 microcuries would be 17 [millirem]. Surveys are conducted on a continual basis, if the package did not go to a landfill it would likely be found during monthly use area surveys or quarterly supervisory surveys. No NOV was issued based on the corrective actions taken by licensee to correct deficiencies prior to report completion." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | KY | OTH | AGR |  |  |  |  | 0 | 2003-08-15
40055 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-08-08 | 2003-08-11 16:32 | 2003-08-11 | AGREEMENT STATE REPORT - TEXAS "On Friday, August 11, 2003, the Licensee was transporting the gauge in a Nissan Pickup truck that had a defective tailgate. The Type 7A package was locked to the pickup with a chain but was held in place with a very small and cheap padlock. Also in the truck were concrete samples being transported for analysis. While transiting FM 471, the tailgate failed to the open position when the concrete samples shifted and pushed the gauge (Troxler Model 3430, Serial No. 28510, with two sealed sources - Am-241 /Be, nominal 40 millicuries, Serial No. 47-25576; and Cs-137, nominal 8 millicuries, Serial No. 750-2732) out of the bed and broke the lock allowing the gauge to become detached from the truck. The gauge was found by a member of the public laying in the middle of Highway FM471 being swerved around by traffic. The member of the public stopped and picked up the package and placed in his vehicle and transported it to his residence at [address deleted], Helotes, Texas. He opened the package which was not secured by a locking device. There is no indication that the member of the public exposed the sources. He made notification to the Helotes Fire Department who in turn notified the Texas Department of Health's Public Health Region 8, Radiation Control Office in San Antonio. The Public Health Region responded with a Radioactive Materials Inspector who determined that the gauge was intact and appeared to have no damage. The Licensee was notified and retrieved the gauge." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-08-14
40054 | 0 | BROWNS FERRY |  | 2 |  | [1] GE-4,[2] GE-4,[3] GE-4 | 2003-08-10 23:31 | 2003-08-11 05:04 | 2003-08-11 | AUTOMATIC START OF EMERGENCY DIESEL GENERATORS DURING BUS TRANSFER FOR MAINTENANCE "Unit 1/2 A and B Diesel Generators auto started on Undervoltage while attempting to transfer Shutdown Bus 1 to Alternate supply, the alternate supply breaker failed to close, resulting in a momentary undervoltage condition on the Shutdown Bus and 4160V Shutdown Boards A & B. Shutdown Bus 1 was reenergized by reclosure of the Normal feeder breaker. The Diesel Generators did not tie onto the board due to the voltage returned to normal prior to the DG obtaining rated speed and voltage when the operator reclosed the normal supply breaker. SBGT [Standby Gas Treatment] & CREV [Control Room Emergency Ventilation] auto started and Refuel Zone ventilation isolated due to a failure of Unit 1 Refuel Zone Rad monitor; Unit 2 Reactor Zone ventilation isolated due to a momentary loss of I & C 'A'. "This event is reportable as an 8 hour report per 10CFR50.72(b)(3)(iv)(A) as 'Any event or condition that results in valid actuation of any of the systems listed in (b)(3)(iv)(B), specifically Emergency AC Electrical power systems, including: Emergency Diesel Generators (EDGs).' "This is also reportable per 10CFR50.73(a)(2)(iv)(A) for the above conditions as a 60 day written report." The licensee reported that affected ventilation systems and electrical systems have been returned to a normal configuration with the exception of the shutdown bus "43 switch" [in normal supply]. All Emergency Diesel Generators are operable and in standby. Offsite electrical power supply to the station is in a normal configuration. The licensee has notified the NRC Resident Inspector. | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | VALID SPECIF SYS ACTUATION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 2 | AL | POW |  | 50.72(b)(3)(iv)(A) |  |  |  | 0 | 2003-08-11
40053 | 0 | CALLAWAY | 1 |  |  | [1] W-4-LP | 2003-08-08 12:54 | 2003-08-08 17:10 | 2003-08-08 | UNANALYZED CONTROL ROOM HABITABILITY ISSUE AT CALLAWAY "On 7/17/03, during a plant walkdown and design review for Control Room Habitability, it was identified that the pressure boundary doors located at Health Physics Access were open. A review of the Request For Resolution that approved leaving the pressure boundary doors open on a continuous basis revealed an error in the engineering evaluation. A previously unidentified air flow-path would allow unfiltered outside air to mix with areas of the Control Building that are credited in the Final Safety Analysis Record (FSAR) analysis of record for post-LOCA radiological consequences to Control Room personnel. The Callaway/SNUPPS Control Room HVAC design is unique in that it credits two separate mixing volumes, the Control Building and the Control Room. The air communication pathway identified on 7/17/03 impacts the Control Building volume. Initial calculations completed on 8/8/03 determined that the post LOCA thyroid dose to Control Room personnel would be approximately 31.5 REM. The FSAR reported value is 25.55 REM and the regulatory limit is 30 REM. This exceeds the current FSAR Analysis Of Record and is being reported as an unanalyzed condition. Upon initial identification of the opened doors and the air communication pathway, the doors were closed and a plant bulletin was issued informing personnel to maintain these doors closed when not in use." The NRC Resident Inspector was notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | MO | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-08-08
40052 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-08-07 09:15 | 2003-08-07 16:49 | 2003-08-07 | LOSS COMM/ASMT/RESPONSE At 0915 EDT on 8/7/03, during testing of the Prompt Alert Notification Sirens, 44 of 112 (39 percent) of the sirens were found to be inoperable due to a failed radio repeater. The repeater was repaired, and all sirens declared fully operable at 1010 EDT on 8/7/03. The NRC Resident Inspector was informed of this event. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-08-07
40051 | 0 | DEPARTMENT OF THE NAVY |  |  |  |  | 2003-06-03 | 2003-08-07 13:35 | 2003-08-07 | RADIOGRAPHIC EXPOSURE DEVICE FAILURE "Description of the equipment problem. On June 3, 2003, gamma radiography operations using an AEA Technology/QSA Model 660A exposure device in a permanent radiography facility at Shore Intermediate Maintenance Activity were being performed under the authority of Naval Radioactive Materials Permit (NRMP) No. 0465918--A1NP. On the tenth exposure of the day the radiographer attempted to retract the radiographic source into the radiographic exposure device. The radiographer placed the drive cable brake in the "off" position and rapidly cranked the source in the retract direction. The number of turns coming in matched the number of turns going out. The permanent facility gamma alarm shut off, however the radiographer did not hear the locking slide mechanism engage which is normally heard clearly when retracting the source. When attempting to re-expose the source as required by the operating procedure, the source did expose again. The Radiation Safety Officer was present and directed the radiographer to retract the source again. As with the first attempt to retract the source, the slide bar did not click in the safe position. Again and the gamma alarm shut off. The Radiation Safety Officer entered the permanent facility with, an operating survey meter. The locking slide bar indicated green (safe) but it was not locked in that position. The Radiation Safety Officer approached the device and observed a reading of approximately 8 millirem/hour on the front of the device and 10 millirem/hour on the back of the device. She exited the permanent facility and discussed the situation with the radiographer. The Radiation Safety Officer then directed the radiographer to maintain control of the crank assembly handle and she entered the permanent facility with a survey meter and pushed the slide bar to the red (expose) position. The Radiation Safety officer exited the permanent facility and instructed the radiographer to retract the source to the fully locked position. The retraction was successful and the slide bar was heard to click to the fully green (safe) position. The Radiation Safety Officer checked her self-indicating pocket dosimeters which both indicated zero exposure. "The source was transferred to an AEA 650L source changer on June 4, 2003. A "dummy" source was installed in the exposure device and the locking slide bar was placed in various positions to experiment and recreate the scenario. Frequently during these tests, the radiographers were not able to lock the slide into place without unlocking the drive cable crank assembly and applying minimal pressure towards the expose position. This is considered a neutral position and not an exposed position. With minimal pressure the slide bar mechanism easily locked into the exposed position. "Cause of each incident. The cause of the incident appears to be twofold. Primarily the compression springs for the posi-lock may have been excessively worn. Secondarily, the Shore Intermediate Maintenance Activity, San Diego operating procedure did not call for them to unlock the crank assembly cable lock prior to rotating the selector ring to the operate position and pushing the posi-lock slide bar from the green (retracted) position to the red (operate) position as stated in the most recent AEA exposure device manual. We believe that the faulty springs were the main factor as the posi-lock slide bar can be pushed to the red position with the crank assembly cable lock in the "on" position but that procedure may have contributed to the excessive wear on the compression springs. "Name of the manufacturer and model number of equipment involved in the incident. The equipment involved in the incident was manufactured by AEA Technology/QSA and consisted of a Model 660A exposure device, serial number A4450 with a 13.6 curie Ir-192 source. "Place, date and time of the incident. The incident occurred at Shore Intermediate Maintenance Activity, San Diego, California in a permanent facility on June 3, 2003. "Actions taken to establish normal operations. The Radiation Safety Officer entered the permanent facility and manually pushed the locking slide bar to the unlocked (red) position. The Radiation Safety Officer exited the permanent facility and instructed the radiographer to attempt to retract the source. The source was successfully retracted to the fully locked position and the locking slide bar was heard to lock. "Corrective actions taken or planned to prevent recurrence. Shore Intermediate Maintenance Facility, San Diego replaced the compression springs for the posi-lock assembly on the exposure device. Additionally, they have changed their operating procedure to unlock the crank assembly cable lock prior to rotating the selector ring to the operate position and pushing the posi-lock slide bar from the green (retracted) position to the red (operate) position." The licensee notified R2 (Diaz). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 30.50(b)(2) |  |  |  | 0 | 2003-08-07
40050 | 0 | PILGRIM | 1 |  |  | [1] GE-3 | 2003-08-07 11:31 | 2003-08-07 13:07 | 2003-08-07 | OFFSITE NOTIFICATION "At approximately 1131 [EDT] on August 7, 2003, an error during prompt alert notification system testing resulted in all sirens in the town of Duxbury, Massachusetts to wail for 15 to 20 seconds. Appropriate state and local authorities have been notified. Investigation into the cause is continuing." The NRC Resident Inspector has been notified. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | MA | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-08-07
40049 | -1 | BEAVER VALLEY |  | 2 |  | [1] W-3-LP,[2] W-3-LP | 2003-08-06 16:30 | 2003-08-06 19:12 | 2003-09-18 | UNANALYZED CONDITION "On 8/06/2003 at 1630 hours, the Beaver Valley Power Station (BVPS) Unit 2 control room was notified by Engineering that the manual operator actions specified in Unit 2 post-fire procedures are not adequate for defeating a potential fire-induced spurious operation of the Power Operated Relief Valves (PORVs). The procedure step de-energizes the PORVs by opening breakers at the d-c distribution panel. This action alone would not be sufficient to prevent a cable-to-cable hot short from re-energizing the circuit since the de-energized circuit is routed in cable trays with other energized circuits in the affected fire areas. Preliminary reviews have identified the following potentially affected fire areas: CB-1 Control Building Instrumentation and Relay Area CB-2 Control Building Cable Spreading Room CB-3 Control Building Main Control Room CB-6 Control Building West Communication Room CT-1 Cable Tunnel CV-1 Cable Vault and Rod Control Area SB-1 Emergency Switchgear Room (Orange) RC-1 Reactor Containment "An hourly roving fire watch patrol has been established for the affected fire areas as compensatory measures, with the exception of the Main Control Room and the Reactor Containment area, until the condition is fully evaluated and resolved. The Main Control Room is continuously manned and does not require an hourly fire watch patrol. The Reactor Containment area is not accessible during normal power operations and, as such, compensatory measures for this area will include a once-per-shift verification of remote instrumentation by operations personnel to confirm that there are no abnormal conditions or indications for this area. "This condition was discovered during the review of manual operator actions for fire-induced spurious operations to confirm the safe shutdown circuit analysis is consistent with the manual actions identified in the procedures. "This condition is being reported pursuant to 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition that significantly degraded plant safety since the failure to assure the PORVs remain in the closed position could result in the failure to meet the fire protection safe shutdown criteria. BVPS Unit 2 was licensed to the NUREG 0800 Standard Review Plan 9.5.1 "Fire Protection Program", and License Condition 2.F requires compliance to the provisions of the approved fire protection program as described in the Final Safety Analysis Report. UFSAR Section 9.5A.1.2.1.6 states that the safe shutdown capability should not be adversely affected by a fire in any plant area which results in spurious actuation of the redundant valves in any one high-low pressure interface line. Even though there is a very low likelihood of multiple shorts causing a spurious PORV actuation in an ungrounded DC circuit, the existing actions to prevent re-energizing the circuit and causing a spurious actuation of the PORVs is not consistent with the NRC guidance for high-low pressure interface valves. "The NRC resident inspector has been notified." * * * UPDATE ON 8/7/03 AT 1726 EDT FROM D. SOMMERS TO E. THOMAS * * * "On 8/07/03 at 1515, the following additional areas were identified as being potentially affected by this condition: CV-2 Cable vault and Rod Control Area (East) CV-3 Cable vault and Rod Control Area (Elev 755'6") SB-2 Emergency Switchgear Room (Purple) SB-3 Service Bldg. Cable Tray Area ASP Alternative Shutdown Panel Room "Interim compensatory measures in the form of hourly roving watch patrols have been expanded to include the above noted areas until the condition is fully evaluated and resolved. "The NRC Resident Inspector has been notified." Notified the Region 1 Duty Officer (C. Anderson) * * * UPDATE 0940 EDT ON 9/18/03 FROM PETE SENA TO S. SANDIN * * * The licensee is retracting this report based on the following: "Beaver Valley Power Station (BVPS) Unit No. 2 retracts the notification made on 08/06/2003 at 19:12 hrs regarding the event reported under 10 CFR 50.72(b)(3)(ii)(B) [ENS #40049]. The previous notification identified a potential unanalyzed condition that significantly degraded plant safety since the failure to assure the PORVs remain in the closed position could result in the failure to meet the Fire Protection Program safe shutdown criteria. "The postulated event for spurious PORV opening due to an external cable-to-cable hot short from a fire was subsequently analyzed. It was determined that since the reactor core does not experience an unrecoverable plant condition and the radiological conditions remained bounded by analyzed DBAs, the plant's safe shutdown capability for a fire event is maintained. Although the now-credible spurious opening of a PORV is a deviation from the current Fire Protection Program criteria, the results of the spurious PORV opening does not adversely impact the plant's safe shutdown capability and hence is not a significant degradation of plant safety. Therefore this condition is not reportable pursuant to either 10 CFR 50.72(b)(3)(ii)(B) nor 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. "Compensatory measures in the form of shiftly fire watch patrols for the affected fire areas, with the exception of the Main Control Room and Reactor Containment area (as described in prior notifications), will remain in place until the Fire Protection Program non-conformance issue is dispositioned." The licensee informed the NRC Resident Inspector. Notified R1DO(Gray). | 0 | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | N | N | N | Power Reactor | UNANALYZED CONDITION |  |  |  | IMode2: Power Operation; FMode2: Power Operation | NON EMERGENCY | 1 | PA | POW |  | 50.72(b)(3)(ii)(B) |  |  |  | 0 | 2003-08-06
40048 | 0 | SC DIV OF HEALTH & ENV CONTROL |  |  |  |  | 2003-07-31 16:00 | 2003-08-06 15:53 | 2003-08-06 | AGREEMENT STATE REPORT - MEDICAL EVENT On 7/31/03, at approximately 1600 EDT, an Iotrex I-125 sealed source was administered to a brachytherapy patient to treat a brain tumor. The sealed source contained 325 millicuries of I-125. On 8/5/03 at 1148 EDT, upon removal of the sealed source from the patient, the hospital staff noted that the amount of I-125 withdrawn from the patient was only 31.5 millicuries. The source is a liquid that is inserted into a balloon inside the patient's skull, then removed after a designated amount of time. On 8/6/03, a manufacturer's representative from Proxima accompanied hospital staff to inspect the catheter and balloon that were used during this administration. The catheter and balloon were visually inspected and tested with a dye for leaks. No leaks were apparent during either test. The licensee did not report any immediate adverse affects on the patient. The referring physician was informed of this event. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 2 | SC | OTH | AGR |  |  |  |  | 0 | 2003-08-11
40047 | 0 | FROEHLING &ROBERTSON INC |  |  |  |  | 2003-08-05 06:30 | 2003-08-05 09:03 | 2003-08-05 | STOLEN MODEL 3411 TROXLER GAUGE A Troxler gauge model # 3411 serial # 10605 containing 4.8 millicuries of Cs-137 (serial # 408040) and 38.8 millicuries Am-241:Be (serial # 462027) was stolen from the back of the technician's pickup truck which was parked in his yard in Norfolk, VA. The gauge was locked in its molded case and chained to the truck. The chain had been cut, and the gauge and case were removed sometime early this morning or late last night from the truck. The police were called to the scene and are investigating. No press release has been issued at this time and no reward has been offered. The licensee notified Reg 2. * * * UPDATE AT 1437 EDT ON 08/04/03 FROM BILL BRIODY TO JOLLIFFE * * * At approximately 1200 EDT on 08/04/03, a private citizen found the gauge on the side of I-64 in the Norfolk, VA area. The lock on the case had been cut and there was no significant damage to the case. The sources were undamaged and intact inside the case. The citizen took the gauge to his home and notified the VA Department of Transportation who took possession of the gauge. The licensee plans to submit a written report to NRC Region 2. Notified R2DO Steve Cahill and NMSS Doug Broaddus. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | LOST/STOLEN LNM>1000X | [9 empty] | NON EMERGENCY | 2 | VA | MAT |  | 20.2201(a)(1)(i) |  |  |  | 0 | 2003-08-05
40046 | 0 | HADDAM NECK | 1 |  |  | [1] W-4-LP | 2003-08-04 10:15 | 2003-08-04 10:44 | 2003-08-04 | OFFSITE NOTIFICATION TO STATE OF CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION APPROXIMATELY ONE TEASPOON OF DIESEL FUEL OIL CONTACTED THE SOIL WHEN THE RAIN WASHED IT OFF THE TOP OF A PORTABLE FUEL OIL TANK. THE AREA WAS CLEANED UP. THE PORTABLE FUEL OIL TANK WAS MOVED TO A PAVED SURFACE. THE LICENSEE NOTIFIED THE STATE OF CONNECTICUT DEPARTMENT OF ENVIRONMENTAL PROTECTION OF THE OIL SPILL. NRC RESIDENT INSPECTOR WAS NOTIFIED OF THIS EVENT BY THE LICENSEE. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | IMode1: Decommissioned; FMode1: Decommissioned | NON EMERGENCY | 1 | CT | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-08-04
40045 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2003-08-03 04:30 | 2003-08-03 11:10 | 2003-08-03 | TURBINE TRIP/REACTOR TRIP The following information was received from the licensee via facsimile: "At 04:30 [EDT], Indian Point 2 lost all load due to an Offsite electrical disturbance. The loss of load caused the Turbine-Generator speed to increase above 1800 RPM resulting in a "TURBINE CONTROL OIL AUTO TRIP" which in turn caused a REACTOR TRIP. "The over frequency condition prevented the FAST TRANSFER of Bus 1, 2, 3 and 4 to the Station Auxiliary Transformer, resulting in a loss of all Reactor Coolant Pumps and power to Safeguards Bus 2A and 3A. "All Emergency Diesel Generators auto-started as required. Power remained available to Safeguards Buses 5A and 6A from the Station Auxiliary Transformer and the EDGs did not assume load. "Auxiliary Feedwater (AFW) Pumps 22 and 23 automatically started on low steam generator level condition. AFW pump 21 did not start due to loss of power to bus 3A. "Power was restored to bus 2A and 3A by manual closure of the output breakers of EDG 22 at approximately 4:40. Initial core cooling was provided by natural circulation cooling. "The Condenser remained available as a heat sink and the Steam Generator Atmospheric Relief Valves and Safety Valves remained closed. "A Pressurizer Power Operated Relief Valve (PORV) actuated, resulting in discharge to the Pressurizer Relief Tank (PRT), which remained intact. The Pressurizer Code Safety Valves remained closed. "Forced RCS circulation was re-established at 05:30. At present 3 RCPs [Reactor Coolant Pumps] have been restored to service, with actions in progress to restore the fourth RCP. "Currently, plant conditions [are] Hot Zero Power with preparations for unit recovery in progress." The electrical disturbance in the switchyard was due to electrical storms in the area. All rods inserted into the core during the trip. The site's other nuclear unit was not affected. All electrical feeders required by Technical Specifications are in service at this time. Notified Region 1 PAO (Neil Sheehan) & Headquarters PAO (Beth Hayden). & EDO Office (Ho Nieh). The licensee has notified the NRC Resident Inspector. | 0 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | A/R | N | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION |  |  | IMode1: Power Operation; FMode1: Hot Standby | NON EMERGENCY | 1 | NY | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) |  |  | 0 | 2003-08-03
40044 | 0 | NATIONAL INSTITUTE OF HEALTH |  |  |  |  | 2003-06-27 | 2003-08-01 15:46 | 2003-08-01 | LOST VIAL OF PHOSPHORUS-32 The following information was obtained from the licensee via facsimile: "This is a potential 30 day report of loss of licensed material in accordance with 10CFR20.2201(a)(ii). I use the qualifier 'potential' because the regulation as written is confusing as to what the activity of the missing material must be to qualify as a reportable at the time of the report. The lost material was a vial of Perkin-Elmer Easytides P-32 [Phosphorus-32]-DCTP, 250 microCurie (9.25 Mbq) on the day of loss. Today, the activity would be approximately 50 microCurie, which would not be reportable under the regulation. However, due to the confusion created by the wording of the regulation, I am conservatively reporting the event. "On July 7, 2003 the NIH Radiation Safety Branch was called by a purchasing agent at the Gerontology Research Center (GRC), Baltimore, MD to inquire as to the status of an item of radioactive material ordered in June. The GRC is a research facility of the National Institute on Aging, part of the NIH. Our database indicated that the item in question had been received and processed in at Building 21 on the Bethesda, MD main campus on June 27, 2003 and subsequently delivered to the GRC facility the afternoon of that same day. "Following the inquiry, a search for the material was conducted by the Authorized User and also, on July 8, 2003, by the Health Physicist assigned to the GRC, accompanied by one of the contract delivery technicians. This search was exhaustive, covering every corridor in the complex as well as each lab where five other items were delivered on June 27, 2003. The item was not discovered in inventory within any laboratory, nor in any corridor. "At this time, our conclusion is that the item was inadvertently misplaced during the delivery run of the six items that day, probably in a corridor. The container for the item was a cardboard box labeled Radioactive Material-Excepted Package-Limited Quantity of Material, UN2910. The box was likely mistaken as empty and disposed of to the refuse dumpster servicing the GRC facility on June 27, 2003. "The low volume comprising the Easytides product is doubly-contained within a very durable Plexiglas vial, which also serves to shield the beta emissions from the P-32. Therefore we believe it is very unlikely that anyone would have been exposed to the P-32 as a result of the disposition of the vial into municipal refuse. "Corrective measures have been implemented with the delivery contractor to prevent the likelihood of another such loss in the future." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | LOST/STOLEN LNM>10X | [9 empty] | NON EMERGENCY | 1 | MD | OTH | GEN | 20.2201(a)(1)(ii) |  |  |  | 0 | 2003-08-01
40043 | 0 | BYRON | 1 | 2 |  | [1] W-4-LP,[2] W-4-LP | 2003-08-01 11:07 | 2003-08-01 15:35 | 2003-08-01 | OFFSITE NOTIFICATION DUE TO MINOR OIL SPILL The following information was received by the licensee via facsimile: "During the restoration of the 0A River Screen House air compressor, lubricating oil leaked internal to the compressor and was blown down to a drain trench which discharged to the Rock River. A film or sheen of approximately 2 square feet was observed on the Rock River water surface. An estimated three cups of lubricating oil was discharged [through] the drain trench to the Rock River. Based on this information, a notification to the Illinois Emergency Management Agency (IEMA) was performed within 15 minutes, and notification to the National Response Center within 1 hour was performed. Actions taken to stop the discharge include isolation of the air compressor blowdown flowpath and placement of oil absorbent rags at the discharge location to the Rock River. The discharge of oil has been terminated." The licensee has notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | OFFSITE NOTIFICATION |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 3 | IL | POW |  | 50.72(b)(2)(xi) |  |  |  | 0 | 2003-08-01
40042 | 0 | ILLINOIS DEPT OF NUCLEAR SAFETY |  |  |  |  | 2003-07-28 | 2003-07-31 17:50 | 2003-08-01 | AGREEMENT STATE REPORT - MEDICAL EVENT The following information was received via e-mail from the Illinois Department of Nuclear Safety: "Abstract: "The agency [Illinois Department of Nuclear Safety] received a call July 29, 2003 from a nuclear medicine technician, at Rush Copley Medical Center in Aurora, IL [deleted]. She reported that a patient who was to receive a 4 milliCi unit dose of Tl-201 [Thallium-201] for a heart test instead received a 4 milliCi unit dose of I-131 [Iodine-131] on July 28, 2003. "Circumstances surrounding the event, as reported by the technician, indicate that both the exterior lead container and syringe were labeled as being Tl-201. Although the injection occurred the previous day it was not determined that I-131 was involved until after the gamma cameras used for patient imaging were checked a second time on the morning of July 29th. Service engineers had been called to the site both days to inspect the cameras after both failed attempts to image the patient. The cause became evident when a gamma camera flood source that had been made from what was thought to be the remaining Tl-201 material in the syringe from 7/29/2003 showed peaks consistent with I-131. The assayed amount from Monday's records showed the dose to be within the expected range for a typical 4 milliCi Tl-201 diagnostic doses and as such, was considered to be normal. The technician indicated that the patient involved had been contacted by the referring physician, the onsite oncologists, the hospital Administrator and lawyer and was informed as to what had happened. The hospital has arranged to perform routine blood analysis throughout the year to monitor any changes in thyroid activity. "The RSO [Radiation Safety Officer] and oncologist at the facility, [deleted], were then contacted by the Agency. He indicated that it is very unlikely that any changes will be noted in the patient. He reports that the dose administered, is only slightly larger than that typically ordered for whole body scans using I-131. Regardless, they have offered to provide routine blood testing of the patient throughout the year for T3, T4 and T7 thyroid hormones levels as part of a follow up evaluation. "A call was then made to the Medi Physics/Amersham Health, [deleted] Wood Dale pharmacy facility where the doses had been prepared the previous Friday. [Deleted], Corporate RSO indicated that they were in the process of determining what had occurred but it appeared that when prescriptions and labels were taken from the computer system a 4 milliCi Tl-201 prescription was mistakenly put in with 4 other prescriptions for 4 milliCi unit doses of I-131 to be filled. Subsequently, the Tl-201 request was mistakenly filled as an I-131 prescription. The difference in nuclides was not noted by the pharmacist when the pre-generated Tl-201 labels were applied to the syringe and lead container which now held I-131. "The Agency sent an investigator to the medical center on the morning or July 30 to observe the labeling on the container and syringe, receipt records, gamma camera QA tests and to verify by gamma spectrum analysis the presence of I-131 as well as to conduct preliminary interviews to obtain additional facts. The investigation then moved on to the pharmacy to continue their review of the event. Based on those visits, the information obtained largely confirmed the preliminary notification. The Agency is continuing its investigation of the matter and is expecting reports to be filed by both parties according to regulatory requirements. "Preliminary estimates of EDE to the whole body of 355 Rem and 11,672 Rad to the thyroid based on ICRP 53 modeling assuming 55% uptake and standard man conditions has been calculated. Similar preliminary estimates based on the package insert assuming 25% uptake resulted in 1,628 Rads and 5,328 Rads respectively. The two estimates vary widely because of unknown factors associated with the patient's condition. NRC Operations Center was notified of the event at 17[50] on 31 July 2003 and assigned Event Number 40042." *** UPDATED AT 1705 EDT ON 8/1/03 FROM KLINGER TO CROUCH *** Last paragraph of above report was amended to read as follows: "Preliminary estimates of dose to the thyroid range from 5,300 Rads to 11,700 Rads. The two estimates vary widely because of unknown factors associated with the patient's condition. NRC Operations Center was notified of the event at 1750 E.S.T on 31 July 2003 and assigned Event Number 40042." | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 3 | IL | OTH | AGR |  |  |  |  | 0 | 2003-08-05
40041 | 0 | HATCH | 1 | 2 |  | [1] GE-4,[2] GE-4 | 2003-07-31 15:20 | 2003-07-31 17:02 | 2003-07-31 | TEMPORARY LOSS OF EMERGENCY ASSESSMENT CAPABILITIES The following information was obtained from the licensee via facsimile: "NOAA Weather Radio Prompt Notification System was found not working. This results in a major loss of the offsite notification system. The State of Georgia (GEMA) [Georgia Emergency Management Agency] and the four EPZ [Emergency Planning Zone] counties were notified of the NOAA Weather Radio Prompt Notification System outage. "NOAA Weather Radio Prompt Notification System was returned to service at 1642 EDT. The State of Georgia (GEMA) and the four EPZ counties were notified of the NOAA Weather Radio Prompt Notification System being returned to service." The four counties notified were: Tattnall, Jeff Davis, Toombs and Appling counties. The licensee notified the NRC Resident Inspector. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | GA | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-07-31
40040 | 0 | VIRGINIA DEPT. OF HEALTH |  |  |  |  | 2003-07-31 | 2003-07-31 14:00 | 2003-07-31 | CESIUM-137 PIPE SOURCE DISCOVERED IN SCRAP METAL NRC Region 2 personnel were notified by the Commonwealth of Virginia, Department of Health, Bureau of Radiological Health that a metal dealer, Smith Iron & Metal Company, located in Richmond, VA had discovered a Cs-137 pipe source in some scrap material. The pipe measured approximately 24 inches long with a 6 inch diameter. The pipe was sheared in two and sent to Chaparral Virginia Steel Recycling, located in Petersburg, VA, where is set off portal monitors. Chaparral isolated the material and returned it to Smith Iron & Metal. Smith contacted the Commonwealth of Virginia who dispatched a response team. The response team determined that there was no external contamination on the pipe. Contact readings are at 120 mR/hr with <2.6 mR/hr readings at three feet. There were no identifying marks on the source. The source is currently isolated on a trailer at Smith Iron & Metal. Region 2 NRC with be sending a team of personnel to investigate. The Environmental Protection Agency has been notified. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | INFORMATION ONLY | [9 empty] | NON EMERGENCY | 2 | VA | MAT | [5 empty] | 0 | 2003-07-31
40039 | 0 | SAINT LUCIE | 1 | 2 |  | [1] CE,[2] CE | 2003-07-31 01:10 | 2003-07-31 05:59 | 2003-07-31 | EMERGENCY RESPONSE DATA ACQUISTION AND DISPLAY SYSTEM (ERDADS) INOPERABLE FOR GREATER THAN ONE HOUR "Emergency Response Data Acquisition and Display (ERDADS) computer failed at 0110 on 7/31/03. It was successfully restored to service at 0235. This resulted in the loss of the Safety Parameter Display System (SPDS) and Emergency Response Data System (ERDS) for greater than one hour. This event is reportable as a eight hour non-emergency notification per 10CFR50.72(b)(3)(xiii) in that the failure constituted a major loss of emergency assessment capability, offsite response capability, or offsite communications capability." The NRC Resident Inspector will be notified of this event by the licensee. | 100 | 100 | 0 | 100 | 100 | 0 | -1 | -1 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | Power Operation | Power Operation |  | Power Operation | Power Operation |  | NON EMERGENCY | 2 | FL | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-07-31
40038 | 0 | INDIAN POINT | 2 |  |  | [2] W-4-LP,[3] W-4-LP | 2003-07-30 12:10 | 2003-07-30 18:15 | 2003-07-30 | CHLORINATION SAMPLING NOT PERFORMED IN ACCORDANCE WITH DISCHARGE PERMIT "On 7/30/03 at 1210 [EDT], chlorination was started on 21 circulating water pump bay. The first sample for chlorine concentration was not obtained until one hour after the start of chlorination. The SPDES permit requires 30-minute samples." The licensee will notify the NRC Resident Inspector. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | OTHER UNSPEC REQMNT |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 1 | NY | POW | [5 empty] | 0 | 2003-07-30
40037 | 0 | PORTSMOUTH GASEOUS DIFFUSION PLANT |  |  |  | URANIUM ENRICHMENT FACILITY | 2003-07-30 03:00 | 2003-07-30 17:51 | 2003-07-30 | REMOTE OPERABILITY OF PIGTAIL LINE ISOLATION DISABLED "On 07/30/03 at 0300 hrs [EDT] the Plant Shift Superintendent's (PSS) office was notified by operations personnel at the X-344 facility, that the air supply line to the Parent Cylinder Safety Valve on Autoclave #3 (Q safety system component) appeared to be severely damaged. The PSS on duty and the Shift Engineer (SE) responded to assess the condition, and determined that the Parent Cylinder Safety Valve air supply line was damaged and would not or could not have performed its intended safety function. The PSS declared the Parent Cylinder Safety Valve inoperable and directed operations personnel at the X-344 facility to place autoclave #3 into mode VII (Shutdown). "The damaged air line had apparently been present during applicable TSR modes, II (Heating), III (Cylinder/Pigtail Operations) and IV (Feeding, Transfer or Sampling). This condition is reportable under 76.120 (c)(2)(ii) and 76.120 (d)(2). The equipment is required by Technical Safety Requirements (TSR) to be available and operable and either should have been operating or should have operated on demand." The certificate holder notified the NRC Resident Inspector. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Fuel Cycle Facility | SAFETY EQUIPMENT FAILURE | [9 empty] | NON EMERGENCY | 3 | OH | FUE |  | 76.120(c)(2) |  |  |  | 0 | 2003-07-30
40036 | 0 | METAL MANAGEMENT AEROSPACE |  |  |  |  | 2003-07-30 15:00 | 2003-07-30 16:52 | 2003-07-30 | LEAK TEST RESULTS OF SEALED SOURCE EXCEED ALLOWABLE LIMITS On 6/11/03 Metal Management Aerospace arranged for leak testing of a 20 millicurie Cd-109 sealed source, S/N 942-24, by RSA Laboratories in Hebron, CT. The results were received at 1500 EDT today, 7/30. The activity was measured at 0.437 microcuries which exceeds the limit of 0.005 microcuries as specified in the license. This source is used in a Kevex Spectrometer model 6700 for alloy identification. The licensee has discontinued use of the spectrometer until it's decontaminated and will contact the source manufacturer, Isotope Products located in Burbank, CA, for return. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | Other Nuclear Material | OTHER UNSPEC REQMNT | [9 empty] | NON EMERGENCY | 1 | CT | MAT | [5 empty] | 0 | 2003-07-30
40035 | 0 | MA RADIATION CONTROL PROGRAM |  |  |  |  | 2003-07-30 | 2003-07-30 12:56 | 2003-09-03 | AGREEMENT STATE REPORT ON DAMAGED GENERALLY LICENSED LEVEL GAUGE "On 7/28/03 Wheelabrator became aware that a TN [Texas Nuclear] Level Gauge, Cs-137 100 mCi [milli Curie] [Model Number: 5197] SN # B728 (SS&D No. TX634D119B) had gone missing. Plant was in shutdown and work was being performed on the associated hopper. The gauge was removed not following standard procedure. A search of the premises was conducted with negative results. A consultant was hired, and located the gauge in a scrap metal pile on the morning of 7/30/03. The shielding was partially melted away, it was surmised that the gauge may have passed through the boiler. The consultant performed radiation surveys and placed the gauge in a metal container in the storage area. The manufacturer was contacted, arrangements will be made to return the gauge. "Cause description: Gauge removed from frame to accommodate work taking place on hopper (steel replacement). "Precipitating factor: Not secured in storage area; typically used a secure holding area prior to shipping/installation." State Event Number: MA 03-0023 Wheelabrator is located at 100 Salem Turnpike, Saugus, MA. * * * UPDATE FROM IANNACCONE TO CROUCH ON 9/03/03 * * * "On July 30, 2003, gauge was located: casing intact, Pb [Lead] shielding melted. Secured, survey. Leak test results SAT, dose assessment for members of public SAT, shipped to [manufacturer], and staff was re-trained." Notified R1DO (Henderson) and NMSS EO (Broaddus). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 1 | MA | OTH | AGR |  |  |  |  | 0 | 2003-08-04
40034 | 0 | PALO VERDE | 1 |  |  | [1] CE,[2] CE,[3] CE | 2003-07-29 23:44 | 2003-07-30 07:45 | 2003-07-30 | LOSS OF 9 OF THE 42 EMERGENCY EVACUATIONS SIRENS DUE TO STORM "On July 29, 2003 at approximately 23:44 Mountain Standard Time, the Palo Verde Unit 1 control room was notified of a power failure, probably due to a storm that recently passed through the area of Buckeye, AZ, causing the loss of 9 of the 42 emergency evacuation sirens. The 9 affected sirens are estimated to impact approximately 26% of the population in the emergency planning zone (EPZ). This call is being placed due to the relatively large segment of the population affected, and the uncertainty of the length of time that will be needed to restore electrical power to the affected areas. The Palo Verde Emergency Plan (section 6.6.2.1) has a contingency for dispatching Maricopa County Sheriff's Office (MCSO) vehicles with loud speakers to alert persons within the affected area (s) when sirens are inoperable. "There are no events in progress that require siren operation. "The NRC Resident Inspector has been notified of the siren failure and this ENS call." * * * UPDATE ON 7/30/03 AT 1200 EDT FROM DAN MARKS TO S. SANDIN * * * "On July 30, 2003, at approximately 08:15 AM (MST), the Palo Verde Unit 1 control room was notified that power had been restored to the 9 emergency evacuation sirens. The NRC Resident Inspector has been notified." Notified R4DO (Cain) | 98 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | LOSS COMM/ASMT/RESPONSE |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(3)(xiii) |  |  |  | 0 | 2003-07-30
40033 | 0 | PALO VERDE |  | 2 |  | [1] CE,[2] CE,[3] CE | 2003-07-29 15:16 | 2003-07-29 21:13 | 2003-08-06 | UNIT 2 WAS MANUALLY TRIPPED AFTER A STUCK OPEN SPRAY VALVE FAILED TO CLOSE "On July 29, 2003, at approximately 1518 Mountain Standard Time (MST) Palo Verde Unit 2 plant operators manually tripped the reactor from approximately 98% rated thermal power due to reduced reactor coolant system pressure when a pressurizer spray valve opened and failed to close on operator demand. Unit 2 was at normal temperature and pressure prior to the trip. All CEAs inserted fully into the reactor core. This was an uncomplicated reactor trip. No emergency classification was required per the Emergency Plan. Containment Isolation and Safety Injection Actuation Signals were received following the manual reactor trip per design. Safety related buses remained energized during and following the reactor trip. No significant LCOs have been entered as a result of this event. The pressurizer spray valve that initiated the event was being placed in service following maintenance. "Unit 2 is stabilized in Mode 3 at approximately 564 degrees F and 2200 psia. The reactor coolant system remains in natural circulation with heat removal via Steam Bypass Control to the main condenser. The event did not result in any challenges to fission product barriers and there were no adverse safety consequences as a result of this event. The event did not adversely affect the safe operation of the plant or the health and safety of the public. "The Resident Inspector was informed of the Unit 2 reactor trip and this notification. The Resident Inspector is onsite to observe response to the reactor trip. "The reactor coolant pumps were secured after the trip to stop continued spray flow and depressurization per the alarm response procedure. The offsite electrical power grid is stable." * * * UPDATE ON 8/6/03 AT 2325 EDT FROM D. GRAFF TO E. THOMAS * * * "At the time of the initial notification it was not believed that an ECCS discharge to the RCS occurred. Subsequent review of post-trip data determined that injection did occur. The total accumulated actuation cycles to date for Palo Verde Unit 2 is 8. The thermal fatigue limit is 160 cycles, thus the unit is well within the 0.70 (70%) usage threshold of 112 cycles. "Unit 2 is in Mode 1 at approximately 98% power, normal operating temperature and pressure. "The NRC Resident Inspector has been notified of this followup notification." The ECCS actuation occurred on a low pressurizer pressure signal. Notified R4DO (J. Whitten) | 0 | 0 | 0 | 0 | 98 | 0 | 0 | -1 | 0 | N | M/R | N | Power Reactor | RPS ACTUATION - CRITICAL | VALID SPECIF SYS ACTUATION | ECCS INJECTION |  | IMode2: Power Operation; FMode2: Hot Standby | NON EMERGENCY | 4 | AZ | POW |  | 50.72(b)(2)(iv)(B) | 50.72(b)(3)(iv)(A) | 50.72(b)(2)(iv)(A) |  | 0 | 2003-07-29
40032 | 0 | HARRIS | 1 |  |  | [1] W-3-LP | 2003-07-29 20:00 | 2003-07-29 20:59 | 2003-07-31 | SURFACE CONTAMINATION LEVELS ABOVE LIMITS "This report is generated due to finding smearable contamination on the spent fuel shipping cask. Smearable contamination in excess of 10CFR71.87 requires a one hour report. Due to 10CFR21, we cannot disclose further information over non-secure communications." The licensee informed the NRC Resident Inspector. Additional information can be obtained from the NRC Operations Center. * * * Update on 07/31/03 at 1011 EDT by G. Gazda to MacKinnon * * * Highest corrected contamination level for beta gamma was 43,980 dpm per 100 square centimeter (limit is 22,000 dpm per 100 square centimeter). All other smears taken were within limits. R2DO (JIM MOORMAN) & NMSS (DANIEL GILLEN) notified. NRC Resident Inspector was notified of this update by the licensee. | 100 | 0 | 0 | 100 | 0 | 0 | -1 | 0 | 0 | N | N | N | Power Reactor | SURFACE CONTAM LEVELS > LIMITS |  |  |  | IMode1: Power Operation; FMode1: Power Operation | NON EMERGENCY | 2 | NC | POW |  | 20.1906(d)(1) |  |  |  | 0 | 2003-07-29
40031 | 0 | TEXAS DEPARTMENT OF HEALTH |  |  |  |  | 2003-07-25 10:45 | 2003-07-29 17:22 | 2003-07-29 | AGREEMENT STATE REPORT OF PERSONNEL OVEREXPOSURE "A [radiography] source was not retracted to the fully shielded position resulting in a 17.978 R exposure to a radiographer and a 2.650 R exposure to a trainee. A trainer was also at the job site, but was not exposed during the event. The radiographers were up on top of a scaffolding platform radiographing a 100 foot high vessel. The first exposure ran for 2 minutes and the film was too light for use. The second exposure ran for 5 minutes and the radiographer cranked the source back, but not all the way. The source remained 6-8 inches outside the shielded position. The radiographers were up on the scaffolding in an 8 foot space for about 15 minutes with the source exposed. When the radiographers came to make a third exposure, they noticed the source was out. It took about 1 to 11/2 cranks to retract it. The crank cables were about 35 feet long and guide tubes were used. "The radiographer's ratemeter did not work and the trainee did not hear his above the excessive noise and the earplugs. Both pocket dosimeters were off scale. The dosimeters were sent for emergency processing on Friday, July 25, 2003, to determine if an overexposure had occurred. The exposure results were received by the Licensee on Monday, July 28, 2003. The Licensee then reported the exposure to the Agency. An Agency inspector made a site visit to the Licensee's facility to investigate the event on July 29, 2003." Equipment: SPEC 300 exposure device ser. #: 009 Source: 99 Curie cobalt-60, SPEC Model G70, ser. #: C60-02 This occurred at the Amoco Refinery in Texas City, TX. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N | N | N | General Information or Other | AGREEMENT STATE | [9 empty] | NON EMERGENCY | 4 | TX | OTH | AGR |  |  |  |  | 0 | 2003-08-01